## Operational Issues
PERSONGROUP | LOGBOOK_MONTH | LDTEXT | DESCRIPTION | EVENTDATE
WW-NORTH | February | Performed station check Decanted/transferred sludge thickening tanks Batch wasted into tank 1, fed tank 2 until full, then directed WAS to tank 3 Completed lab and entered readings into ACE sheet Topped up caustic and hypo tanks Turned off alum feed to floc tank Rotated effluent pump duties. | Keswick Water Resource Recovery Facility | 2026-02-23
WW-NORTH | February | Onsite for daily operations Review scada/trends Decant stt 2 and 3 Transfer stt 3 Collect in house lab samples Complete lab - data in sharepoint Check station Rake and level grit bin | Keswick Water Resource Recovery Facility | 2026-02-27
WW-NORTH | February | Performed station check Decanted/transferred sludge thickening tanks Fed tank 3 until full, then directed WAS to tank 2 Completed lab and entered readings into ACE sheet Rotated UV bank 1A into service and replaced three bulbs on bank 2A (7-7, 15-7 and 15-8) Inspected OCU and recorded readings in binder. | Keswick Water Resource Recovery Facility | 2026-02-26
WW-NORTH | February | Performed station check Decanted/transferred sludge thickening tanks Batch wasted into tank 1, fed tank 3 until full, then directed WAS to tank 2 Completed lab and entered readings into ACE sheet Received alum delivery Inspected air compressors Inspected membrane turbidimeters Inspected OCU and recorded readings in binder Exercised alum chemical panel valves Investigated UV bank 1A low intensity readings. | Keswick Water Resource Recovery Facility | 2026-02-24
WW-NORTH | February | Onsite for daily operations Review scada/trends Decant stt 1 and 3 plus transfer Ras pumps off for batch waste Collect in house lab samples Collect weekly regulatory samples Complete lab - Enter data in sharepoint Check station Rake and level grit bin TSS probe cleaning Replace UV magnetic rod for wiper system on UV 1 rack 9 | Keswick Water Resource Recovery Facility | 2026-02-25
WW-NORTH | February | Attended for sludge handling Decanted/transferred sludge thickening tanks Switched WAS feed to sludge thickening tank 2 Cleaned bar screen and raked bin Reset channel blower #2 alarm Cleared blockage from microscreeen discharge. | Keswick Water Resource Recovery Facility | 2026-02-01
WW-NORTH | February | Onsite for daily operations Review scada/trends Decant stt 1 and 2 Transfer stt 1 Turn off Ras pumps for batch waste Collect in house lab samples Complete lab - data in sharepoint Check station Rake and level bin Miller waste empty grit bin 1 Batch waste approx 80m3 into stt 1 Switch WAS to STT 2 Cl2 Analyzer inspection HCLA pumps inspection Hose membrane sump Membrane room janitorial OCU maintenance | Keswick Water Resource Recovery Facility | 2026-02-02
WW-NORTH | February | switched WAS feed from STT2 to STT3. checked SCADA | Keswick Water Resource Recovery Facility | 2026-02-14
WW-NORTH | February | switched WAS feed from STT3 to STT1 checked SCADA | Keswick Water Resource Recovery Facility | 2026-02-16
WW-NORTH | February | Started Decanted STT 2 and 3 and switched WAS flow from STT 1 to STT 2 | Keswick Water Resource Recovery Facility | 2026-02-22
WW-NORTH | February | Completed monthly PM work orders: -Microscreens 1 & 2 inspection -Recirculation/Neutralization pumps and motors 1 & 2 inspection -Membrane Tanks 1-5, Valve actuator blow down & Inspection -Backpulse Pumps 1-2 Pumps and motors inspection Took down safety guard rail and placed covers back on Train 5 Reset collection blower 2 high differential pressure; cleaned filter and inspected intake line outside | Keswick Water Resource Recovery Facility | 2026-02-13
WW-NORTH | February | Performed station check Decanted/transferred sludge thickening tanks Batch wasted into tank 1, then directed WAS to tank 2 Completed lab and entered readings into ACE sheet Topped up temporary hypo tank Flushed caustic lines and refilled tank Rotated effluent p.1 into duty Reset sludge holding tank blower 1- High differential pressure; cleared ice build up on intake screen Completed scheduled work orders and notified ROC of work being completed Cleaned TSS probe Completed aeration tanks D.O. probe cleaning and verification T1: IN = 1.61 mg/L Grab = 1.66 mg/L OUT = 2.09 mg/L Grab = 2.20 mg/L T2: IN = 1.55 mg/L Grab = 1.76 mg/L OUT = 2.29 mg/L Grab = 2.65 mg/L Completed membranes 1-5 inspection and cleaning Completed membrane room sluice gates (microscreens) exercise and maintenance Started generator in local at 11:20 for Total Power to complete load test Shut down generator at 15:30 and remained until connections were complete and generator was returned to standby. | Keswick Water Resource Recovery Facility | 2026-02-17
WW-NORTH | February | on site 0800hrs sludge handling, started decanting. out 0830hrs to Sutton back @ 0940hrs checked SCADA sludge done, WAS feeding STT3 | Keswick Water Resource Recovery Facility | 2026-02-15
WW-NORTH | February | Onsite for daily operations Review scada/trends Decant stt 2 and 3 plus transfer 3 Ras pumps off for batch waste Collect in house lab samples Complete lab- Enter data in sharepoint Check station Rake/level bin Change was feed to stt 1 and batch waste 80m3 Switch was feed to stt 2 for top up then to stt 3 for remainder of evening Clean/Pump out caustic tank OCU maintenance | Keswick Water Resource Recovery Facility | 2026-02-12
WW-NORTH | February | Performed station check Decanted/transferred sludge thickening tanks Fed tank 3 until full, then directed WAS to tank 2 Completed lab and entered readings into ACE sheet Collected weekly regulatory samples and delivered to Newmarket Completed scheduled work orders and notified ROC of work being completed Cleaned TSS probe Rotated UV bank 1A into service Completed consolidated headworks inspection Tested headworks gas detectors Cleaned membrane turbidimeters Exercised alum chemical panel valves Performed clarifier maintenance Collected alkalinity sample from groundwater dewatering wells (270 mg/L). | Keswick Water Resource Recovery Facility | 2026-02-11
WW-NORTH | February | Nsite to for daily operation Review scada/trends Decant stt 1 2 and 3 plus transfer Was feed stt 3 Check station Rake and level bin Colldct in house lab samples Complete lab Data in sharepoint Exercise outfall sluice gates | Keswick Water Resource Recovery Facility | 2026-02-13
WW-NORTH | February | Performed station check Decanted/transferred sludge thickening tanks Fed tank 2 until full, then directed WAS to tank 3 Completed lab and entered readings into ACE sheet Replaced air filter on headworks collection box blower 2 Topped up hypo tank Cleaned aeration tank 2 outlet DO probe (rag buildup) Cleaned TSS probe Turned on alum p.6 to floc tank Programmed three R-cleans for a 19:00 start (trains 1,4, and 5) Assisted A&B with off-load generator run to test temporary feed directly from bulk tank while work is done on day tank. | Keswick Water Resource Recovery Facility | 2026-02-20
WW-NORTH | February | Replaced broken piping on compressor 2 | Keswick Water Resource Recovery Facility | 2026-02-19
WW-NORTH | February | Performed station check Decanted/transferred sludge thickening tanks Batch wasted into tank 1, filled tank 3, then directed WAS to tank 2 Completed lab and entered readings into ACE sheet Reset collection box blower 2 alarm - keeps faulting upon startup Inspected OCU and recorded readings in binder Returned air compressor 2 to service after maintenance repaired it. | Keswick Water Resource Recovery Facility | 2026-02-19
WW-NORTH | February | Onsite for daily operation Review scada/trends Decant stt 1 and 2 Transfer stt 1 and switch was feed to stt 1 All ras pumps off for batch waste Collect in house lab samples Collect weekly regulatory samples Check compressors - find pinhole leak on pressure switch line for compressor 2 Isolate compressor 2 and place in local off. Disable duty rotate for compressors Check station Rake and level grit bin Pump down both scum tanks TSS probe clean Alum valve exercise Hypo pump inspection Top up caustic tank Hose alum containment area | Keswick Water Resource Recovery Facility | 2026-02-18
WW-NORTH | February | on site 0700hrs sludge handling station checks lab and readings alum delivery, stated unloading at 1450hrs Uv channel 1A rack2 bulb1 replaced scum tanks pumped down. investigated broken chain link fence. | Keswick Water Resource Recovery Facility | 2026-02-06
WW-NORTH | February | Completed monthly PM work orders: -Headworks gas detectors test -Grit vortex dewatering press 1 & 2 inspection -Screenings press 1 & 2 inspection -Travelling screen 2 inspection | Keswick Water Resource Recovery Facility | 2026-02-11
WW-NORTH | February | Onsite for daily operations Review scada/trends Decant stt 2 and 3 RAS pumps off for batch waste Collect in house lab samples complete lab - data in sharepoint Transfer stt 3 Batch waste 80m3 into stt 1 Switch was feed to stt 2 Check station Rake and level grit bin Major fault came in on UV channel 1 (standby) where one rack lost comms. Adjust wiring and clear comm alarm, fault cleared and uv1 back in duty 2 DO probe maintenance | Keswick Water Resource Recovery Facility | 2026-02-10
WW-NORTH | February | Reset collection box, blower left in manual off Received ALUM delivery ALUM overfilled and spilled approximately 10 gallons into containment area | Keswick Water Resource Recovery Facility | 2026-02-06
WW-NORTH | February | Open WAS tank one close WAS tank three Review area SCADA | Keswick Water Resource Recovery Facility | 2026-02-07
WW-NORTH | February | Continue sludge handling Review SCADA Check micro screens Reset channel blower Reset biorim re-cert pump | Keswick Water Resource Recovery Facility | 2026-02-08
WW-NORTH | February | Performed station check Decanted/transferred sludge thickening tanks Fed tank 2 until full, then directed WAS to tank 3 Completed lab and entered readings into ACE sheet Collected weekly samples and delivered to Newmarket Completed scheduled work orders Performed RAS/WAS hoist inspection Inspected RAS/WAS/Scum pumps Cleaned TSS probe Exercised alum chemical panel valves Performed H&S inspection Inspected generator air compressor Prepared plant for upcoming tour Scheduled two hypo R-cleans for 19:00 start (trains 2 and 4) Primed caustic line and topped up hypo tank Reset collection box and channel blowers Placed membrane blower 1 in manual since it faulted multiple times. | Keswick Water Resource Recovery Facility | 2026-02-04
WW-NORTH | February | Completed lab and entered readings into ACE sheet. | Keswick Water Resource Recovery Facility | 2026-02-05
WW-NORTH | February | wrong book | Keswick Water Resource Recovery Facility | 2026-02-03
WW-NORTH | February | Performed station check Decanted/transferred sludge thickening tank Fed tank 3 until full, then directed WAS to tank 2 Completed lab and entered readings into ACE sheet Turned on alum feed to floc tank and rotated aeration feed alum pumps Cleaned TSS probe Scheduled a hypo R-clean on train 3 for 19:00 Reset sludge blower 1 after clearing frost from inlet Completed scheduled work orders Inspected membrane building drain pumps Received hypo delivery Performed monthly plant blower inspections Inspected odour control and RAS/WAS sump pits and tested high level alarms - in @ 13:41/13:44 Inspected air compressors Inspected sludge transfer pumps and topped up oil on pumps 2 and 3 Inspected OCU and recorded readings in binder. | Keswick Water Resource Recovery Facility | 2026-02-09
WW-NORTH | February | Onsite for daily operations Review scada/trends Decant stt 1 and 2 plus transfer Collect in house lab samples Diesel test run - Alert ROC Transfer station to diesel power at 09:45hrs Transfer station back to hydro at 10:52hrs Clear/reset alarms Complete lab/enter data in sharepoint DO probe maintenance Clear rags from barscreen Remove duck from microscreen reject Compressor check Air dryer check | Keswick Water Resource Recovery Facility | 2026-02-03
WW-NORTH | February | Attending site to check Odor Control Room oxygen sensor (W11630972). Sensor has failed. Replaced sensor and calibrated. ROC was notified before and after maintenance activities. | Keswick Water Resource Recovery Facility | 2026-02-03
WW-NORTH | February | Lower decant tubes remotely on tanks 2&3 Continue decant with pumps on site | Keswick Water Resource Recovery Facility | 2026-02-08
WW-NORTH | February | Onsite to check station | Holland Landing Lagoons | 2026-02-23
WW-NORTH | February | Performed site station check- all secure | Holland Landing Lagoons | 2026-02-13
WW-NORTH | February | Onsite to check station Review scada/trends Enter data in sharepoint Clear info alarms Diesel containment check | Holland Landing Sewage Pumping Station | 2026-02-23
WW-NORTH | February | station checks health and safety check | Holland Landing Lagoons | 2026-02-20
WW-NORTH | February | station checks sharepoint data entry | Holland Landing Sewage Pumping Station | 2026-02-26
WW-NORTH | February | Perform pump PM?s Pump 1, 1654 rpm 58 L/sec Pump 2, 1655 rpm 58 L/sec Pump 3, 1665 rpm 47 L/sec Pump 3 needs adjustment. | Holland Landing Sewage Pumping Station | 2026-02-25
WW-NORTH | February | Rebuild air over hydraulic check valve dampeners for pump 3. | Holland Landing Sewage Pumping Station | 2026-02-25
WW-NORTH | February | Performed facility station check Data in sharepoint Checked diesel containment pit Equipment OOS: none | Holland Landing Sewage Pumping Station | 2026-02-02
WW-NORTH | February | On site to provide operational support for CPD performing pump vibration testing. Placed pumps in manual to increase the wet well level. Ran pump 3 in local at 55, 56, 57, 58, 59 and 60 Hz. Placed facility back to auto and observed normal operation. | Holland Landing Sewage Pumping Station | 2026-02-12
WW-NORTH | February | station checks sharepoint data entry. | Holland Landing Sewage Pumping Station | 2026-02-19
WW-NORTH | February | Completed monthly PM work orders: -JHSC H&S inspection -Odour control scrubber system inspection; inches of water column = 1" -Consolidated dry well & hoist inspection Flow rates @ Pump speed 100% (WWL = 1.89 m) P1 = 78 L/s P2 = 77 L/s P3 = 67 L/s -Generator test run Date: February 10, 2026 Start time: 09:11 Start hours: 278.6 Stop Hours: 279.7 Run Time hours: 1.1 Start Fuel: 238 L Stop Fuel: 396 L Pre run checks: Battery Cell Levels: Ok Battery Terminals and Cables: Ok Oil Level: Ok Coolant Level: Ok Fluid Leaks: Ok Coolant Recirculating pump: Ok Faulty Gauges: Ok Operating Current: 105 amps Operating Frequency: 60.0 Hz Operating Voltage: 600 Volts Engine speed: 1800 RPM Water/coolant Temp: 190 F Oil Pressure: 61 psi No issues with test run | Holland Landing Sewage Pumping Station | 2026-02-10
WW-NORTH | February | Performed facility station check Data in sharepoint Equipment OOS: none | Holland Landing Sewage Pumping Station | 2026-02-12
WW-NORTH | February | station checks sharepoint data entry diesel containment inspection | Holland Landing Sewage Pumping Station | 2026-02-09
WW-NORTH | February | station checks received water delivery sharepoint data entry | East Gwillimbury 2nd Concession Sewage Pumping Station | 2026-02-26
WW-NORTH | February | station checks sharepoint data entry | Holland Landing Sewage Pumping Station | 2026-02-05
WW-NORTH | February | Onsite to check station Review scada/trends Enter data in sharepoint No alarms Clear info alarms Reset dialer - diesel error Diesel containment check | East Gwillimbury 2nd Concession Sewage Pumping Station | 2026-02-23
WW-NORTH | February | Performed facility station check Data in sharepoint Checked diesel containment pit; dry Equipment OOS: none | East Gwillimbury 2nd Concession Sewage Pumping Station | 2026-02-02
WW-NORTH | February | Performed facility station check Data in sharepoint Equipment OOS: none | East Gwillimbury 2nd Concession Sewage Pumping Station | 2026-02-12
WW-NORTH | February | station check sharepoint data entry | East Gwillimbury 2nd Concession Sewage Pumping Station | 2026-02-19
WW-NORTH | February | station checks sharepoint data entry | East Gwillimbury 2nd Concession Sewage Pumping Station | 2026-02-05
WW-NORTH | February | station checks sharepoint data entry diesel containment inspection. | East Gwillimbury 2nd Concession Sewage Pumping Station | 2026-02-09
WW-NORTH | February | Completed monthly PM work orders -Consolidated dry well & hoist inspection -JHSC H&S Inspection -Odour control scrubber system inspection; 1.7 inches of water -Recirculation loop actuator and valve inspection and exercise -Generator test run Date: February 03, 2026 Start time: 09:30 Start hours: 240.8 Stop Hours: 242.2 Run Time hours: 1.4 Start Fuel: 745 L Stop Fuel: 648 L Pre run checks: Battery Cell Levels: Ok Battery Terminals and Cables: Ok Oil Level: Ok Coolant Level: Ok Fluid Leaks: Ok Coolant Recirculating pump: Ok Faulty Gauges: Ok Operating Current: 330 Amps Operating Frequency: 60.0 Hz Operating Voltage: 600 Volts Engine speed: 1800 RPM Water/coolant Temp: 165 F Oil Pressure: 67 psi | East Gwillimbury 2nd Concession Sewage Pumping Station | 2026-02-03
WW-NORTH | February | station check meeting Water delivery truck, tank filled sharepoint data entry | Queensville West Sewage Pumping Station | 2026-02-26
WW-NORTH | February | On site to install new channel grinder. Ran tested and left for operators to put back into service. | Queensville West Sewage Pumping Station | 2026-02-25
WW-NORTH | February | On site to assist with replacement channel grinder, reconnection and testing. Channel grinder back in service. | Queensville West Sewage Pumping Station | 2026-02-25
WW-NORTH | February | Performed CSE into wet well to reinstall manual bar screen channel gate leaves. Placed channel grinder back to auto- observed running without issues | Queensville West Sewage Pumping Station | 2026-02-27
WW-NORTH | February | Onsite to check station Review scada/trends Enter data in sharepoint No alarms Diesel containment check Actuator inspection and exercise | Queensville West Sewage Pumping Station | 2026-02-23
WW-NORTH | February | Performed facility station check Data in sharepoint Equipment OOS: Channel grinder | Queensville West Sewage Pumping Station | 2026-02-02
WW-NORTH | February | Onsite to wrap up annual calibrations and to replace Wetwell 1 LIT2 Informed ROC Used cal mode on scada during the work Created CSE permit Completed force main 1 FIT, force main 1 PIT, H2S gas detectors Entered wetwell and replaced hydrostatic LIT2 Completed configuration and calibration Cleared associated alarms Closed CSE permit Informed ROC, armed building and left site No issues | Queensville West Sewage Pumping Station | 2026-02-20
WW-NORTH | February | Onsite for annual calibrations Informed ROC Used cal mode on scada during calibration Instruments calibrated: Discharge FIT #2, LIT 1, 3 and 4, overflow FIT, channel LIT. Issues calibrating LIT2, Discharge FIT #1 and Discharge PIT2. Will return tomorrow to address the issues. Cleared associated alarms Informed ROC, armed building and left site | Queensville West Sewage Pumping Station | 2026-02-19
WW-NORTH | February | station checks sharepoint data entry channel grinder oos | Queensville West Sewage Pumping Station | 2026-02-19
WW-NORTH | February | Pulled grinder from channel Bringing to shop for a rebuild. | Queensville West Sewage Pumping Station | 2026-02-20
WW-NORTH | February | Attending site to check Hydrostatic wetwell LIT2 (W11654153). Found hydrostatic probe goes to 22mA (out of range high) when power is cycled. Will plan to replace probe in the next few weeks. ROC was notified before and after maintenance activities. | Queensville West Sewage Pumping Station | 2026-02-11
WW-NORTH | February | On site responding to Generator fault & LIT 3/4 OOR -Upon arrival, there was no power at the facility but the ATS panel was indicating we were connected to utility power with 600 V on each phase. Switched power to generator power but still the same issue. Although I was able to run a pump in local. -Appears there was a power blip which briefly caused the generator to start. The generator breaker tripped, along with MCC "Panel AA". The tripped MCC Panel AA was the culprit- once breaker was reset, facility power resumed and facility was operating normally. -It was found that the "duct heater"(1, 3, & 5) breaker in "distribution panel AA", was tripped and resetting this caused it to immediately trip again, subsequently tripping MCC "Panel AA". Work order for property services to address this issue will be created. -WWEL_LIT2 (wet well 1 hydrostatic level) began reading OOR once the other issue resolved. Instrumentation will respond to site to correct the issue. Equipment OOS: channel grinder and wet well 1 hydrostatic level | Queensville West Sewage Pumping Station | 2026-02-10
WW-NORTH | February | Completed monthly PM work orders: -Consolidated dry well & hoist inspection Flow rates @ Pump speed 100% (WWL = 2.15 m) P1 = 73 L/s P2 = 65 L/s -Generator test run Date: February 18, 2026 Start time: 09:49 Start hours: 193.3 Stop Hours: 194.3 Run Time hours: 1.0 Start Fuel: 234 L Stop Fuel: 213 L Pre run checks: Battery Cell Levels: Ok Battery Terminals and Cables: Ok Oil Level: Ok Coolant Level: Ok Fluid Leaks: Ok Coolant Recirculating pump: Ok Faulty Gauges: Ok Operating Current: 31 amps Operating Frequency: 60.0 Hz Operating Voltage: 600 Volts Engine speed: 1800 RPM Water/coolant Temp:185 F Oil Pressure: 67 psi Pyrometer: 450 F No issues with test run; Fuel pump control panel power fail alarm came in on power transfers, able to be cleared immediately. will continue to monitor | Queensville West Sewage Pumping Station | 2026-02-18
WW-NORTH | February | Performed facility station check Data in sharepoint On site to provide operational support for CPD performing pump vibration testing. Placed pumps in manual to increase the wet well level. Ran each pump in local at 52, 56, and 60 Hz separately and running together. Placed facility back to auto and observed normal operation. Equipment OOS: Channel grinder and WW1 hydrostatic transmitter | Queensville West Sewage Pumping Station | 2026-02-12
WW-NORTH | February | station checks sharepopint data entry grinder oos | Queensville West Sewage Pumping Station | 2026-02-05
WW-NORTH | February | on site 1115hrs unable to time in on site, keeps requesting to time out, even though its timed out. station checks health and safety checks. ocu inspection, property services was on site. Heater in OCU room broken, property services looking for a new one to install. channel grinder oos. | Queensville West Sewage Pumping Station | 2026-02-09
WW-NORTH | February | on site 1315hrs station checks sharepoint data entry | Queensville West Sewage Pumping Station | 2026-02-09
WW-NORTH | February | Attended for station check Recorded station/monthly meter readings in rounds sheet Checked blower room - fan 2 running in duty Flushed blowdown on recirc line Drained water from temporary OCU Reviewed SCADA/trends. | Morton Avenue Air Management Facility | 2026-02-26
WW-NORTH | February | station checks sharepoint data entry flushed blowdown | Morton Avenue Air Management Facility | 2026-02-23
WW-NORTH | February | station checks sharepoint data entry switched fans duty, #2 fan now in auto flushed blowdown. no outside odours health and safety check | Morton Avenue Air Management Facility | 2026-02-02
WW-NORTH | February | Station checks completed Enter data into SharePoint Flush re cert line Drain water from temporary carbon unit | Morton Avenue Air Management Facility | 2026-02-19
WW-NORTH | February | on site 1310hrs station checks sharepoint data entry flushed blowdown | Morton Avenue Air Management Facility | 2026-02-12
WW-NORTH | February | Onsite to check station Review scada/trends Enter data in sharepoint Switch fan duties #1 duty 1 Blower inspection - greased both while running Recirculation pump strainer clean Fan body and drip leg check Flush blowdown | Morton Avenue Air Management Facility | 2026-02-09
WW-NORTH | February | on site 1310hrs station checks | Morton Avenue Air Management Facility | 2026-02-12
WW-NORTH | February | Performed station check Received Alum delivery Decanted and transferred STT Cleaned debris build up behind bar screen GFL took sludge load 50m3 Completed lab analysis and entered readings into SharePoint Performed daily sand filter inspection - pulled filter A3 and lanced to remove blockages Pushed out grit and rag bins Checked UV wiper system to confirm proper operation | Sutton Water Resource Recovery Facility | 2026-02-24
WW-NORTH | February | Onsite to check station Review scada/trends Enter data in sharepoint | Morton Avenue Air Management Facility | 2026-02-05
WW-NORTH | February | Performed station check Collected weekly samples W11619894 Decanted and transferred STT Cleaned around bar screen Completed lab analysis and entered readings into SharePoint Checked sand filters | Sutton Water Resource Recovery Facility | 2026-02-25
WW-NORTH | February | Performed station check Decanted and transferred STT Cleaned bar screen Completed lab analysis and entered readings into SharePoint Checked all sand filters | Sutton Water Resource Recovery Facility | 2026-02-26
WW-NORTH | February | Performed station check Completed lab analysis and entered readings into SharePoint Decanted and transferred STT GFL took sludge load 51m3 Checked sand filters - ok | Sutton Water Resource Recovery Facility | 2026-02-23
WW-NORTH | February | Started decanting Cleaned bar screen equipment Checked and leveled grit and rag bins Collected samples for in house labs Checked sand filters Finished decanting and raised gate back to top position Truck took load of sludge Started transfer from S.H.T to S.T.T | Sutton Water Resource Recovery Facility | 2026-02-27
WW-NORTH | February | Attended for sludge handling Decanted sludge thickening tank and initiated transfer Cleaned bar screen area - reset on panel as it was running continuously. | Sutton Water Resource Recovery Facility | 2026-02-01
WW-NORTH | February | Performed station check Decanted STT Completed lab analysis entered readings into SharePoint GFL took 38m3 sludge load Transferred STT * Performed monthly diesel generator test run | Sutton Water Resource Recovery Facility | 2026-02-02
WW-NORTH | February | Started decanting S.T.T Collected samples for in house labs Checked sand filters Completed inspections on air compressors Completed inspections on sludge blowers Cleaned off bar screen equipment Checked and leveled grit and rag bins Replaced sleeve on probe of bank 2A Finished decanting and raised gate back to top position Truck took load of sludge Started transfer from S.H.T to S.T.T Recorded readings in SharePoint | Sutton Water Resource Recovery Facility | 2026-02-13
WW-NORTH | February | Started decanting S.T.T Collected samples for YD labs Collected samples for in house labs Checked and leveled grit and rag bins Cleaned bar screen equipment Checked sand filters Completed UV inspections Change bulb on bank 1B rake 3 bulb 3 Finished decanting and raised gate back to top position Truck took sludge load out Started transfer to S.T.T from S.H.T Entered readings in SharePoint | Sutton Water Resource Recovery Facility | 2026-02-18
WW-NORTH | February | Started decanting S.T.T Collected samples for YD labs Collected samples for in house labs Cleaned bar screen equipment Checked sand filters Finished decanting and raised gate back to top position Truck took out load of sludge Started transfer from S.H.T to S.T.T Recorded readings in SharePoint | Sutton Water Resource Recovery Facility | 2026-02-11
WW-NORTH | February | Started decanting S.T.T Collected samples for in house labs Cleaned bar screen equipment Pushed out bins Checked sand filters Finished decanting and raised gate back to top position Started transfer from S.H.T to S.T.T Rolled bins in | Sutton Water Resource Recovery Facility | 2026-02-10
WW-NORTH | February | On site for SBR blower one vibration LOTO Removed cover and found belt worn. Replaced belt and reinstalled cover Operator ran blower one Checked blower and unit is running well Complete | Sutton Water Resource Recovery Facility | 2026-02-17
WW-NORTH | February | Performed station check Decanted and transferred STT Completed lab analysis and entered readings into SharePoint Cleaned bar screen | Sutton Water Resource Recovery Facility | 2026-02-12
WW-NORTH | February | Performed station check Completed lab analysis and entered readings into SharePoint Decanted and transferred STT GFL took 51m3 Completed assigned EZMax work orders: - Cleaned DO probes - Skimmed SBR debris - Consolidated headworks work order - EQ line flush | Sutton Water Resource Recovery Facility | 2026-02-20
WW-NORTH | February | Decanted and refilled STT | Sutton Water Resource Recovery Facility | 2026-02-22
WW-NORTH | February | checked site sludge handling. | Sutton Water Resource Recovery Facility | 2026-02-15
WW-NORTH | February | Performed station check Completed lab analysis and entered readings into SharePoint Decanted and transferred STT GFL took sludge load 50m3 Assisted electricians on site with bar screen trouble shooting. | Sutton Water Resource Recovery Facility | 2026-02-19
WW-NORTH | February | Started decanting S.T.T Checked and leveled grit and rag bins Cleaned off bar screen equipment Collected samples for in house labs Checked sand filters | Sutton Water Resource Recovery Facility | 2026-02-17
WW-NORTH | February | Decant sludge holding and thickening tanks Transfer and put air back on after decant Rag hopper was plugged - ran in hand and raked and cleared material Put aeration blower one in manual off position blower was jumping around will look into it Monday | Sutton Water Resource Recovery Facility | 2026-02-08
WW-NORTH | February | ROC call regarding UV systems high dosage and gate position Switched to uv 1A | Sutton Water Resource Recovery Facility | 2026-02-04
WW-NORTH | February | Started decanting S.T.T Collected samples for in house labs Cleaned off bar screen equipment Checked and leveled grit and rag bins Finished decanting and raised gate back to top position Rolled bins in Started transfer from S.H.T to S.T.T Entered readings into SharePoint | Sutton Water Resource Recovery Facility | 2026-02-03
WW-NORTH | February | Performed station check Decanted STT and SHT | Sutton Water Resource Recovery Facility | 2026-02-09
WW-NORTH | February | Started decanting S.T.T Collected samples for YD labs Collected samples for in house labs Checked and leveled grit and rag bins Cleaned bar screen equipment Finished decanting and raised gate back to top position Started transfer from S.H.T to S.T.T Checked sand filters Completed SBR and Sludge blower air relief inspections Completed inlet channel hose out Entered readings into SharePoint | Sutton Water Resource Recovery Facility | 2026-02-04
WW-NORTH | February | Started decanting S.T.T Collected samples for in house labs Checked and leveled grit and rag bins Cleaned bar screen equipment Checked sand filters Finished decanting and raise gate back to top position Started transfer from S.H.T | Sutton Water Resource Recovery Facility | 2026-02-06
WW-NORTH | February | Test backflow preventers All three passed | Keswick Sewage Pumping Station | 2026-02-26
WW-NORTH | February | station checks sharepoint data entry OCU oos (warranty) | Keswick Sewage Pumping Station | 2026-02-23
WW-NORTH | February | Onsite to check station Review scada/trends Enter data in sharepoint Clear info alarms | Keswick Sewage Pumping Station | 2026-02-26
WW-NORTH | February | on site 0900hrs. issue with e-log, notified lead and supervisor. Log entry done under remotely while on site. Generator test run. health and safety check ocu oos, GHD and CPD are aware and looking into it?. channel communitor inspection Drywell and hoist inspections. Heat trace inspection generator lolo temp alarm test on scada @1005hrs | Keswick Sewage Pumping Station | 2026-02-10
WW-NORTH | February | on site 0800hrs Met Wessuc on site. Starting on wetwell #1 isolated wetwells. #1 wetwell pumped down, #1 channel grinder off. #2 wetwell controlling wetwell. From Auto mode to Pack mode. out 0930hrs, back on site 1230hrs for wetwell #2 cleaning. 1310hrs Wetwell #1 complete. 1400hrs Wetwell #2 started 1715hrs wetwell #2 done, station all back to normal operation, notified cpo Conner before leaving site. | Keswick Sewage Pumping Station | 2026-02-02
WW-NORTH | February | Station checks completed Enter data into SharePoint | Keswick Sewage Pumping Station | 2026-02-19
WW-NORTH | February | on site 0845hrs for pump testing under warranty. Joe Olivera (CPD) and KSB on site. locked out RSP3 at 0938hrs for KSB locked out RSP2 at 1258hrs for KSB, back into service @1320hrs. RSP3 powered on at 1408hrs, Seal leak alarm on MCC and over temp alarm. RSP3 powered off and locked out again at 1426hrs. 1500hrs RSP3 back in service running in duty 1. 1517hrs RSP3 left in Duty 1 | Keswick Sewage Pumping Station | 2026-02-17
WW-NORTH | February | station checks sharepoint data entry OCU oos (warranty) | Keswick Sewage Pumping Station | 2026-02-12
WW-NORTH | February | Onsite to complete station check Review scada/trends Enter data in sharepoint | Keswick Sewage Pumping Station | 2026-02-05
WW-NORTH | February | Onsite to check station Review scada/trends Clear outstanding alarms - p3 vibration Enter data in sharepoint | Keswick Sewage Pumping Station | 2026-02-09
WW-NORTH | February | On site to take vibration readings | Keswick Sewage Pumping Station | 2026-02-06
WW-NORTH | February | Checked station Viewed HMI and Checked phone - ok Hatches secured Recorded readings in SharePoint | Sutton Woodriver Bend Sewage Pumping Station | 2026-02-26
WW-NORTH | February | Checked station Checked HMI and trends Phone - ok Hatches secured Recorded readings in SharePoint | Sutton Woodriver Bend Sewage Pumping Station | 2026-02-23
WW-NORTH | February | Checked station Viewed HMI and trends Checked phone - ok Hatches secured Recorded readings in SharePoint | Sutton Woodriver Bend Sewage Pumping Station | 2026-02-02
WW-NORTH | February | Test backflow preventer 1 st and 2nd checks failed Installed rubber repair kits and retested Passed | Sutton Woodriver Bend Sewage Pumping Station | 2026-02-17
WW-NORTH | February | Checked station Viewed HMI and trends Checked diesel - ok Checked phone - ok Hatches secured Recorded readings in SharePoint | Sutton Woodriver Bend Sewage Pumping Station | 2026-02-12
WW-NORTH | February | Checked station Viewed HMI and trends Ran diesel generator - no issues Checked phone - ok Hatches secured Completed H+S inspection Recorded readings in SharePoint Back to normal station power | Sutton Woodriver Bend Sewage Pumping Station | 2026-02-09
WW-NORTH | February | Checked station Viewed HMI and trends Checked phone - ok Hatches secured Recorded readings in SharePoint | Sutton Woodriver Bend Sewage Pumping Station | 2026-02-05
WW-NORTH | February | Checked station Viewed HMI and trends Hatches secured Recorded readings in SharePoint | Sutton South River Sewage Pumping Station | 2026-02-26
WW-NORTH | February | Checked station Viewed HMI and trends Hatches secured Recorded readings in SharePoint | Sutton South River Sewage Pumping Station | 2026-02-23
WW-NORTH | February | Checked station Viewed HMI and trends Hatches secured Recorded readings in SharePoint | Sutton South River Sewage Pumping Station | 2026-02-02
WW-NORTH | February | Checked station Viewed HMI and trends Hatches secured Recorded readings in SharePoint | Sutton South River Sewage Pumping Station | 2026-02-12
WW-NORTH | February | Checked station Viewed HMI and trends Hatches secured Recorded readings in SharePoint | Sutton South River Sewage Pumping Station | 2026-02-19
WW-NORTH | February | Checked station Viewed HMI and trends Hatches secured Recorded readings in SharePoint | Sutton South River Sewage Pumping Station | 2026-02-05
WW-NORTH | February | Started decanting S.T.T and S.H.T Collected samples for in house labs Checked and leveled grit and rag bins Clean of bar screen equipment Checked sand filters Finished decanting and raised gates back to top positions Started transfer from S.H.T to S.T.T Recorded readings in SharePoint | Sutton South River Sewage Pumping Station | 2026-02-05
WW-NORTH | February | Checked station Viewed HMI and trends Completed H+S inspection Hatches secured Recorded readings in SharePoint | Sutton South River Sewage Pumping Station | 2026-02-09
WW-NORTH | February | Checked station Viewed HMI and trends Hatches secured Recorded readings in SharePoint | Sutton High Street Sewage Pumping Station | 2026-02-23
WW-NORTH | February | Checked station Viewed HMI and trends Hatches secured Completed house keeping Recorded readings in SharePoint | Sutton High Street Sewage Pumping Station | 2026-02-26
WW-NORTH | February | Checked station Viewed HMI and trends Checked pump house - ok Hatches secured Recorded readings in SharePoint | Sutton High Street Sewage Pumping Station | 2026-02-12
WW-NORTH | February | Checked station Viewed HMI and trends Hatches secured Recorded readings in SharePoint | Sutton High Street Sewage Pumping Station | 2026-02-19
WW-NORTH | February | Test backflow preventers Both passed | Sutton High Street Sewage Pumping Station | 2026-02-17
WW-NORTH | February | On site for vibration reads. | Sutton High Street Sewage Pumping Station | 2026-02-06
WW-NORTH | February | Checked station Viewed HMI and trends Checked pump house Recorded readings in SharePoint | Sutton High Street Sewage Pumping Station | 2026-02-09
WW-NORTH | February | station checks sharepoint data entry | Keswick Joe Dales Sewage Pumping Station | 2026-02-26
WW-NORTH | February | Checked station Viewed HMI and trends Hatches secured Entered readings in SharePoint | Sutton High Street Sewage Pumping Station | 2026-02-05
WW-NORTH | February | Test backflow preventers Passed | Keswick Joe Dales Sewage Pumping Station | 2026-02-26
WW-NORTH | February | station checks sharepoint data entry | Keswick Joe Dales Sewage Pumping Station | 2026-02-23
WW-NORTH | February | Performed facility station check Data in SharePoint Equipment OOS: none | Keswick Joe Dales Sewage Pumping Station | 2026-02-02
WW-NORTH | February | Station checks completed Enter data into SharePoint Check drywell | Keswick Joe Dales Sewage Pumping Station | 2026-02-19
WW-NORTH | February | Advised ROC of battery change for generator. Shut off charger and switched batteries Turned charger back on. Checked for faults and cleared faults in SCADA Complete | Keswick Joe Dales Sewage Pumping Station | 2026-02-12
WW-NORTH | February | on site 1030hrs station check sharepoint data entry. out 1100hrs | Keswick Joe Dales Sewage Pumping Station | 2026-02-12
WW-NORTH | February | generator test run ocu inspection Heat exchanger inspection drywell and hoists inspection health and safety inspection | Keswick Joe Dales Sewage Pumping Station | 2026-02-04
WW-NORTH | February | station checks sharepoint data entry | Keswick Joe Dales Sewage Pumping Station | 2026-02-05
WW-NORTH | February | on site 1315hrs station checks sharepoint data entry. | Keswick Joe Dales Sewage Pumping Station | 2026-02-09
WW-NORTH | February | on site 08:55hrs station checks sharepoint data entry | Georgina No. 4 Sewage Pumping Station | 2026-02-23
WW-NORTH | February | Complete pump PM?s. Top up oil in pumps 1 and 3. | Georgina No. 4 Sewage Pumping Station | 2026-02-23
WW-NORTH | February | Checked station Viewed HMI and trends Checked dry well area Checked and cleaned bar screen equipment Recorded readings in SharePoint | Georgina No. 4 Sewage Pumping Station | 2026-02-26
WW-NORTH | February | Completed monthly work orders: -Consolidated bar screen and screw conveyer cleaning | Georgina No. 4 Sewage Pumping Station | 2026-02-25
WW-NORTH | February | station checks put screen bin outside sharepoint data entry | Georgina No. 4 Sewage Pumping Station | 2026-02-02
WW-NORTH | February | Station checks completed Enter data into SharePoint Run bar screen and auger in hand | Georgina No. 4 Sewage Pumping Station | 2026-02-19
WW-NORTH | February | on site 0830hrs station checks sharepoint data entry. out 0900hrs | Georgina No. 4 Sewage Pumping Station | 2026-02-12
WW-NORTH | February | Test backflow preventers Both passed | Georgina No. 4 Sewage Pumping Station | 2026-02-17
WW-NORTH | February | Onsite to check station Review scada/trends Clear info alarm Enter data in sharepoint | Georgina No. 4 Sewage Pumping Station | 2026-02-05
WW-NORTH | February | On site to take vibration readings | Georgina No. 4 Sewage Pumping Station | 2026-02-06
WW-NORTH | February | Performed station check Entered readings into SharePoint Checked bar screen and bin | Georgina No. 4 Sewage Pumping Station | 2026-02-09
WEST | February | Onsite for station check Check trends- All okay Station duty not active. 10:45-verified analyzers Grab free Cl2-0.01 mg/L Analyzer free Cl2- 0.05 mg/L Grab Total Cl2- 1.53 mg/L Analyzer Total Cl2-1.51 mg/L Entered values in PWQ sheet Equipment okay. | Woodbridge East Booster Pumping Station | 2026-02-27
WW-NORTH | February | generator test run Hi/Low temp alarm test, on scada @1004hrs drywell flood alarm test, on dialer 1010hrs sump pit inspection drywell valve exercise. hoist inspection ocu inspection | Georgina No. 4 Sewage Pumping Station | 2026-02-03
WEST | February | Onsite for station check Check trends- All okay Station duty not active. 09:45-verified analyzers Grab free Cl2-0.04 mg/L Analyzer free Cl2- 0.04 mg/L Grab Total Cl2- 1.41 mg/L Analyzer Total Cl2-1.47 mg/L Entered values in PWQ sheet Equipment okay. | Woodbridge East Booster Pumping Station | 2026-02-23
WEST | February | #11583073 jhs #11582177 dehumidifier #11582224 sump pit #11583744 flood #11583765 lo temp #11582349 Depolox maint. 9:40 Verified (mg/l) Free: Grab 0.04, A 0.04 Total: Grab 1.55, A 1.50 | Woodbridge East Booster Pumping Station | 2026-02-24
WEST | February | Onsite for station check Check trends- All okay Station duty not active. 10:50-verified analyzers Grab free Cl2-0.06 mg/L Analyzer free Cl2- 0.05 mg/L Grab Total Cl2- 1.46 mg/L Analyzer Total Cl2-1.51 mg/L Entered values in PWQ sheet Equipment okay. | Woodbridge East Booster Pumping Station | 2026-02-02
WEST | February | Onsite for station check Check trends- All okay Station duty active. Pump 1 running 11:00-verified analyzers Grab free Cl2-0.04 mg/L Analyzer free Cl2- 0.03 mg/L Grab Total Cl2- 1.56 mg/L Analyzer Total Cl2-1.51 mg/L Entered values in PWQ sheet Equipment okay. | Woodbridge East Booster Pumping Station | 2026-02-17
WEST | February | -on site for station check -checked trends: all ok -entered readings in PWQ: all ok -verified analyzer 10:55 -analyzer free: 0.05mg/l grab: 0.07mg/l -analyzer total: 1.67mg/l grab: 1.57mg/l - adjusted -equipment all ok | Woodbridge East Booster Pumping Station | 2026-02-12
WEST | February | Onsite for station check Check trends- All okay Station duty not active. 09:50-verified analyzers Grab free Cl2-0.01 mg/L Analyzer free Cl2- 0.03 mg/L Grab Total Cl2- 1.45 mg/L Analyzer Total Cl2-1.51 mg/L Entered values in PWQ sheet W11585392 washroom light cleaning and supplies check complete Equipment okay. | Woodbridge East Booster Pumping Station | 2026-02-09
WEST | February | Onsite for station check Check trends- All okay Station duty not active. 10:15-verified analyzers Grab free Cl2-0.05 mg/L Analyzer free Cl2- 0.06 mg/L Grab Total Cl2- 1.53 mg/L Analyzer Total Cl2-1.47 mg/L Entered values in PWQ sheet Equipment okay. | Woodbridge East Booster Pumping Station | 2026-02-20
WEST | February | Onsite for station check Check trends- All okay Station duty not active. 10:30-verified analyzers Grab free Cl2-0.05 mg/L (avg-0.05,0.04,0.06) Analyzer free Cl2- 0.10 mg/L Adjusted free analyzer value down to 0.05 mg/L Grab Total Cl2- 1.48 mg/L Analyzer Total Cl2-1.58 mg/L Entered values in PWQ sheet Equipment okay. | Woodbridge East Booster Pumping Station | 2026-02-06
WEST | February | Work orders: #11582186 dehum #11582197 sump #11583083 jhs 11583314 eyewash #11583344 act. valve #11583703 lo temp #11584008 gen #11616659 drain | Woodbridge East Elevated Tank | 2026-02-24
WEST | February | On site for Station Check, W11620824 Micro Sampling Check Trends: All Okay Tower Draining (45%) 09:20- Grabs Taken FCL- 0.02 mg/L TCL- 1.69 mg/L Samples Taken. Entered Values in PWQ sheet. Equipment Okay | Woodbridge East Elevated Tank | 2026-02-25
WEST | February | On site for Station Check, W11589513 Micro Sampling Check Trends: All Okay Tower Draining (45%) 09:50- Grabs Taken FCL- 0.02 mg/L TCL- 1.74 mg/L Samples Taken. Entered Values in PWQ sheet. Equipment Okay | Woodbridge East Elevated Tank | 2026-02-11
WEST | February | On site for Station Check, W11606473 Micro Sampling Check Trends: All Okay Tower Draining (60%) 10:30- Grabs Taken FCL- 0.02 mg/L TCL- 1.81 mg/L Samples Taken. Entered Values in PWQ sheet. Equipment Okay | Woodbridge East Elevated Tank | 2026-02-17
WEST | February | On site to replace network switch with network analyst Aaron Magsakay. Comm failure alarm was triggered due to this. Removed Old switch from VNETAG NAC panel. Wired 24 VDC power to the new switch and plugged in the Cat6 cable to correct ports. Powered up new IE3300 layer 3 switch and checked the comms. Removed unused cat6 cables. Checked with ROC to make sure comms are back and trends are good. | Woodbridge East Elevated Tank | 2026-02-04
WEST | February | On site for Station Check, W11569658 Micro Sampling Check Trends: All Okay Tower Filling (57%) 09:20- Grabs Taken FCL- 0.02 mg/L TCL- 1.98 mg/L Samples Taken. Entered Values in PWQ sheet. Equipment Okay | Woodbridge East Elevated Tank | 2026-02-04
WEST | February | On site for Station Check, W11620824 Micro Sampling Check Trends: All Okay Tower filling (54%) 10:15- Grabs Taken FCL- 0.04 mg/L TCL- 1.48 mg/L Samples Taken. Entered Values in PWQ sheet. Equipment Okay. | Woodbridge West Elevated Tank | 2026-02-25
WEST | February | On site for the following work orders. Informed ROC about the works being done W11621618 VNETFD, JHSC Health and Safety Inspection, W11621605 VNETFD, Sump Pit System Inspection, W11621908 VNETFD, Low Temperature Alarm, Test, W11622354 VNETFD, Inspection Form, W11622293 VNETFD, Flood Alarm, Test, W11622283 VNETFD, West Woodbridge ET, Air Relief Valve, Inspection W11622341 VNETFD, Sensing Line Heat Trace System, Inspection, PM W11622415 VNETFD, Portable Gasoline Generator, Test, Woodbridge | Woodbridge West Elevated Tank | 2026-02-19
WEST | February | -on site to perform following orders: -chamber flood alarm: all ok -chamber inspection: all ok -sump pit tested: all o -temp alarm | Woodbridge West Elevated Tank | 2026-02-19
WEST | February | On site for Station Check, W11589513 Micro Sampling Check Trends: All Okay Tower filling (58%) 10:45- Grabs Taken FCL- 0.04 mg/L TCL- 1.43 mg/L Samples Taken. Entered Values in PWQ sheet. Equipment Okay. | Woodbridge West Elevated Tank | 2026-02-11
WEST | February | On site for Station Check, W11606473 Micro Sampling Check Trends: All Okay Tower draing (72%) 09:45- Grabs Taken FCL- 0.04 mg/L TCL- 1.51 mg/L Samples Taken. Entered Values in PWQ sheet. Equipment Okay. | Woodbridge West Elevated Tank | 2026-02-17
WW-CEAST | February | On site to install the new limitork on pump 1 discharge valve. Supplier sent the wrong parts and will ship it asap | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-02-24
WEST | February | On site for Station Check, W11569658 Micro Sampling Check Trends: All Okay Tower filling (80%) 10:15- Grabs Taken FCL- 0.04 mg/L TCL- 1.47 mg/L Samples Taken. Entered Values in PWQ sheet. Equipment Okay. | Woodbridge West Elevated Tank | 2026-02-04
WW-CEAST | February | On site for media sampling with Contractor, All Round System (John Round), under RFT 2609-25. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-02-26
WW-CEAST | February | Station check completed. See details on sharepoint. Pumps 2,5 & 6 available in timed auto duty rotation every 3 hours. Pump #3 discharge valve for east forcemain is tripped. Unable to clear the 'hardware failure' status on the actuator. Maintenance will check this soon. Pumps 1,3 and 4 remain oos. Checked dry well. ok checked bar screens. changed out rag bins. All lines except 1 available at the dump pad for haulers to use. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-02-23
WW-CEAST | February | Station check completed. See details on sharepoint. pumps 2,3,5 and 6 available in timed auto duty rotation every 3 hours. pumps 1 and 4 still oos. All standby power generators available in auto. Checked dry well. Air compressors inspection and cleaning completed. checked bar screens. switched out rag bins. All lines except no.1 available at the dump pad for haulers to use. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-02-25
WW-CEAST | February | Station check completed. See details on sharepoint. pumps 2,3,5 and 6 available in timed auto duty rotation every 3 hours. pumps 1 and 4 still oos. All standby power generators available in auto. Checked dry well. Checked screen room. ok. Bypass sampling kit inspection completed. Odour control scrubber system inspection completed. All lines except no.1 available at the dump pad for haulers to use. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-02-27
WW-CEAST | February | Greased all discharge valves and east and west main valves. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-02-23
WW-CEAST | February | Station check completed. See details on sharepoint. All pumps available in timed auto duty rotation every 3 hours except pump 1 which is OOS due to discharge valve issue All standby power generators available in auto. Hazardous Waste Collection and Removal Checked dry well. Checked bar screens. switched out rag bin. Added oil on the reservoir tank. All lines available at the dump pad for haulers to use. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-02-02
WW-CEAST | February | -On site to respond to Mechanical Screen 2 Fault. Bar Screen 2 is faulted on an Overload Trip on the bar screen 2 control panel. Unable to clear alarm or run bar screen locally in forward or reverse. Bar screen rake is making contact with metal side of bar screen frame at the top beside the screw conveyor. Inlet gate for bar screen is currently closed until repairs can be made. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-02-01
WW-CEAST | February | On site to remove pump 4 for service, remove actuator from dump pad line one, and greased pump 3 force main discharge vale | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-02-17
WW-CEAST | February | Worked on pump 4 install Installed new wear ring in bowl Placed pump and bowl on pedestal Pump bowl will need to be modified to fit properly. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-02-18
WW-CEAST | February | Station check completed. See details on sharepoint. All pumps available in timed auto duty rotation every 3 hours except pump 1. All standby power generators available in auto. Checked dry well. OK. checked screen room. switched rag bins. All lines available at the dump pad for haulers to use. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-02-13
WW-CEAST | February | On site to troubleshoot pump 4. Found main fuses blown. Checked motor, wiring, supply and control power. Suspect winding contamination. Removed cable entry lid. Found heavy contamination. Unwired pump so mechanics can remove pump. Pump 4 is out of service. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-02-17
WW-CEAST | February | Checked station/rag bin | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-02-15
WW-CEAST | February | On site to prep cables for pump 4 replacement. Mechanics installed replacement pump. Wired pump and tried to test rotation. Breaker tripped and 3rd phase fuse blew on startup. Electrical problem needs further investigation. Pump 4 remains out of service. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-02-19
WW-CEAST | February | On site in response to pump 4 alarms(leakage/estop/fault). Upon arrival, found pump 4 mcc main switch in tripped position on B1. Reset the switch put still no power to Pump 4 MCC. Checked all the estops for the pump and confirmed non are active. Talked to CMS and created CMU4 for this issue | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-02-17
WW-CEAST | February | Station check completed. See details on sharepoint. All pumps available in timed auto duty rotation every 3 hours except pump 1 and 4. All standby power generators available in auto. Checked dry well. OK. Air Compressors Inspection and cleaning completed. checked screen room. Bar Screen Bin Removal and Replacement All lines available except line 1, at the dump pad for haulers. Comprehensive housekeeping completed at station. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-02-18
WW-CEAST | February | -station check of site -reviewed SCADA -entered data into sharepoint -inspected site -rotated bin in screen room -Pump 1 and 4 remain OOS -station okay | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-02-20
WW-CEAST | February | AUEQSJ Onsite for annual calibrations Informed ROC Used cal mode on scada during the work Instruments calibrated: FITs, PITs, LITs and gas detectors Cleared associated alarms Informed ROC, armed building and left site No issues upon leaving | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-02-10
WW-CEAST | February | Weather today Snow and -1 Celsius -On site to complete work orders W11587339, W11586377. -Completed station check. -Entered station readings into SharePoint. -Air Compressors inspection. -Pumps 2, 3, 4, 5, and 6 available in timed auto duty rotation every 3 hours. -Pump 1 out of service due to discharge valve issue. -Standby power generators available in auto. -Checked dry well, Ok. -All lines available in auto at the dump pad for the haulers. -Checked bar screens and Rotated bin. -Cleaned bar screen room of rags and bar screen oil full. -Unclogged drain lines on screw conveyor 3. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-02-11
WW-CEAST | February | -On site to complete work orders. -Consolidated wet well inspection work order completed. -Tipping bucket operational checks completed. -Bar screen cleaning and lubrication completed. -Screw conveyor cleaning and lubrication completed. -Screw press dewatering compartment and drain line flushed. -Sluice gate valve exercises completed. -Wet well valve exercise completed. -Wet well inspection and cleaning completed. -Wet well high level alarm test completed and confirmed by ROC. -Surge tank inspection consolidated work order completed. -Surge tank and inspection completed. -Surge tank valve and actuator, exercise and inspection completed. -Surge tank drain valve inspection completed. -Transmission line flushing completed on both surge tanks. -Cleared all alarms generated from work orders. -Pumps 1 and 4 remain OOS. -Line 1 at the dump pad OOS for valve replacement. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-02-19
WW-CEAST | February | On site in response to generator 1 coolant low temp, generator 1 warning alarm. Verified at GMCP that coolant low temp alarm outstanding. Cleared the block heater trip from LP3. Coolant temp going back up from 23C. Alarm cleared @ 26C. Consult with Tyler Z and notified ROC. All alarms cleared on Gen 1 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-02-12
WW-CEAST | February | -on site at dump pad for line 3 valve overtorque -cleared line, valve was clogged with zip ties, a hauler keeps flushing zip ties and it is an issue -reset alarms on SCADA -line 2 and 3 available, 1 OOS for valve upgrades | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-02-19
WW-CEAST | February | On site to work on pump 4. Continued troubleshooting electrical problem. Checked motor cables and power wiring. Sourced replacement fuse. Was able to power up MCC with motor disconnected. Fault history in Eaton Soft Starter indicated SCR shorted fault. Suspect soft starter failure. Need to source replacement. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-02-20
WW-CEAST | February | Station check completed. See details on sharepoint. All pumps available in timed auto duty rotation every 3 hours except pump 1 which is OOS due to discharge valve issue All standby power generators available in auto. Checked dry well. Air compressors inspection and cleaning completed. JHSC Health and Safety Inspection completed. checked bar screens. Bar Screen Bin Removal and Replacement All lines available at the dump pad for haulers to use. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-02-04
WW-CEAST | February | Station check completed. See details on sharepoint. All pumps available in timed auto duty rotation every 3 hours except pump 1 which is OOS. Cleared pump 3 E Disc Hdr MV4 alarm on scada. All standby power generators available in auto. Checked dry well. OK. Air dryers inspection and cleaning completed. checked screen room. OK. All lines available at the dump pad for haulers to use. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-02-06
WW-CEAST | February | Repair south bar screen and run Put in auto | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-02-06
WW-CEAST | February | On site for bar screen 1 oos found the rake at the bottom and the rollers out of alinement. Repaired the rollers and aligned the rake and it is back in service | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-02-09
WW-CEAST | February | On site in response to barscreen 1 overtorque alarm. Both barscreen OOS. Cleared screen 1 overtorque and attempted to run it in auto. Unit faulted out right away. Noticed rake has fallen near bottom sprocket in crooked position. Got ROC to call in Oncall CMS(Lee F) to site. Cleared overtorque for screen 2 and attempted to run it. Found rake is scratching the plate as it is travelling upwards creating loud screeching sound. Stopped the rake at the top. Lee F and I put screen 2 back in service after adjusting the position of the rake. Inlet gate to screen 2 has been open. Inlet gate to screen 1 has been closed. Notified ROC. Screen 1 OOS, screen 2 back in service | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-02-07
WW-CEAST | February | on site to complete Consolidated Monthly Dry Well Pump Floor Inspection WO Auto Dialer Alarm Test - received by ROC. High Low Temperature Alarm Test - received by ROC. Dry Well Flood Alarm Test - received by ROC. Sump Pit Inspection and operation Raw Sewage Pump and Motor Inspection Pump 1 (VFD) - out of service Pump 2 (VFD) - @ 0% speed, 267 L/s, 771 kPa, 354 A, 518 V, 54 Hz, 1077 Rpm; 60% speed, 404 L/s, 783 kPa, 470 A, 541 V, 57 Hz, 1136 Rpm Pump 3 (Constant) - 429 L/s, 810 kPa, 454 A, 598 V, 60 Hz Pump 4 (Constant) - 451 L/s, 782 kPa, 454 A, 606 V, 60 Hz Pump 5 (VFD) - @ 0% speed, 299 L/s, 777 kPa, 379 A, 515 V, 54 Hz, 1077 Rpm; 60% speed, 420 L/s, 798 kPa, 499 A, 549 V, 57 Hz, 1136 Rpm Pump 6 (VFD) - @ 0% speed, 277 L/s, 743 kPa, 370 A, 513 V, 54 Hz, 1077 Rpm; 60% speed, 408 L/s, 748 kPa, 493 A, 545 V, 57 Hz, 1136 Rpm Check Valves Inspection Air Compressors Inspection Cleared/reset all alarms Station back to normal operations | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-02-03
WW-CEAST | February | -station check of facility -reviewed SCADA -inspected site -reviewed trend -site okay | Newmarket Green Lane Pumping Station | 2026-02-27
WW-CEAST | February | Station check completed. See details on sharepoint. All pumps available in timed auto duty rotation every 3 hours except pump 1. All standby power generators available in auto. Checked dry well. OK. Checked screen room. The auger for screw press was broken. Maintenance arrived on site to fix the issue. Cleaned the floors and put back the press in service after fixing. All lines available at the dump pad for haulers to use. Monthly diesel generator test run completed, readings entered into SharePoint. 10.15 - Transferred site to generator power. Gen 1: Start time: 627.9, Stop time: 629.3, Run time: 1:4hrs. Gen 2: Start time: 620, Stop time: 621.5, Run time: 1.5hrs. Gen 3: Start time: 823.8, Stop time: 823.5, Run time: 1:5hrs. 11.30 - Transferred site back to utility power. cleared/reset all alarms | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-02-09
WW-CEAST | February | On site to troubleshoot dump pad line 1 overtorque alarm. Back flushed the line and cleared the alarm. Put line 1 back in service | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-02-05
WW-CEAST | February | Weather today Clear and -5 Celsius -On site to complete work order W11560074. -Completed station check. -Entered station readings into SharePoint. -Both pumps available in all stop auto duty rotation. -SCADA is trending. -Station has normal operations. -No outstanding alarm | Newmarket Green Lane Pumping Station | 2026-02-02
WW-CEAST | February | Took Station readings and entered into Sharepoint,, reviewed trends - all looks good. Station running under normal ops - no issues found | Newmarket Green Lane Pumping Station | 2026-02-23
WW-CEAST | February | Weather today A few clouds and -6 Celsius -On site to complete work order W11595191. -Completed station check. -Entered station readings into SharePoint. -Both pumps available in all stop auto duty rotation. -SCADA is trending. -Station has normal operations. -No outstanding alarm. | Newmarket Green Lane Pumping Station | 2026-02-13
WW-CEAST | February | Weather today Overcast and 2 Celsius -On site to complete work order W11610960. -Completed station check. -Entered station readings into SharePoint. -Both pumps available in all stop auto duty rotation. -SCADA is trending. -Station has normal operations. -No outstanding alarm. | Newmarket Green Lane Pumping Station | 2026-02-20
WW-CEAST | February | Weather today Snow and -9 Celsius -On site to complete work orders W11558184, W11575567. -Completed station check. -Entered station readings into SharePoint. -JHSC health and safety inspection. -Both pumps available in all stop auto duty rotation. -SCADA is trending. -Station has normal operations. -No outstanding alarm | Newmarket Green Lane Pumping Station | 2026-02-06
WW-CEAST | February | Weather today A few clouds and -10 Celsius -On site to complete work order W11580374. -Completed station check. -Entered station readings into SharePoint. -Both pumps available in all stop auto duty rotation. -SCADA is trending. -Station has normal operations. -No outstanding alarm. | Newmarket Green Lane Pumping Station | 2026-02-09
WW-CEAST | February | Put two bags of soda ash into the aeration tanks and set two up for later,, started de-cant pump and collected the comp samples from yesterdays samples and delivered them to Harry Walker. completed Lab work and wasted 10m3 and added 4 bags of soda ash in total. leaned out post aeration tank and the entry flow gates and also washed down the UV channel. Went through the station sand filters working well, Bar screen just went OOS (flowing through by pass bar screen) I have put in a WO for maintenance. OC unit is still OOS. | Mount Albert Water Resource Recovery Facility | 2026-02-26
WW-CEAST | February | Put two bags in and set two bags up to put in later, and started de-cant pump. Flushed both sand filter reject lines also checked both clarifiers - oil level OK,I did NOT drain the water as I did that 2 weeks ago - same for the greasing. Went through the station - sand filters working good. The OC unit is still OOS put station is running under normal ops. | Mount Albert Water Resource Recovery Facility | 2026-02-24
WW-CEAST | February | February 22, 2026 -09:15 - was on site to do sludge handling and weekend lab -started decant pump for sludge thickening tank upon arriving to site -received call, had to leave site for family emergency, ending my on-call and weekend work -notified ROC operator Ethan, who called the on-call manager to get another operator on site to finish weekend work - told Ethan to notify me of whatever operator is covering the work so I can let them know the status of site -was notified by ROC operator Ethan that Terry Reed was covering my on-call -11:28 called Terry Reed to give him a status update for the area, he did not pickup, left him a text message/iMessage explaining 'the decant pump is running, lab had not been started yet, no other work at the WRRF was started', text message said 'delivered', did not hear back from Terry Reed | Mount Albert Water Resource Recovery Facility | 2026-02-22
WW-CEAST | February | On site completed work orders. Lab Analysis (See results on SharePoint) and Sludge Processing Composite sampler did not take samples overnight, hence, did only the final effluent grab samples for the in-house lab analysis. STT decanted, afterwards dumped remaining sludge into the SHT. Checked DO Probes, removed rags on the probes. Checked Alum dosing injection points at prefilter and post aeration. Removed rags from the inlet/outlet sluice gates of Aeration Tanks. Removed snow from walkways, stairs and all entrance doors of the buildings. Batch wasted 20 m3. Terry R. added two bags of Soda Ash into each Aeration Tanks. | Mount Albert Water Resource Recovery Facility | 2026-02-25
WW-CEAST | February | Put two bags of soda ash into the aeration tanks and set two up for later, started the de-cant pump as well. Collected weekly samples both at the PS and the WRRF (except comp - sampler did NOT work) and delivered to Harry Walker. Worked on the sampler with Marcos and got it up and running again. Cleaned the washroom in the sand filter room as well. Added the other two bags of soda ash. | Mount Albert Water Resource Recovery Facility | 2026-02-25
WW-CEAST | February | Shut off de-cant pump and emptied thickening tank into holding tank. Put two bags of soda ash into the aeration tanks and set up two for later. Pushed bin out for pick up and cleaned around the gates and also the post aeration tank - not much at all in the tank. Checked sand filter operation - all good. Station running under normal ops - no new issues were found , OC is still OOS | Mount Albert Water Resource Recovery Facility | 2026-02-23
WW-CEAST | February | On site for PAC panel and investigation. | Mount Albert Water Resource Recovery Facility | 2026-02-25
WW-CEAST | February | On site completed work orders. Lab Analysis (See results on SharePoint) and Sludge Processing. STT decanted and remaining sludge dumped into the SHT. Batch wasted 20 m3. Completed housekeeping. | Mount Albert Water Resource Recovery Facility | 2026-02-24
WW-CEAST | February | -On site to rake manual bar screen. Fully removed inlet gate to manual bar screen, raked screen. Checked grit bin and aeration tank, no issues noted. | Mount Albert Water Resource Recovery Facility | 2026-02-28
WW-CEAST | February | On site completed work orders. Lab Analysis (See results on SharePoint) and Sludge Processing STT decanted afterwards dumped remaining sludge into the SHT. At around 10:53 am, Alum dosage setpoint for the Post-Aeration has been increased from 190 mg/L to 195 mg/L due to elevated Total P. This is so because the decanting pump at the STT has been left running over the weekend on Sunday, February 22nd, until Monday morning of February 23rd. Checked DO Probes, removed rags on it. Checked Alum dosing injection points at prefilter and post aeration. Cleaned Headworks. TNT reagents inventory confirmation and re-ordering. TNT 843 - 4 boxes; TNT 839 - 1 box; TNT 836 (Nitrate) - 3 boxes but all expiring next month (Will order); TNT 870 - 1 box; TNT 830 - 3 boxes. Pipette, BBP072 /BBP079- ok. Glass-Microfibre discs 90 mm diameter (MLSS) - 3 boxes Glass-Microfibre discs 47 mm diameter (MLSS) - 3 boxes | Mount Albert Water Resource Recovery Facility | 2026-02-27
WW-CEAST | February | On site completed work orders. Lab Analysis (See results on SharePoint) and Sludge Processing. Station Check (See details on SharePoint) Standby power generator available in auto Checked DO Probes Checked Alum dosing injection points at prefilter and post aeration Terry R. started decanting STT and remaining sludge dumped into the SHT. Decanting pump turned off. Terry R. added one bag of Soda Ash into each Aeration Tanks and I added another bag in the afternoon. Batch wasted 20 m3. Short blasted RAS Pumps 1 and 3 to get desired flows of around 13 L/s at 0% auto speed. | Mount Albert Water Resource Recovery Facility | 2026-02-23
WW-CEAST | February | On site completed work orders. Lab Analysis and Sludge Processing (See results on SharePoint) Decanted STT and dumped remaining sludge into the SHT. Added 2 bags of Soda Ash into each Aeration Tanks. Checked Alum dosing injection points at pre-filter and post-aeration. Checked DO, removed rags. Removed rags from the inlet/outlet sluice gates of aeration tanks. Batch wasted 20 m3. JHSC Health and Safety Inspection Hazardous Waste Collection and Removal Standby Power Generator Test Run - pre-test checked, ok. Generator started and stopped running without problem. Cleared/reset all alarms. Station back to normal operations. | Mount Albert Water Resource Recovery Facility | 2026-02-02
WW-CEAST | February | -On site for lab analysis and sludge handling work. -Entered lab results into SharePoint. -Decanted STT to headworks, then emptied tank into SHT. -Added two bags of soda ash to each aeration tank. -Batch wasted 10m3, ran RAS pumps at 100% speed when returning to service. -Verified alum dosing and sand filter operation. -OCU remains OOS. | Mount Albert Water Resource Recovery Facility | 2026-02-01
WW-CEAST | February | On site completed work orders. Lab Analysis (See results on SharePoint) and Sludge Processing STT decanted and remaining sludge dumped into the SHT. Batch wasted 10 m3. Post Filtration/UV Channel Hosed Down. Terry R. added two bags of Soda Ash into each Aeration Tanks. | Mount Albert Water Resource Recovery Facility | 2026-02-19
WW-CEAST | February | Put two bags of soda ash into aeration tanks and set the next two up also got the de-cant pump going. collected samples from the clarifier and sampler for Marcos also checked sand filters - working great. checked blower room and went into air compressor room - all good. station running under normal ops - no issues found. | Mount Albert Water Resource Recovery Facility | 2026-02-20
WW-CEAST | February | Put two bags of soda ash into the aeration tanks and set two up for later,, turned the de-cant pump on. Shovelled the stairs to the aeration tank, front door,garage door,headworks and sand filter room as well. Exercised all the gates around the aeration tanks - partial and around the clarifiers, cleaned the post aeration tank again as well as the inlet gates (nothing there really). Sand filters working good as well. The only alarms outstanding are for the odour control and they have been shelved. | Mount Albert Water Resource Recovery Facility | 2026-02-19
WW-CEAST | February | Put 2 bags of soda ash into the aeration tanks and set the next two up,, started the de-cant pump. went through the station - sand filters working good and i washed down the clarifiers scum trough. Cleaned out the post aeration tank and also the gates of the aeration inlet. Station running under normal ops - no issues were observed. Odour Control is still OOS. | Mount Albert Water Resource Recovery Facility | 2026-02-17
WW-CEAST | February | Dropped in 2 bags of soda ash and set up 2 other bags for the aeration tanks also started de-cant pump. Started the Lab and sludge processing and entered results from the Lab into Sharepoint. Wasted 20m3 today and went through the Head works building - greased the travelling bar screen and cleaned out the back plate. Checked the vortex and both are turning. OC unit is still OOS. | Mount Albert Water Resource Recovery Facility | 2026-02-12
WW-CEAST | February | On site completed work orders. Lab Analysis (See results on SharePoint) and Sludge Processing. Decanted STT and then dumped remaining sludge into the SHT. Station Check (See details on SharePoint) Standby power generator available in auto. Checked Headworks, ok. Checked DO Probes, cleared/removed dangling rags from the probes. Removed rags from the inlet/outlet sluice gates of aeration tanks. Checked Alum dosing injection points at prefilter and post aeration. Added another bag of Soda Ash into the Aeration Tanks. Cleared walkways and all entrance doors of snow. | Mount Albert Water Resource Recovery Facility | 2026-02-11
WW-CEAST | February | Dumped two bags of soda ash into the aeration tank and set up the next two for later,, started de-cant pump and also collected weekly samples for the Lab,, Delivered samples to Harry Walker after collecting the samples at Mt. Albert PS. Back from drop off of the samples and checked all the cranes - all good and working. Went through the station and just the OC unit is still OOS. Rest of the station is running fine. | Mount Albert Water Resource Recovery Facility | 2026-02-11
WW-CEAST | February | On site completed work orders. Lab Analysis (See results on SharePoint) and Sludge Processing Started decanting STT. Station Check (See details on SharePoint) Added one bag each of Soda Ash into the Aeration Tanks. Collected Weekly Sewage Samples under YD# W11605535. Out at 10:45am, to collect sewage samples at the Pumping Station. Back on site at 12 noon, to continue completing work orders. Decanting is done. Turned off decant pump and then dumped remaining sludge into the SHT. Checked DO Probes, removed rags dangling on the probes. Checked Alum dosing injection points at prefilter and post aeration. Removed rags from the inlet/outlet sluice gates of Aeration Tanks. Added another bag of Soda Ash into the Aeration Tanks. Standby power generator available in auto. | Mount Albert Water Resource Recovery Facility | 2026-02-18
WW-CEAST | February | On site completed Lab Analysis (See results on SharePoint) and Sludge Processing. STT decanted and remaining sludge dumped into the SHT. Decanting pump turned off. Terry R. added two bags of Soda Ash into each Aeration Tanks. Batch wasted 10 m3. Short blasted RAS Pumps 1 and 3 to get desired flows of around 13 L/s at 0% auto speed. | Mount Albert Water Resource Recovery Facility | 2026-02-20
WW-CEAST | February | On site completed work orders. Lab Analysis (See results on SharePoint) and Sludge Processing. Decanted STT and then dumped remaining sludge into the SHT. Checked DO Probes, cleared/removed dangling rags from the probes. Checked Alum dosing injection points at prefilter and post aeration. Batch wasted 20 m3. Short blasted RAS Pumps 1 and 3 to get desired flows of around 12 L/s at 0% auto speed. 2 Tonne Hoist System Inspection (Aeration Tank Building) 2 Tonne Hoist System Inspection (Process Building) Sand Filter Filter-Reject Drain Line Flushed | Mount Albert Water Resource Recovery Facility | 2026-02-17
WW-CEAST | February | On site completed work orders. Lab Analysis (See results on SharePoint) and Sludge Processing. Decanted STT. Dumped remaining sludge into the SHT. Added two bags of Soda Ash into each Aeration Tanks. Batch wasted 10 m3. Aeration, sludge and vortex blower belts, oil filters and oil levels checked. | Mount Albert Water Resource Recovery Facility | 2026-02-10
WW-CEAST | February | Dumped 2 bags of soda ash intro the aeration tanks and set 2 up for later,, also started the de-cant pump. Went through the station - sand filters working great , set up hose and flushed both reject lines. checked blower room - all looks good and the air compressors as well. Station running under normal ops - no issues were found, OC unit is still OOS | Mount Albert Water Resource Recovery Facility | 2026-02-10
WW-CEAST | February | On site to change Ras pump two line reactor The VFD is now protected pump placed back on in an auto | Mount Albert Water Resource Recovery Facility | 2026-02-19
WW-CEAST | February | Checked station and lab complete. Data has been entered into the sharepoint. Batch wasted 14m3 in total and dosed 4 bags of soda ash into the aeration. Cleaned aeration inlet/outlet | Mount Albert Water Resource Recovery Facility | 2026-02-15
WW-CEAST | February | On site completed work orders. Station Check (See details on SharePoint) Standby power generator available in auto. Checked Alum dosing injection points at prefilter and post aeration. Post Filtration/UV channel hosed down. RAS/WAS inlet channel inspection and cleaned. Post Aeration Alum mixing chamber cleaned out. Removed rags from the inlet/outlet sluice gates of Aeration Tanks. Checked DO Probes. | Mount Albert Water Resource Recovery Facility | 2026-02-12
WW-CEAST | February | On site completed work orders. Lab Analysis (See results on SharePoint) and Sludge Processing. Decanted STT and then dumped remaining sludge into the SHT. Station Check (See details on SharePoint) Standby power generator available in auto. Checked Headworks, ok. Hosed down screen room. Checked DO Probes, cleared/removed dangling rags from the probes. Removed rags from the inlet/outlet sluice gates of aeration tanks. Checked Alum dosing injection points at prefilter and post aeration. Added another bag of Soda Ash into the Aeration Tanks. Terry R. did the first bag. Batch wasted 20 m3. Short blasted RAS Pumps 1 and 3 to get desired flows of around 12 L/s at 0% auto speed. | Mount Albert Water Resource Recovery Facility | 2026-02-13
WW-CEAST | February | On site completed work orders. Lab Analysis and Sludge Processing (See results on SharePoint). At around 10:00am, Terry R. received 120 bags of 25 kgs. Soda Ash from Glen Chemicals Ltd. under invoice # 00078640. Batch wasted 10 m3. | Mount Albert Water Resource Recovery Facility | 2026-02-03
WW-CEAST | February | On site completed work orders. Lab Analysis and Sludge Processing (See results on SharePoint). Decanted STT. Dumped the remaining sludge into the SHT. Post Filtration/UV Channel Hosed Down Completed station check. Checked DO probes, ok. Checked Alum dosing injection points at prefilter and post aeration. Removed rags from the sluice gates of inlet/outlet of Aeration Tanks. Added two bags of Soda Ash into each Aeration Tanks. | Mount Albert Water Resource Recovery Facility | 2026-02-05
WW-CEAST | February | On site completed work orders. Lab Analysis and Sludge Processing (See results on SharePoint). Terry R. added one bag of Soda Ash into the Aeration Tanks in the morning and I added one bag each in the afternoon. STT decanted. Dumped remaining sludge into the SHT. Batch wasted 22 m3, afterwards dumped into the SHT. Short blasted RAS pumps 1 and 3 to get desired flows of around 12 L/s at 0% auto speed. Also, Terry R. collected weekly and monthly sewage samples and delivered to 145 HWP. | Mount Albert Water Resource Recovery Facility | 2026-02-04
WW-CEAST | February | Station check/Lab complete and the readings have been entered into the sharepoint. Batch wasted 8m3 in total and dosed 4 bags of soda ash into the aeration. Cleaned pre/post aeration tank Noticed ice build up on the scum hopper which could be causing Final effluent TSS increase. Will need to be removed next week when weather warms up. | Mount Albert Water Resource Recovery Facility | 2026-02-08
WW-CEAST | February | On site completed work orders. Lab Analysis and Sludge Processing (See results on SharePoint). Decanted STT. Dumped remaining sludge into the SHT. Added 2 bags of Soda Ash into each Aeration Tanks. Checked Alum dosing injection points at prefilter and post aeration. Batch wasted 10 m3, dumped sludge into the SHT. DO meter verified. Air compressors cleaning and inspection. | Mount Albert Water Resource Recovery Facility | 2026-02-09
WW-CEAST | February | came to the plant and set up the soda ash and turned the de-cant pump on for Marcos,, went to the pumping station and back at 11,, cleaned out the post aeration tank and also the inlet channel gates as well,, went through the station and everything is running fine. OC unit is still OOS though. | Mount Albert Water Resource Recovery Facility | 2026-02-05
WW-CEAST | January | Completed Lab work and wasted 20m3 and added 4 bags of soda ash,, entered results of the Lab into Sharepoint. it was to cold to spray foam the door frame but I swept up the blower room and started on the sand filter room. Washroom has to be cleaned next week. | Mount Albert Water Resource Recovery Facility | 2026-01-30
WW-CEAST | February | Completed Lab work and sludge processing,, entered results from the Lab into Sharepoint. Did not waste today and added 4 bags of soda ash. Had Alum delivery today (16000L) and Orlando to pick up the sludge. Went through the station - sand filters are working good and RAZ pumps have good flow. OC unit is still OOS, | Mount Albert Water Resource Recovery Facility | 2026-02-06
WW-CEAST | February | Set up soda ash - put 2 bags in and 2 set up and waiting,, started de-cant pump and collected weekly samples for the Lab. After dropping off samples cleaned the scum trough - hosed it down till ice was gone. Went through the station and all looks good - Odour Control is still OOS but everything else looks good. | Mount Albert Water Resource Recovery Facility | 2026-02-04
WW-CEAST | February | Set up soda ash for the day - put 2 bags in and 2 bags waiting,, started decant pump. Went through the station and all looks good , sand filters working great. Checked WAZ/RAZ and scum pumps - RAZ pumps have great flow and the oil level is good on all pumps,, also checked both sump pumps in the 2 buildings - both are good. Received soda ash delivery 2 and a 1/2 skids. Also flushed the sand filter reject lines for about a half hour each. Station running under normal ops - OC unit is still OOS | Mount Albert Water Resource Recovery Facility | 2026-02-03
WW-CEAST | February | -station check of site -inspected site -reviewed SCADA -entered data into sharepoint -cleaned RAS/WAS chamber -cleaned alum injection chamber -rotated bins in screen room as necessary -station okay | Mount Albert Water Resource Recovery Facility | 2026-02-09
WW-CEAST | February | Pushed Bin out for pick up,, went through the station and checked equipment - all looks good. Cleaned out post aeration tank and the 2 inlet gates - not much there again. Station running under normal ops - OC still OOS but that's it. | Mount Albert Water Resource Recovery Facility | 2026-02-02
WW-CEAST | February | Took station readings and entered into sharepoint, reviewed the trends - all looks good. Station running under normal ops , no issues found. | Mount Albert Pumping Station | 2026-02-23
WW-CEAST | February | Here to complete station check - entered readings into Share point,, verified the Hi wet well alarm with ROC and also verified Dialer alarm through the dry well flood alarm. Greased both pumps and activated the sump pumps to verify operation and checked the hoist down stairs - the hoist on the main floor is LOTO by maintenance. Checked both check valves and I could not find the building temp alarm - I will ask if there is a way to check Temp alarm. Station running under normal ops - no issues at all. | Mount Albert Pumping Station | 2026-02-13
WW-CEAST | February | On site collected weekly sewage samples under YD# W11605535. Rinse samples container. Reset composite sampler for next week sample collection. Samples delivered to 145 Harry Walker Parkway. | Mount Albert Pumping Station | 2026-02-18
WW-CEAST | February | Here to collect weekly sample ,, took a picture of the sample as requested and then reset sampler after rinsing everything out. Station is running under normal ops. | Mount Albert Pumping Station | 2026-02-11
WW-CEAST | February | Took station readings and entered into Sharepoint,, verified Hi Wet Well alarm - confirmed by ROC. Exercised both inlet gates - partial and also checked the cranes - the crane on the main floor is LOTO by maintenance. Opened the hatch and checked the condition of the wet well - all good. Also flushed water back through the sampler and set it back up for Tuesday. All alarms cleared and station back to normal ops. | Mount Albert Pumping Station | 2026-02-20
WW-CEAST | February | Took station readings and entered into Sharepoint,, checked pump floor - all good,, completed H & S inspection - no issues were found. There was no Hazardous waste to dispose of, could not get into the Diesel room due to lock being frozen. | Mount Albert Pumping Station | 2026-02-02
WW-CEAST | February | Took station readings and entered into Sharepoint,, reviewed trends - all looks good. Station running under normal ops - no issues were found. | Mount Albert Pumping Station | 2026-02-06
WW-CEAST | February | -station check of site -reviewed SCADA -inspected site -entered data into sharepoint -station okay | Mount Albert Pumping Station | 2026-02-09
WW-CEAST | February | Here to collect weekly Lab samples and delivered to Harry Walker,, reset sampler to start on Tuesday morning for next week | Mount Albert Pumping Station | 2026-02-04
WW-CEAST | February | Here to complete the Diesel Test run ,, informed the ROC of the test run and checked all the fluids and entered Data and then switched over to Diesel power - no issues with the transfer and Diesel sounds good. Entered running readings into Sharepoint and after an hour switched back to main power after completed informed ROC that they station is now back to normal ops and back on main power. | Mount Albert Pumping Station | 2026-02-05
WW-CEAST | February | -barscreen 1 tripped out on an over-torque alarm, second time tonight -reset screen, barscreen 1 back online -reset alarm on SCADA | Newmarket Sewage Pumping Station & Equalization Tank | 2026-02-25
WW-CEAST | February | On site for media sampling with Contractor, All Round System (John Round), under RFT 2609-25. | Newmarket Sewage Pumping Station & Equalization Tank | 2026-02-26
WW-CEAST | February | Station Check completed (See details on SharePoint). All pumps available in auto duty rotation. Standby power generator available in auto. Checked dry well, ok. checked screen room. Placed the bar screen bin outside for removal. Bar screen 2 put back to service after maintenance worked on the over-torque fault. Air compressors inspection and cleaning completed. | Newmarket Sewage Pumping Station & Equalization Tank | 2026-02-25
WW-CEAST | February | Barscreen 2 over torque Checked and all components look good and aligned Checked sensor and it is tripped, gear box is in its normal position. Loosened bracket for sensor and adjusted to be in close enough proximity to allow bar screen to run. Barscreen ran for approximately 30 minutes and tripped on over torque. Checked barscreen alignment okay. Checked sensor out of adjustment Found right shaft collar on drive assembly loose allowing shaft to move out of adjustment from torque sensor. Adjusted shaft and tightened collar by bearing. Running barscreen to verify repair complete. | Newmarket Sewage Pumping Station & Equalization Tank | 2026-02-25
WW-CEAST | February | Took station readings and entered into Sharepoint - reviewed trends - all good, levelled out bin in the screening room and bar screen 2 is OOS - not sure why (Chris) . Checked pump floor - all good . Emptied all the garbage and swept and mopped out both the office and the washroom. Station running under normal ops - just bar screen 2 OOS - I will find out more tomorrow. | Newmarket Sewage Pumping Station & Equalization Tank | 2026-02-23
WW-CEAST | February | -station check of site -reviewed SCADA -entered data into sharepoint -inspected site -inspected screen room -station okay | Newmarket Sewage Pumping Station & Equalization Tank | 2026-02-27
WW-CEAST | February | Feb 21 18:30 - inlet gate on bar screen 2 closed, bar screen 2 overtorque alarm, ongoing issue, will investigate when on site, bar screen 1 still in service Feb 25 6:00 - W11688345 created for bar screen 2, unable to reset alarm or run screen, need maintenance to investigate, bar screen 1 tripped too on overtorque, but was reset, and available | Newmarket Sewage Pumping Station & Equalization Tank | 2026-02-21
WW-CEAST | February | -On site to complete general housekeeping tasks. -Assisted maintenance with rotating pumps for maintenance activities while on site. | Newmarket Sewage Pumping Station & Equalization Tank | 2026-02-26
WW-CEAST | February | Complete PM on pump 2 Greased pumps 2. Adjust packing on pumps 3 and 4. Grease pumps and driveshafts on pumps 1,3,& 4 | Newmarket Sewage Pumping Station & Equalization Tank | 2026-02-26
WW-CEAST | February | -on site for bar screen 1 overtorque, reset bar screen, watched it travel, no issues, over torque occurs upon flinging rags, bar screen 1 back in service -bar screen 2 overtorque, screen 2 remains OOS with inlet gate closed, cannot be reset, WO created for maintenance | Newmarket Sewage Pumping Station & Equalization Tank | 2026-02-25
WW-CEAST | February | Weather today Clear and -5 Celsius -On site to complete work order W11558625. -Completed station check. -Entered station readings into SharePoint. -All pumps available in timed auto duty rotation every 3 hours. -Standby power generator available in auto. -Checked dry well. -Checked bar screens room. | Newmarket Sewage Pumping Station & Equalization Tank | 2026-02-02
WW-CEAST | February | Checked station/rag bins. Looked into screen 1 overtorque. Inlet gate has been closed to screen 1. Rake overtorques when it dumps into the conveyor. Created CMU for CMS | Newmarket Sewage Pumping Station & Equalization Tank | 2026-02-15
WW-CEAST | February | Weather today Snow and -2 Celsius -On site to complete work orders W11604338, W11604562, W1164863, W11658386. -Completed station check. -Entered station readings into SharePoint. -Weekly Alarm Management completed. -All pumps available in timed auto duty rotation every 3 hours. -Air compressors inspection and cleaning. -Standby power generator available in auto. -Checked dry well. -Checked bar screens room. -Screw Conveyor Cleaning and hosed out drain lines. -Checked bar screens and Rotated bin. -Cleaned bar screen room of rags and bar screen oil full. | Newmarket Sewage Pumping Station & Equalization Tank | 2026-02-18
WW-CEAST | February | Weather today Rain and snow mixed and 2 Celsius -On site to complete work orders W11604863, W11658706, W11610001, W11611433. -Completed station check. - Wet Well, Audible Alarm Test with Property Services Branch. - Facility Outfall, Inspection & Cleaning. -Entered station readings into SharePoint. -All pumps available in timed auto duty rotation every 3 hours. -Standby power generator available in auto. -Screw Conveyor Cleaning and hosed out drain lines. -Checked bar screens and Rotated bin. -Cleaned bar screen room of rags and bar screen oil full. -Bar Screen Bin Removal and Replacement - pushed rag bins back in after being picked up by Miller Waste. | Newmarket Sewage Pumping Station & Equalization Tank | 2026-02-20
WW-CEAST | February | Weather today Light Snow and -2 Celsius -On site to complete work orders W11587316, W11587867, W11587544.. -Completed station check. -Entered station readings into SharePoint. -All pumps available in timed auto duty rotation every 3 hours. -Air compressors inspection and cleaning. -Standby power generator available in auto. -Checked dry well. -Checked bar screens room. -Screw Conveyor Cleaning and hosed out drain lines. -Checked bar screens and Rotated bin. -Cleaned bar screen room of rags and bar screen oil full. -Bar Screen Bin Removal and Replacement - pushed rag bins out for picked up by Miller Waste. | Newmarket Sewage Pumping Station & Equalization Tank | 2026-02-11
WW-CEAST | February | On site for bar screen 1 adjusted tension arm on the gearbox and opened the inlet valve and put the screen back in auto | Newmarket Sewage Pumping Station & Equalization Tank | 2026-02-17
WW-CEAST | February | Inspect bar screen 2 and found slightly out of adjustment. Will return with additional staff to adjust to complete repairs. | Newmarket Sewage Pumping Station & Equalization Tank | 2026-02-10
WW-CEAST | February | Weather today A few clouds and -6 Celsius -On site to complete work orders W11584553, W11587867, W11594317. -Completed station check. -Entered station readings into SharePoint. -All pumps available in timed auto duty rotation every 3 hours. -Standby power generator available in auto. -Screw Conveyor Cleaning and hosed out drain lines. -Checked bar screens and Rotated bin. -Cleaned bar screen room of rags and bar screen oil full. -Bar Screen Bin Removal and Replacement - pushed rag bins back in after being picked up by Miller Waste. | Newmarket Sewage Pumping Station & Equalization Tank | 2026-02-13
WW-CEAST | February | Weather today Partly Cloudy and -7 Celsius -On site to complete work orders W11650108, W11593563, W11585171, W11560628. - Comprehensive Housekeeping. - 2026 IMS Emergency Procedure Quiz. - Odour Complaint Digital Forms Training ? Virtual. - Consolidated Monthly Surge Tank Inspection. - Surge tank and system inspection. - Surge tank valve and actuator exercise and inspection. - Surge tank drain valve inspection. - Transmission Line Flushing. | Newmarket Sewage Pumping Station & Equalization Tank | 2026-02-12
WW-CEAST | February | Weather today Partly cloudy and -2 Celsius -On site to complete work orders W11658045, W11658670. - Equalization Tank, Tipping Bucket Operational Check - Consolidated Wet Well Inspection, Overflow. - Bar Screen Cleaning/Lubrication. - Screw conveyor clean/lubrication. - Sluice gate valve/actuator exercise. - Wet well inspection and cleaning. - Wet well valve exercise. - High level alarm test. - Tipping bucket operational check. - Facility overflow inspection/clean. | Newmarket Sewage Pumping Station & Equalization Tank | 2026-02-19
WW-CEAST | February | In to Assist with Wet Well Entry. | Newmarket Sewage Pumping Station & Equalization Tank | 2026-02-07
WW-CEAST | February | Placed all pumps in manual off to temporarily reduce the noise while performing a training activity. Placed pumps back to auto- facility back to normal operation | Newmarket Sewage Pumping Station & Equalization Tank | 2026-02-19
WW-CEAST | February | Weather today A few clouds and -13 Celsius -On site to complete work order W11566725, W11557579, W11557751, W11567338, W11566949, W11560884. -Completed station check. -Entered station readings into SharePoint. -All pumps available in timed auto duty rotation every 3 hours. -Standby power generator test run. -JHSC health and safety inspection. -Hazardous waste collection and removal. -Air compressors inspection and cleaning. -Standby power generator available in auto. -Checked dry well. -Checked bar screens room. -Screw Conveyor Cleaning and hosed out drain lines. -Checked bar screens and Rotated bin. -Cleaned bar screen room of rags and bar screen oil full. -Bar Screen Bin Removal and Replacement - pushed rag bins out for picked up by Miller Waste. | Newmarket Sewage Pumping Station & Equalization Tank | 2026-02-04
WW-CEAST | February | Weather today Mostly cloudy and -11 Celsius -On site to complete work order W11585114, W11639140, W11562343. - Check valve inspection. - Dry well flood alarm test. - Sump pit inspection. - High low temp alarm test. - Autodialer test. - Air Compressor Inspection. -Hoist Inspection. -All pumps available in timed auto duty rotation every 3 hours. -Standby power generator available in auto. -Checked dry well. -Checked bar screens room. -Screw Conveyor Cleaning and hosed out drain lines. -Checked bar screens and Rotated bin. -Cleaned bar screen room of rags and bar screen oil full. - RS pump & motor inspection. Pump 1 - @ 0% speed 118.8 L/s, 135 kPa, 106 A, 622 V, 39 Hz; @ 25% speed 215.5 L/s, 145 kPa, 144 A, 622 V, 44 Hz; @ 35% speed 279 L/s, 166 kPa, 170 A, 624 V, 46 Hz Pump 2 - @ 0% speed 188.6 L/s, 147 kPa, 121 A, 384 V, 798 RPM, 40 Hz; @ 25% speed 332.6 L/s, 128 kPa, 152 A, 431 V, 895 RPM, 45 Hz; @ 100% speed 528.8 L/s, 181 kPa, 250 A, 574 V, 1193 RPM, 60 Hz Pump 3 - @ 0% speed 163.3 L/s, 139 kPa, 115 A, 371 V, 769 RPM, 39 Hz; @ 25% speed 232.4 L/s, 153 kPa, 153 A, 423 V, 877 RPM, 44 Hz; @ 35% speed 264.2 L/s, 152 kPa, 165 A, 445 V, 921 RPM, 46 Hz. Pump 4 - @ 0% speed 172.1 L/s, 149 kPa, 123 A, 623 V, 39 Hz; @ 25% speed 326.7 L/s, 144 kPa, 177 A, 622 V, 44 Hz; @ 35% speed 360.5 L/s, 154 kPa, 196 A, 622 V, 46 Hz. | Newmarket Sewage Pumping Station & Equalization Tank | 2026-02-05
WW-CEAST | February | Weather today A few clouds and -10 Celsius -On site to complete work order W11578976. -Completed station check. -Entered station readings into SharePoint. -All pumps available in timed auto duty rotation every 3 hours. -Standby power generator available in auto. -Screw Conveyor Cleaning and hosed out drain lines. -Checked bar screens and Rotated bin. -Cleaned bar screen room of rags and bar screen oil full. -Bar Screen Bin Replacement. | Newmarket Sewage Pumping Station & Equalization Tank | 2026-02-09
WW-CEAST | February | On site in response to mech screen 2 overtorque. Cleared the alarm and ran the screen on hand, noticed rake was slightly to the left touching the plate as it is moving upwards. Called ROC to call in 2nd Ops to close the inlet gate to screen 2 Marcus R on site to assist. Closed inlet gate to screen 2 and put both inlet gates 1 and 2 in remote to be able to operate it remotely without entering wet well. Notified ROC Screen 2 placed OOS, Screen 1 operating as intended. | Newmarket Sewage Pumping Station & Equalization Tank | 2026-02-07
WW-CEAST | February | Weather today Snow and -13 Celsius -On site to complete work order W11567338. -Screw Conveyor Cleaning and hosed out drain lines. -Checked bar screens and Rotated bin. -Cleaned bar screen room of rags and bar screen oil full. -Bar Screen Bin Removal and Replacement - pushed rag bins back in after being picked up by Miller Waste. | Newmarket Sewage Pumping Station & Equalization Tank | 2026-02-03
WW-CEAST | February | Weather today Snow and -9 Celsius -On site to complete work orders W11567338, W11574681. -Completed station check. -Entered station readings into SharePoint. -All pumps available in timed auto duty rotation every 3 hours. -Standby power generator available in auto. -Screw Conveyor Cleaning and hosed out drain lines. -Checked bar screens and Rotated bin. -Cleaned bar screen room of rags and bar screen oil full. -Bar Screen Bin Removal and Replacement - pushed rag bins back in after being picked up by Miller Waste. | Newmarket Sewage Pumping Station & Equalization Tank | 2026-02-06
WW-CEAST | February | -station check of site -reviewed SCADA -inspected site -entered data into sharepoint -station okay | Newmarket Bogart Creek Sewage Pumping Station | 2026-02-27
WW-CEAST | February | Took station readings and entered into sharepoint - reviewed trends, checked pump floor - all good. Station running under normal ops - no issues were found. | Newmarket Bogart Creek Sewage Pumping Station | 2026-02-23
WW-CEAST | February | -On site to complete comprehensive housekeeping tasks. | Newmarket Bogart Creek Sewage Pumping Station | 2026-02-26
WW-CEAST | February | Weather today Clear and -5 Celsius -On site to complete work order W11560674, W11558602, W11557601, W11557784, W11560772. -Completed station check. -Entered station and generator readings into SharePoint. -Standby power generator test run. -JHSC health and safety inspection. -Hazardous waste collection and removal. -All pumps available in all-stop auto duty rotation. -Standby power generator available in auto. | Newmarket Bogart Creek Sewage Pumping Station | 2026-02-02
WW-CEAST | February | Weather today Light Snow and -5 Celsius -On site to complete work orders W11584817, W11578953. -Completed station check. -Entered station readings into SharePoint. -Consolidated Dry Well & Hoist System Inspection. - Hoist System Inspection. - Check valve inspection. - Dry well flood alarm test. - Sump pit inspection. - RS pump inspection. - RS pump motor / inspection. - Air relief valve inspection. - High low temp alarm test. - Autodialer test. -Pumps 1-4 RS pump motor / inspection. Pump 1 -15% - 80.7 L/s Pump 2 constant speed ? 194.1 L/s Pump 3 - 15% - 97.2 L/s Pump 4 - 15% - 82.9 L/s -All pumps available in timed-auto duty rotation every 4 hours. -Standby power generator available in auto. -Checked dry well, ok. -No outstanding alarms. -Station operations normal. | Newmarket Bogart Creek Sewage Pumping Station | 2026-02-10
WW-CEAST | February | Weather today Partly Cloudy and -13 Celsius -On site to complete work order W11594271, W11582123, W11582137. -Completed station check. -Entered station readings into SharePoint. - Ran pump 2 in local for a few minutes with a flow of 198.5 L/s at 114 kPa. -RS Pump Discharge valve actuator inspection and exercise the ones that would work. -Manual valve inspection and exercise. -All pumps available in timed-auto duty rotation every 4 hours. -Standby power generator available in auto. -Checked dry well, ok. - Meter Chamber 2 Flood Alarm shelved will pump out groundwater from chamber next week with warmer weather. -Station operations normal. | Newmarket Bogart Creek Sewage Pumping Station | 2026-02-13
WW-CEAST | February | -On site to complete work orders. -Completed comprehensive housekeeping tasks. -Found outlet air line for OCU has completely torn off unit. Work request created. | Newmarket Bogart Creek Sewage Pumping Station | 2026-02-12
WW-CEAST | February | Weather today Overcast and 2 Celsius -On site to complete work order W11609955. -Completed station check. -Entered station readings into SharePoint. - Ran pump 2 in manual for a few minutes with a flow of 192.8 L/s at 117 kPa. -All pumps available in timed-auto duty rotation every 4 hours. -Standby power generator available in auto. -Checked dry well, ok. | Newmarket Bogart Creek Sewage Pumping Station | 2026-02-20
WW-CEAST | February | Weather today Light snow and -5 Celsius -On site to complete work orders W11579572, W11570187. -Odour control scrubber system inspection. -at 8:30 Wessuc onsite complete Wet well scum removal. -Wet well backup control mode in pac while work is being completed. -Wet well backup control mode back in auto now. -Wet well scum removal work is completed. | Newmarket Bogart Creek Sewage Pumping Station | 2026-02-03
WW-CEAST | February | Weather today Snow and -9 Celsius -On site to complete work order W11574612. -Completed station check. -Entered station readings into SharePoint. -All pumps available in timed-auto duty rotation every 4 hours. -Standby power generator available in auto. -Checked dry well, ok. -No outstanding alarms. -Station operations normal. | Newmarket Bogart Creek Sewage Pumping Station | 2026-02-06
WW-CEAST | February | -On site to complete work orders. -Station check completed, readings entered into SharePoint. -Chemical Tank 1 filled with water, Chemical Tank filled with H2O2 and OOS. -Comprehensive housekeeping tasks completed. | SEC Boxgove Corrosion Control Facility | 2026-02-24
WW-CEAST | February | -On site to complete work orders. -Station check completed, readings entered into SharePoint. -Peristaltic pump inspections completed. -O2 and HVAC alarms keep coming in due to reading fluctuations in GO22 O2 sensor on north wall. Work request created for instrumentation team. Chemical tank room has been stable around 17C. | SEC Boxgove Corrosion Control Facility | 2026-02-02
WW-CEAST | February | -station check of site -reviewed SCADA -inspected site -entered data into sharepoint -inspected chemical pumps -station okay | SEC Boxgove Corrosion Control Facility | 2026-02-17
WW-CEAST | February | -On site to complete work orders. -Turned off water to Chemical Tank 1, water at overflow level with HiHi level alarm in. -Ventilation system inspection completed. -Chemical tanks maintenance completed. -Sump pit system inspections completed. | SEC Boxgove Corrosion Control Facility | 2026-02-20
WW-CEAST | February | Attending site to check oxygen sensors (W11630835). Replaced GO22 sensor on North wall. Also, adjusted transmitters so that SCADA better matches the local gas detector reading. ROC was notified before and after maintenance activities. | SEC Boxgove Corrosion Control Facility | 2026-02-12
WW-CEAST | February | -On site to complete work orders. -Station check completed, readings entered into SharePoint. -Monthly JHSC H&S inspection completed, no issues noted. | SEC Boxgove Corrosion Control Facility | 2026-02-09
WW-CEAST | February | -On site to complete work orders. -Station check completed, readings entered into SharePoint. -Fans impeller bearing lubrication completed. -Nutrient tanks batch mixing completed. -Comprehensive housekeeping tasks completed. -Fan 3 OOS with outlet gate fault. | SEC Markham Odour Control Facility | 2026-02-24
WW-CEAST | February | -On site to complete work orders. -Station check completed, readings entered into SharePoint. -Fans impeller bearing lubrication completed. -Nutrient tank batch mixing completed - Nutrient pumps currently OOS. -Sump pump test and maintenance completed. Functionally tested sump pump and floats. -Water supply pumps, actuators exercise and inspection completed. Fully exercised all valves. -Hoist system inspections completed. -Fan 3 OOS with Outlet MV2 Fault. | SEC Markham Odour Control Facility | 2026-02-17
WW-CEAST | February | -On site to complete work orders. -Station check completed, readings entered into SharePoint. -Fans, impeller bearing lubrication completed. -Nutrient tank batch mixing completed. -OCF Damper Station GO2 Low Alarm outstanding. | SEC Markham Odour Control Facility | 2026-02-02
WW-CEAST | February | -On site to complete comprehensive housekeeping tasks. -Inspected fault on Fan 3 Outlet MV2 Gate. Tried to exercise valve locally, but valve is continually faulting both opening and closing. Appears to be metal shavings around stem, possibly rubbing on metal frame. Will create a work request for maintenance team to investigate further. -Fan 3 OOS. | SEC Markham Odour Control Facility | 2026-02-13
WW-CEAST | February | -On site to complete work orders. -Station check completed, readings entered into SharePoint. -Fans, impeller bearing lubrication completed. -Nutrient tank batch mixing completed. -Ventilation system inspection completed. -Blower inspection completed. -Monthly JHSC H&S inspection completed. | SEC Markham Odour Control Facility | 2026-02-09
WW-CEAST | February | -On site to complete work orders -Monthly diesel generator test run completed, readings entered into SharePoint. -1006 - Transferred station to generator power. -1106 - Transferred station back to utility power. -Generator start hours: 255.4, stop hours: 256.6, run time: 1.2hrs. -Damper and Knife Gate Sets 1-3, exercise and inspection completed. -Recirculation pump and strainer inspections completed. Currently Filter 2, Recirc Pump 2 is the only recirc pump in service. The rest of the recirc pumps are OOS with work request made for repairs/replacement. -OCF Damper Station GO2 Low and O2 Monitor 4 Alarms outstanding, work requests made to have sensors replaced. | SEC Markham Odour Control Facility | 2026-02-05
WW-CEAST | February | -On site to complete work orders. -Station check completed, readings entered into SharePoint. -Checked fan room and generator. -Comprehensive housekeeping tasks completed. | SEC Fairport Air Handling Facility (Shaft 4) | 2026-02-25
WW-CEAST | February | -On site to perform a station check. -Entered station readings into SharePoint. -Checked fan room and generator. | SEC Fairport Air Handling Facility (Shaft 4) | 2026-02-18
WW-CEAST | February | -On site to complete work orders. -Station check completed, readings entered into SharePoint. -Checked generator and fan room. -Manually rotated fan duties. -Heat trace system inspection completed. -Knife gate and electric valve exercise and inspection completed. | SEC Fairport Air Handling Facility (Shaft 4) | 2026-02-11
WW-CEAST | February | Attending site to check GO21 oxygen sensor (W11662062). Replaced sensor and calibrated. ROC was notified before and after maintenance activities. | SEC Fairport Air Handling Facility (Shaft 4) | 2026-02-12
WW-CEAST | February | -On site to complete work orders. -Station check completed, entered readings into SharePoint. -Checked generator and fan room. -Comprehensive housekeeping tasks completed. | SEC Altona Air Handling Facility (Shaft 6/7) | 2026-02-25
WW-CEAST | February | -On site to complete work orders. -Station check completed, readings entered into SharePoint. -Monthly JHSC H&S inspection, noted issue with low water pressure at eyewash station in fan room. Work request created for Property Services to investigate. -Monthly diesel generator test run completed, readings entered into SharePoint. -1140 - Transferred station to generator power. -1240 - Transferred station back to utility power. -Generator run hours, start: 257.3, stop: 258.4, run time: 1.1hrs. -General HVAC Alarm outstanding. | SEC Fairport Air Handling Facility (Shaft 4) | 2026-02-04
WW-CEAST | February | Take vibration readings on blower 2 | SEC Altona Air Handling Facility (Shaft 6/7) | 2026-02-17
WW-CEAST | February | -On site to complete work orders. -Station check completed, readings entered into SharePoint. -Electric valve and knife gate, exercise and inspection completed. -Ventilation system inspection completed. | SEC Altona Air Handling Facility (Shaft 6/7) | 2026-02-18
WW-CEAST | February | -On site to perform monthly diesel generator test run. -0843 - Transferred site to generator power. -0944 - Transferred site back to utility power. -Entered generator readings into SharePoint. -Generator start hours: 223.6, stop hours: 224.8, run time: 1.2hrs. -No signs of leaks before, during, or after generator test run. -Comprehensive housekeeping tasks completed while on site. | SEC Altona Air Handling Facility (Shaft 6/7) | 2026-02-20
WW-CEAST | February | Check for leak on generator Cleaned up coolant under generator Picked up coolant and topped up generator Ran generator up to temperature 189 degrees Shut generator off Rechecked for leaks, none visible Advise monitor generator and reservoir level | SEC Altona Air Handling Facility (Shaft 6/7) | 2026-02-17
WW-CEAST | February | -On site to complete work orders. -Station check completed, readings entered into SharePoint. -Checked fan room and generator. -Found small fluid leak below generator. Leak appears to be coming from fuel filter. Work request created for maintenance team to investigate issue. -Monthly JHSC H&S inspection completed, fire extinguisher in electrical room needs to be recharged. Supervisor notified to created work request for Property Services. -MAU fan found to not be running. Control panel display is blank and fan will not run locally as well. Property Services work request submitted by supervisor. -Heat trace system inspection completed. -Manually rotated fan duties while on site. | SEC Altona Air Handling Facility (Shaft 6/7) | 2026-02-11
WW-CEAST | February | -On site to perform a station check. -Entered station readings into SharePoint. -Checked fan room and generator. | SEC Altona Air Handling Facility (Shaft 6/7) | 2026-02-04
WW-CEAST | February | on-site to perform station check Heater element: 96.1F hydro meter: 282265kWh Fan running, condensate is draining, no foul odour detected. | Bayview & Steeles Air Management Facility | 2026-02-23
WW-CEAST | February | On site completed work orders. Station Check Heater Element - 94.2 F VFD Chiller - no panel to get the temperature. Hydro Meter reading - 279112 kWh No bad odour at time of visit. Station operations normal. Odour control scrubber inspection and filter cleaning. JHSC Health and Safety Inspection | Bayview & Steeles Air Management Facility | 2026-02-06
WW-CEAST | February | Weather today Partly Cloudy and -20 Celsius -On site to complete work order W11579913. -Completed station check. -Heater Element ? 98.7 F -VFD Chiller - no panel to get the temperature. -Hydro Meter reading - 279656 kWh -No bad odour at time of visit. -Station operations normal. | Bayview & Steeles Air Management Facility | 2026-02-09
WW-CEAST | February | Attending site to check air lines on FILT2_PDT1 (W11658828). Repaired broken air lines. Differential pressure transmitter is once again working correctly. | SEC Pickering Odour Control Facility (York/Durham) | 2026-02-26
WW-CEAST | February | -On site to complete work orders. -Reenabled BioFilter 2 BioScrubber Media DP Lo Alarm following repairs made to sensor. -Booster pump, solenoid valve, media spray checks completed on Filter 2 side. Fan 1/BioFilter 1 OOS. -Recirculation pump and strainer inspection completed. BioFilter 2, Recirc Pump 2 OOS. -Blower inspection completed. Fan 1 OOS. -Comprehensive housekeeping tasks completed. | SEC Pickering Odour Control Facility (York/Durham) | 2026-02-27
WW-CEAST | February | -On site to complete work orders. -Station check completed, readings entered into SharePoint. -Fan 1 OOS, panel showing "14 Overtemp" fault after fan ran for less than two hours. Will create work request. -Nutrient tanks and pumps OOS. -Filter 2 BioScrubber Media DP and Drain pH sensors OOS, work requests created. -Comprehensive housekeeping tasks completed. | SEC Pickering Odour Control Facility (York/Durham) | 2026-02-25
WW-CEAST | February | -On site to perform a station check. -Station check completed, readings entered into SharePoint. -Fan 1 OOS, panel showing "14 Overtemp" fault after fan ran for less than two hours. Will create work request. -Nutrient tanks and pumps OOS. -Filter 2 BioScrubber Media DP and Drain pH sensors OOS, work requests created. | SEC Pickering Odour Control Facility (York/Durham) | 2026-02-18
WW-CEAST | February | Attending site to check Biofilter Drain pH FILT2_AIT2 (W11658823), and BioScrubber 2 Media DP PDIT Lines Broken (W11658828). Cannot access pH probe due to snow. Will return once the pH probes can be accessed. PDIT lines are snapped. Will return with parts to complete this work as well as the pH probe maintenance once the snow is gone. ROC was notified before and after maintenance activities. | SEC Pickering Odour Control Facility (York/Durham) | 2026-02-12
WW-CEAST | February | Sheleved biofilter 1 media temp lolo alarm per alarm management. Alarm to be un-sheleved when Fan 1 is back in service. | SEC Pickering Odour Control Facility (York/Durham) | 2026-02-12
WW-CEAST | February | -On site to complete work orders. -Station check completed, readings entered into SharePoint. -Nutrient pumps and tanks OOS. -Monthly diesel generator test run completed, readings entered into SharePoint. -0916 - Transferred station to generator power. -1026 - Transferred station back to utility power. -Generator start hours: 262:48, stop hours: 264:03, run time: 1hr, 15min. -Monthly JHSC H&S inspection completed, no issues noted. -Fan 1 remains OOS. -Fan 2 running in auto with bypass knife gate open. | SEC Pickering Odour Control Facility (York/Durham) | 2026-02-04
WW-CEAST | February | -On site to perform a station check. -Entered station readings into SharePoint. -Placed Fan 1 back in service following previous repairs. -Several low temperature alarms on the Fan 1/BioFilter 1 side of the station are outstanding. Checked instruments, no faults, all readings appear legitimate. All readings also appear to be slowly rising as well. F1 BioFilter Media Temp LoLo, CAU1 Outlet Temp Lo, and BFILT1 Outlet Temp Lo all oustanding. -F2 BioFilter Drain pH HiHi Alarm also outstanding, will create work request for instrumentation team. Sensor is displaying a "Sensor no communication" fault. | SEC Pickering Odour Control Facility (York/Durham) | 2026-02-11
WW-CEAST | February | -Inspect Yonge and Jefferson Forest passive scrubber and change media as required -returned to site Feb 26 now that snow was cleared and inspected passively scrubber and changed as needed -less air seems to be blowing out since Oak Ridges is online | Central-East Wastewater Linear System | 2026-02-25
WW-CEAST | February | -On site to complete passive scrubber maintenance for the following locations: -Major Mackenzie and Leslie -Woodbine and 16th -Warden and Enterprise -Milne Park -Tuclor Lane/Hwy 48 -Inspected passive scrubbers and changed out media as required. | Central-East Wastewater Linear System | 2026-02-13
WW-WEST | February | Monitored wet well level and kept communication with Daniel Lemieux, onsite foreman. Craig Hendry arrived with the lockbox at 05:32. Wet well reached 4.98. Turned forcemain 2 back on. Opened force main 2. Removed LOTO on pump 4 and estop disengaged to begin pumping down the wet well. Once wet well reached 0.8 m, shut off pump 4. Re engaged estop and reestablished LOTO. Closed forcemain 2 and turned it off Key and lockbox sent with Craig Hendry at 05:57 | Vaughan Black Creek Pumping Station | 2026-02-25
WW-WEST | February | Monitored wet well level and kept communication with Daniel Lemieux, onsite foreman. Craig Hendry arrived with the lockbox at 00:57. Wet well reached 4.47 m. Turned forcemain 2 back on. Opened force main 2. Removed LOTO on pump 4 and estop disengaged to begin pumping down the wet well. Once wet well reached 0.8 m, shut off pump 4. Re engaged estop and reestablished LOTO. Closed forcemain 2 and turned it off Key and lockbox sent with Craig Hendry at 01:22 | Vaughan Black Creek Pumping Station | 2026-02-25
WW-WEST | February | On site for station checks, SharePoint readings and review of continuous monitoring data. Levelled rag bin and cleaned floors in screen room. Training Harie Maintenance on site to troubleshoot the south fm actuator. Closed the interconnect valve and the south FM was able to close when the pressure was relieved. Cycled a few times with no issues. | Vaughan Black Creek Pumping Station | 2026-02-24
WW-WEST | February | On site for vibration readings on pump 3. | Vaughan Black Creek Pumping Station | 2026-02-27
WW-WEST | February | Arrived on site at 21:48 to meet with capital sewer and capital delivery for shut down of pumps, foremain valves and to stop all flow through forcemain while work is being performed Notified ROC of the work being performed Performed tailgate meeting with Craig Hendry and reviewed LOTO procedure Placed all pumps to manual at 22:00. Placed pumps 1, 4 and 5 into local off, estop engaged and LOTO three pumps. Disabled low level lockout Daniel Lemieux arrived at Black Creek to view all pipes due to not being able to find chamber 93-04. Accessed all pipes and gave him the coordinates to 93-04 and 93-05. Once Daniel Lemieux gave the okay, manually stopped pump 3. Started pumping down wet well from 3.74 m at 23:33 using VFD pump 2. While pumping down wet well, placed pump 3 into local off, estop engaged, and LOTO pump 3. Once wet well reached 0.80 m at 23:47 manually stopped pump 2. Placed it in local, estop engaged, and LOTO. Placed forcemain 1 into manual off. Placed both forcemain valves into local off from manaul. Capital delivery onsite to witness lockout procedure Once done, keys and lockbox sent with capital sewer at 23:50 | Vaughan Black Creek Pumping Station | 2026-02-23
WW-WEST | February | Monitored wet well level and kept communication with Daniel Lemieux. Craig Hendry arrived with the lockbox at 05:06. Capital sewer is done with the work and is letting it cure. Wet well at 3.8 m when Craig arrived. Allowed enough time to cure. Worked on forcemain 1 actuator valve with electrician on call (Satnam Mann) but could not get the valve to open. Will need to be investigated further. Work order created and at priority 4. Forcemain 1 OOS. Opened interconnect valve between forcemain 1 and 2 to allow pumps 1-3 to push flow into forcemain 2 (north forcemain). Opened forcemain 2. All pumps feeding forcemain 2. Removed LOTO on pump 2 and estop disengaged. At 6:03, when wet well level reached 4.98 m, began pumping the wet well down. Once wet well level reached normal operating parameters, shut off pump 2. Removed LOTO on pumps 1, 3, 4, Disengaged estop and placed the pumps to remote. Manually turned on pump 3 and placed it into auto, and in auto speed Placed pump 1, 3, 4 back into auto, and in auto speed. Kept pump 5 locked out due to it being OOS due to pump seal leak (WO created). Reenabled low level lockout Cleared all active alarms. Reset alarms on wet well backup panel. Reset dialer Checked once again that the plant is back to normal operation Inspected dry well before leaving. No issues | Vaughan Black Creek Pumping Station | 2026-02-24
WW-WEST | February | Monitored wet well level and kept communication with Daniel Lemieux, onsite foreman. Daniel mentioned that guys are out and Craig Hendry is on his way back with the lockbox. Craig Hendry arrived with the lockbox at 01:12. Wet well reached 5.11 m. Turned forcemain 1 back on. Opened force main 1. Removed LOTO on pump 2 and estop disengaged to begin pumping down the wet well. Once wet well reached 0.8 m, shut off pump 2. Re engaged estop and reestablished LOTO. Closed forcemain 1 and turned it off Key and lockbox sent with Craig Hendry at 01:37 | Vaughan Black Creek Pumping Station | 2026-02-24
WW-WEST | February | Monitored wet well level and kept communication with Daniel Lemieux, onsite foreman. Daniel mentioned that guys are out and Craig Hendry is on his way back with the lockbox. Craig Hendry arrived with the lockbox at 23:22. Wet well reached 4.95 m. Turned forcemain 2 back on. Opened force main 2. Removed LOTO on pump 4 and estop disengaged to begin pumping down the wet well. Once wet well reached 0.8 m, shut off pump 4. Re engaged estop and reestablished LOTO. Closed forcemain 2 and turned it off Key and lockbox sent with Craig Hendry at 23:52 | Vaughan Black Creek Pumping Station | 2026-02-24
WW-WEST | February | Arrived on site at 21:52 to meet with capital sewer for shut down of pumps, foremain valves and to stop all flow through forcemain while work is being performed Notified ROC of the work being performed Performed tailgate meeting with Craig Hendry and reviewed LOTO procedure Placed all pumps to manual at 22:00. Placed pumps 1, 2 and 5 into local off, estop engaged and LOTO three pumps. Disabled low level lockout Once Daniel Lemieux gave the okay, manually stopped pump 3. Started pumping down wet well from 3.72 m at 22:02 using VFD pump 4. While pumping down wet well, placed pump 3 into local off, estop engaged, and LOTO pump 3. Closed forcemain 1. Once wet well reached 0.80 m at 22:16 manually stopped pump 4. Placed it in local, estop engaged, and LOTO. Closed forcemain 2. Turned breakers off for forcemain 1 and 2 Once done, keys and lockbox sent with capital sewer at 22:20 | Vaughan Black Creek Pumping Station | 2026-02-24
WW-WEST | February | Monitored wet well level and kept communication with Daniel Lemieux, onsite foreman. Requested Daniel to recall guys and send lockbox back at 03:17 Craig Hendry arrived with the lockbox at 3:27. Wet well reached 5.48 m due to forcemain 1 valve over torque. Could not reset the over torque. Turned on breaker for forcemain 2. Opened forcemain 2. Removed LOTO and disengaged estop on pump 4. Used pump 4 to pump down wet well. Once wet well reached 0.8 m, shut off pump 4. Reengaged e stop and reestablished LOTO. Requested maintenance on call to troubleshoot south forcemain valve over torque Closed forcemain 2. Powered off Key and lockbox sent with Craig Hendry at 4:07 | Vaughan Black Creek Pumping Station | 2026-02-24
WW-WEST | February | On site for Electrical PM. | Vaughan Black Creek Pumping Station | 2026-02-23
WW-WEST | February | - Checked screen, oil is good. Levelled bin - Performed housekeeping. Cleaned toilet and took garbage out - Performed weekly pump test. Ran each pumps 1-4 manually, one at a time, and recorded readings. Check valve for pump 3 not closing. Work order already created. Pump 5 OOS Pump 1: 589.8 L/s, pressure 300 kPa Pump 2: 453 L/s at 100%, pressure 265 kPa Pump 3: 134.8 L/s at 100% speed, pressure 215 kPa Pump 4: 475 L/s at 100% speed, pressure 264 kPa - Checked station and recorded readings on SharePoint. Trends okay. | Vaughan Black Creek Pumping Station | 2026-02-27
WW-WEST | February | Monitored wet well level and kept communication with Daniel Lemieux, onsite foreman. Craig Hendry arrived with the lockbox at 03:03. Wet well reached 5.20 m. Turned forcemain 2 back on. Opened force main 2. Removed LOTO on pump 4 and estop disengaged to begin pumping down the wet well. Once wet well reached 0.8 m, shut off pump 4. Re engaged estop and reestablished LOTO. Closed forcemain 2 and turned it off Key and lockbox sent with Craig Hendry at 03:32 | Vaughan Black Creek Pumping Station | 2026-02-25
WW-WEST | February | On site to troubleshoot disconnect switch for South Force Main Valve MV-11. Disconnect switch in internally corroded. Lubricated to allow the disconnect to close again. Tested disconnect function. Ok. Should be replace in the near future. | Vaughan Black Creek Pumping Station | 2026-02-11
WW-WEST | February | Monitored wet well level and kept communication with Daniel Lemieux. Craig Hendry arrived with the lockbox at 07:07. Capital sewer is done with the work and letting the epoxy cure. Wet well at 4.15 m when Craig arrived. Removed LOTO on pump 4 and estop disengaged. Opened forcemain 2. At 7:34, when wet well level reached 5.14 m, began pumping the wet well down. Once wet well level reached normal operating parameters, shut off pump 4 Removed LOTO on pumps 1, 2, 3, Disengaged estop and placed the pumps to remote. Opened forcemain 1. Manually turned on pump 3 and placed it into auto, and in auto speed Placed pump 1, 2, 4 back into auto, and in auto speed for VFD pumps. Removed loto and disengaged estop for pump 5. Kept pump 5 in local off due to pump 5 being OOS (pump seal leak, WO already created). Reenabled low level lockout Cleared all active alarms. Reset alarms on wet well backup panel. Reset dialer Checked once again that the plant is back to normal operation Inspected dry well before leaving. No issues | Vaughan Black Creek Pumping Station | 2026-02-25
WW-WEST | February | Monitored wet well level and kept communication with Daniel Lemieux. Craig Hendry arrived with the lockbox at 02:40. Capital sewer is done with the work and is letting it cure. Wet well at 4.25 m when Craig arrived. Allowed enough time to cure. Turned forcemain 1 into manual. Opened force main 1. Removed LOTO on pump 2 and estop disengaged. At 3:18, when wet well level reached 5.10 m, began pumping the wet well down. Once wet well level reached normal operating parameters, shut off pump 2. Turned forcemain 2 back to open. Removed LOTO on the remaining pumps 1, 3, 4. Disengaged estop and placed the pumps to remote. Manually turned on pump 3 and placed it into auto, and in auto speed. Placed pump 1, 3, 4 back into auto, and in auto speed. Kept pump 5 in manual due to it being OOS. Reenabled low level lockout Cleared all active alarms. Reset alarms on wet well backup panel. Reset dialer Checked once again that the plant is back to normal operation Inspected dry well before leaving. No issues Update: removed loto on pump 5 and disengaged estop. Left the pump in local. Cleared e stop alarm | Vaughan Black Creek Pumping Station | 2026-02-13
WW-WEST | February | Monitored wet well level and kept communication with Daniel Lemieux. Daniel notified he will be recalling guys and sending the lockbox back at 00:48 before doing concrete work Craig Hendry arrived with the lockbox at 01:00. Wet well reached 4.49 m, peak. Turned forcemain 1 into remote. Opened force main 1. Removed LOTO on pump 2 and estop disengaged to begin pumping down the wet well. Once wet well reached 0.8 m, shut off pump 2. Re engaged estop and reestablished LOTO. Closed forcemain 1 and turned it off Key and lockbox sent with Craig Hendry at 01:25 | Vaughan Black Creek Pumping Station | 2026-02-13
WW-WEST | February | Completed the station check Entered data into SharePoint Placed the rag bins outside for pickup Garage door contact is bent so it appears open in the security system so the building cannot be armed | Vaughan Black Creek Pumping Station | 2026-02-17
WW-WEST | February | Installed new air filters on both Generators. | Vaughan Black Creek Pumping Station | 2026-02-12
WW-WEST | February | On site with safety director Craig from capital sewer. Tailgate meeting re: LOTO. Notified ROC of night work. 10:19 wet well pumped down to 0.76m and all pumps locked out. Key/lockbox offsite with Capital sewer. South FM MV 1 faulted when closed on over torqued. Attempted to reset but, the break stuck open. Called ROC to dispatch electrician to troubleshoot. Will use north FM in the interim. Can open south by hand if required. 23:40 Capital returned with key, unlock and run RS Pump # 4. Wet well peaked at 5.27m. Pumped down to 0.7m and LOTO reestablished at 00:08 (Feb 11) Key sent off with capital sewer. 01:45: wet well at 5.11m peak. Capital returned with key for a pump down. South FM 1 local disconnect lubricated and functioning better and over torque was reset. Use south fm and RS pump 2 for pump down. 02:10: wet well pumped down to 0.70m. LOTO Reestablished and key sent off with Captital Sewer. 04:06 capital sewer returned key for a pump down. Wet well peak 4.89m. Unlock RS Pump 2 and pump down wet well. Wet well pumped down to 0.70m @ 04:26. LOTO reestablished and capital sewer departing with key. 06:33 Capital sewer back on site. LOTO removed and system pumped down back into normal operation ranges. Peak wet well was 4.81m. Capital sewer is finished working for the day. Enabled low level lock outs. All pumps (except Pump 5 returned to remote/auto. Pump 3 in duty 1 @ 132L/s. Wet well at 3.52m. All alarm history cleared and ROC notified that work is complete. | Vaughan Black Creek Pumping Station | 2026-02-10
WW-WEST | February | Onsite for station check and weekly pump run test Station check ok - no new issues. Bar screen oil levels good and leveled bin. Pump run test: Pump1 562.7L/s at 297kpa Pump 2 - 448.4L/s at 265kpa at 100% Pump 3 132.9L/s at 214kpa at 100% Pump4 - 471.7L/s at 263kpa at 100% Pump 5 -OOS | Vaughan Black Creek Pumping Station | 2026-02-13
WW-WEST | February | Onsite to wait for diesel delivery. Delivery onsite at 1:40pm Diesel tank at 93cm and 5.889L Delivery completed at 2:15pm Diesel tank now at 141cm and 9002L Total diesel volume delivered 3374.7Litres. | Vaughan Black Creek Pumping Station | 2026-02-12
WW-WEST | February | Take vibration readings on pump 3. | Vaughan Black Creek Pumping Station | 2026-02-12
WW-WEST | February | - Checked screen, oil is good. Levelled bin - Pushed bin back in - Performed weekly pump test. Ran each pumps 1-4 manually, one at a time, and recorded readings. Check valve for pump 3 not closing. Work order already created. Pump 5 OOS Pump 1: 570.2 L/s, pressure 305 kPa Pump 2: 450 L/s at 100%, pressure 267 kPa Pump 3: 132.4 L/s at 100% speed, pressure 214 kPa Pump 4: 466 L/s at 100% speed, pressure 265 kPa - Checked station and recorded readings on SharePoint. Trends okay. Noticed high vibration on pump 1. Will monitor | Vaughan Black Creek Pumping Station | 2026-02-20
WW-WEST | February | Checked station and trends, and recorded readings on SharePoint. Checked screen, all okay. Levelled bin Mopped floor | Vaughan Black Creek Pumping Station | 2026-02-10
WW-WEST | February | Arrived on site at 21:50 to meet with capital sewer and capital delivery for shut down of pumps, foremain valves and to stop all flow through forcemain while work is being performed Notified ROC of the work being performed Performed tailgate meeting with Craig Hendry and reviewed LOTO procedure Placed all pumps to manual at 22:08. Placed pumps 1, 4 and 5 into local off, estop engaged and LOTO three pumps. Closed forcemain 2, manual off Once Craig Hendry gave the okay, manually stopped pump 3. Disabled low level lock out. Started pumping down wet well from 3.74 m at 22:13 using VFD pump 2. While pumping down wet well, placed pump 3 into local off, estop engaged, and LOTO pump 3. Once wet well reached 0.80 m at 22:31. manually stopped pump 2. Placed it in local, estop engaged, and LOTO. Placed forcemain 1 into manual off. Placed both forcemain valves into local off from manaul off Capital delivery onsite to witness LOTO procedure Once done, keys and lockbox sent with capital sewer at 22:35 Monitored wet well level and kept communication with Daniel Lemieux, foreman onsite. Notified Daniel to recall guys and send lockbox back at 23:14 | Vaughan Black Creek Pumping Station | 2026-02-12
WW-WEST | February | Craig Hendry arrived with the lockbox at 23:28. Wet well reached 4.30 m. Turned forcemain 1 into remote. Opened force main 1. Removed LOTO on pump 2 and estop disengaged to begin pumping down the wet well. Once wet well reached 0.8 m, shut off pump 2. Re engaged estop and reestablished LOTO. Closed forcemain 1 and turned it off Key and lockbox sent with Craig Hendry at 23:52 | Vaughan Black Creek Pumping Station | 2026-02-12
WW-WEST | February | On site with Capital sewer for shuts downs. Notify ROC of work. Tailgate meeting re: LOTO Pump down wet well to 0.7m @ 22:23. LOTO established and key sent with capital sewer / lock box. 23:43: capital sewer returned for a pump down. Unlock pump 2 and cycle to draw down wet well. Wet well peaked at 5.07m. 00:05 wet well pumped down to 0.7m and LOTO reestablished. Key sent away with Captital Sewer. 01:39 Captital Sewer returned with key. Wet well peak at 5.03m. Remove LOTO on RS Pump 2 and draw down wet well. 02:03: wet well pumped down to 0.70m. Reestablished LOTO and sent key with Capital sewer. 03:41 Captial Sewer returned with LOTO key. Unlocked pump 2 and begin to pump down wet well. Wet well peak at 4.61m. 04:01: wet well pumped down to about 0.70m and LOTO reestablished. Captial sewer departed with key. 06:17 capital sewer returned to site. Wet well at 5.03m. Remove all LOTO and station pumped down into normal operating ranges. Re enabled low level lock outs. Reset all active alarms. Both north and south FM available. Notify ROC that work is complete. | Vaughan Black Creek Pumping Station | 2026-02-11
WW-WEST | February | On site to repair the floor drains. Repair was completed | Vaughan Black Creek Pumping Station | 2026-02-06
WW-WEST | February | Replaced rotted cast iron pipe with cast iron and abs fittings. | Vaughan Black Creek Pumping Station | 2026-02-03
WW-WEST | February | Onsite for station check - no new issues reviewed trends and added data into SharePoint. Completed weekly RS pump run test - no new issues Pump1 -573.1L/s at 297kPa Pump 2 - 453.2 L/s at 100% at 262kPA Pump 3 131.3L/s at 100% and 215kPA Pump4 - 460.3 L/s at 100% at 265kPA Pump 5 -OOS pumps placed back into Auto and put in duty. Pump 5 remains in manual OOS Inspected seal water and cleaned screens - all clear and functioning. | Vaughan Black Creek Pumping Station | 2026-02-06
WW-WEST | February | On site with Capital Sewer for person entries into the Jane dufferin collector down stream of station. Tailgate meeting for the LOTO procedures. ROC notified of work. Disabled low level lockout. Pump down wet well to 0.90m with RS Pump 2. All pumps isolated and locked out @ 22:39. Monitor wet well levels for the duration of the shut down. 23:53 wet well reached 5.00m. Capital returned key, unlocked and pump down wet well with RS Pump 2. 00:18 wet well pumped down to 0.75m. LOTO reestablished and key sent off with Capital Sewer. 02:05 capital returned with keys. Pumped down wet well again with pump 2 for another shut down. Level reached 5.22m at peak. Pumped down to 0.71m @ 02:30, LOTO reestablished. 04:32 capital sewer is finished for the night. Remove all LOTO. Pumped down wet well to normal operating range and put all systems back to normal flows. Pump 3 running at 21% @ 80L/s, wet well is at 3.71m. Cleared all alarm history - no alarms on banner. Notify ROC that work is completed. | Vaughan Black Creek Pumping Station | 2026-02-09
WW-WEST | February | On site to finish the drain pipe repair on B1. The job is completed | Vaughan Black Creek Pumping Station | 2026-02-04
WW-WEST | February | Attending site to check screen room oxygen sensor (W11603126). Found sensor not functioning. Replaced sensor and calibrated. ROC was notified before and after maintenance activities. | Vaughan Black Creek Pumping Station | 2026-02-03
WW-WEST | February | Onsite with Young Jung for work orders. ROC notified of work being done. Completed consolidated dry well inspection - Triggered hi/lo temperature alarm and dry well flood alarms. Tested dry well sump pit with floats, no issues. Inspected Check valves - no new issues. Placed pumps 1,2,4 and 5 into manual off to Exercise suction valves on pumps 1,2,4 and 5. Pumps placed back into auto. Pump 5 left in manual off Flushed air relief valves. Completed consolidated wet well work order. Greased and inspected bar screen - no new issues. Manually exercised valves in wetwell. Trigger wetwell overflow alarm 1 and 2. Hosed down and cleaned debris in wetwell | Vaughan Black Creek Pumping Station | 2026-02-09
WW-WEST | February | Replaced petcock on generator 2 block heater south side. | Vaughan Black Creek Pumping Station | 2026-02-03
WW-WEST | February | - Notified ROC of the work being performed - Inspected the generators and fuel level for monthly generator test, all okay. Also testing the generator for leaks after maintenance replaced the petcock. - Started generator 2 at 9:48. Recorded readings after 30 minutes. Run time for generator 2 from 491.6 hrs to 492.7 hrs. No issues with readings. - Started the generator 1 at 11:02. Recorded readings on SharePoint after 30 minutes, no issues. Ran for approximately one hour. Runtime for generator 1 from 479 hrs to hrs - Fuel level readings before: 95 cm (6014 L). After gen test cm ( L) - Performed JHSC inspection. No issues - Inspected odour control unit. Greased fittings. Filters below 2.5 inch - Checked screen. Topped up oil for screen lubrication - Cleaned area. Pushed bin out for pick up. - Checked for hazardous waste. None found - Daniel Hirstwood shelved screen room south o2 Lo alarm but could not shelve screen room south o2 Lo Lo alarm due to it being a highly managed alarm. - Cleared alarms caused by the generator test. Noticed PLC I/O failure on generator, cleared alarm and ran the generator. Generator ran fine. Will monitor this alarm and create a work order for maintenance to investigate if it comes back. | Vaughan Black Creek Pumping Station | 2026-02-03
WW-WEST | February | Remotely unshelved screen room south o2 Lo alarm | Vaughan Black Creek Pumping Station | 2026-02-03
WW-WEST | February | In to Assist with Diesel Generator Fuel Delivery. | Vaughan Humber Pumping Station | 2026-02-23
WW-WEST | February | - Checked station and trends, and recorded readings on SharePoint. No new issues - Raked screen and checked oil, all okay - Pushed bin back in - Assisted with vibrational study and rotated pump duties for maintenance - Moved some stuff in front of the access hatch and charged scissor lift | Vaughan Humber Pumping Station | 2026-02-27
WW-WEST | February | On site for vibration readings. With young?s help to change the duty?s | Vaughan Humber Pumping Station | 2026-02-27
WW-WEST | February | Onsite for station check. No new issues. Reviewed trends and added data into SharePoint. Bins pushed out for pick up. Completed cleaning on bathroom and main room. | Vaughan Humber Pumping Station | 2026-02-24
WW-WEST | February | On site for scheduled work. Levelled bin | Vaughan Humber Pumping Station | 2026-02-28
WW-WEST | February | Onsite for diesel delivery. Diesel delivery onsite at 10:00am Diesel currently at 156.04cm and 13128.05L After delivery diesel tank now at 204cm and 17,482L 4,431.5L total delivered. | Vaughan Humber Pumping Station | 2026-02-23
WW-WEST | February | - Notified ROC of the work being performed - Had issues with the door freezing up despite heaters being turned on over the weekend. Took a while to remove ice. Once done, opened the screen door and pushed bins in - Inspected the generator. Oil level is good, coolant is good, and battery is good. Started the generator test at approximately 10:22 and ran for an hour. Took readings after 30 minutes and recorded on SharePoint. No issues. Generator hours from 295 hrs to 296.3 hrs. Fuel level from 158 cm (13302 L) to 157 cm (13266 L) - Inspected heat exchange radiator while generator was running. No issues - Tested dry well flood alarm. Alarm received - Inspected sum pit. Pumps works well when float lifted. No issues - Tested building hi and low temperature alarm. Alarm received - Performed JHSC inspection. No issues - Inspected check valve. No new issues. Slight minor passing still exist in check valve 3. Maintenance deemed not an issue due to very little flow passing back - Pumps and motors all okay - Suction valves all okay - Checked for hazardous waste. None found | Vaughan Humber Pumping Station | 2026-02-02
WW-WEST | February | Onsite for station check - no new issues. Reviewed trends and added data into SharePoint. Leveled bins and checked bar screen - no issues. | Vaughan Humber Pumping Station | 2026-02-20
WW-WEST | February | Onsite for station check. No new issues. Reviewed trends and entered data into SharePoint. Pushed empty bins back in and leveled bar screen bins | Vaughan Humber Pumping Station | 2026-02-13
WW-WEST | February | Onsite to level bins. No issues. | Vaughan Humber Pumping Station | 2026-02-15
WW-WEST | February | Completed the station check Entered data into SharePoint Placed the rag bins outside for pick up Inspected the forcemain distribution chamber | Vaughan Humber Pumping Station | 2026-02-17
WW-WEST | February | Placed the rag bins back in the screen room Reset pump 2 vfd There was a brief power outage and the generator kicked on When power returned the ats failed Reset the ats and it transferred back ok Everything working as intended | Vaughan Humber Pumping Station | 2026-02-19
WW-WEST | February | Leveled the rag bins | Vaughan Humber Pumping Station | 2026-02-22
WW-WEST | February | Attending site to check diesel tank fill monitor not working (W11653977). Found water damaged power supply. Replaced power supply and the fill monitor is now operating normally. | Vaughan Humber Pumping Station | 2026-02-17
WW-WEST | February | Checked station and trends, and recorded readings on SharePoint. Levelled bin and checked oil level Shovelled in front of the screen door and salted floor Mopped floor | Vaughan Humber Pumping Station | 2026-02-06
WW-WEST | February | Checked station and trends, and recorded readings on SharePoint. Levelled bin and pushed bin out for pick up. Salted in front of the screen door Created a work order to address no power and no audible alarm on RFLM-1 diesel tank fill monitor | Vaughan Humber Pumping Station | 2026-02-10
WW-WEST | February | - On site for wet well inspection and cleaning - Tested the wet well high level alarm. Alarm received. No issues - Tested the metro overflow alarm by tripping the float. Alarm received. - Overflow to Toronto maintenance hole also tested. alarm received - Exercised wet well valves. Greased fittings. The isolation gate after the screen is very stiff - Cleaned wet well - Inspected the bar screen and checked oil. No issues. Greased fittings - Levelled bin and pushed bin back in | Vaughan Humber Pumping Station | 2026-02-04
WW-WEST | February | Onsite for station check and bin replacement. Station check all ok. No new issues. Reviewed trends and entered data into SharePoint. Placed screen bins out for pick up | Vaughan Humber Pumping Station | 2026-02-03
WW-WEST | February | In to Complete Scheduled WO. Reviewed SCADA and Trends. No Issues Found. Levelled and Adjusted Bins. Inspected and Tidied HWs. Exercised Screen Room Roll Up Door Several Cycles. Broke Up and Removed Ice Build Up at Base of Roll Up Door Closure Point. No Other Issues Found. | Vaughan Humber Pumping Station | 2026-02-08
WW-WEST | February | Onsite with Young for consolidated wetwell work order | Vaughan Humber Pumping Station | 2026-02-04
WW-WEST | February | Remotely Rotated RAS Pump Duties. Pumps #1 and 3 Manual Off, Pumps #2 and 4 in Auto. | Kleinburg Water Resource Recovery Facility | 2026-02-23
WW-WEST | February | - Added 9 bags of soda ash into the hopper - Moved hose for foam control in aeration tank 1 outlet to aeration tank 2 outlet - Reset RAS batch wasting mode at 17:00. Placed WAS pumps to manual off | Kleinburg Water Resource Recovery Facility | 2026-02-28
WW-WEST | February | On site to investigate the auto rotation of banks an and b in the uv channels. All setting are enabled to rotate but, system seems to be stuck on bank B. Manually swap the lead from B to A on both channels. Will monitor over next few days to see if it begins to rotate automatically again. If it does not, will generate a CMU. | Kleinburg Water Resource Recovery Facility | 2026-02-27
WW-WEST | February | Harie Rajamithiran(OIT) working under the direction of Daniel Hirstwood(OIC). -Collected weekly compliance samples -Completed lab analysis and station check , no issues found -Completed headworks housekeeping -Started batch wasting process at 10:38 , wasting 26.02m^3 from 12:00-14:00 -Added 8 bags of soda ash into hopper -Ran Bertha for test purposes to detect fuel leakage : start (405.8) end (406.2) -Bertha had a small amount of shake and noise during cooldown idle -Returned WAS pumps 1&2 into Manuel off | Kleinburg Water Resource Recovery Facility | 2026-02-25
WW-WEST | February | In to Complete Scheduled WOs. Lowered Sludge Thickening Tank #1 Decant Slip Tube. Enabled Batch Waste Set-point. RAS Pumps Auto Off in Preparation for Wasting @ 8:50. Decant Complete, Raised Decant Slip Tube. Sludge Thickening Tank #1 Outlet Valve Manual Open, Transferred Thickened Sludge. Outlet Valve Returned to Manual Closed. WAS Pump #1 and 2 Manual On and Off Intermittently and Sequentially for Wasting. Rotated Active Sludge Thickening Tank. WAS Valve #2 Manual Closed, WAS Valve #1 Manual Open. Wasting Complete, Reset Batch Wasting Set-point. RAS Pumps #1 and 3 Running in Auto. Wasted 16 m3 from Clarifier #1 and 19 m3 from Clarifier #2. Topped Up Soda Ash Hopper ?> 10 Bags. Placed Clarifier Helical Skimmers in Manual On for Scum Tank Flushing. Hosed and Flushed Tank. Returned to Auto and Service. Placed Scum Pump #1 in Manual On for Scum Tank Drawdown. Drawdown Complete Returned to Auto and Service. Completed Aer. Tank Outlet Channel Cleaning and Drained Diffuser Line Condensation with No Issues. | Kleinburg Water Resource Recovery Facility | 2026-02-23
WW-WEST | February | In to Complete Scheduled WOs. Enabled Batch Waste Set-point. RAS Pumps Auto Off in Preparation for Wasting @ 8:30. WAS Pump #1 and 2 Manual On and Off Intermittently and Sequentially for Wasting. Wasting Complete, Reset Batch Wasting Set-point. RAS Pumps #1 and 3 Running in Auto. Wasted 12 m3 from Each Clarifier. Inspected and Flushed Filter Reject Wash Boxes, Weirs and Air Lifts with No Issues. Hosed and Flushed Alum Accretion from Filter Inlet Channel Mixer Drive Shaft. Verified Alum Dosage Point. Topped Up Soda Ash Hopper ?> 10 Bags. Flushed Bar-screen Dewatering Press Drainage Line with No Issues. Returned to Service. | Kleinburg Water Resource Recovery Facility | 2026-02-27
WW-WEST | February | Remotely enabled RAS batch wasting mode at 14:00. Set up automatic batch wasting to waste between 15:00~16:00. Set to waste 15 m^3 from train 1 and 15 m^3 from train 2. Will be on site later for scheduled work | Kleinburg Water Resource Recovery Facility | 2026-02-28
WW-WEST | February | In to Complete Scheduled WOs. Enabled Batch Waste Set-point. RAS Pumps Auto Off in Preparation for Wasting @ 8:30. Placed Clarifier Helical Skimmers in Manual On for Scum Tank Flushing. Scum Tank Flushing Complete. Returned to Auto and Service. Lowered Sludge Thickening Tank #2 Decant Slip Tube. Found Filter Air Lift Clogged. Cleared Obstruction and Returned to Service. Decant Complete, Raised Decant Slip Tube. Sludge Thickening Tank #2 Outlet Valve Manual Open, Transferred Thickened Sludge. Outlet Valve Returned to Manual Closed. WAS Pump #1 and 2 Manual On and Off Intermittently and Sequentially for Wasting. Flushed Bar-screen Dewatering Press Drainage Line with No Issues. Returned to Service. Topped Up Soda Ash Hopper ?> 8 Bags. Reject Sump Pump #1 Fault Alarm Outstanding. Reset Fault and Cleared Alarm. Returned Pump to Service. Known Issue, WO Made and Pending for Maintenance. Wasting Complete, Reset Batch Wasting Set-point. RAS Pumps #1 and 3 Running in Auto. Wasted 10 m3 from Clarifier #1 and 13 m3 from Clarifier #2. Inspected and Flushed Filter Reject Wash Boxes, Weirs and Air Lifts with No Issues. Completed Biorem Odour Control Unit Inspection. All Equipment Operational, All Parameters within Optimal Rates. Recirculation Water pH Analysis: 2.79. Greased Blower Driveshaft Bearings. No New Issues Found. Completed Filter Bypass and Alum Containment Float Alarm Tests with No Issues. Confirmed Reception by the ROC. Cleared Associated Alarms and Returned to Service. | Kleinburg Water Resource Recovery Facility | 2026-02-24
WW-WEST | February | Harie Rajamithiran(OIT) working under the direction of Daniel Hirstwood(OIC). -Completed lab analysis and station check , no issues found -Added 8 bags soda ash into the hopper -Started batch wasting process at 11:00 , wasting 26.01m^3 from 12:00 - 14:00 -Completed clarifier sluice gate valve exercise and greased stems -Put WAS pumps 1&2 into manuel off | Kleinburg Water Resource Recovery Facility | 2026-02-26
WW-WEST | February | Harie Rajamithiran(OIT) working under the direction of Daniel Hirstwood(OIC). -No changes to plant process was done, was walking through the plant for training purposes | Kleinburg Water Resource Recovery Facility | 2026-02-24
WW-WEST | February | In to Complete Scheduled WOs. Notified ROC. Received Soda Ash Delivery. Reviewed and Signed Documentation. Completed UV/FE Channel Clean-Out with No Issues. Tested FE Channel Sump Hi Level Float Alarm. Confirmed Reception by the ROC. Returned to Service, Cleared Associated Alarms. Completed UV Channel #1 Bulb Replacement with No Issues. Tested Unit and Returned to Service. Cleared Associated Alarms. Completed Plant Service Water Y-Screen Cleaning with No Issues. Purged Pumps, Flushed PIT and Returned System to Service. Cleared Associated Alarms. Completed Clarifier Sluice Gate Manual Valve Exercises with No Issues. Greased Valve Stems and Returned to Service. | Kleinburg Water Resource Recovery Facility | 2026-02-26
WW-WEST | February | Received call by PCS on call, Kyle Carlene is working on the effluent trend gap and the trend flatlining. Update: fix performs by PCS. correct trend is being displayed and the missing data will be back populated on Monday | Kleinburg Water Resource Recovery Facility | 2026-02-01
WW-WEST | February | On site for high fuel temperature alarm. Fuel system is cool. Cleared alarm 263. Unplugged sensor to confirm location of sensor. Alarm 263 came back in. Test ran generator okay Fuel was not overheating. Will order a fuel temperature sensor to replace. | Kleinburg Water Resource Recovery Facility | 2026-02-02
WW-WEST | February | Onsite for scheduled work orders. Called ROC to inform of monthly generator run test. Transferred power from hydro to Bertha at 9:12am - after checking it to record data Bertha had a ?fuel temp sensor high? warning. Informed team lead. Transferred back to hydro at 10:15 Rotated UV duties from Uv 1 to UV 2 in duty before transferring power to Stella at 10:53 - added data to SharePoint and Transferred back to hydro at 11:54 with no issues. Maintenance onsite to investigate sensors for the fuel temp sensor alarm on Bertha. Alarm cleared and ran Bertha in manual at 1:45 with no alarms. Turned Bertha back to auto at 1:55 Added 11 bags of soda ash to hopper. Inspected circular plant aeration blowers 1-4 All okay, oil levels good, belts good. No issues found. Inspected circular plant aeration blower filters - all okay and clean. Cleaned scum tank. Completed JHSC inspection and checked plant for hazardous waste. | Kleinburg Water Resource Recovery Facility | 2026-02-02
WW-WEST | February | In to Complete Scheduled WOs. Enabled Batch Waste Set-point. RAS Pumps Auto Off in Preparation for Wasting @ 9:40. Lowered Sludge Thickening Tank #1 Decant Slip Tube. Rotated RAS Pump Duties. Pumps #2 and 4 Manual Off, Pumps #1 and 3 in Auto. Rotated Active Sludge Thickening Tank. WAS Valve #1 Manual Closed, WAS Valve #2 Manual Open. Decant Complete, Raised Decant Slip Tube. Sludge Thickening Tank #1 Outlet Valve Manual Open, Transferred Thickened Sludge. Outlet Valve Returned to Manual Closed. WAS Pump #1 and 2 Manual On and Off Intermittently and Sequentially for Wasting. Wasting Complete, Reset Batch Wasting Set-point. RAS Pumps #1 and 3 Running in Auto. Wasted 12 m3 from Clarifier #1 and 15 m3 Clarifier #2. Completed Aer. Tank Outlet Channel Cleaning and Drained Diffuser Line Condensation with No Issues. | Kleinburg Water Resource Recovery Facility | 2026-02-02
WW-WEST | February | Harie Rajamithiran(OIT) working under the direction of Lauren Swanson(OIC). On-site Entry: -Completed lab analysis and station check -Added 10 bags of soda ash into the hopper -Checked aeration outlet for rags Remote Entry: -Started batch wasting process at 10:15, wasting from 11:00-13:00 for 12m^3 per train | Kleinburg Water Resource Recovery Facility | 2026-02-20
WW-WEST | February | Onsite for PMs Assisted Harie with daily lab and station check. Cleaned aeration tank outlet for rags. Created WO for faulting WAS valves(W11679515) - WAS_MV2 closing and won?t stay open. WAS_MV1 interlocking repeatedly during traveling closed and open. Placed WAS pumps back into manual when wasting completed. RAS placed back in operation. | Kleinburg Water Resource Recovery Facility | 2026-02-20
WW-WEST | February | In to Complete Scheduled WOs. WAS Pump #1 and 2 Manual On and Off Intermittently and Sequentially for Wasting. Rotated Active Sludge Thickening Tank. WAS Valve #1 Manual Closed, WAS Valve #2 Manual Open. Topped Up Soda Ash Hopper ?> 8 Bags. Completed Biorem Odour Control Unit Inspection. All Equipment Operational, All Parameters within Optimal Rates. Recirculation Water pH Analysis: 2.21, Will Continue to Monitor. No New Issues Found. Wasting Complete, Reset Batch Wasting Set-point. RAS Pumps #2 and 4 Running in Auto. Wasted 13 m3 from Each Clarifier. | Kleinburg Water Resource Recovery Facility | 2026-02-12
WW-WEST | February | Onsite to complete scheduled PMs Exercised RAS and WAS valves. All okay other than seized valves flagged as a known issue. Inspected WAS and RAS check valves - all okay. No backflow or leaking detectable. Inspected RAS pumps 1-4. All oil levels good, couplings good. No leaking detectable. Greased fittings. Inspected WAS pumps 1 and 2. Oil levels good. Couplings good. No leaking detectable. Greased fittings. Tested sump pit in RAS/WAS building basement. Both pumps work operationally. | Kleinburg Water Resource Recovery Facility | 2026-02-18
WW-WEST | February | Onsite for consolidated headworks work order Greased vortex 1 and 2 while running. Placed both vortex 1 and 2 into off and E stop. Check oil levels - both good. Cleaned rags from blades of both vortex 1 and 2. Both operate normally. Greased traveling bar screen while in operation. Then placed in off and E stop. Placed auger into off and E stop. Checked oil levels in both gear boxes - both ok. Cleaned rags from bar screen and flushed auger. Placed back into operation Greased grit declassify screw and checked oil levels - oil levels ok. | Kleinburg Water Resource Recovery Facility | 2026-02-12
WW-WEST | February | Harie Rajamithiran(OIT) working under the direction of Marcus Remonde(OIC). -Assisted Marcus Remonde with work orders | Kleinburg Water Resource Recovery Facility | 2026-02-18
WW-WEST | February | In to Complete Scheduled WOs. Notified ROC. Enabled Batch Waste Set-point. RAS Pumps Auto Off in Preparation for Wasting @ 8:25. Lowered Sludge Thickening Tank #2 Decant Slip Tube. Reject Sump Pump #1 Fault Alarm Outstanding. Reset Fault and Cleared Alarm. Returned Pump to Service. Known Issue, WO Made and Pending for Maintenance. Topped Up Soda Ash Hopper ?> 14 Bags. WAS Pump #1 and 2 Manual On and Off Intermittently and Sequentially for Wasting. Rotated RAS Pump Duties. Pumps #2 and 4 Manual Off, Pumps #1 and 3 in Auto. Decant Complete, Raised Decant Slip Tube. Sludge Thickening Tank #2 Outlet Valve Manual Open, Transferred Thickened Sludge. Outlet Valve Returned to Manual Closed. Completed Biorem Odour Control Unit Inspection. All Equipment Operational, All Parameters within Optimal Rates. Recirculation Water pH Analysis: 2.43. No New Issues Found. Wasting Complete, Reset Batch Wasting Set-point. RAS Pumps #1 and 3 Running in Auto. Wasted 15 m3 from Each Clarifier. Received Alum Delivery. Reviewed and Signed Documentation. Alum Tank Level: 0.95 ?> 3.58m. Alum Tank Hi and HiHi Alarms Remain Outstanding Until Tank is Gradually Drawn Down. | Kleinburg Water Resource Recovery Facility | 2026-02-17
WW-WEST | February | In to Complete Scheduled WOs. Enabled Batch Waste Set-point. RAS Pumps Auto Off in Preparation for Wasting @ 8:25. Lowered Sludge Thickening Tank #1 Decant Slip Tube. Decant Complete, Raised Decant Slip Tube. Sludge Thickening Tank #1 Outlet Valve Manual Open, Transferred Thickened Sludge. Outlet Valve Returned to Manual Closed. | Kleinburg Water Resource Recovery Facility | 2026-02-19
WW-WEST | February | On site to replace fuel temperature sensor Advised ROC of repair Disconnected generator to prevent startup during repair Removed and replaced fuel temperature sensor Cleaned up spilled diesel fuel Operator ran generator to verify no issues running Alarm did not return during generator run. Complete | Kleinburg Water Resource Recovery Facility | 2026-02-13
WW-WEST | February | Added 13 bags of soda ash to the hopper Batch wasting 12m3 from each clarifier | Kleinburg Water Resource Recovery Facility | 2026-02-22
WW-WEST | February | Remotely Enabled Batch Waste Set-point. RAS Pumps Auto Off in Preparation for Wasting @ 9:50. | Kleinburg Water Resource Recovery Facility | 2026-02-12
WW-WEST | February | In to Complete Odour Control Unit Investigation and Scheduled WOs. Odour Control Building Potable Water Supply Restored. Placed Odour Control Unit Make Up Water Solenoid in Local Open. Relieved Air Lock from Recirculation Pump. Restored and Adjusted Recirc. and Blow Down Flows to Optimal Rates. Returned Odour Control Blower, Recirc. Pump and Make Up Water Solenoid to Auto. Cleared Associated Alarm. Adjusted Odour Control Building Potable Water Supply Line Heat Trace Temp. Set-point: 21 ?> 15 deg. C. Lowered Sludge Thickening Tank #2 Decant Slip Tube. Enabled Batch Waste Set-point. RAS Pumps Auto Off in Preparation for Wasting @ 9:10. WAS Pump #1 and 2 Manual On and Off Intermittently and Sequentially for Wasting. Wasting Complete, Reset Batch Wasting Set-point. RAS Pumps #2 and 4 Running in Auto. Wasted 12 m3 from Each Clarifier. Topped Up Soda Ash Hopper ?> 8 Bags. Decant Complete, Raised Decant Slip Tube. Sludge Thickening Tank #2 Outlet Valve Manual Open, Transferred Thickened Sludge. Outlet Valve Returned to Manual Closed. Completed Biorem Odour Control Unit Inspection. All Equipment Operational, All Parameters within Optimal Rates. Recirculation Water pH Analysis: 2.36, Will Continue to Monitor. No New Issues Found. | Kleinburg Water Resource Recovery Facility | 2026-02-10
WW-WEST | February | In to Complete Reg. Sampling and Scheduled WOs. Notified ROC. Enabled Batch Waste Set-point. RAS Pumps Auto Off in Preparation for Wasting @ 8:20. WAS Pump #1 and 2 Manual On and Off Intermittently and Sequentially for Wasting. Topped Up Soda Ash Hopper ?> 8 Bags. Wasting Complete, Reset Batch Wasting Set-point. RAS Pumps #2 and 4 Running in Auto. Wasted 17 m3 from Each Clarifier. Completed Biorem Odour Control Unit Inspection. All Equipment Operational, All Parameters within Optimal Rates. Recirculation Water pH Analysis: 2.22, Will Continue to Monitor. No New Issues Found. Completed Aer. DO Sensor Maintenance. Placed Probes in Calibration Mode. Cleaned and Inspected Units, No Issues Found. Returned to Service. Cleared Associated Alarms. Completed Clarifier Maintenance. Drive Chains OK, Topped Up Oil Reservoirs and Greased Bearings. Flushed Sprockets and Chains. Tested Shear Pin and Chain Drive Alarms, Confirmed Reception by the ROC. Returned to Service, Cleared Associated Alarms. | Kleinburg Water Resource Recovery Facility | 2026-02-11
WW-WEST | February | In to Complete Reg. Sampling and Scheduled WOs. Enabled Batch Waste Set-point. RAS Pumps Auto Off in Preparation for Wasting @ 8:25. Topped Up Soda Ash Hopper ?> 8 Bags. WAS Pump #1 and 2 Manual On and Off Intermittently and Sequentially for Wasting. Wasting Complete, Reset Batch Wasting Set-point. RAS Pumps #1 and 3 Running in Auto. Wasted 10 m3 from Clarifier #1 and 12 m3 from Clarifier #2. Inspected and Tested Filters in Local. Flushed Reject Wash Boxes, Weirs and Air Lifts with No Issues. Returned to Service, Cleared Associated Alarms. Drained Aer. Tank Diffuser Line Condensation with No Issues. Completed Aer. DO Sensor Maintenance. Placed Probes in Calibration Mode. Cleaned and Inspected Units, No Issues Found. Returned to Service. Cleared Associated Alarms. | Kleinburg Water Resource Recovery Facility | 2026-02-18
WW-WEST | February | Onsite for work orders. Called ROC to notify of hi level alarms being triggered. Inspected headworks sump pit - triggered hi level alarm and tested pumps - pumps functional. Reset alarm. Inspected tertiary building sump pit - triggered hi level alarm and tested pumps - both pumps functional. Reset alarms Inspected raw sewage sampler and effluent sampler - both operating and lines clear. Inspected headworks building heat trace with Marcus | Kleinburg Water Resource Recovery Facility | 2026-02-10
WW-WEST | February | Completed daily lab annd station check - no new issues. added data into SharePoint. Manually wasted 10m3 from tank 1 and 12m3 from tank 2. Reset batch wasting mode when wasting completed. Inspected UV units - no new issues. Added 7 bags of soda ash to soda hopper Cleaned rags from bar screen and confirmed operation. Completed comprehensive housecleaning of tertiary building. | Kleinburg Water Resource Recovery Facility | 2026-02-19
WW-WEST | February | Onsite for consolidated blower inspection work order. Notified ROC of work being done. Placed sludge holding tank blower 1 in manual off and LOTO generating E stop alarms - checked belts, filter and oil levels all ok. Placed back into auto and swapped duties to place sludge blower 2 into manual and LOTO generating e stop alarm. checked belts, filter and oil levels all ok. Placed back into auto. Both blowers operating normally. Place vortex blower 1 into off and checked belts, filter and oil levels. All ok. Placed back into auto Placed vortex blower 2 into off and checked belts, filter and oil level. All ok placed back in auto. Both blowers operating normally. Placed diversion tank blowers 1 and 2 into local off generating E stop alarms checked belts, filters and oil levels. All ok. Placed aeration tank blower 2 into off manual and LOTO generating e stop alarms. Checked belts, filter and oil levels all ok. Placed back into auto and rotated duties to place aerating tank blower 1 into manual off and LOTO generating e stop alarms. Checked belts, filter and oil level - all ok. Placed back into auto. Manually exercised aeration tank butterfly valves. Assisted Marcus with clarifier inspection WO | Kleinburg Water Resource Recovery Facility | 2026-02-11
WW-WEST | February | In to Complete Scheduled WOs. Notified ROC. Enabled Batch Waste Set-point. RAS Pumps Auto Off in Preparation for Wasting @ 8:35. Lowered Sludge Thickening Tank #1 Decant Slip Tube. WAS Pump #1 and 2 Manual On and Off Intermittently and Sequentially for Wasting. Decant Complete, Raised Decant Slip Tube. Sludge Thickening Tank #1 Outlet Valve Manual Open, Transferred Thickened Sludge. Outlet Valve Returned to Manual Closed. Completed Biorem Odour Control Unit Inspection. All Equipment Operational, All Parameters within Optimal Rates. Recirculation Water pH Analysis: 2.38, Will Continue to Monitor. No New Issues Found. Topped Up Soda Ash Hopper ?> 7 Bags. Placed Generator #2 in Manual On for Replacement Fuel Sensor Testing with No Issues. Returned to Auto and Service. Cleared Associated Alarms. Wasting Complete, Reset Batch Wasting Set-point. RAS Pumps #2 and 4 Running in Auto. Wasted 12 m3 from Clarifier #1 and 13 m3 from Clarifier #2. Placed Soda Ash Dispenser in Local Off. Replaced Disch. Ducting and Tested Unit in Local with No Issues. Returned to Service. Activated Scum Pump #1 in Manual for Scum Tank Drawdown. Drawdown Complete, Returned Pump to Auto and Service. Flushed Bar-screen Dewatering Press Drainage Line with No Issues. Returned to Service. Inspected Filters and Compressors. Flushed Reject Wash Boxes, Weirs and Air Lifts. Tested Compressor Condensation Flushing Solenoids with No Issues. Completed Raw Sewage HWs (Distribution Chamber) Blower #1 and 2 Inspections. Oil Levels, Belts and Air Filters OK. Returned to Service. | Kleinburg Water Resource Recovery Facility | 2026-02-13
WW-WEST | February | Onsite for work orders. Pumped down scum tank and cleaned. Opened WAS_MV4 valve to sludge tank to clear interlock for circular plant WAS inspection - inspected WAS pumps 3 and 4. Oil levels ok. Ran in local to confirm flow and operation. Both pumps ok. returned WAS_MV4 to close. Inspected circular plant RAS pumps 1 and 2. Oil levels good. Ran both pumps in hand to confirm flow and operation. Due to discoloured oil during clarifier inspection done previously on clarifier 2 drive box completed an oil change and tried to flush bad oil. Created follow up Workorder W11670806. Inspected odour control unit - no new issues. Completed inspection sheet. | Kleinburg Water Resource Recovery Facility | 2026-02-17
WW-WEST | February | Remotely enabled batch wasting mode at 1:40pm and set WAS to auto waste 30m3 from 3pm to 5pm. Upon completion of wasting at 5pm placed WAS pumps back into manual and reset RAS Aeration tank blower 2 speed deviation alarm present - trends for blower 2 look normal and cannot find issue with blower 2. cleared alarm. Will continue to monitor. Onsite at 3pm added 16 bags of soda ash to hopper | Kleinburg Water Resource Recovery Facility | 2026-02-15
WW-WEST | February | In to Complete Scheduled WOs. Notified ROC. Enabled Batch Waste Set-point. RAS Pumps Auto Off in Preparation for Wasting @ 8:40. Lowered Sludge Thickening Tank #2 Decant Slip Tube. WAS Pump #1 and 2 Manual On and Off Intermittently and Sequentially for Wasting. Decant Complete, Raised Decant Slip Tube. Sludge Thickening Tank #2 Outlet Valve Manual Open, Transferred Thickened Sludge. Outlet Valve Returned to Manual Closed. Topped Up Soda Ash Hopper ?> 8 Bags. Flushed FE Composite Sampler Suction Line and Returned to Service. Wasting Complete, Reset Batch Wasting Set-point. RAS Pumps #1 and 3 Running in Auto. Wasted 10 m3 from Clarifier #1 and 15 m3 Clarifier #2. Hosed and Flushed Alum Accretion from Filter Inlet Channel Mixer Drive Shaft. Verified Alum Dosage Point. Completed Scum Tank #3 Valve and Actuator Exercises and Inspections. Activated Units in Local Several Cycles with No Issues. Returned to Service. Completed Aer. Blower #1 Inspection. Filter and Belts OK. Topped Up Oil Reservoir. No Other Issues Found. Returned to Service. Cleared Associated Alarms. | Kleinburg Water Resource Recovery Facility | 2026-02-05
WW-WEST | February | In to Complete Reg. Sampling and Scheduled WOs. Notified ROC. Enabled Batch Waste Set-point. RAS Pumps Auto Off in Preparation for Wasting @ 10:15. WAS Pump #1 and 2 Manual On and Off Intermittently and Sequentially for Wasting. Rotated Active Sludge Thickening Tank. WAS Valve #2 Manual Closed, WAS Valve #1 Manual Open. Wasting Complete, Reset Batch Wasting Set-point. RAS Pumps #1 and 3 Running in Auto. Wasted 11 m3 from Clarifier #1 and 12 m3 from Clarifier #2. Topped Up Soda Ash Hopper ?> 9 Bags. Flushed Bar-screen Dewatering Press Drainage Line with No Issues. Returned to Service. Completed Aer. DO Sensor Maintenance. Placed Probes in Calibration Mode. Cleaned and Inspected Units, No Issues Found. Returned to Service. Cleared Associated Alarms. | Kleinburg Water Resource Recovery Facility | 2026-02-04
WW-WEST | February | In to Complete Scheduled WOs. Enabled Batch Waste Set-point. RAS Pumps Auto Off in Preparation for Wasting @ 9:00. WAS Pump #1 and 2 Manual On and Off Intermittently and Sequentially for Wasting. Wasting Complete, Reset Batch Wasting Set-point. RAS Pumps #1 and 3 Running in Auto. Wasted 12 m3 from Clarifier #1 and 15 m3 Clarifier #2. Topped Up Soda Ash Hopper ?> 9 Bags. Inspected Filters and Compressors. Flushed Reject Wash Boxes, Weirs and Air Lifts. Tested Compressor Condensation Flushing Solenoids with No Issues. Completed Circular Plant Clarifier and Drive Inspection. Did Not Test Run Unit due to Ice within Clarifier. No Issues Found. Unit Remains OOS. | Kleinburg Water Resource Recovery Facility | 2026-02-06
WW-WEST | February | Remotely Enabled Batch Waste Set-point. RAS Pumps Auto Off in Preparation for Wasting @ 08:45. | Kleinburg Water Resource Recovery Facility | 2026-02-03
WW-WEST | February | In to Complete Scheduled WOs. Enabled Batch Waste Set-point. RAS Pumps Auto Off in Preparation for Wasting @ 8:35. Lowered Sludge Thickening Tank #1 Decant Slip Tube. WAS Pump #1 and 2 Manual On and Off Intermittently and Sequentially for Wasting. Decant Complete, Raised Decant Slip Tube. Sludge Thickening Tank #1 Outlet Valve Manual Open, Transferred Thickened Sludge. Outlet Valve Returned to Manual Closed. Wasting Complete, Reset Batch Wasting Set-point. RAS Pumps #2 and 4 Running in Auto. Wasted 10 m3 from Clarifier #1 and 18 m3 from Clarifier #2. Rotated Active Sludge Thickening Tank. WAS Valve #2 Manual Closed, WAS Valve #1 Manual Open. Topped Up Soda Ash Hopper ?> 8 Bags. Placed Clarifier Helical Skimmers in Manual On for Scum Tank Flushing. Hosed and Flushed Tank. Returned to Auto and Service. Placed Scum Pump #1 in Manual On for Scum Tank Drawdown. Drawdown Complete Returned to Auto and Service. Completed Aer. Tank Outlet Channel Cleaning and Drained Diffuser Line Condensation with No Issues. | Kleinburg Water Resource Recovery Facility | 2026-02-09
WW-WEST | February | Remotely Enabled Batch Waste Set-point. RAS Pumps Auto Off in Preparation for Wasting @ 9:10. | Kleinburg Water Resource Recovery Facility | 2026-02-08
WW-WEST | February | In to Complete Scheduled WOs. WAS Pump #1 and 2 Manual On and Off Intermittently and Sequentially for Wasting. Topped Up Soda Ash Hopper ?> 14 Bags. Wasting Complete, Reset Batch Wasting Set-point. Rotated RAS Pump Duties. Pumps #1 and 3 Manual Off, Pumps #2 and 4 Running in Auto. Wasted 12 m3 from Each Clarifier. | Kleinburg Water Resource Recovery Facility | 2026-02-08
WW-WEST | February | In to Complete Scheduled WOs. Topped Up Soda Ash Hopper ?> 8 Bags. WAS Pump #1 and 2 Manual On and Off Intermittently and Sequentially for Wasting. Wasting Complete, Reset Batch Wasting Set-point. RAS Pumps #1 and 3 Running in Auto. Wasted 12 m3 from Each Clarifier. Completed Biorem Odour Control Unit Inspection. Greased Driveshaft Bearings. No Other Issues Found. Returned to Service. | Kleinburg Water Resource Recovery Facility | 2026-02-03
WW-WEST | February | In Responding to Biorem Odour Control System Recirculation Lo Flow Alarm Communicated by the ROC. Odour Control Unit Make Up Water Line Exhibiting No Pressure. Tested Solenoid, No Flow Observed. Placed Odour Control Recirculation Pump and Blower in Local On, Recirc. Flow @ Approx. 8 L/min, Relieved Potential Air Lock within Pump. Isolated Blow Down Flow Line for Recirc. Water Conservancy. Odour Control Building Not Receiving Potable Water, Confirmed with Eye Wash and Sink Taps. Reviewed Kleinburg Potable Water Distribution and Supply System via SCADA, No Issues Found. Confirmed Potable Water Flow at Admin. and HWs Buildings. Inspected Odour Control Building Potable Water Supply Line and Heat Trace for Potential Freezing Issues. Heat Trace Unit Functioning at 4 deg. C, Increased Heat Trace Set-point to 21 deg. C and Monitored. Reviewed ECA Documentation, Odour Control Unit Remains Functional Until Make Up Water Line Flow Restored. | Kleinburg Water Resource Recovery Facility | 2026-02-09
WW-WEST | February | Harie Rajamithiran(OIT) working under the direction of Daniel Hirstwood(OIC). -Completed station check , no issues found -Rotated pump 2 to OOS-Duty 4 and put pump 1 in duty 2 | King City Pumping Station | 2026-02-24
WW-WEST | February | On arrival note a diesel generator run has occurred for 2.1hrs beginning at approx 01:04am today. Station checks, SharePoint readings and review of continuous monitoring data. Check inlet screen room equipment. Cycle in manual and clean floors/ flush drains. Flush water was still on from last station check. Various stakeholders onsite for a feasibility study. Pump testing for study completed and all controls returned to normal operation. ROC notified. | King City Pumping Station | 2026-02-27
WW-WEST | February | - Pushed bin back in - Cleaned screen area and checked oil level, all okay. Flushed drain line - Checked station and recorded readings on SharePoint. No new issues. Checked trends | King City Pumping Station | 2026-02-20
WW-WEST | February | Onsite for station check. No new issues. Reviewed trends and added data into SharePoint. | King City Pumping Station | 2026-02-13
WW-WEST | February | Onsite for station check - no new issues. Reviewed trends and added data into SharePoint. Rotated manual OOS pump from pump 2 to pump 3. Bar screen flushed and functioning normally. | King City Pumping Station | 2026-02-17
WW-WEST | February | Placed the rag bin outside for pick up | King City Pumping Station | 2026-02-19
WW-WEST | February | Checked station and recorded readings on SharePoint. No new issues Exercised valves Inspected screen and flushed drain lines. Greased fittings. Oil is all good | King City Pumping Station | 2026-02-10
WW-WEST | February | Onsite for work orders. Called ROC to inform of generator run test, and alarms being tested. Transferred power from hydro to generator at 9:07am. Recorded data to SharePoint. Transferred power from generator back to hydro at 10:15am. Transferred smoothly. Maintenance onsite for RS pump inspection PMs Completed dry well inspection - all pumps run ok, check valves operating properly Triggered hi-Lo temp alarm. Triggered dry well flood alarm and tested dry well sump pit. Triggered diesel containment flood alarm. Completed JHSC inspection and checked plant for hazardous waste. Flushed and checked bar screen - no issues. Bin placed out for pick up | King City Pumping Station | 2026-02-05
WW-WEST | February | Onsite for station check - no new issues reviewed trends and added data into SharePoint | King City Pumping Station | 2026-02-06
WW-WEST | February | Onsite with Young Jung for consolidated wetwell work order. Notified ROC of work being done. Cleaned and inspected bar screen - greased bar screen and flushed. Triggered wetwell overflow alarms. Exercised wetwell valves Cleaned debris from wetwell. | King City Pumping Station | 2026-02-04
WW-WEST | February | Completed pump PM?s Added 50 grams of Kluber grease to bearings while pumps running Checked coolant levels. All good Checked leakage chambers. Some minimal leakage at pumps 2 and 3. Not enough to collect. Complete. | King City Pumping Station | 2026-02-05
WW-WEST | February | Checked station and trends, and recorded readings on SharePoint. No new issues Performed OOS pump duty rotation | King City Pumping Station | 2026-02-03
WW-WEST | February | Completed barscreen PM Lubricated sprocket, bushings and all bearings Set chain oiler delivery rate Checked gear box oil levels good. | King City Pumping Station | 2026-02-05
WW-WEST | February | Completed the station check Entered data into SharePoint Everything operating as intended | Nobleton Janet St. Sewage Pumping Station | 2026-02-24
WW-WEST | February | Harie Rajamithiran(OIT) working under the direction of Daniel Hirstwood(OIC). -Dropped off Kleinburg sewage plant weekly compliance samples | Nobleton Janet St. Sewage Pumping Station | 2026-02-25
WW-WEST | February | Harie Rajamithiran(OIT) working under the direction of Daniel Hirstwood(OIC). -Completed comprehensive housekeeping -Completed station check , no issues found | Nobleton Janet St. Sewage Pumping Station | 2026-02-27
WW-WEST | February | Collected weekly compliance samples | Nobleton Janet St. Sewage Pumping Station | 2026-02-25
WW-WEST | February | On site for Capital Sewer to CCTV the sewer from Janet SPS to King Rd. Change Duty 1 start point to 1.1m (from 1.40m) to keep liquid level lower in the inlet sewer. Camera crew was unable to get camera through the grease near the beginning of the sewer from the access hole. They are repositioning to enter from king rd and camera back towards site. Return duty 1 set point to normal 1.4m start point. | Nobleton Janet St. Sewage Pumping Station | 2026-02-26
WW-WEST | February | Collected weekly samples | Nobleton Janet St. Sewage Pumping Station | 2026-02-18
WW-WEST | February | Onsite to troubleshoot erratic diesel LIT reading Informed ROC Found that diesel LIT reading is noisy when RSP#3 is running. RSP#3 VFD speed feedback is connected on same analog input module as diesel LIT, just one channel before. Suspect some type of electrical interference between the two signals. Moved diesel analog signal (I10905) to same analog input channel number but on the next slot (I11005). Asked PCS to make the necessary changes in the PAC program. Monitored for a while. Seems better but will need to verify over the next couple of days Made note on PAC drawings indicating the change Informed ROC, armed building and left site | Nobleton Janet St. Sewage Pumping Station | 2026-02-23
WW-WEST | February | Completed the station check Entered data into SharePoint Everything operating as intended | Nobleton Janet St. Sewage Pumping Station | 2026-02-20
WW-WEST | February | Onsite to check plant for hazardous materials - none found. | Nobleton Janet St. Sewage Pumping Station | 2026-02-13
WW-WEST | February | Collected the weekly sewage sample | Nobleton Janet St. Sewage Pumping Station | 2026-02-11
WW-WEST | February | Harie Rajamithiran(OIT) working under the direction of Daniel Hirstwood(OIC). -Completed station check , no issues found. | Nobleton Janet St. Sewage Pumping Station | 2026-02-13
WW-WEST | February | Harie Rajamithiran(OIT) working under the direction of Lance Johnson(OIC). -Completed station check , no issues found. | Nobleton Janet St. Sewage Pumping Station | 2026-02-17
WW-WEST | February | Complete vibration readings on pumps. Rotated duty to collect all readings. | Nobleton Janet St. Sewage Pumping Station | 2026-02-13
WW-WEST | February | Completed the station check Entered data into SharePoint Test ran the generator Completed the jhsc inspection | Nobleton Janet St. Sewage Pumping Station | 2026-02-10
WW-WEST | February | On site to collect monthly and weekly YDSS raw sewage samples. Review of local continuous monitoring data and station walk through. | Nobleton Janet St. Sewage Pumping Station | 2026-02-04
WW-WEST | February | Completed the station check Entered data into SharePoint Inspected the sampler Everything operating as intended | Nobleton Janet St. Sewage Pumping Station | 2026-02-06
WW-WEST | February | Attending site to replace failing diesel tank level transmitter (W11475801). Replace, configured and verified diesel tank level. ROC was notified before and after maintenance activities. | Nobleton Janet St. Sewage Pumping Station | 2026-02-06
WW-WEST | February | Checked station and trends, and recorded readings on SharePoint. No new issuds | Vaughan Pine Valley Pumping Station | 2026-02-27
WW-WEST | February | Harie Rajamithiran(OIT) working under the direction of Gavin Walker(OIC). -Completed consolidated dry well & hoist system inspection, no issues found -Tested dry well flood alarm, autodialer alarm and Hi/Low temp alarm and confirmed that roc received them -Completed station check, no issues found -Completed manual valve exercise, no issues found | Nobleton Janet St. Sewage Pumping Station | 2026-02-03
WW-WEST | February | Onsite for station check No new issues. Reviewed trends and added data to SharePoint. Odour control unit ok. Completed comprehensive housekeeping work order - swept main floor and cleaned bathroom. | Vaughan Pine Valley Pumping Station | 2026-02-24
WW-WEST | February | Onsite for station check - no new issues. Reviewed trends and entered data into SharePoint. | Vaughan Pine Valley Pumping Station | 2026-02-13
WW-WEST | February | Checked station and trends, and recorded readings on SharePoint. No new issues | Vaughan Pine Valley Pumping Station | 2026-02-10
WW-WEST | February | Onsite for station check - no new issues. Reviewed trends and entered data into SharePoint. | Vaughan Pine Valley Pumping Station | 2026-02-20
WW-WEST | February | Completed the station check Entered data into SharePoint Everything operating as intended | Vaughan Pine Valley Pumping Station | 2026-02-17
WW-WEST | February | Checked station and trends, and recorded readings on SharePoint. All okay Update: exercised valves | Vaughan Pine Valley Pumping Station | 2026-02-06
WW-WEST | February | Attending site to check H2S gas detector fault (W11565040). Found sensor has failed. Replaced failed sensor. ROC was notified before and after maintenance activities. | Vaughan Pine Valley Pumping Station | 2026-02-03
WW-WEST | February | Onsite for station check and work orders. Called ROC to inform of generator run test Completed station check - no new issues reviewed trends and added data into SharePoint. Transferred power from hydro to generator at 12:28pm. Transferred power back to at 1:30pm. Transferred no issues. Completed consolidated dry well inspection - all ok. Tested sump pit floats and dry well flood alarm - triggered alarm Tested hi Lo temperature alarms. Inspected odour control unit - no new issues. At 0.4inches of water. Completed JHSC inspection and checked station for hazardous waste | Vaughan Pine Valley Pumping Station | 2026-02-03
WW-WEST | February | Onsite for scheduled PMs Inspected UVs. Bank A working normally. Bank B has rack 7 not working. Work order has been made for the issue. Completed comprehensive housekeeping WO for process building. | Schomberg Water Resource Recovery Facility | 2026-02-23
WW-WEST | February | Decanted sludge thickening tank and transferred remaining sludge to holding tank. Decanted pump turned off and transfer valve closed upon completion. Completed daily lab and station check - no new issues added data into SharePoint. Cleaned aeration TSS probe. | Schomberg Water Resource Recovery Facility | 2026-02-27
WW-WEST | February | Supernated STT and released to SHT. Completed labs and entered data in ace sheets. Completed station check. UV bank b, rack 7 not lighting up and causing alarm. Problem with power at the socket for rack 7. Created W11693400. Cleaned blower building. Cleaned UV/FE channel. | Schomberg Water Resource Recovery Facility | 2026-02-23
WW-WEST | February | Reset the clarifier and uv system which faulted due to a power blip | Schomberg Water Resource Recovery Facility | 2026-02-23
WW-WEST | February | Completed labs and entered data in ace sheet. Verified and cleaned DO probes. | Schomberg Water Resource Recovery Facility | 2026-02-25
WW-WEST | February | Decanted sludge thickening tank and transferred remaining sludge to holding - decanted pump returned to off and transfer valve closed upon transfer completion. Completed daily labs and station check - added data into SharePoint. No new issues found. Inspected headworks heat trace - no issues. | Schomberg Water Resource Recovery Facility | 2026-02-26
WW-WEST | February | Completed labs and entered data in ace sheets. Completed station check. No issues found. Completed clarifier housekeeping. Also worked on blower building housekeeping. | Schomberg Water Resource Recovery Facility | 2026-02-24
WW-WEST | February | Supernated STT and released to SHT. Started in-house labs. Collected weekly compliance samples. Completed station check. No issues found. | Schomberg Water Resource Recovery Facility | 2026-02-25
WW-WEST | February | Onsite to commission the new pressure switches for the air compressors, compressor needed to be turned off. After multiple attempts the pressure switches are not functioning properly and were not commissioned. Air compressors will still run in auto but can?t be operate locally | Schomberg Water Resource Recovery Facility | 2026-02-18
WW-WEST | February | Completed the station check and daily lab work Entered data into SharePoint Decanted then emptied the sludge thickening tank Inspected the filter compressors Leaving effluent pump 3 in manual off as the vfd is still having issues | Schomberg Water Resource Recovery Facility | 2026-02-02
WW-WEST | February | On site to continue work on effluent pump 3. Effluent pump 3 is still out of service. | Schomberg Water Resource Recovery Facility | 2026-02-02
WW-WEST | February | Supernated STT and released to SHT. Completed labs and entered data in ACE sheets. Completed station check. No issues found. Cleaned TSS probe. Cleaned raw composite sampler jug without any chemical cleaners. | Schomberg Water Resource Recovery Facility | 2026-02-13
WW-WEST | February | Completed daily operations. | Schomberg Water Resource Recovery Facility | 2026-02-10
WW-WEST | February | Completed labs and entered data in ace sheets. Competed station check. No issues found. Inspected PB sump system. ROC received alarm. Inspected BB sump system. ROC received alarm. | Schomberg Water Resource Recovery Facility | 2026-02-12
WW-WEST | February | Completed labs and entered data in ace sheets. Inspected DO probes and verified readings. | Schomberg Water Resource Recovery Facility | 2026-02-11
WW-WEST | February | Maintained DO probes. Inspected filter reject pumps. ROC received alarm. Assisted air compressor contractors. | Schomberg Water Resource Recovery Facility | 2026-02-17
WW-WEST | February | Started labs. | Schomberg Water Resource Recovery Facility | 2026-02-12
WW-WEST | February | Completed labs and entered data in ace sheets. Completed station check. Noted leaks in roof of blower room. Reported to supervior who created work order for property services. Inspected RAS pumps 1, 2 and 3. Inspected WAS pumps 1 and 2. Inspected scum pumps 1 and 2. No issues found with any of these pumps. Ras/was basement floor wet from housekeeping. | Schomberg Water Resource Recovery Facility | 2026-02-19
WW-WEST | February | Completed labs and entered data in ace sheets. Cleaned TSS probe. Assisted contractors with air compressors. Released STT from 3.75m to 2.81m to SHT. | Schomberg Water Resource Recovery Facility | 2026-02-18
WW-WEST | February | Completed labs and entered data in ace sheets. Completed station check. No issues found. Reset alarms and duties after power blip. | Schomberg Water Resource Recovery Facility | 2026-02-10
WW-WEST | February | Supernated STT and released to SHT. Completed labs and entered data in ace sheets. Completed station check. No issues found. Assisted contractors working on new air compressors. | Schomberg Water Resource Recovery Facility | 2026-02-17
WW-WEST | February | Collected weekly compliance samples. Started labs. Completed station check. No issues found. | Schomberg Water Resource Recovery Facility | 2026-02-18
WW-WEST | February | Collected weekly compliance samples. Supernated STT and released to SHT. Completed station check. No issues found. Started labs. | Schomberg Water Resource Recovery Facility | 2026-02-11
WW-WEST | February | Supernated STT and released to SHT. Completed labs and entered data in ace sheets. Completed station check. No issues found. Completed housekeeping around ras/was pumps. Floor wet as a result. | Schomberg Water Resource Recovery Facility | 2026-02-20
WW-WEST | February | Completed labs and entered data in ACE sheets. Completed station check - no issues found. Checked for hazardous waste - none found at this time. Test ran diesel generator. Start hours: 551.9, fuel level: 0.74m. Stop hours: 553.0, fuel level: 0.73m. Completed JHSC inspection - no health or safety issues found. | Schomberg Water Resource Recovery Facility | 2026-02-03
WW-WEST | February | Supernated STT and released to SHT. Completed labs and entered date in ace sheet. Completed station check. No issues found. Cleaned TSS probe. | Schomberg Water Resource Recovery Facility | 2026-02-06
WW-WEST | February | Collected weekly and monthly compliance samples. Supernated STT. Completed labs and entered data in ACE sheet. Completed station check. Cleaned and verified DO probes. Released STT to SHT. | Schomberg Water Resource Recovery Facility | 2026-02-04
WW-WEST | February | In Responding to Filter Room Smoke Alarm Communicated by the ROC. No Signs of Fire Evident. Ventilated Filter Room, Cleaned and Inspected Smoke Detector. Returned to Service. Alarm Acknowledged and Reset. | Schomberg Water Resource Recovery Facility | 2026-02-05
WW-WEST | February | Completed station check. No issues found. | Schomberg Dr. Kay Pumping Station | 2026-02-24
WW-WEST | February | Installed stop logs in headworks to divert all incoming flow to lagoon at 7:54 am. Ran effluent pumps manually to pump out effluent tank. Shut off plant service water system. Shut off filter reject pumps. Shut off plant sewer pumps. Shut off filter sump pumps. Pumped uv/effluent channel in to lagoon overflow. Shut off UV banks. Completed station check. No issues found. Completed labs and entered data in ace sheets. Completed consolidated blower inspection work order. Added oil to aeration blower 1. Otherwise, all good. GFL entered effluent tank to suck out sludge and pressure wash walls. GFL sprayed walls down with sodium hypochlorite. 11:08 turned UV banks back to auto/on. Removed stop logs from headworks to return flow to plant. Set filter sump pumps to auto. Set filter reject pumps to auto. Set plant sewer pumps in auto. Set plant service water system to auto. Effluent tank full and overflowing to lagoon at 13:23. Added dechlorination pucks to effluent tank at 13:23. Turned effluent pumps to auto at 14:43. Tested effluent pumps. All three make appropriate flow. Reset duties for filter reject and effluent pumps. Reset all alarms. Plant back to normal, but with clean effluent tank. | Schomberg Water Resource Recovery Facility | 2026-02-05
WW-WEST | February | Supernated STT and released to SHT. Completed labs and entered data in ACE sheets. Completed station check. No issues found. Exercised SHT overflow valve. Test SHT high level float. ROC received alarm. Completed consolidated headworks work order. ROC received alarms. | Schomberg Water Resource Recovery Facility | 2026-02-09
WW-WEST | February | Onsite for station check - no new issues. Reviewed trends and added data into SharePoint. Completed comprehensive housecleaning of building. | Schomberg Dr. Kay Pumping Station | 2026-02-27
WW-WEST | February | Completed station check. No issues found. | Schomberg Dr. Kay Pumping Station | 2026-02-20
WW-WEST | February | On site to pull pump 1 de- raged pump and adjusted wear ring and ran pump running at 30l/s again put back in auto and informed oic to view in scada | Schomberg Dr. Kay Pumping Station | 2026-02-13
WW-WEST | February | Reset pump 1 VFD after power blip. Test ran diesel generator. Start hours: 558.6, fuel level: 3/4 full. Stop hours: 559.8, fuel level: 3/4 full. Tested high and low temperature alarms. ROC received both alarms. Completed station check. No new issues found. Pump 1 still waiting for cleaning. Completed JHSC inspection. No issues found. No hazardous waste found either. | Schomberg Dr. Kay Pumping Station | 2026-02-10
WW-WEST | February | Completed station check. No issues found. | Schomberg Dr. Kay Pumping Station | 2026-02-17
WW-WEST | February | Completed station check. No issues found. Pump 1 now functioning satisfactorily. | Schomberg Dr. Kay Pumping Station | 2026-02-13
WW-WEST | February | Completed station check. Pump 1 showing signs of ragging. Work order created. No other issues. | Schomberg Dr. Kay Pumping Station | 2026-02-06
WW-WEST | February | Remotely Placed Pump #1 in Manual Speed @ 100% for Pump Flushing. Manually Rotated Pump #1 into Duty #1 for Several Cycles. Pump Flushing Complete. Remotely Returned Pump #1 to Auto Speed. | Schomberg Dr. Kay Pumping Station | 2026-02-05
WW-WEST | February | Completed station check. No issues found. | Schomberg Dr. Kay Pumping Station | 2026-02-03
WW-WEST | February | Noted evidence of clogging on pump 1. Set pump 1 to duty 1, manual 100% speed from 10:30 to 14:50. Afterwards, returned duty rotate to all stop and pump speeds to auto. | Schomberg Dr. Kay Pumping Station | 2026-02-04
ROC | February | SEOC4- Johnathan from property services is on site to restore hot water | ROC General | 2026-02-26
ROC | February | KSETDP, Junji is leaving site | ROC General | 2026-02-23
ROC | February | AUSS- Teodore from AB on site. | ROC General | 2026-02-27
ROC | February | KBSP - Theodore from ABPMC on site to complete generator exhaust work. Will see associated alarms as they take the generator offline. | ROC General | 2026-02-25
ROC | February | KSSP, Drew from Ferguson Electric is leaving site | ROC General | 2026-02-27
ROC | February | Carter D Signing Out | ROC General | 2026-02-23
ROC | February | KBSP, Theodor from AB is finished on site | ROC General | 2026-02-24
ROC | February | Christian Van Beek signing in. Weather: -8C and clear. | ROC General | 2026-02-26
ROC | February | VNRSKS - Swapped supply pump to one MAPS pump and one VNPS pump. *wrong book* | ROC General | 2026-02-26
ROC | February | QVW12/QVETQS/QVW34/MTSS/MTW12/MTW3/MTETNL/MTSP, PCO Pest control operator will be visiting these sites as follows | ROC General | 2026-02-27
ROC | February | GWTP - Terry G from property services on site to complete a breaker replacement. Operations is aware of this work. | ROC General | 2026-02-26
ROC | February | Ethan Ullalkar signing out. | ROC General | 2026-02-23
ROC | February | KSSSQS, Dimitiri from CPD is leaving site | ROC General | 2026-02-27
ROC | February | KSTP - Phil from ABPMC on site. | ROC General | 2026-02-25
ROC | February | Christian Van Beek signing out. | ROC General | 2026-02-25
ROC | February | Adam Button signing out | ROC General | 2026-02-26
ROC | February | BLETNL - Sean from Town of Stouffville will be flushing in Ballantrae today | ROC General | 2026-02-25
ROC | February | SEOC Shaft 6/7, Jonathon from Property Services is on site 12:11, Jonathon is leaving site | ROC General | 2026-02-26
ROC | February | Ethan U signing in Weather -4. | ROC General | 2026-02-23
ROC | February | Carter D Signing In | ROC General | 2026-02-23
ROC | February | KBSP, Theodor from AB is leaving site | ROC General | 2026-02-23
ROC | February | KSSP, Phil from AB is on site | ROC General | 2026-02-24
ROC | February | Angelica Chepiga signing out | ROC General | 2026-02-27
ROC | February | KSSP- Hamid from ETO is done on site | ROC General | 2026-02-25
ROC | February | Carter D Signing Out | ROC General | 2026-02-24
ROC | February | Carter D Signing Out | ROC General | 2026-02-27
ROC | February | Ethan U signing in Weather: -2c | ROC General | 2026-02-25
ROC | February | Angelica Chepiga signing in | ROC General | 2026-02-27
ROC | February | Adeela Khan signing in. Weather: -5C and Cloudy | ROC General | 2026-02-28
ROC | February | Christian Van Beek signing out. | ROC General | 2026-02-24
ROC | February | Ethan Ullalkar signing out. | ROC General | 2026-02-26
ROC | February | SEOC AHF4 - Jon from property services leaving site. | ROC General | 2026-02-26
ROC | February | KBSP - Theodore onsite for curbing work in generator room. Dust contained but may trigger smoke alarm. Call if smoke alarm is triggered 289-839-0704 | ROC General | 2026-02-23
ROC | February | KBSP - Garrick from Ferguson electric signing in. | ROC General | 2026-02-27
ROC | February | Christian Van Beek signing in. | ROC General | 2026-02-27
ROC | February | Adam Button signing in -3C clear | ROC General | 2026-02-25
ROC | February | SEOC67 - Jonathan from Property services on site. 13:07 Jonathan off site. | ROC General | 2026-02-27
ROC | February | AURSBS - Frank from property services on site. | ROC General | 2026-02-25
ROC | February | KSSP - Theodore from ABPMC on site for continuing curb demolition. Theodore has requested that he be contacted if the smoke detector alarms trigger on site. Dust may trigger the smoke detector | ROC General | 2026-02-24
ROC | February | KSETDP, Khalid from Asset Management is on site | ROC General | 2026-02-27
ROC | February | NBW3- Rashad R from Bosh Paladin Technology leaving site. | ROC General | 2026-02-27
ROC | February | KBSP - Garrick from Ferguson electric signing out. | ROC General | 2026-02-27
ROC | February | Christian Van Beek signing out. | ROC General | 2026-02-27
ROC | February | GWTP, Terry G is leaving site | ROC General | 2026-02-26
ROC | February | Adam Button signing out | ROC General | 2026-02-25
ROC | February | Adeela Khan signing out | ROC General | 2026-02-23
ROC | February | KSSP, Phil from AB is leaving site | ROC General | 2026-02-23
ROC | February | Christian Van Beek signing out. | ROC General | 2026-02-26
ROC | February | Connor Smith signing in -8C cloudy | ROC General | 2026-02-24
ROC | February | VNETAG- Meghal from YRP is on site | ROC General | 2026-02-25
ROC | February | AURSBS - Orlando and Frank from property services leaving site. | ROC General | 2026-02-25
ROC | February | HMSS - Rowan from CPD leaving site. | ROC General | 2026-02-24
ROC | February | Christian Van Beek signing in. | ROC General | 2026-02-25
ROC | February | Angelica Chepiga signing out | ROC General | 2026-02-28
ROC | February | Christian Van Beek signing in. Weather: -16C and clear. | ROC General | 2026-02-24
ROC | February | MKETFA- Johnathan from property services is on site | ROC General | 2026-02-26
ROC | February | KSSP, Ben from Property Services is leaving site | ROC General | 2026-02-26
ROC | February | KSTP, Khalid from Property Services is on site | ROC General | 2026-02-23
ROC | February | Carter D Signing Out | ROC General | 2026-02-26
ROC | February | STPSMR, STW12, STW3, STPSTL, STETBR, BLETNL, AUW14, AUW5, BLW3 - Pest control attending site | ROC General | 2026-02-23
ROC | February | KSSP, Ian W testing a new UV Bypass alarm at KSSP. Please disregard until further notice | ROC General | 2026-02-26
ROC | February | KSSP - Drew from Ferguson done at site | ROC General | 2026-02-23
ROC | February | EGSSSC, Dave W from Property services is on site | ROC General | 2026-02-24
ROC | February | Connor Smith signing out | ROC General | 2026-02-24
ROC | February | KSTP - Garrik from Ferguson Electric leaving site. | ROC General | 2026-02-24
ROC | February | NBW3, Rashad R from Bosh Paladin Technology is on site, doing some test reports | ROC General | 2026-02-27
ROC | February | KSSP, Phil from AB is on site | ROC General | 2026-02-27
ROC | February | Adam Button signing in 5C Sunny | ROC General | 2026-02-27
ROC | February | KSSP, Drew from Ferguson Electric is on site | ROC General | 2026-02-26
ROC | February | KBSP- Garrick from Ferguson electric on site | ROC General | 2026-02-26
ROC | February | Carter Dunn Signing In | ROC General | 2026-02-26
ROC | February | **WRONG BOOK** | ROC General | 2026-02-26
ROC | February | KBSP- Garrick from Ferguson electric leaving site. | ROC General | 2026-02-27
ROC | February | Adam Button signing out | ROC General | 2026-02-28
ROC | February | Angelica Chepiga signing in, weather +4C | ROC General | 2026-02-28
ROC | February | KSETDP, Junji from IAM is leaving site | ROC General | 2026-02-24
ROC | February | Connor Smith signing out | ROC General | 2026-02-25
ROC | February | QVSSSC - Franco from Property services on site. 13:05 Franco off site. | ROC General | 2026-02-27
ROC | February | Stouffville Flushing, Stephen from Stouffville Flushing will be flushing the Ballentrae side | ROC General | 2026-02-26
ROC | February | EGSSSC/QVSSSC/HLSSBS/HLPSYS/HLETYS/HLW4/HLW2, PCO Pest Control Is entering the sites | ROC General | 2026-02-24
ROC | February | KSSP- Ben from property services is on site to work on Chem room HVAC system | ROC General | 2026-02-26
ROC | February | AUSS - Teodore from AB leaving site. | ROC General | 2026-02-27
ROC | February | KBSP - Garrick from Ferguson Electric on site. | ROC General | 2026-02-25
ROC | February | KSSP - AB onsite for demolition, may cause dust. Call if alarm comes in 289-839-2474 | ROC General | 2026-02-23
ROC | February | Carter D signing in | ROC General | 2026-02-27
ROC | February | SEOC Shaft 4, Dominic from Honeywell is on site | ROC General | 2026-02-27
ROC | February | KSTP, Drew from Ferguson Electric is on site | ROC General | 2026-02-26
ROC | February | Adam Button signing in | ROC General | 2026-02-26
ROC | February | HMSS - Rowan from CPD on site to complete a walkthrough with contractors. | ROC General | 2026-02-24
ROC | February | QVSSSC - Dave Woods from Property services leaving site. | ROC General | 2026-02-24
ROC | February | Carter Dunn Signing In, -15D/Clear | ROC General | 2026-02-01
ROC | February | Ethan U signing in Weather: 0 | ROC General | 2026-02-26
ROC | February | Carter Dunn Signing In | ROC General | 2026-02-24
ROC | February | NMETIB, Bell operator on site | ROC General | 2026-02-01
ROC | February | Adeela Khan signing in. Weather: -11C and partly cloudy | ROC General | 2026-02-01
ROC | February | Christian Van Beek signing out. | ROC General | 2026-02-01
ROC | February | NMSSBP- Tony from Property Services onsite. 14:01- Offsite. | ROC General | 2026-02-02
ROC | February | Adam Button signing out | ROC General | 2026-02-02
ROC | February | Carter Dunn Signing In, -11D/Clear | ROC General | 2026-02-02
ROC | February | KSETWB- Dennis from Landmark is done on site | ROC General | 2026-02-02
ROC | February | NMETYS- Freedom Mobile onsite. 10:53- Offsite. | ROC General | 2026-02-02
ROC | February | KBSP- Phil from AB offsite | ROC General | 2026-02-02
ROC | February | Adeela Khan signing out | ROC General | 2026-02-02
ROC | February | QVW12- Garrick from Ferguson Electric done on site. Placed generator back in order | ROC General | 2026-02-02
ROC | February | NMETIB - Mohammad from Bell is finished on site | ROC General | 2026-02-01
ROC | February | NMETIB- Teddy from Freedom offsite. | ROC General | 2026-02-02
ROC | February | KBSP- Phil from AB on site | ROC General | 2026-02-02
ROC | February | Adam Button signing in | ROC General | 2026-02-02
ROC | February | SEOC4- Hamid from ETO onsite. | ROC General | 2026-02-02
ROC | February | Connor Smith signing out | ROC General | 2026-02-02
ROC | February | Angelica Chepiga signing out | ROC General | 2026-02-21
ROC | February | Adeela Khan signing out | ROC General | 2026-02-13
ROC | February | Adam Button signing in 3C Foggy | ROC General | 2026-02-20
ROC | February | Adam Button signing out | ROC General | 2026-02-10
ROC | February | Angelica Chepiga signing in | ROC General | 2026-02-10
ROC | February | Angelica Chepiga signing in, weather -9C | ROC General | 2026-02-12
ROC | February | QVW12 - Garrick from Ferguson electric on site. | ROC General | 2026-02-10
ROC | February | Adam Button signing out | ROC General | 2026-02-12
ROC | February | QVW12 - Garric from Ferguson is finished on site. Now headed to KSTP | ROC General | 2026-02-13
ROC | February | Connor Smith signing in 2C Clear | ROC General | 2026-02-21
ROC | February | Adeela Khan signing in. Weather: -15C and sunny QVW12 - Garrick from Ferguson Electric is on site and will be working on the diesel tank. Will not be working on the generator itself | ROC General | 2026-02-13
ROC | February | MKPSSA - Garrick for Ferguson electric on site, will attend SHSP after. | ROC General | 2026-02-12
ROC | February | Carter D Signing In | ROC General | 2026-02-18
ROC | February | QVSSSC- Terry from Property services is done on site | ROC General | 2026-02-11
ROC | February | QVW12 - Theordore from ABPMC on site to complete measurements. | ROC General | 2026-02-17
ROC | February | LSSS, Ubah F (student) is collecting samples on site, placed pump 6 to D1 so she is able to grab a sample | ROC General | 2026-02-18
ROC | February | Ethan U signing in | ROC General | 2026-02-22
ROC | February | BLW3 - Dominic leaving site. | ROC General | 2026-02-13
ROC | February | AUSS - Theodore is finished on site | ROC General | 2026-02-13
ROC | February | QVW34- Mark Process optimization is done on site | ROC General | 2026-02-17
ROC | February | Adam Button signing out | ROC General | 2026-02-19
ROC | February | Christian Van Beek signing in. Weather: 1C and clear. | ROC General | 2026-02-19
ROC | February | QVW12, Phil from AB is on site | ROC General | 2026-02-19
ROC | February | Christian Van Beek signing in. Weather: 1C and clear. | ROC General | 2026-02-17
ROC | February | NMPSKC - Hamid from ETO Engineering is on site. Hamid is on site with Dimitri from IAM | ROC General | 2026-02-13
ROC | February | Adeela Khan signing out | ROC General | 2026-02-20
ROC | February | Angelica Chepiga signing in,weather +2C | ROC General | 2026-02-20
ROC | February | Adam Button signing out | ROC General | 2026-02-11
ROC | February | Adeela Khan signing out | ROC General | 2026-02-22
ROC | February | Adeela Khan signing in. Weather: -2C and Cloudy | ROC General | 2026-02-10
ROC | February | QVW12- Cody from Ferguson onsite. | ROC General | 2026-02-11
ROC | February | LSSS - Ben from Property Services is on site for boiler repair | ROC General | 2026-02-13
ROC | February | Ethan Ullalkar signing out. | ROC General | 2026-02-18
ROC | February | Adam Button signing in in -3C clear | ROC General | 2026-02-11
ROC | February | Christian Van Beek signing in. Weather: -4C and clear. | ROC General | 2026-02-13
ROC | February | Connor Smith signing in -2 Cloudy | ROC General | 2026-02-15
ROC | February | Christian Van Beek signing out. | ROC General | 2026-02-14
ROC | February | Angelica Chepiga signing out | ROC General | 2026-02-12
ROC | February | Carter D Signing In, -6D/Clear | ROC General | 2026-02-19
ROC | February | Ethan U signing in Weather -1. | ROC General | 2026-02-15
ROC | February | NMETYS - Pinchai from YRP on site. | ROC General | 2026-02-12
ROC | February | KSTP - Theodore from AB Project Management is on site and will be completing a structure review 08:48 - Theodore is finished on site | ROC General | 2026-02-13
ROC | February | RHPSPA - Dominic from Honeywell on site. 15:48 Dominic off site. | ROC General | 2026-02-12
ROC | February | Connor Smith signing out. | ROC General | 2026-02-21
ROC | February | KSTP - Apu from Honeywell is on site | ROC General | 2026-02-20
ROC | February | Ethan U signing in Weather -4. | ROC General | 2026-02-14
ROC | February | SECC - Jonathan from Property services on site for fire alarm testing. | ROC General | 2026-02-18
ROC | February | KSETDP- Thomas from IAM is on site with Landmark to work on FCV | ROC General | 2026-02-17
ROC | February | KSTP - Drew from Ferguson Electric on site. 18:18 - KSTP - Drew leaving site. | ROC General | 2026-02-19
ROC | February | Adam Button signing in | ROC General | 2026-02-12
ROC | February | Adam Button signing out | ROC General | 2026-02-16
ROC | February | MAPS- Chris from Property Service onsite for fire test. | ROC General | 2026-02-11
ROC | February | SHSP - Steve from LCD mechanical on site. | ROC General | 2026-02-18
ROC | February | Carter D Signing Ouit | ROC General | 2026-02-13
ROC | February | Ethan U signing in Weather 2. | ROC General | 2026-02-16
ROC | February | QVW12 - Drew from Ferguson electric on site for gen transfer test. | ROC General | 2026-02-10
ROC | February | Gluzen Ramos Ong signing out | ROC General | 2026-02-12
ROC | February | NBW3 - Teodore from AB called, tech on site. 08:00 Off site. | ROC General | 2026-02-12
ROC | February | Adam Button signing in -5C Clear | ROC General | 2026-02-16
ROC | February | ANW23- Pest control on site. | ROC General | 2026-02-10
ROC | February | KSSP - Garrick from Ferguson Electric on site to complete a generator load bank test. The generator will not be available during the load bank test. Called Kevin K to inform. | ROC General | 2026-02-17
ROC | February | QVW34 - Mark S from process optimization on site to take pictures and complete and inspection. | ROC General | 2026-02-17
ROC | February | AURSBS- Dominic from Honeywell on site | ROC General | 2026-02-17
ROC | February | QVW12- Cody from Ferguson Electric is done on site | ROC General | 2026-02-11
ROC | February | Angelica Chepiga signing out | ROC General | 2026-02-18
ROC | February | Carter D Signing Out | ROC General | 2026-02-18
ROC | February | Ethan Ullalkar signing out. | ROC General | 2026-02-15
ROC | February | Christian Van Beek signing out. | ROC General | 2026-02-19
ROC | February | Adam Button signing in | ROC General | 2026-02-19
ROC | February | Christian Van Beek signing out. | ROC General | 2026-02-17
ROC | February | AURSBS, Orlando from property services is leaving site | ROC General | 2026-02-19
ROC | February | NMTKKC - Mike M from Lexsan on site. | ROC General | 2026-02-17
ROC | February | AUSS - Teodore from AB on site. | ROC General | 2026-02-13
ROC | February | Adam Button signing in | ROC General | 2026-02-17
ROC | February | Connor Smith signing out | ROC General | 2026-02-11
ROC | February | Ethan Ullalkar signing out. | ROC General | 2026-02-22
ROC | February | MAPS- Cody from Ferguson Electric is on site | ROC General | 2026-02-12
ROC | February | NMSSBP - Pat B. from Property services is on site for fire alarm testing 08:18 - Pat is finished on site | ROC General | 2026-02-20
ROC | February | QVW12 - Theodore from ABPMC leaving site. | ROC General | 2026-02-17
ROC | February | Adam Button signing out | ROC General | 2026-02-20
ROC | February | Pest Control visiting following sites, NSSSJA, KCSSKR, KCETFS, KCETDS, NBET27 | ROC General | 2026-02-11
ROC | February | Adam Button signing in -6C Snowing | ROC General | 2026-02-10
ROC | February | Connor Smith signing in -1 Cloudy | ROC General | 2026-02-14
ROC | February | LSSS - Dominic from Honeywell on site. 08:50 Dominic off site. | ROC General | 2026-02-13
ROC | February | KSSP- Dan From AB on site | ROC General | 2026-02-19
ROC | February | Angelica Chepiga signing in, weather -2C | ROC General | 2026-02-18
ROC | February | MKPSSA - Garrick from Ferguson electric leaving site. | ROC General | 2026-02-12
ROC | February | STPSTL- Gerrick from Ferguson onsite. | ROC General | 2026-02-11
ROC | February | Angelica Chepiga signing out | ROC General | 2026-02-21
ROC | February | YDOC - Jonathan from Property services testing fire alarm will attend SEOC OCF next. | ROC General | 2026-02-18
ROC | February | QVW12 - Cody from Ferguson electric leaving site. | ROC General | 2026-02-12
ROC | February | Angelica Chepiga signing out | ROC General | 2026-02-10
ROC | February | Angelica Chepiga signing out | ROC General | 2026-02-13
ROC | February | SHSP - Omat from ETO engineering finished with the air compressors and leaving site. | ROC General | 2026-02-17
ROC | February | Adeela Khan signing in. Weather: -1C and flurries | ROC General | 2026-02-22
ROC | February | Ethan U signing in Weather 0. | ROC General | 2026-02-17
ROC | February | KBSP, Phil from AB is on site | ROC General | 2026-02-18
ROC | February | SEOC67 - Jonathan from Property services on site for fire alarm testing. 11:20 Off site | ROC General | 2026-02-18
ROC | February | Christian Van Beek signing out. | ROC General | 2026-02-20
ROC | February | Adeela Khan signing in. | ROC General | 2026-02-20
ROC | February | AUSS - Pat B. from Property Services is on site and will be testing the fire alarm 10: 19 - Pat is finished on site | ROC General | 2026-02-20
ROC | February | AUPSWS - Orlando from property services is on site for a work order 11:42 - Orlando is finished on site | ROC General | 2026-02-20
ROC | February | Carter D Signing In, -3D/Snowing | ROC General | 2026-02-11
ROC | February | Adeela Khan signing out | ROC General | 2026-02-11
ROC | February | AUPSWS- Garrick from Ferguson Electric is on site | ROC General | 2026-02-11
ROC | February | NMPSKC, Phil from AB is on site | ROC General | 2026-02-12
ROC | February | Carter D Signing Out | ROC General | 2026-02-12
ROC | February | JDSS- Jeff from Property Services onsite. | ROC General | 2026-02-11
ROC | February | Christian Van Beek signing out. | ROC General | 2026-02-10
ROC | February | Connor Smith signing in | ROC General | 2026-02-11
ROC | February | SEOC67 - Phil from AB onsite. 11:15 off site. | ROC General | 2026-02-18
ROC | February | Connor Smith signing out | ROC General | 2026-02-15
ROC | February | Adam Button signing out | ROC General | 2026-02-17
ROC | February | NBETRS - Andrew from West Lake construction finished fixing the gate and leaving site. | ROC General | 2026-02-20
ROC | February | Carter Dunn Signing In, -2D/Clear | ROC General | 2026-02-12
ROC | February | SECC- Dave from property services is on site to work on MUA | ROC General | 2026-02-12
ROC | February | KSSP- Christine F on site | ROC General | 2026-02-17
ROC | February | KBSP- Garrick from Ferguson Electric is on site | ROC General | 2026-02-19
ROC | February | BLSS, Dominic from Honeywell is on site | ROC General | 2026-02-19
ROC | February | Adeela Khan signing in. Weather: 0C and rain | ROC General | 2026-02-21
ROC | February | Ethan Ullalkar signing out. | ROC General | 2026-02-17
ROC | February | JDSS - Hamid from ETO Engineering is on site 09:27 - Hamid is finished on site | ROC General | 2026-02-13
ROC | February | Ethan Ullalkar signing out. | ROC General | 2026-02-14
ROC | February | MKETFA - Meghal from YRP is on site | ROC General | 2026-02-20
ROC | February | KSTP- Dominic from Honeywell is on site | ROC General | 2026-02-20
ROC | February | RHAMF - NAC operator successfully cleared the VFD faults and the alarms cleared. Recirculation fans activated. | ROC General | 2026-02-17
ROC | February | wrong book | ROC General | 2026-02-05
ROC | February | Adeela Khan signing out | ROC General | 2026-02-08
ROC | February | Connor Smith signing out | ROC General | 2026-02-05
ROC | February | Christian Van Beek signing out. | ROC General | 2026-02-08
ROC | February | QVW12 - Garrick from Ferguson Electric leaving site. | ROC General | 2026-02-04
ROC | February | Carter D signing in, -9D/Clear | ROC General | 2026-02-03
ROC | February | KSTP- Andrew from Ferguson onsite. 16:02- Offsite. | ROC General | 2026-02-03
ROC | February | Connor Smith signing out | ROC General | 2026-02-03
ROC | February | Adam Button signing in -8C clear | ROC General | 2026-02-04
ROC | February | NMTKKC- Jon from Kingdom Construction onsite. 15:39- Finished onsite | ROC General | 2026-02-03
ROC | February | JFRS- Ben From Property Services finished onsite. | ROC General | 2026-02-03
ROC | February | STW3 - Dominic from Honeywell on site. 09:20 v- Dominic off site. | ROC General | 2026-02-03
ROC | February | KSSP - Ben (PSB) working on MUA9 | ROC General | 2026-02-04
ROC | February | Angelica Chepiga signing in, weather -12C | ROC General | 2026-02-05
ROC | February | QVW12 - Garrick from Ferguson electric on site. | ROC General | 2026-02-05
ROC | February | SEOC4 - Donald (Magnum Fire, 4167861418) on site | ROC General | 2026-02-04
ROC | February | KBSP- Terry from Property Services offsite. | ROC General | 2026-02-05
ROC | February | MKPSSA- Gerrick from Ferguson onsite. | ROC General | 2026-02-05
ROC | February | Adeela Khan signing in. Weather: -19C and clear | ROC General | 2026-02-07
ROC | February | STPSTL - Garrick from Ferguson electric on site. | ROC General | 2026-02-05
ROC | February | Adeela Khan signing in. Weather: -8C and Cloudy | ROC General | 2026-02-05
ROC | February | QVW12- Gerrick from Ferguson onsite. | ROC General | 2026-02-06
ROC | February | MKPSSA - Garrick from Ferguson electric leaving site. | ROC General | 2026-02-05
ROC | February | JDSS- Cody from Ferguson offsite. | ROC General | 2026-02-05
ROC | February | Adeela Khan signing out | ROC General | 2026-02-09
ROC | February | Angelica Chepiga signing in | ROC General | 2026-02-09
ROC | February | QVW12, Garrick from Ferguson Electric is leaving site | ROC General | 2026-02-06
ROC | February | EGSSSC - Rory from property services leaving site. | ROC General | 2026-02-04
ROC | February | EGSSSC - Rory from property services on site to work on heating problems. | ROC General | 2026-02-04
ROC | February | NBET- Samir from Yorknet off site. | ROC General | 2026-02-05
ROC | February | JFRS - Ben from Property services on site, working on heater. | ROC General | 2026-02-03
ROC | February | AUETFC - Dominic from Honeywell on site. | ROC General | 2026-02-05
ROC | February | AUETOH - Will from Chubb on site for a service call. | ROC General | 2026-02-07
ROC | February | AUETFC- Dominic from Honeywell finished onsite. | ROC General | 2026-02-05
ROC | February | QVSSSC - Rory from property services finished and leaving site. | ROC General | 2026-02-04
ROC | February | Angelica Chepiga signing in, weather -15C | ROC General | 2026-02-04
ROC | February | STW56 - Hameed (ETO Engineering, 6478577339) | ROC General | 2026-02-09
ROC | February | Angelica Chepiga signing out | ROC General | 2026-02-05
ROC | February | NMTKKC - Jamie from ETO Engineering offsite. | ROC General | 2026-02-06
ROC | February | QVW12 - Garrick from Ferguson electric on site. KBSP - Phil from AB on site. | ROC General | 2026-02-09
ROC | February | STPSTL - Hameed from ETO Engineering on site. | ROC General | 2026-02-09
ROC | February | STPSMR - Hameed from ETO Engineering off site. | ROC General | 2026-02-09
ROC | February | Pesticon (365-324-1097) at following sites: MARS VNRSKS RHRSTR RHRSWA | ROC General | 2026-02-09
ROC | February | GWTP, Dominic from Honeywell is leaving site | ROC General | 2026-02-09
ROC | February | Adeela Khan Signing in. Weather: -18C and clear | ROC General | 2026-02-08
ROC | February | Adeela Khan signing out | ROC General | 2026-02-06
ROC | February | SEOC OCF - Donald from Magnum fire leaving site. | ROC General | 2026-02-04
ROC | February | Connor Smith signing in | ROC General | 2026-02-05
ROC | February | YWS + NYWS NORMAL | ROC General | 2026-02-04
ROC | February | Christian Van Beek signing out. | ROC General | 2026-02-04
ROC | February | JDSS - Garrick from Ferguson electric on site. | ROC General | 2026-02-05
ROC | February | KBSP - Terry from Property services on site. | ROC General | 2026-02-05
ROC | February | Christian Van Beek signing in. Weather: -9 C and clear. | ROC General | 2026-02-09
ROC | February | Angelica Chepiga signing out | ROC General | 2026-02-09
ROC | February | wrong book | ROC General | 2026-02-05
ROC | February | Carter D Signing in | ROC General | 2026-02-06
ROC | February | NMTKKC - Jon C. from Kingdom Construction is on site | ROC General | 2026-02-09
ROC | February | STPSTL - Garrick from Ferguson electric off site. | ROC General | 2026-02-05
ROC | February | SEOC OCF - Donald from Magnum Fire protection on site. | ROC General | 2026-02-04
ROC | February | Adam Button signing out | ROC General | 2026-02-05
ROC | February | Angelica Chepiga signing in,weather -5C | ROC General | 2026-02-03
ROC | February | Gluzen Ramos Ong signing in | ROC General | 2026-02-04
ROC | February | KSSP - Ben from Property services leaving site. | ROC General | 2026-02-04
ROC | February | Angelica Chepiga signing out | ROC General | 2026-02-03
ROC | February | QVSSSC - Rory from property services on site. | ROC General | 2026-02-04
ROC | February | Carter D Signing In, -24D/Clear | ROC General | 2026-02-09
ROC | February | Connor Smith signing in | ROC General | 2026-02-03
ROC | February | MAPS- PD7 P2 Disch. Valve 1 Uncmd Close, PD7 P2 Uncmd Stop. Pump 3 took over in duty 1. *Wrong Book | ROC General | 2026-02-03
ROC | February | NBET- Samir from Yorknet onsite. | ROC General | 2026-02-05
ROC | February | NMTKKC - John from Kingdom Construction on site. | ROC General | 2026-02-04
ROC | February | Adeela Khan signing in. Weather: -4C and snowing | ROC General | 2026-02-06
ROC | February | Connor Smith signing in -8C Clear | ROC General | 2026-02-06
ROC | February | Christian Van Beek signing in. Weather: -23C and clear. | ROC General | 2026-02-08
ROC | February | Gluzen Ramos Ong signing out | ROC General | 2026-02-04
ROC | February | QVW12 - Garrick 9059263755 Heading to KSTP | ROC General | 2026-02-09
ROC | February | KSSP= Franco from Property Services onsite. | ROC General | 2026-02-06
ROC | February | Connor Smith signing in -8C Clear | ROC General | 2026-02-06
ROC | February | Christian Van Beek signing in. Weather: -25C and clear. | ROC General | 2026-02-07
ROC | February | GWTP - Ben from Property services leaving site. | ROC General | 2026-02-09
ROC | February | QVW12 - Garrick from Ferguson electric on site. | ROC General | 2026-02-04
ROC | February | AUETOH - Will from Chubb leaving site | ROC General | 2026-02-07
ROC | February | Christian Van Beek signing out. | ROC General | 2026-02-07
ROC | February | NMTKKC - Jamie from ETO Engineering reported power is back to normal, card reader not highlighted, notified Corp. security. Mobile security will attend site. | ROC General | 2026-02-09
ROC | February | QVSSSC - Roy from Property services on site. 11:15 Roy off site. | ROC General | 2026-02-05
ROC | February | QVW12 - Cody from Ferguson electric leaving site. | ROC General | 2026-02-05
ROC | February | GWTP - Ben (PSB) working on heaters | ROC General | 2026-02-09
ROC | February | Christian Van Beek signing in. | ROC General | 2026-02-04
ROC | February | BVPS, VNRSKS- Ken from ITS visiting these sites | ROC General | 2026-02-05
ROC | February | NMTKKC, Jamie from ETO Engineering is on site | ROC General | 2026-02-06
ROC | February | GWTP - Low lift , Dominic from Honeywell on site. | ROC General | 2026-02-09
ROC | February | NMTKKC - John from Kingdom Construction off site. | ROC General | 2026-02-04
ROC | February | ARPS, Martin from OCWA called, they are having comm issues on their end which has caused their pump to shut down. Martin tried rotating pumps to see if another pump would start up. No Pumps started up. Martin is contacting PCS to look into this issue. COTFA, Contacted Poulia from Toronto water, notified him that ARPS is having issues on their end, RO may need him to increase the flow but its currently not needed at this time. RO will continue to monitor MARS. 05:18, Martin from OCWA called, they were able to get pump 2 up and running | All Water System ROC General | 2026-02-03
ROC | February | STW12- Placed well 1 back into auto STW3- Placed well 3 back into auto | All Water System ROC General | 2026-02-24
ROC | February | Carter D Signing Out | All Water System ROC General | 2026-02-24
ROC | February | GWTP - Sutton header pH hi alarm. Checked site, trending shows a sudden spike of the pH reading which is slowly dropping. Informed area operator. | All Water System ROC General | 2026-02-24
ROC | February | KCETDS/KCETFS- PAC comm failure on sites. Checked hydro 1 for any power outages and notified Tim H of situation as there are no comms to site at this point. While on the phone with Tim H comms began to return slowly. May have been power blip but TIm H will notify Ops of PAC comm issues. #consult | All Water System ROC General | 2026-02-25
ROC | February | HLETYS, Activated D1 for Stephen B | All Water System ROC General | 2026-02-23
ROC | February | NMW15- Treated total Cl2 hi alarm came in. Checked trends quick spike in influent free Cl2 on well start up. Residual recovered after 3 mins. Cleared alarm | All Water System ROC General | 2026-02-27
ROC | February | KSTP- CO2 hihi alarm came in. Notified Stephen B. Will login to SCADA to investigate. OOR alarm came in while notifying Stephen B. Stephen B Notified ROC that Jackie P will be isolating KSETDP and taking samples once full. | All Water System ROC General | 2026-02-25
ROC | February | NBW5, Influent/Effluent Free Cl2D Lo alarm, placed well man/off, sent email to Tim H | All Water System ROC General | 2026-02-24
ROC | February | RHRSTR- Deactivated duty | All Water System ROC General | 2026-02-25
ROC | February | VNPS7 - Place pumps man/off MAP7 - Place pump 1 & 3 back in auto | All Water System ROC General | 2026-02-25
ROC | February | NMETDD - Talha H completing an OIT reboot. Talha has directed to disregard the associated historian heartbeat alarm. | All Water System ROC General | 2026-02-24
ROC | February | STPSMR - Kyle R called and requested that the pump 2 discharge valve be tested in manual mode. Cleared alarm, opened valve in manual. Kyle informed it is travelling. Valve faulted on a fail to open alarm. Kayle and Sean P investigating. | All Water System ROC General | 2026-02-24
ROC | February | MARS - Res level low alarm. MAPS PD8 duty just deactivated. Activated RHRSTR duty 1 to help with MARS level. | All Water System ROC General | 2026-02-28
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-28
ROC | February | ARPS - Peter from OCWA called to inform they will be completing their daily pump rotation. | All Water System ROC General | 2026-02-24
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-24
ROC | February | GWTP- Sutton header turbidity hi alarm came in D1 not active. UV 1 minor fault and lo UV irradiance. Notified Jack P will take a look at both issues on site KSTP- Post Cl2 lo vacuum alarm came in. Notified Jerry Z Post Cl2 1 working okay and Fluoride res stil low. Jerry Z aware and directed to disregard and give it time to recover | All Water System ROC General | 2026-02-25
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-23
ROC | February | NMW12, Eric S on site, working on pump 1 NMPSKC/ANW23, Kingsley M is resetting OITs on site, disregard historian alarms | All Water System ROC General | 2026-02-23
ROC | February | MAPS PD7, Placed pump 1 man/off VNPS PD7, Placed pump 2 in auto | All Water System ROC General | 2026-02-26
ROC | February | KCETDS - Activated duty 1 early in preparation for MAPS to JFRS Feed run 22:27 - KCPSDS - Pump 2 failed to start alarm came in. Was able to reset alarm. 22:30 - Pump 2 Failed to Start alarm came in again. Rotated duty so that pump 1 is in duty 1 and placed pump 2 man/off | All Water System ROC General | 2026-02-28
ROC | February | NMMCAD, Comm fails on site, notified Yash S, he will look into it | All Water System ROC General | 2026-02-24
ROC | February | NMW136, Eric S on site working on the Free Cl2 analyzer | All Water System ROC General | 2026-02-24
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-24
ROC | February | NMVCBA- Placed valve in man/open at 40L/s | All Water System ROC General | 2026-02-26
ROC | February | KSETDP - Chris S on site, working on altitude valve programming, requested disregard PAC commfail alarm. ET offline, Dan Z on site to assist . | All Water System ROC General | 2026-02-27
ROC | February | KSTP- Noticed High Lift Pump 4 in duty 1 running in manual. Placed into auto. | All Water System ROC General | 2026-02-24
ROC | February | AURSBS- Activated duty | All Water System ROC General | 2026-02-25
ROC | February | AUW14- Placed P2/3 in man/on 7:30-AUW14- Placed P4 in man/on 7:30- ARPS- Peter from Peel called to notify ROC of pump rotation from P6 to P7 | All Water System ROC General | 2026-02-25
ROC | February | MAPS PD7 Placed P2/3 in man/off VNPS PD7- Placed P2/3 in auto | All Water System ROC General | 2026-02-25
ROC | February | Christian Van Beek signing in. Weather: -8C and clear. | All Water System ROC General | 2026-02-26
ROC | February | KSTP - Finished water fluoride lolo alarm. Checked site, high lift flow recently started and trending shows a dip of the fluoride reading. Fluoride pump is active and will monitor to determine if the reading recovers. | All Water System ROC General | 2026-02-25
ROC | February | MKETFA- Travis W on site to actuate valves on site. Tower draining. Notified Peter from Metro of work ongoing NMW136- Alex B on site to inspect Cl2 system and exercise valves on well 13. Well is in man/off | All Water System ROC General | 2026-02-25
ROC | February | Carter Dunn Signing In | All Water System ROC General | 2026-02-26
ROC | February | GWTP- Jack P testing Cl2 leak detection and running scrubber | All Water System ROC General | 2026-02-26
ROC | February | YWS + NYWS NORMAL | All Water System ROC General | 2026-02-28
ROC | February | YWS+NYWS normal | All Water System ROC General | 2026-02-25
ROC | February | MTETNL, Evgeni S working on OIT, directed to disregard historian alarms | All Water System ROC General | 2026-02-24
ROC | February | MKRSEM- Called Toronto (Mehdi) and requested pumps off. | All Water System ROC General | 2026-02-24
ROC | February | NMVCBA- Placed valve manual 20L/s to keep NMETIB NMETHW Offset 00:08- Placed back into auto | All Water System ROC General | 2026-02-24
ROC | February | KCETDS- PAC comm fail on site. Trends okay. cleared upon acknowledgment | All Water System ROC General | 2026-02-26
ROC | February | MKETFA- Kingsley M on site to check wiring no alarms expected | All Water System ROC General | 2026-02-25
ROC | February | KCETDS- Aaron Carlo M switching to cell connection. Will lose comms for a minute | All Water System ROC General | 2026-02-26
ROC | February | GWTP- Hi lift free Cl2 hihi alarms came in. Notified Stephen B. Req call back in 20 mins if value doesn't recover 17:46-GWTP- Hi lift free CL2 residual did not recover. Notified Stephen B. will attend site. Created CMU5 W11692968 #consult #CMU5 | All Water System ROC General | 2026-02-26
ROC | February | YWS+NYWS normal | All Water System ROC General | 2026-02-26
ROC | February | STW12 - Place well 2 back in auto STW3 - Place well back in auto | All Water System ROC General | 2026-02-27
ROC | February | NMETIB - Deactivate duty 1, to assist with offsetting NMETHW | All Water System ROC General | 2026-02-27
ROC | February | HLETYS- Deactivated duty as per Stephen B. | All Water System ROC General | 2026-02-24
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-25
ROC | February | KSETDP, Jackie S on site, Flushing outlet analyzer | All Water System ROC General | 2026-02-27
ROC | February | Adam Button signing in 5C Sunny | All Water System ROC General | 2026-02-27
ROC | February | Ethan Ullalkar signing out. | All Water System ROC General | 2026-02-26
ROC | February | MAP7 - Pump 3 put to man/off VNP7 - Place pump 2 auto | All Water System ROC General | 2026-02-23
ROC | February | MARS - Tim H on site to exercise the interconnect MV1 valve. | All Water System ROC General | 2026-02-26
ROC | February | KSTP - Jerry Z finished at site | All Water System ROC General | 2026-02-23
ROC | February | QVW34, Parth P is finished on site. Isn't sure if wells can be placed back in auto or not. Contacted Jason G, directed to leave wells man/off for the night. If they are needed they can run, Jason G would like to be informed before running wells consult | All Water System ROC General | 2026-02-24
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-25
ROC | February | MKETFA - Mehdi from Toronto water exercising valves, disregard outlet flow alarms for the duration of the test. | All Water System ROC General | 2026-02-28
ROC | February | NBW3 - Hypo pump 1 failed to start. Duty reassigned to Hypo pump 2. Well 3 running in schedule mode. NBW3 - Influent free chlorine LoLo alarm, well 3 interlocked. Influent chlorine residual restored. Cleared Hypo 1 alarm. Cleared influent chlorine residual alarm and restarted Well 3 pump. Hypo pump 1 failed to start again. Placed Hypo pump 1 man/off, Hypo pump 2 running ok. Well 3 running normal. Emailed Benson S. | All Water System ROC General | 2026-02-28
ROC | February | Carter D Signing Out | All Water System ROC General | 2026-02-26
ROC | February | QVW34, Ben H on site, cleaning Cl2 analyzers | All Water System ROC General | 2026-02-23
ROC | February | KSTWKP - Transit contact center and Roads dispatch called to inform that both a resident of Georgina and a Town of Georgina operator contacted York Region to inform of a watermain break on the Queensway south between Walter Dr and Anneshiela Dr. AllPipes shows that the 500mm watermain on this road belongs to the Town of Georgina. Informed both Roads Dispatch and Transit contact center of this. Stated that if they Town of Georgina operator disagrees and believes the watermain belongs to York Region, will contact Linear on call to confirm. | All Water System ROC General | 2026-02-25
ROC | February | YWS + NYWS NORMAL | All Water System ROC General | 2026-02-28
ROC | February | VNPS- Gen diesel fault general alarm outstanding. Notified Tim H directed to disregard tank level hi causing issue | All Water System ROC General | 2026-02-26
ROC | February | STETBR - Tower level low alarm. Placed STW1 and STW3 in manual mode as per the interim procedure. | All Water System ROC General | 2026-02-24
ROC | February | AURSBS- Sample pumps shutdown after Yash S restored comms. Placed P1/2 in man/on as chem system was still manual off | All Water System ROC General | 2026-02-26
ROC | February | Ethan U signing in Weather: 0 | All Water System ROC General | 2026-02-26
ROC | February | QVW12, Donald M on site replacing Cl2 lines. NMETIB, Deactivated D1 AUVCPL, Placed valve chamber in manual and set flow control setpoint to 100L/sec | All Water System ROC General | 2026-02-24
ROC | February | AURSBS- Blown fuse Rack 1 slot 7. Control panel power loss alarm came in. Chemical system faulted not running. Pre injection total Cl2 hihi/ free ammonia hi/ combined Cl2 hi/ mono chloram lolo and post injection mono chloram lolo then hihi alarms came in. Contacted Donald M. Directed to manually start sample P1/2 and place chem system man/off. Chem system was faulted and not dosing during the power outage and reading on analyzers are not accurate. Notified Yash S of issues on site they blew a fuse causing power issues. Still need 30 mins to finish network switch | All Water System ROC General | 2026-02-26
ROC | February | Christian Van Beek signing out. | All Water System ROC General | 2026-02-26
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-27
ROC | February | YWS+NYWS normal | All Water System ROC General | 2026-02-25
ROC | February | SHTP- Found filter 3 turbidity trending erratically. Notified Benson S. Will take a look on SCADA YWS+NYWS normal #consult | All Water System ROC General | 2026-02-27
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-26
ROC | February | KCPSDS - Site power failure, discharge FCV fault. PAC control panel power fail KCETDS - Control panel power failure. Hydro One map shows outage in area with restoration time being 3:00am. Will monitor KCETFS - Isolation valve fault. Informed Benson S of outstanding alarms and power failure. Duty was active at the time of alarms. Pumps interlocked with tower at 71% at the time. Benson S okay to respond in the morning Consult | All Water System ROC General | 2026-02-27
ROC | February | MKRSEM - Request TO (Brent) to drop both pumps | All Water System ROC General | 2026-02-27
ROC | February | STETBR, Tower Level Lo Alarm, Activated D1 STW2/3, Placed Wells 2/3 in man/on to help fill STETBR | All Water System ROC General | 2026-02-27
ROC | February | MKRSEM- Called Metro spoke with Paul to start 2 pumps | All Water System ROC General | 2026-02-27
ROC | February | SHTP- Turbidity trends still abnormally high. Notified Benson S. Will attend site .Created CMU5 W11695345 NMTKKC- Ammonia P1 failed to start P2 started in its place. Reset alarm #CMU5 | All Water System ROC General | 2026-02-27
ROC | February | KSETDP - Outlet free chlorine Low alarm. Jackie S called yesterday from site and requested disregard chlorine residual alarms until Monday. Site offline and isolated until Monday. 11:50 KSETDP - verified with Stephen B , Outlet free chlorine residual low, slowly declining, ok to disregard. Not a distribution water residual. # Consult | All Water System ROC General | 2026-02-28
ROC | February | SHETCS- Post injection total Cl2 lo alarm came in. Checked trends residual lower than normal and is almost the same as inlet analyzer. Hypo pump 2 running and speed increasing. Continued to monitor for 10 mins no change. Rotated to hypo pump 1. Residual recovered after 3 mins alarms cleared . Placed P2 in man/off and emailed West Water team. | All Water System ROC General | 2026-02-27
ROC | February | NBW5- Tim H called and requested a call if the low effluent switch alarm comes in at 0.4mg/L. Well currently man/off | All Water System ROC General | 2026-02-24
ROC | February | KSTP - Carbon Dioxide HiHi alarm. Stephen B called back and directed to activate the KSTP duty 1 high lift pump in manual. Activated high lift pump 4 in manual. Stephen B will attend site to inspect the CO2 system. Created CMU5#W11691423 #CMU5 | All Water System ROC General | 2026-02-25
ROC | February | ARPS- Benesh from OCWA called. Rotating pumps from pump 6 to pump 5. | All Water System ROC General | 2026-02-28
ROC | February | MAPS PD7 Placed P1/3 in man/off VNPS PD7- Placed P2/3 in auto | All Water System ROC General | 2026-02-28
ROC | February | KSTKWP- Tower hi level alarm came in notified Patrick F. Patrick F will make adjustments | All Water System ROC General | 2026-02-25
ROC | February | MKRSEM - Request TO (Brent) to run 2 pumps | All Water System ROC General | 2026-02-26
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-27
ROC | February | STRS48- JOe M on site to test Cl2 leak alarms | All Water System ROC General | 2026-02-26
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-27
ROC | February | GWTP, Parth P is on site at the low lift building, preforming annual calibrations | All Water System ROC General | 2026-02-27
ROC | February | YWS + NYWS NORMAL | All Water System ROC General | 2026-02-28
ROC | February | NMETIB- Activated Duty 1 to offset with NMETHW. | All Water System ROC General | 2026-02-28
ROC | February | Adeela Khan signing in. Weather: -5C and Cloudy | All Water System ROC General | 2026-02-28
ROC | February | GWTP - High lift header free chlorine hit 2.02mg/L. As per shift report notified Stephen B, no issues or change in Keswick or Sutton line free readings upstream. Okay to disregard for the night Consult | All Water System ROC General | 2026-02-26
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-26
ROC | February | AUPSWS, Jerry Z on site, testing temp/flood and running generator | All Water System ROC General | 2026-02-26
ROC | February | MAPS PD7, Placed pumps 1/2/3 to man/off VNPS PD7, Placed pumps 2/3 to auto | All Water System ROC General | 2026-02-27
ROC | February | NMVCBA- Placed valve back in auto | All Water System ROC General | 2026-02-28
ROC | February | BVPS - Activate duty 1 | All Water System ROC General | 2026-02-23
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-23
ROC | February | Ethan U signing in Weather -4. | All Water System ROC General | 2026-02-23
ROC | February | KSTP - CO2 Adjusted pH level LoLo alarm came in. Value turned normal on its own and alarm cleared. Will monitor | All Water System ROC General | 2026-02-23
ROC | February | Carter D Signing In | All Water System ROC General | 2026-02-23
ROC | February | NMETHW/NMETYS - Evgeny rebooting heartbeat alarm QVETQS/QVW12/QVW34/HLW/HLW2 - Kingsley M rebooting OIT for sites | All Water System ROC General | 2026-02-23
ROC | February | NMW136, Eric S is leaving site | All Water System ROC General | 2026-02-24
ROC | February | Carter D signing in | All Water System ROC General | 2026-02-27
ROC | February | SHTP, Treated Water Turbidity Fault, Plant is shutting off/Tower is Draining, notified Cole W and West team before their morning meeting started, they will have someone look into it | All Water System ROC General | 2026-02-27
ROC | February | NMETIB - Deactivated duty 1 to maintain level offset from NMETHW. | All Water System ROC General | 2026-02-27
ROC | February | VNP7 - Place pumps back man/off MAP7 - Place pump 2 & 3 auto | All Water System ROC General | 2026-02-23
ROC | February | NMW15- Combined Cl2 lo alarm came in. Well in man/off no water directed to users | All Water System ROC General | 2026-02-28
ROC | February | NMVCBA- Placed valve in man/open at 40L/s | All Water System ROC General | 2026-02-27
ROC | February | YWS + NYWS NORMAL | All Water System ROC General | 2026-02-28
ROC | February | Christian Van Beek signing out. | All Water System ROC General | 2026-02-25
ROC | February | NMETIB- Activated D1 at 49% to offset from NMETHW as per shift report | All Water System ROC General | 2026-02-28
ROC | February | NMW15 - Dan B and Kyle R finished on site. Cleared alarms and placed the well in auto mode. | All Water System ROC General | 2026-02-25
ROC | February | KSTP - Jerry Z onsite, disregard any alarms coming in while contractors work on intake | All Water System ROC General | 2026-02-23
ROC | February | BVPS - Activated duty 1. MARS - low level alarm. BVPS activation will help to increase MARS level. | All Water System ROC General | 2026-02-24
ROC | February | VNRSKS - Swapped supply pumps from MAPS to VNPS. | All Water System ROC General | 2026-02-24
ROC | February | SECC, Yash S on site, replacing OITs and working on system panel Wrong Book | All Water System ROC General | 2026-02-24
ROC | February | VNPS- Placed PD7 pump to man/off MAPS- Placed PD7 pump 3 in auto | All Water System ROC General | 2026-02-24
ROC | February | NMETIB- Activated D1 to offset from NMETHW as per shift report AURSBS- Cl2 iso valve failed to open alarm came in. Chemical system not being called for and alarm reset. AUW14- Joe D req wells to be running in manual for sampling later this morning. D1 just deactivated. NMTKBS- Activated D1. AUETOH- Activated D1 | All Water System ROC General | 2026-02-25
ROC | February | MKETFA - Toronto Water (Zoran) called and informed that they will be going back to normal operations | All Water System ROC General | 2026-02-26
ROC | February | BLETNL, Phil D is on site, working on the analyzers | All Water System ROC General | 2026-02-26
ROC | February | YWS + NYWS Normal Carter D Signing Out | All Water System ROC General | 2026-02-27
ROC | February | HLSSBS- Terry C and Bill V on site to work on P3 NMSSBP- Mech screen 1 overtorque alarm came in. Notified Kevin S closed gate 2 as 1 was still available. Will try to reset alarm and will escalate if alarm cannot be reset **WRONG BOOK** | All Water System ROC General | 2026-02-25
ROC | February | ARPS- Peter from Peel called to notify ROC that they will be transferring from P7 to P5 STW12/3- Placed well 2/3 in man/on as per interim | All Water System ROC General | 2026-02-26
ROC | February | AURSBS- Activated D1 HLETYS- Activated D1 as per Stephen B. Will be heading to HLW2 to trouble shoot ammonia pumps | All Water System ROC General | 2026-02-26
ROC | February | Ethan U signing in Weather: -2c | All Water System ROC General | 2026-02-25
ROC | February | ARPS- Peter from OCWA called to notify that they are rotating pumps, from P5 to P6. | All Water System ROC General | 2026-02-27
ROC | February | MARS, Tim H on site, working on pump 4 | All Water System ROC General | 2026-02-27
ROC | February | STETBR - Tower low level alarm, Man/started STW12 pump 2 and STW3 to help with fill cycle. | All Water System ROC General | 2026-02-28
ROC | February | NBW5 - Jake M and Benson S on site to re-vamp the chlorination system. May see associated alarms. | All Water System ROC General | 2026-02-24
ROC | February | QVW12 - Donald M and Will M on site to complete maintenance. | All Water System ROC General | 2026-02-24
ROC | February | GWTP, Jack P on site with CMS, they are replacing a valve from the UV channel, directed to disregard Turbidity fault alarms at this current time, Plant is off at this time | All Water System ROC General | 2026-02-24
ROC | February | MTW12, Joe M/Travis W on site, Chemical system/inspection maint/silicate system inspection/Cl2 analyzer cleaning and injection cleaning and hi lo temp alarm are the alarms they will be working on | All Water System ROC General | 2026-02-24
ROC | February | NBW2, John D on site, pulling cables 16:03, John D leaving site | All Water System ROC General | 2026-02-24
ROC | February | GWTP, ZW6 Shutdown//BP Pump 1 flow lolo/Not available alarm, notified Dan Z, she will investigate consult | All Water System ROC General | 2026-02-24
ROC | February | Christian Van Beek signing in. | All Water System ROC General | 2026-02-25
ROC | February | Angelica Chepiga signing in,weather -7C | All Water System ROC General | 2026-02-27
ROC | February | NMW15- Placed well man/on for Dan B MAPS PD7- Chris I done on site P4 OOS KSTKWP- Tower level hihi alarm came in. Patrikc F still making adjustments to help KSETDP fill AUETFC- Kyle C on site STETTL- Lane from town of Stouffville is flushing in system | All Water System ROC General | 2026-02-25
ROC | February | NBW5, Kyle R on site, replacing generator battery | All Water System ROC General | 2026-02-24
ROC | February | NMW136 - Influent free chlorine hi and hihi alarm. Checked site, well recently activated. Trending shows a spike of the influent free chlorine reading which returned to normal range within two reading intervals. Reset alarms. | All Water System ROC General | 2026-02-24
ROC | February | NMETHW - Activated duty 1. | All Water System ROC General | 2026-02-24
ROC | February | HLETYS, Eric S on site, working on Chemical Transfusers on the tanks | All Water System ROC General | 2026-02-23
ROC | February | MTW3 - Jack P & Jackie S onsite working on chlorine system | All Water System ROC General | 2026-02-23
ROC | February | Adam Button signing in -3C clear | All Water System ROC General | 2026-02-25
ROC | February | NMW136 - Alex B finished and leaving site. NMW15 - Kyle R called and requested the pump be shut down so he and Dan B can complete some additional maintenance. | All Water System ROC General | 2026-02-25
ROC | February | VNRSKS - Swapped supply pumps from two MAPS pumps to one VNPS and one MAPS pump. | All Water System ROC General | 2026-02-24
ROC | February | SHTP- Filter 3 Turbidity Hi Alarm. Backwash just completed. Disregard as per SCADA Report. | All Water System ROC General | 2026-02-24
ROC | February | MKPSSA - Combined chlorine lolo alarm. Station is currently offline as the Linear team has completed an isolation and the pipe the analyzer pulls from is currently empty. MKRSEM - Low level alarm. Called Toronto Water (Paul) and requested they activate two pumps to push flow to MKRSEM. | All Water System ROC General | 2026-02-24
ROC | February | MKRSEM- Reservoir hi level alarm came in. Called Metro spoke with Paul to stop pumps | All Water System ROC General | 2026-02-28
ROC | February | NMW12- Treated total/ Combined Cl2 lo alarm came in Well not active no water directed to users. Will continue to monitor 4:03-NMW12- Alarms cleared as residuals recovered. Wells were not called for while alarms were outstanding | All Water System ROC General | 2026-02-28
ROC | February | VNRSKS - Swapped supply pump to one MAPS pump and one VNPS pump. | All Water System ROC General | 2026-02-26
ROC | February | HLETYS- Stephen B called and requested to deactivate duty at 55% | All Water System ROC General | 2026-02-24
ROC | February | NBW3- Influent free CL2 lolo alarm came in interlocking well on start up. Well was running in manual. Notified Jordan B directed to clear alarms and restart well. Rotated hypo pump duty and restarted wells after clearing alarms | All Water System ROC General | 2026-02-25
ROC | February | KSSP, Phil from AB is on site wrong book | All Water System ROC General | 2026-02-27
ROC | February | AUW57 - Joe D finished on site, directed well 5 pump back to auto. | All Water System ROC General | 2026-02-27
ROC | February | MAP8 - Suct. header tot/free resid OOR. Analyzer isolated. Confirmed with Jacob M no flow to site and will be OOS/isolated for a few weeks. Disregard MAPS - Dwayne L took offline, until York peel feeder main returns | All Water System ROC General | 2026-02-23
ROC | February | MTW12- Silicate P1/2 OOS. Notified Phil D will investigate on site | All Water System ROC General | 2026-02-25
ROC | February | SUETDR - Jackie S on site. Building Flood Alarm cleared. Jackie S leaving site. | All Water System ROC General | 2026-02-27
ROC | February | KSETDP- Rick L on site for Cl2 analyzer commissioning | All Water System ROC General | 2026-02-25
ROC | February | NMW12 - Eric S finished onsite, Replaced silicate pump 1 | All Water System ROC General | 2026-02-23
ROC | February | Ethan Ullalkar signing out. | All Water System ROC General | 2026-02-27
ROC | February | VNPS PD7- Placed P3 in man/off MAPS PD7 - Placed P3 in auto | All Water System ROC General | 2026-02-27
ROC | February | YWS+NYWS normal NMVCBA- Changed flow set point from 40l/s to 30L/s | All Water System ROC General | 2026-02-27
ROC | February | SUETDR - Building flood alarm. Notifies Jackie S. She will attend site. | All Water System ROC General | 2026-02-27
ROC | February | QVW34, Eric S on site, working on Total Cl2 analyzer | All Water System ROC General | 2026-02-27
ROC | February | YWS + NYWS NORMAL Angelica Chepiga signing out | All Water System ROC General | 2026-02-27
ROC | February | AUETFC - Deactivated duty 1 for tower sampling as per Joe D. STETBR - Tower level low alarm. Activated STW1 and STW3 in manual mode as per the interim procedure. | All Water System ROC General | 2026-02-25
ROC | February | AURSBS, Yash S is finished with the network switch | All Water System ROC General | 2026-02-26
ROC | February | VNPS PD7, Placed pump 2/3 man/off MAPS PD7, Placed 1/2/3 back to auto AUW57, Placed well 5 back to auto as per Joe D NMVCBA, Placed valve back to auto | All Water System ROC General | 2026-02-26
ROC | February | QVW34 - Treated total chlorine Hi alarm, adjusted chlorinator 2 from 74 to 71%. Well 3 interlocked on Combine chlorine HiHi alarm shortly after. Well 3 pump was running in schedule mode. Notified William M. He will attend site . | All Water System ROC General | 2026-02-27
ROC | February | MKRSEM - Stephen B was able to clear Building smoke alarm. Leaving site. | All Water System ROC General | 2026-02-27
ROC | February | TMC269- Pressure lolo alarm came in. Quick dip in trends and recovered. Cleared alarm | All Water System ROC General | 2026-02-25
ROC | February | AUETFC- Kyle C done on site | All Water System ROC General | 2026-02-25
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-26
ROC | February | HLW1 - Combine chlorine Low alarm, quick dip in trends. Value recovered in 5 minutes. Cleared alarm. | All Water System ROC General | 2026-02-28
ROC | February | Connor Smith signing in -8C cloudy | All Water System ROC General | 2026-02-24
ROC | February | MAP8 - PD8 P3 VFD fault, VFD not ready, informed Jacob M. Will look into it with Tim H NMW15 - Yash S working on OIT | All Water System ROC General | 2026-02-23
ROC | February | NMETIB- Activated D1 to offset from NMETHW as per shift report | All Water System ROC General | 2026-02-26
ROC | February | MKMCLA- Comm Fail. Alarm cleared after about 45 minutes. Gap in trends. Will inform PCS and Linear. | All Water System ROC General | 2026-02-25
ROC | February | MARS - Called Toronto water( Mehdi) and requested to increase the flow. | All Water System ROC General | 2026-02-28
ROC | February | ARPS - Peter D informed they are doing a pump switch. Stopping pump 7 and putting pump 5 in duty 1 | All Water System ROC General | 2026-02-23
ROC | February | MAP7 - Place pump 1 & 2 man/off VNP7 - Place pump 3 auto | All Water System ROC General | 2026-02-23
ROC | February | VNRSKS - Swapped supply pumps from two VNPS pumps to one VNPS pump and one MAPS pump to reduce the demand on RHRSTR. | All Water System ROC General | 2026-02-27
ROC | February | KSTKWP - Jerry Z on site for a chlorine leak test. | All Water System ROC General | 2026-02-24
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-23
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-24
ROC | February | KSTP - Stephen B found CO2 levels coming down and speaking w Ben H will disregard for the night. Will monitor if continuous to go down and will place highlift pump 4 back in auto if trend continuous downward at request of Stephen B GWTP - Followed up with UV reactor 1 lamp #3 lo UV irradiance. Okay to disregard for the night. UV reactor 2 on duty 1 | All Water System ROC General | 2026-02-25
ROC | February | AUW57 - Joe D working on site, testing chlorine leak. Directed Well 5 pump man/off for the duration of the work. | All Water System ROC General | 2026-02-27
ROC | February | KSTP, Jerry Z on site testing the Cl2 leak alarm | All Water System ROC General | 2026-02-24
ROC | February | RHPSPA- Gen. Warning Alarm. Unable to clear. Emailed Jason G. and East Ops. | All Water System ROC General | 2026-02-24
ROC | February | STPSMR, Sean P/Kyle R on site working on pump 2 | All Water System ROC General | 2026-02-24
ROC | February | VNPSAP - Joe W on site to complete a temperature alarm test and a flood alarm test. | All Water System ROC General | 2026-02-24
ROC | February | AURSBS, Notified Donald M that Yash S is finished with the network switch upgrades, Donald M is heading to site. Directed to leave the chemical system in man/off for the time being | All Water System ROC General | 2026-02-26
ROC | February | STW12- Hypo P1 Uncommanded stop alarm came in. Joe M on site working on pump | All Water System ROC General | 2026-02-26
ROC | February | KCETDS - PAC communication failure, PAC comms failure. Hydro One restoring pole in area which is cause of initial power loss in area. Informed Yash S as critical alarm and site appears offline unable to see level. Last reading was around 66%. KCETFS still showing level KCPSDS - PAC communication failure. CMU = 11693012 3:11 - Power restored to site, Hydro One completed with work and power appears to be restored | All Water System ROC General | 2026-02-27
ROC | February | NBW2, Parth P on site, Duty is about to start for the tower and only one well is currently available, notified Parth P to get ahold of the operator to confirm that the tower will fill with 1 well | All Water System ROC General | 2026-02-24
ROC | February | STW12 - Man/start well 1 STW3 - Man/start well 3 STETBR - Low alarm did not come in. Change low alarm from 60 to 61% | All Water System ROC General | 2026-02-23
ROC | February | HLW1 - Treated total chlorine Hi alarm. Effluent free chlorine residual higher than target. Adjusted chlorinator 1 dosage from 119 to 115%. | All Water System ROC General | 2026-02-27
ROC | February | AUW57- Influent free cl2 hi alarm came in. Recovered after 3 mins cleared alarm | All Water System ROC General | 2026-02-27
ROC | February | YWS+NYWS normal | All Water System ROC General | 2026-02-28
ROC | February | KSTP- Fin Water Fluoride Res Fault, Fin Water Tot CL2 Res Fault Alarms. Disregard as per SCADA Report. | All Water System ROC General | 2026-02-24
ROC | February | MARS - Called Toronto water (Paul) and requested decrease flow. | All Water System ROC General | 2026-02-28
ROC | February | NMPSKC- Talha H rebooting OIT disregard historian heartbeat alarm 13:35- NMPSKC- Talha H done rebooting OIT cleared historian heartbeat alarm | All Water System ROC General | 2026-02-25
ROC | February | KCETDS/KCPSDS, Aaron from PCS is done on site, trends looking normal | All Water System ROC General | 2026-02-26
ROC | February | SHTP - Well pump 2 uncommanded start alarm. Checked site, plant is not active. Well pump 2 flow recently stopped. Cleared alarm. | All Water System ROC General | 2026-02-28
ROC | February | MKRSEM- Called Metro spoke with Brett to start two pumps to fill reservoir | All Water System ROC General | 2026-02-25
ROC | February | NMW12, Alex B activated the duty of the site, if the lo/hi residual alarm comes in, Alex B would like ROC to contact Jason G. contacted Jason G but no response, will wait another 5 minutes then give him another call 14:04, Contacted Alex B as the residual is continuing to drop, Alex is on site watching and will react to the residual | All Water System ROC General | 2026-02-26
ROC | February | AURSBS - Chlorine GLCR 1 vlv fail to open. Able to clear. Reoccurring alarm | All Water System ROC General | 2026-02-27
ROC | February | NMPSKC, Dan B on site, Working on pumps 5 and 6. Dan B will have to cut the power to the site. Power loss at NMPSKC will last for 30 minutes. Once power is restored, Pumps 5 and 6 will be OOS while pumps 1-4 will be available if needed | All Water System ROC General | 2026-02-27
ROC | February | Adeela Khan signing out | All Water System ROC General | 2026-02-23
ROC | February | STPSMR - Kyle R & Sean P onsite working on valve replacement | All Water System ROC General | 2026-02-23
ROC | February | NBW2, Parth P/Rick L is finished on site, placed well back to auto | All Water System ROC General | 2026-02-24
ROC | February | Adam Button signing out | All Water System ROC General | 2026-02-25
ROC | February | MARS, Contacted Toronto Operator Brent to increase the flow to the res | All Water System ROC General | 2026-02-23
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-25
ROC | February | VNP7 - Suct Hdr free Cl2 hi, reaching hihi level and trends shows spike in reading after adjustment from today. Total also appears drop in reading. Informed Ben H. Okay to disregard hi/hihi header free. Consult | All Water System ROC General | 2026-02-25
ROC | February | Hub 1/Hub 2 Server/HLW12/HLETYS/STETTL/NMSSHS/STW12, Comm Fail alarms, contacted Yash S, he will look into it 09:24, Comms/Trends have been restored | All Water System ROC General | 2026-02-23
ROC | February | AUPSRR- Donald M on site to run generator test and test Cl2 leak detection alarms | All Water System ROC General | 2026-02-26
ROC | February | SUETDR, Building Flood Alarm, notified Jackie S, she will head to site to investigate the issue CMU5: W11694960 | All Water System ROC General | 2026-02-27
ROC | February | RHRSTR - Deactivated D1 to maintain MARS level. | All Water System ROC General | 2026-02-28
ROC | February | AUW57, Joe D on site, working on the chemical analyzers and the turbidity analyzer | All Water System ROC General | 2026-02-24
ROC | February | NRETCR, Jason G on site, testing Temp alarms, calibrating analyzers and doing valve testing | All Water System ROC General | 2026-02-26
ROC | February | QVW34 - Eric S finished on site. Placed pumps 3 and 4 back to auto as directed by Ben H. | All Water System ROC General | 2026-02-27
ROC | February | AURSBS- Activated D1 | All Water System ROC General | 2026-02-28
ROC | February | VNRSKS - Deactivated duty due to lower levels at RHRSTR. Rotated pumps so that MAPS PD7 was in auto while all pumps at VNPS PD7 are man/off. | All Water System ROC General | 2026-02-28
ROC | February | NRETCR, Activated D1 for Tim H | All Water System ROC General | 2026-02-27
ROC | February | AUW57- Joe D and Jay G on site to work on chlorinator 2 | All Water System ROC General | 2026-02-26
ROC | February | QVW12- Influent free Cl2 lo alarm came in. Slowly recovering alarm cleared after 6 mins | All Water System ROC General | 2026-02-25
ROC | February | NMW136- Influent free Cl2 hihi alarm came in recovered after 3 minas alarm cleared STETTL- STETTL to STW12 comm alarm. Cleared alarm trends okay GWTP- Cl tank 2 weight lo alarm disregard on shift report tank 1 full | All Water System ROC General | 2026-02-25
ROC | February | STETBR- Tower level hi alarm STW12/3- Placed P2/3 in auto as per interim | All Water System ROC General | 2026-02-27
ROC | February | NMETHW, Evgeni S resetting OIT, directed to disregard Historian Heartbeat | All Water System ROC General | 2026-02-23
ROC | February | GWTP, High Lift Free Cl2 hihi, Stephen B has reviewed the system and has directed to disregard the alarm at this time, If the residual on the analyzer hits 3.0mg/L or if the Keswick or Sutton line analyzers hit a hi/hihi alarm, Stephen B would like to be notified. consult | All Water System ROC General | 2026-02-26
ROC | February | Carter Dunn Signing In | All Water System ROC General | 2026-02-24
ROC | February | HLETYS, Activated D1 for Jen S | All Water System ROC General | 2026-02-24
ROC | February | HLETPR - Evgeny S rebooting OIT. Evgeny directed to disregard the associated Historian heartbeat alarm. | All Water System ROC General | 2026-02-24
ROC | February | AUMCBS - Rick L & Parth P onsite working on adjustment to flow meter | All Water System ROC General | 2026-02-23
ROC | February | KSETDP, Junji from IAM is on site GWTP, Tyler Z on site, working on low lift pump 3 | All Water System ROC General | 2026-02-23
ROC | February | YWS+NYWS Normal Adam Button signing out | All Water System ROC General | 2026-02-28
ROC | February | MARS - Request TO (Mehdi) to drop to normal flow | All Water System ROC General | 2026-02-23
ROC | February | NBW3, Rashad R from Bosh Paladin Technology is on site, doing some test reports | All Water System ROC General | 2026-02-27
ROC | February | QVW34, Parth P/Rick L on site, working on the total cl2 analyzer NMW15, Alex B on site, Repriming the silicate pumps | All Water System ROC General | 2026-02-24
ROC | February | NBW5, Kyle R/Sean P leaving site | All Water System ROC General | 2026-02-24
ROC | February | STW12- Placed well 1 back into auto STW3- Placed well back into auto | All Water System ROC General | 2026-02-25
ROC | February | YWS + NYWS Normal Connor Smith signing out | All Water System ROC General | 2026-02-25
ROC | February | NMETIB - Activated duty 1 to maintain level offset with NMETHW. | All Water System ROC General | 2026-02-24
ROC | February | NBW3 - Influent free chlorine lolo alarm. Checked site, well recently activated in schedule mode and then interlocked on the influent free chlorine lolo alarm. Influent free chlorine residual recovered, rotated the hypo pump duty back to pump 2 and cleared alarm. Monitored well start up. | All Water System ROC General | 2026-02-24
ROC | February | AUW14- Placed P1 in man/on MKRSEM/MKRSMR- Peter from Metro called to notify ROC they will be running a generator from 8:30-9:30 on site and would like to activate MKRSMR D1 early. Notified Dan Z of plan and has no issues with this. Notified Peter from Metro there's no issue with generator run. | All Water System ROC General | 2026-02-25
ROC | February | QVW34 - Eric S leaving site. | All Water System ROC General | 2026-02-25
ROC | February | MKRSEM - Request TO (Brent) to drop both pumps | All Water System ROC General | 2026-02-26
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-26
ROC | February | NMW12- Alex B on site to work on silicate system and NTU analyzer. Alex B is placing wells in man/off | All Water System ROC General | 2026-02-26
ROC | February | KSETDP - Rick L on site to complete analyzer calibrations. | All Water System ROC General | 2026-02-26
ROC | February | KSETDP, Parth P is finished on site | All Water System ROC General | 2026-02-26
ROC | February | AUPSOH- Discharge flow lolo alarm came in. Flow with in range cleared alarm | All Water System ROC General | 2026-02-27
ROC | February | MARS - Level Hi alarm. MAPS PD7 duty just activated. Will monitor. | All Water System ROC General | 2026-02-28
ROC | February | MKMCLA - PAC communication failure. will monitor site and will inform PCS if does not clear by start of morning | All Water System ROC General | 2026-02-27
ROC | February | HLW1 - Treated Free chlorine Hi alarm , value gradually increasing. Ammonia pump 1 running on duty 1, Stephen B was troubleshooting ammonia pump 1 earlier today. Notified Stephen B, he directed to switch ammonia pumps. Assigned ammonia pump 2 to duty 1 and placed ammonia pump 1 man/off. | All Water System ROC General | 2026-02-27
ROC | February | GWTP, Parth P leaving site KSETDP, Jack P called to inform the ROC that they are testing the lo/lolo Level lit alarms on site | All Water System ROC General | 2026-02-27
ROC | February | KSETDP - Jackie S finished flushing chlorine analyzers and verified outlet chlorine analyzers. Requested disregard chlorine alarms, ET isolated until Monday. Jackie S leaving site shortly. | All Water System ROC General | 2026-02-27
ROC | February | NMW136- Combined/ treated total Cl2 lo alarms. Dip in trends. Recovered after 6 minutes, alarms cleared. | All Water System ROC General | 2026-02-27
ROC | February | Angelica Chepiga signing in, weather +4C | All Water System ROC General | 2026-02-28
ROC | February | QVW34- Eric S on site to work on total Cl2 analyzer. Well is man/off | All Water System ROC General | 2026-02-25
ROC | February | STW12- Placed well 1 back in auto | All Water System ROC General | 2026-02-26
ROC | February | NMW15-Treated Total Cl2 residual low alarm. Well in man/off no water directed to users. | All Water System ROC General | 2026-02-28
ROC | February | YWS + NYWS NORMAL | All Water System ROC General | 2026-02-28
ROC | February | AURSBS - Activated duty 1 in preparation for MAPS to JFRS feed run | All Water System ROC General | 2026-02-28
ROC | February | MAPS- PD7 P2 Disch. Valve 1 Uncmd Close, Uncmd Stop. Pump 1 took over in duty 1. Cleared alarms. | All Water System ROC General | 2026-02-23
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-24
ROC | February | Ethan Ullalkar signing out. | All Water System ROC General | 2026-02-23
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-23
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-24
ROC | February | NMW15- Station Turbidity Hi Alarm. Rotated silicate pump duties so pump 1 in duty 1. Will monitor. 18:57- Cleared alarm. | All Water System ROC General | 2026-02-23
ROC | February | KCETDS - Aaron C working on site | All Water System ROC General | 2026-02-23
ROC | February | QVW34, Eric S is on site, working on Cl2 analyzers AURSBS, Deactivated D1 | All Water System ROC General | 2026-02-23
ROC | February | Connor Smith signing in -10C Windy | All Water System ROC General | 2026-02-23
ROC | February | YWS + NYWS Normal Connor Smith signing out | All Water System ROC General | 2026-02-24
ROC | February | KCETDS, Deactivated D1 | All Water System ROC General | 2026-02-26
ROC | February | Christian Van Beek signing in. | All Water System ROC General | 2026-02-27
ROC | February | NBW5, Placed well back to auto as per Tim H | All Water System ROC General | 2026-02-24
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-27
ROC | February | Christian Van Beek signing out. | All Water System ROC General | 2026-02-27
ROC | February | NMW12 - Alex B on site to complete work orders including JHSC checks, ammonia system inspection, chlorin system inspection, flood alarm test, chlorine leak detection test, chlorine analyzer maintenance and if there is time a silicate system inspection. | All Water System ROC General | 2026-02-24
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-24
ROC | February | MKPSSA - Total chlorine residual low and combined chlorine residual low alarms. Linear team is completing isolations around this station. Station is offline for the day and no water is being sent to distribution system. | All Water System ROC General | 2026-02-24
ROC | February | YWS + NYWS NORMAL Angelica Chepiga signing out | All Water System ROC General | 2026-02-28
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-28
ROC | February | QVW12, Donald M is finished on site | All Water System ROC General | 2026-02-24
ROC | February | Adam Button signing in | All Water System ROC General | 2026-02-26
ROC | February | KCETDS- Aaron Carlo M on site to swap network from radio to cell connection. May lose comms for a minute or two but no other impacts expected | All Water System ROC General | 2026-02-26
ROC | February | KSETDP- Patrick F will be making adjustments to duty in system and filling tower. KSETWB will be isolated to help fill tower faster and all adjustments will be reverted once the tower reaches 95% and is isolated from system. Tower level high alarms will be expected but directed to disregard by Patrick F | All Water System ROC General | 2026-02-25
ROC | February | NMW136- Combined/ treated total Cl2 lo alarms came in. Looks like dip in trends. Recovered after 3 mins alarms cleared | All Water System ROC General | 2026-02-26
ROC | February | AUW57, Joe D finished on site, will be placing the well back to auto once the cycle is done. Cl2 Pump 2/Booster 2 will be OOS for the night on site. If Cl2 Pump 1/Booster 1 has issues, contact on call | All Water System ROC General | 2026-02-26
ROC | February | HLETPR - Rick L was on site for annual calibrations. Rick has completed the calibrations and is leaving site. | All Water System ROC General | 2026-02-25
ROC | February | YWS+NYWS normal | All Water System ROC General | 2026-02-28
ROC | February | NMVCBA - Placed valve in man/open at 40 L/s | All Water System ROC General | 2026-02-28
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-25
ROC | February | YWS + NYWS Normal Christian Van Beek signing out. | All Water System ROC General | 2026-02-24
ROC | February | NMETIB - Deactivated Duty 1 to offset with NMETHW. | All Water System ROC General | 2026-02-28
ROC | February | RHRSWA- Dan B done on site both RSR MV1/2 back in local. Placed P1-4 at RHPSPA in auto | All Water System ROC General | 2026-02-26
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-26
ROC | February | MKETFA - Toronto Water (Zoran) called and informed that they will be shutting down the pump that is currently supplying MKETFA so they can test a PRV in their system. | All Water System ROC General | 2026-02-26
ROC | February | RHRSTR- Tim H called to req D1 activation for work on site. Activated D1 at 72% | All Water System ROC General | 2026-02-25
ROC | February | AURSBS, Yash S is on site, switching the Network Switch, deactivated D1 | All Water System ROC General | 2026-02-26
ROC | February | AURSBS- CL2 iso valve 1 failed to open. Reset alarm | All Water System ROC General | 2026-02-28
ROC | February | YWS+NYWS normal | All Water System ROC General | 2026-02-28
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-23
ROC | February | KCPSDS- P2 failed to start alarm. Rotated Duty 1 to P1. Reset alarm | All Water System ROC General | 2026-02-27
ROC | February | SHTP- Benson S called back and directed to placed filter 3 in backwash and monitor turbidity trends post backwash and to call back if they are still erratic AUW57- Influent free CL2 hihi alarm came in on well start up. Trends recovered after 3 mins cleared alarm | All Water System ROC General | 2026-02-27
ROC | February | NMW15- Treated free hihi alarm came in. Well not active no water directed to users. Continue to monitor trends did not recover. Placed well in man/off emailed Central water team | All Water System ROC General | 2026-02-27
ROC | February | STW12 - Place well 2 back in auto STW3 - Place well 3 back in auto | All Water System ROC General | 2026-02-26
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-25
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-26
ROC | February | Carter D Signing Out | All Water System ROC General | 2026-02-23
ROC | February | KCETFS, aaron from PCS is on site, examining the network switch, not making any changes, just observing the switch 11:34, Aaron is finished on site | All Water System ROC General | 2026-02-26
ROC | February | KSETDP - Parth P finished and leaving site. | All Water System ROC General | 2026-02-25
ROC | February | RHRSWA - Dan B on site to complete maintenance on one of the valve actuators. Dan B needs to complete a valve exercise test. Deactivated duty 1 for RHRSWA to shut down the RHPSPA pumps and placed all RHRSPA pumps in manual/off to prevent accidental activation. | All Water System ROC General | 2026-02-26
ROC | February | MKPSSA, Rob P called saying they are isolating that pumping station. That station cannot run while it is isolated. East operator are aware and also notified Travis W to confirm that it is now isolated | All Water System ROC General | 2026-02-24
ROC | February | AUW14- Building flood alarm came in. Notified Joe D on site will investigate | All Water System ROC General | 2026-02-25
ROC | February | NBW3, Influent Free Cl2 lolo, Influent dropped at start up, waited roughly 10 minutes for recovery however still residual remains lo. Placed well 3 man/off and notified Jordan B since it is his site | All Water System ROC General | 2026-02-27
ROC | February | Christian Van Beek signing in. Weather: -16C and clear. | All Water System ROC General | 2026-02-24
ROC | February | RHRSTR/VNPSCD - Johnathan from PS testing sprinkler alarm | All Water System ROC General | 2026-02-23
ROC | February | GWTP - Patrick F called to inform that the maintenance team will be on site to work on a valve in the UV system. GWTP will be offline during this work. Patrick will coordinate with Central Team to have KSTP active top fill the system during this time. Patrick will also check the Sutton Header pH high reading. | All Water System ROC General | 2026-02-24
ROC | February | NMW12,NMW136 - Kingsley M rebooting OIT QVW34 - Eric S finished at site, Ben H will return later to test run wells. Currently man/off | All Water System ROC General | 2026-02-23
ROC | February | MKRSEM - Building smoke alarm. Called Stephen B, no response. Will call again later. 16:00 Stephen B will attend site. # CMU5 W11695281 | All Water System ROC General | 2026-02-27
ROC | February | NMTKKC / NMETIB - Talha H completing work on the OIT's and directed to disregard associated historian heartbeat alarms. MAPS pD7 - Chris I on site to complete work on pump 4. | All Water System ROC General | 2026-02-25
ROC | February | NMTKKC- Chris S on site to work on UPS | All Water System ROC General | 2026-02-26
ROC | February | BVPS, Activated D1 for Tim H | All Water System ROC General | 2026-02-26
ROC | February | NMTKKC, Chris S is finished on site | All Water System ROC General | 2026-02-26
ROC | February | Dialer/DMZ Reset. Kingsley M called, resetting System, Dialer/DMZ will be down for a few minutes, he will give a call back once he is finished on his end 12:04, DMZ SCADA is back to normal 12:16, Dialer is back to normal | All Water System ROC General | 2026-02-26
ROC | February | YWS+NYWS normal | All Water System ROC General | 2026-02-26
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-25
ROC | February | AUW14- Treated free Cl2 hihi alarm came in. Continued to monitor. Ammonia dosing slowly adjusting but increased flow and alarms cleared | All Water System ROC General | 2026-02-25
ROC | February | GWTP - High lift Free chlorine residual low alarm. Plant is off, High lift pumps not running, SUETDR line is active. Notified Stephen B. Requested disregard for now and monitor. Call back if receive clear wells chlorine residual alarms. Alarms will clear when duty activated. # Consult 17:38 High lift free chlorine residual low alarm cleared. | All Water System ROC General | 2026-02-28
ROC | February | STETBR - tower level hi alarm. Placed STW1 and STW3 in auto mode. | All Water System ROC General | 2026-02-01
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-01
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-01
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-01
ROC | February | NMW15 - Noticed outstanding Station Turbidity Hi. Checked site. Noticed well is running in schedule mode. Trends indicate that turbidity levels have been higher through each run. Silicate pump 1 is currently running and the only one available. Placed well man/off and will send an email to central water team 21:50 - Called Jerry Z. to confirm compliance during this high turbidity level. Jerry directed to leave the well man/off for the remainder of the night #CONSULT | All Water System ROC General | 2026-02-01
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-01
ROC | February | KCETDS, Outlet Total Cl2 Res lolo, abnormal dip occurred, if residual doesn't recover, will contact operator | All Water System ROC General | 2026-02-01
ROC | February | GWTP, ZW6 Permeate Turbidity Fault/OOR Alarm, notified Jack P, Directed to place the filter off and Jack P will look into it consult | All Water System ROC General | 2026-02-01
ROC | February | MKRSEM, Notified Paul from Toronto to start filling the res MARS, Notified Paul to go back to normal flow for the time being | All Water System ROC General | 2026-02-01
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-01
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-01
ROC | February | STRS48 - High lift pump 1 fail to stop alarm. Checked site, SCADA shows the pump as active but no flow is registered on the flow meter. While monitoring the pump showed as deactivated. Able to clear alarm. Pump was re-assigned duty 1 automatically. | All Water System ROC General | 2026-02-01
ROC | February | JFRS - Deactivated duty 2 and then duty 1 to keep reservoir level low for the Maple to jefferson feed. | All Water System ROC General | 2026-02-01
ROC | February | STETBR - Tower Level Hi alarm came in. Placed STW12 and STW3 back to auto, as per interim | All Water System ROC General | 2026-02-02
ROC | February | YWS + NYWS Normal Christian Van Beek signing out. | All Water System ROC General | 2026-02-01
ROC | February | NBW3 - Influent Free Chlorine Lo and LoLo switch alarm came in. Checked site. This occurred on duty activation. After a few minutes, influent levels went back to optimal range. Cleared alarms and interlock after 10 mins. Well started back up. Will monitor | All Water System ROC General | 2026-02-01
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-02
ROC | February | GWTP - ZW2 34.5 KPa MIT - Press Decay Test Failed and ZW2 Shutdown alarm came in. Checked site. Called Jack P. who directed to place the train off and then initiate MIT. Jack would like a call back if the train fails again 02:41 - ZW2 Test failed and MIT Sequence aborted alarms came in. Called Jack P. who directed to place train 2 off for the night and change the duty 1 flow setpoint from 180 L/s to 160 L/s #CONSULT | All Water System ROC General | 2026-02-02
ROC | February | GWTP - Make up air unit 1 coil low temperature alarm. Shift report states that this MUA coil alarm can be disregarded. Will send email to OCO to inform. | All Water System ROC General | 2026-02-01
ROC | February | NMTKBS, Activated D1 | All Water System ROC General | 2026-02-01
ROC | February | MKRSEM - Called Toronto Water (Zoran) and requested to stop pumping to reservoir | All Water System ROC General | 2026-02-02
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-01
ROC | February | Carter Dunn Signing In, -15D/Clear | All Water System ROC General | 2026-02-01
ROC | February | GWTP - ZW4 Membrane Air Valve Failed, Membrane SetB Air Inlet Valve failed to close and train 4 shutdown alarms came in. Checked site. Plant is running. Called Jack P. who informed he will take a look on SCADA Jack informed that he has placed train 4 back online #CONSULT | All Water System ROC General | 2026-02-01
ROC | February | KSTP - Carbon Dioxide HiHi alarm came in. Value went to normal and alarm cleared on its own | All Water System ROC General | 2026-02-01
ROC | February | YWS + NYWS normal | All Water System ROC General | 2026-02-02
ROC | February | Terminating Maple to Jefferson feed and reverting changes. | All Water System ROC General | 2026-02-01
ROC | February | YWS + NYWS Normal ARPS, David from OCWA called, they are rotating pumps | All Water System ROC General | 2026-02-01
ROC | February | NBW5 - Turbidity Hi alarm came in. Checked site. Well is active. Rotated silicate pumps so that silicate pump 2 is in duty 1. Will monitor 19:20 - Turbidity levels came back to optimal range and alarm cleared | All Water System ROC General | 2026-02-01
ROC | February | NMTKKC - Outlet Total Chlorine LoLo alarms came in. Checked site. Duty is active. Level went back to optimal range right away. Alarm cleared right away | All Water System ROC General | 2026-02-01
ROC | February | MAP7 - PD7 P3 Discharge Valve 1 Uncommanded Close alarm came in. This occurred on duty activation. Duty rotated so that pump 1 and 2 are running in duty 1. Pump 3 is interlocked. 03:59 - Interlock cleared and pump 3 is now available again | All Water System ROC General | 2026-02-01
ROC | February | KSETWB -Evgeny S done reboot. Cleared historian heartbeat. Trends okay NMETIB- Both NMETHW and NMETIB draining. Notified Ben H for direction as per interim. Ben H directed to increase NMETIB D1 stop from 75 to 80 Percent and restart D1 | All Water System ROC General | 2026-02-02
ROC | February | AUPSOH- Ben H done on site and has reverted all system changes | All Water System ROC General | 2026-02-02
ROC | February | KSTKWP- Evgeny S rebooting OIT disregard historian heartbeat alarm until done | All Water System ROC General | 2026-02-02
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-02
ROC | February | NMW15- Influent free Cl2 hi alarm came in on well start up. Cleared alarm after 3 mins as trends recovered | All Water System ROC General | 2026-02-02
ROC | February | NMETIB- Total Cl2 hi/hihi and combined hi alarms came in. Tower fillings. Notified Jay G will head to site. Created CMU5 W11631082 ARPS- Sam from OCWA called back. P1 running in auto after issues with P8 were resolved #CMU5 | All Water System ROC General | 2026-02-02
ROC | February | VNRSKS - Activated duty 1 | All Water System ROC General | 2026-02-02
ROC | February | SUETDR- Talha working on OIT. Disregard Heartbeat Alarm | All Water System ROC General | 2026-02-02
ROC | February | MKRSEM- Called Toronto (Poulan) and requested two pumps on. | All Water System ROC General | 2026-02-02
ROC | February | AUPSRR- Ric L and Parth P finished onsite. Placed chlorinators and ammonia pumps back into auto. | All Water System ROC General | 2026-02-02
ROC | February | KSETWB- Evgeny S rebooting OIT. Disregard Heartbeat Alarm. | All Water System ROC General | 2026-02-02
ROC | February | GWTP- raw water total Cl2 res hihi alarm. Disregard on shift report as it recovered after 30mins cleared alarm | All Water System ROC General | 2026-02-02
ROC | February | YWS + NYWS Normal RHRSTR, Deactivated D1 | All Water System ROC General | 2026-02-03
ROC | February | SHTP- Reservoir Total Chlorine Lo Alarm. Notified Jacob M. He is onsite and just rotated reservoirs. | All Water System ROC General | 2026-02-02
ROC | February | AUW14, Placed wells 1/4 man/off so more water can be moved from AURSBS | All Water System ROC General | 2026-02-03
ROC | February | STW12- Placed well 2 man/on STW3- Placed well 3 man/on For STETBR Fill Cycle | All Water System ROC General | 2026-02-02
ROC | February | YWS+NYWS normal | All Water System ROC General | 2026-02-02
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-03
ROC | February | NBW5, Turbidity Hi alarm, well is currently off, tower is currently draining | All Water System ROC General | 2026-02-03
ROC | February | AURSBS- Activated D1 | All Water System ROC General | 2026-02-02
ROC | February | AURSBS - Activated duty 1 to fill reservoir before the Maple to Jefferson feed | All Water System ROC General | 2026-02-01
ROC | February | MAPS PD7, Placed pumps 1/3 to auto VNPS PD7, Placed pumps 1/4 to man/off | All Water System ROC General | 2026-02-01
ROC | February | NMMCBS- Downstream Pressure LoLo Alarm NMMCAD- Upstream Press Lo Alarm. Justin Q called. Aware of alarms and addressing them | All Water System ROC General | 2026-02-02
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-02
ROC | February | ARPS- Sam from OCWA called. Having issues switching pumps over from pump 7 to 8. He will contact Peel SCADA team for assistance and inform us when pump back running. 11:02- Sam called. Pump 1 running in auto | All Water System ROC General | 2026-02-02
ROC | February | MTETNL- Evgeny S rebooting OIT. Disregard Heartbeat Alarm. | All Water System ROC General | 2026-02-02
ROC | February | Connor Smith signing in -15C Clear | All Water System ROC General | 2026-02-02
ROC | February | Adeela Khan signing out | All Water System ROC General | 2026-02-02
ROC | February | Connor Smith signing out | All Water System ROC General | 2026-02-02
ROC | February | Adam Button signing out | All Water System ROC General | 2026-02-02
ROC | February | AUPSRR- Rick L and Parth P. on site for calibrations. Notified Ben H of work on site. Directed to place chem system in man/off for duration of work. MAPS PD8- Dan B done work on P1 and moving to P2 | All Water System ROC General | 2026-02-02
ROC | February | AUPSOH- Justin Q and Ben H on site shutting down P3/4 for testing. Will call back when done testing | All Water System ROC General | 2026-02-02
ROC | February | MKRSEM - Called Toronto Water (Mehdi) and requested they deactivate the pumps pushing flow to MKRSEM. | All Water System ROC General | 2026-02-01
ROC | February | RHRSTR - Deactivated duty 1. | All Water System ROC General | 2026-02-01
ROC | February | STW1/3, Placed wells 1/3 man/on MAPS PD7, Placed pumps 1/3 man/off VNPS PD7, Placed pumps 1/4 in auto | All Water System ROC General | 2026-02-01
ROC | February | AUPSOH/NMTKBS- Ben H called. Running a test involving these sites in same pressure district. Requested a call for any pressure alarms in Aurora or Newmarket | All Water System ROC General | 2026-02-02
ROC | February | STPSMR- Travis W and Joe M on site for cylinder change ARPS- Sam from OCWA (Peel) is transferring to another pump NMW15- Alex B on site to respond to turbidity issues. Created CMU5 W11630987 #CMU5 | All Water System ROC General | 2026-02-02
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-01
ROC | February | NMVCBA - Placed valve man/open at 40 L/s 00:57 - Placed valve back to auto | All Water System ROC General | 2026-02-01
ROC | February | NBW2- Eric S finished onsite. Placed well back into auto | All Water System ROC General | 2026-02-02
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-02
ROC | February | MKRSEM, Notified Toronto operator Zoran to stop pumping to the res | All Water System ROC General | 2026-02-03
ROC | February | GWTP- Train 4 membran air valve failed to open/ shutdown. Notified Patrick F. Will take a look on site | All Water System ROC General | 2026-02-02
ROC | February | AUPSRR- Gas chlorinators found in man/open. Notified Rick L. Rick L working on system no gas flow just working on position instruments MAPS PD8- Deactivated D1 for AURSBS and placed P2/3 in D1 to run as req by Dan B to ensure proper working order after PMs NBW2- Eric S on site to replace buttons on effluent free Cl2 analyzer. Placed well in man/off SUETDR- Talha H rebooting OIT Disregard historian Heartbeat alarm until done | All Water System ROC General | 2026-02-02
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-03
ROC | February | Carter Dunn Signing In, -11D/Clear | All Water System ROC General | 2026-02-02
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-02
ROC | February | Initiating changes for Maple to Jefferson Feed | All Water System ROC General | 2026-02-01
ROC | February | BLETNL, Activated D1 | All Water System ROC General | 2026-02-02
ROC | February | AUPSOH- Yash S working on OIT. Disregard Heartbeat Alarm. 14:50- Completed | All Water System ROC General | 2026-02-02
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-01
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-01
ROC | February | Adeela Khan signing in. Weather: -11C and partly cloudy | All Water System ROC General | 2026-02-01
ROC | February | QVETQS - System Pressure Lo alarm came in. Checked site. Duty for NMETHW just deactivated and QVW12 shut down. Trends indicate a quick dip and comes back to optimal range. Alarm cleared | All Water System ROC General | 2026-02-02
ROC | February | NMETHW, Activated D1 to help offset the towers | All Water System ROC General | 2026-02-01
ROC | February | HLW2 - Downstream Pressure Hi alarm came in. Checked site. Duty is still active. Lowered flow setpoint to 15 L/s as per shift report. Downstream pressure went back to optimal range and alarm cleared | All Water System ROC General | 2026-02-02
ROC | February | QVW12- William M onsite for chlorine cylinder change | All Water System ROC General | 2026-02-02
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-02
ROC | February | MAPS PD8- Dan B on site for PMs req P1 in man/off. Placed P1 in man/off | All Water System ROC General | 2026-02-02
ROC | February | QVW12- Gerrick from Ferguson onsite for generator work. Disregard any generator alarms. | All Water System ROC General | 2026-02-02
ROC | February | KSETWB, KSETWP, MTETNL- Evegeny S working on OITs. Disregard Heartbeat Alarms. | All Water System ROC General | 2026-02-02
ROC | February | ANMCBL- Tyler Z on site for sump pump work | All Water System ROC General | 2026-02-02
ROC | February | QVW34- Eric S onsite with William M working on treated analyzer. Wells are manual and local off 10:35- Finished onsite. | All Water System ROC General | 2026-02-02
ROC | February | Adam Button signing in | All Water System ROC General | 2026-02-02
ROC | February | VNRSKS- Deactivated D1 MAPS PD7- Placed all pumps in man/off VNPS PD7- Placed P1/4 in auto | All Water System ROC General | 2026-02-02
ROC | February | KSTKWP- Eric S onsite working on chlorinator 1. 11:27- Finished onsite. | All Water System ROC General | 2026-02-02
ROC | February | AURSBS- Activated D1 | All Water System ROC General | 2026-02-02
ROC | February | AUPSRR- RSR outlet total/Combined Cl2 lo alarms outstanding. Notified Rick L. Should be in calibration mode. Rick L will look into it | All Water System ROC General | 2026-02-02
ROC | February | Angelica Chepiga signing out | All Water System ROC General | 2026-02-21
ROC | February | NMETIB- Activated duty | All Water System ROC General | 2026-02-21
ROC | February | NMW136- Influent Free Chlorine HiHi. Value recovered. Cleared alarm. | All Water System ROC General | 2026-02-21
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-21
ROC | February | YWS + NYWS Normal Adeela Khan signing out | All Water System ROC General | 2026-02-13
ROC | February | JFPS- VC UPS ATS Source S2 (Line), RES UPS ATS Source S2 (Line), WPS UPS ATS Source S2 Line) Not OK Alarm. Alarms Cleared. BVPS- Pump 4 Uncommaded Stop, Pump 4 Disch Vlv 1 Failed to Open, Pump 1 Disch Vlv 1 Failed to Open. Deactivated duty and cleared alarms. RHPSPA- Hydro Power Fail. Alarm cleared | All Water System ROC General | 2026-02-15
ROC | February | BLW34-Well 3 Percent Declined LoLo Alarm. Trending shows Well 3 Performance dropping to a negative value last several cycles. Placed well man/off. Alarm cleared on its own after well turned off. Will email Patrick F. 03:40- Influent Free CL2 Res LoLo. Interlocked Well. Well was already man/off | All Water System ROC General | 2026-02-15
ROC | February | SHTP- KMNO Pump 1 Leakage Alarm. Pump 1 Fault Alarm. Pump 2 rotating in and out of duty 1. Notified Cole W. He will take a look. 05:00- Cole W will attend site W11664772 CMU5 | All Water System ROC General | 2026-02-15
ROC | February | AUW14 - Yash S. called back to inform that he will email Danielle M. of these missing trends but wanted to know if this can be resolved on Monday. Requested if Evgheny S. is able to backfill the data. Yash will speak to Evgheny | All Water System ROC General | 2026-02-20
ROC | February | MKRSEM - Reservoir Level Lo alarm came in. Called Toronto Water (Zoran) and requested to start two pumps | All Water System ROC General | 2026-02-20
ROC | February | MAP8 - Suction Header Free Chlorine Residual LoLo alarm. Dwyane L. informed that this alarm can be disregarded | All Water System ROC General | 2026-02-20
ROC | February | NMETIB- Deactivated Duty 1 to offset with NMETHW NMVCBA/NMVCIB - Reverted flow setpoint changes | All Water System ROC General | 2026-02-20
ROC | February | NMTKKC- Jay G placing staion back on utility power. Placing chem pumps in man/off andw ill be monitoring issues with comms to Newmarket wells. Jay G and Ian W will monitor the switchover. | All Water System ROC General | 2026-02-10
ROC | February | MKRSEM, Notified Zoran to stop pumping to the res | All Water System ROC General | 2026-02-12
ROC | February | NMETIB- Activated duty | All Water System ROC General | 2026-02-15
ROC | February | YWS + NYWS Normal Connor Smith signing out | All Water System ROC General | 2026-02-15
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-15
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-16
ROC | February | STW12/3- Placed Well 2/3 in man/on as per interim | All Water System ROC General | 2026-02-16
ROC | February | HLW1/2- HLW1/2 to HLETYS comm alarm came in. Cleared upon acknowledgment. Trends okay | All Water System ROC General | 2026-02-16
ROC | February | GWTP - Patrick F working on UV system | All Water System ROC General | 2026-02-12
ROC | February | Angelica Chepiga signing in | All Water System ROC General | 2026-02-10
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-17
ROC | February | VNRSKS - Deactivate duty 1 nearing stop VNP7 - Place pumps 2 & 3 back in man/off MAP7 - Place pumps 1-3 back in auto | All Water System ROC General | 2026-02-16
ROC | February | NMW136- Kyle R on site to disconnect well 13 motor. Alex B also on site to isolating well 13 ARPS- Martin from Peel called to notify ROC about PCS upgrades on their end | All Water System ROC General | 2026-02-17
ROC | February | QVW12 - Artour L on site, connecting generator, disregard alarms. | All Water System ROC General | 2026-02-10
ROC | February | Adam Button signing out | All Water System ROC General | 2026-02-10
ROC | February | MKRSEM - Called Toronto Water (Paul) and requested to stop pumping to reservoir | All Water System ROC General | 2026-02-11
ROC | February | yws + nyws normal | All Water System ROC General | 2026-02-11
ROC | February | Christian Van Beek signing out. | All Water System ROC General | 2026-02-10
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-10
ROC | February | VNPS- Pre injection total Cl2 hi alarm came in. Spike looks higher than normal and not recovering. Notified Tim H who will verify with grab TMC 317- Called Metro spoke with Mehdi to notify that ARPS is back online and returned flow to normal | All Water System ROC General | 2026-02-11
ROC | February | QVW34- P4 VFD fault and Estop. Called Will M. Maintenance Ops on site replacing motor on P4 | All Water System ROC General | 2026-02-10
ROC | February | MAP8- Suction header com. chlorine residual Hi alarm. As per Dwayne L and Tim H. Suction header is Isolated until further notice. Tim H requested disregard MAP8 Suction header CL2 and PIT alarms. # Consult | All Water System ROC General | 2026-02-20
ROC | February | KCPSDS- Comm fail. Ack/reset. Alarm cleared right away. Trends okay | All Water System ROC General | 2026-02-20
ROC | February | KSETDP - Tower outlet flow fault alarm, ET isolated, site offline. | All Water System ROC General | 2026-02-20
ROC | February | YWS + NYWS NORMAL | All Water System ROC General | 2026-02-21
ROC | February | Angelica Chepiga signing out | All Water System ROC General | 2026-02-18
ROC | February | RHRSWA - Power restored, Historian Heartbeat- alarm notified Ian W, he will check SCADA. | All Water System ROC General | 2026-02-10
ROC | February | YWS + NYWS NORMAL | All Water System ROC General | 2026-02-20
ROC | February | STPSMR, Pump 1/3 VFD Fault, Notified Dan Z, she is heading to site CMU5: W11674045 | All Water System ROC General | 2026-02-18
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-19
ROC | February | MARS - High level alarm. Deactivated RHRSTR duty 1 to stop the BVPS flow. | All Water System ROC General | 2026-02-19
ROC | February | Adam Button signing out | All Water System ROC General | 2026-02-12
ROC | February | NMETIB - Activated D1 to offset with NMETHW. | All Water System ROC General | 2026-02-12
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-16
ROC | February | JFRS - WPS Gen xfer switch to hydro power, ATS source not ok, RES UPS source 2, WPS 3 & 4 failed to start, able to reset alarms except pump 2 & 4 related alarms as they are unable to came back on. Generator not running. Informed Jerry Z, will head to site CMU = 11667801 RHPSPA - Hydro power failure, suction pressure hihi. Spike in pressure but came back within range. VNPSCD - Post-inj comb hihi, chlorine system failure. Alarms came in as BVPS shut down suddenly. Readings came back within range after spike. Informed Jerry Z as well as critical alarms and able to clear BVPS - pumps uncmd stop. Able to clear and after some time pumps able to run without issue. | All Water System ROC General | 2026-02-16
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-16
ROC | February | HLETYS - Post-injection combined chlorine lo. Value within range and alarm cleared | All Water System ROC General | 2026-02-17
ROC | February | MTELNL - Outlet free chlorine hi, reached hihi level in reading. Sudden spike as earlier but no signs of reading coming back doen. Activated duty 1 to direct water to tower. Informed Patrick F, will look into issue Consult | All Water System ROC General | 2026-02-17
ROC | February | MARS - Low level alarm. Called Toronto Water (Paul) and requested to increase flow to reservoir | All Water System ROC General | 2026-02-10
ROC | February | AURSBS - Deactivated duty 1 | All Water System ROC General | 2026-02-10
ROC | February | JFPS- Tim H placed pump 2 into duty 1. Requested to switch pump 3 into duty 3 and back into auto. | All Water System ROC General | 2026-02-11
ROC | February | MAP8 - Suction Header combine chlorine residual HiHi alarm. Disregard alarm as per Tim H. Suction Header is isolated until further notice. | All Water System ROC General | 2026-02-21
ROC | February | MKRSEM - Called Toronto water (Zoran) and requested stop filling Res. | All Water System ROC General | 2026-02-21
ROC | February | YWS + NYWS NORMAL | All Water System ROC General | 2026-02-21
ROC | February | RHRSTR - Deactivated Duty 1. | All Water System ROC General | 2026-02-21
ROC | February | YWS + NYWS NORMAL | All Water System ROC General | 2026-02-21
ROC | February | VNRSKS - Activated duty 1. | All Water System ROC General | 2026-02-21
ROC | February | Adam Button signing in | All Water System ROC General | 2026-02-19
ROC | February | VNRSKS - Swapped supply pumps to two MAPS pumps. | All Water System ROC General | 2026-02-19
ROC | February | STETBR - Tower hi level alarm. Placed STW12 and STW3 in auto mode. | All Water System ROC General | 2026-02-19
ROC | February | YWS + NYWS Normal Carter D Signing Ouit | All Water System ROC General | 2026-02-13
ROC | February | RHPSWA - Power restored, cleared all alarms. | All Water System ROC General | 2026-02-10
ROC | February | STW12, STW3- Placed wells back into auto | All Water System ROC General | 2026-02-11
ROC | February | STPSMR- Lo Cl2 effluent alarm came in on dialer. Travis W on site sampling and residual recovered. Notified Travis W no SCADA alarm came in for issue | All Water System ROC General | 2026-02-11
ROC | February | HLW2, Stephen B is leaving site, well 2 will be man/off for the night | All Water System ROC General | 2026-02-10
ROC | February | SHTP- Cole W directed to placed sample pump 2 in man/on and will Cole W will clear alarm in a few minutes 12:35- SHTP- Cole W req CMU5 and will attend site later this afternoon. Analyzer still working correctly but fault will not clear. Created CMU5 W11667765 12:49- SHTP- Reservoir total Cl2 lolo alarm came in. Notified Cole W. Directed to swap sample pumps again and verify if dosing is in manual for chlorinators. Swapped sample pumps and dosing is in manual. Cole W ill atternd site #CMU5 | All Water System ROC General | 2026-02-16
ROC | February | STW3 - Influent/effluent chlorine residual Hi alarms, Joe M will check SCADA. | All Water System ROC General | 2026-02-18
ROC | February | RHMCMD- Valve 1/2 Fault outstanding. Valves in manual. Valve 1 is showing 3 percent open with normal flow. Notified Rob P of outstanding alarms after power fails across Richmond hill and Vaughan. Rob P will consult Linear team and notify ROC of further actions | All Water System ROC General | 2026-02-10
ROC | February | HLETYS - Stephen B requested to activate Duty 1. | All Water System ROC General | 2026-02-13
ROC | February | AUPSRR - Donald M performing w/o on site including: Chlorine analyzers maintenance, chem scan maintenance, testing ammonia flood alarm. | All Water System ROC General | 2026-02-10
ROC | February | Connor Smith signing in 2C Clear | All Water System ROC General | 2026-02-21
ROC | February | YWS + NYWS Normal Connor Smith signing out. | All Water System ROC General | 2026-02-21
ROC | February | NMW12 - Silicate Pump 1 Failed to Start alarm came in. Checked site. Wells are running. Silicate pump 2 rotated to duty 1. Alarm cleared. Will monitor | All Water System ROC General | 2026-02-21
ROC | February | AUW57- Influent Free Chlorine HiHi Alarm. Value recovered. Cleared alarm. | All Water System ROC General | 2026-02-21
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-22
ROC | February | STW12- Placed well 1 man/on STW3 - Placed Well 3 man/on | All Water System ROC General | 2026-02-11
ROC | February | 145 Harry Walker Parkway Server Room- Talha H accessing SCADA Server Room with badge and access code | All Water System ROC General | 2026-02-12
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-11
ROC | February | GWTP - Patrick F on site to complete a manual backwash of GAC 1. | All Water System ROC General | 2026-02-17
ROC | February | BLW34 -Kyle C and contractors finished on site. | All Water System ROC General | 2026-02-18
ROC | February | AUW57 - Station Turbidity Hi alarm came in. Turbidity levels kept rising after 12 mins. Rotated silicate pumps so that silicate pump 2 is in duty 1. Will monitor. 21:00 - Levels came back to optimal range and alarm cleared 02:23 - Station Turbidity Hi alarm came back in with silicate pump 1 in duty 1 again. Rotated silicate pumps so that pump 2 is in duty 1. Placed silicate pump 1 manual/off 05:15 -Station Turbidity HiHi alarm came in. Placed well man/off. Confirmed with Jerry Z. | All Water System ROC General | 2026-02-10
ROC | February | RHPSPA, JFPS, RHAMF - Site hydro power fail across these sites. Likely a blip as the generators did not run and alarms cleared right away RHAMF - Odour Control system offline alarm came in. Checked site. Both fans are still running. Alarms cleared after 2 mins | All Water System ROC General | 2026-02-10
ROC | February | JFPS- Lee F finished onsite. Requested to leave pump 2 man/off. Can run in emergency. | All Water System ROC General | 2026-02-11
ROC | February | MARS - Changed low level alarm setpoint from 60% to 55%. | All Water System ROC General | 2026-02-17
ROC | February | QVW12 - Artour L called, transferred site to station generator. Man/started Well 1 pump for test. | All Water System ROC General | 2026-02-10
ROC | February | STW12/STW3 - Place well 2 & 3 back in auto | All Water System ROC General | 2026-02-17
ROC | February | SHTP- Highlifts interlocked due to lolo reservoir level. High lifts were called for due to F2 backwash status drawing down high lifts. F2 coming out of backwash notified Jake M of interlock. Jake M cleared alarms on site. Plant will be shut down soon for PCS work | All Water System ROC General | 2026-02-12
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-21
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-21
ROC | February | MKRSEM - Reservoir 1 Level Lo alarm came in. Called Toronto Water (Zoran) and requested 2 pumps on 04:37 - Called Toronto Water (Mehdi) and requested to stop pumping to reservoir | All Water System ROC General | 2026-02-21
ROC | February | VNRSKS - Dave T on site for flood alarm test and health and safety inspection. | All Water System ROC General | 2026-02-10
ROC | February | QVW12, Kyle R on site working on Well 2 failed to start issues | All Water System ROC General | 2026-02-18
ROC | February | AUW14 - Joe D cleaning chlorine analyzers, turbidity meter and running generator. | All Water System ROC General | 2026-02-18
ROC | February | STETBR, Eric S on site working on the Cl2 analyzer KSTP, Jerry Z on site, cleaning the Cl2 analyzers | All Water System ROC General | 2026-02-18
ROC | February | NMW15, Eric S is finished on site AUW14, Joe D is finished on site | All Water System ROC General | 2026-02-18
ROC | February | Angelica Chepiga signing in,weather +2C | All Water System ROC General | 2026-02-20
ROC | February | SHETCS - Eric S working in Hypo pumps. | All Water System ROC General | 2026-02-10
ROC | February | AUW14 - Ammonia pump 1 fault alarm at duty stop. | All Water System ROC General | 2026-02-12
ROC | February | QVW34 - combined chlorine hihi, came back within range shortly | All Water System ROC General | 2026-02-22
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-22
ROC | February | MARS - TO (Mehdi) pushing higher flow | All Water System ROC General | 2026-02-22
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-22
ROC | February | NMTKKC - Ammonia Tank 2 Level HiHi alarm came in. Checked site. Noticed that the trends did not indicate any spike. Ammonia tank level back at optimal range and alarm cleared | All Water System ROC General | 2026-02-22
ROC | February | MAPS PD7 P2 disch valve uncomm close and P2 uncomnd stop alarms came in. Able to clear alarms VNPS- Post injection total Cl2 hi alarm came in. Reset after 3 mins after residuals recovered | All Water System ROC General | 2026-02-17
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-22
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-23
ROC | February | STW3- Joe M on site to work on analyzers. Lo/hi temp alarms. Will be testing Cl2 leak alarm later but will call back to confirm 10:59- STW3- Joe M testing Cl2 leak alarm | All Water System ROC General | 2026-02-12
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-18
ROC | February | HLW2 - Treated total chlorine , combine chlorine residual low alarms. Well 2 duty not active, no water directed to users. Chlorine residual value recovered, alarms cleared. | All Water System ROC General | 2026-02-18
ROC | February | JFPS - Tim H headed to site. | All Water System ROC General | 2026-02-17
ROC | February | QVW34- Tyler Z on site working on generator | All Water System ROC General | 2026-02-19
ROC | February | YWS+NYWS normal | All Water System ROC General | 2026-02-12
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-13
ROC | February | MAPS - Tim H and Dan B on site troubleshooting PD7 pumps. | All Water System ROC General | 2026-02-18
ROC | February | VNRSKS- Lee F working on eyewash , disregard alarm for now. | All Water System ROC General | 2026-02-18
ROC | February | GWTP, Patrick F on site working on all Turbidity Analyzers | All Water System ROC General | 2026-02-18
ROC | February | ARPS - David from OCWA notified OP performing maintenance on Total and free ammonia analyzers. | All Water System ROC General | 2026-02-18
ROC | February | ARPS - David from OCWA called, rotating pumps from Pump 1 to Pump 2. | All Water System ROC General | 2026-02-18
ROC | February | STW12, STW3 - Man/started pumps 1 and 3 for STETBR fill cycle. ok with Joe M | All Water System ROC General | 2026-02-18
ROC | February | NMETIB- Activated D2 to offset from NMETHW as per shift report | All Water System ROC General | 2026-02-19
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-20
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-20
ROC | February | AUPSRR - Post injection free chlorine hihi alarm. Checked site, trending shows a spike of the post injection free chlorine reading which returned to normal range within one reading interval. reset alarm. SHTP - Well pump 2 uncommanded start alarm. Checked site, plant is not active. Well pump 2 flow recently stopped. Cleared alarm. NMETIB - Inlet flow hi alarm. Checked system, NMVCBA flow is above setpoint. Trending shows the valve tried to increase flow to reach the setpoint but opened too much. Will monitor valve to ensure it returns to the flow setpoint. | All Water System ROC General | 2026-02-20
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-20
ROC | February | Initiating MAPS to JFRS feed run - Placed KCPSDS pumps man/off - Placed VNPS PD8 and MAPS PD8 pumps man/off - Placed VC MV3 into man - Placed AURSBS Res MV4 to man and close - Man/start pump 3 at MAPS 02:40 - Reverted all changes | All Water System ROC General | 2026-02-23
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-23
ROC | February | AURSBS - Activated duty 1 YWS + NYWS Normal | All Water System ROC General | 2026-02-23
ROC | February | Adam Button signing in | All Water System ROC General | 2026-02-12
ROC | February | STRS48- Joe M on site to run generator and clean Cl2 analyzers NMW15- Yash S on site for network switch. Placed well in man/off | All Water System ROC General | 2026-02-19
ROC | February | NMVCBA - Flow setpoint from 40L/s to 80L/s to offset NMETIB/NMETHW NMVCIB - Flow setpoint from 80L/s to 40L/s to offset NMETIB/NMETHW | All Water System ROC General | 2026-02-20
ROC | February | NMW15 - Treated total chlorine residual Hi alarm. Adjusted chlorinator 1 dosing factor from 48 to 45%. | All Water System ROC General | 2026-02-20
ROC | February | VNPS PD7 - Pump 3 man/stop MAPS PD7 - Pump 1 to auto. | All Water System ROC General | 2026-02-20
ROC | February | NMW15, Alex B on site, testing Cl2 leak alarms MAPS PD7, Placed pumps 1/2 man/off VNPS PD7, Placed pumps 2/3 in auto | All Water System ROC General | 2026-02-19
ROC | February | VNETFD, Benson S on site doing health and safety checks and hooking up the portable generator | All Water System ROC General | 2026-02-19
ROC | February | KSTP- Eric S on site to work on Pre total Cl2 analyzer | All Water System ROC General | 2026-02-20
ROC | February | QVW34- Tyler ZJ finished on site. | All Water System ROC General | 2026-02-12
ROC | February | NBW3- Influent free Cl2 lolo switch alarm , starting in schedule mode / wells interlocked. Influent free Cl2 residual to recovered , reset alarms and restarted P7 | All Water System ROC General | 2026-02-13
ROC | February | Adeela Khan signing in. Weather: 0C and rain | All Water System ROC General | 2026-02-21
ROC | February | HLETYS- Post injection combined lo alarm came in. Tower filling and dosing. Monitored for improvement as hypo system tends to slowly increase speed as fill cycle progresses. After 20 mins hypo pump increasing speed and Combined Residual not improving. Decreased max flow of P1 from 190 to 187. Slight improvement over 10 mins decreased max flow to 185. Continued to monitor | All Water System ROC General | 2026-02-20
ROC | February | MKRSEM- Called Metro spoke with Pouran to start 2 pumps RHPSPA- Travis W on site to Gen test run, surge valve test and perform valve exercises AURSBS- CL2 iso valve1/2 failed to open. ack reset aalrms. Found Post total and free Cl2 analyzers in calibration mode. Notified Donald M. Directed to disable calibration mode on both analyzers. KSTP- Artour L on site to commission diesel tank LITs QVETQS- Jay G on site to clean outlet analyzer. Taking grab on site while working on analyzer. NMETIB- Deactivated at 72% NMETHW- Activated D1 at 48% AURSBS- Post injection free hihi switch alarm came in. Notified Donald M. Will attend site to 0 analyzer. Created CMU5 W11676555 SHTP-Jake M returned planet to normal Ops #CMU5 | All Water System ROC General | 2026-02-19
ROC | February | SHETCS -Activated Duty 1 as per Memo | All Water System ROC General | 2026-02-18
ROC | February | STPSMR - Dan Z leaving site. QVW34 - Treated total and combine chlorine Hi alarms. Adjusted chlorinator 1 dosing factor from 77 to 72%. | All Water System ROC General | 2026-02-18
ROC | February | NMTKKC - Ammonia pump 1 uncommanded stop alarm. Checked site, ammonia pump 2 rotated into duty 1 and is operating. Able to clear alarm. | All Water System ROC General | 2026-02-19
ROC | February | Carter Dunn Signing Out | All Water System ROC General | 2026-02-19
ROC | February | COTFA - PD6 and PD5 Pressure LoLo alarm came in. Checked site. Trends indicate a dip but came back within 2 mins. Alarms cleared | All Water System ROC General | 2026-02-20
ROC | February | AUW14- Yash S on site for network switch. Placed all wells man/off and will lose comms QVW34- Dan B on site for well 4 electrical work MKVCSA- PAC Control panel power fail MV general alarm and site power fail. Comms loss on site but valve in man open at 18% will continue to monitor and check for outage | All Water System ROC General | 2026-02-20
ROC | February | BVPS - Ben H shutting down BVPS to save on diesel fuel during the ALectra utility network issues. | All Water System ROC General | 2026-02-17
ROC | February | STW12- Placed Well 1 in man/on as per interim STW3- Placed Well 3 in man/on as per interim | All Water System ROC General | 2026-02-17
ROC | February | NMW15- Alex B onsite working on silicate injection points. Will have well Local off. | All Water System ROC General | 2026-02-11
ROC | February | JFPS- Tim H going to placed site back on utility | All Water System ROC General | 2026-02-17
ROC | February | HLW1 - Treated Free Chlorine Hi alarm came in. Checked site. Trends indicate a spike. but came back to optimal range. Alarm cleared after 5 mins | All Water System ROC General | 2026-02-20
ROC | February | KCPSDS- Tim H able to reset VFD not ready alarm and is heading to KCETFS to investigate potential power outage on site | All Water System ROC General | 2026-02-20
ROC | February | KCETDS- Yash S able to restore comms. after network switch. KCPSDS- P2 VFD not ready aalrm KCETFS - Inlet valve fault alarm outstanding. Called Tim H. Will investigate both outstanding alarms | All Water System ROC General | 2026-02-20
ROC | February | YWS+NYWS normal Adam Button signing out | All Water System ROC General | 2026-02-20
ROC | February | VNETFD - Site hydro failure alarm. Checked site, tower is draining and there is no rechlorination or analyzers on site. Able to clear alarms. No power outage on the Alectra outage map for the local area. Likely a power blip. VNVCIA - Site power failure alarm. Valve was closed and duty off when alarms triggered. Able to clear alarm. No power outage on the Alectra outage map for the local area. Likely a power blip. KLMCHR - Site power failure alarm. Checked site, trending shows no impact to operations, able to clear alarm. No power outage on the Alectra outage map for the local area. Likely a power blip. | All Water System ROC General | 2026-02-20
ROC | February | COTFA - Communication failures to NRETBR, MKRSMR, MKRSEM, and STPSTL. Checked sites. After 5 mins, all alarms cleared and trending is okay 12:55 - Alarms came back in. After 5 mins, alarms cleared | All Water System ROC General | 2026-02-20
ROC | February | NMVCBA- Placed valve back in auto | All Water System ROC General | 2026-02-20
ROC | February | NMETIB - Combined chlorine, total chlorine hihi. Found reading spike up suddenly during drain cycle. Activated duty to direct water to tower. Informed Jerry Z, will head to site for a grab sample CMU = 11667856 3:37 - Jerry Z requested instrumentation assistance. Informed Parth P to follow-up with Jerry Z Consult 3:44 - Combined chlorine hihi (critical) Jerry Z onsite | All Water System ROC General | 2026-02-17
ROC | February | KCETFS- Created CMU5 for Tim H W11679626 in response to power fail on site #CMU5 | All Water System ROC General | 2026-02-20
ROC | February | HLW2 - Tim H. called to inform that he is finished on site and the well is back up and running. | All Water System ROC General | 2026-02-21
ROC | February | QVW12- Treated free Cl2 hihi alarm came in. Trends recovered after 6 mins alarms cleared | All Water System ROC General | 2026-02-11
ROC | February | STW12 - Well 1 man/on STW3 - Place man/on | All Water System ROC General | 2026-02-22
ROC | February | STW3, Influent Free Cl2 hi alarm, adjusted Chlorinator 1 dosing factor from 288 to 260%, will continue to monitor | All Water System ROC General | 2026-02-10
ROC | February | STETBR - Eric S finished on site. | All Water System ROC General | 2026-02-18
ROC | February | AUW14- Missing trends during the network switch. Wells were ramping down while switch occurred. Notified Joe D. Joe D took grab at 11:45 today. Notified Yash S off missing trends. Yash S will email Danielle M to see if they can be backfilled. MAPS PD8- Dwayne L on site to work on PIT onPD8 suction | All Water System ROC General | 2026-02-20
ROC | February | KCETDS- Comm fail. Alarm cleared upon acknowledgement. Trends okay | All Water System ROC General | 2026-02-20
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-22
ROC | February | VNP7 - Activate duty 1 as MARS level high | All Water System ROC General | 2026-02-22
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-11
ROC | February | QVW34- Tyler ZJ on site to work on generator will not be transferring | All Water System ROC General | 2026-02-12
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-22
ROC | February | NMETIB - Activated duty 1 to help offset with NMETHW | All Water System ROC General | 2026-02-22
ROC | February | VNRSKS - Swapped supply pumps to MAPS. | All Water System ROC General | 2026-02-19
ROC | February | KSTKWP - Total Chlorine Lo Lo switch alarm came in. Checked site. Tank is draining. Trends indicate a dip and then comes back to optimal range. Will monitor | All Water System ROC General | 2026-02-22
ROC | February | VNP7 - Place pump 3 auto MAP7 - Place pump 1 & 2 man/off | All Water System ROC General | 2026-02-22
ROC | February | GWTP - ZW2 34.5 KPa MIT - Press Decay Test Failed and ZW2 Shutdown alarms came in. Checked site. Duty is still active. Called Joe M. who directed to leave train off for the night and alarms can be disregarded 02:08 - Joe M. called back and directed to deactivate duty 02:09 - Hi Lift Pumps Exceeded Membrane Filter Flow limit alarm came in. Joe informed that this alarm will clear once the hi lift pump shuts down #CONSULT | All Water System ROC General | 2026-02-11
ROC | February | VNPS PD7 - Pump 2 man/sop. MARS PD7 - Pump 2 to auto. | All Water System ROC General | 2026-02-20
ROC | February | NMVCBA - Placed back to auto | All Water System ROC General | 2026-02-21
ROC | February | VNPS - Deactivated duty and switched from VNPS PD7 to MAPS PD7 as RHRSTR is low 20:49 - Placed pump 1 man/off at MAPS PD7 and Placed pump 2 at VNPS PD7 in auto | All Water System ROC General | 2026-02-10
ROC | February | RHMCH7 - PAC Communication Failure alarm came in. Checked site. Trending had stopped at approximately 16:22. Checked Alectra Power which indicated a power outage still on going. ETA of restoration is approximately 19:00-21:00. Called Ian W. who informed that this PAC alarm came in due to the UPS on site running put. Ian informed that even after restoration, the alarm can be disregarded until tomorrow as this is a meter chamber #CONSULT | All Water System ROC General | 2026-02-10
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-10
ROC | February | NMW136 - Alex B finished on site. | All Water System ROC General | 2026-02-12
ROC | February | GWTP - Jack P working on fluoride system. Disregard alarms for the duration of the work. | All Water System ROC General | 2026-02-10
ROC | February | AURSBS, Donald M on site, working on chemical analyzers and chemical pumps and dosing systems, testing leak alarms QVSSSC, Rick L/Parth P on site doing annual calibrations | All Water System ROC General | 2026-02-19
ROC | February | STW3- Influent/Effluent Free Chlorine Hi Alarm. Adjusted chlorinator 1 dosing factor back down to 260% proposed setpoint. | All Water System ROC General | 2026-02-11
ROC | February | KCETDS- Combined Chlorine Lo Alarm. Analyzer back to normal next reading. Cleared alarm | All Water System ROC General | 2026-02-11
ROC | February | ARPS, Hwy50 Total Cl2 Value, Residual had a bit of a dip but then recovered, Peter from OCWA called, confirm that everything is fine on their end, the slug was pushed through, most likely caused by putting the system back to normal operation | All Water System ROC General | 2026-02-11
ROC | February | STW12, STW3 - Placed to auto. | All Water System ROC General | 2026-02-13
ROC | February | VNRSKS - Placed all pumps at VNPS PD7 man/off and placed pumps 1,2,3 at MAPS PD7 into auto | All Water System ROC General | 2026-02-13
ROC | February | AUW14- Placed wells back into auto. | All Water System ROC General | 2026-02-14
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-22
ROC | February | BVPS - Activate duty 1 | All Water System ROC General | 2026-02-22
ROC | February | MAPS PD7 - Dan B working on Pump 4. Will run pump 4 for test. VNPS PD7 Man/stopped Pump 2. | All Water System ROC General | 2026-02-18
ROC | February | MARS - Request TO (Zhoran) to go back to regular flow KCETDS - PAC communication failure. Alarm cleared quickly | All Water System ROC General | 2026-02-22
ROC | February | NMW136- Alex B on site to work on Cl2 and NTU analyzers as well as test Cl2 leak detection and valve work | All Water System ROC General | 2026-02-10
ROC | February | GWTP, ZW7 Neutralization Exceeded Dur Alarm and Tank Hi alarm, notified Joe M, he will look into it consult | All Water System ROC General | 2026-02-10
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-15
ROC | February | HLW1- Treated Free Chlorine Hi Alarm. Rotated Ammonia Pumps so that pump 2 in duty 1. Will Monitor. 23:02- Value went to normal range. Cleared alarm. Placed Ammonia Pump 1 into manual and will email West Ops | All Water System ROC General | 2026-02-15
ROC | February | HLW2- Ammonia Pump 1 Fault Alarm. Ammonia Pump 2 took over in duty 1. Cleared alarm. | All Water System ROC General | 2026-02-15
ROC | February | NMTKKC - Jason G testing flood alarm and performing chlorine and ammonia systems maintenance. | All Water System ROC General | 2026-02-18
ROC | February | MARS - Cell 1 Lo level alarm came in. Called Toronto Water (Zoran) and requested additional flow, as per interim procedure | All Water System ROC General | 2026-02-22
ROC | February | Carter D Signing In, -6D/Clear | All Water System ROC General | 2026-02-19
ROC | February | QVW12, Artour L on site with contractors, will be testing generator alarms on site with the contractors | All Water System ROC General | 2026-02-19
ROC | February | NMW12 - Influent Free Chlorine Hi and HiHi alarms came in. After 7 mins, levels came down to optimal range and alarms cleared | All Water System ROC General | 2026-02-20
ROC | February | VNETFD - Tower low level alarm. Checked site, tower level is below duty start. The duty is active but flow from Toronto is not adequate to overcome system demand. Contacted Toronto Water who activated a pump to boost flow to the East Woodbridge PD4 West area. The tower is still draining however the outlet flow is greatly reduced, and the tower will fill once evening demand eases. | All Water System ROC General | 2026-02-13
ROC | February | YWS + NYWS Normal Christian Van Beek signing out. | All Water System ROC General | 2026-02-14
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-14
ROC | February | MARS - Request TO (Mehdi) for max flow | All Water System ROC General | 2026-02-14
ROC | February | VNPS PD7- Placed P2/3 in auto MAPS PD7- Placed P1-4 in man/off | All Water System ROC General | 2026-02-11
ROC | February | NBW2- Dave T onsite for work orders including silicate system, Cl system, Cl analyzers, turbidimeter, and Cl leak detection test. | All Water System ROC General | 2026-02-11
ROC | February | NMVCBA- Placed valve manual 40L/s 00:52- Placed valve back into auto | All Water System ROC General | 2026-02-14
ROC | February | ARPS- Airport Rd Discharge Flow LoLo MARS- Called Toronto (Mehdi) to decrease flow to Maple MKRSEM- Called Toronto (Mehdi) to turn off pumps | All Water System ROC General | 2026-02-15
ROC | February | MAPS/JFRS- Reverted Maple to Jefferson Feed. | All Water System ROC General | 2026-02-15
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-15
ROC | February | VNMCBA, RHMCMD, MCMCCW,MKMCSA - Power blip, all alarms cleared. | All Water System ROC General | 2026-02-10
ROC | February | MARS- Dave T on site for Cl2 analyzer maintenance, JHS inspections and to test flood alarm | All Water System ROC General | 2026-02-10
ROC | February | NMTKKC - Header ammonia LoLo, outlet total amonia LoLo alarms, Historian heartbeat alarm, called Jason G( running gen at NMPSKC). Jason G will check. NMW12 - interlocked on NMTKKC to NMW12 commfail. Alarm cleared. NMTKKC - Historian Heartbeat alarm. Notified Ian W, he will check. | All Water System ROC General | 2026-02-10
ROC | February | NMVCBA- Placed valve in manual 20L/s | All Water System ROC General | 2026-02-20
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-21
ROC | February | NBW3- Influent Free Chlorine LoLo Alarm. Interlocked well on startup. Value recovered and cleared alarm. Well started back up in duty. | All Water System ROC General | 2026-02-21
ROC | February | NMETIB- Deactivated duty | All Water System ROC General | 2026-02-21
ROC | February | Adam Button signing in -5C Clear | All Water System ROC General | 2026-02-16
ROC | February | YWS + NYWS Normal Connor Smith signing out | All Water System ROC General | 2026-02-16
ROC | February | YWS + NWYS Normal | All Water System ROC General | 2026-02-18
ROC | February | QVW12 - Man/stopped well 1 pump, Artour L on site. | All Water System ROC General | 2026-02-10
ROC | February | KCETDS-Outlet total Cl2 res lolo alarm came in. Looks like analyzer dropped out but recovered after one reading alarm cleared | All Water System ROC General | 2026-02-20
ROC | February | AUETFC- Donald M called back tie valve is normally closed. Cleared alarm | All Water System ROC General | 2026-02-17
ROC | February | AUETAD, Donald M on site, Testing temp and doing Cl2 analyzer main | All Water System ROC General | 2026-02-18
ROC | February | NMW136, Influent Free Cl2 hihi, contacted Tyler Z who was talking to Ben H. Tyler Z will be back flushing the site | All Water System ROC General | 2026-02-10
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-15
ROC | February | Adam Button signing out | All Water System ROC General | 2026-02-11
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-14
ROC | February | SHTP- Jake M on site for step test | All Water System ROC General | 2026-02-19
ROC | February | ARPS- Discharge flow hi alarm came in. Called Peel spoke with Jason. Peel tehcnicians are working on chemical quills causing flow meter readings as all pumps are currently off. Jason Notified they will be running a pump later today as per RFS | All Water System ROC General | 2026-02-10
ROC | February | STW3, Influent Free Cl2 hi, Adjusted dosing factor from 280 to 260, will continue to monitor site | All Water System ROC General | 2026-02-13
ROC | February | STW3- Historian heartbeat alarm came in interlocking well. Notified Chris S. Will take a look on SCADA | All Water System ROC General | 2026-02-17
ROC | February | AURSBS - Ben H. is on site for work orders. This includes testing the eyewash. Ben directed to disregard all alarms until work is complete | All Water System ROC General | 2026-02-20
ROC | February | NBW5- Influent Free CL2 Lo Alarm. Value recovered. Effluent Free CL2D Lo Alarm and Effluent Free Chlorine LoLo Switch alarm came in shortly after. Well interlocked. Notified Tim H. He will attend site. Tim H requested to change Influent Lo Alarm from 1.0 to 1.5 and Effluent Lo Alarm from 0.65 to 1.0 16:54- Tim H finished onsite. He will leave well man/off for the weekend. Requested a call if needed to run in emergency. W11679721 CMU5 | All Water System ROC General | 2026-02-21
ROC | February | AUPSOH- Jerry Z on site to run generator and test hi lo temp alarm | All Water System ROC General | 2026-02-19
ROC | February | ANW23 - Res inlet free chlorine Lolo alarm, quick dip, duty recently activated, Wells interlocked. Cleared alarms, wells 2&3 pumps restarted, Res free inlet chlorine residual normal. | All Water System ROC General | 2026-02-20
ROC | February | NMW15, Eric S on site, working on influent analyzer | All Water System ROC General | 2026-02-19
ROC | February | KCPSDS - PAC Communication alarm came in and the value turned normal. Trending is okay | All Water System ROC General | 2026-02-22
ROC | February | MMW1 - Well 8 and Well 13 hi level alarms came in. Likely due to the ongoing power issues in Richmond Hill/Vaughan. Checked site. Noticed all the wells man/off. Placed well 13 and well 8 man/on. Confirmed with Rob P. who informed well 13 should be opened at 21% and well 8 open at 42% #CONSULT | All Water System ROC General | 2026-02-10
ROC | February | NRETCR - Deactivated duty 1 | All Water System ROC General | 2026-02-10
ROC | February | VNPS- Utility source 1 not available came in. Notified Tim H. Tim H req Satnam M to call him for a consult. Notified Satnam M. Will update ROC KCETDS- Yash S changing switch | All Water System ROC General | 2026-02-20
ROC | February | Angelica Chepiga signing out | All Water System ROC General | 2026-02-10
ROC | February | NMW12 - Influent Free Chlorine HiHi alarm came in. Checked site. Wells just activated 20:33 - Influent levels are back to optimal range and alarms cleared | All Water System ROC General | 2026-02-10
ROC | February | SHETCS - Jacob M running generator, testing Hi/Low temp alarms, cleaning chlorine analyzers, inspecting hypo system. | All Water System ROC General | 2026-02-12
ROC | February | KCETFS - David T running generator, testing Hi/Low level and temp alarms, cleaning chlore analyzers. | All Water System ROC General | 2026-02-12
ROC | February | STETBR- Free Cl2 lo alarm came in. Notified Joe M. Will attend site to check MTETNL- Phil D on site to work on Cl2 analyzer. Directed to disregard alarms until done | All Water System ROC General | 2026-02-17
ROC | February | Angelica Chepiga signing out | All Water System ROC General | 2026-02-12
ROC | February | Christian Van Beek signing in. Weather: -4C and clear. | All Water System ROC General | 2026-02-13
ROC | February | MKRSEM - PAC control panel power fail alarm. Cleared alarm. | All Water System ROC General | 2026-02-18
ROC | February | MKPSSA, Travis W on site, Running generator/Testing pumps and testing flood alarms. notified Toronto of this work as well, they shouldn't be impacted | All Water System ROC General | 2026-02-19
ROC | February | SHETCS - Activated Duty 1. | All Water System ROC General | 2026-02-18
ROC | February | AUW14- Yash S done on site. Placed wells 2/3 in man/on. Trends okay | All Water System ROC General | 2026-02-20
ROC | February | AUW14 - Joe D. called to inform that Yash S. is still working on cable repairs and it may cause a communication loss. Joe will place well 2/3 man/off until the work is complete | All Water System ROC General | 2026-02-20
ROC | February | Ethan Ullalkar signing out. | All Water System ROC General | 2026-02-15
ROC | February | BVPS - Danielle Z leaving site. | All Water System ROC General | 2026-02-17
ROC | February | Adeela Khan signing out | All Water System ROC General | 2026-02-22
ROC | February | VNRSKS - Swapped supply pumps to one MAPS and one VNPS pump. | All Water System ROC General | 2026-02-18
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-18
ROC | February | Angelica Chepiga signing in, weather -12C | All Water System ROC General | 2026-02-13
ROC | February | HLW2 - Ammonia Pump 1 fault alarm, Cole W will attend site. | All Water System ROC General | 2026-02-13
ROC | February | NMW15, Placed back to auto | All Water System ROC General | 2026-02-19
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-18
ROC | February | AUETFC, Joe D finished on site | All Water System ROC General | 2026-02-19
ROC | February | MKRSEM - Request Mehdi (TO) to drop both pumps | All Water System ROC General | 2026-02-17
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-17
ROC | February | MTW3 - Turbidity Fault alarm. Checked site, turbidity trending shows a small increase around the time of the fault but no abnormal trend lines. Attempted to reset alarm, will not reset. Placed well in manual/off. System has one well available to fill tower. Activated duty to determine if one well pump is sufficient. Placed well 3 manual/off. | All Water System ROC General | 2026-02-18
ROC | February | NMTKKC - Ammonia pump 1 uncommanded stop , Hypo pump 3 uncommanded stop alarms, PAC control panel door open alarm- Notified Jerry z and Ben H. As per Ben H- Ian W working on site. Called Ian W and Jason G, no response. Will call later. 13:15 Chris S working on UPS, Notified Jason G about outstanding alarms. Was able to clear alarms. | All Water System ROC General | 2026-02-13
ROC | February | NMETIB, Activated D1 | All Water System ROC General | 2026-02-13
ROC | February | Christian Van Beek signing in. Weather: 1C and clear. | All Water System ROC General | 2026-02-19
ROC | February | AUW57 - Influent Free Chlorine LoLo Switch alarm came in. Checked site. Influent level did not recover. Called Joe D. who will head to site. CMU5 Created W11664471 15:10 - Joe D. called back to inform that the chlorine cylinders were switching over and the regulator dropped. Joe D. will stay on site to monitor #CMU5 | All Water System ROC General | 2026-02-13
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-15
ROC | February | MKRSEM- Called Toronto (Mehdi) and requested pumps off | All Water System ROC General | 2026-02-16
ROC | February | STW12- Placed well 1 back into auto STW3- Placed well back into auto | All Water System ROC General | 2026-02-16
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-16
ROC | February | KCETDS - Kyle R on site to complete work orders including a heat trace inspection, sump pump inspection and damper and exhaust fan inspections. | All Water System ROC General | 2026-02-17
ROC | February | BVPS- Dan Z on site to work on analyzers and testing flood alarm | All Water System ROC General | 2026-02-17
ROC | February | VNRSKS - Deactivated duty 1 | All Water System ROC General | 2026-02-22
ROC | February | MMW1, Well 8/13 hi alarm, notified Tyler Z, directed to place wells back to manual/on as a power outage occurred and knocked them man/off RHAMF1, Fan 1/2 Faulted, Notified Jimmy from NAC, he will send his team over to the site | All Water System ROC General | 2026-02-13
ROC | February | AURSBS- Cl2 valve 1/2 failed to open alarms came in. Reset | All Water System ROC General | 2026-02-20
ROC | February | ARPS - Dereck from Peel informed they will rotate pump 1out and put pump 2 in auto duty 1. BLW3 - Duty running with well 3 active, well 3 percent declined lolo. Noticed on trend it occurs now with well 3 running reading goes into negative value | All Water System ROC General | 2026-02-14
ROC | February | STW12 - Well 1 running place man/on STW3 - Well 3 running, place in man/on | All Water System ROC General | 2026-02-14
ROC | February | MKRSEM - Request TO (Paul) to run 2 pumps | All Water System ROC General | 2026-02-14
ROC | February | BVPS- Dan Z on site inquiring if D1 can be activated at RHRSTR as power has stabilized. Instrumentation working on chlorination system on site at RHRSTR/VNPS. Notified Dan Z D1 should not be activated until they are done | All Water System ROC General | 2026-02-17
ROC | February | YWS+NYWS normal ARPS- Martin from Peel called to notify ROC that they will be transferring from P5 to P6 | All Water System ROC General | 2026-02-16
ROC | February | QVW12 - William M on site for turbidity meter maintenance and chlorine leak test. | All Water System ROC General | 2026-02-12
ROC | February | YWS + NYWS NORMAL | All Water System ROC General | 2026-02-12
ROC | February | NMVCBA - Placed valve man/open at 30 L/s | All Water System ROC General | 2026-02-20
ROC | February | STETBR- Joe M notified ROC that instrumentation was not able to attend site today and the Cl2 analyzer will be offline all night. Confirmed Joe M took a grab sample while attending earlier. | All Water System ROC General | 2026-02-17
ROC | February | YWS+NYWS normal | All Water System ROC General | 2026-02-17
ROC | February | Possible Main Break, Queensway and Bessborough, Abdula from Dispatched called saying there is a possible main break north of the intersection, after checking all pipes, the pipes belong to Georgina. Abdula informed the Georgina of their main break | All Water System ROC General | 2026-02-18
ROC | February | MAPS - Artour L. is on site for asset tagging | All Water System ROC General | 2026-02-13
ROC | February | NMTKKC - Eyewash Flow alarms came in. Checked site. Jason G. on site flushing eyewash stations | All Water System ROC General | 2026-02-13
ROC | February | Ethan U signing in Weather -4. | All Water System ROC General | 2026-02-14
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-14
ROC | February | NBW3- Influent free lolo switch alarm interlocked well. Continued to monitor reset after influent free Cl2 recovered. | All Water System ROC General | 2026-02-16
ROC | February | YWS + NYWS Normal Carter D Signing Out | All Water System ROC General | 2026-02-12
ROC | February | AUW14 - Placed pumps 3&4 and AUW5 pump back to auto. | All Water System ROC General | 2026-02-12
ROC | February | BLW3 - Patrick F finished at site. Leaving chlorinator 1 OOS for the weekend, disregard well 3 percent decline alarm. Will bring it up to team start of week | All Water System ROC General | 2026-02-15
ROC | February | RHRSTR- Deactivated duty | All Water System ROC General | 2026-02-16
ROC | February | BVPS - Pump 1 & 4 uncmd stop again. Able to clear and reset after some time pumps gradually came back. Sudden drop caused VNPSCD chlorine system failure to occur with hihi post-inj chlorine total/combined VNPSCD - Chlorine system failure, combined/total post-inj hihi after BVPS sudden stop. Informed Jerry Z RHPSPA - suction pressure hihi, pump 4 inhibited as duty 1, disch valve partially closed. Rotated pump 3 to duty 1. | All Water System ROC General | 2026-02-16
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-22
ROC | February | STETBR - Tower Level Hi alarm came in. Placed STW3 and STW1 back to auto as per inteirm | All Water System ROC General | 2026-02-22
ROC | February | MTW3 - Chlorine gas leak, scrubber running. Informed Patrick F, will head to site CMU = 11670914 | All Water System ROC General | 2026-02-17
ROC | February | MKRSEM - Request TO (Brent) to run 2 pumps | All Water System ROC General | 2026-02-17
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-17
ROC | February | Gluzen Ramos Ong signing in | All Water System ROC General | 2026-02-12
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-15
ROC | February | Connor Smith signing in -2 Cloudy | All Water System ROC General | 2026-02-15
ROC | February | AURSBS- Activated duty | All Water System ROC General | 2026-02-16
ROC | February | QVW12- William M working on chlorine analyzers. Disregard related alarms. | All Water System ROC General | 2026-02-11
ROC | February | MAPS PD7, Placed pumps 2/3 auto VNPS PD7, Placed pumps 2/3 back to man/off | All Water System ROC General | 2026-02-11
ROC | February | SHTP, Deactivated D1 to help recover the res MKRSEM, Notified Toronto operator Zoran to start filling the res | All Water System ROC General | 2026-02-11
ROC | February | NRETCR, Activated D1 | All Water System ROC General | 2026-02-12
ROC | February | MARS - Approaching high level. Called Toronto Water and requested they drop one pump. RHAMF - Generator running status alarm. Richmond Hill is suffering from power failures. Already contacted NAC regarding the VFD pump faults on site. Generator is on but the ATS is pointing to utility hydro. | All Water System ROC General | 2026-02-10
ROC | February | MMW1 - Well 8 and well 13 hi level alarms. Wells were knocked out during the most recent power blip in Richmond Hill. Activated well 8 and well 13 pumps in manual. | All Water System ROC General | 2026-02-10
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-10
ROC | February | NMPSKC - Jason G running generator, will attend NMTKKC re-chlor building after. | All Water System ROC General | 2026-02-10
ROC | February | RHPSPA- Placed all pumps in manual and started 1/2 | All Water System ROC General | 2026-02-10
ROC | February | Gluzen Ramos Ong signing out | All Water System ROC General | 2026-02-12
ROC | February | MAPS PD7- Tim H on site to trouble shoot PD7 pump lo switch alarms issues from yesterday. | All Water System ROC General | 2026-02-12
ROC | February | KSTP - CO2 adjusted pH lolo, status went to normal as reading went back within range Settl water cond level lolo. Found it dropped. Informed Patrick F, as both filters were in production at time. During call appears both fitlers changed to off. Patrick F will take a look Consult | All Water System ROC General | 2026-02-15
ROC | February | NMVCBA- Placed valve in manual 20L/s 23:58- Placed back into auto | All Water System ROC General | 2026-02-15
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-14
ROC | February | VNRSKS to COTFA Comm Alarm COTFA to MARS Comm Fail COTFA to RHRSWA Comm Fail COTFA to ROYKS Comm Fail COTFA to VNETAG Comm Fail COTFA to VNPS7 Comm Fail COTFA to VNPS8 Comm Fail JFPS to COTFA Comm Fail NRETBR to COTFA Comm Fail RHPSWA to COTFA Comm Fail All alarms Cleared | All Water System ROC General | 2026-02-14
ROC | February | RHPSPA- Activated and rotated duty and placed pumps back in auto. SHTP/ SHETCS- Power fail on both site. Notified Jacob M will check SCADA and reset alarms outstanding STPSTL- Joe M on site to run generator | All Water System ROC General | 2026-02-10
ROC | February | RHRSTR- Deactivate duty | All Water System ROC General | 2026-02-11
ROC | February | ARPS- David from Peel notified ROC they are starting 1 pump in auto in pressure mode 12:40- ARPS- Peel ammonia analyzer a alarm came in. Called Peel about alarm spoke to Masoud. They are making adjustments on their end and trying to get the residuals to stabilize before making anymore adjustments. Masoud confirmed they have done the calculations themselves to ensure proper dosing and will have ops call back within a half hour with update. 13:00-ARPS- David from Peel called back. residuals stabilized cleared alarms and P5 running in auto | All Water System ROC General | 2026-02-11
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-12
ROC | February | HLW1 - Treated free chlorine hi, wells just activated, monitored site, well free reading dropped back down | All Water System ROC General | 2026-02-14
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-15
ROC | February | MAPS PD7 - Pumps 2&3 man/off VNPS PD7 - Pumps 2&3 to auto. | All Water System ROC General | 2026-02-13
ROC | February | Angelica Chepiga signing out | All Water System ROC General | 2026-02-13
ROC | February | JFPS - Assigned P4 to Duty 1 and disabled Duty rotation. | All Water System ROC General | 2026-02-12
ROC | February | YWS + NYWS Normal NMVCBA - Adjusted flow setpoint from 40L/s to 80L/s to maintain NMETIB/NMETHW offset. NMVCIB - Adjusted flow setpoint from 80L/s to 40L/s to maintain NMETIB/NMETHW offset. | All Water System ROC General | 2026-02-13
ROC | February | NBW3 - Influent free chlorine lolo alarm. Checked site, well just activated to fill system. Trending shows the influent free chlorine dipped on well start. Rotated chlorine pump duty and waited for the influent free chlorine reading to rebound. Then placed well in auto and cleared alarms. Monitored start up. | All Water System ROC General | 2026-02-13
ROC | February | VNPSCD - Pre - injection total chlorine and combined chlorine lolo. Checked site, chemical system is currently active as RHRSTR is filling. trending shows a sudden drop of the total and combined chlorine values. Contacted Jerry Z who directed to disable to chemical system and will attend site to check the analyzer. Created CMU5#W11664539 23:28 - VNPSCD - Jerry Z called to inform he needs the assistance of on call instrumentation. Called Parth P to inform, Parth will attend site to assist Jerry. Created CMU5#W11664549 #consult #CMU5 | All Water System ROC General | 2026-02-13
ROC | February | VNPSCD - Parth P on site and requested that the duty be deactivated. Deactivated duty 1 for RHRSTR. | All Water System ROC General | 2026-02-14
ROC | February | VNETFD- Site Hydro Power Failure Alarm, Isolation Valve General Alarm. Alarms cleared KLMCHR- Site Power Failure Alarm. Alarm cleared | All Water System ROC General | 2026-02-15
ROC | February | VNETFD- Control Panel Power Failure Alarm, Isolation Valve General Alarm. Alarms cleared. | All Water System ROC General | 2026-02-16
ROC | February | MAPS PD7- Placed P2/3 in man/off VNPS PD7- Placed P2/3 in auto | All Water System ROC General | 2026-02-16
ROC | February | QVW34, Will M is on site, testing Cl2 analyzers/leak/temp alarms, directed to disregard alarms | All Water System ROC General | 2026-02-18
ROC | February | STPSMR - Travis W working on site, deactivating duty , testing chlorine leak alarm. | All Water System ROC General | 2026-02-18
ROC | February | GWTP - Patrick F backwashing GAC3. NRETBR - Jason G cleaning chlorine analyzers, testing temp alarms and eyewash alarm | All Water System ROC General | 2026-02-18
ROC | February | MKRSEM- Called Toronto water (Poulin) requested stop filling res. | All Water System ROC General | 2026-02-13
ROC | February | Carter D Signing In, -3D/Snowing YWS + NYWS Normal | All Water System ROC General | 2026-02-11
ROC | February | Angelica Chepiga signing in, weather -9C | All Water System ROC General | 2026-02-12
ROC | February | ARPS - David from OCWA called, rotating pumps from Pump 5 to Pump 6. | All Water System ROC General | 2026-02-12
ROC | February | 13:50 BLW12 - Kyle C restarting OIT, Disregard Historian Heartbeat alarm. 14:14 Kyle C completed work. | All Water System ROC General | 2026-02-12
ROC | February | NMTKKC - Jason G and Ian W working on site, requested Man/off all chemical pumps. Disregard alarms. | All Water System ROC General | 2026-02-10
ROC | February | KSTP- Eric S onsite for turbidimeter troubleshooting. 14:24- Finished onsite | All Water System ROC General | 2026-02-11
ROC | February | KCETDS- Activated D1 | All Water System ROC General | 2026-02-11
ROC | February | AUW57- John D rebooting OIT. Disregard Heartbeat Alarm | All Water System ROC General | 2026-02-11
ROC | February | VNPS PD7 - Pumps 2&3 to auto. MAPS PD7 - Pumps 1&2 man/off | All Water System ROC General | 2026-02-12
ROC | February | RHRSWA- Pac Panel died on site lossing comms. RHPSPA interlocked due to comm fail/ Notified Tim H. Time H req consult with Ian W to troubleshoot. Notified Ian W to call Tim H. MKRSMR- Called Metro spoke with Pouria activated D1 | All Water System ROC General | 2026-02-10
ROC | February | KCETDS- Outlet Total CL2 Res LoLo Alarm. Recovered next reading. Cleared alarm | All Water System ROC General | 2026-02-15
ROC | February | ARPS - Peel informed they are rotating pump 4 off and placing pump 5 auto duty 1 | All Water System ROC General | 2026-02-15
ROC | February | QVW12, Influent Free Cl2 hihi alarm, abnormal spike occurred. After 1 reading, residual came back down to normal levels | All Water System ROC General | 2026-02-18
ROC | February | QVW34, Ben H is heading to site to reset the wells CMU: W11674030 | All Water System ROC General | 2026-02-18
ROC | February | NMW136 - Alex B and Christian B on site, working on silicate and ammonia systems, disregard alarms for the duration of the work. | All Water System ROC General | 2026-02-12
ROC | February | RHRSTR, MKRSMR, MKRSEM - not trending. Notified Chris S. | All Water System ROC General | 2026-02-12
ROC | February | NMETHW - Deactivate duty 1 as Ivsbridge remains active and keep offset | All Water System ROC General | 2026-02-17
ROC | February | NMETIB- Parth P done on site Cl2 analyzer reading properly | All Water System ROC General | 2026-02-17
ROC | February | GWTP- Patrick F on site to test chemical leak alarms and flood alarms | All Water System ROC General | 2026-02-10
ROC | February | NMW15 - PAC commfail. PCS working on NMETYS to NMW15 communication as per Alex B. | All Water System ROC General | 2026-02-10
ROC | February | ANW23 - Pre-Inj free chlorine lo. Noticed trend dropping in reading slowly. Informed Cole W, will head to site CMU = W11664823 | All Water System ROC General | 2026-02-15
ROC | February | BVPS 1 & 4 uncmd stop came back in with power blip in area. Able to clear alarm and pumps were able to gradually come back in service JFRS - VC UPS ATS source and source S2 line not okay related alarms came back in. RES/PS UPS ATS source 2. RES CP PWR failure. Alarms able to clear but pumps remain unable to run RHPSWA - Control panel power failure RHPSPA - Suction pressure hihi, able to clear after spike VNVCIA - PAC control panel power failure, Chris S called back informing AUMCBR will remain outstanding over night. VNVCIA is on battery power and will lose comms within 4 hours as power failure remains outstanding. Infomred Harsh P as well of scenario, will leave for morning Consult | All Water System ROC General | 2026-02-16
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-16
ROC | February | SHTP- Changed duty setpoints from 15/45% to 30/80% Interim Procedure | All Water System ROC General | 2026-02-11
ROC | February | YWS + NYWS NORMAL | All Water System ROC General | 2026-02-18
ROC | February | MKRSMR- Called Metro spoke with Peter to stop pumping to reservoir | All Water System ROC General | 2026-02-10
ROC | February | McCowan Road and 14th Avenue - Dwayne L. called to inform that he will be responding to a potential watermain break and requested a CMU5. Harsh P. and Peter T. will also be responding. CMU5 Created W11664363 #CMU5 | All Water System ROC General | 2026-02-13
ROC | February | MARS- Called Toronto (Mehdi) and requested increase flow | All Water System ROC General | 2026-02-11
ROC | February | VNPS- Ric L and Parth P onsite for annual calibrations. | All Water System ROC General | 2026-02-11
ROC | February | AUW14, Treated Free Cl2 hihi alarm, trends show an abnormal spike occurred, if recovery doesn't happen within 2 readings, will take further action | All Water System ROC General | 2026-02-13
ROC | February | Carter D Signing Out | All Water System ROC General | 2026-02-18
ROC | February | YWS+NYWS normal | All Water System ROC General | 2026-02-16
ROC | February | GWTP- ZW3 memb tank level hi alarm came in. Notified Patrick F. Directed to disregard as tank should drain after a few mins but call for hihi #consult | All Water System ROC General | 2026-02-16
ROC | February | VNRSKS- Activated D1 | All Water System ROC General | 2026-02-17
ROC | February | MKRSEM- Called Toronto (Mehdi) and requested pumps on. | All Water System ROC General | 2026-02-15
ROC | February | Richmond Hill - Followed up with Joanna from Alectra regarding power blips in area. Still no update of restoration as crew continues to work on resolving issue | All Water System ROC General | 2026-02-17
ROC | February | SHTP - Reservoir level hi alarm. Activated SHETCS duty 1 to draw down the reservoir. | All Water System ROC General | 2026-02-18
ROC | February | MKRSEM - Called Toronto Water (Paul) and requested they deactivate the pumps pushing flow to MKRSEM. MTETNL - Site to site communications fail with MTW12. The alarmn ahs interlocked MTW2 which was active when the alarm triggered. Placed MTW2 in manual to prevent immediate start up when alarm clears. Alarms reset. Will place the well in auto in ten minutes. | All Water System ROC General | 2026-02-19
ROC | February | KSTP - Raw water turbidity fault alarm. Checked site, plant is not active at the moment. No flow being generated by low lift pumps. Disregard alarm as per the shift report. | All Water System ROC General | 2026-02-19
ROC | February | NMTKKC - Sean P on site to cut power to the re-chlor facility on site to complete maintenance on the header system. | All Water System ROC General | 2026-02-17
ROC | February | AURSBS - Activated duty 1 to draw down MARS. | All Water System ROC General | 2026-02-19
ROC | February | SHTP- Placed well 2 in man/off as per interim. Confirmed with Tim H before shutting down | All Water System ROC General | 2026-02-19
ROC | February | ARPS, David from OCWA called, he is switching their D1 pump from pump 4 to pump 5 | All Water System ROC General | 2026-02-19
ROC | February | NMW12- Christian B and Alex B is on site to work on silicate system and backflush VNPS- Rick L and Parth P done on site STETBR- Joe M was not able to get analyzer back online and Instrumentation will be attending site to trouble shoot | All Water System ROC General | 2026-02-17
ROC | February | SHTP- Treated Water Turbidity Fault. Notified Cole W. Can disregard for the night. Requested a call if it stops trending. CONSULT | All Water System ROC General | 2026-02-16
ROC | February | AUMCBR - PAC communication failure. Loss of trends high priority. Informed Chris S who will look into it CMU = 11667808 | All Water System ROC General | 2026-02-16
ROC | February | BLETNL - Activate duty 1 YWS + NYWS Normal | All Water System ROC General | 2026-02-17
ROC | February | STW12 - Place well 1 back in auto STW3 - Place well 3 back in auto | All Water System ROC General | 2026-02-18
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-18
ROC | February | BLW12 - Phil D cleaning chlorine analyzers and turbidity meter, cleaning injection points and running generator. | All Water System ROC General | 2026-02-18
ROC | February | SHETCS, Kevin W doing a network switch, once tower hits D1 stop, he will do his work. Notified Darrick Simm will attend site if issues arise. 12:08, Kevin W is finished his work 12:09, Adjusted D1 start from 45% to 60% and D1 stop from 15 to 20% | All Water System ROC General | 2026-02-18
ROC | February | ARPS - Airport rd pressure LoLo alarm, confirmed all pumps Local/off for ARPS shutdown. | All Water System ROC General | 2026-02-10
ROC | February | Ethan Ullalkar signing out. | All Water System ROC General | 2026-02-18
ROC | February | STPSMR- Travis W on site for Cl2 analyzer maintenance | All Water System ROC General | 2026-02-12
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-13
ROC | February | JFRS - VC UPS ATS source S2 (line, UPS ATS source S2, WPS Gen xfer switch hydro power. Alarm status switched to normal and alarms cleared. No pumps running at the time. | All Water System ROC General | 2026-02-14
ROC | February | NBW5- Turbidity hi outstanding. Rotated from silicate P 1 to silicate P2. Will monitor for improvement Placed silicate P 1 in man/off and disabled all stop duty rotation | All Water System ROC General | 2026-02-12
ROC | February | ARPS - David from OCWA called, rotating pumps from Pump 6 to Pump 1. | All Water System ROC General | 2026-02-13
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-17
ROC | February | MKRSEM, Notified Toronto operator Zoran to start filling the res | All Water System ROC General | 2026-02-12
ROC | February | NMTKKC - Ammonia pump 1failed to start, notified Jason G. He is on site, will check. | All Water System ROC General | 2026-02-18
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-13
ROC | February | Ethan U signing in Weather 2. | All Water System ROC General | 2026-02-16
ROC | February | JFRS - Jerry Z finished at site and able to reset pumps. GWTP - Train 5 membrane pressure lo, value went back to normal and cleared upon acknowledging alarm | All Water System ROC General | 2026-02-16
ROC | February | QVW34- Treated total and / combined Cl2 lo alarms came in. Wells not active Checked trends looks like analyzer dropped out. Continued to monitor and cleared alarms as residuals recovered after 6 mins no water directed to users | All Water System ROC General | 2026-02-16
ROC | February | AUETFC- Tie valve uncommanded close alarm came in. Notified Donald M. Will investigate and update ROC | All Water System ROC General | 2026-02-17
ROC | February | STW12- Comm alarm to STETTL. Trends okay cleared alarm ANW23- RSVR inlet free Cl2 lolo alarm came in. Checked trends. Residual dropped suddenly. Reset alarms. | All Water System ROC General | 2026-02-11
ROC | February | VNPS PD7, Placed pumps 2/3 man/on VNPS PD8, Placed pumps 2/3 man/on Lee F Preforming Pump vibration testing on pumps 2/3 at VNPS PD7/PD8 | All Water System ROC General | 2026-02-19
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-19
ROC | February | YWS + NYWS Normal MKRSEM - Called Toronto Water (Paul) and requested they deactivate the pumps pushing flow to MKRSEM. | All Water System ROC General | 2026-02-19
ROC | February | AURSBS - Activated duty 1 to draw down MARS. | All Water System ROC General | 2026-02-20
ROC | February | Adeela Khan signing in. Weather: -15C and sunny | All Water System ROC General | 2026-02-13
ROC | February | VNP7 - Man/stop pupmp 2 MAP7 - Place pump 2 back in auto | All Water System ROC General | 2026-02-14
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-11
ROC | February | SUSP- Satnam M done on site. Notified Satnam M barscreen and vortex/ dewatering screws are not in auto. Will place back in auto 11:56- Satnam M confirmed with Ops headworks is normally in local but runs in auto **WRONG BOOK** | All Water System ROC General | 2026-02-19
ROC | February | JFRS - Followed up with Alectra as constant power interruption occur. Nothing reported on the outage map but they confirmed they are aware of the situation across Richmond Hill and Vaughan area being impacted with power loss and interruptions. They have no further updates on estimated time of restoration and sounds like there team is still searching for cause of these faults as they believe these interruptions could be cause from tree contact or wildlife. With them actively investigating they have no further updates at this time. Informed Jerry Z of situation and will remain on site for some time to see any further issues before running generator | All Water System ROC General | 2026-02-16
ROC | February | ANW23- Deactivated Duty and reactivated to get wells to start up. MARS- Called Metro spoke with Mehdi to reduce flow | All Water System ROC General | 2026-02-11
ROC | February | NMETIB- Deactivated D1 to offset from NMETHW as per shift report AUPSRR- Post injection free Cl2 hihi alarm came in. Reset as trends recovered after 3 mins | All Water System ROC General | 2026-02-11
ROC | February | AUW57- turbidity hihi alarms outstanding. Turbidity recovered. Cleared alarms and will continue to monitor well run | All Water System ROC General | 2026-02-11
ROC | February | NMTKKC- Sean P done on site site back to normal and all alarms cleared | All Water System ROC General | 2026-02-17
ROC | February | STPSTL - Dan Z. called and directed to place the duty start for STETBR back to 60% as the deep cycling of the tower is complete. Dan also directed to place the low level alarm at STETBR back to 60 % | All Water System ROC General | 2026-02-20
ROC | February | NBW5 - Silicate Pump 1 failed to stop alarm came in. Checked site. Well is running. Silicate pump 2 rotated to duty 1 but silicate pump 1 was still running. Called Jordan B. who is not on site but informed this is okay | All Water System ROC General | 2026-02-20
ROC | February | VNPS- Tim H confirmed Line 1 became available alarms cleared on site | All Water System ROC General | 2026-02-20
ROC | February | SHTP, Activated D1 | All Water System ROC General | 2026-02-11
ROC | February | yws + nyws normal | All Water System ROC General | 2026-02-12
ROC | February | KCETDS, Activated D! | All Water System ROC General | 2026-02-12
ROC | February | VNETFD- Deactivated D1 to help the tower cycle | All Water System ROC General | 2026-02-20
ROC | February | AUW5 - Joe D requested to place well 5 pump to Duty 1 and leave running in manual mode for now. | All Water System ROC General | 2026-02-10
ROC | February | MARS- Called Metro spoke with Poulan to increase flow to reservoir | All Water System ROC General | 2026-02-10
ROC | February | HLW2- Stephen B heading to site for workorders | All Water System ROC General | 2026-02-10
ROC | February | MARS- Called Metro spoke with Zorhan to reduce flow | All Water System ROC General | 2026-02-12
ROC | February | NMW136, Placed well 16 man/off | All Water System ROC General | 2026-02-10
ROC | February | AUW14/5, Placed wells 2/3/5 in man/off so more water can be taken from AURSBS | All Water System ROC General | 2026-02-12
ROC | February | VNRSKS - Switched feed from VNPS PD7 to MAPS PD7 In preparation to chem scan calibration at RHRSTR/VNPS re-chlor. | All Water System ROC General | 2026-02-12
ROC | February | Carter D Signing In | All Water System ROC General | 2026-02-18
ROC | February | SHETCS - Common in/out Total chlorine LoLo alarm, Jacob M working on Hypo system, no water to analyzers, Jacob M collected grab sample. 14:05 Jacob M called Eric S. | All Water System ROC General | 2026-02-12
ROC | February | NMPSKC- Aaron Carlos from Networking is done work on site QVW12- jerry Z on site to work on treated total Cl2 analyzer | All Water System ROC General | 2026-02-12
ROC | February | MMW1- Power blip, Well 8 and well 13 High level. All wells interlocked. Cleared alarms and restarted Well 13 pump @ 20% and well 8 @ 41%. Verified with Rob P. High level alarms cleared. | All Water System ROC General | 2026-02-10
ROC | February | GWTP- Train two TMP lo. Cleared upon acknowledgement YWS+NYWS normal | All Water System ROC General | 2026-02-10
ROC | February | VNRSKS - Deactivated duty due to low levels at MARS YWS + NYWS Normal | All Water System ROC General | 2026-02-10
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-14
ROC | February | STW12 - Place well 1 man/on STW3 - Place well 3 man/on | All Water System ROC General | 2026-02-15
ROC | February | Ethan Ullalkar signing out. | All Water System ROC General | 2026-02-22
ROC | February | SHTP, Deactivated D1 | All Water System ROC General | 2026-02-12
ROC | February | STW12/3- Placed P2/3 in auto as per interim | All Water System ROC General | 2026-02-10
ROC | February | SHETCS - Eric S leaving site. Hypo Pump 2 man/off, can run if needed. | All Water System ROC General | 2026-02-10
ROC | February | NBW3- Influent free Cl2 lolo switch alarm came in while starting up in schedule mode interlocking wells. Waited for Influent free Cl2 residual to recover and reset alarms | All Water System ROC General | 2026-02-12
ROC | February | KSETDP - Dan Z. called to inform that the outlet chlorine analyzer is reading system water and tower remains isolated. Dan directed to disregard low chlorine alarms after hours | All Water System ROC General | 2026-02-20
ROC | February | SHTP - Yash S completed Network switch replacement, all alarms cleared. Jacob M will start the plant. | All Water System ROC General | 2026-02-12
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-12
ROC | February | RHRSTR- Activated D1 | All Water System ROC General | 2026-02-12
ROC | February | QVW34- Tyler ZJ onsite with William M for generator maintenance. | All Water System ROC General | 2026-02-11
ROC | February | AUW14, AUW5 - Placed back to auto. | All Water System ROC General | 2026-02-13
ROC | February | NMTKKC - Historian Heartbeat alarm. Notified Ian W, he is on site. Jason G on site, monitoring. | All Water System ROC General | 2026-02-10
ROC | February | Adam Button signing in -6C Snowing | All Water System ROC General | 2026-02-10
ROC | February | JFPS- Power fail on site generator running RHRSWA- Power fail on site RHPSPA- Power failure on site power blip pumps running okay BVPS- P1/3 uncomammnded stop alarm. P1 discharge valve failed to open. Deactivated D1 reset alarms Will continue to monitor power fails on other sites | All Water System ROC General | 2026-02-10
ROC | February | RMMCMD- Rob P notified ROC that there is no response at this time as there is still no power to site. Once power is restored faults can be reset. | All Water System ROC General | 2026-02-10
ROC | February | KSTP- Fin Water Fluoride Res Fault, Fin Water Tot CL2 Res Fault Alarms. Disregard as per SCADA Report. | All Water System ROC General | 2026-02-14
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-14
ROC | February | STW12, STW3 - Man/start for STETBR fill cycle. | All Water System ROC General | 2026-02-13
ROC | February | MTW3, Chlorinator 1 Vacuum Switch, Patrick F on site working on the Cl2 leak | All Water System ROC General | 2026-02-18
ROC | February | GWTP, ZW6 Recovery over extended, notified Patrick F, as calling, the alarm cleared, Patrick F directed to disregard at this time however if it start coming in multiple times, he would like a call | All Water System ROC General | 2026-02-12
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-12
ROC | February | MAPS PD7 - Pump 4 off for the night as per Tim H. | All Water System ROC General | 2026-02-12
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-13
ROC | February | RHRSTR, Deactivated D1 NRETCR, Deactivated D1 JFRS, Deactivated D1 | All Water System ROC General | 2026-02-13
ROC | February | ARPS, Peter from OCWA called, Peter confirmed OCWA will not be running any pumps tonight | All Water System ROC General | 2026-02-10
ROC | February | STETBR- Tower level lo STW12/3- Placed well 2/3 in man/on as per interim | All Water System ROC General | 2026-02-10
ROC | February | Carter D Signing Out | All Water System ROC General | 2026-02-10
ROC | February | NBW3- influent free Cl2 lolo alarm came in interlocking well on start up. Residuals recovered reset alarms. | All Water System ROC General | 2026-02-19
ROC | February | STPSMR - Travis W. is on site and will be completing a hard reset on the effluent analyzer. Travis will be stopping the pumps | All Water System ROC General | 2026-02-13
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-15
ROC | February | KCETFS - Control Panel Power Failure alarm came in. Outage reported on hydro one outage map. ETA of restoration is 1900 16:51 - Tim called back to inform that he is finished on site and power has been restored | All Water System ROC General | 2026-02-20
ROC | February | QVW34- Tyler ZJ finished onsite. | All Water System ROC General | 2026-02-11
ROC | February | QVW34 - Treated combined chlorine hihi alarm. Well pump was running in manual for sampling. Will M was in site. Will contact Will to inform if changes are not observed on SCADA. 13"50 - QVW34 - Will M is on site and managing the situation. | All Water System ROC General | 2026-02-17
ROC | February | Adeela Khan signing in. Weather: -2C and Cloudy | All Water System ROC General | 2026-02-10
ROC | February | NMVCBA - Placed valve in manual | All Water System ROC General | 2026-02-10
ROC | February | VNPSCD - Tim H. is on site with Parth P. and Art P. who will be taking the chem scan offline for about 10-15 mins. 11:25 - Parth P. and Art P. are finished on site | All Water System ROC General | 2026-02-13
ROC | February | QVW34 - Treated Total chlorine Low alarm, Ben H on site monitoring. | All Water System ROC General | 2026-02-10
ROC | February | VNETAG- Yash S working on OIT disregard historian heartbeat alarm until done 11:47-VNETAG- Yash S done working on OIT | All Water System ROC General | 2026-02-11
ROC | February | BLW3 - Phil D running generator and testing low temp alarm. | All Water System ROC General | 2026-02-12
ROC | February | VNPS - Rick L on site for calibration. Deactivated RHRSTR duty and placed BVPS pumps man/off. | All Water System ROC General | 2026-02-12
ROC | February | KBPS27 - Benson S cleaning chlorine analyzers, exercising valves, PRV and temp alarms test and health and safety inspection. | All Water System ROC General | 2026-02-12
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-14
ROC | February | NMETIB - Activate duty 1 | All Water System ROC General | 2026-02-14
ROC | February | KSTP- Jerry Z called and requested CMU5 for Eric S for turbidimeter. W11658745 CMU5 | All Water System ROC General | 2026-02-11
ROC | February | MKETFA - Travis W testing Hi/Lo level and Hi/Lo temp alarms, inspecting and exercising altitude valve, cleaning chlorine analyzers. | All Water System ROC General | 2026-02-12
ROC | February | KSTP - Raw water turbidity fault alarm. Disregard as per the shift report. | All Water System ROC General | 2026-02-13
ROC | February | RHPSPA RHMCMD RHRSWA JFPS, AUMCBS RHPSWA VNMCBA - Power blip. Cleared all alarms. | All Water System ROC General | 2026-02-13
ROC | February | YWS + NYWS NORMAL | All Water System ROC General | 2026-02-20
ROC | February | STW12, STW3 - placed back to auto. | All Water System ROC General | 2026-02-21
ROC | February | Christian Van Beek signing in. Weather: 1C and clear. | All Water System ROC General | 2026-02-17
ROC | February | STW2 / STW3 - Activated these well pumps in manual mode as directed by Joe M. | All Water System ROC General | 2026-02-17
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-21
ROC | February | STPSTL- Discharge Flow FWD LoLo Alarm. Pump shut down and Pump 1 went into duty 1. STW12- Placed pump 1 man/on STW3- Placed well man/on | All Water System ROC General | 2026-02-21
ROC | February | NMW12- Silicate Pump 1 Uncommanded Stop Alarm. Silicate Pump 2 took over in duty 1. Cleared alarm | All Water System ROC General | 2026-02-21
ROC | February | VNPS- Placed PD7 Pump 2 man/off MAPS- Placed PD7 pump 2 in auto | All Water System ROC General | 2026-02-21
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-21
ROC | February | MARS - Low level alarm, activated RHRSTR Duty 1. | All Water System ROC General | 2026-02-10
ROC | February | STW3 - Effluent free chlorine hi alarm. Checked site, influent and effluent values are nigher than normal. Checked the chlorinator dosing setpoints and noted that the dosing setpoint of the active chlorinator has climbed higher than the initial setpoint. Re-applied the initial setpoint and monitored. Tyler ZJ on site to complete a station disconnect. Will see alarms related to generator disconnection. | All Water System ROC General | 2026-02-17
ROC | February | NMETHW- Deactivated D1 | All Water System ROC General | 2026-02-17
ROC | February | MTW3, Patrick F on site, resetting well 3 and also working on the silicate injection point | All Water System ROC General | 2026-02-19
ROC | February | NMW12, Eric S is on site working on Silicate pump 1 | All Water System ROC General | 2026-02-19
ROC | February | VNPS PD7- Placed P3 in man/off and Placed P2/3 in auto | All Water System ROC General | 2026-02-19
ROC | February | VNPSPD7/8 - RHRSTR, Benson S on site, testing health and safety alarms | All Water System ROC General | 2026-02-19
ROC | February | NMETIB- Activated D1 at 55% to offset from NMETHW as per shift report | All Water System ROC General | 2026-02-16
ROC | February | STW12- Placed Well 1 in man/off and rotated D1 to P2 due to VFD speed fluctuations over past 5 days. Emailed East water team about potential issue | All Water System ROC General | 2026-02-16
ROC | February | Ethan U signing in Weather -4. | All Water System ROC General | 2026-02-22
ROC | February | YWS + NYWS Normal ARPS - Peel informed they will switch active pump 6 to pump 7 to duty 1 | All Water System ROC General | 2026-02-22
ROC | February | NMW12 Silicate pump 1 failed to start. Issue that occurred throughout the weekend. Emailed central team regarding issue. Placed silicate pump 1 man/off | All Water System ROC General | 2026-02-22
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-19
ROC | February | NMETIB, Deactivated D1 NMVCIB, Reverted flow back to 80L/sec NMVCBA, Reverted flow back to 40L/sec | All Water System ROC General | 2026-02-12
ROC | February | NMVCBA, Placed valve in manual and set flow to 40L/sec | All Water System ROC General | 2026-02-12
ROC | February | QVW12 - Jerry Z on site, requested to disregard chlorine room gas leak alarm. | All Water System ROC General | 2026-02-13
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-13
ROC | February | VNPSCD - Parth P finished his work on the pre-injection chlorine analyzer. Placed the chemical system in auto mode and monitored. Chemical system activated and within five minutes the combined chlorine residual triggered a hihi alarm. Parth P collecting a grab sample. 01:42 - VNPSCD - Grab sample was below the hihi alarm setpoint. When the chemical system activates the post injection combined reading will likely hit the same value. Contacted Jerry Z who directed to try again. Parth P standing by with a grab sample to determine if the reading is accurate. 01:50 - VNPSCD - Alarms returned on second attempt to activate chemical system. Parth P collected a grab sample and confirmed that the post injection analyzer is reading accurately. Called Jerry Z to inform that the system is not operating as expected. Jerry Z informed that the combined chlorine average is what controls the dosing setpoints and this analyzer is currently reading low. Jerry stated that if the twenty minute average analyzer reading does not update then PCS should be contacted. 02:13 - VNPSCD - The twenty minute average combined chlorine reading has not updated after forty minutes. Contacted Chris S who walked through the process of completing a combined chlorine average reading reset. Completed the combined chlorine average reading reset at the request of Chris S and the combined chlorine average value matched the current pre-injection combined chlorine reading. Returned the chemical system to auto and monitored the post injection values. The post injection readings stabilized within normal range indicating that dosing is normal and the issue has been resolved. Will monitor site closely. Created CMU5#W11664563 for Chris S. #consult #CMU5 | All Water System ROC General | 2026-02-14
ROC | February | GWTP- Pre Chlor booster P1 overload alarm came in. P2 in man/off. Notified Patrick F. Patrick F reset alarms and pump restarted. Directed to disregard if alarms come back in as prechlor is not required #consult | All Water System ROC General | 2026-02-16
ROC | February | SHTP- Reservoir total Cl2 fault alarm came in. Notified Cole W. Will take a look on SCADA #consult | All Water System ROC General | 2026-02-16
ROC | February | SHTP- Cole W was able to reset alarm. Cole W rotated sample pumps. and Directed to do so if alarm comes back in 11:51- SHTP- Total Cl2 fault came back in. Rotated sample pumps from P2 to P1. cleared alarm 11:59- SHTP- Total Cl2 fault came in again. Notified Cole W. Will check SCADA and reach out if he will attend site | All Water System ROC General | 2026-02-16
ROC | February | NMVCBA- Placed valve in manual open at 40L/s | All Water System ROC General | 2026-02-16
ROC | February | KCETDS- total/combined Cl2 alarms came in. Looks like analyzer dropped out and recovered after 3 mins alarms cleared | All Water System ROC General | 2026-02-17
ROC | February | MAP7 - Place pump 2 back in auto VNP7 - Place pump 3 back man/off | All Water System ROC General | 2026-02-22
ROC | February | Adeela Khan signing in. Weather: -1C and flurries | All Water System ROC General | 2026-02-22
ROC | February | GWTP - ZW3 Membrane Tank Level Switch LoLo alarm came in. Value turned normal and alarm cleared | All Water System ROC General | 2026-02-22
ROC | February | AUW57, Placed well 5 man/off to help take more flow from AURSBS AUW14, once contact tank has been cleared, will be placing wells 2/3 man/off to allow more water to be taken from AURSBS | All Water System ROC General | 2026-02-13
ROC | February | YWS + NYWS Normal RHRSTR - Activated duty 1 to fill the reservoir. NMETIB - Deactivated duty 1. NMVCBA/NMVSIB - Reverted flow setpoint changes made earlier. | All Water System ROC General | 2026-02-14
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-14
ROC | February | YWS+NYWS normal | All Water System ROC General | 2026-02-16
ROC | February | YWS+NYWS normal | All Water System ROC General | 2026-02-16
ROC | February | YWS+NYWS normal AUPSRR- Post injection free Cl2 hihi/ combined lo alarms came in. Reset as residuals recovered VNPS- Free amm hi alarm came in. Looks like residuals higher than normal after adjustments on site. Will continue to monitor. | All Water System ROC General | 2026-02-17
ROC | February | AURSBS - Activated reservoir in preparation for MAPS to JFRS Feed run | All Water System ROC General | 2026-02-22
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-18
ROC | February | BLW34 - Kyle C with contractor working on site. Well 3 pump man/off. | All Water System ROC General | 2026-02-18
ROC | February | NBW2 - Parth P, Rick L and Art on site rebuilding chlorinator. Cole W on site to assist. | All Water System ROC General | 2026-02-18
ROC | February | YWS + NYWS Normal Christian Van Beek signing out. | All Water System ROC General | 2026-02-19
ROC | February | HLW2 - Ammonia pump 1 fault. Pump 2 able to run. Able to clear pump 1 fault | All Water System ROC General | 2026-02-17
ROC | February | STRS48 - Joe M cleaning chlorine analyzers. NMW15 - Alex B called, well 15 pump man/off for now, chlorine analyzer issue, Eric S will attend site. | All Water System ROC General | 2026-02-18
ROC | February | VNETFD- Angelica C and Tim H on site to test hi lo temp and flood alarms | All Water System ROC General | 2026-02-19
ROC | February | VNPS PD8, Placed pumps back to auto | All Water System ROC General | 2026-02-19
ROC | February | YWS + NYWS Normal Christian Van Beek signing out. | All Water System ROC General | 2026-02-20
ROC | February | VNRSKS - Placed all MAPS PD7 pumps man/off and placed pump 2 and 3 at VNPS into auto | All Water System ROC General | 2026-02-20
ROC | February | MKRSEM - High level alarm setpoint from 75 to 70% as per Patrick F. | All Water System ROC General | 2026-02-13
ROC | February | MTW3 - Chlorine Gas Leak alarm came in. Well was not running. Called Dan Z. who will attend site. CMU5 Created W11679951 23:26 - Dan Z. called back to inform that MTW3 will be OOS for the night as a minor leak has been identified. Both cylinders are now closed. #CONSULT #CMU5 | All Water System ROC General | 2026-02-22
ROC | February | YWS + NWYS Normal | All Water System ROC General | 2026-02-19
ROC | February | STPSMR - Discharge pressure hi alarm. Checked site, pumps are active and system is close to duty 1 stop setpoint. Will monitor site and deactivate duty 1 if the discharge pressure continues to increase | All Water System ROC General | 2026-02-14
ROC | February | JFPS - Called back Alectra, speaking with Jill. Confirmed cause of power blips and faults in area of Vaughan & Richmond hill are due to drastic temperature increasing from below negative to above 0 quickly in area which caused salt and moisture going airborne causing flashover and temporary faults in line and dips in voltage. As well as ice shedding in areas. No concrete time of restoration but said it could be at least 12h to a day or two for these power blips in area. Informed Jerry Z of situation and he will head home. JFPS & BVPS remain on generator power to prevent continues drop in pumps due to power blips. Outage map does not reflect these areas of concern and faults as its dips in voltage but Alectra team is aware of the heavy power blips caused in areas and are actively responding and cleaning lines. They suggesting calling back in the morning for another update on situation | All Water System ROC General | 2026-02-17
ROC | February | NMETIB - Deactivate duty 1 | All Water System ROC General | 2026-02-17
ROC | February | KLPSWL - Pump 3 & 4 hi temp, able to clear alarms right away. Pumps were not running at time MTELNL - Outlet free chlorine spike in reading, came back within range shortly and able to clear | All Water System ROC General | 2026-02-17
ROC | February | STW1/3, Placed wells 1/3 man/on | All Water System ROC General | 2026-02-19
ROC | February | KSTP- Jerry Z req ROC to create CMU5 for Eric S for a total Cl2 analyzer fault. Created CMU5 W11679195 #CMU5 | All Water System ROC General | 2026-02-20
ROC | February | MTW3 - Chlorine Gas Leak alarm came in. Called Phil D. who will head to site. CMU5 Created W11679209 #CMU5 | All Water System ROC General | 2026-02-20
ROC | February | Connor Smith signing in -1 Cloudy | All Water System ROC General | 2026-02-14
ROC | February | MAPS/JFRS- Initiated Maple to Jefferson Feed. | All Water System ROC General | 2026-02-14
ROC | February | NMPSKC, NMTKKC, NMMCWA - Kevin W switching from Radio to cellular APN. | All Water System ROC General | 2026-02-18
ROC | February | Christian Van Beek signing in. Weather: -4C and snow | All Water System ROC General | 2026-02-18
ROC | February | YWS + NYWS Normal QVW34 - Treated total chlorine hihi alarm. Checked site, well is off no water being directed to users. Reset alarm. | All Water System ROC General | 2026-02-18
ROC | February | SHTP - Made changes for the interim procedure. Noted that there is a "well raw water tank level override stop" setpoint that is currently set to a level that is lower than the new Raw water tank level stop setpoint. Contacted Tim H to ask if this override stop setpoint will interlock the well pump if it is below the target stop setpoint for the raw water tank. Tim will check SCADA and call back. 21:22 - SHTP - Tim H called back and directed to change the well water tank level override stop alarm to 5.30m, from 5.10m. Tim also adjusted the manual speed setpoint for well #2 from 70% to 92% because the well was only producing 15L/s but the interim requires 17L/s. Tim also adjusted the reservoir high level alarm to 85% which will trigger if the reservoir fills and the plant stops. At this time Tim H requested that the SHETCS duty be activated to ensure the raw water well 2 does not stop. #consult | All Water System ROC General | 2026-02-18
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-19
ROC | February | MKRSMR- Pouran from Metro called wanting to test P10 for 30 mins | All Water System ROC General | 2026-02-20
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-17
ROC | February | MAPSN1 - Communication Failure alarm came in for various sites on the server. After 5 mins, all communications alarms cleared and trending is okay 12:44 - MAPSN1 Server communications alarm came in again. Called Yash S. who will take a look 12:58 - Yash S. called back to inform that the server is back online and that he is finished the KCETFS and KCETDS upgrades. Alarms cleared and trending is okay 13:!3 - PAC communication alarms for KCETDS and KCETFS came in again. Called Yash S. who is looking into it. Also informed Yash about the outstanding ANMCBL - PAC Communication Alarms | All Water System ROC General | 2026-02-20
ROC | February | AUW14, Joe D on site, testing cl2 leak alarm | All Water System ROC General | 2026-02-18
ROC | February | MAPS- Placed PD7 pumps to manual VNPS- Placed PD7 duty 1 pumps into auto | All Water System ROC General | 2026-02-21
ROC | February | BLW3 - Patrick F attending site CMU = 11664802 | All Water System ROC General | 2026-02-15
ROC | February | MAPS PD7 - Dan B called, P4 will remain man/off, Pumps 1,2,3 back to normal. VNPS PD7 - placed Pump 2 back to auto. | All Water System ROC General | 2026-02-18
ROC | February | NMW15 - Eric S working on total chlorine analyzer. | All Water System ROC General | 2026-02-18
ROC | February | SHTP - Filter 1 and 3 Turbidity Hi alarm came in. Checked site. Filter 2 just came out of backwash. Spoke to Derrick S. and Jacob M. Jacob M. directed to Ack/reset alarms | All Water System ROC General | 2026-02-20
ROC | February | HLW2 - Stephen B leaving site to grab supplies from HLW1 and will be back to change cylinders at HLW2 with Jacob M STPS48- Lee F on site to work on high lift P2 NMTKKC- Ian W and Jay G done on site. Jay G will activate D1 with chem system off and place back in auto once flow stabilizes. NMPSKC- Pac Comm fail came in on site. Notified Jay G who will consult with Ian W | All Water System ROC General | 2026-02-10
ROC | February | NMETIB - Total Chlorine Hi alarm came in. Checked site. Tower is filling. Will continue to monitor site 04:58 - Combined Chlorine Hi alarm came in. Trends indicate an increase of total and combined levels over the past day. Called Jerry Z. who informed if the combined level goes above 3.7, he will attend site. | All Water System ROC General | 2026-02-11
ROC | February | MAPS PD8- Placed all pumps in man/off. Placed P2/4 in D1 and started both for Lee F. | All Water System ROC General | 2026-02-11
ROC | February | Connor Smith signing in | All Water System ROC General | 2026-02-11
ROC | February | Adam Button signing in in -3C clear | All Water System ROC General | 2026-02-11
ROC | February | STW3 - Influent Free chlorine residual Hi, Effluent Free chlorine residua Hi alarms at duty start. Value back to normal, cleared alarms. | All Water System ROC General | 2026-02-12
ROC | February | VNRSKS - Activated duty 1 to draw down MARS. | All Water System ROC General | 2026-02-19
ROC | February | JFPS- WPS P2 failed to start and MV2 failed to close alarms came in as power transferred back to utility cleared alarms KSETDP- Jackie P on site to test lo temp, Cl2 leak alarms and perform JHS inspections AUW57- Joe D on site to get well back on line. MAPS- Dave T on site to test lo temp, Gas leak alarms and perform JHS HVAC inspections BLW3- Phil D on site to work on silicate and Cl2 systems. Dan Z also on site to test alarms on site and directed to disregard all alarms on site until done | All Water System ROC General | 2026-02-10
ROC | February | Adeela Khan signing out | All Water System ROC General | 2026-02-11
ROC | February | MAPS- Lee F called and requested to run PD7 pumps 1,3. Placed VNPS duty 1 pumps man/off and MAPS PD7 pumps 1,3 into auto. 10:05- Pump 1 shut down on Pressure Switch Low Alarm. Notified Lee F. Cleared alarm and placed back into duty 1. 10:15- Pump 2 shut down on same alarm, Lee F will inform Tyler ZJ. 10:20- Lee F requested pumps 2,4 in duty 1. 11:10- Lee F finished. Placed Maple PD7 pumps in manual. Placed VNPS PD7 Duty 1 pumps into auto | All Water System ROC General | 2026-02-11
ROC | February | NMETYS- Yash working on comms network. Will lose comms to towers valves and meter chambers in system but no impact expected AURSBS- Donald M done on site QVW12- Artour done commissioning diesel LIT | All Water System ROC General | 2026-02-19
ROC | February | VNPS PD7 - Pumps 2&3 to auto. MAPS PD7 - Pumps 1&2 man/off. | All Water System ROC General | 2026-02-10
ROC | February | AUMCBS - Power blip, cleared alarm. | All Water System ROC General | 2026-02-10
ROC | February | QVW12 - Artour L working on OIT, disregard Historian Heartbeat alarm. Placed Well pumps 1&2 man/off. | All Water System ROC General | 2026-02-10
ROC | February | QVW12 - Influent free chlorine hihi. Checked site, wells are running in manual mode. Trending shows a sudden spike of the influent free chlorine reading which returned to normal range within one reading interval. Reset alarm. | All Water System ROC General | 2026-02-17
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-22
ROC | February | SHTP, Activated D1 | All Water System ROC General | 2026-02-12
ROC | February | QVW12 - Garrick from Ferguson electric disconnecting portable generator and connecting to station generator, may send alarms. | All Water System ROC General | 2026-02-10
ROC | February | QVETQS - System pressure lo alarm came in when QVW12 deactivated. Pressure took a dip and came back immediately. Alarm cleared NMVCBA - Placed valve back to auto NMETIB - Activated duty to help offset with NMETHW | All Water System ROC General | 2026-02-11
ROC | February | JFPS- WPS P2 failed to start/ MV2 failed to open alarm came in. Came in yesterday as well. Notified Tim H heading to site | All Water System ROC General | 2026-02-11
ROC | February | MAPS PD7, Placed pumps 2/3 man/off VNPS PD7, Placed pumps 2/3 in auto RHRSTR, Activated D1 | All Water System ROC General | 2026-02-12
ROC | February | YWS + NYWS Normal Connor Smith signing out | All Water System ROC General | 2026-02-11
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-11
ROC | February | BVPS - Diesel delivery on its way, informed Jerry Z to meet Consult | All Water System ROC General | 2026-02-17
ROC | February | NMETIB - activated D1 to offset with NMETHW. | All Water System ROC General | 2026-02-10
ROC | February | MKMCLA - Power blip, alarms cleared | All Water System ROC General | 2026-02-10
ROC | February | MAPS- Tim H on site to run generator | All Water System ROC General | 2026-02-10
ROC | February | NMTKKC-Activated D1 | All Water System ROC General | 2026-02-11
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-11
ROC | February | MKRSEM - Noted that the trendline appears flatlined. Level value changes slightly over time. Reservoir is draining and flatline level is abnormal during reservoir draining. MKRSMR is currently filling, backflow down to MKRSEM is possible. Will monitor situation. 20:58 - MKRSEM - Reservoir has begun filling with no duty active. This abnormal fill/drain trend could be related to an ongoing watermain break in Markham. If valves are being turned in Markham it would be affecting flow pathways. No York Region operators are in the field at the moment but CPD is investigating and trying to determine who has ownership of the break. If ownership has been claimed and they are working on the fix, valving has likely influenced the fill cycle. | All Water System ROC General | 2026-02-13
ROC | February | MKETFA/MKRSEM/MKRSMR- Poulan from Metro called to inform ROC that we will lose comms for pumps supplying storages. Pumps that are active currently will remain on but Metro is working on software updates for pumps in this area | All Water System ROC General | 2026-02-10
ROC | February | NMETIB- Parth P on site to work on Cl2 analyzer | All Water System ROC General | 2026-02-17
ROC | February | NMETIB - Free chlorine hi. Checked site, trending shows the free chlorine reading is climbing following a visit from instrumentation and operations. Called Joe W who will return to site to check the analyzer. | All Water System ROC General | 2026-02-17
ROC | February | ARPS, David from OCWA called, Rotating pumps from pump 2 to pump 4 | All Water System ROC General | 2026-02-19
ROC | February | Adeela Khan signing in. | All Water System ROC General | 2026-02-20
ROC | February | STW12 - Joe M performing w/o including: generator run, chlorine analyzers maintenance, health and safety inspection. | All Water System ROC General | 2026-02-10
ROC | February | NBW56 - Jordan B on site, cleaning chlorine analyzers and testing chlorine leak alarm. | All Water System ROC General | 2026-02-10
ROC | February | SHTP - Kevin W on site for network upgrades. Jacob M on site to assist | All Water System ROC General | 2026-02-12
ROC | February | NBW3- Influent free Cl2 lolo switch. Called Jordan B. Directed to reset and allow well to run in schedule mode | All Water System ROC General | 2026-02-12
ROC | February | STW12, STW3 - man/start for STETBR fill cycle. | All Water System ROC General | 2026-02-12
ROC | February | BVPS - Dan Z on site to swap the station back to utility power and shut down the generator. | All Water System ROC General | 2026-02-17
ROC | February | SHTP - Well 2 pump uncommanded start alarm. Checked site, flow recently stopped as the reservoir is full. Cleared alarm. | All Water System ROC General | 2026-02-17
ROC | February | NMETIB - Activate duty 1 | All Water System ROC General | 2026-02-18
ROC | February | GWTP- Joe M notified ROC ZW7 neutralization exceeded dur and recirc inlet V failed to close alarm will remain outstanding for night | All Water System ROC General | 2026-02-10
ROC | February | Bathurst and North of Shaw - Karen from Roads dispatch called to inform that there has been a report of a watermain break at this intersection. After checking this location on all pipes, york region does not have any watermains in this area. Karen will contact the city of richmond hill. Karen will also give the ROC a call back with any new information | All Water System ROC General | 2026-02-11
ROC | February | ARPS - Clarified from Peter (OCWA) that flow registered between 13:44-14:16 is a result of service water flow through chemical quill during maintenance work on injection system. Flow through FIT34310 not a result of pump run. Notified Jeremy H. | All Water System ROC General | 2026-02-10
ROC | February | AUW57 - Influent Free chlorine LoLo interlock on duty start. Placed man/off. Notified Joe D. 15:00 Jerry Z will attend site. | All Water System ROC General | 2026-02-10
ROC | February | RHRSTR - Tim H and Carter D on site. Tim requested that the VNPS PD8 pumps be activated. Activated duty 1 and then duty 2. | All Water System ROC General | 2026-02-17
ROC | February | SHTP- Backwash high lift required alarm came in. Notified Jake M. Jake M reset alarms high lifts back in auto. | All Water System ROC General | 2026-02-17
ROC | February | Christian Van Beek signing out. | All Water System ROC General | 2026-02-17
ROC | February | NMETHW - Deactivated duty to keep level offset from NMETIB. | All Water System ROC General | 2026-02-19
ROC | February | BVPS- Peter from Metro notified ROC they are having a technician work on software updates at bayview reservoir and will lose comms for 10 mins RHRSWA- Tim H heading to site with portable generator created CMU5 #CMU5 | All Water System ROC General | 2026-02-10
ROC | February | HLW2- Station Turbidity Fault. Interlocked well. Notified Tim. H. Can disregard. Increased HLW2 VC from 20L/s to 40L/s. 15:10- Tim H will attend site after attending NBW5 W11679730 CMU5 | All Water System ROC General | 2026-02-21
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-22
ROC | February | MKRSEM - Reservoir Level Lo alarm came in. Called Toronto Water (Zoran) and requested two pumps on 03:00 - Called Toronto Water (Zoran) and requested to stop pumping to reservoir | All Water System ROC General | 2026-02-22
ROC | February | NMVCBA - Placed valve in manual at 40 L/s 01:59 - Placed valve back to auto | All Water System ROC General | 2026-02-22
ROC | February | STETBR- Tower level hi STW12/3- Placed P1/3 back in auto as per interim | All Water System ROC General | 2026-02-12
ROC | February | HLW2- Treated Total and Combined Cl2 lo alarms came in. Well not active no water directed to users and alarm cleared after 3 mins | All Water System ROC General | 2026-02-16
ROC | February | NMW12- Influent free Cl2 lo alarm came in on well start up cleared after 3 mins | All Water System ROC General | 2026-02-16
ROC | February | MAPS PD7 - Tim H and Dan B finished on site. Pump 4 man/off until further notice. MAPS PD7 pumps 1,2,3 man/off VNPS PD7 Pumps 2 and 3 to auto. | All Water System ROC General | 2026-02-18
ROC | February | NMVCIB, changed flow setpoint from 80 to 40L/sec NMVCBA, Changed flow setpoint from 40 to 80L/sec 22:05, Reverted changes | All Water System ROC General | 2026-02-12
ROC | February | MKPSSA - Garrick from Ferguson electric running generator and testing containment foods. 09:40 All alarms cleared, Garrick leaving site. | All Water System ROC General | 2026-02-12
ROC | February | Carter Dunn Signing In, -2D/Clear | All Water System ROC General | 2026-02-12
ROC | February | GWTP- Jackie S on site backwashing GAC 3 | All Water System ROC General | 2026-02-19
ROC | February | AUETFC, Joe D on site, working on the health and safety alarms//temp alarms and working on the analyzers on site | All Water System ROC General | 2026-02-19
ROC | February | TMC317, Forward Flow Lo, Valve shows no flow going to MARS, contacted Zoran from Toronto, he is rotating pumps which caused the flow to drop. will continue to monitor the until it is back to normal range | All Water System ROC General | 2026-02-11
ROC | February | NMVCBA - Placed valve in man at 30 L/s 01:30 - Placed valve back to auto | All Water System ROC General | 2026-02-21
ROC | February | VNRSKS - Deactivated duty 1 and switched all VNPS PD7 pumps man/off and placed pumps 1,2,3 at MAPS PD7 in auto | All Water System ROC General | 2026-02-21
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-22
ROC | February | HLETYS - Stephen B testing temp alarms and cleaning chlorine analyzers. | All Water System ROC General | 2026-02-12
ROC | February | HLW2- Treated free Cl2 hihi alarm came in. Rotated ammonia pumps and notified Stephen B. Stephen B on site working on ammonia system MKRSEM- Called Metro spoke with Poulin to start 2 pumps to reservoir QVW34- Donny M on site to work on analyzer sand get the well back up and running | All Water System ROC General | 2026-02-10
ROC | February | Adam Button signing out | All Water System ROC General | 2026-02-16
ROC | February | JFRS - WPS pump 3 & 4 failed to start. Reoccurring issue with iste. WPS MV#3 & 4 failed to close. Informed Jerry Z again of situation. Unable to clear on my end, Jerry will go back to site | All Water System ROC General | 2026-02-16
ROC | February | JFPS - Pump 3 & 4 uncmd stop on power trip. WPS pump 3 faile to start, pump 4 MV#4 failed to close. Generator running No update from Alectra (Kevin) when called for update. Was informed no news or anything concrete to share at this time. Still investigating. BVPS - Pump 1 & 4 multilin trip/warning. Unable to clear alarm. Informed Jerry Z again of issue and will try and run generator at BVPS VNPSCD - Post-inj free/comb hihi due to BVPS shutting down and readings spike. RHPSPA - Surge valve 2 open | All Water System ROC General | 2026-02-16
ROC | February | ARPS - Martin from Peel/OCWA called to inform they are completing a pump duty rotation. | All Water System ROC General | 2026-02-17
ROC | February | GWTP - Backpulse Tank 2 Level HiHi and Backpulse Tank Level Hi alarm came in. Checked site. Spoke to Jackie S. who will take a look | All Water System ROC General | 2026-02-13
ROC | February | AURSOH, Deactivated D1 AURSBS, Deactivated D1 | All Water System ROC General | 2026-02-19
ROC | February | GWTP- MAU 1 coil lo temp alarm came in. Notified Jackie P. Will try to clear after chem delivery is completed | All Water System ROC General | 2026-02-19
ROC | February | VNPS- Tim H on site to work on post injection hi ammonia residual analyzer. Req RHRSTR D1 be activated RHRSTR- Activated D1 | All Water System ROC General | 2026-02-19
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-20
ROC | February | BLW12- Tyler Z restored power to site and req D1 activation to ensure wells running okay after work. Activated D1 for BLETNL 17:29- BLW12- VFD Fault alarm came in. Notified Tyler Z. Will go back to site and check VFD 17:40- BLW12- Tyler Z cleared VFD alarm well started up okay 17:48-BLW12- Notified Patrick F that Well is back up and running #consult | All Water System ROC General | 2026-02-17
ROC | February | STETBR - Tower Level Hi alarm came in. Placed STW3 and STW1 back to auto, as per interim | All Water System ROC General | 2026-02-23
ROC | February | VNPS - Rick L completed work on site, Placed BVPS pumps back to auto. | All Water System ROC General | 2026-02-12
ROC | February | SHTP- Cole W done on site directed to clear alarms. All alarms cleared trends okay AUW57- influent free Cl2 hihi alarm came in on well start up cleared after 3 mins | All Water System ROC General | 2026-02-16
ROC | February | NMMCBA - Parth P on site to complete a flowmeter calibration. *wrong book* | All Water System ROC General | 2026-02-17
ROC | February | Adam Button signing in 3C Foggy | All Water System ROC General | 2026-02-20
ROC | February | RHPSWPA, Travis W on site, testing flood alarms | All Water System ROC General | 2026-02-19
ROC | February | Adeela Khan signing out | All Water System ROC General | 2026-02-20
ROC | February | YWS + NYWS NORMAL | All Water System ROC General | 2026-02-21
ROC | February | QVW12- Artour L done testing on generator. Placed Well 1 back in auto. KLET27- Deactivated D1 | All Water System ROC General | 2026-02-10
ROC | February | STETBR - tower level hi alarm. Placed STW1 and STW3 in auto mode. | All Water System ROC General | 2026-02-14
ROC | February | STW12- Placed well 1 back into auto STW3- Placed well back into auto | All Water System ROC General | 2026-02-15
ROC | February | Carter D Signing In | All Water System ROC General | 2026-02-10
ROC | February | MARS- Called Metro spoke with Pouran to increase flow to reservoir | All Water System ROC General | 2026-02-12
ROC | February | BLW34 - Kyle C restarting OIT for updates, disregard Heartbeat Alarm until further notice. | All Water System ROC General | 2026-02-12
ROC | February | NMPSKC - Aaron M making network changes. | All Water System ROC General | 2026-02-12
ROC | February | QVETQS, Jason G is finished on site | All Water System ROC General | 2026-02-19
ROC | February | NMETIB, Changed D1 stop back to 75% from 85% | All Water System ROC General | 2026-02-18
ROC | February | MKRSEM -low level alarm. Called Toronto Water (Paul) and requested they activate two pumps to push flow. | All Water System ROC General | 2026-02-18
ROC | February | VNP8 - Proc sump pump 1 & 2 fault, able to clear RHRSTR - Site power failure, able to clear as site continuous to run on generator | All Water System ROC General | 2026-02-17
ROC | February | Ethan Ullalkar signing out. | All Water System ROC General | 2026-02-17
ROC | February | Adam Button signing in | All Water System ROC General | 2026-02-17
ROC | February | MKRSEM -Request TO (Brent) to drop both pumps | All Water System ROC General | 2026-02-18
ROC | February | GWTP-CIP feed water flow hi alarm came in. Cleared upon acknowledgement | All Water System ROC General | 2026-02-16
ROC | February | YWS+NYWS normal | All Water System ROC General | 2026-02-16
ROC | February | YWS+NYWS normal | All Water System ROC General | 2026-02-16
ROC | February | MKRSEM- Called Metro spoke with Paul to start two pumps to reservoir | All Water System ROC General | 2026-02-16
ROC | February | NMVCBA- Placed valve back inauto NMETHW- Activated D1 at 43% to offset from NMETIB as per shift report | All Water System ROC General | 2026-02-16
ROC | February | BVPS- Notified Dan Z that instrumentation is done work at VNPS and pumps can go back into auto. Notified Tim H that we will be activating D1 at RHRSTR | All Water System ROC General | 2026-02-17
ROC | February | Ethan U signing in Weather 0. | All Water System ROC General | 2026-02-17
ROC | February | Adam Button signing out | All Water System ROC General | 2026-02-17
ROC | February | NMTKKC - Ammonia tank 2 hihi. Able to clear, level within range | All Water System ROC General | 2026-02-18
ROC | February | Angelica Chepiga signing in, weather -2C | All Water System ROC General | 2026-02-18
ROC | February | ARPS- Martin from Peel called to notify ROC they will be transferring from P5 to P6 KCETDS- Activated D1 as per interim | All Water System ROC General | 2026-02-20
ROC | February | 9255 Jane St- Kai Ming C. from Access York (Customer Relations) notified ROC of ongoing leak in Vaughan that was called in by Property manager. City of Vaughan was first point of contact claiming it is not their infrastructure. Checked all pipes. No York Region infrastructure in area. Complex being fed by Vaughan main and most likely private connection to complex. Emailed Access York explaining that this location does not have York region infrastructure in area of leak and followed up with Nolan from City of Vaughan. (416-550-8419). #Accessyork | All Water System ROC General | 2026-02-19
ROC | February | MAP7 - Place pumps man/off. VNP7 - Place pump 2 & 3 auto | All Water System ROC General | 2026-02-14
ROC | February | STW3- Chris S cleared historian heartbeat. Placed well 2 in man/on trends okay | All Water System ROC General | 2026-02-17
ROC | February | VNPS- Rick L on site for chlorination system calibrations | All Water System ROC General | 2026-02-17
ROC | February | ARPS - Peel ammonia analyzer B airport Rd discharge. Ammonia level/readings within normal range. Called Peel, no response 16:17 - Called back and spoke with Bineesh. Said Readings are okay on their end, they received same alarm but analyzer B is their spare and all ammonia and related alarms are in good standing | All Water System ROC General | 2026-02-14
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-14
ROC | February | Ethan Ullalkar signing out. | All Water System ROC General | 2026-02-14
ROC | February | Ethan U signing in Weather -1. | All Water System ROC General | 2026-02-15
ROC | February | NMW15, Alex B/Christian are on site, doing site PMS, working on the chemical analyzers/turbidity analyzers | All Water System ROC General | 2026-02-18
ROC | February | NBET27 - Jordan B running generator, testing Hi/Low level and temperature alarms. | All Water System ROC General | 2026-02-12
ROC | February | NMETIB - Deactivate duty 1 MAP7 - Place pump 3 man/off VNP7 - Place pump 3 auto | All Water System ROC General | 2026-02-15
ROC | February | NMW136 - Influent free chlorine hihi, Came in during startup of well. Monitored site and reading came down within range | All Water System ROC General | 2026-02-15
ROC | February | NBW3 - Influent free chlorine lolo on startup for schedule mode. Able to reset alarm next couple reading | All Water System ROC General | 2026-02-15
ROC | February | YWS + NYWS Normal NMETIB - Activate duty 1 | All Water System ROC General | 2026-02-15
ROC | February | STETBR - Tower Level Hi alarm came in. Placed STW12 and STW3 back to auto as per interim | All Water System ROC General | 2026-02-06
ROC | February | NBW5 - Turbidity Hi alarm came in. Checked site. Well is running but duty is 2% from deactivating. Trends indicate turbidity was high during the day. Rotated silicate pumps. Will continue to monitor 18:55 - After about 20 mins, turbidity did not come down. Placed well man/off and will send an email to Jacob M. 19:09 - Spoke to Jacob M. instead. Jacob directed to prime both silicate pumps. Started with silicate pump 1 and placed it in manual with 100% setpoint and started the pump. After about a minute, placed silicate pump 1 man/off and then started priming silicate pump 2. Jacob also directed to place the well and all pumps back to auto once duty deactivates #CONSULT | All Water System ROC General | 2026-02-06
ROC | February | ARPS - Peel OCWA (David) called to inform he is rotating duty 1 pump at ARPS | All Water System ROC General | 2026-02-07
ROC | February | QVW34- Yash S finished with work. Wells are back in auto | All Water System ROC General | 2026-02-05
ROC | February | HLW2- Combined Chlorine HiHi Alarm. Interlocked well. Notified Stephen B. He will take a look. | All Water System ROC General | 2026-02-06
ROC | February | VNPS PD7- Placed duty 1 pumps in auto MAPS PD7- Placed duty 1 pumps in manual | All Water System ROC General | 2026-02-06
ROC | February | QVW12 - Influent Free Chlorine Hi alarm came in. Checked site. Influent Free levels are just below the target level. Will monitor | All Water System ROC General | 2026-02-05
ROC | February | SCADA server - Evgheny S. called to inform he will be rebooting remote SCADA. Lose access for 20 Seconds 21:25 - Server Restart complete | All Water System ROC General | 2026-02-05
ROC | February | NMW12 - Treated Total Chlorine Lo and Combined Chlorine Lo alarms came in. Wells are not running and water is not being directed to users | All Water System ROC General | 2026-02-08
ROC | February | Adeela Khan signing out | All Water System ROC General | 2026-02-08
ROC | February | GWTP - Make Up Air Unit 1 Coil Low Temp alarm came in. Critical alarm. Shift report directs to disregard the MAU fault, not the low temp. Called Joe M. who directed to disregard alarm for the rest of the weekend #CONSULT | All Water System ROC General | 2026-02-08
ROC | February | VNPS/RHRSTR - Yash S. completed planned network work. Placed BVPS and VNP8 back to auto. | All Water System ROC General | 2026-02-04
ROC | February | GWTP, Sutton/Keswick Header Fluoride Lo alarm, Notified Patrick F, Jack P is currently working on the analyzers | All Water System ROC General | 2026-02-06
ROC | February | VNVCIA - Site Power Fail alarm came in. Checked site. Valve was closing and in local. After about 5 mins, valve went back to auto and alarm cleared. | All Water System ROC General | 2026-02-06
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-06
ROC | February | NMVCBA - Placed valve in manual at 30 L/s 04:15 - Placed valve back to auto | All Water System ROC General | 2026-02-06
ROC | February | QVW34 - Well producing less flow than normal. Placed well manual/off and sent email to area operators to have it inspected. | All Water System ROC General | 2026-02-08
ROC | February | GWTP - ZW2 recovery exceeded recovery setpoint. Alarm status changed to normal while navigating to site. Alarm cleared on acknowledgement. | All Water System ROC General | 2026-02-08
ROC | February | NBW37- Jordan B onsite working on Cl analyzers and Turbidimeter as well as running generator. | All Water System ROC General | 2026-02-05
ROC | February | AUPSWS- Sean P onsite running generator. 09:40- Sean P finished with generator run. Lee F onsite working on pump 4 | All Water System ROC General | 2026-02-03
ROC | February | AUW57- CT Not Achieved Alarm. Called Joe D. Notified that William M is onsite running well to waste for sample | All Water System ROC General | 2026-02-03
ROC | February | NBW5, Turbidity Hi Alarm, Placed well man/off for the time being | All Water System ROC General | 2026-02-03
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-04
ROC | February | AUW14 - Placed wells2 and 3 pumps back to auto. | All Water System ROC General | 2026-02-04
ROC | February | Carter D signing in, -9D/Clear | All Water System ROC General | 2026-02-03
ROC | February | VNPS PD7, Placed pumps 1/4 man/off MAPS PD7, Placed pumps 1/3 in auto | All Water System ROC General | 2026-02-03
ROC | February | Carter Dunn Signing Out | All Water System ROC General | 2026-02-03
ROC | February | ARPS-Martin from OCWA (Peel) is switching pumps. P5 has a leak on the gasket. Martin will start pump 8. | All Water System ROC General | 2026-02-04
ROC | February | MARS, Notified Toronto operator Zoran to go back down to normal flow MKRSEM, Notified Toronto Operator Zoran to stop pumping to the res | All Water System ROC General | 2026-02-04
ROC | February | GWTP, Backpulse Tank 2 Level hi alarm trends show the level higher than normal, Shift report doesn't say to disregard, notified Jack P as RO doesn't have OIC for site, Notified Jack P, directed to disregard for the night consult | All Water System ROC General | 2026-02-04
ROC | February | JFPS - David T. testing flood alarm ANW23 - Stephen B. working on NTU analyzer | All Water System ROC General | 2026-02-04
ROC | February | AUPSOH - Inlet Pipe Heat Trace Fault alarm came in. Called Jason G. who directed to disregard alarm as he will take a look later on in the day #CONSULT | All Water System ROC General | 2026-02-07
ROC | February | RHMCMD - Closed valve to help RHRSTR fill for the interim procedure. | All Water System ROC General | 2026-02-08
ROC | February | Adeela Khan Signing in. Weather: -18C and clear | All Water System ROC General | 2026-02-08
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-04
ROC | February | Christian Van Beek signing out. | All Water System ROC General | 2026-02-04
ROC | February | HLW1 - Ian W working on OIT, disregard Historian Heartbeat alarm. 13:00 Ian W completed work on OIT | All Water System ROC General | 2026-02-04
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-03
ROC | February | NMETHW- Deactivated duty to keep offset with NMETIB | All Water System ROC General | 2026-02-05
ROC | February | NMTKKC- Jason G onsite for work orders. May receive hi sanitary pit, flood alarm, hi/low temp, process room flood. Will also be working on chlorine analyzers later on | All Water System ROC General | 2026-02-05
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-08
ROC | February | NMW15 - Combined Chlorine Lo alarm came in. Checked site. Well is running in schedule mode. Trends indicate a dip in combined levels but came back to optimal range within 2 mins. Alarm cleared | All Water System ROC General | 2026-02-08
ROC | February | NRETCR - Deactivated duty in preparation for interim | All Water System ROC General | 2026-02-08
ROC | February | NBW5 - Effluent Free Chlorine Lo alarm came in. Checked site. Well is active. Monitored site for 10 minutes and effluent free chlorine levels did not recover. Influent levels are within range, but lower than usual. Switched chlorinators so that chlorinator 2 is in duty 1. Will continue to monitor 21:24 - Effluent Free Chlorine LoLo switch alarm came in. Checked site. Effluent chlorine levels did not hi lolo levels. Placed well man/off. Called Jacob M. who will take a look on SCADA. 21:50 - Jacob M. called back to inform he is headed to site. CMU5 Created W11646068 23:30 - Jacob called back to inform that he is finished on site. Jake informed he backflushed well 5 with system water and then restarted the well. Chlorinator 2 has been put back into duty 1. Jake informed this may trigger a hi influent due to this but will readjust shortly. Jake also informed that a turbidity hi may come in due to the backflushing and starting and stopping the well. If a high turbidity occurs and lasts more than an hour, Jake directed to prime each silicate pump. 23:34 - Turbidity Hi alarm came in. Will monitor 00:07 - Placed well back to auto. Turbidity levels have gone back to optimal range and alarm cleared #CONSULT #CMU5 | All Water System ROC General | 2026-02-08
ROC | February | ARPS - David from OCWA Called to inform that he is shutting down pump 2 and will have no flow, as per ARPS Shutdown Interim | All Water System ROC General | 2026-02-08
ROC | February | YWS + NYWS Normal RHMCMD - Placed valve man/open as per interim | All Water System ROC General | 2026-02-08
ROC | February | HLPSYS - Tim H running generator. | All Water System ROC General | 2026-02-03
ROC | February | SHTP- Jacob M onsite for work orders. UV reactor check, Chlorine and turbidity analyzer cleaning, KNMO system inspection. | All Water System ROC General | 2026-02-03
ROC | February | VNETAG- Aaron C switching over network. May receive communication alarms. 11:39- Work is complete | All Water System ROC General | 2026-02-06
ROC | February | GWTP, Activated D1 | All Water System ROC General | 2026-02-04
ROC | February | NMETHW- Combined, Total Chlorine HiHi Alarms. Called Jason G. No answer. Will try again 09:26- Jason G called back. He will look into it. | All Water System ROC General | 2026-02-03
ROC | February | MKRSEM - Called Toronto water (Zoran) and requested start filling Res with 2 pumps. | All Water System ROC General | 2026-02-03
ROC | February | HLW2 - Eric S finished and leaving site. | All Water System ROC General | 2026-02-04
ROC | February | STW12- Placed in auto STW3- Placed in auto | All Water System ROC General | 2026-02-03
ROC | February | NMETHW- Ben H called to request a CMU for Eric S to troubleshoot chlorine analyzer W11634388 CMU5 | All Water System ROC General | 2026-02-03
ROC | February | GWTP - CIP inlet valve failed to open alarm. Patrick F requested reset alarm. | All Water System ROC General | 2026-02-03
ROC | February | BLW12- Joe M onsite with contractors for electrical upgrades. Wells will be Local off. | All Water System ROC General | 2026-02-03
ROC | February | AUPSRR- Ric L finished onsite. Placed chemical pumps back into auto. | All Water System ROC General | 2026-02-03
ROC | February | JFPS - Multiple power related alarms came in. Value immediately turned normal. Generator is not running and site is still connected to generator power. Trending is okay. Will continue to monitor | All Water System ROC General | 2026-02-06
ROC | February | MARS- Ric L onsite for calibrations. | All Water System ROC General | 2026-02-06
ROC | February | KSETDP, BLETNL - Talha H working on OIT, disregard Historian Heartbeat alarms. | All Water System ROC General | 2026-02-03
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-03
ROC | February | KLW34- Eric S onsite working on turbidimeter. 11:46- finished onsite. | All Water System ROC General | 2026-02-06
ROC | February | SHETCS - Eric S on site, working on Hypo tank level and Hypo pump 2. 13:58 Eric S leaving site and heading to NMETHW. | All Water System ROC General | 2026-02-03
ROC | February | Connor Smith signing out | All Water System ROC General | 2026-02-03
ROC | February | Angelica Chepiga signing out | All Water System ROC General | 2026-02-03
ROC | February | AUW14 - Placed well 1 and 4 in auto mode. | All Water System ROC General | 2026-02-04
ROC | February | JFRS - Activated Duty 2. | All Water System ROC General | 2026-02-04
ROC | February | HLW2- Eric S onsite working on effluent, treated and total chlorine analyzers | All Water System ROC General | 2026-02-05
ROC | February | Linear- Rob P called the ROC for an update on the main break in EG. No one called ROC with update. Rob P will call Ryan from EG and update ROC | All Water System ROC General | 2026-02-04
ROC | February | VNETAG - Yash S. on site for planned network work. | All Water System ROC General | 2026-02-04
ROC | February | STPSMR- Travis W onsite running generator. He will place pumps man/off then back on when generator starts up. | All Water System ROC General | 2026-02-03
ROC | February | RHRSTR - Activated duty 1 to help push more water into MARS | All Water System ROC General | 2026-02-09
ROC | February | KSETWB - Jackie S on site performing w/o, including - Chlorine gas leak test, chlorine analyzer maintenance, recirculation pump run, valves exercising. | All Water System ROC General | 2026-02-05
ROC | February | HLW1 - Stephen B on site for chlorine leak alarm test, chlorine analyzers maintenance. | All Water System ROC General | 2026-02-05
ROC | February | YWS+NYWS normal 22:10-Linear- Cory from GIP (416-677-7682) req York Region OPs to attend site to throttle down main to complete repair. Notified Rob P who will head to site. Notified Cory that Rob P will be on site within the hour 22:10-GWTP- Back pulse tank fill failed to close alarm. Valve showing closed and tank not filling,. Reset alarm. | All Water System ROC General | 2026-02-04
ROC | February | NMMCBR- Upstream pressure lolo alarm came in. Called Rob P to confirm it was caused by work going on to fix main. ROB P closed valve in area to help EG repair main. #consult | All Water System ROC General | 2026-02-04
ROC | February | YWS+NYWS normal | All Water System ROC General | 2026-02-05
ROC | February | NMTKKC- Ammonia P1 failed to start alarm. reset alarm | All Water System ROC General | 2026-02-05
ROC | February | ARPS - Peel Ammonia analyzer airport road discharge free ammonia fault alarm came in. Called Peel spoke with Bineesh. No issues with ammonia system cleared alarm | All Water System ROC General | 2026-02-05
ROC | February | YWS + NYWS normal | All Water System ROC General | 2026-02-09
ROC | February | MAP8 - Rick L. doing annual calibrations. Duty just deactivated, placed pumps man/off AUW14 - AU central just activated, will place W2 and 3 man/on. Notified Joe D. | All Water System ROC General | 2026-02-04
ROC | February | Adam Button signing out | All Water System ROC General | 2026-02-05
ROC | February | GWTP - Keswick and Sutton Header Fluoride Lo alarms came in. Disregarded as per Joe M. | All Water System ROC General | 2026-02-05
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-09
ROC | February | GWTP - Pressurized Vestibule Lo Temp alarm came in. Higher priority alarm. Called Joe M. who directed to disregard alarm for the night #CONSULT | All Water System ROC General | 2026-02-07
ROC | February | Christian Van Beek signing in. Weather: -22C and clear. | All Water System ROC General | 2026-02-07
ROC | February | VNRSKS - Activated duty 1. | All Water System ROC General | 2026-02-07
ROC | February | GWTP - Sutton Header fluoride low. Value is not recovering as expected, fluoride pump 1 still pushing flow at the same interval. Called Joe M who directed to increase the fluoride pump 1 dosing factor from 1.00 to 1.05 and wait one hour. If the value does not recover Joe would like to be contacted. #consult | All Water System ROC General | 2026-02-07
ROC | February | ARPS- Peter from OCWA called and is rotating pumps. | All Water System ROC General | 2026-02-05
ROC | February | SHTP - Jacob M working on chlorine system, testing chlorine leak alarm and running generator. | All Water System ROC General | 2026-02-05
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-07
ROC | February | HLW2 - Ian W working on OIT, disregard Historian Heartbeat alarm. | All Water System ROC General | 2026-02-04
ROC | February | GRTPLL - Raw water total chlorine Res HiHi alarm, value back to normal. Cleared alarm. Disregard as per shift report. | All Water System ROC General | 2026-02-04
ROC | February | ARPS- Peter from OCWA called.. Working on Free and Total Ammonia analyzers. Will return to normal shortly | All Water System ROC General | 2026-02-06
ROC | February | AUPSRR - Post injection free chlorine hihi. Checked site, trending shows a spike of the post injection free chlorine reading which dropped to normal range within one reading interval. Reset alarm. | All Water System ROC General | 2026-02-04
ROC | February | Gluzen Ramos Ong signing out | All Water System ROC General | 2026-02-04
ROC | February | AUETFC - Joe D headed to site for sampling. Joe D directed to deactivate the duty so the tower is draining. | All Water System ROC General | 2026-02-04
ROC | February | YWS + NYWS normal | All Water System ROC General | 2026-02-07
ROC | February | STW3 - Influent and Effluent Free chlorine Hi alarm came in. Monitored site for 15 mins. Levels kept rising. Lowered Chlorinator 1 dosing factor to 260. Will monitor | All Water System ROC General | 2026-02-07
ROC | February | STRS48 - High lift pump 1 failed to stop alarm at duty stop. Cleared alarm. | All Water System ROC General | 2026-02-05
ROC | February | ARPS- Peter from OCWA called. Pump 5 shutdown. Working on getting another pump going. 14:45- Peter called back. Pump 4 running in auto. Back to normal operations. | All Water System ROC General | 2026-02-06
ROC | February | QVW34- Yash S onsite. Disregard comm fails. | All Water System ROC General | 2026-02-05
ROC | February | QVW3, Tyler Z on site, doing some well maint, Will M has talked with Tyler Z on running the well in man/on. Tyler Z will call when he is finished working on the site | All Water System ROC General | 2026-02-06
ROC | February | RHPSWA - Karen from property services called to inform that security has received several security intrusion alarms from site. Karen stated that there is a door that is usually held closed by a key padlock and latch however half of the latch is missing and can no longer be locked. Karen requested that area operations be consulted to determine Contacted Jacob M who was unfamiliar with why the latch would be missing its connection. Karen stated that directing security to disregard the security intrusion alarm is an option. Jacob was not able to make that decision and requested that the situation be escalated to water on call management. Contacted Aaron W who directed to have the area ops on call operator attend site to determine if they can prop the door shut to complete a tight seal and prevent the security intrusion alarms from triggering. If that fails Aaron W wants on call mechanical to attend site to replace the broken latch. Contacted Joe D to dispatch. Created CMU5#W11645836 #consult #CMU5 | All Water System ROC General | 2026-02-07
ROC | February | GWTP - Sutton header fluoride low. Called Joe M who directed to leave the dosing where it is for the weekend. #consult | All Water System ROC General | 2026-02-07
ROC | February | RHPSWA - Joe D leaving site. Joe worked with Security to secure the location and prevent further intrusion alarms from triggering. Joe stated that with this door secured if any more security intrusion alarms trigger security should attend site. | All Water System ROC General | 2026-02-07
ROC | February | STW3 - Influent Free Chlorine Hi alarm came in. Checked site. Duty recently activated. Level is just above the hi level. Will continue to monitor site 02:13 - Both Effluent Free Chlorine Hi and Influent Free Chlorine Hi alarms came in. Checked site. After 15 mins, levels came back to optimal range and alarms cleared | All Water System ROC General | 2026-02-05
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-06
ROC | February | AURSBS - Activated duty 1 | All Water System ROC General | 2026-02-06
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-06
ROC | February | Adeela Khan signing out | All Water System ROC General | 2026-02-06
ROC | February | KSTKWP, Jerry Z on site working on the Cl2 analyzers | All Water System ROC General | 2026-02-06
ROC | February | QVW34- Historian Heartbeat Alarm. Notified Ian W. He will take a look. Spoke with Tyler ZJ. Well 3 can go back into auto and well 4 to remain man/off | All Water System ROC General | 2026-02-06
ROC | February | MARS - Level low alarm. Activated BVPS and swapped supply pumps to VNRSKS to VNPS. | All Water System ROC General | 2026-02-07
ROC | February | NBW3 - Influent free chlorine lolo alarm. Checked site, well recently activated for schedule mode. Trending shows the influent free chlorine reading dropped on start up. Placed well in manual mode. Monitoring site to determine if the influent reading will recover. 13:13 - NBW37 - Influent free chlorine reading has recovered. Able to clear alarms. Placed hypo pump 2 back in duty 1 and activated the well. Monitored start up. | All Water System ROC General | 2026-02-07
ROC | February | QVW12 - Treated free chlorine hihi alarm. Checked site, well recently activated to fill system. Trending shows a spike of the treated free chlorine residual. Rotated ammonia pump duty and monitored. | All Water System ROC General | 2026-02-07
ROC | February | NMW136 - Well 16 pump fault alarm. Checked site, unable to clear alarm. Rotated duty 1 to pump 16. | All Water System ROC General | 2026-02-07
ROC | February | STW1 - Placed well pump in auto. | All Water System ROC General | 2026-02-07
ROC | February | MKRSEM - Low level alarm. Called Toronto Water (Brett) and requested they activate two pumps to push flow to MKRSEM. | All Water System ROC General | 2026-02-07
ROC | February | Adeela Khan signing in. Weather: -19C and clear | All Water System ROC General | 2026-02-07
ROC | February | KSTP - Jerry Z running generator. | All Water System ROC General | 2026-02-05
ROC | February | JFRS - Dave T on site to complete a low temp alarm test and a generator test run. | All Water System ROC General | 2026-02-04
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-06
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-08
ROC | February | AUPSOH - Inlet Pipe Heat Trace Fault alarm came in. Checked site. Trending is okay. Will continue to monitor AUETFC - Inlet Line Standby Heat Trace alarm came in. Checked site. Trending is okay. Inlet and outlet heat trace is on. The standby has faulted. Shift report directs to disregard alarm | All Water System ROC General | 2026-02-08
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-08
ROC | February | 01:00 - EZ MAX ISSUES 01:35 - MKRSEM - Called Toronto Water (Brett) and requested to stop pumping to reservoir 02:00 - EZMAX Issues resolved | All Water System ROC General | 2026-02-08
ROC | February | YWS + NYWS Normal KCETDS - Activated duty 1 in preparation for MAPS to JFRS Feed run | All Water System ROC General | 2026-02-07
ROC | February | Town of East Gwillimbury operator (Ryan) called to inform of a watermain break on Yonge St south of Green Lane. Informed Dwayne L who sent Rob P to site. Created CMU5#W11639194 for Rob P. #CMU5 MAPS - Rick L finished annual calibrations and normal operations can resume. | All Water System ROC General | 2026-02-04
ROC | February | JFRS - Deactivated duty 1 and 2 | All Water System ROC General | 2026-02-08
ROC | February | NMETIB - Heat Trace Controller 1 Fault alarm came in. Both heat trace controllers have faulted and is extremely cold. Called Joe D. but no answer. Will try again 02:38 - Called Joe D. again. Joe informed that he will take a look in the morning but to keep on the level trending. If any more issues arise, Joe would like a call back #CONSULT | All Water System ROC General | 2026-02-08
ROC | February | NMETHW - Riser Pipe Heat Trace Controller 1 and 2 Fault alarms came in. Checked site. Trending is okay. Will send an email to Joe D. | All Water System ROC General | 2026-02-08
ROC | February | Carter D Signing in | All Water System ROC General | 2026-02-06
ROC | February | Connor Smith signing in -8C Clear | All Water System ROC General | 2026-02-06
ROC | February | STW12- Placed well 2 back into auto STW3- Placed well 3 back into auto | All Water System ROC General | 2026-02-05
ROC | February | NRETCR - Activated duty 1 for the interim procedure. | All Water System ROC General | 2026-02-04
ROC | February | YWS + NYWS Normal KCETFS - Ian W leaving site. Communications and trending have been restored. Ian directed to disregard the historian heartbeat alarm for the night. | All Water System ROC General | 2026-02-09
ROC | February | KCETDS - Outlet total chlorine residual lolo alarm. Checked site, trending shows a sudden dip of the total chlorine residual reading. The reading recovered within two reading intervals. Reset alarm. | All Water System ROC General | 2026-02-09
ROC | February | NMNPSKC - PAC comm fail alarm. Checked site, operations appear normal. Trending not impacted. Alarm cleared. | All Water System ROC General | 2026-02-09
ROC | February | YWS + NYWS Normal Connor Smith signing out | All Water System ROC General | 2026-02-05
ROC | February | ARPS - ROYKS to ROPKS comm failure alarm - cleared right away | All Water System ROC General | 2026-02-05
ROC | February | Angelica Chepiga signing in | All Water System ROC General | 2026-02-09
ROC | February | NMETRIB - Deactivated duty 1. NMVCBA/NMVCIB - Reverted setpoint changes. | All Water System ROC General | 2026-02-09
ROC | February | MKRSEM - Called Toronto Water (Paul) and requested they stop pumping to MKRSEM. | All Water System ROC General | 2026-02-10
ROC | February | NRETCR, Activated D1 JFRS, Will activate D1 once level hits 80% for interim procedure NMTKBS, Activated D1 | All Water System ROC General | 2026-02-04
ROC | February | AUW14- Placed wells back into auto. | All Water System ROC General | 2026-02-06
ROC | February | ARPS- Peter from OCWA Called and is rotating transfer pumps. | All Water System ROC General | 2026-02-06
ROC | February | RHPSPA - Hydro power failure alarm. Checked site, generator is not running and ATS is pointing to utility hydro. One pump reactivated in duty 1. Cleared alarms and placed a second pump in duty 1. JFPS - WPS GEN xfer switch hydro power alarm. Checked site, generator not running and ATS pointing to utility hydro. Power blip affected Richmond Hil facilities. Pumps were not active when alarm came in. Cleared alarms. RHRSWA - Control panel power failure alarm. Power blip in Richmond Hill. Site operations normal, cleared alarm. MMW1 - Control panel power failure alarm, Well 8 high level and well 13 high level alarms. Re-activated well pumps 8 and 13. Cleared alarms when level dropped. | All Water System ROC General | 2026-02-10
ROC | February | JFPS - Tyler ZJ working on P1 motor. | All Water System ROC General | 2026-02-03
ROC | February | VNRSKS - Placed all VNPS PD7 pumps man/off and placed MAPS PD7 pumps in auto | All Water System ROC General | 2026-02-06
ROC | February | STETBR - Tower Level Lo alarm came in. Placed STW12 and STW3 man/on as per interim | All Water System ROC General | 2026-02-07
ROC | February | NMETIB - Activated duty to help offset with NMETHW | All Water System ROC General | 2026-02-07
ROC | February | RHPSPA - Lee F on site for pumps vibration test. Requested Pumps 2&3 to duty 4, Pumps 1&4 to duty 1. | All Water System ROC General | 2026-02-03
ROC | February | ANW23- Stephen B leaving site. Generator is still running. Will be back onsite in roughly 40 minutes. Requested a call for any issues. | All Water System ROC General | 2026-02-03
ROC | February | GWTP- ZW4 Memb Air Inlet V Failed to Close, Membrane Air Valve Failed, Shutdown. Notified Patrick F. He will look into it. | All Water System ROC General | 2026-02-03
ROC | February | Angelica Chepiga signing in, weather -15C | All Water System ROC General | 2026-02-04
ROC | February | Carter Dunn Signing Out | All Water System ROC General | 2026-02-04
ROC | February | VNPS- Tim H onsite for work on chlorine analyzers. Requested to activate RHRSTR duty. | All Water System ROC General | 2026-02-05
ROC | February | KSTP - Technician from Black and MacDonald called. He is on site for CO2 system maintenance. Requested to send OP to open the gate. Notified Joe M. He contacted contractor (Bernard 905 301 4919). Work rescheduled for tomorrow. Joe M directed HL pumps man/off. Plant is off for the night. # Consult | All Water System ROC General | 2026-02-04
ROC | February | YWS + NYWS NORMAL | All Water System ROC General | 2026-02-05
ROC | February | AUW14 - Placed all wells man/off | All Water System ROC General | 2026-02-06
ROC | February | GWTP- Back pulse fill V failed to close alarm came in again notified Joe M. Directed to clear alarm if it comes in as long as valve closes #consult | All Water System ROC General | 2026-02-04
ROC | February | GWTP- ZW5 recovery exceeded recovery SP. Alarm cleared upon acknowledgment | All Water System ROC General | 2026-02-05
ROC | February | AUW14- Placed wells 1-4 in man/off | All Water System ROC General | 2026-02-05
ROC | February | Connor Smith signing in | All Water System ROC General | 2026-02-05
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-03
ROC | February | NMMCBR- Rob P notified ROC they are done on site EG flushing as valve has been reopened in system. | All Water System ROC General | 2026-02-05
ROC | February | YWS+NYWS normal | All Water System ROC General | 2026-02-05
ROC | February | KSSP- Mem oper area MUA 10 temp switch lo alarm. Disregard on shift report | All Water System ROC General | 2026-02-05
ROC | February | VNRSKS - Activated Duty 1 to keep BVPS pumps running. | All Water System ROC General | 2026-02-09
ROC | February | NMTKKC - Sanitary pump station high level alarm, notified Joe D. Ian W confirmed- sanitary pump is running. | All Water System ROC General | 2026-02-09
ROC | February | MARS, Rick L on site doing calibrations to the LIT, Notified Toronto operator Pooja and ARPS Operator Peter that there is work being done on the LIT and that it should be disregarded till the work is completed 13:15, Rick L is finished on site, notified Toronto and ARPS that the work is finished | All Water System ROC General | 2026-02-06
ROC | February | QVW34 - Treated total chlorine low alarm. Wells not running, No water directed to users. Alarm cleared in two readings. | All Water System ROC General | 2026-02-04
ROC | February | YWS+NYWS normal | All Water System ROC General | 2026-02-05
ROC | February | RHRSTR - Activated duty 1 to fill system for the interim procedure | All Water System ROC General | 2026-02-04
ROC | February | SHTP - UV reactor 3 minor fault alarm, Jacob M requested disregard minor faults alarms from UV1,UV3. | All Water System ROC General | 2026-02-03
ROC | February | SHTP - Treated Water Turbidity Fault alarm came in. Checked site. High lifts are not running. Called Jacob M. who will take a look 23:31 - Jacob M. called back to inform that this can be disregarded for the night. Jacob would like a call back if this starts to interlock any of the pumps #CONSULT | All Water System ROC General | 2026-02-06
ROC | February | NMETIB - Activated duty 1 to help offset with NMETHW | All Water System ROC General | 2026-02-09
ROC | February | VNPS/RHRSTR - Yash S. on site for planned network work. Deactivated BVPS and VNP8, placed pumps man/off | All Water System ROC General | 2026-02-04
ROC | February | AURSBS - Activated duty 1 | All Water System ROC General | 2026-02-07
ROC | February | STW12 - Joe M requested man/start well 2 pump. | All Water System ROC General | 2026-02-09
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-06
ROC | February | ANW23 - Stephen B on site for generator run , chlorine analyzers maintenance and Health and Safety inspection. | All Water System ROC General | 2026-02-03
ROC | February | YWS + NYWS NORMAL | All Water System ROC General | 2026-02-03
ROC | February | RHRSWA- Cell 2 Valve Fault Alarm. Came in during power blip. Valve is Local Open. Notified Tim H. He will reset tomorrow. | All Water System ROC General | 2026-02-03
ROC | February | RHPSPA - Discharge header flow 1 LoLo alarm. Checked site, duty just deactivated and the pumps shut down. Cleared alarms. | All Water System ROC General | 2026-02-04
ROC | February | GWTP- Patrick F working on compressors. Disregard Low pressure alarms. | All Water System ROC General | 2026-02-05
ROC | February | MTETNL, Sean P on site, disregard intrusion alarms | All Water System ROC General | 2026-02-06
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-07
ROC | February | NBET27 - Outlet temp lolo alarm. Checked site, trending shows the outlet water temperature slowly dropping. No indication of a heat trace fault. Contacted Jacob M who will check SCADA. 13:00 - NBET27 - Jake M will monitor the situation for one hour and call back. #consult | All Water System ROC General | 2026-02-07
ROC | February | Initiating MAPS to JFRS feed run - Placed KCPSDS pumps man/off - Placed VNPS PD8 and MAPS PD8 pumps man/off - Placed VC MV3 into man - Placed AURSBS Res MV4 to man and close - Man/start pump 1 at MAPS 04:54 - Reverted all changes | All Water System ROC General | 2026-02-08
ROC | February | YWS + NYWS Normal Adeela Khan signing out | All Water System ROC General | 2026-02-07
ROC | February | MTW3- Phil D onsite for Cl analyzer maintenance and running generator. | All Water System ROC General | 2026-02-05
ROC | February | GWTP - ZW6 membrane tank hi level alarm. Spoke with Patrick F who stated the alarm will clear itself once the neutralization process is complete. | All Water System ROC General | 2026-02-04
ROC | February | STETBR-Tower level lo STW12/3- Placed P2/3 in man/on as per interim | All Water System ROC General | 2026-02-04
ROC | February | AUW14- Joe D placed pumps man/off, working on chemical system. | All Water System ROC General | 2026-02-05
ROC | February | NMETHW- Eric S onsite working on Total Chlorine Analyzer 16:06- Eric S finished onsite | All Water System ROC General | 2026-02-03
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-08
ROC | February | Carter D Signing Out | All Water System ROC General | 2026-02-06
ROC | February | KSTP- Jerry Z and Patrick F on site for generator training. | All Water System ROC General | 2026-02-03
ROC | February | KSTP- Carbon Dioxide HiHi Alarm. Notified Jack P. Can disregard. While on the phone alarm cleared. Can disregard if it comes back in. CONSULT | All Water System ROC General | 2026-02-03
ROC | February | NMETHW - Duty 1 just activated, deactivated NMETIB Duty 1 to offset towers. Reverted system changes. NMETIB duty 1 stop from 85 back to 75% and NMVCBA flow from 20 back to 40l/s. Confirmed with Cole W. | All Water System ROC General | 2026-02-04
ROC | February | KSETDP - Sean P. working on influent pH meter. Site offline | All Water System ROC General | 2026-02-09
ROC | February | Angelica Chepiga signing in,weather -5C | All Water System ROC General | 2026-02-03
ROC | February | Adeela Khan signing in. Weather: -8C and Cloudy | All Water System ROC General | 2026-02-05
ROC | February | MAPS PD7 - pump 3 uncommanded stop alarm. Checked site, pump 1 has activated and is pushing flow. Pump 2,3,4 all interlocked on the pump 3 shutdown. Waited for interlock to clear and reset alarms. Duty 1 rotated to pump 2, monitored pump start. | All Water System ROC General | 2026-02-07
ROC | February | GWTP - Sutton header fluoride low alarm. Checked site, Sutton system is filling. Trending shows a dip of the fluoride reading which recovered slightly. Will monitor site. | All Water System ROC General | 2026-02-07
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-07
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-07
ROC | February | KCETDS - Combine chlorine Low alarm, quick dip, value back to normal, cleared alarm. | All Water System ROC General | 2026-02-09
ROC | February | MKRSEM- Called Metro spoke with Mehdi to stop pumping to reservoir | All Water System ROC General | 2026-02-05
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-05
ROC | February | STETBR - Tower Level Hi alarm came in. Placed STW2 and STW3 back to auto, as per interim procedure | All Water System ROC General | 2026-02-09
ROC | February | NMW12 - Silicate pump 1 uncommanded stop and leakage alarm. Checked site, well recently activated, duty rotated to silicate pump 2. Will monitor silicate tank level to determine if silicate is leaking through possible broken lines. Sent email to OCO. | All Water System ROC General | 2026-02-07
ROC | February | NMVCBA - Placed valve in manual at 40 L/s | All Water System ROC General | 2026-02-07
ROC | February | GWTP - Sutton Header Fluoride Low alarm. Notified Patrick F, he is on site. | All Water System ROC General | 2026-02-09
ROC | February | HUB 2 Server - Kyle C restarting server. QVW34 - Tyler ZJ working on pumps, will run pumps. William M on site monitoring. | All Water System ROC General | 2026-02-09
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-10
ROC | February | JFRS - Activated duty 1 to keep reservoir high for the interim procedure. | All Water System ROC General | 2026-02-08
ROC | February | JFRS - Activated duty 2. | All Water System ROC General | 2026-02-08
ROC | February | NRETCR - Activated duty 1 to fill the towers for the interim procedure. | All Water System ROC General | 2026-02-08
ROC | February | RHRSTR - Activated duty 1 to maintain reservoir level for the interim procedure. | All Water System ROC General | 2026-02-08
ROC | February | STW3 - Influent free chlorine hi alarm. Checked site, well recently activated. Noted that the dosing setpoint for the active chlorinator is higher than the desired setpoint. Re-applied the initial setpoint and monitored site. 10:33 - STW3 - Effluent free chlorine hi alarm triggered as the initial spike of free chlorine exits the contact tank. The influent free chlorine reading is dropping following the dosage changes made. Monitoring site. | All Water System ROC General | 2026-02-08
ROC | February | AURSBS - Activated duty 1. | All Water System ROC General | 2026-02-08
ROC | February | NBW3 - Influent free chlorine lolo alarm. Checked site, well activated in schedule mode. Trending shows a sudden drop of the influent free chlorine reading on well start. Influent free chlorine residual recovered quickly. Cleared alarms, returned hypo pump 2 to duty 1 and reset alarm. Monitored well activation. | All Water System ROC General | 2026-02-08
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-08
ROC | February | MKPSSA, Combined Cl2 Residual lolo, Pumping Station is offline at this time, very little water going through the analyzer, Travis W was on site and took a grab sample | All Water System ROC General | 2026-02-09
ROC | February | NMETIB - Activated duty 1 to keep level offset from NMETHW. | All Water System ROC General | 2026-02-08
ROC | February | VNRSKS - Swapped supply pumps to two MAPS pumps. | All Water System ROC General | 2026-02-08
ROC | February | NBW3 - Influent Free Chlorine LoLo switch alarm came in. Checked site. Duty just activated. Well locked out on duty start. After 5 mins, influent levels came back to optimal range. 19:43 - Cleared alarms after 10 mins. Well re activated and will monitor | All Water System ROC General | 2026-02-08
ROC | February | NMVCBA - Placed valve man/open at 40 L/s 04:07 - Placed valve back to auto | All Water System ROC General | 2026-02-05
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-06
ROC | February | KSTP - post chlorinator 2 low vacuum alarm. Checked site, post chlorinator 1 rotated into duty 1 and is operating. Able to clear alarm. | All Water System ROC General | 2026-02-08
ROC | February | NMW1/2/13/16/15, Placed wells back to auto. Jason G called saying everyone is working well on his end and things can go back to normal operation. Notified Jason G that well 13 is faulted at this current time, he will look into it NMTKKC, Activated D1 to have the system filling for Jason G | All Water System ROC General | 2026-02-09
ROC | February | MARS - Parth P. and Rick L. continuing annual calibrations on analyzers and generator LITs | All Water System ROC General | 2026-02-09
ROC | February | NMETIB - Activated Duty 1 to offset with NMETHW, ok with William M. | All Water System ROC General | 2026-02-09
ROC | February | YWS + NYWS Normal VNRSKS - Swapped supply pump to one MAPS one VNPS pump. | All Water System ROC General | 2026-02-10
ROC | February | KSTP - Settle water turbidity hihi alarm. Plant offline for the night, no water directed to users and no operations on site. | All Water System ROC General | 2026-02-10
ROC | February | JFPS- Generator Running Status Alarm. Will notify Ops RHMCMD- Valve 1 Fault ALarm. Pac Control Power Fail. Alarm cleared RHRSWA- Power fail. Alarm cleared | All Water System ROC General | 2026-02-03
ROC | February | HLETPR- Jordan onsite testing low temp | All Water System ROC General | 2026-02-03
ROC | February | GTWP - ZW8 recovery - Exceeded Recovery SP. Checked site, ZW8 completing a backwash sequence. Alarm status changed to normal while checking site. Alarm cleared on acknowledgement. | All Water System ROC General | 2026-02-07
ROC | February | JFPS- Power Fail. Alarm cleared RHMCMD- Power Fail. Alarm cleared. RHPSWA- Power Fail. Alarm cleared RHRSWA- Power Fail. Alarm cleared RHPSPA- Power Fail. Alarm cleared BVPS- Pump 1 Failed to start. Alarm cleared | All Water System ROC General | 2026-02-05
ROC | February | BLETNL- Kyle C updating OIT, disregard heartbeat alarms until further notice. 13:00 Kyle C completed work | All Water System ROC General | 2026-02-05
ROC | February | MKRSEM- Called Toronto (Paul) and requested pumps on. | All Water System ROC General | 2026-02-05
ROC | February | Angelica Chepiga signing out | All Water System ROC General | 2026-02-05
ROC | February | YWS+NYWS normal | All Water System ROC General | 2026-02-05
ROC | February | MKRSEM - low level alarm. Called Toronto Water (Paul) and requested they activate two pumps to push flow to MKRSEM. | All Water System ROC General | 2026-02-04
ROC | February | Gluzen Ramos Ong signing in | All Water System ROC General | 2026-02-09
ROC | February | AUW14 - Placed pumps 1&4 back to auto. | All Water System ROC General | 2026-02-09
ROC | February | HLW2 - Placed well in auto. | All Water System ROC General | 2026-02-04
ROC | February | Carter D Signing In, -24D/Clear | All Water System ROC General | 2026-02-09
ROC | February | SHTP, KMNO Pump 2 Leak/Fault, Notified Jacob M, he will look into it | All Water System ROC General | 2026-02-09
ROC | February | BLW3 - Kyle C working on new PLC, performing tests, disregard Historian Heartbeat alarm. 09:00 Dan Z on site with Kyle C for testing. Monitoring. | All Water System ROC General | 2026-02-09
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-09
ROC | February | YWS + NYWS Normal Carter D Signing Out | All Water System ROC General | 2026-02-09
ROC | February | Christian Van Beek signing in. Weather: -9 C and clear. | All Water System ROC General | 2026-02-09
ROC | February | VNPS - Tim H running generator , will attend re- chlor after for chlorine analyzers maintenance and chlorine leak alarm test. | All Water System ROC General | 2026-02-05
ROC | February | STETTL - Joe M cleaning chlorine analyzers and performing Health and Safety inspection. | All Water System ROC General | 2026-02-05
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-07
ROC | February | KCETDS - Inlet Riser Heat Tracing Fault alarm came in. Checked site. Duty recently activated. Checked trends and trending is okay. Called Jacob M. who directed to continue monitoring tower and to give a call back if level starts flatlining #CONSULT | All Water System ROC General | 2026-02-07
ROC | February | ARPS - Airport Rd Discharge Flow lo alarm came in. Activated duty at KLET27 as per interim | All Water System ROC General | 2026-02-07
ROC | February | STETBR - Tower level low alarm. Placed STW2 and STW3 in manual mode. | All Water System ROC General | 2026-02-08
ROC | February | NMVCBA - Placed valve man/open at 40 L/s 01:58 - Placed valve back to auto | All Water System ROC General | 2026-02-08
ROC | February | GWTP - Train 2 - transmembrane pressure lo alarm. Alarm status changed to normal shortly after the alarm triggered. Alarm reset on acknowledgement. | All Water System ROC General | 2026-02-09
ROC | February | AUW14 - Joe D and Lee F completed work , site is back to normal OP. | All Water System ROC General | 2026-02-05
ROC | February | STETBR - Joe M cleaning chlorine analyzers , performing Health and Safety inspection. | All Water System ROC General | 2026-02-05
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-09
ROC | February | NMW12 - Silicate pump 1 leakage alarm outstanding. Alex B working on it. # CMU5 W11649902 | All Water System ROC General | 2026-02-09
ROC | February | NBW5 - Jordan B working on chlorinator 1. | All Water System ROC General | 2026-02-09
ROC | February | MARS, Parth P has finished annual calibrations | All Water System ROC General | 2026-02-09
ROC | February | NMVCBA, Placed valve in manual and set the flow to 40L/sec | All Water System ROC General | 2026-02-09
ROC | February | NMETIB - Increased Duty stop from 75% to 85% and lowered NMVCBA flow from 40 to 20l/s, confirmed with Cole W. | All Water System ROC General | 2026-02-04
ROC | February | VNPS PD7 - Pump 3 man/off MAPS PD7 - Pump 1 to auto. | All Water System ROC General | 2026-02-05
ROC | February | NRETCR - Activated duty 1 | All Water System ROC General | 2026-02-08
ROC | February | MARS - Adjusted low level alarm setpoint from 55% to 60% for the interim procedure. | All Water System ROC General | 2026-02-08
ROC | February | NMETIB - activated duty 1@ 51% as per Alex B. to offset with NMETHW. | All Water System ROC General | 2026-02-04
ROC | February | STETBR - Wess from town of Stouffville flushing in zone 1. Notified Joe M. | All Water System ROC General | 2026-02-04
ROC | February | Angelica Chepiga signing in, weather -12C | All Water System ROC General | 2026-02-05
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-07
ROC | February | VNRSKS - Swapped supply pumps from two MAPS pumps to one MAPS one VNPS. | All Water System ROC General | 2026-02-07
ROC | February | GWTP - Sutton header fluoride low alarm. Value has not recovered. Contacted Joe M again and he directed to increase dosing factor from 1.05 to 1.10 and monitor for another hour. #consult | All Water System ROC General | 2026-02-07
ROC | February | MARS - Called Toronto Water (Poriya) and requested to increase flow | All Water System ROC General | 2026-02-09
ROC | February | BLW34, Dan Z is leaving site, Kyle C is still working on the historian heartbeat | All Water System ROC General | 2026-02-09
ROC | February | STW12, STW3 - Placed manual/ currently running for STETBR fill cycle. | All Water System ROC General | 2026-02-09
ROC | February | MKRSEM, Notified Toronto operator paul to start filling the res | All Water System ROC General | 2026-02-09
ROC | February | NMVCBA, Placed valve to 80L/sec NMVCIB, Placed valve to 40L/sec ROC doing this to help offset the towers as both are active | All Water System ROC General | 2026-02-09
ROC | February | NRETBR - Heat Trace 2 Fault alarm came in. Checked site. Tower is draining. Heat Trace 1 is on and normal. Tower is still trending. Will call out if tower starts flatlining | All Water System ROC General | 2026-02-09
ROC | February | AUPSRR- Ric L onsite for calibrations. Deactivated AURSOH and placed Ridge Road chemical pumps in manual after confirming with with Jason G. | All Water System ROC General | 2026-02-03
ROC | February | MAPS PD7 pumps 1&3 man/off VNPS PD7 pumps 1&4 to auto | All Water System ROC General | 2026-02-05
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-03
ROC | February | ARPS - Peel OCWA (Peter) called to inform they are completing the daily pump rotation. | All Water System ROC General | 2026-02-04
ROC | February | NMTKKC, Contractor on site notified ROC that the card reader isn't working, notified Security, they will look into it. Site is back to normal | All Water System ROC General | 2026-02-09
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-09
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-10
ROC | February | MARS - Cross Connect valve uncom. Close alarm. Cole W requested disregard alarm. valve local/closed. | All Water System ROC General | 2026-02-09
ROC | February | MARS, Notified Toronto operator Zoran to increase the flow to MARS as both sites that take water from the res are active and are drawing it down at a decent rate | All Water System ROC General | 2026-02-03
ROC | February | AUW14, Deactivated D1 AURSBS, Deactivated D1 VNRSKS, Deactivated D1 | All Water System ROC General | 2026-02-03
ROC | February | JFRS - activated duty 2. | All Water System ROC General | 2026-02-04
ROC | February | VNRSKS- Deactivated D1 VNPS PD7- placed P1/4 in man/off MAPS PD7- placed P1/3 in auto | All Water System ROC General | 2026-02-04
ROC | February | Adeela Khan signing out | All Water System ROC General | 2026-02-09
ROC | February | NBET27 - Outlet temp lolo. Jake M called back to inform that he will not be attending site. Jake directed to continue to monitor site and if the temperature continues to decrease to monitor the fill and drain cycles. | All Water System ROC General | 2026-02-07
ROC | February | NMETIB- Deactivated duty. | All Water System ROC General | 2026-02-06
ROC | February | HLW2- Stephen B requested to place chlorinators from "all stop" to "disabled" mode for duty change/rotation so that chlorinator 1 will run over the weekend. | All Water System ROC General | 2026-02-06
ROC | February | NMETHW - Activated duty 1. | All Water System ROC General | 2026-02-07
ROC | February | GWTP- Generator Alarm. Jack P working on it with contractor. Patrick F working on fluoride probes. | All Water System ROC General | 2026-02-05
ROC | February | NMW136 - Influent free chlorine hihi alarm. Checked site, well recently activated. Trending shows that the influent free chlorine reading spiked and then returned to normal range within two reading intervals. Reset alarm. | All Water System ROC General | 2026-02-04
ROC | February | HLW2 - Eric S on site , working on chlorine analyzers. Placed well 2 pump man/off . | All Water System ROC General | 2026-02-04
ROC | February | MAPS PD7 - Pumps 1&3 man/off VNPS PD7 - Pumps 1&4 to auto. | All Water System ROC General | 2026-02-04
ROC | February | RHRSWA - Power failure alarm/restored,alarm cleared. RHPSPA - pumps stopped and restarted/ generator off. | All Water System ROC General | 2026-02-03
ROC | February | Christian Van Beek signing in. | All Water System ROC General | 2026-02-04
ROC | February | NBW3 - well 7 pump on schedule mode, Influent chlorine residual low/low lockout, value back to normal. Cleared alarms and restarted well 7 pump. | All Water System ROC General | 2026-02-09
ROC | February | NMTKKC - Jason G called with update, Ian W on site powered UPS, Jason G collected grab sample. | All Water System ROC General | 2026-02-09
ROC | February | NBW3- Influent Free Chlorine LoLo. Well interlocked on schedule mode start up. Reset alarms and well started back up. | All Water System ROC General | 2026-02-06
ROC | February | AUPSRR - Post Injection Free Chlorine Hi alarm came in. Checked site. Noticed levels are back to optimal range. Trends indicate a slight spike and then comes back down. Cleared alarm | All Water System ROC General | 2026-02-05
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-05
ROC | February | JFPS- Tyler S called. Pump 1 will remain OOS Local off RHPSWA- Tyler S also notified that Pump 1 will remain Local off | All Water System ROC General | 2026-02-03
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-04
ROC | February | YWS+NYWS Normal 20:38- GWTP- Backpulse tank 2 level hi alarm. Notified Joe M. Directed to backwash train 1 and activate KSTKWP Duty #consult | All Water System ROC General | 2026-02-04
ROC | February | MAPS- PD7 P2 Disch. Valve 1 Uncmd Close, PD7 P2 Uncmd Stop. Pump 3 took over in duty 1. | All Water System ROC General | 2026-02-03
ROC | February | GWTP - Joe M. called and directed to activated duty 1. Joe also informed that if a lo fluoride alarm comes in, it can be disregarded. Joe would like a call back if the LoLo alarm comes in | All Water System ROC General | 2026-02-05
ROC | February | QVETQS- William M onsite testing hi and low level alarms. | All Water System ROC General | 2026-02-06
ROC | February | AUW14 - Placed pumps 1&4 manual/currently running. Notified Joe D. | All Water System ROC General | 2026-02-09
ROC | February | NMTKKC - Joe D called , site on portable generator, Ian W with contractors working on site. Ian W will call later to transfer site to normal power. | All Water System ROC General | 2026-02-09
ROC | February | Connor Smith signing in | All Water System ROC General | 2026-02-03
ROC | February | RHPSPA - Lee F finished on site. | All Water System ROC General | 2026-02-03
ROC | February | RHPSWA - Sean P on site, rebuilding Pump 1. | All Water System ROC General | 2026-02-03
ROC | February | VNRSKS - Placed all VNPS PD7 pumps man/off and placed all pumps at MAPS PD7 back to auto | All Water System ROC General | 2026-02-05
ROC | February | VNRSKS - Swapped supply p[umps to one VNPS and one MAPS pump. | All Water System ROC General | 2026-02-08
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-08
ROC | February | VNPSCD, Pre-Inj Free Cl2 Hi//MonoChloram lo alarm, notified David T, he will look into it but isn't to concerned, if the hihi comes in, he would like a call | All Water System ROC General | 2026-02-06
ROC | February | HLW2- Eric S finished onsite. Placed well back into auto. | All Water System ROC General | 2026-02-05
ROC | February | NRETCR - Deactivated duty 1 so JFRS can fill for the interim procedure. | All Water System ROC General | 2026-02-04
ROC | February | MTW12, MTW3 - Phil D requested to place pumps manual mode. Currently running. | All Water System ROC General | 2026-02-04
ROC | February | AUPSOH - Lee F on site for pumps 1-4 motor service. 13:25 Lee F working on pumps 3&4 , deactivated Duty 1 and placed pumps man/off . | All Water System ROC General | 2026-02-05
ROC | February | MTW12 - MTW12 to MTETNL Commfail alarm. Cleared alarms. Well 2 pump restarted. | All Water System ROC General | 2026-02-05
ROC | February | MKRSEM - Called Toronto Water (Mehdi) and requested to stop pumping to reservoir | All Water System ROC General | 2026-02-06
ROC | February | RHRSTR- Deactivated duty | All Water System ROC General | 2026-02-05
ROC | February | Angelica Chepiga signing out | All Water System ROC General | 2026-02-09
ROC | February | GWTP Low lift Patrick F cleaning turbidity meter, chlorine analyzers, testing chlorine leak alarm and Health and Safety check. | All Water System ROC General | 2026-02-03
ROC | February | Adeela Khan signing in. Weather: -4C and snowing | All Water System ROC General | 2026-02-06
ROC | February | STETBR - Tower Level Lo alarm came in. Checked site. Placed STW12 and STW3 man/on as per interim | All Water System ROC General | 2026-02-06
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-06
ROC | February | NBW5- Turbidity Hi Alarm. Rotated silicate duties so pump 1 running. Will monitor. 14>28- Turbidity still hi. Notified Jordan B. He will take a look. | All Water System ROC General | 2026-02-06
ROC | February | KLPSWL- Benson S onsite for work orders. Generator run, Cl Leak detection, scrubber test, all analyzers, valve exercising, hi/low temp and health and safety. | All Water System ROC General | 2026-02-03
ROC | February | MAPS PD7 - Pumps 1&3 man/off VNPS PD7 - Pumps 1&4 to auto. | All Water System ROC General | 2026-02-03
ROC | February | KSTP - Donald M called, working on site, plant is off until further notice. | All Water System ROC General | 2026-02-09
ROC | February | NMTKKC - Commfail alarm, not able to deactivate Duty 1. Notified Jason G. NMTKKC - Ian W will call Jason G . | All Water System ROC General | 2026-02-09
ROC | February | SUETDR - Jackie S on site for chlorine analyzers maintenance, Low temp alarm testing and Valves exercising. | All Water System ROC General | 2026-02-03
ROC | February | NMW12 - Influent free chlorine hihi alarm. Checked site, well recently activated. Trending shows the influent free chlorine reading spiked on well activation. monitoring site to ensure the influent free chlorine residual reading drops to normal range. | All Water System ROC General | 2026-02-08
ROC | February | MKRSMR - Travis W testing flood alarm, Hi/low level alarms, chlorine analyzers maintenance and performing Health and safety inspection. | All Water System ROC General | 2026-02-05
ROC | February | AUPSOH- Lee F finished onsite. Placed Pumps 3,4 back into auto. | All Water System ROC General | 2026-02-05
ROC | February | MAPS- Ric L finished onsite. | All Water System ROC General | 2026-02-05
ROC | February | AUW14, Placed well 1/4 man/off to take more from AURSBS | All Water System ROC General | 2026-02-04
ROC | February | QVETQS - System Pressure Low alarm, quick dip, recovered immediately at QVW12 duty stop. | All Water System ROC General | 2026-02-04
ROC | February | STW12 - Joe M requested STW12 pump 1 man/on. | All Water System ROC General | 2026-02-04
ROC | February | YWS + NYWS Normal Connor Smith signing in -8C Clear | All Water System ROC General | 2026-02-06
ROC | February | NMETHW - Riser pipe heat trace controller 1 fault alarm. Joe D attending site after leaving RHPSWA. Created CMU5#W11645865 #CMU5 | All Water System ROC General | 2026-02-07
ROC | February | YWS + NYWS Normal Christian Van Beek signing out. | All Water System ROC General | 2026-02-07
ROC | February | Christian Van Beek signing in. Weather: -23C and clear. | All Water System ROC General | 2026-02-08
ROC | February | MKPSSA, Gary P notified the ROC that the station is back to normal working order, valves are open. notified him to get in contact with Travis W to let him know that the residuals may need to be looked at. A grab sample was taken on site | All Water System ROC General | 2026-02-09
ROC | February | GWTP - Jack P running generator, disregard alarms. | All Water System ROC General | 2026-02-05
ROC | February | MKRSEM - Reservoir 1 Level Lo alarm came in. Called Toronto Water (Brett) and requested two pumps on 03:08 - Called Toronto Water (Brett) and requested to stop pumping to reservoir | All Water System ROC General | 2026-02-06
ROC | February | Gluzen Ramos Ong signing in | All Water System ROC General | 2026-02-04
ROC | February | Adam Button signing in -8C clear | All Water System ROC General | 2026-02-04
ROC | February | AURSBS - Deactivated duty 1, in preparation for interim | All Water System ROC General | 2026-02-08
ROC | February | MKRSEM - Reservoir low level alarm. Called Toronto Water (Zoran) and requested two pumps to push flow to MKRSEM. NMETHW - Activated duty 1. | All Water System ROC General | 2026-02-08
ROC | February | QVW12 - Justin Q and Ben H on site. Requested disregard Low pressure alarm. Testing. | All Water System ROC General | 2026-02-05
ROC | February | AUW14 - Lee F on site, working/locking out well 3 pump. Will call when work complete. | All Water System ROC General | 2026-02-05
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-04
ROC | February | MKPSSA - Travis W on site for station check. | All Water System ROC General | 2026-02-09
ROC | February | KCETFS, PAC Rack 1-8 Alarm. Low priority, notified Benson S as he is responsible for the site, he will be passing it on to the on call operator 15:30, Jacob M called RO asking about the alarms, notified him about the original call out, Jacob M requested for PCS on call to take a look into it. Notified Ian W, he will look into, Ian believes it to be a blown fuse. 15:36, Notified Jacob M that Ian W will look into the issue 16:00, Ian W is heading to site CMU5: W11650111 | All Water System ROC General | 2026-02-09
ROC | February | NMETHW - ET @ 74%, notified Alex B, ok to activate NMETIB when NMETHW @75% to offset towers. | All Water System ROC General | 2026-02-04
ROC | February | VNRSKS - Swapped supply pumps to two MAPS pumps for one fill cycle. | All Water System ROC General | 2026-02-10
ROC | February | STETTL - Tower is struggling to fill while STETBR duty i1 is also active. Activated STW1 in manual mode to assist fill cycle. | All Water System ROC General | 2026-02-07
ROC | February | RHRSTR - Deactivated duty 1. | All Water System ROC General | 2026-02-07
ROC | February | AURSBS - Activated duty 1. | All Water System ROC General | 2026-02-07
ROC | February | VNRSKS - Swapped supply pumps to one MAPS one VNPS pump. | All Water System ROC General | 2026-02-07
ROC | February | AUW14- Placed wells back into auto | All Water System ROC General | 2026-02-05
ROC | February | QVW12 - Influent free chlorine hi alarm. Checked site, influent is above target. Checked chemical dosing setpoints. The dosing setpoint for the active chlorinator has climbed above its setpoint. Re-applied initial chlorine dosage factor. | All Water System ROC General | 2026-02-07
ROC | February | MTW3 - SIlicate pump 1 fault alarm. Checked site, well has been running for several hours. Silicate pump duty rotated to silicate pump 2 and normal operations resumed. Unable to clear alarm. Sent mail to OCO. NBW5 - Turbidity high alarm. Checked site, well recently activated. Trending shows a pattern of turbidity spikes on well start. Will monitor site. | All Water System ROC General | 2026-02-07
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-07
ROC | February | MAPS PD7- Ric L onsite for calibrations. Placed Pumps man/off. MAPS PD8- Ric L working on flow meter. No pumps are running. | All Water System ROC General | 2026-02-05
ROC | February | STETBR - Tower Level Hi alarm came in. Placed STW12 and STW3 back to auto, as per interim | All Water System ROC General | 2026-02-08
ROC | February | HLW2 - Treated Free Chlorine HiHi alarm came in. Checked site. Well is running. Trends indicate a spike. After 10 mins, treated free chlorine levels came back to optimal range and alarm cleared | All Water System ROC General | 2026-02-08
ROC | February | VNRSKS - Placed all pumps at VNPS PD7 Man/off and placed all pumps at MAPS PD7 into auto | All Water System ROC General | 2026-02-08
ROC | February | QVETQS - System Pressure Lo alarm came in. Quick dip in trends but pressure comes back to optimal range. Alarm has cleared | All Water System ROC General | 2026-02-08
ROC | February | NMETIB - Activated duty 1 to help offset with NMETHW | All Water System ROC General | 2026-02-08
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-08
ROC | February | JFPS - WPD GEN xfer switch hydro power. Checked site, generator is running. Able to reset alarms. Pumps were not running when power failed. Operations normal. RHPSPA - Site hydro failure alarm. Checked site, trending shows flow did stop but the pumps started again. Operations normal, cleared alarms. RHPSWA - Site power failure alarm. Checked site no generator on site. Unable to reset power related alarms but the pump alarms did reset. Operations Normal RHMCMD - Valve 1 and valve 2 fault alarms. Checked site, valves are showing as closed but still registering flow. Shortly after the valves showed as open in manual again. Cleared alarms, operations normal. AUMCBS/VNMCBA - Control panel power failure. Trending shows normal operations on site. reset alarms. | All Water System ROC General | 2026-02-10
ROC | February | YWS + NYWS Normal QVW34 - influent free chlorine hihi alarm. Checked site, well is running in schedule mode. Trending shows a sudden reductio in flow production by the well but the chemical dosing stayed the same resulting in a high influent free chlorine reading. Adjusted the chlorinator dosing factor as it had increased slightly above the desired setpoint. Monitored site and the influent free chlorine reading dropped on the next reading. Will monitor the effluent free chlorine residual. NMTKBS - Activated duty 1 to maintain tank level for the interim procedure. ARPS - Peel/OCWA (David) called to inform he is rotating pump duty. | All Water System ROC General | 2026-02-08
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-08
ROC | February | NMTKKC - Sanitary pump fail to stop alarm, notified Jason G. He is on site. Contractor cut a power cable. No power on site. NMW12, NMW136, NMW15 Commfail alarm . Jason G requested all wells place man/off. TK at 73%, Jason G investigating on site, will call back. | All Water System ROC General | 2026-02-09
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-08
ROC | February | KSTP - low lift pump 3 uncommanded stop alarm. Checked site, low lift pump 2 accepted duty 1 and is running. Reset alarm. | All Water System ROC General | 2026-02-08
ROC | February | GWTP - ZW trans membrane pressure low alarm. Alarm status changed to normal shortly after alarm triggered. Alarm reset on acknowledgement. | All Water System ROC General | 2026-02-08
ROC | February | YWs + NYWS Normal Christian Van Beek signing out. | All Water System ROC General | 2026-02-08
ROC | February | VNRSKS - Deactivated duty 1 in preparation for interim | All Water System ROC General | 2026-02-08
ROC | February | YWS + NYWS Normal | All Water System ROC General | 2026-02-08
ROC | February | YWS + NYWS NORMAL | All Water System ROC General | 2026-02-04
ROC | February | VNRSKS - Deactivated duty. Switched pump 2 at MAPS PD7 man/off and placed pump 2 at VNPS PD7 into auto 03:00 - Placed PD7 to VNPS PD7 | All Water System ROC General | 2026-02-09
ROC | February | MKRSEM - Called Toronto Water (Brett) and requested to stop pumping to reservoir | All Water System ROC General | 2026-02-09
ROC | February | QVETQS - System Pressure Lo alarm came in. Quick dip in trends but pressure comes back to optimal range. Alarm has cleared | All Water System ROC General | 2026-02-09
ROC | February | MKPSSA - discharge lo pressure. Confirmed with Dwayne L. linear team doing valving at discharge of facility at McCowan and 16th Ave. Req. not to run pumps. Emailed ROC, Linear and East teams. | All Water System ROC General | 2026-02-09
ROC | February | Ethan Ullalkar signing out. | All Wastewater System ROC General | 2026-02-23
ROC | February | YDSS + YNSS Normal Christian Van Beek signing out. | All Wastewater System ROC General | 2026-02-24
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-25
ROC | February | KBSP, Marcus R on site, testing the Filter Inlet Flood/Alum Leak-Flood alarm | All Wastewater System ROC General | 2026-02-24
ROC | February | SUSP- UV ch1 critical fail/ high level/common critical alarms. Flow started up and channel 2 active disregard on shift report. Alarms cleared upon acknowledgement. | All Wastewater System ROC General | 2026-02-28
ROC | February | NBSP - Inlet channel Hi alarm, Mech Bar screen fail to stop and OOS alarms. All alarms cleared in a few minutes. Will monitor. | All Wastewater System ROC General | 2026-02-28
ROC | February | SUSP- UV ch1 critical fail/ high level/common critical alarms. Flow started up and channel 2 active disregard on shift report. Alarms cleared upon acknowledgement. | All Wastewater System ROC General | 2026-02-28
ROC | February | NMSSBP - Talha H working on OIT's and has directed to disregard historian heartbeat alarms. | All Wastewater System ROC General | 2026-02-25
ROC | February | KCSSKR - Site back to normal OP, Dan H leaving site. | All Wastewater System ROC General | 2026-02-27
ROC | February | Adeela Khan signing in. Weather: -5C and Cloudy | All Wastewater System ROC General | 2026-02-28
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-28
ROC | February | SUSP - UV System Critical Failure, UV Ch 1 High Level, and UV CH 1 Common Critical Alarms came in. Checked site. Site just activated. Alarms value turned to normal and cleared right away. Disregarded as per shift report | All Wastewater System ROC General | 2026-02-28
ROC | February | Carter D Signing Out | All Wastewater System ROC General | 2026-02-23
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-28
ROC | February | BLSS - Young J leaving site. Normal operations have resumed. | All Wastewater System ROC General | 2026-02-25
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-24
ROC | February | HLSSBS- Hydrogen Sulphide Sample 1 Fault Alarm. Disregard as per SCADA Report | All Wastewater System ROC General | 2026-02-24
ROC | February | Carter Dunn Signing In | All Wastewater System ROC General | 2026-02-26
ROC | February | MTSP - Ian W working on the OIT and has directed to disregard the historian heartbeat alarm. | All Wastewater System ROC General | 2026-02-26
ROC | February | KSSP- Neil O on site to work on UV system | All Wastewater System ROC General | 2026-02-26
ROC | February | YDSS+YNSS normal | All Wastewater System ROC General | 2026-02-25
ROC | February | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-02-28
ROC | February | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-02-28
ROC | February | SUSP- Influent Flow HiHi Alarm. Quick spike. Cleared alarm. | All Wastewater System ROC General | 2026-02-24
ROC | February | AUSS- Kyle B from PCS is working on P4 | All Wastewater System ROC General | 2026-02-25
ROC | February | NMSSHS, PAC Comm fail, Notified Yash S, he is looking into it | All Wastewater System ROC General | 2026-02-26
ROC | February | SUSP- UV ch1 critical fail/ high level/common critical alarms. Flow started up and channel 2 active disregard on shift report. Alarms cleared upon acknowledgement. | All Wastewater System ROC General | 2026-02-28
ROC | February | YDSS+YNSS normal | All Wastewater System ROC General | 2026-02-26
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-25
ROC | February | Adam Button signing in -3C clear | All Wastewater System ROC General | 2026-02-25
ROC | February | SUSP - Ian W testing a new UV Bypass alarm, requested disregard until further notice. 15:55 Ian W finished on site. | All Wastewater System ROC General | 2026-02-27
ROC | February | AUSSYS - Odour control e stop alarm. Kevin S signed in on site in the logbook. Called Kevin who will investigate the alarm. | All Wastewater System ROC General | 2026-02-26
ROC | February | Adam Button signing out | All Wastewater System ROC General | 2026-02-25
ROC | February | Carter D Signing Out | All Wastewater System ROC General | 2026-02-26
ROC | February | Connor Smith signing in -10C Windy | All Wastewater System ROC General | 2026-02-23
ROC | February | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-02-28
ROC | February | AUSSSR - Aysix System Heartbeat alarm came in. Ack/rest and site went back to normal operations | All Wastewater System ROC General | 2026-02-28
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-26
ROC | February | SEOC4 - Shaft 4 to shaft 2 comm failure, PAC communication failure. Gound generator running status. Status went to normal within couple minutes and able to clear alarm | All Wastewater System ROC General | 2026-02-26
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-26
ROC | February | BLSS- Young J onsite for south collector repairs. Will be shutting off all pumps. Disregard all alarms. | All Wastewater System ROC General | 2026-02-23
ROC | February | AUSS - Marcos T on site and will be turning off the Odor control system. | All Wastewater System ROC General | 2026-02-26
ROC | February | YDSS+YNSS normal | All Wastewater System ROC General | 2026-02-27
ROC | February | Adam Button signing in 5C Sunny | All Wastewater System ROC General | 2026-02-27
ROC | February | YDSS+YNSS normal | All Wastewater System ROC General | 2026-02-27
ROC | February | NBSP- Aeration basin 2 back DO lo alarm came in. Recovered after 12 mins alarm cleared | All Wastewater System ROC General | 2026-02-25
ROC | February | NMSSHS - Evgeni S rebooting OIT, disregard heartbeat alarm | All Wastewater System ROC General | 2026-02-25
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-25
ROC | February | YDSS+YNSS normal | All Wastewater System ROC General | 2026-02-26
ROC | February | KCSSKR - Generator running due to , Duty was not active at the time Alarm panel AC power restored dialer alarm came in right after | All Wastewater System ROC General | 2026-02-27
ROC | February | Angelica Chepiga signing in, weather +4C | All Wastewater System ROC General | 2026-02-28
ROC | February | KSSP - UV Panel 1 Lamp Low intensity alarm, disregard as per shift report. | All Wastewater System ROC General | 2026-02-28
ROC | February | MTSP, Bar Screen Fault Alarm, Terry R called back, informed the ROC that the bar screen will be off for the night and that they will be diverting to the lagoon till the issue is resolved | All Wastewater System ROC General | 2026-02-26
ROC | February | Ethan Ullalkar signing out. | All Wastewater System ROC General | 2026-02-27
ROC | February | LSSS - Ubah student from EME , sampling P6, assigned P6 to duty 1. | All Wastewater System ROC General | 2026-02-27
ROC | February | LSSS - Pump 1 fault alarm. Notified Chris R, he will investigate. | All Wastewater System ROC General | 2026-02-27
ROC | February | Ethan U signing in Weather: 0 | All Wastewater System ROC General | 2026-02-26
ROC | February | EGSSSC- Diesel containment flood alarm came in Notified Cam B. Directed to disregard alarm #consult | All Wastewater System ROC General | 2026-02-28
ROC | February | Carter D Signing In | All Wastewater System ROC General | 2026-02-23
ROC | February | SEOC Fan 1 and Fan 2 Uncommanded stop alarms. Contacted Phil R who directed to clear alarms. Alarms cleared and fans activated. | All Wastewater System ROC General | 2026-02-24
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-25
ROC | February | Christian Van Beek signing in. | All Wastewater System ROC General | 2026-02-25
ROC | February | Angelica Chepiga signing out | All Wastewater System ROC General | 2026-02-27
ROC | February | MTSP, Bar Screen Fault, notified Terry R, he is looking into it | All Wastewater System ROC General | 2026-02-26
ROC | February | Carter D Signing Out | All Wastewater System ROC General | 2026-02-24
ROC | February | YDSS + YNSS Normal Carter D Signing Out | All Wastewater System ROC General | 2026-02-27
ROC | February | SHSP - Ian W on site to test the new UV system bypass alarm. Ian has directed to disregard this alarm until the work is done. | All Wastewater System ROC General | 2026-02-25
ROC | February | KBSP, Marcus R on site, working on the UV system and the water service system on site | All Wastewater System ROC General | 2026-02-26
ROC | February | AUSS - Pump 5 W discharge header MV3 failed to open alarm. Checked site, duty rotated to pump 3 which is active and pushing flow. Reset alarm. | All Wastewater System ROC General | 2026-02-26
ROC | February | NBSP- System minor fault alarm came in. switching from bank 1a to bank 1b disregard on shift report NMSSHS- PAC comm failure. Cleared upon acknowledgement. Trends show gaps. Notified Yash S will investigate | All Wastewater System ROC General | 2026-02-26
ROC | February | KCSSKR - As per Daniel H stakeholders onsite for a feasibility study. Directed to disregard alarms including wet wells Hi and HiHi alarms. He is on site monitoring. | All Wastewater System ROC General | 2026-02-27
ROC | February | YDSS+YNSS NORMAL Angelica Chepiga signing out | All Wastewater System ROC General | 2026-02-28
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-24
ROC | February | KBSP - Water sump level hi switch alarm. Marcus R called to inform he triggered this alarm. | All Wastewater System ROC General | 2026-02-26
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-23
ROC | February | YDSS+YNSS normal | All Wastewater System ROC General | 2026-02-28
ROC | February | NMSSBP- Mech Screen 1 Overtorgue Alarm. Screen 2 already OOS. Notified Chris R. He will attend site. 04:00- Finished onsite. Screen 1 back into service. 05:35- Mech Screen 1 Overtorque Alarm came back in. Chris R will attend site. W11688330 CMU5 | All Wastewater System ROC General | 2026-02-25
ROC | February | NMSSHS/EGSSSC- Evgeny S working on OITs disregard historian heartbeat alarms | All Wastewater System ROC General | 2026-02-25
ROC | February | SHSP - Generator running, clarifier 2 rake drive cut, UV major. Power blip in area. Restored shortly after but alarms outstanding. Called Gavin W, will head to site SHSSDK - Generator running CMU = W11683632 | All Wastewater System ROC General | 2026-02-23
ROC | February | Ethan Ullalkar signing out. | All Wastewater System ROC General | 2026-02-26
ROC | February | HLSSBS - Hydrogen Sulphide Sample 1 fault alarm- disregard after hours as per shift report. | All Wastewater System ROC General | 2026-02-28
ROC | February | SEOC - OCF Water Supply Unusual Flow Rate alarm came in. Disregarded as per shift report | All Wastewater System ROC General | 2026-02-28
ROC | February | SEOC5, Comm fail, Notified Yash S, he is looking to fix the issue 15:49, Yash S ended up going to site to fix the issue, he is now finished on site CMU: W11695267 | All Wastewater System ROC General | 2026-02-27
ROC | February | KBSP, Marcus R on site, working on aeration probe alarms | All Wastewater System ROC General | 2026-02-27
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-24
ROC | February | Christian Van Beek signing out. | All Wastewater System ROC General | 2026-02-27
ROC | February | KSSP= Scum Chamber hi level alarm came in. Disregard on shift report | All Wastewater System ROC General | 2026-02-25
ROC | February | NMSSBP- Talha H done rebooting OIT cleared historian heartbeat alarm KBSP- Ian W done work on site | All Wastewater System ROC General | 2026-02-25
ROC | February | SEOC OCF - Fan 1 and Fan 2 uncommanded stop and General HVAC alarms. Fan 1 and Fan 2 restarted after ack/reset alarms. General HVAC alarm outstanding. Disregarded as per SCADA review. | All Wastewater System ROC General | 2026-02-27
ROC | February | KSSP - RAS combined no flow alarm. Checked site, all RAS pumps manual/off but the WAS pumps are active indicating that operators are wasting sludge | All Wastewater System ROC General | 2026-02-25
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-24
ROC | February | MTSS - David D on site to complete a dialer alarm test. | All Wastewater System ROC General | 2026-02-24
ROC | February | SECC, Yash S on site, replacing OITs and working on system panel | All Wastewater System ROC General | 2026-02-24
ROC | February | YDSS + YNSS Normal Connor Smith signing out | All Wastewater System ROC General | 2026-02-24
ROC | February | Carter D signing in | All Wastewater System ROC General | 2026-02-27
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-23
ROC | February | Christian Van Beek signing in. Weather: -8C and clear. | All Wastewater System ROC General | 2026-02-26
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-26
ROC | February | LSSS - Pump 1 Fault alarm. Checked site, duty 1 is assigned to pump 5 which is active. Pump 1 is listed as out of service duty 7 in the shift report. | All Wastewater System ROC General | 2026-02-24
ROC | February | KSSP, Neil O is on site, working on the UV alarms | All Wastewater System ROC General | 2026-02-24
ROC | February | NBSP - UV system minor fault alarm. Checked site one UV bank is active and the duty for the UV banks recently swapped. Alarm is a disregard on the shift report as long as one bank is active. | All Wastewater System ROC General | 2026-02-24
ROC | February | Christian Van Beek signing in. Weather: -16C and clear. | All Wastewater System ROC General | 2026-02-24
ROC | February | YDSS + YNSS Normal Connor Smith signing out | All Wastewater System ROC General | 2026-02-25
ROC | February | Ethan U signing in Weather: -2c | All Wastewater System ROC General | 2026-02-25
ROC | February | Ethan U signing in Weather -4. | All Wastewater System ROC General | 2026-02-23
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-23
ROC | February | NMSSHS- Yash S restored comms on site trends okay | All Wastewater System ROC General | 2026-02-26
ROC | February | KSSP - UV Panel 1 Lamp low intensity and UV Ch1 bank 1A Low UV intensity fault alarm. Checked site , UV 1 is running. High priority alarms, not in the shift report. Notified Cam B, he will investigate. # Consult | All Wastewater System ROC General | 2026-02-28
ROC | February | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-02-27
ROC | February | KSSP - UV CH.1 Bank 1A Low UV Intensity Fault alarm came back in. Alarm was coming in and immediately turning normal. Alarm came back in but did not clear on its own. Checked site. Noticed that UV Ch 1 is running. Called Cam B. who will investigate further #CONSULT | All Wastewater System ROC General | 2026-02-28
ROC | February | NMEQBP- Kingsley M is rebooting OIT on site. Disregard historian heartbeat until done KSSP- Ian W testing UV bypass alarms | All Wastewater System ROC General | 2026-02-26
ROC | February | YDSS+YNSS normal | All Wastewater System ROC General | 2026-02-28
ROC | February | KBSP, Marcus R is working on the SCUM tanks NBSSJA, Parth P/Rick L are finished on site | All Wastewater System ROC General | 2026-02-23
ROC | February | NBSP - UV System Minor alarm. Checked site, UV Bank 1 B is running. Disregard alarm as per shift report. | All Wastewater System ROC General | 2026-02-28
ROC | February | Christian Van Beek signing in. | All Wastewater System ROC General | 2026-02-27
ROC | February | Carter Dunn Signing In | All Wastewater System ROC General | 2026-02-24
ROC | February | BLSS - Young J called to inform that the south forcemain and pump 5 will remain out of service. Normal operations have resumed through the other pumps. Young J leaving site. | All Wastewater System ROC General | 2026-02-24
ROC | February | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-02-28
ROC | February | NMSSBP- Mech screen 2 fault alarm. Notified Kevin S will try to clear remotely and reach out to CMS if work order is need to fix issue. | All Wastewater System ROC General | 2026-02-25
ROC | February | SUSP- UV CH 1 common critical/high level and critical failure alarm came in. Channel 2 in D1 alarms cleared upon acknowledgement | All Wastewater System ROC General | 2026-02-25
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-26
ROC | February | SHSP - Ian W working on OIT, disregard Historian Heartbeat alarm for the duration of the work. 13:19 Ian W completed work | All Wastewater System ROC General | 2026-02-27
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-25
ROC | February | BLSS- Young J onsite with contractors for South Collector work. WIll be placing all pumps off. and isolating forcemain. Disregard alarms while onsite. | All Wastewater System ROC General | 2026-02-24
ROC | February | KBSP - Dan H on site to oversee the generator TSSA upgrades. | All Wastewater System ROC General | 2026-02-25
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-26
ROC | February | HLSSBS- Terry C and Bill V on site to work on P3 NMSSBP- Mech screen 1 overtorque alarm came in. Notified Kevin S closed gate 2 as 1 was still available. Will try to reset alarm and will escalate if alarm cannot be reset. Talha H rebooting OIT disregard historian heartbeat alarm | All Wastewater System ROC General | 2026-02-25
ROC | February | NMSSHS - PAC Communication failure alarms multiple times. Notified Yash S. He will investigate. | All Wastewater System ROC General | 2026-02-27
ROC | February | MTSP - Ian W testing the UV bypass alarm. Ian directed to directed to disregard the alarm until his work is complete. | All Wastewater System ROC General | 2026-02-26
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-27
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-27
ROC | February | NBSP- Alum ROC alarm/ tank lo alarm came in. Alum tank filled yesterday level was not low before LIT level dropped suddenly. Trends recovered. Able to reset alarms SUSP- UV ch1 critical fail/ high level/common critical alarms came in. Flow started up and channel 2 active disregard on shift reports. alarms cleared upon acknowledgement | All Wastewater System ROC General | 2026-02-28
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-23
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-24
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-24
ROC | February | AUSS- Satnam M called and requested to manually open Pump 3 MV4 valve. placed manual open. Valve fully opened. Placed back into auto. He is leaving site. | All Wastewater System ROC General | 2026-02-23
ROC | February | QVSSSC- Inlet Channel High Switch Alarm. Disregard as per SCADA Report. | All Wastewater System ROC General | 2026-02-23
ROC | February | BLSS- Young J called and requested on call Electrician to attend site for assistance with South Main Vlv Overtorque. Notified Satnam M. W11683750 CMU5 | All Wastewater System ROC General | 2026-02-24
ROC | February | EGSSSC- Evgeny S rebooting OIT disregard historian heartbeat until done | All Wastewater System ROC General | 2026-02-25
ROC | February | LSSS- P 1 motor trip on high temp. Rotated to P5 automatically Notified Chris R will create W/O | All Wastewater System ROC General | 2026-02-26
ROC | February | Angelica Chepiga signing in, weather -7C | All Wastewater System ROC General | 2026-02-27
ROC | February | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-02-28
ROC | February | KBSP - UV Ch2 bank 1A Low UV intensity fault alarm, UV Ch 2 Common Minor alarm, UV channel 2 in running - Disregard alarms as per shift report. | All Wastewater System ROC General | 2026-02-28
ROC | February | YDSS+YNSS normal Adam Button signing out | All Wastewater System ROC General | 2026-02-28
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-27
ROC | February | YDSS+YNSS normal | All Wastewater System ROC General | 2026-02-28
ROC | February | QVSSSC, HLSSBS - Talha H completing an OIT reboot. Talha has directed to disregard the associated historian heartbeat alarm. | All Wastewater System ROC General | 2026-02-24
ROC | February | Christian Van Beek signing out. | All Wastewater System ROC General | 2026-02-25
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-25
ROC | February | Christian Van Beek signing out. | All Wastewater System ROC General | 2026-02-26
ROC | February | NBSP- Alum tank level lo/ ROC alarm came in. Second time it has come in today. Left outstanding and emailed west waste water about issue | All Wastewater System ROC General | 2026-02-28
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-23
ROC | February | Adeela Khan signing out | All Wastewater System ROC General | 2026-02-23
ROC | February | Adam Button signing in | All Wastewater System ROC General | 2026-02-26
ROC | February | HMSS - Barscreen 1 and 2 not in auto alarm. Called Lauren S who is on site and will swap the bar screens back to auto mode. | All Wastewater System ROC General | 2026-02-24
ROC | February | KBSP- Ian W on site to test UV bypass alarms. Disregard until done work 10:51- KBSP- Ian W working on OIT disreagrd historian heartbeat until done | All Wastewater System ROC General | 2026-02-25
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-27
ROC | February | KSSSQW- Wetwell 1 LOE alarm came in. Trends show potential issue with LIT 1. Emailed North wastewater. Controlling LIT is LIT 2. Site okay. | All Wastewater System ROC General | 2026-02-28
ROC | February | Connor Smith signing in -8C cloudy | All Wastewater System ROC General | 2026-02-24
ROC | February | MTSP, Dewatering Press Fault, Notified Terry R, directed to disregard at this time, Maint will be looking at it on Tuesday (March 3rd) | All Wastewater System ROC General | 2026-02-27
ROC | February | NBSSJA, Rick L/Parth P on site, working on the Diesel LIT | All Wastewater System ROC General | 2026-02-23
ROC | February | KSSP- Neil O on site for UV work | All Wastewater System ROC General | 2026-02-25
ROC | February | Adam Button signing out | All Wastewater System ROC General | 2026-02-26
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-01
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-01
ROC | February | SEOC4 - Shaft 4 fan duty rotation imminent alarm. Disregard as per the shift report. | All Wastewater System ROC General | 2026-02-01
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-01
ROC | February | AUSS, Bar Screen not in auto, notified Phil R, he is heading to site CMU5: W11627091 | All Wastewater System ROC General | 2026-02-01
ROC | February | Adeela Khan signing in. Weather: -11C and partly cloudy | All Wastewater System ROC General | 2026-02-01
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-01
ROC | February | KSSP - Makeup Air Unit 6 Temp Sw Lo alarm came in. Disregarded as per shift report YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-02
ROC | February | SECC, HVAC General Alarm/O2 Monitoring Alarm, Phil R was heading to do his Sunday rounds, notified him that these 2 alarms came in on Christians night shift again (went out on Saturday to clear them). Directed to disregard for the night, someone will look at it on monday | All Wastewater System ROC General | 2026-02-01
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-01
ROC | February | SUSP - UV System Critical Failure alarm came in. Checked site. Alarms went normal. Occurred on plant startup. Disregarded as per shift report | All Wastewater System ROC General | 2026-02-01
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-02
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-01
ROC | February | YDSS+ YNSS Normal | All Wastewater System ROC General | 2026-02-01
ROC | February | AUSS - Phil R. called to inform that he will need a second person to assist with the bar screen. Called Young j. no answer. Called Neil O. who will speak with Phil R. 18:30 - Neil O. called back to inform that he is headed to site. CMU5 Created W11627111 #CONSULT #CMU5 | All Wastewater System ROC General | 2026-02-01
ROC | February | NMSSHS- Barry M onsite running diesel generator. | All Wastewater System ROC General | 2026-02-02
ROC | February | KSSSQW- Darren B finished onsite. | All Wastewater System ROC General | 2026-02-02
ROC | February | HMSS- Illegal entry alarm no OPS on site followed up with security spoke with Divij who will dispatch security to site | All Wastewater System ROC General | 2026-02-02
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-03
ROC | February | BLSS. Screen Upstream Lvl hihi, trends look completely off, notified Young J, he will look into the issue consult | All Wastewater System ROC General | 2026-02-02
ROC | February | SUSSWB- Venthilation H2S hihi alarm came in. Notified Cam B. Directed to disregard | All Wastewater System ROC General | 2026-02-02
ROC | February | LSSS, Wet Well 1/2 Screen Differential Level LOE/hihi alarm, contacted Phil R, he is heading to site CMU5: W11631417 | All Wastewater System ROC General | 2026-02-03
ROC | February | YDSS+YNSS normal | All Wastewater System ROC General | 2026-02-02
ROC | February | KBSP- Lauren S running generator on site | All Wastewater System ROC General | 2026-02-02
ROC | February | SUSSHS- Talha H working on OIT. Disregard Heartbeat Alarm. | All Wastewater System ROC General | 2026-02-02
ROC | February | HLSSBS- Historian heartbeat alarm came in. Notified Kyle C will investigate SUSSHS-Talha H rebooting OIT Disregard historian Heartbeat alarm until done GRSSWA- Talha H rebooting OIT Disregard historian Heartbeat alarm until done | All Wastewater System ROC General | 2026-02-02
ROC | February | Adam Button signing in | All Wastewater System ROC General | 2026-02-02
ROC | February | KSSSQW- Darren B onsite for wetwell cleaning. Disregard related alarms. Also informed of Pump 3 Vibration Out of Range Alarm that came in. | All Wastewater System ROC General | 2026-02-02
ROC | February | YDSS + YNSS Normal Christian Van Beek signing out. | All Wastewater System ROC General | 2026-02-01
ROC | February | Carter Dunn Signing In, -15D/Clear | All Wastewater System ROC General | 2026-02-01
ROC | February | AUSS- Kyle B from PCS onsite working on UPS Faults. | All Wastewater System ROC General | 2026-02-02
ROC | February | KBSP- Lauren S on site to run generator | All Wastewater System ROC General | 2026-02-02
ROC | February | NMVCBP - EGSSSC force main pressure lolo alarm. Checked site, pump is running and flow is heading to Newmarket pumping station. Email from Niel O stated this alarm can be disregarded if it comes in early morning while the pumps are running. Cleared alarm. | All Wastewater System ROC General | 2026-02-01
ROC | February | SUSP- UV ch 2 bank 2 a low UV intensity fault alarm. Disregard on shift report as dosage okay. | All Wastewater System ROC General | 2026-02-02
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-03
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-01
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-01
ROC | February | SUSP - UV CH.2 Bank 2A Low UV Intensity Fault alarm keeps coming in. Neil informed this can be disregarded. Neil also directed to disregard the sludge hi alarm that may come in later tonight | All Wastewater System ROC General | 2026-02-01
ROC | February | Connor Smith signing out | All Wastewater System ROC General | 2026-02-02
ROC | February | Carter Dunn Signing In, -11D/Clear | All Wastewater System ROC General | 2026-02-02
ROC | February | Adam Button signing out | All Wastewater System ROC General | 2026-02-02
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-02
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-02
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-03
ROC | February | SUSP- Bar screen hi level alarm. Notified Mike B. will take a look on site | All Wastewater System ROC General | 2026-02-02
ROC | February | Carter Dunn Signing Out | All Wastewater System ROC General | 2026-02-01
ROC | February | KBSP. Young J called the ROC to request a CMU5 for Kyle C. Kyle C will be looking into the effluent trending issue CMU5: W11627065 | All Wastewater System ROC General | 2026-02-01
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-01
ROC | February | NMVCBP - EGSSSC FM Pressure Lo alarm and ROC FM Pressure Lo alarm came in multiple times. Neil was aware and is headed to site. CMU5 Created W11627122 19:50 - Neil called back and requested Brent S. to give him a call. Called Brent S. 20:15 - Neil called back to inform that he is finished on site and has placed the ROC Forcemain valve in duty 2. The alarms can continue to be disregarded as long as the pumps are running when the alarms come in and the pressure comes back to optimal range within 5 mins #CONSULT #CMU5 | All Wastewater System ROC General | 2026-02-01
ROC | February | KSSP - Alum Chem Rm MUA - 11 Differential pressure Switch hi alarm came in. Checked site. Fan is running. Will call if the low temp alarm comes in. Will send an email to Neil O. | All Wastewater System ROC General | 2026-02-02
ROC | February | YDSS + YNSS normal | All Wastewater System ROC General | 2026-02-02
ROC | February | SUSP- Mike B onsite running generator. | All Wastewater System ROC General | 2026-02-02
ROC | February | MTSP- Generator Running Status. Called Marcos T. He is onsite running generator. | All Wastewater System ROC General | 2026-02-02
ROC | February | HMSS- Young J on site to run generator, test drywell flood alarm, hi lo temp and exercise valves on each pump | All Wastewater System ROC General | 2026-02-02
ROC | February | Adeela Khan signing out | All Wastewater System ROC General | 2026-02-02
ROC | February | KBSP- Theo from AB on site. Grinding on generator room may cause smoke detection alarms to come in. Theo will call back when done. | All Wastewater System ROC General | 2026-02-02
ROC | February | AUSSYS- Kevin S onsite for generator run. Also testing hi/low temp and drywell flood alarms. | All Wastewater System ROC General | 2026-02-02
ROC | February | LSSS - Bar Screen 1 Fault alarm came in. Checked site. Called Phil R. who directed to disregard alarm and will take a look first thing in the morning. #CONSULT | All Wastewater System ROC General | 2026-02-01
ROC | February | Connor Smith signing in -15C Clear | All Wastewater System ROC General | 2026-02-02
ROC | February | SUSSHS- Cam B onsite running generator. | All Wastewater System ROC General | 2026-02-02
ROC | February | SUSP - Sludge Tank Level HiHi alarm came in. Disregarded as per Neil O. YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-02
ROC | February | YDSS+YNSS normal Adam Button signing out | All Wastewater System ROC General | 2026-02-20
ROC | February | KSSP- Headworks building flood alarm came in. Notified Neil O. Chris C on site testing alarm | All Wastewater System ROC General | 2026-02-20
ROC | February | SUSP- UV system Critical failure/ ch1 high level/UV CH.1 Common Critical Alarm. All alarms cleared upon acknowledgment. UV2B running normal. | All Wastewater System ROC General | 2026-02-20
ROC | February | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-02-20
ROC | February | QVSSSC- Tyson C will attend site. created CMU5 W11653911 #CMU5 | All Wastewater System ROC General | 2026-02-10
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-11
ROC | February | YDSS + YNSS Normal Connor Smith signing out | All Wastewater System ROC General | 2026-02-15
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-16
ROC | February | NBSP - Alum pump 3,4 & 5. Alum pump 5 general alarm. Alum pumps 2 & 4 running at the time. Informed Lauren S, will look into issue Consult | All Wastewater System ROC General | 2026-02-16
ROC | February | Ethan U signing in Weather -4. | All Wastewater System ROC General | 2026-02-14
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-10
ROC | February | BLSS, Pump 1/4 had an emergency stop, all pumps were turning off, security system showing armed, contacted Lauren S as all pumps are randomly turning off, Lauren S directed to call Dan H as he is doing work at the site all night. Contacted Dan H for confirmation and confirmed to disregard alarms at still till hes finished consult | All Wastewater System ROC General | 2026-02-11
ROC | February | Christian Van Beek signing out. | All Wastewater System ROC General | 2026-02-10
ROC | February | AUSS- Dan K. done on site was able to get coolant temp alarm cleared. Heater is back on line and directed to disregard alarm if it comes back in | All Wastewater System ROC General | 2026-02-12
ROC | February | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-02-21
ROC | February | RHAMF - Kyle C on site to complete work with Kevin Shaji. Kyle has directed to disregard all alarms from site. | All Wastewater System ROC General | 2026-02-17
ROC | February | BLSS - Power outage, Generators 1 and 2 running alarms. Notified Gavin W. # Consult HMSS - Power blip , Pump 2 fault alarm placed man/off. 4 pumps available. | All Wastewater System ROC General | 2026-02-18
ROC | February | Adeela Khan signing out | All Wastewater System ROC General | 2026-02-20
ROC | February | Connor Smith signing in 2C Clear | All Wastewater System ROC General | 2026-02-21
ROC | February | AUSSSR, Line 3 Valve Overtorque Alarm, Notified Chris R, he is heading to site CMU5: W11676699 | All Wastewater System ROC General | 2026-02-19
ROC | February | BLSS - Dan H called, station back to normal operation. Dan H and contractors leaving site. | All Wastewater System ROC General | 2026-02-12
ROC | February | KSSP- UV ch 1 bank 1a Low UV intensity fault. No dip in intensity or dosage. Alarm cleared upon acknowledgement | All Wastewater System ROC General | 2026-02-12
ROC | February | YDSS + YNSS normal | All Wastewater System ROC General | 2026-02-10
ROC | February | QVSSSC- Kevin K called back. Power has been restored to site and no Vac truck required. Kevin K notified ROC that he called Wessuc to cancel truck and they are no longer being dispatched. Tyson C on site and Kevin K will be shortly to troubleshoot outstanding issues | All Wastewater System ROC General | 2026-02-10
ROC | February | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-02-21
ROC | February | BLSS - Site power failure alarm. Checked site, utility power has been restored and the generators have shut down. Alectra map still shows a local power outage but it is affecting a much smaller amount of customers. Will monitor site to ensure proper operation | All Wastewater System ROC General | 2026-02-19
ROC | February | RHAMF1 - Power blip, generator started and stopped. Fan 1 and Fan 2 VFD faults alarm came back. Jimmy from NAC on site, reset alarms. Fans 1and 2 restarted. | All Wastewater System ROC General | 2026-02-13
ROC | February | Connor Smith signing in | All Wastewater System ROC General | 2026-02-11
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-13
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-15
ROC | February | NBSP- UV system minor fault. Disregard on shift report as banks transfer over | All Wastewater System ROC General | 2026-02-16
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-21
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-11
ROC | February | NMVCBP - Parth P finished on site. | All Wastewater System ROC General | 2026-02-17
ROC | February | YDOC - Eric S leaving site, will attend site another time to work on biofilter drain pH | All Wastewater System ROC General | 2026-02-12
ROC | February | SHSP -Lance J testing Filter Drain sump High float alarm and RAS/WAS Drain Sump High Float alarm. | All Wastewater System ROC General | 2026-02-12
ROC | February | Adam Button signing in | All Wastewater System ROC General | 2026-02-17
ROC | February | SUSP, UV Common major alarms, contacted Cam B, he is on site working the UV alarms SHSP, Compressor 1 E Stop/Motor overload alarm, notified Lance J, he is on site, directed to disregard compressor alarms till we hear back from him or if it hits the end of the day | All Wastewater System ROC General | 2026-02-18
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-21
ROC | February | SEOC67- Terry C on site to run generator. Not transferring over | All Wastewater System ROC General | 2026-02-17
ROC | February | YWS + NYWS Normal | All Wastewater System ROC General | 2026-02-22
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-22
ROC | February | YDSS + YNSS normal | All Wastewater System ROC General | 2026-02-11
ROC | February | KBSP - Reject Sump Pump #1 E-Stop Alarm. Disregard as per shift report | All Wastewater System ROC General | 2026-02-17
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-22
ROC | February | Ethan Ullalkar signing out. | All Wastewater System ROC General | 2026-02-18
ROC | February | AUSS- P4 e stop ,moisture and leakage alarms came in. Called Dan K. who will investigate | All Wastewater System ROC General | 2026-02-17
ROC | February | Adam Button signing out | All Wastewater System ROC General | 2026-02-19
ROC | February | Carter Dunn Signing Out | All Wastewater System ROC General | 2026-02-19
ROC | February | Gluzen Ramos Ong signing out | All Wastewater System ROC General | 2026-02-12
ROC | February | Adam Button signing out | All Wastewater System ROC General | 2026-02-12
ROC | February | YDSS + YTNSS Normal | All Wastewater System ROC General | 2026-02-12
ROC | February | KSSP- UV ch1 bank 1a lo UV intensity fault came in again. notified Neil O will take a look on site | All Wastewater System ROC General | 2026-02-12
ROC | February | NBSP - Inlet level Hi alarm, mechanical bar screen failed to stop, Bar screen out of service alarm. All alarms cleared in a few minutes. Will monitor. | All Wastewater System ROC General | 2026-02-20
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-21
ROC | February | Adeela Khan signing in. Weather: 0C and rain | All Wastewater System ROC General | 2026-02-21
ROC | February | Christian Van Beek signing in. Weather: 1C and clear. | All Wastewater System ROC General | 2026-02-17
ROC | February | NBSP- Young J and Gluzen R on site to work on clarifier 2 | All Wastewater System ROC General | 2026-02-19
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-19
ROC | February | Adam Button signing in | All Wastewater System ROC General | 2026-02-19
ROC | February | Ethan Ullalkar signing out. | All Wastewater System ROC General | 2026-02-17
ROC | February | BLSS - Generator running status still active. Checked Alectra Utility website. Outage map shows a power failure on top of BLSS location with an estimated time of restoration of 02:00 - 04:00 am. | All Wastewater System ROC General | 2026-02-18
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-19
ROC | February | MTSS- Terry R to test Wetwell hi level alarm | All Wastewater System ROC General | 2026-02-20
ROC | February | HMSS- Power loss on site. Gavin W on site will take a look and investigate | All Wastewater System ROC General | 2026-02-19
ROC | February | Adam Button signing in 3C Foggy | All Wastewater System ROC General | 2026-02-20
ROC | February | SUSP - Terry C on site to complete maintenance on blower 1. | All Wastewater System ROC General | 2026-02-17
ROC | February | AUSSSR- Line 1 OOS due to valve fault. Notified Dan K. Directed to disregard. Maintenance is working to get it online but may be out for a couple days | All Wastewater System ROC General | 2026-02-17
ROC | February | KBSP - Marcus R on site to complete an Alum tank fill. BLSS - Gavin W leaving site. Issue with security contacts on the door, unable to arm the system. Transferred to security. | All Wastewater System ROC General | 2026-02-17
ROC | February | KSSP- Gen eye wash activation alarm came in. Notified Kevin K. Will confirm with contractors on site | All Wastewater System ROC General | 2026-02-20
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-20
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-22
ROC | February | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-02-20
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-10
ROC | February | yds + ynss normal | All Wastewater System ROC General | 2026-02-11
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-22
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-22
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-22
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-23
ROC | February | MTSP - Aeration tank 1 DO lo. Currently tank1 is the controlling tank with 2 blowers running. No mention of running a third blower on shift report. Followed up with Dan K. Okay to run third blower in man/on. Around 19:00 when tank 1 took a dive in reading to lo level. Will continue to monitor Consult | All Wastewater System ROC General | 2026-02-16
ROC | February | BLSS- Dan H done on site all back in auto | All Wastewater System ROC General | 2026-02-11
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-15
ROC | February | MTSP - Terry R called to request opening sludge transfer valve to drain thickening tank. Man/open Sludge transfer Vlv and closed after tank reached 0.0m | All Wastewater System ROC General | 2026-02-22
ROC | February | Ethan Ullalkar signing out. | All Wastewater System ROC General | 2026-02-14
ROC | February | SUSP- Satnam M on site to work on barscreen | All Wastewater System ROC General | 2026-02-19
ROC | February | PVSS- Pump 3 Fault Alarm, Odour Fan Umcommanded Stop. Alarms cleared. | All Wastewater System ROC General | 2026-02-15
ROC | February | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-02-21
ROC | February | SUSP - UV System Major Fault alarm outstanding. Called Cam B. who will take a look | All Wastewater System ROC General | 2026-02-13
ROC | February | YDSS+ YNSS Normal | All Wastewater System ROC General | 2026-02-18
ROC | February | NBSP - Sludge thickener level hi, called and confirmed Lauren S still onsite wasting Consult | All Wastewater System ROC General | 2026-02-15
ROC | February | AUSS- Gen 1 engine warning, gen 1 engine coolant temperature low alarms - notified Barry M. | All Wastewater System ROC General | 2026-02-12
ROC | February | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-02-12
ROC | February | NBSSJA - Gavin W running generator. | All Wastewater System ROC General | 2026-02-10
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-14
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-14
ROC | February | JDSS - Terry C finished on site. | All Wastewater System ROC General | 2026-02-12
ROC | February | SUSR - David D working on floats, disregard wet well Hi level alarms for the duration of the work. | All Wastewater System ROC General | 2026-02-18
ROC | February | Adeela Khan signing in. Weather: -1C and flurries | All Wastewater System ROC General | 2026-02-22
ROC | February | BLSS - Multiple Emergency stop alarms came in. Daniel H. called to inform that he will be on site all night for a shutdown. Dan informed that all alarms can be disregarded 22:33 - Daniel called back and requested to call on call electrician. Called David D. who will give Daniel a call 01:40 - David D. called back and requested a CMU5. CMU5 Created W11654525 #CONSULT | All Wastewater System ROC General | 2026-02-10
ROC | February | Carter D Signing In, -6D/Clear | All Wastewater System ROC General | 2026-02-19
ROC | February | H5NBSP - Ian W restarting server. | All Wastewater System ROC General | 2026-02-12
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-10
ROC | February | Adeela Khan signing in. Weather: -2C and Cloudy | All Wastewater System ROC General | 2026-02-10
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-18
ROC | February | YDSS + YNSS Normal AUSSYS - Line trouble high wetwell on dialer. Site appears okay on trends and levels okay | All Wastewater System ROC General | 2026-02-15
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-15
ROC | February | RHAMF - Eric S reset fans onsite, leaving shortly | All Wastewater System ROC General | 2026-02-15
ROC | February | Connor Smith signing in -2 Cloudy | All Wastewater System ROC General | 2026-02-15
ROC | February | KSSP - Alum Chem Room MUA -11 Differential Pressure Switch Hi alarm came in. Higher priority alarm. Called Chris C. who will take a look. | All Wastewater System ROC General | 2026-02-13
ROC | February | SHSP - Lance J on site to test the filter reject sump float alarm. | All Wastewater System ROC General | 2026-02-17
ROC | February | SEOC6 - Terry C finished and leaving site. | All Wastewater System ROC General | 2026-02-17
ROC | February | RHAMF - Unit 2 recirculation water flow lolo and pump pressure low alarm. Checked site, pump 2 has interlocked due to the lolo flow alarm. Attempted to reset alarms, alarms cleared and then returned. Shift report states that all alarms can be disregarded as long as one fan is running. Checked fans, both AMF fans are currently active. Disregard alarms. | All Wastewater System ROC General | 2026-02-18
ROC | February | HLSSBS - Tyson C. doing pump 3 inspection | All Wastewater System ROC General | 2026-02-12
ROC | February | QVSSSC, Tyson C on site, running generator/testing temp alarms and testing flood/sump alarms | All Wastewater System ROC General | 2026-02-18
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-17
ROC | February | YDSS + YYNSS Normal | All Wastewater System ROC General | 2026-02-13
ROC | February | RHAMF1, Fan 1/2 Faulted, Notified Jimmy from NAC, he will send his team over to the site | All Wastewater System ROC General | 2026-02-13
ROC | February | SECC- Eric S on site for gas analyzer work. Will call when done 12:13- SECC-Eric S done on site | All Wastewater System ROC General | 2026-02-12
ROC | February | KCSSKR- Screen failed to stop alarm came in. Able to reset alarm | All Wastewater System ROC General | 2026-02-20
ROC | February | NBSP - Ian W testing new alarm for UV system. | All Wastewater System ROC General | 2026-02-13
ROC | February | SUSP- UV bank 1a Major alarm common major alarms came in. Bank 1b running okay and flow stated up. Disregard on shift report cleared upon acknowledgment | All Wastewater System ROC General | 2026-02-20
ROC | February | Adam Button signing out | All Wastewater System ROC General | 2026-02-19
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-19
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-14
ROC | February | BLSS, Young J is finished on site | All Wastewater System ROC General | 2026-02-13
ROC | February | KBSP - Terry C working on generator, disregard alarms for the duration of the work. 11:03 Marcus R running generator. | All Wastewater System ROC General | 2026-02-13
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-19
ROC | February | NBSP - Vortex #2 Water Scour Uncommanded Close alarm came in. Ack/reset as per shift report | All Wastewater System ROC General | 2026-02-20
ROC | February | KBSP - Marcus R working on Head work blowers. | All Wastewater System ROC General | 2026-02-13
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-23
ROC | February | NBSP- Alum P 3 uncommanded stop alarm came in. Left outstanding as alum P2 is running in its place. Emailed West waste water Ops | All Wastewater System ROC General | 2026-02-17
ROC | February | Ethan Ullalkar signing out. | All Wastewater System ROC General | 2026-02-15
ROC | February | YDSS + YNSS Normal Carter D Signing Out | All Wastewater System ROC General | 2026-02-12
ROC | February | YDSS + YNSS Normal Connor Smith signing out | All Wastewater System ROC General | 2026-02-16
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-17
ROC | February | YDSS + YNSS normal | All Wastewater System ROC General | 2026-02-22
ROC | February | AUSS- Dan K notified ROC. P1/4 will be OOS for tonight and if P3 valve faults come in try to reset and if it doesn't it should be able to clear remotely a couple hours later. Placed P4 in man/off | All Wastewater System ROC General | 2026-02-17
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-18
ROC | February | SUSP - Cameron B. is on site working on the UV's. Directed to disregard bank 2A alarms | All Wastewater System ROC General | 2026-02-13
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-15
ROC | February | Carter D Signing In | All Wastewater System ROC General | 2026-02-10
ROC | February | AUSS- P3 MV4 interlocked on fault. Would not reset. Notified Dan K. Directed to leave outstanding for the day HLSSBS- Tyson C on site to run generator test flood alarms sump alarms and JHS inspections | All Wastewater System ROC General | 2026-02-10
ROC | February | AUSS- Dan K req Tyler ZJ to give him a call regarding generator issues on site | All Wastewater System ROC General | 2026-02-12
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-15
ROC | February | QVSSSC- Dan from Wessuc Called and spoke with Kevin K that a operator will be dispatched within in an hour if needed SHSP- Power fail on site blowers clarifier faults as well as generator running. Notified Lance j on site and will reset outstanding alarms SHSSDK-P1 failed to start and vfd fault alarms came in P2 uncommanded stop during power outage. Reset alarms P2 running in auto Notified Lance J of outage and will attend site when done at SHSP | All Wastewater System ROC General | 2026-02-10
ROC | February | Angelica Chepiga signing out | All Wastewater System ROC General | 2026-02-12
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-13
ROC | February | NBSP - UV system minor fault, disregard as per shift report | All Wastewater System ROC General | 2026-02-14
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-15
ROC | February | Angelica Chepiga signing in, weather -12C | All Wastewater System ROC General | 2026-02-13
ROC | February | BLSS - Site hydro fail alarm and low flow alarms. Checked site, generator is running and pump duty has resumed. Pumps cycled through duty as they struggled with discharge valve faults. Waiting for the wet well level to drop to normal levels before clearing pump alarms. HMSS - PAC Control panel power failure alarm and wetwell level alarms. Checked site, generator is running and ATS is pointing to the generator indicating a true power outage. Operations appear normal with pump 2 in duty 1 pushing flow. Overflow to Toronto maintenance hole 1 alarm triggered but there is no indication of higher than normal wet well levels. Cleared all alarms except generator running. 20:31 - BLSS/HMSS - Alectra power outage map shows a large power outage in the area of BLSS and HMSS. Will monitor situation. 21:39 - BLSS - Utility power has been restored and generators have shut down. On power transfer the duty 1 pump (pump 3) faulted, and duty rotated to pump 2 which is operating normally. Will let pump 2 run for a few minutes before resetting alarms as the duty will rotate back to pump 3. | All Wastewater System ROC General | 2026-02-13
ROC | February | YDSS + YNSS Normal NBSP - Vortex 1 air scour uncommanded close alarm. Cleared alarm as per the shift report. | All Wastewater System ROC General | 2026-02-14
ROC | February | NBSP- Sludge Thickener Level HiHi Alarm. Can disregard as per Lauren S CONSULT | All Wastewater System ROC General | 2026-02-15
ROC | February | Adam Button signing in | All Wastewater System ROC General | 2026-02-12
ROC | February | Carter D Signing In, -3D/Snowing YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-11
ROC | February | RHAMF1- Station Power Failure. AMF Fan 1, Fan 2 VFD Fault Alarms, Odour Control System Offline. Notified Jimmy from NAC. He will send someone in the morning to reset. | All Wastewater System ROC General | 2026-02-15
ROC | February | Ethan U signing in Weather -1. | All Wastewater System ROC General | 2026-02-15
ROC | February | LSSS, LSSS2 to LSSS4 Comm Fail, notified Yash S, he will look into it | All Wastewater System ROC General | 2026-02-18
ROC | February | LSSS- Phil R on site to test sump pit flood and auto dialer NMSSBP- Terry R on site for site inspections may be rotating duty | All Wastewater System ROC General | 2026-02-10
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-16
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-16
ROC | February | LSSS - Emily B from EME on site for sampling and requested that pump 6 be placed in duty 1. Made necessary change. | All Wastewater System ROC General | 2026-02-17
ROC | February | NMSSBP - Mech screen 1 fault alarm. Checked site, channel 1 inlet gate is manual/closed. No flow to the faulted barscreen. | All Wastewater System ROC General | 2026-02-17
ROC | February | Carter D Signing Out | All Wastewater System ROC General | 2026-02-18
ROC | February | YDSS+YNSS normal | All Wastewater System ROC General | 2026-02-16
ROC | February | YDSS + YNSS normal | All Wastewater System ROC General | 2026-02-13
ROC | February | YDSS + YNSS Normal Christian Van Beek signing out. | All Wastewater System ROC General | 2026-02-19
ROC | February | YDSS+YNSS normal | All Wastewater System ROC General | 2026-02-16
ROC | February | MTSP - Man/stop blower 1 | All Wastewater System ROC General | 2026-02-16
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-17
ROC | February | RHAMF - Unit 2 reciculation pump presure lolo, water flow lolo. Disregard alarm as per shift report as fans running | All Wastewater System ROC General | 2026-02-17
ROC | February | KSSP - Sludge holding Blwr 1 hi dif press alarm, alum, chem Rm MUA-11 Dif press Sw hi alarm. Both sludge blowers are off. Informed Darren B, disregard for the night Consult | All Wastewater System ROC General | 2026-02-18
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-18
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-13
ROC | February | LSSS4- PAC comm fail. Cleared upon acknowledgement. Trends okay | All Wastewater System ROC General | 2026-02-12
ROC | February | LSSS - Artour L. is on site for asset tagging | All Wastewater System ROC General | 2026-02-13
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-17
ROC | February | KSSP- Tyson C on site to work on membrane and to disregard membranes not inauto and low water alarms on site | All Wastewater System ROC General | 2026-02-17
ROC | February | BLSS, Young J on site with contractor, directed to disregard alarms all night as he will be there watching over the station, pumps will be in local | All Wastewater System ROC General | 2026-02-12
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-18
ROC | February | RHAMF - AMF Fan 1 & 2 VFD fault. Informed Eric S as primary oncall Jimmy H unavailable. Will look into issue in the morning | All Wastewater System ROC General | 2026-02-16
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-20
ROC | February | Adeela Khan signing in. Weather: -15C and sunny | All Wastewater System ROC General | 2026-02-13
ROC | February | NBSP - Vortex #1 Air Scour Uncommanded close alarm came in. Ack/reset as per shift report | All Wastewater System ROC General | 2026-02-11
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-16
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-17
ROC | February | SHSP- Compressor 1 e stop switch hihi and overload alarms came in. Notified Lance J. Contractors on siter working on compressor and compressor 2 is D1. Directed to disregard until work is completed | All Wastewater System ROC General | 2026-02-17
ROC | February | NMVCBP - Parth P on site to complete a flowmeter calibration. | All Wastewater System ROC General | 2026-02-17
ROC | February | NMSSBP - Barry M. called to inform that he is on site looking into the high wet well levels | All Wastewater System ROC General | 2026-02-20
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-11
ROC | February | Ethan Ullalkar signing out. | All Wastewater System ROC General | 2026-02-22
ROC | February | ABMC - Kyle B on site for UPS maintenance. | All Wastewater System ROC General | 2026-02-18
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-12
ROC | February | AUSS- P3 disc hdr MV4 fault alarm came in. Wasn't able to clear Placed P3 in man/off emailed Central-east wastewater | All Wastewater System ROC General | 2026-02-16
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-23
ROC | February | JDSS- Terry C on site to replaced batteries on generator | All Wastewater System ROC General | 2026-02-12
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-12
ROC | February | Angelica Chepiga signing in, weather -9C | All Wastewater System ROC General | 2026-02-12
ROC | February | QVSSSC - Tyson C on site for pumps testing. Will run pumps in manual mode, disregard High wet well level alarms. | All Wastewater System ROC General | 2026-02-12
ROC | February | AUEQSJ - Rick L on site for annual calibration. | All Wastewater System ROC General | 2026-02-10
ROC | February | NMSSHS- Barry M on site to test dialer, hi lo temp and drywaell flood alarms KSSSQW- Darren B o n site to run generator and perform JHS inspections | All Wastewater System ROC General | 2026-02-10
ROC | February | YDSS + YNSS Normal Carter D Signing Out | All Wastewater System ROC General | 2026-02-13
ROC | February | RHAMF1- Jimmy from NAC on site resetting alarms. Notified Jimmy of outstanding VFD alarms and generator running status | All Wastewater System ROC General | 2026-02-10
ROC | February | KSSP - UV Channel 1 1 A bank low intensity fault alarm. Checked site, UV channel 1 bank 1A is currently active. Dosage and power levels are good and trending shows intensity is stable but slightly dipping below low alarm setpoint. Shift transfer states that minor fault alarms are a disregard. The major fault box status is normal indicating this is a minor fault alarm. Alarm cleared on acknowledgement and triggered again. Monitoring site. | All Wastewater System ROC General | 2026-02-13
ROC | February | BLSS - Scrubber blower 1 uncommanded stop alarm, drywell SF3 uncommanded stop alarm, pump room EF4 uncommanded stop alarm, pump 3 uncommanded stop alarm, screen 1 uncommanded stop alarm and pump 5 fault alarm. Checked site, operations appear normal, pump 4 is operating in duty 1 and pushing flow. Fans and ventilation systems seem to have faulted, possibly due to a power blip. Able to clear all alarms except the pump5 fault but pump 5 is currently local off and OOS. Ventillation and screen systems back online. HMSS - PAC control panel power fail alarm and pump 4 uncommanded stop alarm. Checked site, pump 5 is operating in duty 1 and pushing flow. Possible power blip, able to reset alarms. GRSSWA - wet well 1 ultrasonic lolo level alarm. Checked site, operations appear normal. Reset alarm. | All Wastewater System ROC General | 2026-02-13
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-14
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-12
ROC | February | Christian Van Beek signing in. Weather: -4C and clear. | All Wastewater System ROC General | 2026-02-13
ROC | February | Angelica Chepiga signing out | All Wastewater System ROC General | 2026-02-13
ROC | February | Carter D Signing Out | All Wastewater System ROC General | 2026-02-10
ROC | February | NMSSBP - Mechanical Screen 2 Overtorque Alarm came in. Will send an email to Daniel K. | All Wastewater System ROC General | 2026-02-11
ROC | February | SEOC4 Eric S finished on site. | All Wastewater System ROC General | 2026-02-12
ROC | February | NMSSBP, Mech Screen 2 Emergency stop, notified Barry M, he will look into it | All Wastewater System ROC General | 2026-02-10
ROC | February | Angelica Chepiga signing out | All Wastewater System ROC General | 2026-02-10
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-14
ROC | February | Angelica Chepiga signing in,weather +2C | All Wastewater System ROC General | 2026-02-20
ROC | February | Angelica Chepiga signing out | All Wastewater System ROC General | 2026-02-21
ROC | February | KSSP - UC Ch, 1 bank 1A low UV intensity fault, alarm cleared to normal status. UB panel 1 lamp low intensity, reading appears okay for intensity and UV running okay | All Wastewater System ROC General | 2026-02-14
ROC | February | NMSSBP- Mech Screen 1 Overtorque Alarm. Called Chris R. Requested to place Screen 2 Gate 1 man/closed and will leave outstanding for the weekend. Requested a call if any issues with screen 1. CONSULT | All Wastewater System ROC General | 2026-02-21
ROC | February | Christian Van Beek signing in. Weather: -4C and snow | All Wastewater System ROC General | 2026-02-18
ROC | February | SUSP- Satnam M done on site. Notified Satnam M barscreen and vortex/ dewatering screws are not in auto. Will place back in auto 11:56- Satnam M confirmed with Ops headworks is normally in local but runs in auto | All Wastewater System ROC General | 2026-02-19
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-21
ROC | February | MTSP - Aeriation tank 2 DO lolo, man/start blower 2 13:28 - Place blower 2 back in auto | All Wastewater System ROC General | 2026-02-22
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-18
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-13
ROC | February | SEOC 4 - Shaft 4 air DMP2 uncommanded close alarm and shaft 4 FAN2 uncommanded stop alarm. The DMP2 uncommanded close alarm is a disregard on the shift report. Fan 2 is faulted but duty rotated to fan 1 which is operating. Able to clear both alarms. | All Wastewater System ROC General | 2026-02-14
ROC | February | SUSP- Sludge tanke level hihi alarm came in. Notified Darren B directed to disregard alarm #consult | All Wastewater System ROC General | 2026-02-16
ROC | February | MTSP- Aeration tank 2 DO lo alarm came in. Will continue to monitor and placed blower in manual if DO lolo comes in | All Wastewater System ROC General | 2026-02-16
ROC | February | SUSP - UV Ch1 critical failure, high level. Alarm due to fault upon plant start up due to a high channel level. Alarm will clear once UV gates open. Disregard as per shift report. Alarms cleared when acknowledged | All Wastewater System ROC General | 2026-02-22
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-14
ROC | February | SUSP- UV system Critical failure/ ch1 high level/Critical alarm/ UV2 high level and common critical alarms came in. Cleared upon acknowledgment and came in as UV ch1 opened up disregard on shift report | All Wastewater System ROC General | 2026-02-16
ROC | February | Christian Van Beek signing in. Weather: 1C and clear. | All Wastewater System ROC General | 2026-02-19
ROC | February | YDSS+YNSS normal | All Wastewater System ROC General | 2026-02-16
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-17
ROC | February | Adeela Khan signing in. | All Wastewater System ROC General | 2026-02-20
ROC | February | YDSS + YNSS Normal Adeela Khan signing out | All Wastewater System ROC General | 2026-02-13
ROC | February | KBSP - Marcus R working on filters and DO sensors. | All Wastewater System ROC General | 2026-02-18
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-20
ROC | February | SUSSWB - Ventilation H2S OOR Alarms. Disregarded as per shift report | All Wastewater System ROC General | 2026-02-22
ROC | February | HLSSBS - Hydrogen Sulphide Sample 1 Fault alarm came in. Critical alarm. Shift report directs to disregard alarm. | All Wastewater System ROC General | 2026-02-22
ROC | February | KSSP - RSHW Grit room H2S OOR/Fault alarm, disregard as per shift report | All Wastewater System ROC General | 2026-02-14
ROC | February | QVSSSC - Ricardo L. is on site for annual calibrations. May need to enter a confined space but will inform the ROC. | All Wastewater System ROC General | 2026-02-20
ROC | February | KSSP - Phil from AB Project Management and Construction is on site and will be working in the generator room. Phil informed he will call back if he will be running the generator 09:01 - Chase J. called to inform that he will be running the generator in test mode 15:58 - Phil is finished on site | All Wastewater System ROC General | 2026-02-20
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-18
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-19
ROC | February | KSSP - Collection blower 2 high diff pressure alarm. Checked site, duty rotated to blower 1 which activated. Unable to clear alarm, shift report states it is a disregard. | All Wastewater System ROC General | 2026-02-19
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-22
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-14
ROC | February | RHAMF1- Eric from NAC on site. He cleared alarms on site, Ack/reset alarms, Recirculation Pump 1 restarted. | All Wastewater System ROC General | 2026-02-18
ROC | February | AUSS - Generator 1,2,3 not in auto alarms, cleared right away. | All Wastewater System ROC General | 2026-02-21
ROC | February | QVSSSC- Rick L and Parth P on site for annual calibrations AUSS- Phil R on site working on P4, wet well high level test, surge tanks and inlet gates | All Wastewater System ROC General | 2026-02-19
ROC | February | 10030 Bayview Ave Richmond Hill Storm Sewer- Called Roads spoke with Karen to notify them that storm sewers are operated by the roads department not water or waste water Ops. | All Wastewater System ROC General | 2026-02-11
ROC | February | KSSP. Neut Process (MC) Took Too Long alarm, critical alarm, notified Darren B, he is looking into it 19:38, Darren B is heading to site CMU: W11658868 | All Wastewater System ROC General | 2026-02-11
ROC | February | Ethan U signing in Weather -4. | All Wastewater System ROC General | 2026-02-22
ROC | February | HLSSBS- Tyson C done on site heading to QVSSSC | All Wastewater System ROC General | 2026-02-10
ROC | February | Adam Button signing in in -3C clear | All Wastewater System ROC General | 2026-02-11
ROC | February | Adam Button signing in -6C Snowing | All Wastewater System ROC General | 2026-02-10
ROC | February | 10030 Bayview Avenue, Richmond Hill - City of Richmond Hill Operator (Eve 416 460 2683) called Roads Operator Karen to inform of a broken lead on a Storm Sewer main. Karen called the ROC and informed this is a W/WW issue. 05:20 - Called Marcus R. who informed this is a c-east WW. 05:25 - Called Daniel K. who requested an email and will attend site. After checking all pipes, Daniel noticed that this is not anything related to central east WW and would be under roads jurisdiction. 06:00 - Passed all information onto Adam B. #CONSULT | All Wastewater System ROC General | 2026-02-11
ROC | February | Angelica Chepiga signing out | All Wastewater System ROC General | 2026-02-18
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-19
ROC | February | QVSSSC - PAC Commfail alarm. Trends missing since 10:51, notified Ian W, he will check SCADA. 11:15 Ian W will call Kevin K. | All Wastewater System ROC General | 2026-02-10
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-14
ROC | February | Angelica Chepiga signing in | All Wastewater System ROC General | 2026-02-10
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-10
ROC | February | AUSSSR - Aysix System Heartbeat alarm came in. Cleared alarm and site is back to normal operations | All Wastewater System ROC General | 2026-02-21
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-22
ROC | February | KBSP - Reject sump pmp 1 E. stop. Disregard as per shift report | All Wastewater System ROC General | 2026-02-22
ROC | February | KBSP - Lauren S working on headworks, disregard alarms for the duration of the work. | All Wastewater System ROC General | 2026-02-12
ROC | February | KSSP- UV panel lamp lo intensity and intensity fault alarms came in. Have been reoccurring all day. Notified Darren B. Directed to disregard for night as long as dosage is okay #consult | All Wastewater System ROC General | 2026-02-12
ROC | February | KSSP- Neil O cleared alarms on site and is leaving. Contractors are done for the dya | All Wastewater System ROC General | 2026-02-17
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-11
ROC | February | QVSSSC - Kevin K called, he placed pumps man/off for pump testing and monitoring remotely, disregard wet well level alarm. Tyson C will attend site. | All Wastewater System ROC General | 2026-02-12
ROC | February | YDSS+YNSS normal | All Wastewater System ROC General | 2026-02-17
ROC | February | Christian Van Beek signing out. | All Wastewater System ROC General | 2026-02-17
ROC | February | QVSSSC- Kevin K req vac truck services to pump down wetwell. Called Wessuc (1-866-493-7782) as per procedure. Spoke with Mark who will follow up with Ops and notify ROC in 10 mins for truck dispatch. | All Wastewater System ROC General | 2026-02-10
ROC | February | SEOC 67- Phil R onsite running generator | All Wastewater System ROC General | 2026-02-11
ROC | February | Adeela Khan signing out | All Wastewater System ROC General | 2026-02-11
ROC | February | SHSP- Garrick from Ferguson Electric is on site fore generator work. Not transferring over | All Wastewater System ROC General | 2026-02-12
ROC | February | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-02-12
ROC | February | Carter Dunn Signing In, -2D/Clear | All Wastewater System ROC General | 2026-02-12
ROC | February | RHAMF1- Power back to normal, generator stopped, Jimmy from NAC reset all alarms and leaving site. | All Wastewater System ROC General | 2026-02-10
ROC | February | YDOC- Fan 1 Fault Alarm outstanding from this morning. Notified Phil R. | All Wastewater System ROC General | 2026-02-11
ROC | February | Adam Button signing out | All Wastewater System ROC General | 2026-02-10
ROC | February | KBSP - Marcus R. working on DO probes and rectangular clarifiers | All Wastewater System ROC General | 2026-02-11
ROC | February | QVSSSC- Tyson C called. He will be running pumps in manual and local. Disregard related alarms. | All Wastewater System ROC General | 2026-02-11
ROC | February | KSSSP- Neil O working on membrane turbidimeters. | All Wastewater System ROC General | 2026-02-11
ROC | February | NBSP- UV system minor fault alarm. UV 1b running okay disregard on shift report | All Wastewater System ROC General | 2026-02-10
ROC | February | LSSS- Brent St C on site with Wajax. They will be performing maintenance on generators on site and will be running them during this time. Later in the day Chris R will be on site for power transfer. KBSP- Lauren S on site to work on all blowers including sludge/aeration and diversion tank blowers | All Wastewater System ROC General | 2026-02-11
ROC | February | QVSSSC- Eric S on site to work on LIT 2 NBSP- Young J on site to work on sani sump hi level and reject sumps | All Wastewater System ROC General | 2026-02-11
ROC | February | KSSP- Tyson C onsite testing headworks gas detectors. | All Wastewater System ROC General | 2026-02-11
ROC | February | RHAMF - UNIT Recirculation Water flow LoLo and pump pressure low alarm. Same alarms that triggered for recirculation pump 2. Both AMF fans still running. Disregard as per the shift report. | All Wastewater System ROC General | 2026-02-19
ROC | February | YDSS + YNSS Normal Connor Smith signing out | All Wastewater System ROC General | 2026-02-11
ROC | February | YDSS + YNSS Normal Christian Van Beek signing out. | All Wastewater System ROC General | 2026-02-20
ROC | February | AUSS- David D and Satnam M on site to work on P4 10:09-KBSP- Marcus R and Lauren are on site. Lauren S working on RAS/WAS system and contractors will be working on HVAC system | All Wastewater System ROC General | 2026-02-17
ROC | February | MTSP - Final Effluent Flow LoLo alarm came in. Disregarded as per shift report | All Wastewater System ROC General | 2026-02-11
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-15
ROC | February | QVSSSC- Power loss on site Force main 1 2 valve fault and wet well 1/2 hydrostatic lolo/OOR alarms came in. Notified Tyson C will be on site later today but to call if site doesnt run in duty KBSP- Lauren S on site to test hi sump level for head works. and tertiary building | All Wastewater System ROC General | 2026-02-10
ROC | February | YDOC - Eric S. working on biofilter drain pH | All Wastewater System ROC General | 2026-02-12
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-17
ROC | February | Ethan U signing in Weather 0c | All Wastewater System ROC General | 2026-02-17
ROC | February | Carter D Signing In | All Wastewater System ROC General | 2026-02-18
ROC | February | MTSS - Terry R testing wet well hi and sump pit alarms. | All Wastewater System ROC General | 2026-02-13
ROC | February | QVSSSC- Eric S finished onsite. | All Wastewater System ROC General | 2026-02-11
ROC | February | AUEQSJ - Rick L finished on site. | All Wastewater System ROC General | 2026-02-10
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-19
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-21
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-21
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-22
ROC | February | Gluzen Ramos Ong signing in | All Wastewater System ROC General | 2026-02-12
ROC | February | Adam Button signing out | All Wastewater System ROC General | 2026-02-11
ROC | February | YDSS+YNSS normal | All Wastewater System ROC General | 2026-02-16
ROC | February | SEOC4 - Eric S on site replacing O2 sensor. | All Wastewater System ROC General | 2026-02-12
ROC | February | KSSP, Lo UV Intensity fault, notified Darren B as he is on site and its not in the shift report, directed to disregard consult | All Wastewater System ROC General | 2026-02-11
ROC | February | SUSP- UV CH 1 Common Critical Alarm. UV Ch. 1 High Level Alarm. UV System Critical Failure Alarm. Alarms cleared upon acknowledging. Known issue on SCADA Report | All Wastewater System ROC General | 2026-02-21
ROC | February | KSSP- UV ch1 common major/ Major/ Module Comm fail and UV panel major fault alarms came in. Bank 2 running currently. Notified Neil O of alarms and will take a look on site | All Wastewater System ROC General | 2026-02-10
ROC | February | Ethan U signing in Weather 2. | All Wastewater System ROC General | 2026-02-16
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-16
ROC | February | SUSP - Outstanding UV System Major Fault alarm. Called Darren B. who directed to disregard alarm. #CONSULT | All Wastewater System ROC General | 2026-02-13
ROC | February | Adam Button signing out | All Wastewater System ROC General | 2026-02-16
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-18
ROC | February | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-02-21
ROC | February | AUSS - Pump 5 dicharge MV@ failed to open alarm. Checked site. Duty 1 rotated to pump 4 which is pushing flow. Cleared alarms. | All Wastewater System ROC General | 2026-02-14
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-15
ROC | February | KBSP - Reject sump pump 1 Estop alarm. Checked site . Reject pump 2 is running. Disregard alarm as per SCADA review. | All Wastewater System ROC General | 2026-02-18
ROC | February | YDSS + YNSS Normal Connor Smith signing out. | All Wastewater System ROC General | 2026-02-21
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-21
ROC | February | KSSP- UV panel lamp lo intensity and intensity fault alarms, UV1 running, intensity normal. Disregard alarm as per Darren B. | All Wastewater System ROC General | 2026-02-13
ROC | February | NMSSBP - Mech screen 1 overtorque alarm. Checked site, mechanical screen 1 has interlocked and is local/off. Called Dan K who directed to close the screen 1 inlet gate 1. Made the necessary change. Daniel K will inspect the screen on Sunday. #consult | All Wastewater System ROC General | 2026-02-13
ROC | February | NBSP- Harie R on site working on air compressors | All Wastewater System ROC General | 2026-02-17
ROC | February | Adeela Khan signing out | All Wastewater System ROC General | 2026-02-22
ROC | February | Adam Button signing in -5C Clear | All Wastewater System ROC General | 2026-02-16
ROC | February | YDSS+YNSS normal | All Wastewater System ROC General | 2026-02-16
ROC | February | YDSS+YNSS normal | All Wastewater System ROC General | 2026-02-16
ROC | February | YDSS + YNSS Normal Christian Van Beek signing out. | All Wastewater System ROC General | 2026-02-14
ROC | February | Connor Smith signing in -1 Cloudy | All Wastewater System ROC General | 2026-02-14
ROC | February | KSSP- Citric Acid Tank Lvl HiHi. Tank showing in normal range. Cleared alarm YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-14
ROC | February | KSSP - Scum chamber 1 high level. Disregard as per shift report | All Wastewater System ROC General | 2026-02-18
ROC | February | Angelica Chepiga signing in, weather -2C | All Wastewater System ROC General | 2026-02-18
ROC | February | SEOC6 - Phil R. called to inform that he is on site and will be testing the generator | All Wastewater System ROC General | 2026-02-20
ROC | February | AUSSYS- All pumps in man/off and wetwell 1/2 no discharge path alarms came in. Notified Kevin S. On site with pumps off to actuate valves | All Wastewater System ROC General | 2026-02-20
ROC | February | Adam Button signing out | All Wastewater System ROC General | 2026-02-17
ROC | February | MTW3 - Patrick F found a verry small leak after attending site. Leaving scrubber local/on over night | All Wastewater System ROC General | 2026-02-17
ROC | February | RHAMF - Station power failure, AMF fan 1 & 2 VFD fault. Called Jimmy H (NAC contact) unable to get a hold. Called Eric S, will follow up with Jimmy later and follow back up if he will attend site today 9:40 - Eric onsite reset fans | All Wastewater System ROC General | 2026-02-14
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-14
ROC | February | KSSP - UV panel 1 lamp low intensity. UV still running with intensity. Email sent to North WW regarding alarm | All Wastewater System ROC General | 2026-02-14
ROC | February | BLSS - Pump 3 uncmd stop, scrubber blo 2 uncmd stop/start, drywell SF3 uncd stop, disch vlv failed to open. Able to clear alarms | All Wastewater System ROC General | 2026-02-17
ROC | February | NMSSHS - High well well on dialer. Site appears fine no duty active with levels within range PVSS - Pump failure on dialer, site appears in good standing, no issues with pumps, duty 1 off | All Wastewater System ROC General | 2026-02-17
ROC | February | SEOC 4 - Shaft 4 O2 Monitor alarm, disregard as per shift report. | All Wastewater System ROC General | 2026-02-12
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-15
ROC | February | KBSP- Lauren S performing oil change on clarifier 2 | All Wastewater System ROC General | 2026-02-17
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-06
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-06
ROC | February | Adeela Khan signing out | All Wastewater System ROC General | 2026-02-06
ROC | February | Adeela Khan signing out | All Wastewater System ROC General | 2026-02-08
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-08
ROC | February | YDSS + YNSS normal | All Wastewater System ROC General | 2026-02-08
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-08
ROC | February | AUSSSR- Line1 valve overtorque/ failed to close. Created CMU5 W11639400 and emailed Dan K as per shift report. #CMU5 | All Wastewater System ROC General | 2026-02-04
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-06
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-06
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-08
ROC | February | RHAMF1 - Power failure, generator running, odour control system offline alarms, Recirculation pumps interlocked on pressure low/low alarm. Power restored, alarms outstanding. Notified Phil R. He will check SCADA and contact NAC. 08:30 Fan 1 VFD fault alarm outstanding. Notified Jimmy H from NAC, he will attend site. | All Wastewater System ROC General | 2026-02-03
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-04
ROC | February | KSSP - Eric S replacing O2 sensor. 10:10 Eric S completed work, leaving site. | All Wastewater System ROC General | 2026-02-03
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-03
ROC | February | KSSP - Chase J requested disregard UV Panel Major fault alarm, UV 2 running normal. And disregard collection Blower 2 High Diff Pressure alarm. # Consult | All Wastewater System ROC General | 2026-02-05
ROC | February | KSSP - Mem Operating Area MUA - 10 Temp Switch Lo alarm came in. Disregarded as per shift report | All Wastewater System ROC General | 2026-02-07
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-08
ROC | February | Adeela Khan Signing in. Weather: -18C and clear | All Wastewater System ROC General | 2026-02-08
ROC | February | KSSP - Makeup Air Unit 6 Temp Switch Lo alarm came in. Disregarded as per shift report | All Wastewater System ROC General | 2026-02-08
ROC | February | Carter Dunn Signing Out | All Wastewater System ROC General | 2026-02-03
ROC | February | NBSP- Gavin W onsite for generator test. Also will be doing Health and Safety work orders. | All Wastewater System ROC General | 2026-02-03
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-04
ROC | February | RHAMF1 - Jimmy H from NAC called, he is on site, reset VFD fault alarm. As per Daniel K cleared alarm and restarted Fan 1. | All Wastewater System ROC General | 2026-02-03
ROC | February | KSSP - Membrane Air Blower 1 failed to start, called Chris C, no response, will call again. Chris C on site. 12:50 Chris C will check. | All Wastewater System ROC General | 2026-02-03
ROC | February | KCSSKR - Young J on site to test the wet well level hi alarm. | All Wastewater System ROC General | 2026-02-04
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-08
ROC | February | PVSS - Eric S working on H2S sensor. 13:15 Eric S finished on site. | All Wastewater System ROC General | 2026-02-03
ROC | February | KSSP- Mike B onsite working on chemical containment flood alarms | All Wastewater System ROC General | 2026-02-06
ROC | February | Connor Smith signing out | All Wastewater System ROC General | 2026-02-03
ROC | February | KSSP - Chase J on site to test the eyewash stations. Will trigger JHSC alarms. | All Wastewater System ROC General | 2026-02-04
ROC | February | SHSP- David D onsite working on Effluent Pumps | All Wastewater System ROC General | 2026-02-03
ROC | February | RHAMF - Multiple power related alarms came in. Checked site. Both fans are no longer running. AMF Fan 1, 2 VFD Fault and Odour Control System Offline alarms are outstanding. Generator is not running and site is still connected to hydro power.Called Jimmy H (416 826 0586) from NAC, as per interim, who will send his operators to site. Jimmy did not mention if he will call a Central East Operator to site yet. | All Wastewater System ROC General | 2026-02-06
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-09
ROC | February | NMSSJA- Harie R onsite testing drywell flood, hi/low temp, and autodialer. | All Wastewater System ROC General | 2026-02-03
ROC | February | SHSP - Lance J cleaning effluent tank. UV system off for the duration of work. | All Wastewater System ROC General | 2026-02-05
ROC | February | Angelica Chepiga signing in, weather -15C | All Wastewater System ROC General | 2026-02-04
ROC | February | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-02-04
ROC | February | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-02-04
ROC | February | YDSS+YNSS normal | All Wastewater System ROC General | 2026-02-05
ROC | February | NBSP - Process Building Temp Hi/Low alarm came in. Will send an email to the west ww team | All Wastewater System ROC General | 2026-02-09
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-09
ROC | February | YDSS+YNSS normal | All Wastewater System ROC General | 2026-02-05
ROC | February | Adam Button signing out | All Wastewater System ROC General | 2026-02-05
ROC | February | BLSS - Screen Differential Level Hi alarm came in. Disregarded as per shift report due to a foamy influent. Will call if hi wet well comes in | All Wastewater System ROC General | 2026-02-05
ROC | February | YDSS + YNSS normal | All Wastewater System ROC General | 2026-02-06
ROC | February | Angelica Chepiga signing in, weather -12C | All Wastewater System ROC General | 2026-02-05
ROC | February | NMSSBP - Daniel K. attended site to take a look at a gas monitor and noticed the front gate is stuck open. Spoke to Corporate security and they will dispatch mobile security to close the gate | All Wastewater System ROC General | 2026-02-06
ROC | February | KSSP - MUA2 Low Temp alarm came in. Disregarded as per shift report | All Wastewater System ROC General | 2026-02-07
ROC | February | MTSP - Final Effluent LoLo alarm came in. Disregarded as per shift report YDSS + YNSS Normal Adeela Khan signing out | All Wastewater System ROC General | 2026-02-07
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-07
ROC | February | NMSSBP - Mech screen 2 overtorque alarm. Checked site, barscreen 2 is interlocked and local off. Barscreen 1 is duty 1 and operating. Called Daniel K who will attend site later today. Created CMU5#W11645852 #consult #CMU5 | All Wastewater System ROC General | 2026-02-07
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-05
ROC | February | MTSP - Aeration tank 2 DO lolo alarm. Checked site, two blowers are active. Trending shows that the DO reading is recovering. Reset alarm | All Wastewater System ROC General | 2026-02-07
ROC | February | NBSP - Sludge thickener level hihi alarm. Checked site, trending shows the sludge thickener level increased rapidly to above the hihi alarm setpoint. No mention of this alarm on the disregard list. Contacted Marcus R who directed to place the WAS pumps into manual/off mode and disregard the alarm until Monday at 09:00. #consult | All Wastewater System ROC General | 2026-02-07
ROC | February | RHAMF- Ji Xiao from NAC onsite requested to reset alarms. Fans started back up | All Wastewater System ROC General | 2026-02-06
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-07
ROC | February | MTSP - Final Effluent Free Chlorine LoLo alarm came in. Disregarded as per shift report | All Wastewater System ROC General | 2026-02-09
ROC | February | Carter D Signing Out | All Wastewater System ROC General | 2026-02-06
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-06
ROC | February | SUSP - Sludge Tank Level HiHi alarm came in. Checked site. Noticed that level had gone back below the hihi level and alarm cleared | All Wastewater System ROC General | 2026-02-07
ROC | February | MTSS - Talha H completing an OIT reboot and directed to disregard the historian heartbeat alarm. | All Wastewater System ROC General | 2026-02-04
ROC | February | Connor Smith signing in -8C Clear | All Wastewater System ROC General | 2026-02-06
ROC | February | KBSP - Marcus R leaving site. Odour system recirc pump low flow is a disregard for the night. | All Wastewater System ROC General | 2026-02-09
ROC | February | YDSS + YNSS Normal Connor Smith signing out | All Wastewater System ROC General | 2026-02-05
ROC | February | Carter D Signing In, -24D/Clear | All Wastewater System ROC General | 2026-02-09
ROC | February | Angelica Chepiga signing in | All Wastewater System ROC General | 2026-02-09
ROC | February | SECC - Sump 1 level low switch alarm. Checked site, sump pump 1 is interlocked on the alarm. Trending shows a dip of the sump level which recovered quickly. Cleared alarm. | All Wastewater System ROC General | 2026-02-09
ROC | February | BLSS - Daniel H on site to complete scheduled work. Dan will be manually operating the site and has directed to disregard all alarms from site. | All Wastewater System ROC General | 2026-02-09
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-10
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-04
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-06
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-10
ROC | February | BLSS - Eric S on site, replacing O2 sensor. | All Wastewater System ROC General | 2026-02-03
ROC | February | AUSSMP - Bar Screen 1 General and Not in Auto alarms came in. Checked site. Bar screen 1 turned local and bar screen 2 is OOS. Called Daniel K. who is headed to site. CMU5 Created W11645773 22:42 - Daniel K. called back to inform he will need Lee F. to attend site. Called Lee F. who will speak to Daniel K 22:59 - Lee F. is headed to site. CMU5 Created W11645784 04:00 - Daniel K. called back to inform that he and Lee F. are finished on site. They were unable to get Bar Screen 1 back online but have now put Bar Screen 2 back online. Daniel informed that he had to close channel 1 inlet gate #CONSULT #CMU5 | All Wastewater System ROC General | 2026-02-06
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-04
ROC | February | NBSSJA- Eric S finished onsite. | All Wastewater System ROC General | 2026-02-06
ROC | February | YDSS+YNSS normal | All Wastewater System ROC General | 2026-02-04
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-03
ROC | February | YDSS+YNSS normal | All Wastewater System ROC General | 2026-02-05
ROC | February | LSSS - assigned P6 to Duty 1 for Ubah F ( IAM student), for sampling. | All Wastewater System ROC General | 2026-02-09
ROC | February | RHAMF1 - Jimmy from NAC called, he reset recirculation pump 2 VFD. Cleared alarm, Recirculation pump 2 restarted. | All Wastewater System ROC General | 2026-02-09
ROC | February | RHAMF - Station power failure alarm. Power blip affected several Richmond Hill facilities. Various additional alarms triggered which interlocked the pumps. Able to clear most alarms. Outstanding alarms include AMF fan 1 and 2 VFD faults and odor control system offline. Attempted to contact Jimmy Huiman but the call would not connect to the given number. Called Eric Sang who stated they will contact Jimmy. | All Wastewater System ROC General | 2026-02-10
ROC | February | KSSP- Uv Ch2 2a adjacent lamp fail. Disregard on shift report | All Wastewater System ROC General | 2026-02-04
ROC | February | KSSP- alum chem room MUA dif press sw hi alarm came in. Emailed north wastewater about outstanding alarm | All Wastewater System ROC General | 2026-02-05
ROC | February | Christian Van Beek signing in. | All Wastewater System ROC General | 2026-02-04
ROC | February | YDSS+YNSS normal KSSSQW- P3 vibration OOR alarm came in. Disregard on shift report | All Wastewater System ROC General | 2026-02-05
ROC | February | NBSSJA- Diesel tank level hihi alarm came in. Disregard on shift report | All Wastewater System ROC General | 2026-02-05
ROC | February | LSSS - Pump 4 Disch valve overtorque alarm. Pump in local mode, Daniel K on site. | All Wastewater System ROC General | 2026-02-04
ROC | February | JDSS- Evgeny S rebooting OIT. Disregard Heartbeat Alarm. 15:40- Work Completed | All Wastewater System ROC General | 2026-02-03
ROC | February | Christian Van Beek signing in. Weather: -22C and clear. | All Wastewater System ROC General | 2026-02-07
ROC | February | Angelica Chepiga signing out | All Wastewater System ROC General | 2026-02-03
ROC | February | SHSP- Filter Room Smoke Detector. Notified Lance J. Can disregard. | All Wastewater System ROC General | 2026-02-05
ROC | February | YDOC - Phil R. running generator | All Wastewater System ROC General | 2026-02-04
ROC | February | QVSSSC - Inlet channel high switch alarm. Disregard as per the shift report. | All Wastewater System ROC General | 2026-02-07
ROC | February | SUSSWB- Evgeny S rebooting OIT. Disregard Heartbeat Alarm. | All Wastewater System ROC General | 2026-02-03
ROC | February | KSSP - Chris C called, work on generators completed. | All Wastewater System ROC General | 2026-02-03
ROC | February | Connor Smith signing in | All Wastewater System ROC General | 2026-02-05
ROC | February | SHSP - Filter Room smoke detector alarm. Notified Marcus R , he will check SCADA and attend site. # CMU5 W11643074 | All Wastewater System ROC General | 2026-02-05
ROC | February | YDSS+YNSS NORMAL Angelica Chepiga signing out | All Wastewater System ROC General | 2026-02-05
ROC | February | NBSP - Process Bld UPS Fault alarm, notified Ian W. He will check SCADA. # CMU5 W11643060 17:50 Ian W checked SCADA, requested disregard alarm until tomorrow. | All Wastewater System ROC General | 2026-02-05
ROC | February | KSSP- UV Major Alarms. Called Chris C. He will look into it. | All Wastewater System ROC General | 2026-02-05
ROC | February | LSSS- Wet well screen diff level LOE came in trends okay. Reset alarm | All Wastewater System ROC General | 2026-02-05
ROC | February | SHSP - Filter Room Smoke Detector alarm. Marcus R. called back to inform that he is finished on site and has cleaned the smoke detector. Marcus informed this alarm can be disregarded for the night. | All Wastewater System ROC General | 2026-02-05
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-05
ROC | February | SEOC - OCF Fan Room 1 GO2 Low alarm came in. Disregarded as per shift report | All Wastewater System ROC General | 2026-02-05
ROC | February | KSSP - Channel Aeration Blower 2 High Differential Pressure alarm came in. Checked site. Noticed duty had rotated so that blower 1 is in duty 1. Will send an email to OIC | All Wastewater System ROC General | 2026-02-07
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-07
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-07
ROC | February | YDSS - Master Control Panel Failure alarm came in. Checked site. After 5 mins, alarms cleared and site is back to normal operations. Site was still connected to hydro power and generator did not run 20:11 - Alarm came back in along with control Panel Power Failure at YDOC3 and YDOC6. Called Ian W. who will take a look. CMU5 Created W11645765 20:56 - Ian W. called back to inform that everything looks okay and that these alarms may have been triggered due to high winds #CONSULT #CMU5 | All Wastewater System ROC General | 2026-02-06
ROC | February | AUSS - Bill VB working on bar screens/ conveyors. | All Wastewater System ROC General | 2026-02-09
ROC | February | YDSS + YNSS Normal Carter D Signing Out | All Wastewater System ROC General | 2026-02-09
ROC | February | KSSP - Recirculation pump no flow alarm. Checked site, recirculation p[ujmp showing in local off. Chase J is signed into site in the log book. While monitoring noticed the pump start in local indicating that Chase J is aware and making changes. | All Wastewater System ROC General | 2026-02-08
ROC | February | NMSSHS - Meter chamber 2 flood alarm. Checked site, operations are normal. Shift report directs to disregard. | All Wastewater System ROC General | 2026-02-08
ROC | February | RHAMF- Contractor Ji Xiao onsite requested to clear alarms. Fans started back up. He will remain onsite for 20 minutes. | All Wastewater System ROC General | 2026-02-05
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-09
ROC | February | KSSSQW - Pump 3 Vibration OOR alarm came in. Disregarded as per shift report | All Wastewater System ROC General | 2026-02-09
ROC | February | PVSS- Ultrasonic mode alarm. Pumps 2, 3 in manual and pump 1 interlocked. Notified Young J. Requested to place pumps into auto and clear alarm. | All Wastewater System ROC General | 2026-02-06
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-07
ROC | February | Gluzen Ramos Ong signing in | All Wastewater System ROC General | 2026-02-09
ROC | February | NBSP - David D. working on generator, oil changes. Station to stay in utility power. | All Wastewater System ROC General | 2026-02-09
ROC | February | BLSS - Dan H leaving site. | All Wastewater System ROC General | 2026-02-10
ROC | February | SUSP - UV system low dosage, critical failure, lolo transmittance and major fault alarm. Checked site, noted UV system dosage reading was very high and UV intensity was very high. Contacted Chase J. While speaking with Chase noted that the UV weir gate was not open for the active channel, but was open for the inactive channel. Chase J directed to swap the UV bank duty to channel 1. Made necessary changes. Chase J will check SCADA to determine if a site visit or further changes are needed. #consult | All Wastewater System ROC General | 2026-02-04
ROC | February | Adam Button signing in -8C clear | All Wastewater System ROC General | 2026-02-04
ROC | February | SHSP - WAS Pump 2 Uncommanded Stop alarm came in. Pump was not running. Alarm was able to be cleared | All Wastewater System ROC General | 2026-02-06
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-09
ROC | February | KCSS - Satnam M on site for pumps maintenance. | All Wastewater System ROC General | 2026-02-05
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-07
ROC | February | Angelica Chepiga signing out | All Wastewater System ROC General | 2026-02-09
ROC | February | KBSP - Odor system recirculation pump low H2O flow alarm. Called Marcus R who will check SCADA. 19:52 - KBSP - Marcus R attending site to determine if the piping system or pump couplings have failed. Created CMU5#W11650161 #consult #CMU5 | All Wastewater System ROC General | 2026-02-09
ROC | February | KCSS - Lauren S testing Drywell flood alarm. | All Wastewater System ROC General | 2026-02-05
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-06
ROC | February | Carter D Signing in | All Wastewater System ROC General | 2026-02-06
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-09
ROC | February | MTSP - Final Effluent Flow LoLo alarm came in. Disregarded as per shift report | All Wastewater System ROC General | 2026-02-06
ROC | February | KSSP - Membrane Control Room RTU - 3 Temp Switch Low alarm came in. Checked site. Will monitor | All Wastewater System ROC General | 2026-02-08
ROC | February | YDSS + YNSS Normal Christian Van Beek signing out. | All Wastewater System ROC General | 2026-02-08
ROC | February | NBSP - Vortex #2 Air lift uncommanded close alarm came in. Ack/reset as per shift report | All Wastewater System ROC General | 2026-02-09
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-07
ROC | February | KSSP - Alum Chem Rm MUA - 11 Differential pressure Switch hi alarm came in. Checked site. Fan is running. Will send an email to North WW | All Wastewater System ROC General | 2026-02-09
ROC | February | KSSP - Membrane air blower 1 failed to start. Checked site, blower 2 has rotated into duty 1 and is operating as expected. Alarm cleared on reset. | All Wastewater System ROC General | 2026-02-04
ROC | February | Gluzen Ramos Ong signing in | All Wastewater System ROC General | 2026-02-04
ROC | February | BLSS - Young J and Lauren S testing High wet well level, dry well flood and temp alarms. | All Wastewater System ROC General | 2026-02-09
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-09
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-09
ROC | February | Gluzen Ramos Ong signing out | All Wastewater System ROC General | 2026-02-04
ROC | February | Christian Van Beek signing out. | All Wastewater System ROC General | 2026-02-04
ROC | February | SUSP - UC common critical alarm, high level alarm and critical failure alarm. Checked site, UV channel flow recently started. Shift report states this scenario is a disregard. Alarm status changed to normal while checking site and the alarms cleared on acknowledgement. | All Wastewater System ROC General | 2026-02-07
ROC | February | Adeela Khan signing in. Weather: -4C and snowing | All Wastewater System ROC General | 2026-02-06
ROC | February | NMSSBP - Daniel K off site. Barscreen 2 is OOS. All flow going through barscreen 1. | All Wastewater System ROC General | 2026-02-07
ROC | February | YDSS + YNSS Normal Christian Van Beek signing out. | All Wastewater System ROC General | 2026-02-07
ROC | February | Carter Dunn Signing Out | All Wastewater System ROC General | 2026-02-04
ROC | February | SUSP - UV channel 1 Bank 2 A low UV intensity fault. Checked site, one UV bank is running. Shift report directs to disregard all UV minor alarms. This alarm is classified as a minor alarm, as the major alarm status is normal. | All Wastewater System ROC General | 2026-02-04
ROC | February | EGSSSC - Tyson C completed generator run test. Leaving site. BLSS - Eric S finished on site. PVSS - Lauren S running generator, testing temperature and drywell flood alarms. | All Wastewater System ROC General | 2026-02-03
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-08
ROC | February | SHSP - Lance J running generator. | All Wastewater System ROC General | 2026-02-03
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-03
ROC | February | EGSSSC- Tyson C onsite for work orders. Running generator, health and safety, drywell flood, sump pump and auto dialer test. | All Wastewater System ROC General | 2026-02-03
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-07
ROC | February | SEOC4 - Phil R. running generator YDOC - informed Phil R. outstanding BFILT 2 outlet temp lo from earlier gen run, okay to disregard | All Wastewater System ROC General | 2026-02-04
ROC | February | SEOC- Phil R onsite running diesel generator. | All Wastewater System ROC General | 2026-02-05
ROC | February | KSSP - Chris C running generator test, contractors on site for semi-annual gen inspection. Chris C will call when site back to normal power. | All Wastewater System ROC General | 2026-02-03
ROC | February | KSCSSKR- Lauren onsite running generator, testing diesel containment flood and hi/low temp MTSS- Terry R onsite running diesel generator. | All Wastewater System ROC General | 2026-02-05
ROC | February | RHAMF1 - Power blip, Generator started and stopped, FAN 1 and Fan 2 VFD fault alarms, Recirculation pumps 1/2 not running. Notified Daniel K. He requested to call NAC. Called Jimmy (NAC), he will attend site. | All Wastewater System ROC General | 2026-02-05
ROC | February | HMSS - Young J on site to complete a high wetwell level alarm test and a metro overflow alarm test. | All Wastewater System ROC General | 2026-02-04
ROC | February | NBSP, UV System Minor Fault, As per shift report, directed to disregard since bank 1b is running | All Wastewater System ROC General | 2026-02-04
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-04
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-10
ROC | February | NBSP- Gavin W working on Grit Blowers. Disregard related alarms | All Wastewater System ROC General | 2026-02-03
ROC | February | Angelica Chepiga signing in,weather -5C | All Wastewater System ROC General | 2026-02-03
ROC | February | YDSS+YNSS normal | All Wastewater System ROC General | 2026-02-04
ROC | February | NMSSBP- Barry M onsite testing hi/low temp, aurodialer, and drywell flood | All Wastewater System ROC General | 2026-02-05
ROC | February | JDSS - Darren B on site to complete a generator test run. | All Wastewater System ROC General | 2026-02-04
ROC | February | NBSP - UV System Minor Fault alarm came in. Checked site. Disregarded as per shift report. 1 Bank is running | All Wastewater System ROC General | 2026-02-06
ROC | February | Connor Smith signing in | All Wastewater System ROC General | 2026-02-03
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-08
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-08
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-03
ROC | February | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-02-03
ROC | February | GRSSWA- Darren B onsite running generator and performing health and safety work orders. | All Wastewater System ROC General | 2026-02-03
ROC | February | NMSSBP - Barry M. running generator | All Wastewater System ROC General | 2026-02-04
ROC | February | EGSSSC - Diesel failure alarm came in on the dialer. Checked site. Generator is not running and site is connected to hydro power | All Wastewater System ROC General | 2026-02-06
ROC | February | AUSS - Kevin S testing temperature, Drywell flood alarms and dialer alarms. | All Wastewater System ROC General | 2026-02-03
ROC | February | NBSP- Inlet Channel High Float, Mech Bar Screen Dif. Level HiHi Alarm, Bar Screen max successive starts. Notified Gavin W. Requested to clear alarm | All Wastewater System ROC General | 2026-02-05
ROC | February | SUSP, SUSSWB, JDSS- Evgeny S rebooting OITs. Disregard Heartbeat alarms. KSSSQW- Talha H working on OITs. Disregard Heartbeat Alarm. | All Wastewater System ROC General | 2026-02-03
ROC | February | AUSSSR - cleared line valve faults from generator run at AUSS. Notified Kevin S. SUSSWB - Cam B. running generator | All Wastewater System ROC General | 2026-02-09
ROC | February | Carter D signing in, -9D/Clear | All Wastewater System ROC General | 2026-02-03
ROC | February | RHRSTR, Deactivated D1 | All Wastewater System ROC General | 2026-02-04
ROC | February | LSSS, Marcos T on site, requests PCS to reset OIT, notified Ian W who instructed to call Artour L as Ian is currently driving. Notified Artour L, he will look into the matter | All Wastewater System ROC General | 2026-02-06
ROC | February | Christan Van Beek signing in. Weather: -23C and clear. | All Wastewater System ROC General | 2026-02-08
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-07
ROC | February | BLSS - Screen Differential Level Hi alarm came in. Disregarded as per shift report | All Wastewater System ROC General | 2026-02-06
ROC | February | KBSP - Marcus R working on DO sensors. | All Wastewater System ROC General | 2026-02-04
ROC | February | NBSP - Scum Hopper Level HiHi alarm came in. Checked site. Trends indicate a spike but came back to optimal range. Alarm cleared | All Wastewater System ROC General | 2026-02-08
ROC | February | AUSS - Satnam M. working on generator, will be disconnected for 30min 9:00 - finished power work, cleared related alarms. | All Wastewater System ROC General | 2026-02-09
ROC | February | AUSSSR - Aysix System Heartbeat alarm came in. Checked site. Alarm was able to clear | All Wastewater System ROC General | 2026-02-07
ROC | February | Christian Van Beek signing in. Weather: -9 C and clear. | All Wastewater System ROC General | 2026-02-09
ROC | February | MTSS- Communication Loss to MTSS. Alarm cleared on its own. | All Wastewater System ROC General | 2026-02-06
ROC | February | NBSSJA, Eric S on site, replacing diesel level sensor | All Wastewater System ROC General | 2026-02-06
ROC | February | MTSS - Talha H finished with the OIT reboot and has cleared the historian heartbeat alarm. | All Wastewater System ROC General | 2026-02-04
ROC | February | NMSSBP - Daniel K called to inform that the gate is open on site and requested a call to security. Contacted security who informed that the gate is missing a piece of locking hardware which has been ordered. Security is completing two manual checks of the site daily. 14:37 - NMSSBP - Daniel K requested the assistance of an additional operator to complete work required to get the barscreen active. Contacted Marcus R who will attend site. Created CMU5#W11645886 #consult #CMU5 | All Wastewater System ROC General | 2026-02-07
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-07
ROC | February | NMSSBP - Marcus R leaving site. | All Wastewater System ROC General | 2026-02-07
ROC | February | BLSS - Young J running generator and testing eyewash alarm. | All Wastewater System ROC General | 2026-02-03
ROC | February | Adeela Khan signing in. Weather: -8C and Cloudy | All Wastewater System ROC General | 2026-02-05
ROC | February | Adeela Khan signing in. Weather: -19C and clear | All Wastewater System ROC General | 2026-02-07
ROC | February | RHAMF1 - Unit Recirculation Pump 2 Overload Alarm came in. Checked site. Both fans are still running. Disregarded as per shift report | All Wastewater System ROC General | 2026-02-07
ROC | February | AUSS - Kevin S running generator. | All Wastewater System ROC General | 2026-02-09
ROC | February | Adeela Khan signing out | All Wastewater System ROC General | 2026-02-09
ROC | February | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-02-08
ROC | February | KBSP- Marcus R working on aeration blower 1. | All Wastewater System ROC General | 2026-02-05
WEST | February | On site for station check Reviewed scada and trends, Duty active, reservoir at 67%, Visual inspection in and around station Verification of equipment and instrumentation Verified chlorine analyzers readings. Outstanding alarm: None Chlorine residual Grabs @ 1505 hrs Reservoir pre: FCL = 2.26 mg/l. Analyzer: 2.30 mg/l @ 1530 hrs: Reservoir Post: FCL= 1.59 mg/l. Analyzer: 1.53 mg/l @ 1534 hrs: Treated FCL = 1.53 mg/l Analyzer: 1.57mg/l TCL = 1.71 mg/l Chemicals: Hypo System: Duty1: pump2 Pumps speed: 49% Dosage: 10:50 mL/min Standby: hypo pump1 Chlorine Dosage factor for P1 ~ 145% P2 ~ 145% Well pump discharge pressure: P2 ~ 445 P3 ~ 729 No issues | Ansnorveldt Wells 2, 3 & Reservoir | 2026-02-27
ROC | February | KSSP - Membrane air blower 1 failed to start, collection blower 2 high diff pressure alarm and Alum chem room MUA diff pressure hi alarm. Called Chase J to inform. | All Wastewater System ROC General | 2026-02-04
WEST | February | Onsite to complete station check. Verified online chlorine analyzers via hach field kit. Post reservoir analyzer: 0.98 mg/L Post reservoir grab: 0.78/0.80/0.79 mg/L Treated analyzer: 0.92 mg/L Treated free grab: 0.75/0.75 mg/L Calibrated analyzers based on grab results. | Ansnorveldt Wells 2, 3 & Reservoir | 2026-02-23
WEST | February | On site to collect weekly bact samples from raw and treated sample taps (W11619988). Verified online chlorine analyzers via hach field kit. Post-reservoir free analyzer: 1.03 mg/L Grab: 1.00 mg/L @ 11:55 Treated free analyzer: 0.96 mg/L Treated free grab: 0.93 mg/L Treated total grab: 1.00 mg/L Reservoir inlet free analyzer: 3.58 mg/L Reservoir inlet free grab: 3.10/3.12 mg/L Calibrated reservoir inlet free analyzer based on average of grab results. | Ansnorveldt Wells 2, 3 & Reservoir | 2026-02-25
WEST | February | Restarted the Operator Interface Terminal due to Windows OS updates. The wells were off during the updates and the Remote Operations Center was notified prior to doing the work. | Ansnorveldt Wells 2, 3 & Reservoir | 2026-02-23
WEST | February | - increase dosage factor 130% - 140% | Ansnorveldt Wells 2, 3 & Reservoir | 2026-02-24
WEST | February | On site for station check Reviewed Scada and trends, Duty just deactivated, reservoir at 89%, Visual inspection in and around station Verification of equipment and instrumentation Verified chlorine analyzers readings. Outstanding alarm: None | Ansnorveldt Wells 2, 3 & Reservoir | 2026-02-02
WEST | February | -increased dosage factor in 1 & 2 125% - 130% -activated duty early target an inlet residual of over 3.00mg/l | Ansnorveldt Wells 2, 3 & Reservoir | 2026-02-23
WEST | February | Responding to post reservoir analyzer low alarm; Pre-inj (mg/L) 1635 Analyzer FCl 0.46 Grab FCl 1.11 Treated (mg/L 1644 Analyzer FCl 0.78 Grab FCl 1.12 Drained sample reservoirs, zero calibrated, then span calibrated based on multiple grabs for both Treated and Post-Reservoir chlorine analyzers. Analyzer values spiked once reservoirs were drained. Added Depolox sand to keep probe clean. Drifting analyzer values may have been interference from recent analyzer maintenance / cleaning, or changes in aquifer chemistry. Will continue to monitor. Based on grabs and pre-reservoir analyzer, chlorine dosing appears to have been adequate. Reservoir just finished filling to duty 1, will not run to test analyzers and dosage at this time. Primed hypo P2 line, pump also appears fine. No other issues. | Ansnorveldt Wells 2, 3 & Reservoir | 2026-02-15
WEST | February | In to complete station check. Review trends. Inspect hypo P1 and 2, suction and discharge lines have air pockets (post-reservoir analyzer trending down over last cycle). Replace tube elements and prime pumps / lines. Activate duty to monitor hypo dosing. Enter data into PWQ. Span calibrate: Treated FCl analyzer from 1.33 to 1.59mg/L Post-Reservoir FCl from 0.87 to 1.50mg/L Pre-Reservoir FCl from 2.69 to 3.20mg/L -based on grabs Dose calculation and analyzer trending combined with air pockets in chemical lines indicated lower chemical dosing over previous cycle. Analyzers will need to be monitored and adjusted on next station check, based on grabs and span cal adjustments from today. | Ansnorveldt Wells 2, 3 & Reservoir | 2026-02-13
WEST | February | On site for station check and collection of weekly bacT sample Reviewed scada and trends, Duty active, reservoir at 79%, Visual inspection in and around station Verification of equipment and instrumentation Verified chlorine analyzers readings. Outstanding alarm: None Chlorine residual Grabs @ 1505 hrs Reservoir pre: FCL = 2.94 mg/l. Analyzer: 2.95 mg/l @ 1508 hrs: Reservoir Post: FCL= 1.38 mg/l. Analyzer: 1.51 mg/l Adjusted Post FCL analyzer from 1.54 to 1.38 mg/l based on average of 3 grabs @ 0924 hrs: Treated FCL = 1.2 mg/l Analyzer: 1.54mg/l TCL = 1.53 mg/l Adjusted Adjusted treated FCL analyzer reading from 1.51 to 1.28 mg/l based on average of 3 grabs Chemicals: Hypo System: Duty1: pump2 Pumps speed: 42% Dosage: 9.03 mL/min Standby: hypo pump2 Rotated hypo pumps duty, placed hypo p1 in duty1 Chlorine Dosage factor for P1 ~ 125% P2 ~ 125% Well pump discharge pressure: P2 ~ 446 P3 ~ 731 No issues | Ansnorveldt Wells 2, 3 & Reservoir | 2026-02-17
WEST | February | On site to top up hypo | Ansnorveldt Wells 2, 3 & Reservoir | 2026-02-18
WEST | February | Filled hypo tanks 26/27 L to 37/37 L | Ansnorveldt Wells 2, 3 & Reservoir | 2026-02-13
WEST | February | On site for station check and collection of weekly bacT samples Reviewed scada and trends, Duty active, reservoir at 77%, Visual inspection in and around station Verification of equipment and instrumentation Verified chlorine analyzers readings. Outstanding alarm: None Chlorine residual Grabs @ 0901 hrs Reservoir pre: FCL = 3.14 mg/l. Analyzer: 3.11 mg/l @ 0909 hrs: Reservoir Post: FCL= 1.77 mg/l. Analyzer: 1.78 mg/l @ 0924 hrs: Treated FCL = 1.66 mg/l TCL = 1.79 mg/l Analyzer: 1.26mg/l Adjusted treated FCL analyzer reading from 1.26 to 1.66 mg/l based on average of 3 grabs Chemicals: Hypo System: Duty1: pump2 Pumps speed: 42% Dosage: 9.03 mL/min Standby: hypo pump2 Chlorine Dosage factor for P1 ~ 125% P2 ~ 125% Well pump discharge pressure: P2 ~ 446 P3 ~ 731 No issues | Ansnorveldt Wells 2, 3 & Reservoir | 2026-02-11
WEST | February | On site for station check Reviewed scada and trends, activated duty Duty active, reservoir at 64%, Visual inspection in and around station Verification of equipment and instrumentation Verified chlorine analyzers readings. Outstanding alarm: None Chlorine residual Grabs @ 1240 hrs Reservoir pre: FCL = 2.84 mg/l. Analyzer: 2.86 mg/l @ 1233 hrs: Reservoir Post: FCL= 1.63 mg/l. Analyzer: 1.59 mg/l @ 1225 hrs: Treated FCL = 1.59 mg/l Analyzer: 1.81mg/l TCL = 1.00 mg/l Adjusted treated chlorine analyzer based of repeated 2 grabs from 1 mg/l to 1.59 mg/l Chemicals: Hypo System: Duty1: pump2 Pumps speed: 42% Dosage: 9.02 mL/min Standby: hypo pump1 Chlorine Dosage factor for P1 ~ 125% P2 ~ 125% Well pump discharge pressure: P2 ~ 446 P3 ~ 729 Deactivated duty after station checks | Ansnorveldt Wells 2, 3 & Reservoir | 2026-02-06
WEST | February | On site to complete the following WOs: JHSC Health and Safety Inspection (1M) Generator Test Run Pressure Regulating Valve Maintenance Turbidity Analyzer TU5300 Maintenance and Calibration Sodium Hypochlorite System Maintenance, Wells 2/3 , Valve Exercise Wells 2/3, Pumps 2 and 3 Strainer Air Release valve inpection and cleaning Siemens Depolox 5/Micro 2000 Chlorine Analyzer started diesel generator at 1050 hrs and stopped at 1216 hrs Generator hours at start 311.12 Generator hours at stop 312.18 Notified ROC before and after completion of WOs Activated duty, verified analyzers reading NO issues | Ansnorveldt Wells 2, 3 & Reservoir | 2026-02-03
WEST | February | On site for station check Reviewed scada and trends, activated duty Duty active, reservoir at 73%, Visual inspection in and around station Verification of equipment and instrumentation Verified chlorine analyzers readings. Outstanding alarm: None Chlorine residual Grabs @ 1230 hrs Reservoir pre: FCL = 3.24 mg/l. Analyzer: 3.20 mg/l @ 1234 hrs: Reservoir Post: FCL= 1.77 mg/l. Analyzer: 1.76 mg/l @ 1244 hrs: Treated FCL = 1.67 mg/l Analyzer: 1.87mg/l TCL = 1.64 mg/l Chemicals: Hypo System: Duty1: pump1 Pumps speed: 43% Dosage: 9.20 mL/min Standby: hypo pump2 Rotated hypo pumps duty, placed hypo p1 in duty1 Chlorine Dosage factor for P1 ~ 125% P2 ~ 125% Well pump discharge pressure: P2 ~ 454 P3 ~ 731 Deactivated duty after station checks | Ansnorveldt Wells 2, 3 & Reservoir | 2026-02-09
WEST | February | <span style="color: rgba(0, 0, 0, 0.87); font-family: Muli, sans-serif; font-size: 14.4px; letter-spacing: 0.2864px; background-color: rgb(255, 255, 255);">Did some troubleshoot with post reservoir treated analyzer and turbidity meter. Noticed chlorine analyzer dropping after several adjustments. Cleaned analyzer sample bowl, flushed sample line and zeroed analyzer. Chlorine analyzer share sample line with turbidity analyzer, cleaned turb analyzer and calibrated.</span><br style="outline: none; box-sizing: border-box; cursor: pointer; overflow-wrap: inherit; word-break: inherit; color: rgba(0, 0, 0, 0.87); font-family: Muli, sans-serif; font-size: 14.4px; letter-spacing: 0.2864px; background-color: rgb(255, 255, 255);"><span style="color: rgba(0, 0, 0, 0.87); font-family: Muli, sans-serif; font-size: 14.4px; letter-spacing: 0.2864px; background-color: rgb(255, 255, 255);">Returned both analyzers to service after cleaning and activated duty for raw and treated water bacT sample collection</span> | Ansnorveldt Wells 2, 3 & Reservoir | 2026-02-04
CENTRAL | February | Onsite for station check/collect sample- WO# W11620710: Sample results (08:12): Free- 0.05, Total- 2.84 * Adjusted free analyzer from 0.15 to 0.05 based on multiple grabs (0.05, 0.05, 0.06) * Adjusted total analyzer from 2.61 to 2.84 based on multiple grabs (2.84, 2.84, 2.84) * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Aurora (East) First Commerce Elevated Tank | 2026-02-25
CENTRAL | February | On-site for a station and equipment check No issues found Took weekly bacti sample Verified analyzer and entered all readings and grabs into PWQ sheet Outlet Free@0943 G:0.05 A:0.06mg/L Outlet Total@0944 G:2.80 A:2.86mg/L Mono-2.45 FA-0.06 TA-0.55 | Aurora (East) First Commerce Elevated Tank | 2026-02-12
CENTRAL | February | Onsite to complete assigned work orders- informed ROC: H/S inspection Low temp tests Ventilation inspection Inlet/outlet heat trace inspection Dehumidifier cleaning/inspection Depolox analyzer maintenance Air valve flush/inspection Portable generator test/inspection Performed station housekeeping Station/equipment- Ok | Aurora (East) First Commerce Elevated Tank | 2026-02-19
CENTRAL | February | Onsite for station check/collect sample- WO# W11606256: Sample results (10:18): Free- 0.00, Total- 2.60 * Adjusted total analyzer from 2.77 to 2.60 based on multiple grabs (2.58, 2.60, 2.60) * Topped up acetate depolox reagent * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Aurora (East) First Commerce Elevated Tank | 2026-02-17
CENTRAL | February | Onsite for station check/collect samples- WO# W11569241, W11569211: Sample results (14:38): Free- 0.07, Total- 2.80 * Replaced KI depolox reagent * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Aurora (East) First Commerce Elevated Tank | 2026-02-04
CENTRAL | February | On site for station check. Pumps 4 and 5 in standby. Entered data into process sheets. No issues found. | Aurora (East) Wellington Pumping Station | 2026-02-27
CENTRAL | February | -Performed station check - logged station readings into PWQ sheet | Aurora (East) Wellington Pumping Station | 2026-02-24
CENTRAL | February | -Finished the following work orders *Valve exercises *Pump and motor inspection *Ventilation inspection *Performed sump pit inspection *Tested low temp alarm *Tested flood alarm *Diesel generator test run Start fuel- 1803 L Stop fuel- 1763 L Start hours- 372.1 Stop hours- 373.3 Pre test inspection completed- no abnormalities* Generator tested under load (P4): 1799 rpm 600 V 60 Hz 97 A Oil pressure- 40psi Oil temp - 65C Coolant temp- 170 F No abnormalities during generator test run- placed generator back into auto once test completed- station back on hydro power *Performed H&S inspection | Aurora (East) Wellington Pumping Station | 2026-02-26
CENTRAL | February | On-site for a station and equipment check No issues found All readings entered into PWQ sheet | Aurora (East) Wellington Pumping Station | 2026-02-02
CENTRAL | February | Look at check valve 4 Can?t hear any water passing with pump 5 running Need operations to isolate valve to open top cover plate for visual inspection | Aurora (East) Wellington Pumping Station | 2026-02-02
CENTRAL | February | Onsite to put pump 4 back in service after check valve replacement. Tested the pump-ok Performed air valve maintenance on discharge header valve that was passing water-ok Leaving site with pump 4 running in auto | Aurora (East) Wellington Pumping Station | 2026-02-25
CENTRAL | February | Onsite for station check Recordings in PD sheet Pump 4 OOS until wired by electrician. Station ok | Aurora (East) Wellington Pumping Station | 2026-02-20
CENTRAL | February | Vibration reading | Aurora (East) Wellington Pumping Station | 2026-02-19
CENTRAL | February | Chris Iliohan Tyler Smith in to remove check valve on pump 4 work in progress | Aurora (East) Wellington Pumping Station | 2026-02-19
CENTRAL | February | Chris Iliohan Tyler Smith complete install of new check valve on pump 4. Electrician to wire up pressure sensor. | Aurora (East) Wellington Pumping Station | 2026-02-20
CENTRAL | February | Onsite for station check: Station/equipment- Ok | Aurora (East) Wellington Pumping Station | 2026-02-06
CENTRAL | February | On site for station check. 09:24 Pump 5 running at 165 l/s. Pump 4 remains LOTO and isolated due to passing CV. Entered data into process sheets. No issues found. | Aurora (East) Wellington Pumping Station | 2026-02-18
CENTRAL | February | On site for station check. 11:27 Pump 5 standby. Pump 4 remains LOTO and isolated due to passing CV. Entered data into process sheets. No issues found. | Aurora (East) Wellington Pumping Station | 2026-02-13
CENTRAL | February | Station Check (no issues found) Input data to PWQ | Aurora (East) Wellington Pumping Station | 2026-02-09
CENTRAL | February | Measure slanted disc Motor running backwards check passing Closed discharge valve put operation lock on ordering new swing flex check for replacement | Aurora (East) Wellington Pumping Station | 2026-02-03
CENTRAL | February | Onsite for station check/collect sample- WO# W11620710: Sample results (12:36): Free- 0.09, Total- 2.88 * Adjusted total analyzer from 2.67 to 2.88 based on multiple grabs (2.84, 2.88, 2.88) * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Aurora (North) Orchard Heights Elevated Tank | 2026-02-25
CENTRAL | February | On site for station check and sampling. MBDW - W11589385. 13:53 hrs. Tower level at 45% and draining. 13:55 hrs. Verified analyzer (mg/l) and collected sample. Free chlorine grab: 0.09. Analyzers: 0.07. Total chlorine grab: 2.92. Analyzer 2.95. Filled out data into process sheets. Topped up analyzer KI and acetate reagent. No issues found on site. | Aurora (North) Orchard Heights Elevated Tank | 2026-02-11
CENTRAL | February | Onsite for station check/collect sample- WO# W11606256: Sample results (14:20): Free- 0.00, Total- 2.70 * Adjusted total analyzer from 3.22 to 2.70 based on multiple grabs (2.66, 2.70, 2.68, 2.70) * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Aurora (North) Orchard Heights Elevated Tank | 2026-02-17
CENTRAL | February | -Finished the following work orders *Depolox analyzer maintenance *H&S inspection *Valve exercises | Aurora (North) Orchard Heights Elevated Tank | 2026-02-19
CENTRAL | February | Onsite for station check/collect samples- WO# W11569241, W11569211: Sample results (11:52): Free- 0.04, Total- 2.84 * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Aurora (North) Orchard Heights Elevated Tank | 2026-02-04
CENTRAL | February | Station and equipment check Took grabs @ 9:45 am (reform/boost) from post sample tap Total: 3.22 mg/l Free0.05 mg/l All other readings on PD sheets Batched ammonia tank 1 Chemicals/reagents on Ops normal | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2026-02-23
CENTRAL | February | On site for station check and sampling. W11619908 11:13 outlet flow at 400 L/s. Rechloramination boosting on. Reservoir level at 74%. Topped up chemscan sulphuric acid reagent. Verified residuals (mg/l): 11:25 Pre-injection/outlet grabs. Collected sample. Free grab: 0.03 Depolox 5: 0.06. Total grab: 1.62 Micro2000: 1.61 Chemscan: 1.59 Monochloramine grab: 1.52 Chemscan: 1.59. Free ammonia grab: 0.07. Chemscan: 0.06. Total ammonia grab: 0.38. Chemscan: 0.35. Nitrite: 0.003. pH: 8.00. Temperatrue: 7 Celsius. 11:32 Post-injection chlorine grabs: Free grab: 0.07. Depolox 5: 0.05. Total grab: 3.20. Micro2000: 3.22 Chemscan: 1.32 Monochloramine grab: 2.85 Chemscan: 2.77. Free ammonia grab: 0.04. Chemscan: 0.08. Total ammonia grab: 0.61. Chemscan: 0.59. No other issues found. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2026-02-25
CENTRAL | February | Under the direction of Ben Hess, Worked along side Network Analyst Aaron Magsakay, to replaced a Network switch to Cisco IE3300 inside a Control panel and Remote IO panel. Informed ROC prior to begin this work Provided 24 VDC power to new switch from 24VDC power supply. When powered up Remote IO panel network switch, RACK 0 SLOT 7 Digital Input Card fuse was blown. Replaced the Fuse. all ok There is a trend gap on SCADA between 09:27 AM to 10:04 AM due to this work. Some of the trends will be Back filled from PAC Back up files After the replacement, checked all the ports and reset the comm alarms. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2026-02-26
CENTRAL | February | On site for station check. 13:55 outlet flow at 366 L/s. Rechloramination boosting on. Reservoir level at 46%. Topped up ammonia tank 2. Replaced chlorine cylinder bank A with Joseph D?eMarco. Verified residuals (mg/l): 14:08 Pre-injection/outlet grabs. Free grab: 0.02 Depolox 5: 0.05. Total grab: 1.63 Micro2000: 1.66 Chemscan: 1.61. Monochloramine grab: 1.56 Chemscan: 1.61. Free ammonia grab: 0.08. Chemscan: 0.06. Total ammonia grab: 0.39. Chemscan: 0.37. 14:29 Post-injection chlorine grabs. Rechloramination has stopped dosing. Free grab: 0.02. Depolox 5: 0.01. Total grab: 1.70. Micro2000: 1.77 Monochloramine grab: 1.53 Chemscan: 1.58 Free ammonia grab: 0.04. Chemscan: 0.12. Total ammonia grab: 0.41. Chemscan: 0.51. No issues found on site. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2026-02-27
CENTRAL | February | Onsite for station check: Changed CL2 cylinders: 0/26 kg to 68/26 kg * Verified analyzers Calculated dosages Chemical levels- Ok Depolox reagents- Ok Chemscan reagents- Ok Station/equipment- Ok | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2026-02-02
CENTRAL | February | 10:06 ROC notified while I was not at site that that SCADA tech Yash Patel was performing network upgrades to AURSBS and that sample pumps 1 and 2 had stopped running. These sample pumps supply water to chlorine analyzers and when they dont run the analyzer readings spike high, triggering hihi alarms (5.00 mg/l). ROC notified me they had turned on both sample pumps back on and that dosing systems currently interlocked. I directed ROC to place chlorine and ammonia dosing systems in manual off. 10:37 notified Ben Hess and Justin Quail of chlorine dosing occuring while a loss of trends and accurate analyzer readings occured. 11:14 Arrived on site. Reviewed trends. Station chlorine dosing system and chlorine sample trends are missing from at 09:27 until 10:04. Station was dosing and outlet flow at 480 l/s before the data loss. Yash informed me missing data should be recorded in PAC and processed/ back dated by tomorrow morning at 08:30. Station trends currently show chlorinator 2 open and closing at 10:04, and fully closed by 10:05:15, with 1 minute and 15 seconds of dosing occuring while analyzers reading 5.00 mg/l, and a furhter 38 minutes without any trending data. 11:26 verified chlorine analyzers (mg/l): Post injection free: 0.02. Depolox 5: 0.01. Post injection total: 1.66 micro2000: 1.68. Chemscan: 1.66. 11:52 placed chemical dosing system back online. Notified ROC system is back online. No issues remain. Will discuss with Team lead and supervisor is adverse filling required. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2026-02-26
CENTRAL | February | Onsite to complete work orders. 09:36 Notified ROC of working on site. Station outlet flow a 440 l/s and currently dosing. Dehumidifier cleaning and inspection. Dechlorination puck dispenser cleaning. Sump pit inspection. JHSC inspection. Chlorine Chemical dosing system inspection. Ammonia pump 1 inpsection. Replaced tubing element. Max pumprate 1500 ml/ min. Ammonia dosing system inspection. Changed chlorine cylinder bank B with Alex Bell. 11:39 chemscan analyzer maintenance. Analyzer offline alarm triggered. Chemical systems are no longer dosing as duty is off. Ammonia pumps in manual off. Tested zero with no issues. Flushed/cleaned strainers. Topped up Potassium Iodine reagent. No issues found. Siemens Depolox 5/micro 2000 chlorine anlayzer maintenance. Verified analyzers (mg/l) 11:55. Pre injection free: 0.04. depolox: 0.06. Pre injection total: 1.64. Micro2000: 1.58. Chemscan: 1.62. 12:00 Post injection free: 0.07/0.08/0.07. Analyzer: 0.01. Adjusted analyzer to match grabs: Post injection total: 1.65. micro2000: 1.70. Chemscan: 1.63. 12:18 Chlorine leak detection test. Removed shut off valves from cylinders and tested leak sensor. Chlorine emerg system fault alarm triggered and chlorine gas alarm triggered. No issues found with system. Acknowledged and cleared alarm. No new issues found on site. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2026-02-19
CENTRAL | February | Onsite to respond to post injection free chlorine hihi of 0.30 mg/l. Dosing system interlocked at 13:45. 14:15 grab 0.05. Analyzer: 0.05. Cleared interlock and dosing resumed. Analyzer began climbing. 14:25 Grab 0.05/0.05/0.05. Analyzer 0.28. Adjusted to match grabs. Analyzer stabilized and no issues remain. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2026-02-19
CENTRAL | February | On site for station check and sampling. Card readers not operating. Notified Security and Christine floyd. Technition on the way. Accessed site using eKey. 11:59 outlet flow at 40 L/s. Rechloramination boosting on. Reservoir level at 74%. Topped up ammonia tank 1. 12:09 Central duty stopped and rechloramination dosing stopped. Verified residuals (mg/l): 12:23 Pre-injection/outlet grabs. Collected sample. W11605405 Free grab: 0.08 Depolox 5: 0.06. Total grab: 1.69 Micro2000: 1.72 Chemscan: 1.65 Monochloramine grab: 1.57. Chemscan: 1.64. Free ammonia grab: 0.07. Chemscan: 0.05. Total ammonia grab: 0.38. Chemscan: 0.35. Nitrite: 0.003. pH: 8.05. Temperatrue: 7 Celsius. 12:36 Post-injection chlorine grabs: Free grab: 0.05. Depolox 5: 0.01. Total grab: 1.70. Micro2000: 1.66 Chemscan: 1.70 Monochloramine grab: 1.56 Chemscan: 1.60. Free ammonia grab: 0.08. Chemscan: 0.09. Total ammonia grab: 0.39. Chemscan: 0.36. No other issues found. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2026-02-17
CENTRAL | February | Onsite for station check Recordings in PD sheet Filled ammonia tank 2 JHSC inspection -ok Air valve flush Hoist and crane inspection -ok Station ok | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2026-02-20
CENTRAL | February | Station Check (no issues found) Input data to PWQ Verified Depoloxs (mg/L) 8:43 Pre: Free: Grab 0.04, A 0.06 Total: Grab 1.60, A 1.54 8:55 Post: Free: Grab 0.07, A 0.06 Total: Grab 3.12, A 3.09 9:20 #11588572 bact. & operational samples Ammonia Tank 2 (new batch) | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2026-02-11
CENTRAL | February | On site for station check. 08:50 outlet flow at 0 L/s. Rechloramination boosting not on. Reservoir level at 56%. Topped up ammonia tank 2. Verified residuals (mg/l): 09:26 Pre-injection/outlet grabs: Free grab: 0.09 Depolox 5: 0.06. Total grab: 1.55 Micro2000: 1.53. Chemscan: 1.60 09:49 Monochloramine grab: 1.38. Chemscan: 1.44. Free ammonia grab: 0.09. Chemscan: 0.09. Total ammonia grab: 0.36. Chemscan: 0.27. Adjusted offset to match grab. 09:41 Post-injection chlorine grabs: Free grab: 0.06. Depolox 5: 0.01. Total grab: 1.53. Micro2000: 1.52 Chemscan: 1.55 Monochloramine grab: 1.44. Chemscan: 1.52 Free ammonia grab: 0.08. Chemscan: 0.12. Total ammonia grab: 0.37. Chemscan: 0.36. 10:01 activated Aurora Central duty. Found left chlorine cylinder bank not pulling any more chlorine. Scale reading 10.3 kg but appear empty. Manually adjusted scale to read 0 kg. 10:30 Joe D. onsite and assisted in replacing left chlorine cylinder bank. No other issues found. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2026-02-13
CENTRAL | February | Station and equipment check Change chlorine cylinders with Joe D (right bank) Took grabs from pre injection sample tap @ 8:25 am Total: 1.70 mg/l Free: 0.05 mg/l Analyzers matched Took grabs from post injection sample tap @ 8:35 am Total: 3.21 mg/l Free: 0.05 mg/l Analyzers matched All other readings on PD sheets shared online file Changed yellow reagent on chemscan unit @ 9:40 am Chemicals/reagents ok Ops normal | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2026-02-06
CENTRAL | February | Station and equipment check Take weekly BacT sample and grabs @ 13:15 (post) Total: 1.91 mg/l Free: 0.02 mg/l No adjustments required Topped up Ammonia tank 1 Chemicals/reagents ok Chemical system not active at time of readings Ops normal | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2026-02-04
CENTRAL | February | Station Check (no issues found) Input data to PWQ Verified Depolox (mg/L) 12:25 PRE: Free: Grab 0.06, A 0.06 Total: Grab 1.72, A 1.73 12:36 POST: Free: Grab 0.04, A 0.01 Total: Grab 1.70, A 1.67 Chemscan: (Green, Muratic/distilled top up) Ammonia Tank #2 (new batch) | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2026-02-09
CENTRAL | February | On site for station check and sampling. W11619908. 12:25 Tower level at 56% and draining at 4 l/s. 12:30 Verified chlorine analyzer (mg/l) and collected sample. Free chlorine grab: 0.05. Analyzer: 0.02. Total chlorine grab: 2.22 analyzer: 2.22. Nitrite grab: 0.000. Free ammonia: 0.08 Total ammonia: 0.46. Monochloramine: 1.93. Temperature: 3.6 celsius. pH: 8.01. No issues on site. | Aurora (Southwest) Allenvale Elevated Tank | 2026-02-25
CENTRAL | February | On site for station check and sampling. MBDW - W11605405. 13:05 Deactivated zone 3 duty. 13:08 Tower level at 64% and draining. 13:33 hrs. Verified analyzer (mg/l) and collected sample. Free chlorine grab: 0.09. Analyzers: 0.07. Total chlorine grab: 2.11. Analyzer 2.09. Monochloramine: 1.90. Free ammonia: 0.08. Total ammonia: 0.46. Nitrite: 0.004. pH: 8.01. Temperature: 5.4 Celsius. Filled out data into process sheets. No issues found on site. | Aurora (Southwest) Allenvale Elevated Tank | 2026-02-17
CENTRAL | February | Onsite to complete work orders: Heat trace inspection. 10:27 Low building temperature alarm. triggered alarm no issues. Reservoir sample line flow is low. Dissasembled and found turberculation build up before valve. flushed out and reassembled line. Site cleaning. Portable gas generator inspection and test run. JHSC inspection 11:30 Chlorine analyzer maintenance. Verified chlorine analyzer (mg/l): free grab: 0.05. Analyzer: 0.08. Total grab: 2.11. Analyzer: 2.12. No issues remaining. | Aurora (Southwest) Allenvale Elevated Tank | 2026-02-18
CENTRAL | February | Deleted accidental double entry. See prior post. | Aurora (Southwest) Allenvale Elevated Tank | 2026-02-17
CENTRAL | February | Station Check (no issues found) Input data to PWQ 11:25 Verified CL17s (mg/l) Free: Grab 0.05, A 0.00 (performed zero calibration then cal. standard to 0.05) Total: Grab 2.10, A 2,17 12:45 #11588572 bact. & operational samples | Aurora (Southwest) Allenvale Elevated Tank | 2026-02-11
CENTRAL | February | Onsite for station check/collect samples- WO# W11568172, W11568601: Sample results (12:38): Free- 0.02, Total- 2.15 * Adjusted total analyzer from 1.99 to 2.15 based on multiple grabs (2.15, 2.15, 2.15) * Replaced KI depolox reagent * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Aurora (Southwest) Allenvale Elevated Tank | 2026-02-04
CENTRAL | February | Onsite for station check/collect sample- WO# W11620710: Sample results (13:15): Free- 0.01, Total- 2.92 * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Aurora Orchard Heights Pumping Station & Reservoir | 2026-02-25
CENTRAL | February | Onsite for station check: Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Aurora Orchard Heights Pumping Station & Reservoir | 2026-02-27
CENTRAL | February | Onsite for station check: Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Aurora Orchard Heights Pumping Station & Reservoir | 2026-02-24
CENTRAL | February | Onsite for Bathurst tank isolation trial Isolated zone valve (Aurora west PD and Newmarket West PD) in the yard, opened HV11 in PS. Ran pumps in different configurations. Performed station check Station ok Reversed changes all back to normal operations | Aurora Orchard Heights Pumping Station & Reservoir | 2026-02-02
CENTRAL | February | Onsite for station check: Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Aurora Orchard Heights Pumping Station & Reservoir | 2026-02-13
CENTRAL | February | -Finished the following work orders *Chlorine analyzer maintenance *Vent inspection *Tested hi/lo temp alarm *Pump and motor inspection *Dehumidifier cleaning *Performed diesel generator test run Start fuel- 2505 L Stop fuel- 2485 L Start hours- 204.5 Stop hours- 205.8 Pre test inspection completed- no abnormalities* Generator tested under load (P3 and P4): 1799 rpm 600 V 60 Hz 94 A Oil pressure- 428 kpa Coolant temp- 87 C No abnormalities during generator test run- placed generator back into auto once test completed- station back on hydro power *Performed H&S inspection *Performed PRV inspection | Aurora Orchard Heights Pumping Station & Reservoir | 2026-02-19
CENTRAL | February | On-site for reservoir station check and sampling. W11589385 Reservoir at 63% filling and draining. NM West pumps running in duty. Entered data into pumping station process sheets. 13:23 verified analyzer (mg/l): Free grab: 0.03. Analyzer: 0.04. Total grab: 2.94. Analyzer: 2.95. Collected sample. No other issues found. Left site. | Aurora Orchard Heights Pumping Station & Reservoir | 2026-02-11
CENTRAL | February | Onsite for station check/collect sample- WO# W11606256: Sample results (13:35): Free- 0.01, Total- 2.90 * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Aurora Orchard Heights Pumping Station & Reservoir | 2026-02-17
CENTRAL | February | Onsite for station check/complete WO: Verified analyzers Depolox reagents- Ok Performed station housekeeping Station/equipment- Ok | Aurora Orchard Heights Pumping Station & Reservoir | 2026-02-20
CENTRAL | February | Motor service 1 - 4 Changed oil on all four motors | Aurora Orchard Heights Pumping Station & Reservoir | 2026-02-05
CENTRAL | February | Onsite for station check: Adjusted total analyzer from 2.83 to 3.00 based on multiple grabs (2.98, 3.00, 3.00) * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Aurora Orchard Heights Pumping Station & Reservoir | 2026-02-09
CENTRAL | February | Onsite for station check/collect samples- WO# W11569241, W11569211: Sample results (11:00): Free- 0.03, Total- 3.08 * Adjusted total analyzer from 2.85 to 3.08 based on multiple grabs (3.08, 3.08, 3.08) * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Aurora Orchard Heights Pumping Station & Reservoir | 2026-02-04
CENTRAL | February | Onsite for station check: Adjusted total analyzer from 3.08 to 2.90 based on multiple grabs (2.88, 2.90, 2.90) * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Aurora Orchard Heights Pumping Station & Reservoir | 2026-02-06
CENTRAL | February | Onsite to complete work orders: Diesel generator inspection and test run. 09:25 Generator pre-inspection. Run hours at 239 and 40 minutes. Battery 27.3 Volts. Oil level ok. Battery terminals ok. Coolant level ok. Fuel level 2188 L (44%). Notified ROC of work to be completed. 09:37 initiated Diesel run. 09:42 Activated zone 3 to run pump 2 to increase generator load. AUETAD tower level at 49%. 09:50. Placed all chemical dosing in manual off. 09:53 Chlorine leak detection test. Halogen emergency valve shut off inpsection. Scrubber 1 fail to start. Retested for longer and found no issues. Acknowledged and cleared alarms. 12:12. Placed all dosing systems back online. Found chlorine room supply fan 2 and exhaust fan 1 breakers open. Closed breakers and fans worked with no issues. Dechlorination puck dispenser cleaning and inspection. 10:40 Chlorine chemical system inspection. Uncommanded chlorine system stop alarms triggered while completing a vacuum test on chlorine dosing system. No issues found. 10:42 deactivated zone 3 duty. 10:55 completed generator test. Fuel level at: 2159 L. Run hours: 240 and 53 minutes. No issues remaining. | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2026-02-26
CENTRAL | February | On site for rechlorination station check. 12:50 Reservoir filling at 81 l/s. Zone 3 Pump 1 and 2 in standby. Chemical boosting active. Reservoir level at 68%. Replaced cl17 post injection free and zone 3 total analyzer reagents. Verified analyzer residuals (mg/l): 13:00 Pre-injection grabs: Free chlorine grab: 0.03. Analyzer: 0.04. Total Chlorine grab: 1.94 CL17: 1.91. Chemscan: 1.98. monochloramine grab: 1.66. Chemscan: 1.72. Free ammonia grab: 0.09. Chemscan: 0.05. Adjusted offset to match grab. Total Ammonia: 0.41. Chemscan: 51. Adjusted offset to match grab. 13:16 Post-injection grabs: Free chlorine grab: 0.03 Analyzer: 0.05. Total Chlorine grab: 2.54 CL17: 2.59. Chemscan: 2.64. monochloramine grab: 2.21. Chemscan: 2.23. Free ammonia grab: 0.05. Chemscan: 0.02. Total Ammonia: 0.49. Chemscan: 53. Station and equipment ok. No issues found. Entered readings into process sheets. | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2026-02-27
CENTRAL | February | On site to complete station check. -Verified analyzers: Pre Injection Free Chlorine @ 13:08 Grab: 0.06 mg/L Analyzer: 0.04 mg/L Pre Injection Total Chlorine @ 13:08 Grab: 1.87 mg/L Analyzer: 1.92 mg/L Post Injection Free Chlorine @ 13:14 Grab: 0.03 mg/L Analyzer: 0.05 mg/L Post Injection Total Chlorine @ 13:14 Grab: 2.40 mg/L Analyzer: 2.40 mg/L Zone 3 Free Chlorine @ 13:11 Grab: 0.07 mg/L Analyzer: 0.04 mg/L Zone 3 Total Chlorine @ 13:11 Grab: 2.32 mg/L Analyzer: 2.31 mg/L Reservoir Outlet Free Chlorine @ 13:19 Grab: 0.03 mg/L Analyzer: 0.03 mg/L Reservoir Outlet Chlorine @ 13:19 Grab: 2.26 mg/L Analyzer: 2.31 mg/L -Topped up reservoir outlet free chlorine analyzer reagents -Entered data into PD sheet | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2026-02-23
CENTRAL | February | On site for station check and sampling. W11619908 10:19 Reservoir draining at 17 l/s. Zone 3 Pump 1 and 2 in standby. Chemical boosting not active. Reservoir level at 66%. Verified analyzer residuals (mg/l): 10:25 Pre-injection grabs: Free chlorine grab: 0.07. Analyzer: 0.04. Total Chlorine grab: 2.40 CL17: 2.35. Chemscan: 2.39. 10:35 Post-injection grabs: Free chlorine grab: 0.3 Analyzer: 0.04. Total Chlorine grab: 2.34 CL17: 2.32. Chemscan: 2.45. 10:38 Zone 3 grabs: Free chlorine 0.04. Analyzer: 0.04 Total chlorine: 2.20. Analzyer: 2.25 10:42 Reservoir outlet grabs and collected sample: Free chlorine grab: 0.02. Analyzer: 0.03. Total chlorine grab: 2.22 Analyzer: 2.29. Monchloramine grab: 2.04. Free ammonia: 0.07. Total ammonia: 0.47. pH: 8.02 Temperature: 5.4 Station and equipment ok. No issues found. Entered readings into process sheets. | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2026-02-25
CENTRAL | February | Station and equipment check Verified outlet analyzer only as instrumentation was on site for calibrations, will re verify Wednesday during samples Outlet grabs @ 2:30 pm Total: 2.25 mg/l Free: 0.04 mg/l No adjustments required Chemicals/reagents ok Ops normal | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2026-02-02
CENTRAL | February | Onsite for annual calibrations Informed ROC. They placed duty in manual off Performed maintenance and calibration on Zone 3 Total, Res Outlet free and total, pre injection total AIT, Chlorinators. Zone 3 total A = 2.26 mg/L G = 2.31 mg/L Reservoir Outlet Free A = 0.03 mg/L G = 0.05 mg/L Reservoir Outlet Total. A = 2.24 mg/L G = 2.28 mg/L Pre injection total A = 2.28 mg/L G = 2.30 mg/L Pre injection total chlorine reading briefly went Low/High during mA check. Put everything back in service. All the related alarms were cleared. No issues. Informed ROC, armed building and left site | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2026-02-02
CENTRAL | February | Onsite to complete work orders: 09:07 Notified ROC of work. Placed dosing system in manaul off. Completed maintenance on all CL17 and CL17sc analzyers. Replaced pre-injection free and reservoir outlet total analyzer reagent. 10:00 Cleaned chemscan analyzer strainers. Tested zero. No issues found. Verified chlorine analyzers (mg/l). 10:25 Pre injection free: 0.08 CL17: 0.03 pre injection total: 1.81 Cl17:1.86. Chemscan analyzer: 1.77. 10:35 Post injection free: 0.05 CL17:0.03 post injection total: 1.78 CL17: 1.84. Chemscan analyzer outlet free: 0.02 cl17:0.03 outlet total: 2.22. CL17: 2.27 Zone 3 free: 0.02 CL17: 0.04 zone 3 total: 2.22. CL17: 2.27. JHSC inspection. Ammonia point visual inspection. 11:19 Chemical tank inspection. Tested ammonia flood alarm. 11:21 placed all dosing pumps back in auto. No issues found. | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2026-02-10
CENTRAL | February | On site for station check and sampling. W11605405 14:20 eservoir filling at 68 l/s. Zone 3 Pump 1 and 2 in standby. Chemical boosting active. Reservoir level at 72%. Topped up ammonia tank 2. Verified analyzer residuals (mg/l): 14:32 Pre-injection grabs: Free chlorine grab: 0.08. Analyzer: 0.04. Total Chlorine grab: 1.77 CL17: 1.82. Chemscan: 1.81. 14:36 Post-injection grabs: Free chlorine grab: 0.08 Analyzer: 0.05. Total Chlorine grab: 2.60 CL17: 2.60. Chemscan: 2.71. 14:46 Reservoir outlet grabs and collected sample: Free chlorine grab: 0.03. Analyzer: 0.04. Total chlorine grab: 2.32 Analyzer: 2.33. Monchloramine grab: 2.06 Free ammonia: 0.07. Total ammonia: 0.48. Nitrite: 0.003. pH 8.01. Temperature 5.4 Celsius. 14:46 Zone 3 grabs: Free chlorine 0.03. Analyzer: 0.04 Total chlorine: 2.32. Analzyer: 2.32 Station and equipment ok. No issues found. Entered readings into process sheets. | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2026-02-17
CENTRAL | February | Replaced zone 3 free analyzer reagents. Replaced right chlorine cylinder with Joe Demarco. No issues found. | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2026-02-18
CENTRAL | February | On site to complete station check. -Verified analyzers: Pre Injection Free Chlorine @ 12:23 Grab: 0.07 mg/L Analyzer: 0.04 mg/L Pre Injection Total Chlorine @ 12:23 Grab: 2.32 mg/L Analyzer: 2.36 mg/L Post Injection Free Chlorine @ 12:29 Grab: 0.05 mg/L Analyzer: 0.03 mg/L Post Injection Total Chlorine @ 12:29 Grab: 2.36 mg/L Analyzer: 2.33 mg/L Zone 3 Free Chlorine @ 12:36 Grab: 0.08 mg/L Analyzer: 0.04 mg/L Zone 3 Total Chlorine @ 12:36 Grab: 2.30 mg/L Analyzer: 2.25 mg/L Reservoir Outlet Free Chlorine @ 12:44 Grab: 0.07 mg/L Analyzer: 0.03 mg/L Reservoir Outlet Chlorine @ 12:44 Grab: 2.30 mg/L Analyzer: 2.31 mg/L -Topped up chemscan DI water -Entered data into PD sheet -Checked trends | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2026-02-20
CENTRAL | February | Station Check (no issues found) Input data to PWQ Verified CL17s (mg/L) 11:00 PRE: Free: Grab 0.06, A 0.04 Total: Grab 1.80, A 1.85 11:20 POST: Free: Grab 0.05, A 0.03 Total: Grab 2.20, A 2.29 11:30 Reservoir: Free: Grab 0.04, A 0.03 Total: Grab 2.20, A 2.29 11:45 Zone 3: Free: 0.05, A 0.04 Total: 2.15, 2.29 11:10 #11588572 bact. & operational samples | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2026-02-11
CENTRAL | February | On site for station check: 13:13 Reservoir draining at 13 l/s. Zone 3 Pump 1 and 2 in standby. Chemical boosting not active. Reservoir level at 60%. Verified analyzer residuals (mg/l): 13:29 Pre-injection grabs: Free chlorine grab: 0.06. Analyzer: 0.04. Total Chlorine grab: 2.36 CL17: 2.33. Chemscan: 2.37. Monchloramine grab: 2.00 Chemscan: 2.00 Free ammonia: 0.06. Chemscan: 0.02. Total ammonia: 0.45. Chemscan: 0.50. 13:42 Post-injection grabs: Free chlorine grab: 0.05 Analyzer: 0.03. Total Chlorine grab: 2.30 CL17: 2.33. Chemscan: 2.49. 10:09 Monchloramine grab: 2.05. Chemscan: 2.05 Free ammonia: 0.05. Chemscan: 0.02. Total ammonia: 0.46. chemscan: 0.46. 13:56 Zone 3 grabs: Free chlorine 0.03. Analyzer: 0.02 Total chlorine: 2.28. Analzyer: 2.29 13:56 Reservoir outlet grabs and collected sample: Free chlorine grab: 0.03. Analyzer: 0.02. Total chlorine grab: 2.28 Analyzer: 2.32 Station and equipment ok. No issues found. Entered readings into process sheets. | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2026-02-13
CENTRAL | February | Station Check (no issues found) Input data to PWQ Verified CL17s (mg/L) 9:30 PRE: Free: Grab 0.03, A 0.03 Total: Grab 1.81, 1.85 9:45 POST: Free: Grab 0.04, A 0.05 Total: Grab 2.48, A 2.44 10:05 Reservoir: Free: Grab 0.03, A 0.03 Total: Grab 2.40, 2.31 10:15 Zone 3: Free: Grab 0.06, A 0.03 Total: Grab 2.38, A 2.29 Chemscan (Green and distilled top up) | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2026-02-09
CENTRAL | February | Station and equipment check Took grabs @ 10:50 am Post injection Total: 2.35 mg/l Free: 0.04 mg/l Outlet sample tap Total: 2.30 mg/l Free: 0.04 mg/l Chemical system not active at time of readings No adjustments required Topped up ammonia tank 1 Chemicals/reagents ok Ops normal | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2026-02-06
CENTRAL | February | Onsite for station check/collect samples- WO# W11568172, W11568601: Sample results (13:35): Free- 0.02, Total- 2.18 * Replaced post inj total CL17 reagents * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Chemscan reagents- Ok Station/equipment- Ok | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2026-02-04
CENTRAL | February | Onsite for annual calibrations Informed ROC. They placed duty in manual off Performed maintenance and calibration on pre injection and post injection free AIT, post Total AIT, chlorine room gas detector and Chemscan analyzer. Took a multiple grab samples. No adjustments required. Post injection total AIT A = 1.82 mg/L G = 1.81 mg/L Post injection free AIT A = 0.03 mg/L G = 0.05 mg/L Pre injection feee AIT A = 0.04 mg/L G = 0.05 mg/L Post injection total chlorine reading briefly went Low due to tubing popped out. Took a grab sample and confirmed reading of 1.83 mg/l. Secured the tubing and monitored for a while. No issues. Put everything back in service. All the related alarms were cleared. No issues. Informed ROC, armed building and left site | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2026-02-03
CENTRAL | February | Onsite for station check/complete assigned work orders- informed ROC: CL2 leak test Performed station housekeeping Replaced treated free CL17 reagents * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok Work orders created to install safety guard for well motor shaft * | Aurora Well 5 | 2026-02-27
CENTRAL | February | Onsite to complete assigned work orders, and troubleshoot CL2 ejector #2- informed ROC: Rebuilt ejector #2, replaced diaphragm with new one. Once rebuilt, attempted to draw vacuum by locally running CL2 booster #2. Released any air from chlorine booster #2. Still not dosing via chlorinator #2. Will create work order for chlorinator #2 to be investigated further. CL2 booster #2 and chlorinator #2 in local/off until issue resolved. Performed maintenance on silicate injection #1 due to suspected clogged injection point. Isolated the station and pulled silicate injection point #1. Flushed with hot water and cleaned injection point. Re-opened station isolation valves and primed silicate pump #1. Placed pump #1 back into auto and will monitor on next run cycle. Changed CL2 cylinders: 0/41 kg to 68/41 kg * Ammonia system inspection Silicate system inspection Chlorine system inspection Station/equipment- Ok | Aurora Well 5 | 2026-02-26
CENTRAL | February | Onsite for station check/collect samples- WO# W11620710: Sample results (11:58): Free- 0.07, Total- 2.88 * Quarterly raw ph sample: Well 5 raw ph- 8.04 Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok | Aurora Well 5 | 2026-02-25
CENTRAL | February | Onsite for station check/complete assigned work orders- informed ROC: H/S inspection Deep well exhaust inspection Exhaust fan/damper inspection CL2 analyzer maintenance Turbidimeter maintenance Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok | Aurora Well 5 | 2026-02-24
CENTRAL | February | Onsite for station check: Replaced treated total CL17 reagents * Verified analyzers Chemical levels- Ok Station/equipment- Ok Well 5 remains in local/off * | Aurora Well 5 | 2026-02-02
CENTRAL | February | -Performed station check - logged station readings into PWQ sheet Grab: treated free=0.15mg/L total=2.88mg/L@13:15 influent free=2.62mg/L effluent free=2.48mg/L Analyzer: treated free=0.12mg/L total=2.90mg/L influent free=2.60mg/L effluent free=2.39mg/L -Collected weekly BacT sample YD# W11606256 & in-house water quality samples -Checked CL17 reagents - OK | Aurora Well 5 | 2026-02-17
CENTRAL | February | Onsite to put well 5 back in service- motor repaired and raw water sample passed 08:45- started back flushing using dechlorination pucks 09:55- treated total grab: 2.58, treated total analyzer: 2.57 09:58- influent total grabs: 2.00, 2.02, 1.98 10:00- backflush completed- closed backflush valve. Contact tank turned over 10:08- selected backflush completed via scada 10:10- started well in man/on- will monitor residuals onsite. Confirmed all chemical systems in auto. influent free recovered shortly after start up 10:20: influent free grab- 2.65 10:20: influent free analyzer- 2.74 10:22: influent free grab- 2.80 10:22: influent free analyzer- 2.83 10:28: influent free grab- 2.86 10:29: influent free analyzer- 2.86 10:38: influent free grab- 2.70 10:38: influent free analyzer- 2.78 10:40: effluent free grab- 0.32 10:40: effluent free analyzer- 0.22 10:45: treated free grab- 0.12 10:45: treated total grab- 1.87 10:45: treated free analyzer- 0.04 10:45: treated total analyzer- 1.94 10:50: effluent free grab- 0.73 10:50: effluent free analyzer- 0.66 10:58: effluent free grab- 1.27 10:58: effluent free analyzer- 1.17 11:06: influent free grab- 2.70 11:06: influent free analyzer- 2.73 11:25: treated free grab- 0.08 treated free analyzer- 0.10 11:25: treated total grab- 2.60 treated total analyzer- 2.54 11:25: Mono- 2.17 FA- 0.02 TA- 0.45 11:42: influent free grab- 2.58 11:42: influent free analyzer- 2.65 11:42: effluent free grab- 2.20 11:42: effluent free analyzer- 2.26 Verified all analyzers Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok Well 5 back in service- Auto Duty 1. Informed Central and ROC operators | Aurora Well 5 | 2026-02-10
CENTRAL | February | Onsite for station check: Changed CL2 cylinders: 50/0 kg to 50/68 kg * Replaced influent free CL17 reagents * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok | Aurora Well 5 | 2026-02-20
CENTRAL | February | Onsite for station check: Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok | Aurora Well 5 | 2026-02-13
CENTRAL | February | -Responded influent free LoLo - upon arrival, influent free analyzer reading=0.32mg/L - performed grab test influent free=0.39mg/L - checked treads - chlorinator 2 was running in the last cycle - checked chlorinator 2 - not dosing - put chlorinator 1 in duty 1 and disabled duty rotation - locked out chlorine booster 2 - backflushed contact tank until influent free=0.93mg/L - restarted well 5 in auto - well 5 was running normally for 10 mins | Aurora Well 5 | 2026-02-10
CENTRAL | February | On-site for station check and sampling. W11589385 and W11476274. Chlorinator 2 remains locked out. Silicate pump 1 is OOS after hi turbidity lock out over night. Silicate pump 2 ran this morning with no issues. 12:00 Remotly placed well 5 in manual on. 12:23 running at 45.3 l/s. 12:31 collected raw samples. Verified chlorine analyzers (mg/l). 12:35. Influent free chlorine grab: 2.66 Analyzer: 2.67. 12:38 Effluent free chlorine grab. 2.46. Analyzer: 2.36 12:38. Treated free chlorine grab: 0.07 CL17: 0.12. 12:38. Treated total chlorine grab: 2.82 CL17: 2.88. Collected treated sample. Will investigate silicate pump 1 more tomorrow and leave OOS for now. Entered data into process sheets. No other issues found. | Aurora Well 5 | 2026-02-11
CENTRAL | February | Onsite for CL2 cylinder change: 0/20 kg to 68/20 kg * | Aurora Well 5 | 2026-02-17
CENTRAL | February | Onsite to respond to lolo influent causing station lockout- informed by ROC: Upon arrival, took grab to verify influent free analyzer: Grab (14:44): 1.20 Analyzer (14:44): 1.27 Based on influent scada trending, appears that regulator didn?t drop down quick enough during CL2 cylinder switch over, causing influent residual to drop 14:47- ack/reset all outstanding alarms- well 5 started back up in auto duty 1. Informed ROC, will continue to monitor station via scada Station/equipment- Ok | Aurora Well 5 | 2026-02-13
CENTRAL | February | On-site to collect raw water bacti sample. Ran well 5 to waste. All chemical pumps off. Isolated well from distribution system CT not achieved alarm came in due to flow meters calculation, not applicable After sample collected return system back to normal while keeping well off in local | Aurora Well 5 | 2026-02-03
CENTRAL | February | Onsite for station check: Verified analyzers Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok Well 5 in local/off- waiting for passing raw sample results prior to putting well back in service * | Aurora Well 5 | 2026-02-06
CENTRAL | February | Onsite for station check: Verified analyzers Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok Well 5 remains in local/off * | Aurora Well 5 | 2026-02-09
CENTRAL | February | -Performed station check | Aurora Well 6 | 2026-02-24
CENTRAL | February | On site to complete PMs. Site offline. Completed JHSC inspection. | Aurora Well 6 | 2026-02-20
CENTRAL | February | Onsite for station check: Station offline * Station/equipment- Ok | Aurora Well 6 | 2026-02-18
CENTRAL | February | Onsite for station check: Station offline * Station/equipment- Ok | Aurora Well 6 | 2026-02-03
CENTRAL | February | Onsite for station check: Station offline * Station/equipment- Ok | Aurora Well 6 | 2026-02-09
CENTRAL | February | -Collected in-house water quality sample | Aurora Wells 1-4 Water Treatment Plant | 2026-02-26
CENTRAL | February | -Performed station check at Raw Building | Aurora Wells 1-4 Water Treatment Plant | 2026-02-24
CENTRAL | February | Under the direction of Joseph Demarco, Worked along side Network Analyst Aaron Magsakay, to replaced a Network switch to Cisco IE3300 inside a Network panel at AUW14 Treatment Building and Raw water building. Provided 24 VDC power to new switch. Informed the ROC regarding possible comm fail alarm. Well were Manual off. There is a trend gap on SCADA between 9:16 AM to 9:47 AM due to this work. Some of the trend data will be back filled by PAC backup file After the replacement, checked all the ports and reset the comm alarms. | Aurora Wells 1-4 Water Treatment Plant | 2026-02-20
CENTRAL | February | On site to take silicate for MTW1/2 and MTW3. No issues on site put everything back to normal. | Aurora Wells 1-4 Water Treatment Plant | 2026-02-25
CENTRAL | February | Onsite for CL2 cylinder change: 60/0 kg to 60/68 kg * | Aurora Wells 1-4 Water Treatment Plant | 2026-02-26
CENTRAL | February | Onsite for raw station check/collect raw samples- WO# W11620710: Quarterly raw ph samples: Well #1 raw ph- 8.09 Well #2 raw ph- 8.06 Well #3 raw ph- 8.05 Well #4 raw ph- 8.05 Building flood alarm received- noticed float tipped underneath grading. Sump doesn?t appear to be pumping- will create work order * Onsite for treated station check/collect sample- WO# W11620710: Sample results (10:30): Free- 0.07, Total- 2.90 * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok | Aurora Wells 1-4 Water Treatment Plant | 2026-02-25
CENTRAL | February | Onsite for treated station check: Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok Onsite for raw station check: Work order created to install safety guard for well 4 motor shaft * Station/equipment- Ok | Aurora Wells 1-4 Water Treatment Plant | 2026-02-27
CENTRAL | February | Onsite for station check: Received ammonia skid delivery * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok | Aurora Wells 1-4 Water Treatment Plant | 2026-02-02
CENTRAL | February | On-site for station check. Wells 2 and 3 running at 102.9 l/s. Topped up silicate day tanks. topped up ammonia tank 1. Verified chlorine analyzer (mg/L): 13:50 Influent free grab: 2.58. Analzyer: 2.63. 14:11 Effluent free grab: 2.64. Analyzer: 2.52. 13:20. Treated free grab: 0.00. Analyzer: 0.12. 13:20. Treated total grab: 3.19. Analyzer: 2.96. No new issues found on site. | Aurora Wells 1-4 Water Treatment Plant | 2026-02-23
CENTRAL | February | Look at check valve passing | Aurora Wells 1-4 Water Treatment Plant | 2026-02-02
CENTRAL | February | Onsite for raw station check/complete assigned work orders: Rotork actuator inspections Pump and motor inspections Station/equipment- Ok | Aurora Wells 1-4 Water Treatment Plant | 2026-02-13
CENTRAL | February | Onsite to complete assigned work orders- informed ROC: CL17 analyzer maintenance Turbidimeter maintenance CL2 leak test Generator test run: Start time:12:10 Stop time: 13:28 Start hours: 91.15 Stop hours: 92.50 Start fuel: 6,850 L Stop fuel: 7,030 L Pre test inspection completed- no abnormalities Generator operating stats (under load- P2/P3): 1800 rpm 600 Volts 60 hertz Oil pressure 78 psi Oil temp 187 F Coolant temp 177 F Fuel pressure 102 psi No abnormalities during generator test run- placed generator back into auto once test run completed Changed CL2 cylinders: 0/60 kg to 68/60 kg (Donald M onsite to assist) * Station back in auto Station/equipment- Ok | Aurora Wells 1-4 Water Treatment Plant | 2026-02-18
CENTRAL | February | Onsite for treated station check: Received CL2 cylinders: 24 received, 24 returned Replaced influent free CL17 reagents Replaced treated total CL17 reagents Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok Onsite for raw station check/completed WO: Air release valve inspection Station/equipment- Ok | Aurora Wells 1-4 Water Treatment Plant | 2026-02-20
CENTRAL | February | Onsite for treated station check/collect sample- WO# W11606256: Sample results (11:30): Free- 0.10, Total- 3.10 * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok Onsite for raw station check/collect samples- WO# W11606256: Station/equipment- Ok | Aurora Wells 1-4 Water Treatment Plant | 2026-02-17
CENTRAL | February | Onsite for treated station check: Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok | Aurora Wells 1-4 Water Treatment Plant | 2026-02-13
CENTRAL | February | Onsite to complete assigned work orders- informed ROC: H/S inspection Chlorine system inspection Silicate system inspection Ammonia system inspection Adjusted silicate p1 max flow from 680 to 760 mL/min Adjusted silicate p2 max flow from 740 to 800 mL/min Adjusted ammonia p1 max flow from 350 to 360 mL/min Adjusted ammonia p2 max flow from 350 to 380 mL/min Performed station housekeeping Completed on-call SCADA review Station/equipment- Ok | Aurora Wells 1-4 Water Treatment Plant | 2026-02-05
CENTRAL | February | On-site for station check and sampling. Micro sampling - W11589385. 09:16 Wells 1 and 4 running with a combined flow of 100 l/s. Collected well 1 and 4 raw samples. 09:45 rotated to running wells 2 and 3. 09:55 collected well 2 and 3 raw samples. Topped up well 3 oil reservoir from 1/4 to full. Topped up silicate day tanks. Verified chlorine analyzer (mg/L): 10:16 Influent free grab: 2.78/2.78/2.78. Analzyer: 2.68. Adjusted to match grab average. Changed right chlorine cylinder bank with Joe Williams. 10:50 Effluent free grab: 2.62/2.67/2.68. Analyzer: 2.47. Adjusted to match grab average. 11:01. Treated free grab: 0.09. Analyzer: 0.12. 11:01. Treated total grab: 3.08. Analyzer: 3.03. Collected treated sample. Changed treated free analyzer reagent. recored station data into process sheets. No new issues found on site. | Aurora Wells 1-4 Water Treatment Plant | 2026-02-11
CENTRAL | February | Onsite for treated station check: Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok Onsite for raw station check: Station/equipment- Ok | Aurora Wells 1-4 Water Treatment Plant | 2026-02-06
CENTRAL | February | Onsite for CL2 cylinder change: 0/49 kg to 68/49 kg * | Aurora Wells 1-4 Water Treatment Plant | 2026-02-03
CENTRAL | February | Onsite to receive silicate delivery: 3,530L / 3,425L to 11,534L / 11,450L | Aurora Wells 1-4 Water Treatment Plant | 2026-02-03
CENTRAL | February | Onsite for station check/collect samples- WO# W11569241: Sample results (09:10): Free- 0.07, Total- 2.84 * Replaced effluent free CL17 reagents * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok Onsite for raw station check/collect samples: Station/equipment- Ok | Aurora Wells 1-4 Water Treatment Plant | 2026-02-04
CENTRAL | February | Well 3 motor service | Aurora Wells 1-4 Water Treatment Plant | 2026-02-05
CENTRAL | February | Onsite for treated station check: Adjusted ammonia p1 max flow from 360 to 350 Adjusted ammonia p2 max flow from 380 to 350 Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok Onsite for raw station check: Station/equipment- Ok | Aurora Wells 1-4 Water Treatment Plant | 2026-02-09
EAST | February | Under Direction of OIC (Dan Zhou) On site for; - Station checks @ 13:52 switched pump duty, pump 3 duty 1 to duty 2, pump 4 duty 2 to duty 1 Grabs @ 14:02 hrs. FCl: 0.05 mg/L TCl: 1.56 mg/L Analyzer Free Chlorine: FCl: 0.04 mg/L Analyzer Total Chlorine: TCl: 1.53 mg/L Pumps 1 and 4 active in duty 1 Equipment OOS: Pump 2 (being rebuilt off-site) Facility OK | Bayview Pumping Station | 2026-02-26
EAST | February | Under Direction of OIC (Dan Zhou) On site for; - Station checks Grabs @ 10:21 hrs. FCl: 0.06 mg/L TCl: 1.54 mg/L Analyzer Free Chlorine: FCl: 0.04 mg/L Analyzer Total Chlorine: TCl: 1.57 mg/L Pumps 1 and 3 not active in duty 1 Equipment OOS: Pump 2 (being rebuilt off-site) Facility OK | Bayview Pumping Station | 2026-02-23
EAST | February | Under Direction of OIC (Dan Zhou) On site for; - Station checks @ 12:08 hrs. Let city of Toronto employee (Mohammed) in station to take a picture of the totalizer. Grabs @ 11:12 hrs. FCl: 0.04 mg/L TCl: 1.43 mg/L Analyzer Free Chlorine 0.06 mg/L Analyzer Total Chlorine: 1.44 mg/L Duty Inactive Changed pump duty from pumps 1 and 4 to 1 and 3. Equipment OOS: Pump 2 (being rebuilt off-site) Facility OK | Bayview Pumping Station | 2026-02-02
EAST | February | Under Direction of OIC (Dan Zhou) On site for; - Station checks Grabs @ 13:20 hrs. FCl: 0.07 mg/L TCl: 1.50 mg/L Analyzer Free Chlorine: FCl: 0.04 mg/L Analyzer Total Chlorine: TCl: 1.44 mg/L @ 13:12 hrs. manually stopped pump 4 to switch duty to pump 3 Duty active @13:24 returned pumps 1 and 3 to auto Pumps 1 and 3 active in duty 1 Equipment OOS: Pump 2 (being rebuilt off-site) Facility OK | Bayview Pumping Station | 2026-02-20
EAST | February | Under Direction of OIC Joe Mazza On site for; - Station checks Grabs @ 13:56 hrs. FCl: 0.04 mg/L TCl: 1.47 mg/L Analyzer Free Chlorine 0.08 mg/L Analyzer Total Chlorine: 1.47 mg/L @ 10:56 hrs. manually stopped pump 3 to switch duty to pump 4 Duty active @11:06 returned pumps 3 and 4 to auto Pumps 1 and 4 active in duty 1 Equipment OOS: Pump 2 (being rebuilt off-site) Facility OK | Bayview Pumping Station | 2026-02-13
EAST | February | Changed the diesel fuel tank high level alarm from 150 to 155 cm. Current level is 153/153 cm or 4073/4087L. | Bayview Pumping Station | 2026-02-18
EAST | February | -Received 7000L diesel fuel | Bayview Pumping Station | 2026-02-18
EAST | February | -The power at Bayview Pumping station very unstable and blipped a couple of times tonight - informed Alectra and ran the station under diesel generator - Diesel hours=126.2 Fuel=2024+2074L | Bayview Pumping Station | 2026-02-16
EAST | February | Generator was running upon arrival. 11:23 placed generator from test mode to auto. Utility power is available. Switched back to utility power with no issues. Pump duty is not active and controlling reservoir is at 81%. Informed ROC. Changed fuel tank low level alarm from 50 to 70 cm. Completed following work orders while on site: Station check JHSC inspection Flood alarm test Ventilation system inspection Dehumidifier cleaning/inspection Sump pump maintenance Chlorine analyzer maintenance Air compressor system maintenance 12:25 grab chlorine analyzer reading, FCL = 0.03 mg/l, TCL = 1.60 mg/l. Chlorine analzyer reading, FCL = 0.09 mg/l, TCL = 1.61 mg/l. 12:51 standardized analyzer reading after maintenance. Monthly generator test is considered to be completed. It was running overnight. Performed post run checks, no issues. Generator stop hour: 138.8 hrs. Fuel level: 772/824 L Diesel fuel order was placed and it is coming in the next few hours. 13:25 Activated duty. P1 and P4 are in duty 1. Pump 2 is OOS for rebuild. Station is back to normal operation. | Bayview Pumping Station | 2026-02-17
EAST | February | Under direction of OIC Dan Zhou On site for; - Station checks Data in PWQ workbook Grabs @ 13:48 hrs. FCl: 0.06 mg/L TCl: 1.51 mg/L Analyzer: FCl: 0.06 mg/L TCl: 1.48 mg/L Equipment OOS: Pump2 (offsite for rebuild) Facility OK | Bayview Pumping Station | 2026-02-06
WEST | February | -on site to trouble shoot diesel system fault alarm -diesel tank high alarm still outstanding -transfer over more to 89% -alarm not clear -spoke with Dan B electrician - restarted panel - alarm did not clear - | East Vaughan Teston Pumping Station | 2026-02-26
EAST | February | Under Direction of OIC (Dan Zhou) On site for; - Station checks Grabs @ 13:56 hrs. FCl: 0.06 mg/L TCl: 1.61 mg/L Analyzer Free Chlorine 0.08 mg/L Analyzer Total Chlorine: 1.63 mg/L Duty active Pumps 1 and 3 active in duty 1 Equipment OOS: Pump 2 (being rebuilt off-site) Facility OK | Bayview Pumping Station | 2026-02-09
WEST | February | -on site for station check -check trends: all ok -entered readings in PWQ: all ok -verified analyzer 10:00 -analyzer free: 0mg/l grab: 0.05mg/l - zero calibrate and set to 0.05mg/l -analyzer total: 1.93/l grab: 2.03mg/l - adjusted -reagents all ok -flushed sanitary pit -equipment all ok | East Vaughan Teston Pumping Station | 2026-02-27
WEST | February | -on site to receive 5000L of diesel and verify VNPS free reading -received 3500L - high alarm on tank came in at 85% - filled to 86% -driver silenced alarm -transfer fuel over to day tank until 87% - still unable to clear diesel fault alarm on SCADA -transfer pumps back to auto -diesel fault will be outstanding until bulk tank level drops -verified PD7 free reason 10:15 -analyzer free: 0.14mg/l grab: 0.06mg/l - adjusted | East Vaughan Teston Pumping Station | 2026-02-26
WEST | February | Onsite wife station check Checked residuals mg/l @1353 Total analyzer 2.14 grab 2.06 Free analyzer 0.01 grab 0.03 Reagents ok | East Vaughan Teston Pumping Station | 2026-02-23
WEST | February | -on site to clean lower level -noticed analyzer free reading 0mg/l -took grab 13:00 -analyzer free: 0mg/l grab:0.04/mg/l adjusted -analyzer total: 2.14mg/l grab: 2.04mg/l - adjusted -reagents all ok | East Vaughan Teston Pumping Station | 2026-02-25
WEST | February | -on site for station check -checked trends: all ok -entered readings in PWQ: all ok -verified analyzer 10:00 -analyzer free: 0.08mg/l grab: 0.08mg/l -analyzer total: 2.07mg/l grab: 2.03mg/l -reagents all ok -checked free reading on analyzer - flow and trending working correctly -equipment and heating all ok | East Vaughan Teston Pumping Station | 2026-02-02
WEST | February | -Responded LoLo pre-total and pre-combined - upon arrival, pre-total analyzer reading=0.14mg/L free=0.12mg/L - Performed grab test, total=1.62mg/L free=0.07mg/L - checked depolox analyzer - reagents, sample flow, grit are all OK - noticed a motor at the total analyzer stopped spinning - called in instrument technician on-call, Parth Patel - review trends - all good - chemical system in manual off | East Vaughan Teston Pumping Station | 2026-02-13
WEST | February | Informed ROC and operations. Onsite for annual maintenance/calibrations. Used calibration mode. Devices were done as below: WPS_SH1_AIT1 , WPS_SH1_AIT2. Took a multiple grab samples and adjusted analyzers accordingly. AL SH1_AIT1 A- 0.04 mg/l G- 0.04 mg/l AL SH1_AIT2 A- 2.01 mg/l G- 2.03 mg/l Put everything back in service, all the related alarms were cleared. No issues. Informed ROC, armed the building and left the site. | East Vaughan Teston Pumping Station | 2026-02-11
WEST | February | Informed ROC. Onsite to troubleshoot pre injection total and pre injection combined chlorine lo Lo reading issue. Put the device in calibration mode and turned off the power to the analyzer. Noticed the shaft came off loose. Installed new shaft. Turned on the power to the analyzer. Took a multiple grab samples and adjusted analyzer accordingly. All the related alarms were cleared. No issues. Informed ROC, armed the building and left the site. | East Vaughan Teston Pumping Station | 2026-02-14
WEST | February | - on site to receive diesel | East Vaughan Teston Pumping Station | 2026-02-18
WEST | February | -on site for station check -check trends: all ok -entered readings in PWQ: all ok -verified analyzer 10:55 -analyzer free: 0.01mg/l grab: 0.06mg/l - adjusted -analyzer total: 2.24mg/l grab: 2.28mg/l -reagents all ok -equipment all ok | East Vaughan Teston Pumping Station | 2026-02-17
WEST | February | -on site to for station check -checked trends: all ok -entered reading in PWQ: all ok -verified analyzer 08:00 -analyzer free: 0.02mg/l grab: 0.02mg/l -analyzer total: 2.02mg/l grab: 2.05mg/l -reagents all ok -flushed sanitary pit | East Vaughan Teston Pumping Station | 2026-02-13
WEST | February | -Reviewed the trends during the repair work last night - The chlorine dosage was based on 20 mins average pre-combined, when put the chemical system back to service. The 20 mins average pre-combined was not updated yet which caused a chlorine overdosage - from 0132 to 0137 and 0150 to 0155 two events that combined residual were greater than 3.00mg/L, the highest combined chlorine was 3.62mg/L (total=3.71mg/L free=0.09mg/L) - during that period time, reservoir was filling@250L/s. The high residual water was pushed into the reservoir and mixed with other water - no user was affected - reviewed trends at PD7 pumping station - normal, combined chlorine around 2.00mg/L, highest analyzer reading total=2.23mg/L - not reportable | East Vaughan Teston Pumping Station | 2026-02-14
WEST | February | - on site for station check -checked trends: all ok -entered readings in PWQ: all ok -verified analyzer 11:45 -analyzer free: 0.03mg/l grab: 0.05mg/l -analyzer total: 2.16mg/l grab: 2.12mg/l -topped KI reagents -flushed sanitary pit -power blip at 12:14 - reset alarms - power source 1 not available - informed on - call electrician - ROC contacting Electra | East Vaughan Teston Pumping Station | 2026-02-20
WEST | February | On site to replace network switch with network analyst Aaron Magsakay. All pumps were in manual. Comm failure alarm was triggered due to this. Removed Old switch from VNPSCD PAC panel. Wired 24 VDC power to the new switch and plugged in the ports. Powered up new IE3300 layer 3 switch and checked the comms. Removed unused cat6 cables. Checked with ROC to make sure comms are back and trends are good. | East Vaughan Teston Pumping Station | 2026-02-04
WEST | February | Vibration readings | East Vaughan Teston Pumping Station | 2026-02-19
WEST | February | -on site for station check -checked trends: all ok -entered reading in PWQ: all ok -verified analyzer 09:20 -analyzer free:0.04mg/l grab: 0.03mg/l -analyzer total: 2.06mg/l grab: 2.06mg/l -reagents all ok -equipment all ok | East Vaughan Teston Pumping Station | 2026-02-09
WEST | February | -on site to complete following work order -hoist inspection: all ok -analyzer verification/maintenance -analyzer verification 09:30 -analyzer free: 0.08mg/l grab: 0.06mg/l -analyzer total: 2.16mg/l grab: 2.14mg/l -reagents all ok/flushed sample lines/adjusted flow/checked motor/pressure/electrolyte - all ok -PD7/PD8 air valve flush: -semi annual diesel test run: power source on site at 10:45 -start time: 235.8 hrs -stop time: 237hrs -diesel level: 2024L 80%, 6290L 47.1% | East Vaughan Teston Pumping Station | 2026-02-05
WEST | February | Onsite for annual calibrations Tower currently off-line Informed ROC Calibrated FIT and LIT Cleared associated alarms Informed ROC Checked building is armed Left site | Holland Landing East Elevated Tank | 2026-02-25
WEST | February | -on site to complete PS station check -PD7 and PD8 duties not active -checked equipment -reviewed trends PD7 Pump Hours: #1 = 8137.4 #2 = 6708.9 #3 = 14650.6 #4 = 11617.1 PD8 Pump Hours: #1 = 17858.2 #2 = 18275.7 #3 = 21514.7 #4 = 21211.9 -analyzer reagents ok Verified analyzers: 08:57 - Analyzer readings: Free Chlorine = 0.10 mg/L Total Chlorine = 2.20 mg/L 08:57 - Grabs: Free Chlorine = 0.04/0.03/0.04 mg/L Total Chlorine = 2.04/2.09/2.06 mg/L 09:02 - adjusted free chlorine analyzer to 0.04 mg/L based on average of 3 grabs 09:06 - adjusted total chlorine analyzer to 2.06 mg/L based on average of 3 grabs -no other issues found -completed Sanitary Pit flush | East Vaughan Teston Pumping Station | 2026-02-06
WEST | February | On site for the following HLETPR, JHSC Health and Safety Inspection, Holland Landing East El HLETPR, Low Temperature Alarm, Test, Holland Landing East, ET (1M) HLETPR, Gasoline Portable Generator, Test, Holland Landing East, ET (1M) No issues on site | Holland Landing East Elevated Tank | 2026-02-03
WEST | February | On site for station check Tower offline, no flow Visual inspection in and around station Verification of equipment and instrumentation. Cleared low temp alarm No issues | Holland Landing East Elevated Tank | 2026-02-09
WEST | February | On-site for station check Review scada and trends Visual inspection of equipment and instrumentation Outstanding alarms: None Residual Chlorine 1300: FCL = 0.03 mg/l TCL = 1.33 mg/l No issues | Holland Landing Sherwood Pumping Station | 2026-02-27
WEST | February | On-site for station check Review scada and trends Visual inspection of equipment and instrumentation Verified analyzer reading Outstanding alarms: None Residual Chlorine: FCL = 0.05 mg/l TCL = 1.38 mg/l No issues | Holland Landing Sherwood Pumping Station | 2026-02-20
WEST | February | On-site for station check Review scada and trends Visual inspection of equipment and instrumentation Verified analyzer reading Outstanding alarms: None Residual Chlorine: FCL = 0.04 mg/l TCL = 2.08 mg/l No issues | Holland Landing Sherwood Pumping Station | 2026-02-13
WEST | February | On-site for station check Review scada and trends Visual inspection of equipment and instrumentation Verified analyzer reading Outstanding alarms: None Residual Chlorine: FCL = 0.06 mg/l TCL = 1.88 mg/l | Holland Landing Sherwood Pumping Station | 2026-02-17
WEST | February | On-site for station check Review scada and trends Visual inspection of equipment and instrumentation Verified analyzer reading Outstanding alarms: None Residual Chlorine: FCL = 0.05 mg/l TCL = 1.12 mg/l No issues | Holland Landing Sherwood Pumping Station | 2026-02-06
WEST | February | -on site to perform following work order -diesel test -diesel start: 1430.5hr -diesel stop: 1431.6hr -diesel level: 667L -received hypo at HLETYS 173L - 570L -completed JHSC inspection: all ok -tested low temp: all ok -exercise suction valve: all ok -exercised discharge valve: all ok | Holland Landing Sherwood Pumping Station | 2026-02-03
WEST | February | On-site for station check Review scada and trends Visual inspection of equipment and instrumentation Verified analyzer reading Outstanding alarms: None Time: 1122 hrs Residual Chlorine: FCL = 0.05 mg/l TCL = 2.48 mg/l No issues | Holland Landing Sherwood Pumping Station | 2026-02-09
WEST | February | Onsite for station check and to collect weekly micro sample W11620194 Activated duty Checked residuals mg/l Influent free @0927 Free analyzer 2.92 grab 2.90 Total grab 3.62 Effluent free @0931 Free analyzer 2.68 grab 2.72 Total grab 3.20 Treated @0937 Total analyzer 3.25 grab 3.20 Free analyzer 0.15 grab 0.16 Sl1000 Mcl grab 2.88 F nh3 grab 0.10 T nh3 grab 0.67 Another total sl1000 grab @0952 Mcl grab 2.81 F nh3 0.09 T nh3 0.64 Increased ammonia p2 max flow from 105 to 115 ml/min Sl1000 grab @1010 Mcl grab 2.78 F nh3 0.07 T nh3 0.62 | Holland Landing Well No. 1 | 2026-02-25
WEST | February | On-site for station check Reviewed scada and trends, duty active, ET at 65% Verified chlorine analyzers readings Visual inspection on instrumentation and equipment AOK Chemical pumps: Chlorine: chlorinator#2 opened @ 34% and dosing at 36 ppd Chlorine dose scada = 15.3 kg/d Chlorinator1 and BP1 in duty2 Chlorine booster1 pressure: 145 psi (1,000 kpa) Ammonia: Pump2 in duty1 running at 47% speed Dosing 49.05 mL/min P1 MAX flow = 85 mL/min P2 MAX flow = 115 mL/min Pump discharge pressure: 595 kpa Silicate : pump2 running in duty1 @ 32% Silicate dose = 35.70 mL/min Chlorine grabs: @ 1323 hrs Influent FCL FCL = 2.74mg/l Analyzer reading: FCL = 2.77 mg/l Effluent FCL @ 1340 hrs: FCL = 2.52 mg/l Analyzer: 2.60 mg/l Analyzer adjusted to 2.52 based on 2 repetitive grabs Treated grabs @ 1200 hrs FCL : 0.10 mg/l Analyzer reading: FCL : 0.14 mg/l TCL : 3.04 mg/l TCL : 3.09 mg/l SL1000: @ 1323 hrs with Ammonia pump2 FA = 0.07 mg/ TA = 0.59 mg/l Mono = 2.64 mg/l | Holland Landing Well No. 1 | 2026-02-23
WEST | February | Restarted the Operator Interface Terminal due to Windows OS updates. The well was off and the Remote Operations Center was notified prior to doing the work. | Holland Landing Well No. 1 | 2026-02-23
WEST | February | Onsite to complete the following WOs: - Flow control valve test - Washroom room light cleaning and supplies - Chlorine scrubber inspection - Chemical system inspection ~ ammonia - Chlorinator 2 vacuum gauge troubleshoot - Replace air / vacuum release valve - Relocate sample lines Notified ROC placed well 1 in manual off Notified ROC after completion No issues | Holland Landing Well No. 1 | 2026-02-24
WEST | February | On-site for station check Reviewed scada and trends, duty active, ET at 48% Verified chlorine analyzers readings Visual inspection on instrumentation and equipment AOK Chemical pumps: Chlorine: chlorinator#1 opened @ 33% and dosing at 36 ppd Chlorine dose scada = 14.8 kg/d Chlorinator2 and BP2 in duty Chlorine booster1 pressure: 145 psi (1,000 kpa) Ammonia: Pump2 in duty1 running at 44% speed Dosing 49.05 mL/min P1 MAX flow = 85 mL/min P2 MAX flow = 115 mL/min Pump discharge pressure: 600 kpa Silicate : pump2 running in duty1 @ 36% Silicate dose = 34.07 mL/min Chlorine grabs: @ 0950 hrs Influent FCL FCL = 2.84mg/l Analyzer reading: FCL = 2.85 mg/l Effluent FCL @ 1036 hrs: FCL = 2.72 mg/l Analyzer: 2.71 mg/l Treated grabs @ 1200 hrs FCL : 0.12 mg/l Analyzer reading: FCL : 0.16 mg/l TCL : 3.30 mg/l TCL : 3.29 mg/l SL1000: @ 1033 hrs with Ammonia pump2 FA = 0.07 mg/ TA = 0.56 mg/l Mono = 2.49 mg/l Troubleshoot with ammonia pump1, adjusted Max flow from 100 down to 85 mL/min Ammonia pump1 running @ 61% at a dosage of 61.34 mL/min 1106 hrs: Ammonia pump1 SL1000 grab: FA = 0.05 mg/ TA = 0.60 mg/l Mono = 2.76 mg/l | Holland Landing Well No. 1 | 2026-02-27
WEST | February | Changed cl2 cylinder with S. Baidy | Holland Landing Well No. 1 | 2026-02-25
WEST | February | On-site for station check Reviewed scada and trends, duty active, ET at 70% Verified chlorine analyzers readings Visual inspection on instrumentation and equipment AOK Chemical pumps: Chlorine: chlorinator#1 opened @ 34% and dosing at 38 ppd Chlorine dose scada = 15.3 kg/d Chlorinator2 and BP2 in dury2 Chlorine booster pressure: 155 psi (1,069 kpa) Ammonia: Pump1 in duty1 running at 43% speed Dosing 51.15 mL/min P1 MAX flow = 120 mL/min P2 MAX flow = 120 mL/min Pump discharge pressure: 453 kpa Silicate : pump1 running in duty1 @ 36% Silicate dose = 34.07 mL/min Chlorine grabs: @ 1208 hrs Influent FCL FCL = 2.88mg/l Analyzer reading: FCL = 2.87 mg/l Effluent FCL @ 1210 hrs: FCL = 2.70 mg/l Analyzer: 2.72 mg/l Treated grabs @ 1216 hrs FCL : 0.09 mg/l Analyzer reading: FCL : 0.14 mg/l TCL : 3.38 mg/l TCL : 3.37 mg/l SL1000: @ 1200 hrs with Ammonia pump1 FA = 0.07 mg/l TA = 0.62 mg/l Mono = 2.78 mg/l | Holland Landing Well No. 1 | 2026-02-02
WEST | February | On site to collect weekly bact samples from raw (11:00) and treated (11:05) sample taps (W11568853). Tested chlorine residuals via hach field kit. Free: 0.16 mg/L Total: 3.07 mg/L | Holland Landing Well No. 1 | 2026-02-02
WEST | February | Filled silicate tanks 176/167 L to 408/396 L | Holland Landing Well No. 1 | 2026-02-02
WEST | February | On-site for station check Reviewed scada and trends, duty active, ET at 66% Verified chlorine analyzers readings Visual inspection on instrumentation and equipment AOK Chemical pumps: Chlorine: chlorinator#1 opened @ 33% and dosing at 36 ppd Chlorine dose scada = 14.8 kg/d Chlorinator2 and BP2 in duty2 Chlorine booster1 pressure: 145 psi (1,000 kpa) Ammonia: Pump2 in duty1 running at 43% speed Dosing 49.40 mL/min P1 MAX flow = 85 mL/min P2 MAX flow = 115 mL/min Pump discharge pressure: 393 kpa Silicate : pump1 running in duty1 @ 36% Silicate dose = 34.07 mL/min Chlorine grabs: @ 1150 hrs Influent FCL FCL = 2.72mg/l Analyzer reading: FCL = 2.74 mg/l Effluent FCL @ 1155 hrs: FCL = 2.64 mg/l Analyzer: 2.64 mg/l Treated grabs @ 1200 hrs FCL : 0.07 mg/l Analyzer reading: FCL : 0.16 mg/l TCL : 3.08 mg/l TCL : 3.10 mg/l SL1000: @ 1156 hrs with Ammonia pump2 FA = 0.01 mg/ TA = 0.53 mg/l Mono = 2.62 mg/l Adjusted max flow on ammonia pump2 from 100 to 115% FA = 0.02 mg/l TA = 0.52 mg/l Mono = 2.58 mg/l 1218 hrs: switched ammonia pumps duty, placed p1 in lead duty @ 100 mL/min (49% speed), pump1 was not dosing for some reasons, which caused treated FCL to spike to 1.7 mg/l. switched back to p2 and FCL came back down to normal levels. Placed p1 in manual off will return for further troubleshoot. Adjusted max flow on ammonia pump2 from 100 to 105% FA = 0.05 mg/l TA = 0.54 mg/l Mono = 2.65 mg/l | Holland Landing Well No. 1 | 2026-02-20
WEST | February | On-site for station check Reviewed scada and trends, duty active, ET at 67% Verified chlorine analyzers readings Visual inspection on instrumentation and equipment AOK Chemical pumps: Chlorine: chlorinator#1 opened @ 33% and dosing at 37 ppd Chlorine dose scada = 14,8 kg/d Chlorinator2 and BP1 in duty2 Chlorine booster1 pressure: 145 psi (1,000 kpa) Ammonia: Pump2 in duty1 running at 41% speed Dosing 49.53 mL/min P1 MAX flow = 85 mL/min P2 MAX flow = 100 mL/min Pump discharge pressure: 393 kpa Silicate : pump1 running in duty2 @ 36% Silicate dose = 34.07 mL/min Chlorine grabs: @ 0840 hrs Influent FCL FCL = 2.78mg/l Analyzer reading: FCL = 2.81 mg/l Made adjustment to influent FCL analyzer reading from 2.85 down to 2.76 based on average of 3 grabs Effluent FCL @ 0943hrs: FCL = 2.62 mg/l Analyzer: 2.66 mg/l Treated grabs @ 0948 hrs FCL : 0.08 mg/l Analyzer reading: FCL : 0.16 mg/l TCL : 3.32 mg/l TCL : 3.35 mg/l SL1000: @ 0948 hrs with Ammonia pump2 FA = 0.04 mg/l TA = 0.57 mg/l Mono = 2.67 mg/l | Holland Landing Well No. 1 | 2026-02-13
WEST | February | -on site to install new pump head on ammonia pump #1 -installed new pump head and completed drawdown, pump max flow = 77.5 ml/min -adjusted scada max flow setpoint 120 to 85 ml/min -put pump #1 into duty 1 and collected ammonia grab: MCL = 2.55 mg/L TNH3 = 0.54 mg/L FNH3 = 0.03 mg/L -will continue to monitor | Holland Landing Well No. 1 | 2026-02-12
WEST | February | Onsite to top up silicate day tank from 225 to 419 L | Holland Landing Well No. 1 | 2026-02-18
WEST | February | On-site for station check Reviewed scada and trends, duty active, ET at 57% Verified chlorine analyzers readings Visual inspection on instrumentation and equipment AOK Chemical pumps: Chlorine: chlorinator#1 opened @ 33% and dosing at 37 ppd Chlorine dose scada = 14,8 kg/d Chlorinator2 and BP1 in duty2 Chlorine booster1 pressure: 145 psi (1,000 kpa) Ammonia: Pump1 in duty1 running at 41% speed Dosing 48.80 mL/min P1 MAX flow = 120 mL/min P2 MAX flow = 120 mL/min Pump discharge pressure: 393 kpa Silicate : pump1 running in duty2 @ 36% Silicate dose = 34.07 mL/min Chlorine grabs: @ 1104 hrs Influent FCL FCL = 2.76mg/l Analyzer reading: FCL = 2.85 mg/l Made adjustment to influent FCL analyzer reading from 2.85 down to 2.76 based on average of 3 grabs Effluent FCL @ 1114hrs: FCL = 2.58 mg/l Analyzer: 2.58 mg/l Treated grabs @ 1121 hrs FCL : 0.08 mg/l Analyzer reading: FCL : 0.15 mg/l TCL : 3.20 mg/l TCL : 3.22 mg/l SL1000: @ 1520 hrs with Ammonia pump1 FA = 0.03 mg/l TA = 0.50 mg/l Mono = 2.39 mg/l Increased ammonia pump2 max flow from 120 down to 100 mL/min SL1000: @ 1520 hrs with Ammonia pump1 FA = 0.02 mg/l TA = 0.51 mg/l Mono = 2.56 mg/l | Holland Landing Well No. 1 | 2026-02-11
WEST | February | On-site for station check and collection of weekly bacT and operational samples Reviewed scada and trends, duty active, ET at 88% Verified chlorine analyzers readings Visual inspection on instrumentation and equipment AOK Chemical pumps: Chlorine: chlorinator#2 opened @ 33% and dosing at 36 ppd Chlorine dose scada = 14.8 kg/d Chlorinator1 and BP1 in duty2 Chlorine booster1 pressure: 145 psi (1,000 kpa) Ammonia: Pump2 in duty1 running at 37% speed Dosing 49.53 mL/min P1 MAX flow = 85 mL/min P2 MAX flow = 135 mL/min Pump discharge pressure: 393 kpa Silicate : pump1 running in duty2 @ 36% Silicate dose = 34.07 mL/min Chlorine grabs: @ 1132 hrs Influent FCL FCL = 2.74mg/l Analyzer reading: FCL = 2.77 mg/l Effluent FCL @ 1139 hrs: FCL = 2.62 mg/l Analyzer: 2.65 mg/l Treated grabs @ 1152 hrs FCL: 0.09 mg/l Analyzer reading: FCL: 0.14 mg/l TCL: 3.04 mg/l TCL: 3.00 mg/l SL1000: @ 1200 hrs with Ammonia pump2 FA = 0.21 mg/l TA = 0.78 mg/l Mono = 2.86 mg/l Adjusted max flow on ammonia pump2 from 100 to 136% FA = 0.04 mg/l TA = 0.56 mg/l Mono = 2.72 mg/l | Holland Landing Well No. 1 | 2026-02-17
WEST | February | Onsite for for completion of the following WOs HLW1, Chlorine Gas Detector, Test, Chlorine Analyzers cleaning and maintenance Turbidity Analyzer TU5300, Maintenance and Calibration, Chemical System Inspection - Chlorine , Cl2 Emergency Repair Kit Inspection, Flow Control Valve, Test, Chemical System Inspection - Silicate, rebuilt and installed a release valve Chemical System Inspection - Ammonia System Chlorine Scrubber, Notified ROC before starting WOs Activated duty and monitored station no issues Deactivated duty, notified ROC before leaving site | Holland Landing Well No. 1 | 2026-02-05
WEST | February | On-site for station check Reviewed scada and trends, duty active, ET at 48% Verified chlorine analyzers readings Visual inspection on instrumentation and equipment AOK Chemical pumps: Chlorine: chlorinator#1 opened @ 33% and dosing at 37 ppd Chlorine dose scada = 14,8 kg/d Chlorinator1 and BP1 in duty2 Chlorine booster1 pressure: 145 psi (1,000 kpa) Ammonia: Pump1 in duty1 running at 39% speed Dosing 46.86 mL/min P1 MAX flow = 120 mL/min P2 MAX flow = 120 mL/min Pump discharge pressure: 393 kpa Silicate : pump1 running in duty2 @ 42% Silicate dose = 35.37 mL/min Chlorine grabs: @ 1514 hrs Influent FCL FCL = 2.88mg/l Analyzer reading: FCL = 2.86 mg/l Effluent FCL @ 1518hrs: FCL = 2.48 mg/l Analyzer: 2.48 mg/l Treated grabs @ 1529 hrs FCL : 0.10 mg/l Analyzer reading: FCL : 0.17 mg/l TCL : 3.16 mg/l TCL : 3.20 mg/l SL1000: @ 1520 hrs with Ammonia pump1 FA = 0.04 mg/l TA = 0.54 mg/l Mono = 2.47 mg/ | Holland Landing Well No. 1 | 2026-02-09
WEST | February | On-site for station check Reviewed scada and trends, duty active, ET at 48% Verified chlorine analyzers readings Visual inspection on instrumentation and equipment AOK Chemical pumps: Chlorine: chlorinator#1 opened @ 33% and dosing at 37 ppd Chlorine dose scada = 14,3 kg/d Chlorinator1 and BP1 in duty2 Chlorine booster1 pressure: 145 psi (1,000 kpa) Ammonia: Pump1 in duty1 running at 39% speed Dosing 46.86 mL/min P1 MAX flow = 120 mL/min P2 MAX flow = 120 mL/min Pump discharge pressure: 393 kpa Silicate : pump1 running in duty2 @ 42% Silicate dose = 35.37 mL/min Chlorine grabs: @ 1123 hrs Influent FCL FCL = 2.92mg/l Analyzer: FCL = 2.90 mg/l Effluent FCL @ 1126hrs: FCL = 2.48 mg/l Analyzer: 2.50 mg/l Treated grabs @ 1133 hrs FCL : 0.08 mg/l Analyzer reading: FCL : 0.13 mg/l TCL : 3.04 mg/l TCL : 3.09 mg/l SL1000: @ 1133 hrs with Ammonia pump1 FA = 0.05 mg/l TA = 0.54 mg/l Mono = 2.49 mg/l changed tubing element on silicate pump2, primmed and placed back in service, in duty1 Completed JHSC health and safety inspection | Holland Landing Well No. 1 | 2026-02-06
WEST | February | Reviewed scada and trends, duty active, ET at 65% Verified chlorine analyzers readings Visual inspection on instrumentation and equipment AOK Chlorine grabs: @ 1205 hrs Influent FCL FCL = 2.62 mg/l Analyzer reading: FCL = 2.64 mg/l Effluent FCL @ 1220 hrs: FCL = 2.52 mg/l Analyzer: 2.51 mg/l Treated grabs @ 1228 hrs FCL : 0.14 mg/l Analyzer reading: FCL : 0.13 mg/l TCL : 3.10 mg/l TCL : 3.15 mg/l SL1000: @ 0926 hrs with Ammonia pump2 FA = 0.07 mg/l TA = 0.59 mg/l Mono = 2.57 mg/l Adjusted ammonia p2 max flow from 110 to 125 mL/min based on FA grab Chemical pumps: Chlorine: chlorinator#2 opened @ 68% and dosing at 68 ppd Chlorine dose scada = 30.7 kg/d Dosage factor = 155 % Chlorinator1 and BP1 in duty2 Chlorine booster2 pressure: 1,150 kpa Ammonia: Pump2 in duty1 running at 56% speed Dosing 70.09 mL/min P1 MAX flow = 85 mL/min P2 MAX flow = 125 mL/min Pump2 discharge pressure: 700 kpa Silicate : pump2 running in duty2 @ 36% Silicate dose = 42:93 mL/min Pump1 in duty2 | Holland Landing Well No. 2 | 2026-02-27
WEST | February | Reviewed scada and trends, duty active, ET at 73% Verified chlorine analyzers readings Visual inspection on instrumentation and equipment AOK Chlorine grabs: @ 1430 hrs Influent FCL FCL = 2.60mg/l Analyzer reading: FCL = 2.65 mg/l Effluent FCL @ 1436 hrs: FCL = 2.50 mg/l Analyzer: 2.53 mg/l Treated grabs @ 1449 hrs FCL : 0.16 mg/l Analyzer reading: FCL : 0.15 mg/l TCL : 3.10 mg/l TCL : 3.06 mg/l SL1000: @ 1449 hrs with Ammonia pump2 FA = 0.02 mg/l TA = 0.50 mg/l Mono = 2.45 mg/l Adjusted ammonia p2 max flow from 113 to 118 mL/min based on FA grab 1015 hrs: Did grab of FA after adjustments: 0.02 mg/l Chemical pumps: Chlorine: chlorinator#2 opened @ 67% and dosing at 65 ppd Chlorine dose scada = 30.5 kg/d Dosage factor = 152 % Chlorinator1 and BP1 in duty1 Chlorine booster2 pressure: 1,150 kpa Ammonia: Pump2 in duty1 running at 59% speed Dosing 70.09 mL/min P1 MAX flow = 85 mL/min P2 MAX flow = 118 mL/min Pump2 discharge pressure: 700 kpa Silicate : pump2 running in duty2 @ 36% Silicate dose = 42:93 mL/min Pump1 in duty2 | Holland Landing Well No. 2 | 2026-02-23
WEST | February | Onsite for station check and to collect weekly micro sample W11620194 Duty running Checked residuals mg/l Influent @1104 Free analyzer 2.70 grab 2.80 Total grab 3.64 Effluent @1109 Free analyzer 2.54 grab 2.46 Total grab 2.80 Treated @1117 Total analyzer 3.06 grab 3.12 Free analyzer 0.14 grab 0.19 Sl 1000 Mcl grab 2.41 F nh3 grab 0.00 T nh3 grab 0.47 Sharon feed @1122 Total grab 2.13 Decreased ammonia p2 max flow from 118 to 100 ml/min Sl1000 grab @1240 Mcl 2.67 F nh3 0.07 T nh3 0.60 | Holland Landing Well No. 2 | 2026-02-25
WEST | February | Filled silicate tank 318 L to 531 L | Holland Landing Well No. 2 | 2026-02-02
WEST | February | Restarted the Operator Interface Terminal due to Windows OS updates. The well was off and the Remote Operations Center was notified prior to doing the work. | Holland Landing Well No. 2 | 2026-02-23
WEST | February | -on site to complete station check -well running in auto -cl2 booster pump # 2 running at 170 psi -chlorinator # 2 67% open dosing 65 ppd, vac = -270 mbar, DF = 153% -silicate pump # 1 running at 36%, 21.9 rpm -ammonia pump # 1 running at 71%, 80 psi, 128 strokes/min -checked equipment -reviewed trends -CL17 reagents ok 13:12 - Sharon Valve grab: TCL = 2.37 mg/L MCL = 1.91 mg/L TNH3 = 0.47 mg/L FNH3 = 0.09 mg/L -verified chlorine analyzers: 13:14 - Influent FCL Analyzer = 2.38 mg/L 13:14 - Influent grab: Free chlorine = 2.58 mg/L -unable to adjust influent analyzer due to issues with keyboard, work order issued for instrumentation 13:19 - Effluent FCL Analyzer = 2.42 mg/L 13:19 - Effluent grab: Free chlorine = 2.36 mg/L 13:22 - Treated water analyzers: FCL = 0.17 mg/L TCL = 2.93 mg/L 13:22 - Treated water grabs: FCL = 0.19 mg/L TCL = 2.90 mg/L MCL = 2.45 mg/L TNH3 = 0.61 mg/L FNH3 = 0.13 mg/L -increased ammonia pump #1 max flow 95 to 115 ml/min 14:15 - collected treated water grab: MCL = 2.48 mg/L TNH3 = 0.57 mg/L FNH3 = 0.08 mg/L -recorded readings in PWQ sheet -no other issues found | Holland Landing Well No. 2 | 2026-02-02
WEST | February | Onsite to top up silicate day tank from 273 L to 567 L | Holland Landing Well No. 2 | 2026-02-18
WEST | February | -on site to respond to NTU fault -no flow on unit - confirm flow - sensor not working -disabled and confirmed flow -adjusted heater in chlorine room -restarted well | Holland Landing Well No. 2 | 2026-02-21
WEST | February | In to complete station check. Enter data into PWQ. Analyzer reagent levels good. Span Calibrated Treated TCL cl17 analyzer from 3.00 to 2.90mg/L based on grabs. Disable auto duty All Stop rotate on Ammonia pumps; to test new pump head on Ammonia P1. Dosing appears to be working well. | Holland Landing Well No. 2 | 2026-02-13
WEST | February | Onsite for station check and collection of weekly of bacT and operational samples Reviewed SCADA and trends, duty active, ET at 86% Verified chlorine analyzers readings Visual inspection on instrumentation and equipment AOK Chlorine grabs: @ 1036 hrs Influent FCL FCL = 2.60mg/l Analyzer reading: FCL = 2.63 mg/l Effluent FCL @ 1024 hrs: FCL = 2.70 mg/l Analyzer: 2.68 mg/l Treated grabs @ 1000 hrs FCL: 0.12 mg/l Analyzer reading: FCL: 0.14 mg/l TCL : 3.04 mg/l TCL: 3.00mg/l SL1000: @ 1000 hrs with Ammonia pump2 FA = 0.07 mg/l TA = 0.60 mg/l Mono = 2.67 mg/l Chemical pumps: Chlorine: chlorinator#1 opened @ 68% and dosing at 69 ppd Chlorine dose scada = 30.9 kg/d Dosage factor = 155 % Chlorinator2 and BP2 in duty2 Chlorine booster1 pressure: 1,350 kpa Ammonia: Pump2 in duty1 running at 65% speed Dosing 73.99 mL/min P1 MAX flow = 85 mL/min P2 MAX flow = 1139 mL/min Pump discharge pressure: 525 kpa Silicate : pump2 running in duty2 @ 36% Silicate dose = 43:36 mL/min Pump1 in duty2 | Holland Landing Well No. 2 | 2026-02-17
WEST | February | Onsite to complete the following WOs: JHSC Health and Safety Inspection, Chlorine Gas leak Detector alarm test Chlorine Analyzer Maintenance Chemical System Inspection - Chlorine, Pressure Relief Valve, Maintenance, Chlorine Scrubber, Check, Holland Landing, Low/High Temperature Alarm, Test, Turbidimeter, Maintenance Chemical System Inspection - Silicate, Chemical System Inspection - Ammonia, Pressure Relief Valve, Maintenance, Notified ROC placed well 2 pump in manual off Completed WOs cleared alarms and reset Verified chlorine analyzer as follows Influent FCL @1216 hrs: FCL = 2.98mg/l Analyzer reading: FCL = 2.95 mg/l Effluent FCL @ 1220hrs: FCL = 2.44 mg/l Analyzer: 2.48 mg/l Treated grabs @ 1229 hrs FCL : 0.27 mg/l Analyzer reading: FCL : 0.29 mg/l TCL : 3.10 mg/l TCL : 3.07 mg/l SL1000 FA = 0.02 mg/l TA = 0.47 mg/l Mono = 2.25 mg/l Replaced new liquid head on ammonia pump1 Ammonia pumps require further adjustment, placed well 2 pump in manual off due to time constraints will return tomorrow continue troubleshooting. Notified ROC before leaving site | Holland Landing Well No. 2 | 2026-02-10
WEST | February | Reviewed scada and trends, duty active, ET at 57% Verified chlorine analyzers readings Visual inspection on instrumentation and equipment AOK Chlorine grabs: @ 9:55 hrs Influent FCL FCL = 2.54mg/l Analyzer reading: FCL = 2.57 mg/l Effluent FCL @ 9:51 hrs: FCL = 2.66 mg/l Analyzer: 2.64 mg/l Treated grabs @ 0926 hrs FCL : 0.14 mg/l Analyzer reading: FCL : 0.15 mg/l TCL : 3.28 mg/l TCL : 3.29mg/l SL1000: @ 0926 hrs with Ammonia pump2 FA = 0.09 mg/l TA = 0.62 mg/l Mono = 2.69 mg/l Adjusted ammonia p2 max flow from 113 to 120 mL/min based on FA grab 1015 hrs: Did grab of FA after adjustments: 0.04 mg/l Chemical pumps: Chlorine: chlorinator#2 opened @ 67% and dosing at 69 ppd Chlorine dose scada = 30.5 kg/d Dosage factor = 154 % Chlorinator1 and BP2 in duty1 Chlorine booster2 pressure: 1,150 kpa Ammonia: Pump2 in duty1 running at 58% speed Dosing 73.99 mL/min P1 MAX flow = 85 mL/min P2 MAX flow = 120 mL/min Pump2 discharge pressure: 700 kpa Silicate : pump2 running in duty2 @ 36% Silicate dose = 43:11 mL/min Pump1 in duty2 | Holland Landing Well No. 2 | 2026-02-20
WEST | February | On site to complete chlorine overhaul annual. Replaced regulators, ejectors, PE tubing and parker fittings. Replaced 3 chemline ball valves that had not been replaced in 2024 (interconnects). Vacuum tested without issue, backflushed small volume to clear highly chlorinated water and reprime chlorine BP discharge lines. No issues. | Holland Landing Well No. 2 | 2026-02-19
WEST | February | Onsite to complete the following WOs: - Changed and replaced chlorine regulators - Changed and replaced chlorine injectors - Changed and replaced chlorine lines and fittings tested chlorine system after maintenance, tested chlorine regulators for vacuum, both regulators responded normally Did visual inspection on chlorine system, no issues prepared new batch of ammonia for tank2 1400hrs, backflashed system and started well 2 in manual 1435 hrs; Did grab on influent FCL analyzer when analyzer was reading 2.44 mg/l = grab was 2.40 mg/l SL1000 reading: FA = 0.06 TA = 0.47 Mono = 2.08 Treated = 2.78 FCL = 0.16 mg/l 1520 hrs shut down well and returned to auto. | Holland Landing Well No. 2 | 2026-02-19
WEST | February | Onsite for station check and collection of weekly bacT samples Reviewed scada and trends, duty active, ET at 53% Verified chlorine analyzers readings Visual inspection on instrumentation and equipment AOK Chlorine grabs: @ 1342 hrs Influent FCL FCL = 2.76mg/l Analyzer reading: FCL = 2.74 mg/l Effluent FCL @ 1344 hrs: FCL = 2.50 mg/l Analyzer: 2.54 mg/l Treated grabs @ 1352 hrs FCL : 0.18 mg/l Analyzer reading: FCL : 0.21 mg/l TCL : 3.10 mg/l TCL : 3.05mg/l SL1000: @ 1352 hrs with Ammonia pump2 FA = 0.02 mg/l TA = 0.53 mg/l Mono = 2.54 mg/l Chemical pumps: Chlorine: chlorinator#1 opened @ 68% and dosing at 69 ppd Chlorine dose scada = 30.9 kg/d Dosage factor = 156 % Chlorinator2 and BP2 in duty2 Chlorine booster1 pressure: 1,350 kpa Ammonia: Pump2 in duty1 running at 90% speed Dosing 76.78 mL/min P1 MAX flow = 85 mL/min P2 MAX flow = 1139 mL/min Pump discharge pressure: 525 kpa Silicate : pump1 running in duty2 @ 36% Silicate dose = 43.11 mL/min Pump2 in duty2 troubleshoot with ammonia pump2 with new liquid head run through cal column and adjusted accordingly placed ammonia pump1 in duty1 and started duty adjusted max flow to 85 mL/min, verified pump1 dosage by SL1000 grabs recorded above. no issues | Holland Landing Well No. 2 | 2026-02-11
WEST | February | -on site to complete station check and to collect samples -sample work order # W11639094 -cl2 booster pump # 1 running at 195 psi -chlorinator # 1 66% open dosing 67 ppd, vac = -660 mbar, DF = 151% -silicate pump # 2 running at 36%, 21.8 rpm -ammonia pump # 2 running at 57%, 80 psi, 100 strokes / min -checked equipment -reviewed trends -CL17 reagents ok 09:17 - Sharon Valve grab: TCL = 1.58 mg/L MCL = 0.67 mg/L TNH3 = 0.32 mg/L FNH3 = 0.19 mg/L -verified chlorine analyzers: 09:18 - Influent FCL Analyzer = 2.83 mg/L 09:18 - Influent grab: Free chlorine = 2.88 mg/L 09:23 - Effluent FCL Analyzer = 2.42 mg/L 09:23 - Effluent grab: Free chlorine = 2.42 mg/L 09:28 - Treated water analyzers: FCL = 0.19 mg/L TCL = 2.97 mg/L 09:28 - Treated water grabs: FCL = 0.16 mg/L TCL = 3.02 mg/L MCL = 2.52 mg/L TNH3 = 0.56 mg/L FNH3 = 0.06 mg/L 09:33 - collected weekly treated water micro sample 09:34 - collected weekly raw water micro sample -recorded readings in PWQ sheet -no issues found -influent analyzer repaired, enabled auto dosing mode and adjusted chlorine residual setpoint from 3.30 mg/L to 2.80 mg/L -returned well to auto | Holland Landing Well No. 2 | 2026-02-05
WEST | February | Attending site to check Influent Free chlorine analyzer (W11622780). Push button switches were found to be not functioning. Replaced switches and verified reading. Reading as found = 2.11mg/L, reading as left = 2.28 mg/L Free chlorine based on average of three grabs. ROC was notified before and after maintenance activities. | Holland Landing Well No. 2 | 2026-02-04
WEST | February | Attending site to complete chlorine analyzer push button replacements (W11622780). Completed repairs on the Treated Total and Effluent Free chlorine analyzers. Analyzer readings were verified after work was completed. ROC was notified before and after maintenance activities. | Holland Landing Well No. 2 | 2026-02-05
WEST | February | On-site for station check and to respond to combine chlorine hihi interlock alarm @0848 hrs well interlocked and placed in manual off 1330 hrs verified analyzers readings upon arrival: Treated FCL = 0.03 mg/l TCL = 1.84, 1.88 and 1.82 mg/l Analyzer reading FCL = 0.04 mg/l TCL = 2.03 mg/l 1350 hrs Did grab on Influent FCL = 2.50 mg/l Analyzer reading = 2.55 mg/l 1416 hrs Did grab on Effluent FCL = 2.15 mg/l Analyzer = 2.13 mg/l 1403 hrs cleared alarms and reset. Placed well 2 pump back to auto, well started in auto. Chlorine grabs: @ 1429 hrs Influent FCL FCL = 2.88mg/l Analyzer reading: FCL = 2.83 mg/l Effluent FCL @ 1435 hrs: FCL = 2.40 mg/l Analyzer: 2.38 mg/l Treated grabs @ 1446 hrs FCL : 0.12 mg/l Analyzer reading: FCL : 0.18 mg/l TCL : 3.06 mg/l TCL : 3.03mg/l SL1000: @ 1422 hrs with Ammonia pump2 FA = 0.12 mg/l TA = 0.53 mg/l Mono = 2.40 mg/l Chemical pumps: Chlorine: chlorinator#1 opened @ 68% and dosing at 67 ppd Chlorine dose scada = 30.3 kg/d Dosage factor = 153 % Chlorinator2 and BP2 in dury2 Chlorine booster1 pressure: 1,350 kpa Ammonia: Pump2 in duty1 running at 61% speed Dosing 68.88 mL/min P1 MAX flow = 115 mL/min P2 MAX flow = 113 mL/min Pump discharge pressure: 453 kpa Silicate : pump1 running in duty2 @ 36% Silicate dose = 43.38 mL/min Reviewed scada and trends, duty active, ET at 53% Verified chlorine analyzers readings Visual inspection on instrumentation and equipment AOK Notified ROC before leaving site | Holland Landing Well No. 2 | 2026-02-06
WEST | February | -on site to change cylinder 35.6kg- 103kg -no issues | Holland Landing Well No. 2 | 2026-02-03
WEST | February | Reviewed scada and trends, duty active, ET at 69% Verified chlorine analyzers readings Visual inspection on instrumentation and equipment AOK Chlorine grabs: @ 1400 hrs Influent FCL FCL = 2.90mg/l Analyzer reading: FCL = 2.87 mg/l Effluent FCL @ 1406 hrs: FCL = 2.50 mg/l Analyzer: 2.48 mg/l Treated grabs @ 1419 hrs FCL : 0.13 mg/l Analyzer reading: FCL : 0.17 mg/l TCL : 3.14 mg/l TCL : 3.10mg/l SL1000: @ 1400 hrs with Ammonia pump2 FA = 0.04 mg/l TA = 0.51 mg/l Mono = 2.38 mg/l Chemical pumps: Chlorine: chlorinator#1 opened @ 65% and dosing at 67 ppd Chlorine dose scada = 29.6 kg/d Dosage factor = 149 % Chlorinator2 and BP2 in duty2 Chlorine booster1 pressure: 1,350 kpa Ammonia: Pump2 in duty1 running at 61% speed Dosing 69.08 mL/min P1 MAX flow = 115 mL/min P2 MAX flow = 113 mL/min Pump discharge pressure: 453 kpa Silicate : pump1 running in duty2 @ 36% Silicate dose = 43.10 mL/min Pump2 in duty2 | Holland Landing Well No. 2 | 2026-02-09
WEST | February | On site to complete station check and receive 400L of sodium hypochlorite. Readings entered into PWQ sheet. | Holland Landing West Elevated Tank | 2026-02-24
WEST | February | Attending site to check Hypo and Ammonia tank level transmitters due to erratic behaviour (W11528810). Replaced both transducers. Will monitor SCADA, to see if readings improve. ROC was notified before and after maintenance activities. | Holland Landing West Elevated Tank | 2026-02-23
WEST | February | Station checked, equipment checked and ok All measurements are in mg/l Time: 9:41 Free grab 0.02 Total grab 1.11, second reading 1.10, third reading 1.11, vs analyzer 1.55. Adjusted pre injection analyzer to match grab average Mono 0.27 Free ammonia 0.15 Total ammonia 0.2 Post injection Time 10:07 Total chlorine grab 3.61, 3.44 seconded grab, 3.41 third grab, vs analyzer 3.32. Adjusted analyzer to match grab average Free chlorine grab 0.00 Mono 2.58 Free ammonia 0.09 Total ammonia 0.60 Bottom of the bowl tower Total chlorine 1.68 Free chlorine 0.08 | Holland Landing West Elevated Tank | 2026-02-24
WEST | February | On-site for station check Reviewed scada and trends, duty active, ET @ 78% and filling @ 68 l/s Verified chlorine analyzers readings Visual inspection on instrumentation and equipment AOK Chemical pumps: Chlorine: Hypo pump #1 in duty1 and running at 32% speed Dose scada: 64:64 mL/min Hypo system pressure:440 kpa Ammonia: Pump2 in duty1 running 17% speed Dosing 17:45 mL/min P1 MAX flow = 98 mL/min P2 MAX flow = 98 mL/min Pump discharge pressure: 320 Chlorine grabs: @ 1438 hrs Tank Grabs: Analyzer reading TCL = 1.90 mg/l TCL = mg/l FCL = 0.06 mg/l FCL = mg/l Mono = 0.72 mg/l TA = 0.22 mg/l FA = 0.07mg/l Nitrite = 0.002 mg/l Temp = C Nitrate = Did grabs on Pre. Pre Grabs: @ 1430 hrs: Analyzer TCL = 1.31 TCL = 1.33 mg/l FCL = 0.06 FCL = 0.06 mg/l Mono = 0.53 mg/l TA = 0.27 mg/l FA = 0.13 mg/l Post/ Treated Sample Grab @ 1416 hrs Mono = 2.49 mg/l TA = 0.55 mg/l FA = 0.050 mg/l FCL = 0.03 mg/l Analyzer: FCL = 0.04 mg/l TCL = 3.30mg/l TCL = 3.34 mg/l Deactivated duty No issues | Holland Landing West Elevated Tank | 2026-02-27
WEST | February | Onsite to investigate and troubleshoot with ammonia pumps Reviewed SCADA, duty was active tower filing at 64 l/s ammonia p2 was in duty1 and running at 11% speed Did grab on post FA = 0.00 mg/l TA = 0.45 mg/l Mono = 2.27 mg/l FCL = 0.10 mg/l Analyzer: FCL = 0.05mg/l TCL = 3.38 mg/l TCL = 3.43 mg/l performed calibration test through the cal column, there was no flow through cal column. Cleaned check valves on both ammonia pumps and replaced tubing and changed pumps orientation, switched ammonia pump duties, placed p1 in duty1 and adjusted ammonia pump1 max flow from 95 down to 85 mL/min Collected another grab again, FA = 0.04 mg/l TA = 0.50 mg/l Mono = 2.46 mg/l No issues | Holland Landing West Elevated Tank | 2026-02-26
WEST | February | On-site for station check Reviewed scada and trends, duty active, Verified chlorine analyzers readings Visual inspection on instrumentation and equipment AOK Upon arrival duty was not active, tower at 85% and draining at 68 s/l Chemical pumps: Chlorine: Hypo pump #2 in duty1 and running at 36% speed Dose scada: 68.62 mL/min Hypo system pressure:440 kpa Ammonia: Pump2 in duty1 running 14% speed Dosing 23.05 mL/min P1 MAX flow = 125 mL/min P2 MAX flow = 120 mL/min Pump discharge pressure: 320 Chlorine grabs: @ 1456 hrs Tank Grabs: Analyzer reading TCL = 2.54 mg/l TCL = mg/l FCL = 0.04 mg/l FCL = mg/l Mono = 0.50 mg/l TA = 0.31 mg/l FA = 0.21 mg/l Nitrite = 0.002 mg/l Nitrate = 0.049 Did grabs on Pre. Pre Grabs: @ 1350 hrs: Analyzer TCL = 1.26 TCL = 1.28 mg/l FCL = 0.05 FCL = 0.05 mg/l Mono = 0.26 mg/l TA = 0.32 mg/l FA = 0.29 mg/l Post/ Treated Sample Grab @ 1407 hrs Mono = 2.56 mg/l TA = 0.45 mg/l FA = 0.04 mg/l FCL = 0.04 mg/l Analyzer: FCL = 0.03 mg/l TCL = 3.24 mg/l TCL = 3.28 mg/l Deactivated duty No issues | Holland Landing West Elevated Tank | 2026-02-02
WEST | February | On-site for station check and collection of weekly bacT samples Reviewed scada and trends, duty active, ET @ 78% and filling @ 64 l/s Verified chlorine analyzers readings Visual inspection on instrumentation and equipment AOK Chemical pumps: Chlorine: Hypo pump #1 in duty1 and running at 38% speed Dose scada: 43.09 mL/min Hypo system pressure:440 kpa Ammonia: Pump2 in duty1 running 8% speed Dosing 11:27 mL/min P1 MAX flow = 125 mL/min P2 MAX flow = 125 mL/min Pump discharge pressure: 320 Chlorine grabs: @ 1400 hrs Tank Grabs: Analyzer reading TCL = 2.40 mg/l TCL = mg/l FCL = 0.06 mg/l FCL = mg/l Mono = 0.72 mg/l TA = 0.22 mg/l FA = 0.08 mg/l Nitrite = 0.003 mg/l Temp = 6.9 C Nitrate = Did grabs on Pre. Pre Grabs: @ 1406 hrs: Analyzer TCL = 1.31 TCL = 1.29 mg/l FCL = 0.07 FCL = 0.06 mg/l Mono = 0.49 mg/l TA = 0.27 mg/l FA = 0.17 mg/l Post/ Treated Sample Grab @ 1416 hrs Mono = 2.29 mg/l TA = 0.41 mg/l FA = 0.00 mg/l FCL = 0.06 mg/l Analyzer: FCL = 0.08 mg/l TCL = 3.44 mg/l TCL = 3.48 mg/l Deactivated duty No issues | Holland Landing West Elevated Tank | 2026-02-25
WEST | February | On-site for station check and collection of weekly bacT and operational samples Reviewed scada and trends, not duty active, ET @ 71% and filling Verified chlorine analyzers readings Visual inspection on instrumentation and equipment AOK Chemical pumps: Chlorine: Hypo pump #1 in duty1 and running at 31% speed Dose scada: 58.00 mL/min Hypo system pressure:440 kpa Ammonia: Pump2 in duty1 running 12% speed Dosing 15:03 mL/min P1 MAX flow = 125 mL/min P2 MAX flow = 125 mL/min Pump discharge pressure: 320 Post/ Treated Sample Grab @ 15:40 hrs Mono = 2.24 mg/l TA = 0.49 mg/l FA = 0.04 mg/l FCL = 0.04 mg/l Analyzer: FCL = 0.02 mg/l TCL = 3.16 mg/l TCL = 3.20 mg/l | Holland Landing West Elevated Tank | 2026-02-11
WEST | February | Changed duty stop from 88 to 75% | Holland Landing West Elevated Tank | 2026-02-10
WEST | February | On-site for station check Reviewed scada and trends, duty active, ET @ 80% and filling @ 44 l/s Verified chlorine analyzers readings Visual inspection on instrumentation and equipment AOK Changed tower stop level from 88 to 80% for a little deep cycle | Holland Landing West Elevated Tank | 2026-02-20
WEST | February | On site to complete the following WO: Siemens Depolox 5/Micro 2000, Chlorine Analyzer, Maintenance, Sump Pit System Inspection, Manual Valve, Exercise, Sensing Line Heat Trace System, Maintenance Low Temperature Alarm, Test, Ammonia System Inspection Sodium Hypochlorite System Inspection Notified ROC prepared ammonia batch with 2 bags Cleaned and verified depolox 5 analyzers Cleaned hypo board and panel, ran pumps through cal column no adjustment required Tower filling, no issues Notified ROC before leaving site | Holland Landing West Elevated Tank | 2026-02-12
WEST | February | On-site for station check and collection of weekly bacT sample Reviewed scada and trends, duty active, ET @ 80% and filling @ 44 l/s Verified chlorine analyzers readings Visual inspection on instrumentation and equipment AOK Chemical pumps: Chlorine: Hypo pump #1 in duty1 and running at 22% speed Dose scada: 43.09 mL/min Hypo system pressure:440 kpa Ammonia: Pump2 in duty1 running 8% speed Dosing 11:27 mL/min P1 MAX flow = 125 mL/min P2 MAX flow = 125 mL/min Pump discharge pressure: 320 Chlorine grabs: @ 0844 hrs Tank Grabs: Analyzer reading TCL = 1.90 mg/l TCL = mg/l FCL = 0.07 mg/l FCL = mg/l Mono = 0.61 mg/l TA = 0.25 mg/l FA = 0.13 mg/l Nitrite = 0.003 mg/l Temp = 6.9 C Nitrate = Did grabs on Pre. Pre Grabs: @ 0830 hrs: Analyzer TCL = 1.35 TCL = 1.38 mg/l FCL = 0.07 FCL = 0.02 mg/l Mono = 0.38 mg/l TA = 0.27 mg/l FA = 0.20 mg/l Post/ Treated Sample Grab @ 08:20 hrs Mono = 1.97 mg/l TA = 0.44 mg/l FA = 0.05 mg/l FCL = 0.08 mg/l Analyzer: FCL = 0.03 mg/l TCL = 2.68 mg/l TCL = 2.71 mg/l Deactivated duty No issues | Holland Landing West Elevated Tank | 2026-02-17
WEST | February | On-site for station check Reviewed scada and trends, not duty active, ET @ 71% and filling Verified chlorine analyzers readings Visual inspection on instrumentation and equipment AOK | Holland Landing West Elevated Tank | 2026-02-13
WEST | February | On-site for station check Reviewed scada and trends, not duty active, Verified chlorine analyzers readings Visual inspection on instrumentation and equipment AOK Upon arrival duty was active, tower at 43% and draining at 57 s/l Chemical pumps: Chlorine: Hypo pump #2 in duty1 and running at 36% speed Dose scada: 68.62 mL/min Hypo system pressure:440 kpa Ammonia: Pump2 in duty1 running 14% speed Dosing 23.05 mL/min P1 MAX flow = 125 mL/min P2 MAX flow = 120 mL/min Pump discharge pressure: 320 Chlorine grabs: @ 0910 hrs Tank Grabs: Analyzer reading TCL = 1.42 mg/l TCL = mg/l FCL = 0.06 mg/l FCL = mg/l Mono = 0.53 mg/l TA = 0.21 mg/l FA = 0.17 mg/l Nitrite = 0.003 mg/l Nitrate = 0.038 mg/l Did grabs on Pre. Pre Grabs: @ 0850 hrs: Analyzer TCL = 1.33 TCL = 1.32 mg/l FCL = 0.06 FCL = 0.03 mg/l Mono = 0.26 mg/l TA = 0.26 mg/l FA = 0.21 mg/l Post/ Treated Sample Grab @ 0800 hrs Mono = 1.99 mg/l TA = 0.41 mg/l FA = 0.05 mg/l FCL = 0.06 mg/l Analyzer: FCL = 0.02 mg/l TCL = 3.18 mg/l TCL = 3.19 mg/l Deactivated duty No issues | Holland Landing West Elevated Tank | 2026-02-06
WEST | February | onsite for station check collected grabs on tank, analyze and recorded into pwq data sheet | Holland Landing West Elevated Tank | 2026-02-09
WEST | February | -on site to complete station check and weekly bacti W11620180 -checked trends: all ok -entered readings in PWQ: all ok -took chlorine grab and sample east cell 14:50 -free cl: 0.05mg/l -total cl: 1.98mg/l -west cell grab 14:55 -free cl: 0.06mg/l -total cl: 1.99mg/l -equipment all ok | Jefferson Pumping Station & Reservoir | 2026-02-25
WEST | February | On site to collect weekly bact sample (W). Tested chlorine residuals via hach field kit. Free: 0.04 mg/L Total: 1.68 mg/L | Holland Landing West Elevated Tank | 2026-02-03
WEST | February | Onsite for station check P1 oos P2 in man off P3&4 in service Checked residuals mg/l @1145 Total grab 1.85 Free grab 0.03 | Jefferson Pumping Station & Reservoir | 2026-02-23
WEST | February | -on site for station check -checked trends: all ok -entered readings in PWQ: all ok -took chlorine grab 08:05 -free cl: 0.07mg/l -total cl: 1.91mg/l -equipment all ok | Jefferson Pumping Station & Reservoir | 2026-02-27
WEST | February | -on site to complete station -checked trends: all ok -entered readings in PWQ: all ok -took chlorine grab 08:50 -free cl: 0.08mg/l -total cl: 1.91mg/l -equipment and heating all ok | Jefferson Pumping Station & Reservoir | 2026-02-02
WEST | February | -Ran the pumping station under generator due to unstable power supply - Diesel hours=658.7 Fuel=6045L | Jefferson Pumping Station & Reservoir | 2026-02-16
WEST | February | -Reset P3 & P4 fail to start , MV3 & MV4 fail to open alarm - alarm reset and pumps restarted in auto duty 1 | Jefferson Pumping Station & Reservoir | 2026-02-16
WEST | February | - on site to complete station for Res/Ps and weekly bacti W11605685 -checked trends: all ok -entered readings in PWQ: all ok -collected west cell sample and chlorine grab 08:55 -free cl: 0.09mg/l -total cl: 1.94mg/l -east cell sample 09:00 -free cl: 0.09mg/l -total cl: 1.98mg/p -equipment all ok -checked PS trends -entered reading in PWQ: all ok -took chlorine grab 09:15 -free cl: 0mg/l -total cl: 2.17mg/l -diesel is still running - informed supervisor diesel at 56% - order being placed -diesel all ok | Jefferson Pumping Station & Reservoir | 2026-02-17
WEST | February | On site for station check Check Trends: All okay Station Duty not Active Pump 1 OOS. 15:00- Grabs taken Free Cl2- 0.07 mg/L Total Cl2- 1.88 mg/L Entered values into PWQ sheet. Equipment okay. | Jefferson Pumping Station & Reservoir | 2026-02-12
WEST | February | -delivery did not show up -called driver delayed due to weather condition and went to wrong site | Jefferson Pumping Station & Reservoir | 2026-02-18
WEST | February | -on site for station check -checked trends: all ok -entered reading in PWQ: all ok -took chlorine grab 14:40 -free cl: 0.03mg/l -total cl: 1.96mg/l -equipment all ok | Jefferson Pumping Station & Reservoir | 2026-02-20
WEST | February | -on site to troubleshoot pump 2 valve fail to open -place pump 2 in local -exercise rotors valve -placed in duty 1 and tested: no issues -collected weekly bacti W11588844 and station check -chlorine grab and sample collect from east 08:45 -free cl: 0.06mg/l -total cl: 1.85mg/l -west cell 08:50 -free cl: 0.06mg/l -total cl: 1.90mg/l -equipment all ok | Jefferson Pumping Station & Reservoir | 2026-02-11
WEST | February | -on site to place generator back to auto -confirmed with ROC power restored -no issues | Jefferson Pumping Station & Reservoir | 2026-02-17
WEST | February | -on site to receive diesel delivery | Jefferson Pumping Station & Reservoir | 2026-02-18
WEST | February | Vibration readings Pump 2 loud Leaving pump 3 in duty | Jefferson Pumping Station & Reservoir | 2026-02-11
WEST | February | -on site to receive 4000L of diesel | Jefferson Pumping Station & Reservoir | 2026-02-18
WEST | February | Onsite for station check Duty active P1 oos Checked residuals mg/l @1048 Total grab 1.91 Free grab 0.06 | Jefferson Pumping Station & Reservoir | 2026-02-09
WEST | February | -On-site to complete reservoir station check and collect sample -reservoir level = 76%, draining -checked equipment -reviewed trends -collected grab samples: 09:22 - East Cell: Free Chlorine = 0.03 mg/L Total Chlorine = 2.05 mg/L 09:26 - West Cell: Free Chlorine = 0.01 mg/L Total Chlorine = 2.01 mg/L MCL = 1.78 mg/L TNH3 = 0.42 mg/L FNH3 = 0.07 mg/L NO2 = 0.000 mg/L temp = 5.7 09:30 - collected weekly regulatory micro. sample from West Cell - W/O # W11568536 -recorded readings in PWQ sheet -no issues found -completed work orders, informed ROC of work -completed JFRS, Sump Pit System Inspection, Jefferson RES -completed JFRS, Actuated Valve Exercise & Inspection, Jefferson RES -completed JFRS, Air Valve Flush & Inspection, Jefferson RES -completed JFRS, Dehumidifier Inspection & Cleaning, Jefferson RES -completed JFRS, External Venting Screens Inspection, Jefferson RES -completed JFRS, JHSC Health and Safety Inspection, Jefferson RES and BPS -completed JFRS, Ventilation System Inspection, Jefferson Valve House -completed JFRS, Sump Pit System Inspection, Jefferson Valve House -completed JFRS, Flood Alarm Test Jefferson Valve House -completed JFRS, Dehumidifier Inspection & Cleaning, Jefferson, Valve House -completed JFRS, Air Valves Flush & Inspection Jefferson, Valve House -completed JFPS, Standby Power Generator Test Run and Run Hours log, Jefferson WPS -pre inspection ok Start hours = 653.3 Stop hours = 654.5 Run time = 1.2 hours Start fuel = 6257 L Stop fuel = 6188 L Fuel used = 69 L 11:37 - transfer to generator power -activated system duty 12:46 - transfer back to utility power -completed JFPS, Low Temperature Alarm Test, Jefferson WPS -completed JFPS, Sump Pit System Inspection, Jefferson WPS -completed JFPS, Ventilation System Inspection, Jefferson WPS -completed JFPS, Dehumidifier Inspection & Cleaning, Jefferson WPS -completed JFPS, Pump & Motor Inspection, Jefferson WPS -completed JFPS, Actuated Valves Exercise & Inspection, Jefferson WPS -no issues, site back to normal operation | Jefferson Pumping Station & Reservoir | 2026-02-04
WEST | February | -on site to complete PS station check -system duty active -pump #1 OOS, pumps 2 and 4 running -checked equipment -reviewed trends -recorded readings in PWQ sheet -checked residuals: 14:02 - Grabs: Free Chlorine = 0.00 mg/L Total Chlorine = 2.18 mg/L -no issues found | Jefferson Pumping Station & Reservoir | 2026-02-06
WEST | February | Onsite for station check Check trends: All okay Station duty not active. 09:00- Grabs taken Grab free CL2- 0.04 mg/L Grab Total Cl2- 1.74 mg/L entered values in PWQ sheet Equipment okay | King City Dufferin Booster Pumping Station | 2026-02-27
WEST | February | Onsite for station check Check trends: All okay Station duty not active. 14:06- Grabs taken Grab free CL2- 0.02 mg/L Grab Total Cl2- 1.712 mg/L entered values in PWQ sheet Equipment okay | King City Dufferin Booster Pumping Station | 2026-02-23
WEST | February | Onsite for station check Check trends: All okay Station duty active; Pump 1 running 13:40- Grabs taken Grab free CL2- 0.04 mg/L Grab Total Cl2- 1.72 mg/L entered values in PWQ sheet Equipment okay | King City Dufferin Booster Pumping Station | 2026-02-02
WEST | February | Onsite for station check Check trends: All okay Station duty not active. reset pump 2 VFD fault on MCC panel 14:20- Grabs taken Grab free CL2- 0.02 mg/L Grab Total Cl2- 1.70 mg/L entered values in PWQ sheet Equipment okay | King City Dufferin Booster Pumping Station | 2026-02-20
WEST | February | Onsite for station check Check trends: All okay Station duty active; Pump 2 running. 09:00- Grabs taken Grab free CL2- 0.01 mg/L Grab Total Cl2- 1.67 mg/L entered values in PWQ sheet Equipment okay | King City Dufferin Booster Pumping Station | 2026-02-13
WEST | February | -on site to complete station check -system duty not active -checked equipment -reviewed trends -recorded readings in PWQ sheet -checked residuals: 12:49 - Grabs: Free Chlorine = 0.00 mg/L Total Chlorine = 1.87 mg/L -no issues found | King City Dufferin Booster Pumping Station | 2026-02-17
WEST | February | On site for Scheduled PM work orders given below. Informed ROC about the works being done W11602154 KCPSDS, JHSC Health and Safety Inspection W11602164 KCPSDS, Valve Exercise W11602257 KCPSDS, Critical Air Valve Flush and Inspection | King City Dufferin Booster Pumping Station | 2026-02-10
WEST | February | Onsite for station check Check trends: All okay Station duty not active 14:35 Grabs taken Grab free CL2- 0.02 mg/L Grab Total Cl2- 1.72 mg/L entered values in PWQ sheet Equipment okay | King City Dufferin Booster Pumping Station | 2026-02-06
WEST | February | Onsite for station check Check trends: All okay Station duty not active; 13:30- Grabs taken Grab free CL2- 0.04 mg/L Grab Total Cl2- 1.58 mg/L entered values in PWQ sheet Equipment okay | King City Dufferin Booster Pumping Station | 2026-02-09
WEST | February | on site to collect weekly bacti W11568288 and station check -checked trends: all ok - Tower draining- 63% -verified analyzer 14:00 -analyzer free: 0.04mg/l grab: 0.02mg/l -analyzer total: 1.70mg/l grab: 1.64mg/l -reagents all ok -entered reading in PWQ -equipment all ok | King City Dufferin Elevated Tank | 2026-02-25
WEST | February | Replaced Total and Free analyzer reagents | King City Dufferin Elevated Tank | 2026-02-02
WEST | February | On site to investigate inlet heat trace, chlorine rm exhaust fan, and meter chamber pump. ROC notified. Low temp. heat trace alarms cleared and RTD function verified. Heat trace system operational. Chlorine rm exhaust fan/damper is energized by light switch in addition to exhaust thermostat. Light and exhaust fan now separated and temperature control on heater and exhaust adjusted to avoid conflict. Meter chamber will be investigated in future. | King City Dufferin Elevated Tank | 2026-02-17
WEST | February | On site for scheduled PM workorders given below. Informed ROC about the works being done. W11571363 KCETDS, JHSC Health and Safety Inspection W11570892 KCETDS, Manual Valve, Exercise W11570910 KCETDS, Air Valve Flush & Inspection W11570940 KCETDS, Inlet/Outlet Heat Trace System, Inspection System fault, CMU created already W11570971 KCETDS, Actuated Valve, Exercise & Inspection W11571589 KCETDS, Dehumidifier, Cleaning & Inspection W11571862 KCETDS, Ventilation System, InspectionW11572030 KCETDS, Low Temperature Alarm Test Damper fail to close in cl2 room, informed team. W11570921 KCETDS, CL17 Chlorine Analyzer, Maintenance 14:00-Verified Treated Free & Total Analyzer Free cl2 Grab- 0.03 mg/L, Analyzer - 0.03 mg/L Total Cl2 Grab- 1.60 mg/L, Analyzer - 1.65 mg/L | King City Dufferin Elevated Tank | 2026-02-10
WEST | February | -On-site to complete station check and collect sample -system duty not active, tower = 57 % -checked equipment -reviewed trends -CL17 reagents ok -verified chlorine analyzers: 12:30 - Analyzer readings: Free Chlorine = 0.02 mg/L Total Chlorine = 1.69 mg/L 12:30 - Grabs: Free Chlorine = 0.02 mg/L Total Chlorine = 1.71 mg/L MCL = 1.64 mg/L TNH3 = 0.37 mg/L FNH3 = 0.05 mg/L temp = 5.9 C 12:37 - collected weekly regulatory micro. sample - W/O # W11605507 -recorded readings in PWQ sheet -no issues found -collected operational ATP and phosphorous samples | King City Dufferin Elevated Tank | 2026-02-17
WEST | February | Details: on site to collect weekly bacti W11588830 and station check -checked trends: all ok - Tower draining- 71% -verified analyzer 14:05 -analyzer free: 0.03mg/l grab: 0.02mg/l -analyzer total: 1.53mg/l grab: 1.53mg/l -reagents all ok -Heat trace unit reset. -entered reading in PWQ -equipment all ok | King City Dufferin Elevated Tank | 2026-02-11
WEST | February | on site to collect weekly bacti W11568288 and station check -checked trends: all ok - Tower draining- 54% -verified analyzer 14:05 -analyzer free: 0.03mg/l grab: 0.02mg/l -analyzer total: 1.70mg/l grab: 1.71mg/l -reagents all ok -entered reading in PWQ -equipment all ok | King City Dufferin Elevated Tank | 2026-02-04
WEST | February | Reset Heat trace Alarm in the Heat trace unit. Unable to clear from Scada. CMU W11650037 created | King City Dufferin Elevated Tank | 2026-02-09
WEST | February | On site for station check, W11620166 Micro Sampling Check Trends- All Okay Tower draining- 66% 13:20- Verified Analyzers Free Cl2 Grab - 0.05mg/L; Analyzer 0.02mg/L Total Cl2 Grab - 1.60 mg/L, Analyzer 1.64 mg/L Reagent all good. Samples collected Equipment Okay | King City Fisher Elevated Tank | 2026-02-25
WEST | February | -on site to repair chlorine room service water line -leaving line isolated to allow glue to dry | King City Dufferin Elevated Tank | 2026-02-03
WEST | February | Under the direction of Cole Warnica, Worked along side Network Analyst Aaron Magsakay, to replaced a Network switch to Cisco IE3300 inside a Network panel. Provided 24 VDC power to new switch from 24VDC power supply. There is a trend gap on SCADA between 12:30 PM to 12:45 PM due to this work. After the replacement, checked all the ports and reset the comm alarms. | King City Fisher Elevated Tank | 2026-02-20
WEST | February | -on site responding to power outage -site running on generator power | King City Fisher Elevated Tank | 2026-02-20
WEST | February | -On-site to complete station check and collect sample -system duty not active, tower = 62 % -checked equipment -reviewed trends -filled acetate buffer -verified chlorine analyzers: 11:26 - Analyzer readings: Free Chlorine = 0.03 mg/L Total Chlorine = 1.65 mg/L 11:26 - Grabs: Free Chlorine = 0.02 mg/L Total Chlorine = 1.60 mg/L SL1000 Readings: MCL = 1.51 mg/L TNH3 = 0.36 mg/L FNH3 = 0.06 mg/L NO2 = 0.000 mg/L temp = 5.3 C 11:34 - collected weekly regulatory micro. sample - W/O # W11605507 -recorded readings in PWQ sheet -no issues found -collected operational ATP and phosphorous samples | King City Fisher Elevated Tank | 2026-02-17
WEST | February | -on site to complete work orders -informed ROC of work -completed Low Temperature Alarm, Test -completed High & Low Water Level Alarm, Test -completed Inlet/Outlet Heat Trace System, Inspection -completed Sensing Line Heat Trace System, Inspection -completed PRV Valve, Inspection -completed Portable Gasoline Generator, Test -transferred PAC panel power to portable generator, no issues -filled generator fuel -completed JHSC Health and Safety Inspection -completed Siemens Depolox 5/Micro 2000, Chlorine Analyzer, Maintenance -verified analyzers after maintenance: 10:24 - Analyzer readings: Free Chlorine = 0.01 mg/L Total Chlorine = 1.58 mg/L 10:24 - Grabs: Free Chlorine = 0.02 mg/L Total Chlorine = 1.54 mg/L -no issues, site back to normal operation | King City Fisher Elevated Tank | 2026-02-12
WEST | February | Onsite to replace OIT computer. | King City Fisher Elevated Tank | 2026-02-10
WEST | February | Responded to PAC card alarms found issues with hardware. Replaced PAC power supply. OIT failed while at site. Repointed tag collection to H4AUSSP1 server and informed ROC to disregard historian heartbeat alarm | King City Fisher Elevated Tank | 2026-02-09
WEST | February | On site for station check, W11588830 Micro Sampling Check Trends- All Okay Tower draining- 75% 12:23- Verified Analyzers Free Cl2 Grab - 0.04mg/L; Analyzer 0.01mg/L Total Cl2 Grab - 1.53 mg/L(Avg- 1.50,1.53,1.57); Analyzer 1.40mg/L Adjudged total analyzer value up to 1.53 Reagent all good. Samples collected Equipment Okay | King City Fisher Elevated Tank | 2026-02-11
WEST | February | On site for station check, W11568288 Micro Sampling Check Trends- All Okay Tower draining- 55% 13:30- Verified Analyzers Free Cl2 Grab - 0.02mg/L; Analyzer 0.01mg/L Total Cl2 Grab - 1.60 mg/L; Analyzer 1.63mg/L Reagent all good. Samples collected Equipment Okay | King City Fisher Elevated Tank | 2026-02-04
WEST | February | On site for Station Check, W11620283 Micro Sampling Check Trends: All Okay Tower Draining (86%) 12:25- Grabs Taken FCL- 0.07 mg/L TCL- 1.91 mg/L Samples Taken. Entered Values in PWQ sheet. Equipment Okay. | Kleinburg Elevated Tank | 2026-02-25
WEST | February | On site for Station Check, W11605699 Micro Sampling Check Trends: All Okay Tower Draining (77%) 12:45- Grabs Taken FCL- 0.05 mg/L TCL- 2.00 mg/L Samples Taken. Entered Values in PWQ sheet. Equipment Okay. | Kleinburg Elevated Tank | 2026-02-17
WEST | February | On site for the following KLET27, JHSC Health and Safety Inspection, Kleinburg ET (1M) KLET27, Inlet/Outlet Heat Trace System, Inspection, Kleinburg ET (1M) [WINTER] KLET27, Gasoline Generator, Test Run, Kleinburg ET (1M) KLET27, Low Temperature Alarm, Test, Kleinburg ET (1M) [WINTER] KLET27, Dehumidifier, Cleaning & Inspection, Kleinburg ET (1M) No new issues | Kleinburg Elevated Tank | 2026-02-18
WEST | February | On site for Station Check, W11568550 Micro Sampling Check Trends: All Okay Tower Draining (73%) 12:35- Grabs Taken FCL- 0.04 mg/L TCL- 2.01 mg/L Samples Taken. Entered Values in PWQ sheet. Equipment Okay. | Kleinburg Elevated Tank | 2026-02-04
WEST | February | On site for Station Check, W11588947 Micro Sampling Check Trends: All Okay Tower Draining (88%) 14:00- Grabs Taken FCL- 0.04 mg/L TCL- 1.92 mg/L Samples Taken. Entered Values in PWQ sheet. Equipment Okay. | Kleinburg Elevated Tank | 2026-02-11
WEST | February | On site for Station Check. Check Trends: All okay Station Duty Active: Pump 1 & 2 active. 12:25-Verified Analyzers Free Cl2 Grab- 0.01mg/L Free Cl2 Analyzer- 0.03mg/L Total Cl2 Grab- 1.92 mg/L Total Cl2 Analyzer- 1.87mg/L Reagents All okay Entered values into PWQ sheet. Equipment Okay. | Kleinburg HWY 27 Booster Pumping Station | 2026-02-27
WEST | February | On site for Station Check. Check Trends: All okay Station Duty Active: Pump 1 & 2 active. 12:45-Verified Analyzers Free Cl2 Grab- 0.04mg/L Free Cl2 Analyzer- 0.02mg/L Total Cl2 Grab- 1.90 mg/L Total Cl2 Analyzer- 1.84mg/L Reagents All okay Entered values into PWQ sheet. Equipment Okay. | Kleinburg HWY 27 Booster Pumping Station | 2026-02-23
WEST | February | On site for Station Check. Check Trends: All okay Station Duty Active: Pump 1& 2 running 13:00-Verified Analyzers Free Cl2 Grab- 0.04mg/L Free Cl2 Analyzer- 0.02mg/L Total Cl2 Grab- 2.06 mg/L Total Cl2 Analyzer- 1.99mg/L Reagents All okay Entered values into PWQ sheet. Equipment Okay. | Kleinburg HWY 27 Booster Pumping Station | 2026-02-02
WEST | February | On site for Station Check. Check Trends: All okay Station Duty Active: Pump 2 & 3 active. 12:25-Verified Analyzers Free Cl2 Grab- 0.04mg/L Free Cl2 Analyzer- 0.02mg/L Total Cl2 Grab- 1.90 mg/L Total Cl2 Analyzer- 1.86mg/L Reagents All okay Entered values into PWQ sheet. Equipment Okay. | Kleinburg HWY 27 Booster Pumping Station | 2026-02-20
WEST | February | On site for Station Check. Check Trends: All okay Station Duty not Active 12:20-Verified Analyzers Free Cl2 Grab- 0.03mg/L Free Cl2 Analyzer- 0.03mg/L Total Cl2 Grab- 1.96 mg/L Total Cl2 Analyzer- 1.98mg/L Reagents All okay Entered values into PWQ sheet. Equipment Okay. | Kleinburg HWY 27 Booster Pumping Station | 2026-02-17
WEST | February | On site for the following PM workorders, Informed ROC about the works being done W11582972 KLPS27, JHSC Health and Safety Inspection, W11583371 KLPS27, Low Temperature Alarm, Test, W11583417 KLPS27, Header Suction and Discharge Valve, Exercise, W11583526 KLPS27, Pump Suction and Discharge Valve, Exercise W11583691 KLPS27, Kleinburg WPS - KLPS27, Critical Air Valve Flush and Inspection (1M) W11583384 KLPS27, Sump Pit System, Inspection W11583400 KLPS27, Storm Sump Pump, Maintenance W11583667 KLPS27, Bypass Valve Actuator, Exercise & Inspection, W11583776 KLPS27, Pressure Relief Valve, Inspection W11583734 KLPS27, Flood Alarm, Test, Kleinburg, W11584095 KLPS27, Hoist, Inspection, Kleinburg, WPS W11582982 KLPS27, Chlorine Analyzer, Maintenance, Kleinburg W11594142 KLPS27, Kleinburg Booster BPS, Station Check Check Trends: All okay Station Duty not Active Entered values into PWQ sheet. Equipment Okay.13:50-Verified Analyzers Free cl2 Grab- 0.03 mg/L, Analyzer - 0.03 mg/L Total Cl2 Grab- 1.99 mg/L, Analyzer - 1.92 mg/L Topped up both KI and Acetate reagents. | Kleinburg HWY 27 Booster Pumping Station | 2026-02-12
WEST | February | On site for Station Check. Check Trends: All okay Station Duty Active: Pump 1& 3 running 13:00-Verified Analyzers Free Cl2 Grab- 0.03mg/L Free Cl2 Analyzer- 0.03mg/L Total Cl2 Grab- 2.04 mg/L Total Cl2 Analyzer- 1.97mg/L Reagents All okay Entered values into PWQ sheet. Equipment Okay. | Kleinburg HWY 27 Booster Pumping Station | 2026-02-06
WEST | February | On site for Station Check. Check Trends: All okay Station Duty Active: Pump 1& 2 running 12:10-Verified Analyzers Free Cl2 Grab- 0.04mg/L Free Cl2 Analyzer- 0.02mg/L Total Cl2 Grab- 2.04 mg/L Total Cl2 Analyzer- 1.95mg/L Reagents All okay Entered values into PWQ sheet. Equipment Okay. W11585332- Washroom cleaning complete | Kleinburg HWY 27 Booster Pumping Station | 2026-02-09
WEST | February | On site for station check Check trends: All okay Ran pump 1 & 2 locally for 15 minutes 11:20- Verified Analyzers Grab free Cl2- 0.01 mg/L Analyzer free Cl2- 0.05 mg/L Grab Total Cl2- 1.87 mg/L Analyzer Total Cl2- 1.88 mg/L Reagents all good. entered values into PWQ sheet Equipment okay. | Kleinburg Whisper Lane Booster Pumping Station | 2026-02-23
WEST | February | On site for station check Check trends: All okay 13:15- Verified Analyzers Grab free Cl2- 0.02 mg/L Analyzer free Cl2- 0.06 mg/L Grab Total Cl2- 1.85 mg/L (AVG -1.85,1.85,1.83) Analyzer Total Cl2- 1.70 mg/L Adjusted analyzer up to 1.80 mg/L Reagents all good. entered values into PWQ sheet Equipment okay. | Kleinburg Whisper Lane Booster Pumping Station | 2026-02-27
WEST | February | On site for station check Check trends: All okay Ran pump 1 & 2 locally for 15 minutes 12:00- Verified Analyzers Grab free Cl2- 0.05 mg/L Analyzer free Cl2- 0.06 mg/L Grab Total Cl2- 2.03 mg/L Analyzer Total Cl2- 1.98 mg/L Replaced KI reagent. entered values into PWQ sheet Equipment okay. | Kleinburg Whisper Lane Booster Pumping Station | 2026-02-02
WEST | February | -on site for station check -checked trends: all ok -entered readings in PWQ: all ok - verified analyzer 09:55 -analyzer free: 0.05mg/l grab: 0.07mg/l -analyzer total: 1.81mg/l grab: 1.88mg/l - adjusted -topped up acetate at KLPSWL and KLW3/4 -equipment all ok | Kleinburg Whisper Lane Booster Pumping Station | 2026-02-12
WEST | February | On site for station check Check trends: All okay Ran pump 1 & 2 locally for 15 minutes 11:20- Verified Analyzers Grab free Cl2- 0.05 mg/L Analyzer free Cl2- 0.04 mg/L Grab Total Cl2- 1.85 mg/L Analyzer Total Cl2- 1.82 mg/L Reagents all good. entered values into PWQ sheet Equipment okay. | Kleinburg Whisper Lane Booster Pumping Station | 2026-02-20
WEST | February | On site for station check Check trends: All okay Ran pump 1 & 2 locally for 15 minutes 11:05- Verified Analyzers Grab free Cl2- 0.01 mg/L Analyzer free Cl2- 0.05 mg/L Grab Total Cl2- 2.02 mg/L Analyzer Total Cl2- 1.95 mg/L Reagent all good entered values into PWQ sheet Equipment okay. | Kleinburg Whisper Lane Booster Pumping Station | 2026-02-09
WEST | February | On site for station check Check trends: All okay Ran pump 1 & 2 locally for 15 minutes 14:10- Verified Analyzers Grab free Cl2- 0.05 mg/L Analyzer free Cl2- 0.06 mg/L Grab Total Cl2- 1.97 mg/L Analyzer Total Cl2- 1.96 mg/L Topped up Acetate. entered values into PWQ sheet Equipment okay. | Kleinburg Whisper Lane Booster Pumping Station | 2026-02-17
WEST | February | Onsite for the following PM Work orders. Informed ROC about the works being done. W11571876- High/Low temp Alarm test W11571889 - Flood Alarm test W11572068- Siemens Depolox 5/Micro 2000, Chlorine Analyzer, Maintenance 14:35-Verified Analyzer Free cl2 Grab- 0.04 mg/L, Analyzer - 0.06 mg/L Total Cl2 Grab- 1.90 mg/L, Analyzer - 1.84 mg/L | Kleinburg Whisper Lane Booster Pumping Station | 2026-02-03
W-MAINT | February | Station check Well 3 and 8 in manual 11.1 l/s Totals well pump 8 - 11 hrs. Total 35137 Well pump 13 - 11 hrs Total 34464 Well 8 RPM 2450 Well 13 RPM 2112 | Major MacKenzie and Newkirk Road Dewatering Wells | 2026-02-06
WEST | February | On site for station check Check trends: All okay Ran pump 1 & 2 locally for 15 minutes 11:40- Verified Analyzers Grab free Cl2- 0.05 mg/L (avg-0.05,0.07,0.02) Analyzer free Cl2- 0.12 mg/L Adjusted analyzer down to 0.05 Grab Total Cl2- 1.92 mg/L Analyzer Total Cl2- 1.88 mg/L Reagent all good. entered values into PWQ sheet Equipment okay. | Kleinburg Whisper Lane Booster Pumping Station | 2026-02-06
WEST | February | -on site for station check and weekly bacti W11620190 -checked trends: all ok -entered readings in PWQ: all ok -took sample and chlorine grab east cell 09:55 -free cl: 0.05mg/l -total cl: 1.66mg/l -west cell chlorine grab 10:00 -free cl: 0.07mg/l -total cl: 1.64mg/l -equipment all ok | Maple North Reservoir | 2026-02-25
WEST | February | -on site to complete work orders -informed ROC of work -completed JHSC Health and Safety Inspection -found eyewash booster pump pressure gauge not working, created follow up work order to replace gauge and verify pressure switches. Leaving booster pump off for now -completed Sump Pump, Inside Inspection & Maintenance | Maple North Reservoir | 2026-02-10
WEST | February | -On-site to complete station check and collect sample -reservoir level = 66 %, filling -checked equipment -reviewed trends -collected grab samples: 10:40 - East Cell: Free Chlorine = 0.02 mg/L Total Chlorine = 1.70 mg/L 10:43 - West Cell: Free Chlorine = 0.01 mg/L Total Chlorine = 1.65 mg/L MCL = 1.51 mg/L TNH3 = 0.37 mg/L FNH3 = 0.07 mg/L NO2 = 0.001 mg/L temp = 7.0 10:46 - collected weekly regulatory micro. sample from West Cell - W/O # W11605685 -recorded readings in PWQ sheet -no issues found -collected operational ATP and phosphorous samples | Maple North Reservoir | 2026-02-17
WEST | February | -on site for station check and weekly bacti W11588844 -east cell chlorine grab 10:30 -free cl: 0.05mg/l -total cl: 1.60mg/l -west cell chlorine 10:35 -free cl: 0.08mg/l -total cl: 1.56mg/l -equipment all ok | Maple North Reservoir | 2026-02-11
WEST | February | Check pressure on pump for eyewash | Maple North Reservoir | 2026-02-18
WEST | February | -on site for station check and weekly bacti W11568536 -checked trends: all ok -entered readings in PWQ: all ok -took grab and sample from West cell 09:45 -free cl: 0.11mg/l -total cl: 1.71mg/l -east cell grab 09:50 -free cl: 0.06mg/l -total cl: 1.67mg/l -equipment all ok | Maple North Reservoir | 2026-02-04
WEST | February | -on site to reset PD8 pump 3 -no issues - alarms reset | Maple Pumping Station | 2026-02-25
WEST | February | Onsite for station check Checked residuals mg/l Pd7 @1010 Total analyzer 1.67 grab 1.67 Free grab 0.06 Pd8 Cl2 analyzer isolated trends erratic | Maple Pumping Station | 2026-02-23
WEST | February | Removed spool piece on PD7 pump 4, disassembled check valve on discharge side of pump to determine root cause of the issue. Pump 4 will remain out of service until parts arrive. Ops notified. | Maple Pumping Station | 2026-02-25
WEST | February | -on site to receive 10 000L of diesel -no issues | Maple Pumping Station | 2026-02-26
WEST | February | -on site for station check -checked trends: all ok -entered readings in PWQ: all ok -verified PD7 analyzer 13:45 -analyzer free: 0.03mg/l grab: 0.06mg/l -analyzer total: 1.69mg/l grab: 1.69mg/l -PD8 analyzer offline -PD8 pump 4 multin warning alarm - unable to reset W11695175 -equipment all ok | Maple Pumping Station | 2026-02-27
WEST | February | On site to remove and replace cooling fans for PD8 VFDs 1-3. Tested all VFDs for proper operation. | Maple Pumping Station | 2026-02-02
WEST | February | -on site for station check -checked trends: -entered readings in PWQ: all ok -verified PD7 analyzer 13:35: -analyzer free: 0.04mg/l grab: 0.07mg/l -analyzer total: 1.73mg/l grab: 1.71mg/l -verified PD8 analyzer 13:45: -analyzer free: 0.04mg/l grab: 0.05mg/l -analyzer total: 1.44mg/l grab: 1.43mg/l -equipment all ok and heating all ok | Maple Pumping Station | 2026-02-02
WEST | February | -spoke with Dwayne Lewis who is on site- PD8 suction main isolated - PD8 analyzer will be offline for 2-3 weeks during isolation | Maple Pumping Station | 2026-02-20
WEST | February | -on site to complete work orders -informed ROC of work -completed Air Handling Units, Inspection & Maintenance -found broken belt in AHU3 blower - removed belt and will source a replacement -completed JHSC Health and Safety Inspection -completed Diesel Flood Alarm, Test -completed Fuel Transfer Pump Control Panel, Test -completed AC Units 1-4 (Backup) Test Run | Maple Pumping Station | 2026-02-10
WEST | February | Pump 4 check valve | Maple Pumping Station | 2026-02-18
WEST | February | -on site for station check -checked trends: all ok -entered reading in PWQ: all ok -verified PD7 analyzer 13:10 -analyzer free: 0.04mg/l grab: 0.07mg/l -analyzer total: 1.77mg/l grab: 1.67mg/l - adjusted -verified PD8 analyzer 13:15 -analyzer free: 0.04mg/l grab: 0.08mg/l -analyzer total: 1.41mg/l grab: 1.40mg/l - tested PD7 pumps 1&4 due to high differential switch alarms -flushed transmitter and exercised valves -pump 1 all ok pump 4 oos | Maple Pumping Station | 2026-02-12
WEST | February | -received call about high PD8 chlorine alarms -informed to disregard - suction header isolated/ analyzer isolated | Maple Pumping Station | 2026-02-20
WEST | February | -on site to troubleshoot PD7 pump pressure differential alarms with Dan Boate -manually and locally started pump 1 - 4 -pump 4 check valve is seized shut - placed in local off -informed team lead and supervisor of incorrect alarming -investigating time delay option | Maple Pumping Station | 2026-02-18
WEST | February | -on site for station check -checked trends: all ok -entered readings in PWQ: all ok -verified PD7 analyzer 10:20 -analyzer free: 0.03mg/l grab: 0.06mg/l -analyzer total: 1.62mg/l grab: 1.69mg/l - adjusted -verified PD8 analyzer 10:25 -analyzer free: 0.05mg/l grab: 0.06mg/l -analyzer total: 1.70mg/l grab: 1.67mg/l -equipment all ok -linear on site draining PD8 header - -PD8 may fail during draining - analyzer not being directed to user | Maple Pumping Station | 2026-02-20
WEST | February | Vibration readings | Maple Pumping Station | 2026-02-11
WEST | February | -on site for station checked trends - start time: 482.7/496.5 -stop time: 484/497.7 -diesel level: -sump pit inspection: all ok -hoist inspection: all ok -screen inspection: all ok | Maple Pumping Station | 2026-02-10
WEST | February | -on site to complete station check -checked equipment -reviewed trends -recorded readings in PWQ sheet Verified analyzers: 09:31 - PD7 Analyzer readings: Free Chlorine = 0.04 mg/L Total Chlorine = 1.63 mg/L 09:31 - PD7 Grabs: Free Chlorine = 0.04 mg/L Total Chlorine = 1.67 mg/L 09:39 - PD8 Analyzer readings: Free Chlorine = 0.06 mg/L Total Chlorine = 1.72 mg/L 09:39 - PD8 Grabs: Free Chlorine = 0.03 mg/L Total Chlorine = 1.61/1.61/1.61 mg/L 09:49 - adjusted PD8 total chlorine analyzer to 1.61 mg/L based on average of 3 grabs -no other issues found | Maple Pumping Station | 2026-02-17
WEST | February | On site to troubleshoot pressure differential issues with PD7 P1 and P4. Found check valve stuck closed on P4. Could not find any problem with P1. | Maple Pumping Station | 2026-02-18
WEST | February | Informed ROC. Onsite to perform annual maintenance/calibrations. Devices were done as below: MAP8 AITs, MAP8 Suction and discharge PIT. Used the calibration mode. Took multiple grab samples. No adjustments required. MAP8 Total AIT A - 1.42 mg/l G - 1.43 mg/l. MAP8 Free AIT A- 0.07 mg/l G - 0.07 mg/l. Put all the devices back in service. All the related alarms were cleared. No issues. Informed ROC and left the site. | Maple Pumping Station | 2026-02-04
WEST | February | -on site to complete station check -PD7 and PD8 duties not active -checked equipment -reviewed trends -recorded readings in PWQ sheet Verified analyzers: 12:02 - PD7 Analyzer readings: Free Chlorine = 0.10 mg/L Total Chlorine = 1.62 mg/L 12:02 - PD7 Grabs: Free Chlorine = 0.05/0.04/0.04 mg/L Total Chlorine = 1.69/1.72/1.71 mg/L 12:09 - adjusted PD7 free chlorine analyzer to 0.04 mg/L based on average of 3 grabs 12:12 - adjusted PD7 total chlorine analyzer to 1.71 mg/L based on average of 3 grabs 12:14 - PD8 Analyzer readings: Free Chlorine = 0.05 mg/L Total Chlorine = 1.45 mg/L 12:14 - PD8 Grabs: Free Chlorine = 0.03 mg/L Total Chlorine = 1.44 mg/L -no other issues found | Maple Pumping Station | 2026-02-06
WEST | February | -on site to complete station checked trends -checked trends: all ok -entered readings in PWQ: all ok -verified PD7 analyzer 12:40 -analyzer free: 0.05mg/l grab: 0.05mg/l -analyzer total: 1.60mg/l grab: 1.72mg/l - adjusted -verified PD8 analyzer 12:50 -analyzer free: 0.07mg/l grab: 0.10mg/l -analyzer total:1.63mg/l grab: 1.70mg/l - adjusted -equipment all ok | Maple Pumping Station | 2026-02-09
WEST | February | Informed ROC. Onsite to perform annual maintenance/calibrations. Devices were done as below: MAP7 and MAP8 FIT, MAP7 AITs, MAP7 Suction and discharge PIT. Used the calibration mode. Took multiple grab samples. adjusted analyzers accordingly. MAP7 Total AIT A - 1.68 mg/l G - 1.67 mg/l. MAP7 Free AIT A- 0.08 mg/l G - 0.09 mg/l. Put all the devices back in service. All the related alarms were cleared. No issues. Informed ROC and left the site. | Maple Pumping Station | 2026-02-05
WEST | February | On site to continue wiring for PD8 VFD remote reset signals. | Maple Pumping Station | 2026-02-06
WEST | February | Took grab in reservoir of isolated section mg/l @1052 Total grab 1.07 Free grab 0.03 | Maple South Reservoir | 2026-02-23
WEST | February | On site to investigate wiring and schematical details of connecting each PD8 VFD to a remote scada reset signal. | Maple Pumping Station | 2026-02-03
WEST | February | On site to continue work on PD8 VFD remote reset signal connections. | Maple Pumping Station | 2026-02-04
WEST | February | -on site to freshen up isolated metro line -took chlorine grab 11:15- -free cl: 0.03mg/l -total cl: 0.95mg/l -activated BVPS -opened interconnect valve quarter way -opened site valve 6 turns - 15l/s -took chlorine grab 11:45 -free cl: 0.05mg/l -grab: 0.86mg/l -will monitor | Maple South Reservoir | 2026-02-26
WEST | February | -on site for station check and weekly bacti W11620180 -check trends: all ok -entered reading in PWQ: all ok -took sample and chlorine grab north cell 08:50 -free cl: 0.06mg/l -total cl: 1.69mg/l -verified peel analyzer 08:55 -analyzer 1.71mg/l grab: 1.68mg/l -reagents all ok -verified metro analyzer 09:00 -analyzer free: 0.02mg/l grab: 0.04mg/l -analyzer total: 1.66mg/l grab: 1.67mg/l -construction on going | Maple South Reservoir | 2026-02-25
WEST | February | YPFM to PD8 suction chlorine analyzer (WPS SUCH1 AIT1) powered off, isolated and placed OOS. YPFM is isolated from system during shipwell project works, analyzer not currently sampling from system / no sample flow to analyzer. Shelved outstanding alarms associated with analyzer (other than HMA, out of range). | Maple South Reservoir | 2026-02-23
WEST | February | -on site to complete work orders -informed ROC of work -completed Isolating Valve Box Cover, Inspection -completed JHSC health and safety inspection -completed Sump Pump Inspection -tested flood alarm -completed Chlorine Analyzer Maintenance: -filled electrolyte and grit sand in metro depolox analyzer -cleaned Peel CL17 and flushed sample lines -verified analyzers after maintenance: 09:29 - Metro Analyzer readings: Free Chlorine = 0.13 mg/L Total Chlorine = 1.38 mg/L 09:29 - Metro Grabs: Free Chlorine = 0.02/0.02/0.01 mg/L Total Chlorine = 1.63/1.62/1.60 mg/L 09:37 - adjusted metro free chlorine analyzer to 0.02 mg/L based on average of 3 grabs 09:40 - adjusted metro total chlorine analyzer to 1.62 mg/L based on average of 3 grabs 09:41 - Peel TCL analyzer = 1.63 mg/L 09:41 - Peel TCL grab = 1.61 mg/L -completed 3 Tonne Hoist, Inspection -completed Ventilation & Dehumidifier, Maintenance -site back to normal operation | Maple South Reservoir | 2026-02-10
WEST | February | -On-site to complete station check and collect sample -South Cell OOS -reservoir level = 82%, filling -checked equipment -reviewed trends -analyzer reagents ok -verified Peel Total Chlorine Analyzer: 08:55 - Peel TCL analyzer = 1.71 mg/L 08:55 - Peel FCL grab = 0.00 mg/L Peel TCL grab = 1.70 mg/L -verified Metro chlorine analyzers: 08:56 - Analyzer readings: Free Chlorine = 0.02 mg/L Total Chlorine = 1.69 mg/L 08:56 - Grabs: Free Chlorine = 0.01 mg/L Total Chlorine = 1.72 mg/L -collected grab samples: 09:02 - North Cell: Free Chlorine = 0.02 mg/L Total Chlorine = 1.71 mg/L MCL = 1.62 mg/L TNH3 = 0.37 mg/L FNH3 = 0.05 mg/L NO2 = 0.000 mg/L temp = 3.7 09:05 - collected weekly regulatory micro. sample from North cell - W/O # W11605685 -recorded readings in PWQ sheet -no issues found -collected operational ATP and phosphorous samples | Maple South Reservoir | 2026-02-17
WEST | February | -on site to complete station check and weekly W11588844 -checked trends: all ok -entered readings in PWQ: all ok -verified peel analyzer 09:50: 1.56mg/l grab:1.54mg/l -reagents all ok -took chlorine grab and sample from north cell 09:55 -free cl: 0.08mg/l -total cl: 1.55mg/l -verified metro analyzer 10:00 -analyzer free: 0.02mg/l grab: 0.04mg/l -analyzer total: 1.56mg/l grab: 1.54mg/l -construction on going | Maple South Reservoir | 2026-02-11
WEST | February | -on site for station check and weekly bacti W11568536 -checked trends: all ok -entered readings in PWQ: all ok -verified Peel analyzer 08:30 -analyzer: 1.73mg/l grab: 1.70mg/l -reagents all ok -north cell grab 08:35 -free cl: 0.03mg/l -total cl: 1.66mg/l -verified metro analyzer 08:40 -analyzer free: 0.03mg/l grab: -analyzer total: 1.74mg/l grab: -construction on going -no issues | Maple South Reservoir | 2026-02-04
WEST | February | Onsite for annual calibrations Informed ROC Needed to complete site orientation with Torbear and verify that completed safety training is up to date. Continued with calibrations Completed reservoir inlet FITs South reservoir OOS. Completed LIT calibration Ask ROC for permission to proceed with North reservoir LIT calibration. ROC made some calls and granted permission. Completed North reservoir LIT calibration. Informed ROC immediately after completion Will return to continue calibrations next week Informed ROC. Signed out from Torbear Left site No issues upon leaving | Maple South Reservoir | 2026-02-06
WEST | February | Informed ROC. Onsite to perform annual maintenance/calibrations. Used calibration mode. Devices were done as below : Generator room LITs, RES_INLT1_AIT1, RES_INLT2_AIT1, RES_INLT2_AIT2 Took a multiple grab samples and adjusted analyzers accordingly. AL RES_INLT1_AIT1 A- 1.60 mg/l G- 1.62 mg/l AL RES_INLT2_AIT1 A - 1.62 mg/l G - 1.62 mg/l AL RES_INLT2_AIT2 A - 0.13 mg/l G - 0.13 mg/l Put all devices back in service. All the related alarms were cleared. No issues. Informed ROC and left the site. | Maple South Reservoir | 2026-02-09
WEST | February | On site to test isolation of MARS south cell, south inlet outlet piping for next stage of project works. Linear isolate Keele 900 PD6 isolation to South Cell at t0304-01 and T0564-01. Isolate pipe gallery interconnect valve, confirm isolation of 3? gv on washdown line. Install gauge on south cell inlet outlet air valve to monitor pressure after isolation. Currently at approximately 3psi. | Maple South Reservoir | 2026-02-09
CENTRAL | February | Station Check (no issues found) Input data to PWQ 13:35 Verified Depolox (mg/L) Free: Grab 0.02, A 0.02 Total: Grab 2.70, A 2.62 13:45 #11620724 bact. sample | Newmarket (East) Harry Walker Elevated Tank | 2026-02-25
CENTRAL | February | Station Check (no issues found) Input data to PWQ 3:00 Verified Depolox (mg/L) Free: Grab 0.04, A 0.03 Total: Grab 2.86, A 2.83 3:10 #11605447 bact. & operational samples taken Depolox (new KI/distilled) OIT not working | Newmarket (East) Harry Walker Elevated Tank | 2026-02-17
CENTRAL | February | Station and equipment check Take weekly BacT sample W11589399 and grabs @ 13:15 Total: 2.68 mg/l Free: 0,02 mg/l *standardized analyzer to match grabs Reagents ok All other readings on PD sheets Utilized laptop for data entry ET ops normal | Newmarket (East) Harry Walker Elevated Tank | 2026-02-11
CENTRAL | February | Station and equipment check Take weekly BacT sample W11568241 and grabs @ 8:00 am Total: 2.80 mg/l Free: 0.03 mg/l Analyzer Total: 2.96 mg/l Analyzer Free: 0.03 mg/l *standardized analyzer to match grabs Reagents ok ET ops normal | Newmarket (East) Harry Walker Elevated Tank | 2026-02-04
CENTRAL | February | Attending site to check chlorine analyzer issue (W11634388). Found leaking at sample pump peristaltic tubing. Replaced all pump tubing and calibrated to 2.77mg/L Total chlorine based on average of three grabs. ROC was notified before and after maintenance activities. | Newmarket (East) Harry Walker Elevated Tank | 2026-02-03
CENTRAL | February | Onsite to complete monthly maximo workorders Informed ROC (Angelica/Connor) Added acetate to Depolox 5 @ 9:00 am Took grabs to verify readings @ 9:10 am Total: 3.00 mg/l Free: 0.03 mg/l hihi analyzer reading came in at approximately 9:12 am possibly from acetate top up and air bubble Readings returned to normal Re took grabs @ 10:00 am Total: 2.80 mg/l Free: 0.02 mg/l *standardized analyzer to match grabs Completed all other workorders no issues ET ops normal | Newmarket (East) Harry Walker Elevated Tank | 2026-02-03
CENTRAL | February | Onsite to respond to riser pipe heat trace fault: Ensured continuous flow through riser pipe to prevent freezing Confirmed heat trace active- heater on at 100% No abnormalities with level trending Station/equipment- Ok | Newmarket (East) Harry Walker Elevated Tank | 2026-02-07
CENTRAL | February | Station and equipment check Top up both Hypo day tanks Took grabs @ 1:45 pm from post (draining) Header Total: 3.30 mg/l Header Free: 0.05 mg/l Alll other readings on PD sheets Chemicals/reagents ok Ops normal | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2026-02-27
CENTRAL | February | Station and equipment check Tank draining took grabs from post @ 13:10 Header Total: 3.26 mg/l Header Free: 0.05 mg/l Topped up both hypo day tanks Chemicals/reagents ok Contractor onsite backfilling previously excavated trench, no assistance required from ops Ops normal | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2026-02-23
CENTRAL | February | Station Check (no other issues found) Input data to pwq Verified CL17s (mg/l) Pre: (Header) Free: Grab 0.03, A 0.02 Total: Grab 1,73, A 1.74 Post: (Inlet) Free: Grab 0.03, A 0.02 Total: Grab 1.80, A 1.87 Ammonia Mixer #1 not working Ammonia Tank #2 (new batch) | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2026-02-25
CENTRAL | February | Receive 350 L of Hypo Ops normal | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2026-02-24
CENTRAL | February | Station and equipment check Tank filling at time of readings Grabs @ 9:15 am Inlet Total: 2.28 mg/l Inlet Free: 0.04 mg/l All other readings on PD sheets Chemicals/reagents ok Ops normal | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2026-02-02
CENTRAL | February | Informed ROC (Angelica) would be completing monthly Maximo workorders Place ALL analyzers in CAL mode and chemscan unit offline to conduct hot water flush of supply lines to analyzers Also turned manual OFF chlorine/ammonia pumps Tank currently filling Hot water flush from 8:15 am - 9:15 am Returned all analyzers to ?in service? aprox 9:30 am (all readings accurate) Wash down VC1 floor Tested sanitary hi level float ack/reset alarm Teated sanitary sump pumps both ok Visual inspection of hypo pumps and conducted drawdown of ammonia pumps after p1 failed to start (one off) all ok Ops normal | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2026-02-18
CENTRAL | February | Contractor finished temporary domestic water service Opened mainstop at 1:15 pm and flushed temporary service for debris, ran clear right away with air gap Isolated service @ 1:30 pm so that plumber can tie into building services Opened mainstop @ 2:15 pm and flushed all building services for approximately 15 min, all ran clear Took grab @ 2:30 from sink in chlorine room Total: 2.70 mg/l Free: 0.05 mg/l Domestic water back in service Informed ROC Angelica eye wash station test and flush all ok Ops normal | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2026-02-13
CENTRAL | February | Onsite to assist with flushing of temporary water service Opened curbstop at aprox. 8:45 am and found small leak at first coupling, turned back off Waiting on plumber Coupling tightened and failed leak test again, will require new coupling Water service remains OFF Ops otherwise normal | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2026-02-12
CENTRAL | February | Station and equipment check Contractors onsite working on upgrades Took grabs from ?Post? as tank filling Inlet Total: 2.20 mg/l Inlet Free: 0.04 mg/l Reagents ok Topped up both hypo day tanks Topped up Ammonia tank 2 Ops normal | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2026-02-13
CENTRAL | February | Station Check (no issues found) Input data to PWQ Verified CL17s (mg/L) 1:34 PRE Free: Grab 0.04, A 0.01 Total: Grab 1.72, A 1.80 1:50 POST Free: Grab 0.03, A 0.04 Total: Grab 3.13, A 3.19 Ammonia tank #1 (new batch) (may have been switched prematurely (level high but ok)) Hypo tank #2 top up Contractor on site Chemscan (distilled top up) | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2026-02-20
CENTRAL | February | Station Check (no issues found) Input data to PWQ Verified CL17s 12:46 Post/Header (Draining) Free: Grab 0.04, A 0.04 Total: Grab 3.20, A 3.19 12:51 Pre/Outlet (Draining) Free: Grab 0.03, A 0.01 Total: Grab 1.80, A 1.89 13:20 #11605447 bact. & operational samples taken Bulk Hypo delivery accepted | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2026-02-17
CENTRAL | February | Onsite to investigate w/ Ian W (PCS) problem with ups while running Kirby ps diesel generator. During transfer lose comms and analyzer readings Chemical system turned off during test and analyzer readings remained stable, may have to reload trending Could not find an issue with ups, may need new in the near future Complete Maximo workorders Receive Hypo delivery aprox 410 L Top up ammonia tank 1 Top up chemscan reagents as follows: grey, green and muriatic cleaning solution (red) Changed CL17 sc reagent ?inlet total? Removed garbage from site Waiting on update for temporary water service | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2026-02-10
CENTRAL | February | Station and equipment check Take weekly BacT sample W11589399 and grabs @ 10:20 am Sample tap Total: 1.69 mg/l Sample tap Free: 0.04 mg/l All other readings on PD sheets, no adjustments required on all analyzers Chemicals/reagents ok Contractors working onsite Ops normal | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2026-02-11
CENTRAL | February | Onsite to assist contractor with sanitary repair, manually start/stop sump pumps as needed contractor finished repairs at aprox. 10:00 am Informed ROC (Connor S) will be completing maximo workorders Tank currently filling Cleaned all CL17 analyzers in Cal mode aprox.10:30 am - 11:30 am, readings stabilized to normal after clean Will verify readings at next station check Ops normal | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2026-02-05
CENTRAL | February | Station and equipment check Take weekly BacT sample W11568241 and grabs from sample tap @ 10:50 am Total: 2.00 mg/l Free: 0.02 mg/l Draining between 17-20 L/s chemical system not active at time of readings Chemicals/reagents ok All other readings on PD sheets Ops normal | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2026-02-04
CENTRAL | February | Station and equipment check Took grabs and verified ALL CL17 analyzers due to yesterdays cleaning (24 hr stabilization) Inlet @ 13:20 Total: 2.00 mg/l Free: 0.02 mg/l No adjustments required Header @ 13:30 Total: 3.10 mg/l Free: 0.05 mg/l No adjustments required Topped up hypo tanks 1 and 2 Chemicals/reagents ok Ops normal | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2026-02-06
CENTRAL | February | Station and equipment check Took grabs @ 10:20 am (filling) Inlet Total: 2.10 mg/l Inlet Free: 0.05 mg/l No adjustments required Changed CL17 reagent inlet free Topped up both hypo day tanks *Contractor onsite digging hit hydro line feeding chemical building @ approximately 10:45 am Informed ROC (Angelica) placed all chemical pumps manual Off and deactivated duty as could not monitor Level. Ian W (pcs) onsite to help with temporary generator hookup Temp power until hydro can be repaired, Verfied all analyzers @ 2:30 pm they are all accurate Ian W onsite until repair conplete | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2026-02-09
CENTRAL | February | Onsite to respond to comm failure to tank due to power lines being cut by contractors excavator. Placed PAC panel on generator power while repair was made. Transferred back to normal power one temporary repair was made. | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2026-02-09
CENTRAL | February | On site to complete station check. Site offline and secure. | Newmarket (London) Yonge Street Elevated Tank | 2026-02-27
CENTRAL | February | Under the direction of Ben Hess, Worked along side Network Analyst Kevin Wen, to replaced a Network switch to Cisco IE3300 inside a Control panel. Provided 24 VDC power to new switch from 24VDC power supply. Pulled the fiber cables from Yorknet panel to control panel. Informed the ROC regarding possible comm fail alarm. After the replacement, checked all the ports and reset the comm alarms. | Newmarket (London) Yonge Street Elevated Tank | 2026-02-19
CENTRAL | February | On site to complete station check with Christian B. Site offline and secure. | Newmarket (London) Yonge Street Elevated Tank | 2026-02-12
CENTRAL | February | On site for PMs. -Completed JHSC inspection. All good | Newmarket (London) Yonge Street Elevated Tank | 2026-02-19
CENTRAL | February | On site to perform station check. Site offline and secure. | Newmarket (London) Yonge Street Elevated Tank | 2026-02-17
CENTRAL | February | On site to complete station check with Christian B. Site offline and secure. | Newmarket (London) Yonge Street Elevated Tank | 2026-02-06
CENTRAL | February | Onsite for station and equipment check All ok ET remains OFFLINE JHSC inspection complete no issues Ops normal | Newmarket (Northeast) Davis Drive Elevated Tank | 2026-02-24
CENTRAL | February | Station and equipment check ET remains OFFLINE Ops normal | Newmarket (Northeast) Davis Drive Elevated Tank | 2026-02-12
CENTRAL | February | Station and equipment check ET remains OFFLINE No issues noted Ops normal | Newmarket (Northeast) Davis Drive Elevated Tank | 2026-02-05
CENTRAL | February | Station Check (no issues found) Input data to PWQ 14:15 Verified Depolox (mg/L) Free: Grab 0.05, A 0.07 Total: Grab 2.90, A 2.91 14:25 #11620724 bact. sample Portable generator returned and secured | Newmarket (Southeast) Ivsbridge Elevated Tank | 2026-02-25
CENTRAL | February | Responding to call from ROC (Adam B) Total chlorine hihi alarm On arrival took grabs @ 11:45 am Total: 2.80 mg/l Free: 0.05 mg/l Analyzer false reading due to low flow, adjusted prv to give flow to analyzer and readings returned to normal Will monitor ET ops normal | Newmarket (Southeast) Ivsbridge Elevated Tank | 2026-02-02
CENTRAL | February | Station Check (no issues found) Input data to PWQ 8:37 Verified Depolox (mg/L) (after instrumentation repair) Free: Grab 0.12, A 0.11 Total: Grab 2.69, A 2.19 (adjusted to match grabs) 8:56 #11605447 bact. and operational samples 10:10 Return for a High Free on the analyzer. (Performed zero cal and standard cal to 0.06mg/l to match grabs) | Newmarket (Southeast) Ivsbridge Elevated Tank | 2026-02-17
CENTRAL | February | Work orders #11603775 JHS #11604938 flood #11605125 heat tr #11605176 manual valves #11608067 port. gen (at HW ET) #11603736 Depolox maint. 9:45 verified (mg/l) Free: Grab 0.06, A 0.05 Total: Grab 3.00, A 3.23 (adjusted to match grabs) Acetate top up | Newmarket (Southeast) Ivsbridge Elevated Tank | 2026-02-12
CENTRAL | February | Station and equipment check Take weekly BacT sample W11589399 and grabs @ 8:10 am Total: 2.90 mg/l Free: 0.04 mg/l As previously reported by oncall operator analyzer reading hihi on total. Analyzer Total: 3.48 mg/l Analyzer Free: 0.04 mg/l *standardized analyzer back down to match grabs, will monitor Reagents ok ET ops normal | Newmarket (Southeast) Ivsbridge Elevated Tank | 2026-02-11
CENTRAL | February | Onsite to troubleshoot Hi-Hi total & combined chlorine readings. Informed ROC. Put the device in calibration mode. Noticed that there was no flow to the chlorine analyzer causing false HI-HI total and combined chlorine readings. Found the problem with the PRV at the sample inlet. Removed it from the process and dismantled it. Cleaned it and relubricated all the gaskets and fittings. Put the PRV back in the process and checked for the flow. No issues. Put the analyzer back in service. Readings came back to normal. All the related alarms were cleared. Joe Williams took a grab samples adjusted the analyzer. Informed ROC and left the site. | Newmarket (Southeast) Ivsbridge Elevated Tank | 2026-02-17
CENTRAL | February | -Responded HiHi combine chlorine residual - upon arrival analyzer reading total=9.99mg/L - performed grab test total=2.98mg/L - checked the analyzer - noticed no sample flow to the total analyzer - called instrument technician on call Parth P. - he will come to clean the pressure sustaining valve first thing in the morning - reviewed trends - the total chlorine at the upstream, Aurora South Reservoir, is always around 3.20mg/L - the hihi total analyzer reading is a false reading - not reportable | Newmarket (Southeast) Ivsbridge Elevated Tank | 2026-02-17
CENTRAL | February | Station and equipment check Take weekly BacT sample W11568214 and grabs @ 9:05 am Total: 2.93 mg/l Free: 0.05 mg/l Analyzer readings matched grabs, reagents ok ET ops normal | Newmarket (Southeast) Ivsbridge Elevated Tank | 2026-02-04
CENTRAL | February | Work Orders #11607360 Depolox maint (new reagents, & electrolyte top up) 11:25 Verified (mg/l) Free: Grab 0.05, A 0.05 Total: Grab 1.80, A 1.74 #11607476 jhs #11608497 Dechlor Sump pump not running (found tripped breaker (#16), reset and runs) | Newmarket (West) Bathurst Tank | 2026-02-26
CENTRAL | February | Station Check (no issues found) Input data to PWQ 12:40 Verified Depolox (mg/L) Free: Grab 0.06, A 0.06 Total: Grab 2.88, A 2.90 Depolox (New acetate jug) 12:50 #11620724 bact. sample | Newmarket (West) Bathurst Tank | 2026-02-25
CENTRAL | February | Onsite to trial isolate bathurst tank while feeding water from Orchard Heights ET. Isolated bathurst tank at 10:35 am Reversed the isolation of bathurst tank at 12:05, tank back into service. Station ok | Newmarket (West) Bathurst Tank | 2026-02-02
CENTRAL | February | Station Check (no issues found) Input data to PWQ 11:30 Verified Depolox (mg/L) Free: Grab 0.05, A 0.06 Total: Grab 2.72, A 2.77 Depolox (Acetate & Electrolyte top up) 11:45 #11605447 bact. & operational samples | Newmarket (West) Bathurst Tank | 2026-02-17
CENTRAL | February | Station and equipment check Take weekly BacT sample W11568214 and grabs @ 10:05 am from Outlet sample tap Total: 2.80 mg/l Free: 0.05 mg/l No adjustments necessary, reagents ok Ops normal | Newmarket (West) Bathurst Tank | 2026-02-04
CENTRAL | February | Station and equipment check Take weekly BacT sample W11589399 and grabs @ 9:10 am Total: 2.77 mg/l Free: 0.05 mg/l Analyzer Total: 2.72 mg/l Analyzer Free: 0.06 mg/l Reagents ok Ops normal | Newmarket (West) Bathurst Tank | 2026-02-11
CENTRAL | February | Station and equipment check All ops normal | Newmarket Kirby Pumping Station | 2026-02-23
CENTRAL | February | Station and equipment check Ops normal | Newmarket Kirby Pumping Station | 2026-02-27
CENTRAL | February | Restarted the Operator Interface Terminal due to Windows OS updates. The Remote Operations Center was notified prior to doing the work. | Newmarket Kirby Pumping Station | 2026-02-23
CENTRAL | February | Station and equipment check Suction pressure: 75 kPa Discharge pressure: 334 kPa Flow: 20 L/s Tank level: 50% All pumps available Ops normal | Newmarket Kirby Pumping Station | 2026-02-02
CENTRAL | February | Station Check (no issues found) Input data to PWQ | Newmarket Kirby Pumping Station | 2026-02-20
CENTRAL | February | Station and equipment check All pumps available FCV: 17% @ 19.9 L/s Ops normal *security aware swipe card not working | Newmarket Kirby Pumping Station | 2026-02-12
CENTRAL | February | Station check (no issues found) Input data to PWQ | Newmarket Kirby Pumping Station | 2026-02-18
CENTRAL | February | Station and equipment check All ok No issues Duty not active Ops normal | Newmarket Kirby Pumping Station | 2026-02-06
CENTRAL | February | Onsite to complete monthly Maximo workorders Diesel test run, ran ok Stop hours: 33.40 On transfer lost analyzers in chemical building PCS Ian W on way to investigate Will log into chemical building elog Also swipe cards not working around station or chemical building, CPD looking into issue Pump station otherwise ok | Newmarket Kirby Pumping Station | 2026-02-10
CENTRAL | February | Station and equipment check Ops normal Duty 1 active FCV 17% All pumps standby and ready All ok | Newmarket Kirby Pumping Station | 2026-02-09
CENTRAL | February | On site to complete station check and collect operational samples. -Verified analyzers: Influent Free Chlorine @ 9:48 Grab: 2.64 mg/L Analyzer: 2.67 mg/L Effluent Free Chlorine @ 9:41 Grab: 2.72 mg/L Analyzer: 2.67 mg/L Treated Free Chlorine @ 9:37 Grab: 0.10 mg/L Analyzer: 0.14 mg/L Treated Total Chlorine @ 9:37 Grab: 3.04 mg/L Analyzer: 3.07 mg/L -Placed well 15 in manual-on -Entered data into PD sheet -Checked trends | Newmarket Well 1 & 2 | 2026-02-23
CENTRAL | February | Changed reagents for effluent free and treated free chlorine analyzers | Newmarket Well 1 & 2 | 2026-02-23
CENTRAL | February | On site with Christian B to complete station check and weekly bacti samples (W11619950). -Verified analyzers: Influent Free Chlorine @ 9:54 Grab: 2.54 mg/L Analyzer: 2.63 mg/L Effluent Free Chlorine @ 9:58 Grab: 2.60 mg/L Analyzer: 2.62 mg/L Treated Free Chlorine @ 10:02 Grab: 0.14 mg/L Analyzer: 0.15 mg/L Treated Total Chlorine @ 10:05 Grab: 2.90 mg/L Analyzer: 3.02 mg/L -Entered data into PD Sheet -Checked trends -Topped up Well 2 mineral oil -Returned wells to auto | Newmarket Well 1 & 2 | 2026-02-25
CENTRAL | February | Deliver 1.5 load of silicate Alex B onsite | Newmarket Well 1 & 2 | 2026-02-24
CENTRAL | February | Attending site for silicate pump 1 uncommanded stop (W11683625). Cycled power on pump which tripped the circuit breaker. Tried again and the breaker tripped again. Replaced pump and configured. Performed drawdown and entered 240mL/min as maximum pump output in SCADA. Left pump#1 in duty 1 to test performance. ROC was notified before and after maintenance activities. | Newmarket Well 1 & 2 | 2026-02-23
CENTRAL | February | On site to complete PMs. Notified ROC of relevant alarms. -Completed JHSC inspection: all good -Completed ammonia system inspection: flood alarm functional, performed drawdowns: pump 2 max flow setpoint on SCADA changed from 200 to 190 mL/min -Deactivated duty, placed wells in manual-off to complete PMs -Completed chlorine leak detection test: all good -Completed chlorine system inspection: Prior to work, added dechlor to waste chamber and opened waste valve slightly. Returned system to normal after work completed. All good. -Completed CL17 chlorine analyzer maintenance and verified as follows: Influent Free Chlorine @ 12:58 Grab: 2.54 mg/L Analyzer: 2.55 mg/L Effluent Free Chlorine @ 12:53 Grab: 0.10 mg/L Analyzer: 0.14 mg/L Treated Free Chlorine @ 12:44 Grab: 0.07 mg/L Analyzer: 0.09 mg/L Treated Total Chlorine @ 12:44 Grab: 2.62 mg/L Analyzer: 2.56 mg/L Exit button on influent free CL17 nonfunctional ? Restarted analyzer after cleaning via power cycle. Created WO W11688098 for instrumentation to address fixing the button. -Returned wells to auto | Newmarket Well 1 & 2 | 2026-02-24
CENTRAL | February | On site to complete PMs with Christian B. Notified ROC of relevant alarms. -Placed wells in manual-off -Performed maintenance on well 1 deep well exhaust valve -Performed maintenance on well 2 deep well exhaust valve -Performed maintenance on and calibrated turbidimeter. Analyzer read 0.039 NTU afterwards. -Performed maintenance on and inspection of silicate system. Placed well 2 in local, well 1 in manual. Added dechlor to waste chamber, opened waste valve slightly. Ran hot water flush through chemical board and lines. Isolated influent side of contact tank and depressurized raw main. Pulled and cleaned injection points. Performed drawdowns. Pump 1 SCADA max flow setpoint changed from 240 to 220 mL/min. -Placed wells in manual-on to test silicate dosing. Activated area duty. Lo total and combined chlorine alarm and effluent lo alarm during well startup due to having drawn back distribution water via opened waste valve during all silicate work. Switched silicate pumps at 14:29. Silicate dosing all good. -Topped up ammonia tank 1 -Returned wells to auto | Newmarket Well 1 & 2 | 2026-02-26
CENTRAL | February | Restarted the Operator Interface Terminal due to Windows OS updates. The wells were off during the updates and the Remote Operations Center was notified prior to doing the work. | Newmarket Well 1 & 2 | 2026-02-23
CENTRAL | February | On site to complete station check. -Verified analyzers: Influent Free Chlorine @ 11:36 Grab: 2.70 mg/L Analyzer: 2.74 mg/L Effluent Free Chlorine @ 11:33 Grab: 2.42 mg/L Analyzer: 2.34 mg/L Treated Free Chlorine @ 11:30 Grab: 0.12 mg/L Analyzer: 0.13 mg/L Treated Total Chlorine @ 11:30 Grab: 2.64 mg/L Analyzer: 2.66 mg/L -Entered data into PD Sheet -Checked trends | Newmarket Well 1 & 2 | 2026-02-27
CENTRAL | February | On site to complete station check with Christian B. -Placed wells in manual-on for duration of work -Verified analyzers: Influent Free Chlorine @ 9:29 Grab: 2.52 mg/L Analyzer: 2.56 mg/L Effluent Free Chlorine @ 9:26 Grab: 2.58 mg/L Analyzer: 2.57 mg/L Treated Free Chlorine @ 9:22 Grab: 0.15 mg/L Analyzer: 0.13 mg/L Treated Total Chlorine @ 9:22 Grab: 2.92 mg/L Analyzer: 3.00 mg/L -Entered data into PD sheet -Checked trends -Returned wells to auto -Placed wells 13/16 in manual | Newmarket Well 1 & 2 | 2026-02-02
CENTRAL | February | Silicate Top Up Before: 38.6cm/350.0L After: 101.0cm/916.0L | Newmarket Well 1 & 2 | 2026-02-10
CENTRAL | February | On site to complete station check with Christian B. -Verified analyzers: Influent Free Chlorine @ 10:53 Grab: 2.52 mg/L Analyzer: 2.45 mg/L Effluent Free Chlorine @ 10:48 Grab: 2.62 mg/L Analyzer: 2.59 mg/L Treated Free Chlorine @ 10:43 Grab: 0.10 mg/L Analyzer: 0.13 mg/L Treated Total Chlorine @ 10:43 Grab: 2.94 mg/L Analyzer: 2.97 mg/L -Entered data into PD sheet -Checked trends -Topped up ammonia tank 1 -Topped up well 2 mineral oil | Newmarket Well 1 & 2 | 2026-02-13
CENTRAL | February | On site to complete PMs with Christian B. Notified ROC of relevant alarms. -Placed wells in manual, added dechlor to waste chamber. Opened waste valve slightly -Found SCADA speed deviation issue with silicate pump 1, created WO W11670844 for instrumentation -Ran hot water flush through silicate pump and injection point 2. Reprimed line with silicate after. Ended flow to waste valve | Newmarket Well 1 & 2 | 2026-02-17
CENTRAL | February | On site to complete station check with Christian B and collect weekly bacti samples (W11606270). -Placed wells in manual for duration of station check -Verified analyzers: Influent Free Chlorine @ 10:26 Grab: 2.60 mg/L Analyzer: 2.58 mg/L Effluent Free Chlorine @ 10:31 Grab: 2.54 mg/L Analyzer: 2.58 mg/L Treated Free Chlorine @ 10:34 Grab: 0.10 mg/L Analyzer: 0.14 mg/L Treated Total Chlorine @ 10:38 Grab: 2.88 mg/L Analyzer: 2.96 mg/L -Placed NMW15 in manual, returned NMW12 to auto -Entered data into PD sheet -Checked trends | Newmarket Well 1 & 2 | 2026-02-17
CENTRAL | February | Attending site to check silicate pump#1 - SCADA speed control not working (W11670844). - Found pump input/output module not responding to speed reference signal injected directly from a digital multimeter. Replaced I/O module. - Found that after I/O module replacement, pump was able to be controlled from a multimeter but was still not able to follow speed command from SCADA. Found speed reference wiring leaving PAC panel was not connected correctly and completely loose. Re-terminated wire and checked all other analog outputs on that card for correct termination. Suspect that intermittent connection to pump had caused the pump I/O module to fail. - Once pump was able to be controlled by SCADA, found that pump would not discharge silicate - even with very little back pressure. - Replaced pump roller with a used spare part, which corrected the issue, and was able to perform drawdowns on pump#1. - Entered pump#1 maximum flow of 210 mL/min, as determined by drawdown tests. - Left silicate pump#1 in duty#1. - Notified Ben Hess and Alex Bell ROC was notified before and after maintenance activities. | Newmarket Well 1 & 2 | 2026-02-19
CENTRAL | February | On site to complete station check with Christian B and collect weekly bacti samples W11588614. -Verified analyzers: Influent Free Chlorine @ 14:27 Grab: 2.66 mg/L Analyzer: 2.61 mg/L Effluent Free Chlorine @ 14:24 Grab: 2.42 mg/L Analyzer: 2.39 mg/L Treated Free Chlorine @ 14:21 Grab: 0.09 mg/L Analyzer: 0.13 mg/L Treated Total Chlorine @ 14:21 Grab: 2.84 mg/L Analyzer: 2.88 mg/L -Entered data into PD sheet -Checked trends -Returned wells 1/2 to auto -Returned well 15 to auto after confirming silicate injection point 1 dosing effectively | Newmarket Well 1 & 2 | 2026-02-11
CENTRAL | February | On site to complete station check. -Verified analyzers: Influent Free Chlorine @ 9:12 Grab: 2.64 mg/L Analyzer: 2.69 mg/L Effluent Free Chlorine @ 9:09 Grab: 2.60 mg/L Analyzer: 2.59 mg/L Treated Free Chlorine @ 9:06 Grab: 0.15 mg/L Analyzer: 0.13 mg/L Treated Total Chlorine @ 9:06 Grab: 3.00 mg/L Analyzer: 2.95 mg/L -Topped up ammonia tank 2 -Entered data into PD sheet -Checked trends | Newmarket Well 1 & 2 | 2026-02-20
CENTRAL | February | turbidity spike went above 0.200 NTU rotated silicate P2 into duty 1. Silicate P1 OOS until operator can troubleshoot | Newmarket Well 1 & 2 | 2026-02-10
CENTRAL | February | Changed chlorine cylinder bank A with Joe Williams. | Newmarket Well 1 & 2 | 2026-02-18
CENTRAL | February | On-site for a station and equipment check No issues found Chemical levels and systems ok 15 cylinders and 0 bags of ammonia in inventory Weekly bacti samples taken Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@0829 G:2.72 A:2.61mg/L Effluent Free@0835 G:2.46 A:2.56mg/L Treated Free@0836 G:0.14 A:0.13mg/L Treated Total@0839 G:2.96 A:2.96mg/L Mono-2.50 FA-0.04 TA-0.54 | Newmarket Well 1 & 2 | 2026-02-04
CENTRAL | February | On site to complete station check and address silicate pump 1 leak alarm. -Verified analyzers: Influent Free Chlorine @ 10:15 Grab: 2.54 mg/L Analyzer: 2.55 mg/L Effluent Free Chlorine @ 10:12 Grab: 2.74 mg/L Analyzer: 2.69 mg/L Treated Free Chlorine @ 9:57 Grab: 0.09 mg/L Analyzer: 0.13 mg/L Treated Total Chlorine @ 9:57 Grab: 3.06 mg/L Analyzer: 3.01 mg/L -Entered data into PD sheet -Checked trends -Replaced tubing for and cleaned silicate pump 1. Ran hot water through chemical board to loosen PRV and PSV. Performed drawdown, SCADA max flow setpoint changed from 180 mg/L to 220 mg/L. Observed pressure was normal through injection point when running to system briefly. Returned silicate pump 1 to auto. Observed silicate pump pressure while wells running. Confirmed effective dosing. | Newmarket Well 1 & 2 | 2026-02-09
CENTRAL | February | On site to complete station check with Christian B. -Verified analyzers: Influent Free Chlorine @ 10:53 Grab: 2.64 mg/L Analyzer: 2.59 mg/L Effluent Free Chlorine @ 10:59 Grab: 2.62 mg/L Analyzer: 2.53 mg/L Treated Free Chlorine @ 11:04 Grab: 0.10 mg/L Analyzer: 0.14 mg/L Treated Total Chlorine @ 11:09 Grab: 3.08 mg/L Analyzer: 2.97 mg/L -Changed influent free chlorine analyzer reagents -Topped up ammonia tank 2 -Changed cylinder bank B with Will M. -Entered data into PD sheet -Checked trends | Newmarket Well 1 & 2 | 2026-02-06
CENTRAL | February | #11624577 main flushed for 90mins. | Newmarket Well 14 | 2026-02-26
CENTRAL | February | Onsite for station check. Tower offline. Building secure. No issues. | Newmarket Well 14 | 2026-02-19
CENTRAL | February | On site with Dan Boate to investigate possible well motor overheating. Well running upon arrival. ROC contacted to stop well pump and notified about work being conducted. Well de-energized. Found motor operating within nameplate temperature and current range. Reenergized motor and returned to normal operation. ROC notified. | Newmarket Well No. 15 | 2026-02-25
CENTRAL | February | On site to complete station check and collect operational samples. -Verified analyzers: Influent Free Chlorine @ 10:57 Grab: 2.86 mg/L Analyzer: 2.89 mg/L Effluent Free Chlorine @ 10:52 Grab: 2.82 mg/L Analyzer: 2.86 mg/L Treated Free Chlorine @ 10:44 Grab: 0.14 mg/L Analyzer: 0.15 mg/L Treated Total Chlorine @ 11:05 Grab: 3.46 mg/L Analyzer: 3.56 mg/L Adjusted analyzer to match average of 3 grabs. Analyzer read 3.44mg/L afterwards. -Replaced Influent free chlorine CL17 analyzer reagents -Returned well to auto -Entered data into PD sheet -Checked trends | Newmarket Well No. 15 | 2026-02-23
CENTRAL | February | On site to reprime silicate lines after they ran dry due to low chemical storage. Notified ROC of relevant alarms. -Placed dechlor in waste chamber, opened waste valve slightly -Identified silicate injection point 1 check valve was completely passing -Switched to injection point 2, ran both silicate pumps manually -Placed well in manual-on to observe silicate dosing -Returned wells to auto after confirming injection point 2 works | Newmarket Well No. 15 | 2026-02-24
CENTRAL | February | Under the direction of Ben Hess, Worked along side Network Analyst Kevin Wen, to replaced a Network switch to Cisco IE3300 inside a Control panel. Provided 24 VDC power to new switch from 24VDC power supply. Pulled the fiber cables from Yorknet panel to control panel. Informed the ROC regarding possible comm fail alarm. Well were Manual off. After the replacement, checked all the ports and reset the comm alarms. | Newmarket Well No. 15 | 2026-02-19
CENTRAL | February | Restarted the Operator Interface Terminal due to Windows OS updates. The well was off during the updates and the Remote Operations Center was notified prior to doing the work. | Newmarket Well No. 15 | 2026-02-23
CENTRAL | February | On site to complete station check. -Put well into manual -Verified analyzers: Influent Free Chlorine @ 12:30 Grab: 3.02 mg/L Analyzer: 2.90 mg/L Effluent Free Chlorine @ 12:25 Grab: 2.84 mg/L Analyzer: 2.86 mg/L Treated Free Chlorine @ 12:21 Grab: 0.10 mg/L Analyzer: 0.14 mg/L Treated Total Chlorine @ 12:21 Grab: 3.32 mg/L Analyzer: 3.40 mg/L -Entered data into PD Sheet -Checked trends -Topped up well 15 mineral oil -Put well back into auto | Newmarket Well No. 15 | 2026-02-27
CENTRAL | February | On site with Christian B to complete station check and weekly bacti samples (W11619950). -Put well into manual-on -Verified analyzers: Influent Free Chlorine @ 11:24 Grab: 2.96 mg/L Analyzer: 2.92 mg/L Effluent Free Chlorine @ 11:27 Grab: 2.48 mg/L Analyzer: 2.59 mg/L Treated Free Chlorine @ 11:31 Grab: 0.14 mg/L Analyzer: 0.14 mg/L Treated Total Chlorine @ 11:34 Grab: 3.20 mg/L Analyzer: 3.29 mg/L -Entered data into PD Sheet -Checked trends -Changed chlorine bank B with Will M -Put well back into auto | Newmarket Well No. 15 | 2026-02-25
CENTRAL | February | Silicate Fill 85.8 L to 384 L Also slight drip from silicate injection point 1, was able to stop drip keep an eye Ops normal Well manual off for now | Newmarket Well No. 15 | 2026-02-24
CENTRAL | February | On site to complete station check with Christian B. -Verified analyzers: Influent Free Chlorine @ 10:53 Grab: 2.52 mg/L Analyzer: 2.61 mg/L Effluent Free Chlorine @ 11:06 Grab: 0.02mg/L Analyzer: 0.03 mg/L Treated Free Chlorine @ 11:16 Grab: 0.01 mg/L Analyzer: 0.01mg/L Treated Total Chlorine @ 11:23 Grab: 1.22 mg/L Analyzer: 1.24 mg/L Responded to high turbidity alarm. -Well in manual off. Placed well in local. Added dechlor to waste chamber. Isolated contact chamber on influent side. Depressurized raw main. Cleaned silicate injection points. Repressurized raw main. Tested silicate pumps to sight glass ? pump 2 good, pump 1 issue with drawing silicate from tank. Reprimed silicate injection lines via pump 2. Ran well in manual testing both injection points sequentially. Injection point 1 left in service. Neither dosed as well as would be expected, further troubleshooting needed. -Returned well to auto -Entered data into PD sheet -Checked trends | Newmarket Well No. 15 | 2026-02-02
CENTRAL | February | turbidity went hi while silicate P2 was running. Silicate P1 already OOS. Put well to manual off until operator can troubleshoot silicate P1 and P2. | Newmarket Well No. 15 | 2026-02-10
CENTRAL | February | On site to complete station check, collect weekly bacti samples (W11588614), and troubleshoot silicate dosing problems with Christian B. ?Placed well in local. Added dechlor to waste chamber. Depressurized raw main by isolating influent side of contact tank and opening waste valve. Pulled and cleaned injection points. Lo and Lolo influent chlorine alarms caused by loss of flow to analyzer from isolating on influent side of contact tank. Ran hot water through chemical board to loosen PRV and PSV, ran through injection points. Cleaned foot valves. Raised silicate supply lines up from bottom of tank. Performed drawdowns, SCADA max flow setpoints not changed. Repressurized raw main and primed silicate injection points while backflushing slightly to waste. Placed silicate pumps back in auto. Placed well 15 back in manual. Turned well 15 on to confirm effective dosing. -Turned Newmarket well 13 on for Will M. to complete sampling -Topped up ammonia tank 1 -Verified analyzers: Influent Free Chlorine @ 13:16 Grab: 2.78 mg/L Analyzer: 2.81 mg/L Effluent Free Chlorine @ 13:19 Grab: 2.62 mg/L Analyzer: 2.56 mg/L Treated Free Chlorine @ 13:25 Grab: 0.14 mg/L Analyzer: 0.13 mg/L Treated Total Chlorine @ 13:29 Grab: 3.14 mg/L Analyzer: 3.17 mg/L -Put Newmarket wells 1/2 in manual-on -Switched to injection point 1 @ 13:54 after confirming injection point 2 doses effectively -Entered data into PD sheet -Checked trends | Newmarket Well No. 15 | 2026-02-11
CENTRAL | February | Silicate Top Up Before: 32.7cm/149.0L After: 84.2cm/384.0L | Newmarket Well No. 15 | 2026-02-10
CENTRAL | February | On site to complete station check with Christian B and collect weekly bacti samples (W11606270). -Verified analyzers: Influent Free Chlorine @ 11:21 Grab: 3.02 mg/L Analyzer: 2.91 mg/L Effluent Free Chlorine @ 11:24 Grab: 3.00 mg/L Analyzer: 2.88 mg/L Treated Free Chlorine @ 11:27 Grab: 0.13 mg/L Analyzer: 0.15 mg/L Treated Total Chlorine @ 11:30 Grab: 3.41 mg/L Analyzer: 3.36 mg/L -Topped up mineral oil for well 15 -Returned well to auto -Completed JHSC inspection: all good -Entered data into PD sheet -Checked trends | Newmarket Well No. 15 | 2026-02-17
CENTRAL | February | On site to complete station check with Christian B. -Placed well in manual for duration of check -Verified analyzers: Influent Free Chlorine @ 8:52 Grab: 2.60 mg/L Analyzer: 2.58 mg/L Effluent Free Chlorine @ 8:49 Grab: 0.15 mg/L Analyzer: 0.13 mg/L Treated Free Chlorine @ 8:46 Grab: 0.04 mg/L Analyzer: 0.07 mg/L Treated Total Chlorine @ 8:46 Grab: 2.68 mg/L Analyzer: 2.77 mg/L -Topped up mineral oil well 15 -Entered data into PD sheet -Checked trends -Returned well 15 to auto -Placed well 16 in manual | Newmarket Well No. 15 | 2026-02-10
CENTRAL | February | Attending site to check chlorine analyzer fault (W11674000). Analyzer had a motor error. Replaced optical sensor. Verified reading at 1.82 mg/L Total. Analyzer reading 1.76mg/L. Adjusted analyzer to 1.82mg/L Total, based on 3 dpd grabs. Placed well back to Auto, as requested by Alex Bell. ROC was notified before and after maintenance activities. | Newmarket Well No. 15 | 2026-02-18
CENTRAL | February | On site to complete station check with Christian B. -Placed Newmarket well 13 in duty 1 and Newmarket well 16 in duty 2 -Verified analyzers: Influent Free Chlorine @ 13:16 Grab: 2.78 mg/L Analyzer: 2.81 mg/L Effluent Free Chlorine @ 13:19 Grab: 2.62 mg/L Analyzer: 2.56 mg/L Treated Free Chlorine @ 13:25 Grab: 0.14 mg/L Analyzer: 0.13 mg/L Treated Total Chlorine @ 13:29 Grab: 3.14 mg/L Analyzer: 3.17 mg/L -Changed reagents for treated free and treated total chlorine analyzers -Entered data into PD sheet -Checked trends | Newmarket Well No. 15 | 2026-02-13
CENTRAL | February | Attending site to check Influent Free chlorine analyzer buttons (W11673928). Replaced all push buttons as existing ones were not functioning. Verified readings after maintenance work - analyzer did not require any adjustments. ROC was notified before and after maintenance activities. | Newmarket Well No. 15 | 2026-02-19
CENTRAL | February | On site to complete PMs with Christian B. Notified ROC of relevant alarms. -Inspected ammonia system, performed pump drawdowns and tested flood alarm; all good -Placed well in manual-off -Inspected chlorine system: added dechlor to waste chamber and performed inspection while waste valve slightly open. System operating well ? vacuum releasing slightly fast, so made W11673879 to revisit in a few weeks and reassess -Performed maintenance on and calibrated turbidimeter. Analyzer read 0.050 NTU afterwards. -Performed maintenance on CL17 analyzers Verified analyzers: Influent Free Chlorine @ 12:05 Grab: 2.70 mg/L Analyzer: 2.73 mg/L Effluent Free Chlorine @ 12:08 Grab: 0.17 mg/L Analyzer: 0.17 mg/L Treated Free Chlorine @ 12:11 Grab: 0.08 mg/L Analyzer: 0.08 mg/L Could not verify treated total analyzer due to persistent motor error. Contacted Eric S from instrumentation who is on his way to troubleshoot. Treated and Combined lo and lolo alarms are thus caused by analyzer error. Leaving well in manual-off and notifying ROC. | Newmarket Well No. 15 | 2026-02-18
CENTRAL | February | On site to complete station check. -Placed well in manual for duration of station check -Verified analyzers: Influent Free Chlorine @ 10:31 Grab: 3.04 mg/L Analyzer: 2.91 mg/L Effluent Free Chlorine @ 10:26 Grab: 2.82 mg/L Analyzer: 2.75 mg/L Treated Free Chlorine @ 10:19 Grab: 0.12 mg/L Analyzer: 0.15 mg/L Treated Total Chlorine @ 10:19 Grab: 3.44 mg/L Analyzer: 3.44 mg/L -Topped up ammonia tank 2 -Returned well to auto -Entered data into PD sheet -Checked trends | Newmarket Well No. 15 | 2026-02-20
CENTRAL | February | On site to complete PMs. Notified ROC of relevant alarms. -Completed chlorine leak detection test: all good -Inspected and performed maintenance on deep well exhaust valve: all good | Newmarket Well No. 15 | 2026-02-19
CENTRAL | February | On-site for a station and equipment check No issues found. Chemical levels and systems ok 6 cylinders and 4 bags of ammonia in inventory Weekly bacti samples taken Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@0928 G:2.90 A:2.92mg/L Effluent Free@0932 G:2.94 A:2.89mg/L Treated Free@0936 G:0.18 A:0.14mg/L Treated Total@0939 G:3.44 A:3.34mg/L Mono-2.91 FA-0.04 TA-0.62 | Newmarket Well No. 15 | 2026-02-04
CENTRAL | February | On site to complete PMs with Christian B. Notified ROC of relevant alarms. -Added dechlor to well 13 waste chamber -Performed chlorine inspection: all good except water noticed in chlorinator 2 vacuum gauge, created WO -Performed well 13 PRV inspection and maintenance: used PRV to backflush slightly to minimize excess chlorine from chlorine inspection -Inspected well 13 deep well exhaust valve and reviewed operations via trends and inspection during other station checks -Returned well 13 to auto | Newmarket Wells 13-16 | 2026-02-25
CENTRAL | February | On site to complete station check with Christian B and collect weekly bacti samples (W11619950). -Topped up ammonia tank 2 -Topped up well 13 mineral oil -Verified analyzers: Influent Free Chlorine @ 8:08 Grab: 2.80 mg/L Analyzer: 2.73 mg/L Effluent Free Chlorine @ 8:05 Grab: 2.38 mg/L Analyzer: 2.40 mg/L Treated Free Chlorine @ 8:01 Grab: 0.08 mg/L Analyzer: 0.12 mg/L Treated Total Chlorine @ 8:01 Grab: 2.70 mg/L Analyzer: 2.73 mg/L -Performed drawdown, changed ammonia pump 2 SCADA max flow setpoint from 230 to 220 mL/min due to low free ammonia SL1000 grabs -Placed wells 1 and 2 in manual -Entered data into PD sheet -Checked trends | Newmarket Wells 13-16 | 2026-02-25
CENTRAL | February | On site to complete station check. -Verified analyzers: Influent Free Chlorine @ 14:25 Grab: 2.40 mg/L Analyzer: 2.43 mg/L Effluent Free Chlorine @ 14:22 Grab: 0.13 mg/L Analyzer: 0.15 mg/L Treated Free Chlorine @ 14:17 Grab: 0.10 mg/L Analyzer: 0.07 mg/L Treated Total Chlorine @ 14:17 Grab: 2.40 mg/L Analyzer: 2.32 mg/L -Replaced reagents for influent free and treated total chlorine analyzers -Entered data into PD sheet -Checked trends | Newmarket Wells 13-16 | 2026-02-27
CENTRAL | February | Silicate load 1648 L - 2527 L Ops normal | Newmarket Wells 13-16 | 2026-02-24
CENTRAL | February | Restarted the Operator Interface Terminal due to Windows OS updates. The wells were off during the updates and the Remote Operations Center was notified prior to doing the work. | Newmarket Wells 13-16 | 2026-02-23
CENTRAL | February | Attending site to check Treated Free chlorine analyzer analog output (W11664335). Adjusted Treated Free analog output so that SCADA better matches the analyzer display value. ROC was notified before and after maintenance activities. | Newmarket Wells 13-16 | 2026-02-24
CENTRAL | February | On site to complete station check with Christian B. -Verified analyzers: Influent Free Chlorine @ 8:39 Grab: 2.70 mg/L Analyzer: 2.72 mg/L Effluent Free Chlorine @ 8:35 Grab: 2.46 mg/L Analyzer: 2.45 mg/L Treated Free Chlorine @ 8:29 Grab: 0.11 mg/L Analyzer: 0.12 mg/L Treated Total Chlorine @ 8:29 Grab: 2.82 mg/L Analyzer: 2.79 mg/L -Took pH raw sample for well 13 -Entered data into PD sheet -Checked trends | Newmarket Wells 13-16 | 2026-02-02
CENTRAL | February | On site to complete station check and collect operational samples. -Verified analyzers: Influent Free Chlorine @ 8:34 Grab: 2.76 mg/L Analyzer: 2.69 mg/L Effluent Free Chlorine @ 8:31 Grab: 2.42 mg/L Analyzer: 2.38 mg/L Treated Free Chlorine @ 8:28 Grab: 0.07 mg/L Analyzer: 0.11 mg/L Treated Total Chlorine @ 8:28 Grab: 2.80 mg/L Analyzer: 2.72 mg/L -Changed treated free chlorine analyzer reagents -Entered data into PD sheet -Checked trends | Newmarket Wells 13-16 | 2026-02-23
CENTRAL | February | Returned wells to auto. Water Resources on site. | Newmarket Wells 13-16 | 2026-02-02
CENTRAL | February | On site to complete station check. -Verified analyzers: Influent Free Chlorine @ 8:08 Grab: 2.62 mg/L Analyzer: 2.69 mg/L Effluent Free Chlorine @ 8:05 Grab: 2.40 mg/L Analyzer: 2.39 mg/L Treated Free Chlorine @ 8:02 Grab: 0.11 mg/L Analyzer: 0.12 mg/L Treated Total Chlorine @ 8:02 Grab: 2.78 mg/L Analyzer: 2.70 mg/L -Entered data into PD sheet -Checked trends | Newmarket Wells 13-16 | 2026-02-20
CENTRAL | February | On site to complete PMs. Notified ROC of relevant alarms. -Placed wells in manual-off -Performed chlorine gas detector test: all good -Performed turbidimeter analyzer maintenance and calibrated using standard. Read 0.046 NTU afterwards. -Performed CL17 chlorine analyzer maintenance, verified analyzers afterwards: Influent Free Chlorine @ 11:17 Grab: 2.42 mg/L Analyzer: 2.46 mg/L Effluent Free Chlorine @ 11:14 Grab: 1.32 mg/L Analyzer: 1.36 mg/L Treated Free Chlorine @ 11:20 Grab: 0.02 mg/L Analyzer: 0.05 mg/L Treated Total Chlorine @ 11:20 Grab: 2.46 mg/L Analyzer: 2.44 mg/L -Performed JHSC inspection: all good -Returned well 16 to auto | Newmarket Wells 13-16 | 2026-02-10
CENTRAL | February | On site to disconnect Well 16 motor. ROC notified. Well 16 starter locked/tagged out. Motor feeder and level probe disconnected. | Newmarket Wells 13-16 | 2026-02-17
CENTRAL | February | On site to complete station check with Christian B and collect weekly bacti samples (W11606270). -Placed well 16 in manual. Electricians Kyle and Sean on site, locked out well 16 electrically. I isolated well 16 via valve 00041307, LOTO?d the valve. Isolated FCV (00041305) bonnet via two ball valves on the FCV. Placed LOTO tag and made visually obvious via a sign. Added dechlor to waste chamber and opened waste valve to depressurize main and confirm full isolation. Reported LOTO to other central operators. -Well 16 level lo and lolo alarms caused by LOTO of electronics -Verified analyzers: Influent Free Chlorine @ 9:03 Grab: 2.74 mg/L Analyzer: 2.73 mg/L Effluent Free Chlorine @ 9:07 Grab: 2.32mg/L Analyzer: 2.38 mg/L Treated Free Chlorine @ 9:11 Grab: 0.13 mg/L Analyzer: 0.12 mg/L Treated Total Chlorine @ 9:14 Grab: 2.62 mg/L Analyzer: 2.68 mg/L -Topped up well 13 mineral oil -Rotated ammonia pumps so pump 1 active -Entered data into PD sheet -Checked trends | Newmarket Wells 13-16 | 2026-02-17
CENTRAL | February | On site to complete PMs with Christian B. Notified ROC of relevant alarms. -Added dechlor to waste chamber, isolated contact tank on influent side in order to depressurize raw main. Pulled injection points, ran hot water through chemical boards and injection points. Returned system to normal. Influent chlorine lo and lolo alarms caused by lack of flow during raw main isolation. Flushed from waste valve to remove excess silicate from main. Closed waste valve and fully reopened influent contact tank valve. -Changed chlorine cylinder bank A with Jason G. -Completed ammonia inspection. Containment flood alarm tested. Performed drawdowns on both pumps ? no change needed. No issues found -Completed silicate pump drawdowns. Max flow setpoints on SCADA changed for pump 1 to 290 mL/min and for pump 2 to 265 mL/min -Returned wells to auto | Newmarket Wells 13-16 | 2026-02-12
CENTRAL | February | -on site to troubleshoot the well 13 faults. I called roc at 1330 to stop w16 and I started well 13 1350 witnessed a waste cycle and no major issue was noted transferring to system. During did have the a high chlorine alarm 1400. Stopped well with Ben and back flushed the contact tank till reading a suitable level on analyzers. We placed well back to remote Ben started and I witnessed another waste cycle no faults while running to system. Ben H. Placed well back to duty and we will monitor for more faults. Under direction of oic. | Newmarket Wells 13-16 | 2026-02-10
CENTRAL | February | On site to complete station check with Christian B. -Found silicate pump 1 in hand, returned to remote and cleared fail to start alarm. Rotated it into duty 1 at 8:58 to test dosing effectiveness -Verified analyzers: Influent Free Chlorine @ 9:08 Grab: 2.64 mg/L Analyzer: 2.71 mg/L Effluent Free Chlorine @ 9:03 Grab: 2.50 mg/L Analyzer: 2.49 mg/L Treated Free Chlorine @ 9:00 Grab: 0.09 mg/L Analyzer: 0.13 mg/L Treated Total Chlorine @ 9:00 Grab: 2.90 mg/L Analyzer: 2.87 mg/L -Switched from ammonia pump 1 to 2 at 9:27 due to high ammonia dosing. Confirmed dosing high across both pumps. Adjusted chlorine:ammonia ratio from 4.20 to 4.30 -Rotated duty for the wells so well 16 is in duty 1 and well 13 is in duty 2 to allow well 16 to continue to run after IWS visited site and I manually rotated the wells to allow well 16 to be inspected while running -Based on turbidity rising slowly while running silicate pump 1, adjusted max flow SCADA setpoint back from 290 mL/min to 280 mL/min (dose prior to yesterday?s adjustment) -Topped up ammonia tank 1 -Entered data into PD sheet -Checked trends | Newmarket Wells 13-16 | 2026-02-13
CENTRAL | February | On-site for a station and equipment check No issues found Weekly bacti samples taken Chemical levels and systems ok 12 cylinders and 2 bags of ammonia in inventory Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@1350 G:2.52 A:2.54mg/L Effluent Free@1306 G:2.36 A:2.39mg/L Treated Free@1406 G:0.08 A:0.12mg/L Treated Total@1410 G:2.74 A:2.72mg/L Mono-2.33 FA-0.08 TA-0.54mg/L | Newmarket Wells 13-16 | 2026-02-11
CENTRAL | February | On site to complete station check and respond to well 13 pump fault alarm. -Verified analyzers: Influent Free Chlorine @ 8:44 Grab: 2.74 mg/L Analyzer: 2.77 mg/L Effluent Free Chlorine @ 8:40 Grab: 2.48 mg/L Analyzer: 2.51 mg/L Treated Free Chlorine @ 8:36 Grab: 0.12 mg/L Analyzer: 0.13 mg/L Treated Total Chlorine @ 8:36 Grab: 2.84 mg/L Analyzer: 2.87 mg/L -Collected operational samples -Entered data into PD sheet -Checked trends -Cleared well 13 fault alarm with no issues. However, upon manually starting the well, the fault returned after a few minutes of the well running to waste (confirmed via masl drawdown). Created work order W11649808 for maintenance to address possible waste valve fail to close or other cause of fault. | Newmarket Wells 13-16 | 2026-02-09
CENTRAL | February | On-site for a station and equipment check No issues found Chemical levels and systems ok Topped up ammonia day tank 2 12 cylinders and 0 bags of ammonia in inventory Weekly bacti samples taken Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@1040 G:2.60 A:2.67mg/L Effluent Free@1043 G:2.42 A:2.41mg/L Treated Free@1046 G:0.08 A:0.12mg/L Treated Total@1047 G:2.62 A:2.68mg/L Mono-2.30 FA-0.04 TA-0.50 | Newmarket Wells 13-16 | 2026-02-04
CENTRAL | February | On site to complete station check with Christian B. -Verified analyzers: Influent Free Chlorine @ 8:58 Grab: 2.62 mg/L Analyzer: 2.73 mg/L Effluent Free Chlorine @ 9:05 Grab: 2.40 mg/L Analyzer: 2.34 mg/L Treated Free Chlorine @ 9:16 Grab: 0.10 mg/L Analyzer: 0.12 mg/L Treated Total Chlorine @ 9:22 Grab: 2.72 mg/L Analyzer: 2.75 mg/L -Topped up mineral oil well 13 -Entered data into PD sheet -Checked trends | Newmarket Wells 13-16 | 2026-02-06
WEST | February | Station Check (no issues found) Pump running | Nobleton Booster Pumping Station | 2026-02-23
WEST | February | On site for station check. Pump running, chamber dry - site all ok | Nobleton Booster Pumping Station | 2026-02-02
WEST | February | On site for station check. Pump running, completed jhsc inspection - site all ok | Nobleton Booster Pumping Station | 2026-02-17
WEST | February | -on site to complete station check -unable to access site due to snow, visual inspection only | Nobleton Booster Pumping Station | 2026-02-13
WEST | February | In to Complete Station Check and to collect bacti sample w11620002 Residuals free Grab 1.15mg/L Analyzer 1.13mg/L Total Grab: 1.58mg/L, Analyzer: 1.56mg/L Topped up both reagents on site ki and acetate No new known issues on site | Nobleton North Elevated Tank | 2026-02-25
WEST | February | In to Complete Station Check and to collect bacti sample w11588666 Residuals free Grab 1.23mg/L Analyzer 1.18mg/L Total Grab: 1.78mg/L, Analyzer: 1.86mg/L Collected in house lab sample No new known issues on site | Nobleton North Elevated Tank | 2026-02-11
WEST | February | In to Complete Station Check and to collect bacti sample w11605377 Residuals free Grab 1.42mg/L Analyzer 1.37mg/L Total Grab: 1.86mg/L, Analyzer: 1.90mg/L No new known issues on site | Nobleton North Elevated Tank | 2026-02-17
WEST | February | On site for the following NBET27, JHSC Health and Safety Inspection, Nobleton North ET (1M NBET27, Siemens Depolox 5/Micro 2000, Chlorine Analyzer, Maintenance, Nobleton North ET (1M) NBET27, Inlet/Outlet Heat Trace System, Inspection, Nobleton North ET [WINTER] (1M) NBET27, High & Low Water Level Alarm, Test, Nobleton North ET (2M) NBET27, Low Temperature Alarm, Test, Nobleton North, ET (1M) NBET27, Nobleton North ET - Portable Gasoline Generator Test (1M) No new issues on site | Nobleton North Elevated Tank | 2026-02-12
WEST | February | In to Complete Station Check and to collect bacti sample w11568074 Residuals free Grab 1.44mg/L Analyzer 1.41mg/L Total Grab: 1.95mg/L, Analyzer: 1.99mg/L No new known issues on site | Nobleton North Elevated Tank | 2026-02-04
WEST | February | In to Complete Station Check and to collect bacti sample w11620002 Residuals free Grab 1.33mg/L Analyzer 1.31mg/L Total Grab: 1.89mg/L, Analyzer: 1.85mg/L No new known issues on site | Nobleton South Elevated Tank | 2026-02-25
WEST | February | On site to replace unit heater | Nobleton South Elevated Tank | 2026-02-26
WEST | February | In to Complete Station Check and to collect bacti sample w11605377 Residuals free Grab 1.42mg/L Analyzer 1.41mg/L Total Grab: 1.89mg/L, Analyzer: 1.83mg/L No new known issues on site | Nobleton South Elevated Tank | 2026-02-17
WEST | February | On site for the following NBET, JHSC Health and Safety Inspection, Nobleton South ET (1M) NBET, Sump Pit System, Inspection, Nobleton South ET (1M) NBET, Siemens Depolox 5/Micro 2000, Chlorine Analyzer, Maintenance, Nobleton South, ET (1M) - adjusted total from 1.60-1.90mg/L after multiple grabs Topped up acetate NBET, Inlet/Outlet Heat Trace System, Inspection, Nobleton South ET [WINTER] (1M) - system was in alarm - cleared alarms - all ok NBET, Sensing Line Heat Trace System, Inspection, Nobleton South, ET LWINTER_ (1M) NBET, Low Temperature Alarm, Test, Nobleton South, ET (1M) NBET, Gasoline Generator, Test Run, Nobleton South ET (1M) | Nobleton South Elevated Tank | 2026-02-12
WEST | February | In to Complete Station Check and to collect bacti sample w11588666 Residuals free Grab 1.45mg/L Analyzer 1.50mg/L Total Grab: 1.65mg/L, Analyzer: 1.63mg/L Replaced KI solution Gate on site is broken - informed TL Collected in house lab sample No new known issues on site | Nobleton South Elevated Tank | 2026-02-11
WEST | February | In to Complete Station Check and to collect bacti sample w11568074 Residuals free Grab 1.48mg/L Analyzer 1.50mg/L Total Grab: 1.78mg/L, Analyzer: 1.74mg/L Reagents all ok Heater not working created work order W11639030 and informed TL No new known issues on site | Nobleton South Elevated Tank | 2026-02-04
WEST | February | Onsite for station check Well running Checked residuals mg/l Influent @1244 Free analyzer 1.89 grab 2.02 Effluent @1241 Free analyzer 1.84 grab 1.84 Total grab 2.15 | Nobleton Well 2 | 2026-02-20
WEST | February | In to Complete Station Check and bactisample w11620002 Residuals Effluent free Grab: 1.60mg/L, Analyzer: 1.54mg/L Total grab 1.92mg/L Influent free Grab: 1.92mg/L, Analyzer: 1.93mg/L Reagents - all okay No new known issues on site | Nobleton Well 2 | 2026-02-25
WEST | February | Station Check (no issues found) Input data to PWQ Verified CL17s (mg/L) 10:40 Influent Free: Grab 1.92, A 1.87 10:30 Treated Free: Grab 1.90, A 1.87 Total: Grab 2.66 10:45 operational samples taken 11:00 Deactivated duty | Nobleton Well 2 | 2026-02-23
WEST | February | In to Complete Station Check Residuals Effluent free Grab: 1.45mg/L, Analyzer: 1.45mg/L Influent free Grab: 1.58mg/L, Analyzer: 1.59mg/L No other issues on site | Nobleton Well 2 | 2026-02-27
WEST | February | Attending site to check Effluent Chlorine analyzer (W11611597). Push button switches were found to be inoperable. Replaced bush buttons and verified reading. Also checked Chlorinator #1 due to leak at stem (W11625398). Greased stem as the existing grease was clumping and dry. Notified Operations to try it out next time they are on site. It was left in Manual. ROC was notified before and after maintenance activities. | Nobleton Well 2 | 2026-02-02
WEST | February | Onsite to troubleshoot AIT1 (Influent) buttons not working Informed ROC. ROC asked us to confirm with operations as duty was just about to start. All OK. ROC placed duty to manual off. Replaced main board and colorimeter. Took grabs. No adjustments required G = 1.81mg/L A = 1.83mg/L Cleared associated alarms Asked ROC to return duty to auto. Well 2 started. Monitored for a while. All OK Armed building and left site | Nobleton Well 2 | 2026-02-24
WEST | February | In to Complete Station Check Residuals Effluent free Grab: 1.78mg/L, Analyzer: 1.76mg/L Influent free Grab: 1.86mg/L, Analyzer: 1.81mg/L Reagents - all okay Chlorinator 1 still oos work order has been created No other issues on site | Nobleton Well 2 | 2026-02-02
WEST | February | Onsite to perform annual maintenance/Rebuild both chlorinators. Informed ROC and Cole was on site, isolated gas cylinders and purged the lines. We rebuilt both the chlorinators. performed vacuum test by running booster pumps in local mode. No leak found. Performed gas calibration and Performed verification and Put chlorinators back in service. No issues. Cole was onsite and back flushed the lines and started well in auto mode. No issues. Informed ROC, armed the building and left the site. | Nobleton Well 2 | 2026-02-18
WEST | February | On site to assist INST with chlorinator overhauls. Repair minor leak on cl2 tubing/parker fitting from regulator 1 to PVC ball valve. Replace 4 inlet ball valves to chlorinators, will replace remaining ball valves and label (last changed 2024, some in good condition, some fair). Tested and both chlorine systems holding vacuum, chlorinator 2 vacuum much higher than 1, could be related to issue with corp stop ball valve and lance (due for replacement). | Nobleton Well 2 | 2026-02-18
WEST | February | -On site to complete station check and collect weekly micro. samples -sample work order # W11588666 -well running in manual -cl2 booster pump # 2 running at 208 psi -chlorinator # 2 43% open dosing 23.5 ppd, vac = - 620 mbar, DF = 87.0% -silicate pump #2 running at 46%, 55.9 ml/min, 90 psi -checked equipment -reviewed trends -CL17 reagents ok -verified chlorine analyzers: 08:44 - Effluent Analyzer = 1.70 mg/L 08:44 - Effluent grab: Free chlorine = 1.76 mg/L Total chlorine = 2.12 mg/L 08:49 - collected weekly treated water micro. sample 08:50 - collected weekly raw water micro. sample -recorded readings in PWQ sheet -completed work orders, informed ROC of work -completed Dechlorination Puck Dispenser Inspection and Cleaning -completed Chemical System Inspection - Silicate -cleaned and flushed injection points -ran pumps into graduated cylinder: Pump #1 max flow = 117 ml/min Pump #2 max flow = 110 ml/min -reinstalled injection points, silicate system back to normal operation -completed Chemical System Inspection - Chlorine -found vacuum leak upstream of chlorinators, created follow up work order to troubleshoot -backflushed for several minutes as a precaution -completed Chlorine Analyzer, Maintenance -cleaned analyzers, flushed sample lines -replaced effluent sample line -verified analyzers after maintenance: 12:26 - Effluent Analyzer = 2.35 mg/L 12:26 - Effluent grab: Free chlorine = 2.42 mg/L 12:27 - Influent Analyzer = 1.86 mg/L 12:27 - Influent grab: Free chlorine = 1.91 mg/L -completed JHSC Health and Safety Inspection -completed Turbidimeter, Maintenance -cleaned and verified turbidimeter -completed Deep Well Exhaust Valve, Test -completed Pressure Relief Valve, Test -completed Chlorine Leak Detector, Test -started well in manual, tested all chemical systems in auto -site back to normal operation | Nobleton Well 2 | 2026-02-11
WEST | February | Backflush well 2 to remove highly chlorinated water after calibrations. Place Cl2 booster pumps, w2 back to auto. Monitor startup, no issues. | Nobleton Well 2 | 2026-02-18
WEST | February | -on site to complete station check -well running in manual -cl2 booster pump # 2 running at 208 psi -chlorinator # 2 42% open dosing 22.5 ppd, vac = - 620 mbar, DF = 85.0% -silicate pump #2 running at 46%, 55.8 ml/min, 90 psi -checked equipment -reviewed trends -CL17 reagents ok -verified chlorine analyzers: 08:20 - Effluent Analyzer = 1.75 mg/L 08:20 - Effluent grab: Free chlorine = 1.76 mg/L Total chlorine = 2.11 mg/L 08:28 - Influent Analyzer = 1.82 mg/L 08:28 - Influent grab: Free chlorine = 1.77 mg/L -recorded readings in PWQ sheet -no issues found -well back into auto - off | Nobleton Well 2 | 2026-02-13
WEST | February | In to Complete Station Check and bactisample w11605377 Residuals Effluent free Grab: 1.81mg/L, Analyzer: 1.85mg/L Total grab 2.02mg/L Influent free Grab: 1.91mg/L, Analyzer: 1.85mg/L Reagents - all okay No new known issues on site | Nobleton Well 2 | 2026-02-17
WEST | February | In to Complete Station Check Residuals Effluent free Grab: 1.62mg/L, Analyzer: 1.67mg/L Influent free Grab: 1.79mg/L, Analyzer: 1.80mg/L Reagents - replaced effluent reagents Collected sample for in house lab No other issues on site | Nobleton Well 2 | 2026-02-09
WEST | February | In to Complete Station Check and bactisample w11568074 Residuals Effluent free Grab: 1.75mg/L, Analyzer: 1.76mg/L Total grab 1.92mg/L Influent free Grab: 2.12mg/L, Analyzer: 2.07mg/L Reagents - all okay Raw pH 7.99 Placed chlorinator 1 back online - all seems okay will continue to monitor No new known issues on site | Nobleton Well 2 | 2026-02-04
WEST | February | In to Complete Station Check and to collect bacti sample w11620002 Residuals Effluent free Grab: 1.56mg/L, Analyzer: 1.57mg/L Effluent total Grab 1.82mg/L Influent free Grab: 2.30mg/L, Analyzer: 2.23mg/L Reagents - all okay No other issues on site | Nobleton Wells 3 & 7 | 2026-02-25
WEST | February | Station Check (no issues found) Input data to PWQ Verified CL17s (mg/L) 11:35 Influent: Free: Grab 2.08, A 2.12 11:40 Treated: Free: Grab 1.63, A 1.63 Total Grab 1.90 Reagent change for both Influent and Treated cl17s Hypo tanks top up Operational samples collected | Nobleton Wells 3 & 7 | 2026-02-23
WEST | February | On site to receive Sodium Hypochlorite. | Nobleton Wells 3 & 7 | 2026-02-24
WEST | February | In to Complete Station Check Residuals Effluent free Grab: 1.48mg/L, Analyzer: 1.41mg/L Influent free Grab: 1.80mg/L, Analyzer: 1.86mg/L Reagents - all okay No other issues on site | Nobleton Wells 3 & 7 | 2026-02-02
WEST | February | In to Complete Station Check and to collect bacti sample w11588666 Topped up hypo tanks Residuals Effluent free Grab: 1.78mg/L, Analyzer: 1.77mg/L Effluent total Grab 1.98mg/L Influent free Grab: 2.18mg/L, Analyzer: 2.16mg/L Reagents - all okay No other issues on site | Nobleton Wells 3 & 7 | 2026-02-11
WEST | February | On site for station check Check trends: all okay Duty not active Verified Analyzers 10:20-Effluent free Grab: 1.49mg/L, Analyzer: 1.45mg/L 10:25-Influent free Grab: 1.52mg/L, Analyzer: 1.49mg/L Reagents all good entered values in PWQ sheet Equipment all okay. | Nobleton Wells 3 & 7 | 2026-02-13
WEST | February | Onsite for station check Well running Checked residuals mg/l Effluent @11:28 Free analyzer 1.69 grab 1.61 Total grab 1.91 Influent @11:30 Free analyzer 2.15 grab 2.19 Total grab 3.14 | Nobleton Wells 3 & 7 | 2026-02-20
WEST | February | In to Complete Station Check and to collect bacti sample w11588666 Topped up hypo tanks Residuals Effluent free Grab: 1.57mg/L, Analyzer: 1.44mg/L Effluent total Grab 1.89mg/L Adjusted effluent free from 1.44-1.57 after multiple grabs Influent free Grab: 2.02mg/L, Analyzer: 2.04mg/L Accepted chlorine hypo delivery Reagents - all okay No other issues on site | Nobleton Wells 3 & 7 | 2026-02-17
WEST | February | On site for the following NBW3, Deep Well Exhaust Valve, Test, Nobleton Well 3 (1M) NBW3, Sodium Hypochlorite System Maintenance, Nobleton Well 3 (1M) NBW3, Surge Relief Valve, Exercise, Nobleton Well 3 (6M) NBW3, Pressure Relief Valve, Test, Nobleton Well 3 (1M) NBW3, Diesel Generator Test Run, Nobleton Well 3 (1M) Hours start 371.1 stop 372.3hrs Fuel start 850 stop 844L NBW3, Chlorine Analyzer Maintenance, Nobleton Well 3 (1M) NBW3, Low/High Temperature Alarm, Test, Nobleton Well 3 (1M) NBW3, Ventilation System, Inspection, Nobleton Well 3 (1M) NBW3, Turbidimeter, Maintenance, Nobleton Well 3 (1M) NBW3, Check Valve, Inspection, Nobleton Well 3 (6M) NBW3, Sodium Hypochlorite System Inspection, Nobleton Well 3 (1M) NBW3, Chemical System Inspection - Silicate, Nobleton Well 3 (1M) Completed JHSC inspection No new issues on site | Nobleton Wells 3 & 7 | 2026-02-05
WEST | February | On site to receive sodium hypochlorite. | Nobleton Wells 3 & 7 | 2026-02-03
WEST | February | In to Complete Station Check Residuals Effluent free Grab: 1.62mg/L, Analyzer: 1.60mg/L Influent free Grab: 1.74mg/L, Analyzer: 1.78mg/L Reagents - all okay No other issues on site | Nobleton Wells 3 & 7 | 2026-02-06
WEST | February | In to Complete Station Check Residuals Effluent free Grab: 1.48mg/L, Analyzer: 1.50mg/L Influent free Grab: 1.54mg/L, Analyzer: 1.51mg/L Reagents - all okay No other issues on site | Nobleton Wells 3 & 7 | 2026-02-06
WEST | February | In to Complete Station Check and to collect bacti sample w11568074 Well locked out on low influent. Residual came up after well shut down. Inspected hypo lines for leaks and primed hypo pump 2 no issues noticed restarted well with hypo pump 2 Raw pH 8.08 Residuals Effluent free Grab: 1.60mg/L, Analyzer: 1.55mg/L Effluent total Grab 1.78mg/L Influent free Grab: 2.44mg/L, Analyzer: 2.53mg/L Reagents - all okay No other issues on site | Nobleton Wells 3 & 7 | 2026-02-04
WEST | February | On site for station check Residuals Effluent free Grab: 1.61mg/L, Analyzer: 1.65mg/L Influent free Grab: 1.56mg/L, Analyzer: 1.55mg/L Topped up hypo tanks - logged in pwq Collected in house lab sample No other issues on site | Nobleton Wells 3 & 7 | 2026-02-09
WEST | February | In to troubleshoot NBW5 following low influent lockout yesterday, hours after placing online following chlorine system overhaul (ejector regulator, fittings, lines). Started back flushing to sanitary sewer. Tested Chlorinator 2 system. Vacuum is good, capacity is good, no obvious issues. Operating vacuum -80mmHg. Broke chlorinator 1 rotameter during vacuum purge, will replace. Start w5 manual on after backflush to test cl2 dosing and system performance. Observed yesterday on startup that raw water to exhaust was very odorous (sulfur etc). Not as odorous on startup today. Residual dropped off during runtime after first hour yesterday, will monitor performance. Lower NBW5 flow setpoint from 28L/s to 21L/s to allow higher chlorine dose if aquifer demand is increased or unstable. Residuals: mg/L 1138 Influent G FCl 3.48 A FCl 0.76 (Wait for analyzer sample / average to catch up to grab residuals) 1142 Influent G FCl 3.24 A FCl 3.27 Adjust chlorinator DFs from 195 to 180 based on residuals and dosing change when lowering flow to 21L/s. Increase residual SP from 2.60 to 2.80mg/L while monitoring performance. | Nobleton Wells 5 & 6 | 2026-02-25
WEST | February | -Filled silicate tank 45.69 cm to 77.97 cm -Installed and set up replacement silicate pump #1 -ran pump from scada into calibration column - max flow = 155 ml/min, adjusted scada max flow setpoint 130 to 150 ml/min -started well in manual and tested silicate pump 1 in auto - no issues -noticed pump 1 discharge pressure high - stopped well and replaced injection point check valve -tested pump again - ok | Nobleton Wells 3 & 7 | 2026-02-09
WEST | February | In to Complete Station Check and to collect bacti sample w11620002 Residuals Effluent free Grab: 1.55 mg/L, Analyzer: 1.62mg/L Effluent total Grab 2.09mg/L Influent free Grab: 3.14mg/L, Analyzer: 3.30mg/L Primed Nasi p1 and p2 are air in line Reagents - all okay No other issues on site | Nobleton Wells 5 & 6 | 2026-02-25
WEST | February | In to Complete Station Check Residuals Effluent free Grab: 1.89mg/L, Analyzer: 1.95mg/L Influent free Grab: 2.62mg/L, Analyzer: 2.66mg/L Reagents - all okay No other issues on site | Nobleton Wells 5 & 6 | 2026-02-27
WEST | February | Changed cl2 cylinder with J.Muzzin | Nobleton Wells 5 & 6 | 2026-02-26
WEST | February | Station Check (no issues found) Input data to PWQ Verified CL17s (mg/l) 1:25 Influent Free: Grab 0.076, A 0.72 1:30 Effluent Free: Grab 1.78, A 1.83 Total Grab 2.60 Station manual off due to suspected Chlorination issues | Nobleton Wells 5 & 6 | 2026-02-23
WEST | February | On site with Sean Peoples to replace battery on generator. ROC notified. New battery installation complete. Generator controller removed from Auto. Generator run locally to ensure battery function. ROC notified. Generator run complete. Generator controller returned to Auto. ROC notified. | Nobleton Wells 5 & 6 | 2026-02-24
WEST | February | Onsite to work on chlorination system Purged system Changed out regulators and injectors Changed out tubing and Parker fittings Tested for vacuum on both chlorinators and booster pumps Primed lines Started well Influent grabs @1518 Free analyzer 3.68 grab 3.34 @1536 Free analyzer 2.88 grab 2.90 Left cl2 booster pumps in local off | Nobleton Wells 5 & 6 | 2026-02-24
WEST | February | -replaced chlorinator #1 rotameter -attempted to vacuum test chlorinator however found ejector #1 not producing vacuum -replaced ejector, however service water line is too short, leaving chlorinator #1 OOS until can collect materials | Nobleton Wells 5 & 6 | 2026-02-27
WEST | February | -on site to complete station check -well running in manual -well #6 offline and isolated from distribution system -chlorinator #1 OOS -cl2 booster pump # 2 running at 180 psi -chlorinator # 2 87% open dosing 43 ppd, vac = - 80 mbar, DF = 189% -silicate pump #2 running at 58%, 11.6 rpm, 105 psi -checked equipment -reviewed trends -CL17 reagents ok -verified chlorine analyzers: 08:53 - Effluent Analyzer = 2.34 mg/L 08:53 - Effluent grab: Free chlorine = 2.40 mg/L Total chlorine = 2.82 mg/L 08:57 - Influent Analyzer = 2.61 mg/L 08:57 - Influent grab: Free chlorine = 3.04/3.08/3.02 mg/L 09:02 - adjusted influent analyzer to 3.05 mg/L based on average of 3 grabs -recorded readings in PWQ sheet -no other issues found -silicate pump #1 OOS due to high turbidity, primed pump and tested in auto - no issues observed, pumping at max flow of 114 ml/min. Will leave pump in auto duty 2 -completed JHSC Health and Safety Inspection | Nobleton Wells 5 & 6 | 2026-02-13
WEST | February | In to Complete Station Check Residuals Effluent free Grab: 2.16mg/L, Analyzer: 2.22mg/L Influent free Grab: 1.82mg/L, Analyzer: 1.88mg/L Reagents - changed out influent free reagents No other issues on site | Nobleton Wells 5 & 6 | 2026-02-02
WEST | February | Insulate hot water pipes Test backflow preventer Passed | Nobleton Wells 5 & 6 | 2026-02-13
WEST | February | Work on hot water line for flushing silicate lines | Nobleton Wells 5 & 6 | 2026-02-12
WEST | February | On site with Total Power generator technician to conduct annual generator maintenance and load bank test. Generator not in auto. ROC notified. 2 hr load bank test completed. Generator returned to auto. 15 min station transfer test completed. Station returned to Utility supply. ROC notified. | Nobleton Wells 5 & 6 | 2026-02-10
WEST | February | In to Complete Station Check and to collect bacti sample w11588666 Residuals Effluent free Grab: 2.18mg/L, Analyzer: 2.17mg/L Effluent total Grab 2.52mg/L Influent free Grab: 2.52mg/L, Analyzer: 2.52mg/L Reagents - all okay No other issues on site | Nobleton Wells 5 & 6 | 2026-02-11
WEST | February | Onsite for station check Started duty to have well running for station check Checked residuals mg/l Influent @1007 Free analyzer 2.67 grab 2.66 Total grab 3.00 Effluent @1009 Free analyzer 1.88 grab 1.86 Total grab 2.24 Adjusted flow to ntu analyzer causing spike Primed silicate p1 Chlorinator 1 oos | Nobleton Wells 5 & 6 | 2026-02-20
WEST | February | In to Complete Station Check and to collect bacti sample w11605377 Residuals Effluent free Grab: 2.02mg/L, Analyzer: 1.90mg/L Effluent total Grab 2.64mg/L Influent free Grab: 2.70mg/L, Analyzer: 2.68mg/L Primed Nasi p2 air in line Reagents - all okay No other issues on site | Nobleton Wells 5 & 6 | 2026-02-17
WEST | February | -on site to respond to low effluent switch lockout -started backflushing/dechlor 15:15 -checked chlorine system - chlorinated/vaccum and booster pump all ok -tighten fitting -checked trends: influent dropped and chlorinated not able to keep ?? -verified effluent analyzer 15:35: 1.53mg/l grab:1.50mg/l -verified influent analyzer 15:34: 0.36mg/l grab: 0.32mg/l -stopped backflushing at 16:00 -place well back into duty and started well -chlorinated maxing out with an influent of 1.70- 1.80mg/l -man/stopped well - will keep well as backup for the rest of the weekend | Nobleton Wells 5 & 6 | 2026-02-21
WEST | February | On site for the following NBW56, Air Release, Valve Flushing, Nobleton, Well 5/6 (1M) NBW5, Sodium Silicate Feed Peristaltic Pump Inspection, Nobleton Well 5 (1200 Hrs.) NBW56, Turbidimeter Maintenance, Nobleton Well 5/6 (1M) NBW56, Chlorine Analyzer, Maintenance, Nobleton Well 5/6 (1M) NBW56, Chlorine Cylinder Emergency Repair Kit Inspection, Nobleton, Well 5/6 (1M) NBW56, Chlorine Leak Detector, Test, Nobleton, Well 5/6 (1M) NBW56, High/Low Alarm, Test, Nobleton, Well 5/6 (1M) NBW56, Chemical System Inspection - Silicate, Nobleton W5/6 (1M) NBW56, Diesel Generator Test Run, Nobleton, Well 5/6 (1M) - contractor (TotalPower) on site with electrician for annual testing generator ran 2 hours on load and transferred to site - all ok. Start hours 258:42 stop hours 261:10 Start fuel 91/89cm stop fuel 85/83cm NBW56, Diesel Fuel Spill Alarm, Test, Nobleton Well 5/6 (1M) NBW5, Dehumidifier, Cleaning & Inspection, Nobleton Well 5 (1M) NBW56, Pressure Relief Valve, Inspection, Nobleton Well 5/6 (1M) NBW56, Chemical System Inspection - Chlorine, Nobleton W5/6 (1M) NBW56, Chlorine Scrubber, Check, Nobleton, Well 5/6 (1M) | Nobleton Wells 5 & 6 | 2026-02-10
WEST | February | In to Complete Station Check Checked chlorinator 1 seems to be an issue. Rotates bouncing when in service. No vacuum leak. Will place in manual off and inform TL. Residuals Effluent free Grab: 1.62mg/L, Analyzer: 1.58mg/L Influent free Grab: 2.60mg/L, Analyzer: 2.64mg/L Collected sample for in house lab No other issues on site | Nobleton Wells 5 & 6 | 2026-02-09
WEST | February | On site with Dave T to change chlorine cylinder 1 from 0-68kg Troubleshooting chlorinator one. Think the issue is with the ejector, will speak with TL. Troubleshooting caused a low influent. Backflushed well; placed dechlor in chamber. Leaving chlorinator 1 and booster pump 1 in manual off for the night will inform oncall | Nobleton Wells 5 & 6 | 2026-02-09
WEST | February | In to Complete Station Check and to collect bacti sample w11568074 Residuals Effluent free Grab: 2.12mg/L, Analyzer: 2.02mg/L Effluent total Grab 2.42mg/L Influent free Grab: 2.66mg/L, Analyzer: 2.72mg/L Reagents - all okay Raw pH 8.07 Cleaned turbidimeter No other issues on site | Nobleton Wells 5 & 6 | 2026-02-04
WEST | February | Install water heater for flushing silicate lines Called away to Keswick for emergency | Nobleton Wells 5 & 6 | 2026-02-09
WEST | February | Onsite to respond to well being locked out due to low effluent cl2 Checked residuals mg/l @1036 Free analyzer 0.44 grab 0.48 Started back flush @1041 Grab @1046 Analyzer 0.49 grab 0.77 Flushed ntu analyzer @1101 Effluent free analyzer 1.48 grab 1.42 @1102 Influent free analyzer 0.31 grab 0.42 @1113 Influent analyzer 0.49 grab 0.80 Stopped back flush @1115 Approximately 41m3 Restated well @1117 Primed silicate p2 | Nobleton Wells 5 & 6 | 2026-02-08
CENTRAL | February | On-site for a station and equipment check No issues found Weekly bacti samples taken Verified analyzers and entered all readings and grabs into PWQ sheet INLET- Free@1054 G:0.06 A:0.02mg/L Total@1056 G:2.68 A:2.65mg/ Mono-2.54 FA-0.03 FA-0.53 NO2-0.0 OUTLET Free@1057 G:0.03 A:0.08mg/L Total@1100 G:2.34 A:2.41mg/L Mono-2.06 FA-0.06 TA-0.47 NO2-0.001 | Queensville Elevated Tank | 2026-02-25
WEST | February | In to Complete Station Check Residuals Effluent free Grab: 1.89mg/L, Analyzer: 1.90mg/L Influent free Grab: 1.88mg/L, Analyzer: 1.81mg/L Reagents - all okay No other issues on site | Nobleton Wells 5 & 6 | 2026-02-06
CENTRAL | February | Restarted the Operator Interface Terminal due to Windows OS updates. The Remote Operations Center was notified prior to doing the work. | Queensville Elevated Tank | 2026-02-23
CENTRAL | February | Onsite to trouble shoot lower readings on outlet analyzer Informed ROC (Adam B) of ongoings, Deactivated duty at Ivsbridge so that QVET would be filling during maintenance Placed outlet analyzer in Cal mode at 13;30 Cleaned debris from all parts of analyzer and took grabs at 14:05 Out Total: 2.20 mg/l Out Free: 0.08 mg/l Outlet analyzer now reading accurately back in service ET ops normal | Queensville Elevated Tank | 2026-02-19
CENTRAL | February | On-site for a station and equipment check Filling/Draining Operational sample taken Bacti sample taken Verified analyzers, entered all grabs and readings into PWQ sheet Inlet Free@0927 G:0.05 A:0.01mg/L Inlet Total@0931 G:2.26 A:2.55mg/L Outlet Free@0936 G:0.07 A:0.07mg/L Outlet Total@0938 G:1.71 A:1.68mg/L | Queensville Elevated Tank | 2026-02-17
CENTRAL | February | On-site for a station and equipment check No issues found Took weekly bacti sample Verified analyzers and entered all readings and grabs into PWQ sheet Inlet Free@1218 G:0.04 A:0.01mg/L Inlet Total@1220 G:2.90 A:2.80mg/L Outlet Free@1223 G:0.09 A:0.06mg/L Outlet Total@1227 G:1.98 A:1.92mg/L | Queensville Elevated Tank | 2026-02-11
CENTRAL | February | Tested high and low level alarms. | Queensville Elevated Tank | 2026-02-06
CENTRAL | February | on-site for various work orders; Dechlor puck dispenser cleaned and re-stocked JHSC inspection completed inlet/outlet heat trace inspection completed Air valve inspection completed Actuated vales exercised portable generator testing completed Comprehensive housekeeping completed | Queensville Elevated Tank | 2026-02-03
CENTRAL | February | On-site for a station and equipment check No issues found Changed reagent KI in outlet analyzer Took weekly bacti sample Verified analyzers and entered all readings and grabs into PWQ sheet Inlet Free@0911 G:0.03 A:0.01mg/L Inlet Total@0914 G:2.84 A:2.75mg/L Outlet free@09:15 G:0.05 A:0.06mg/L Outlet Total@0917 G:2.07 A:2.01mg/L | Queensville Elevated Tank | 2026-02-05
CENTRAL | February | On-site for a station and equipment check No issues found Chemical levels and systems ok 15 cylinders and 2 bags of ammonia in inventory Cylinder change bank B wit J Zhang Topped up NaSi tanks Topped up ammonia day tank 2 Changed treated total reagents Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@1250 G:2.66 A:2.71mg/L Effluent Free@1251 G:0.11 A:0.12mg/L Treated Free@1251 G:0.07 A:0.09mg/L Treated Total@1255 G:2.76 A:2.74mg/L | Queensville Wells No. 1 and 2 | 2026-02-27
CENTRAL | February | Restarted the Operator Interface Terminal due to Windows OS updates. The wells were off and the Remote Operations Center was notified prior to doing the work. | Queensville Wells No. 1 and 2 | 2026-02-23
CENTRAL | February | On-site for a station and equipment check No issues found Weekly bacti samples taken Chemical levels and systems ok 18 cylinders and 4 bags of ammonia in inventory Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@1311 G:2.88 A:2.91mg/L Effluent Free@1319 G:2.82 A:2.74mg/L Treated Free@1326 G:0.13 A:0.21mg/L Treated Total@1330 G:3.42 A:3.47mg/L Mono-2.81 FA-0.05 TA-0.61mg/L | Queensville Wells No. 1 and 2 | 2026-02-25
CENTRAL | February | Onsite to complete chlorine system overhaul PM. 10:10 Notified ROC of work being completed. 10:20 Activiated duty 1 to top up QVETQS before working on chlorine system. 11:45. Deactivated duty and locked out wells 1 and 2. Purged chlorine system with William M. replaced injector 1 and 2. Replaced PE tubing downstream of chlorinators. Tested chlorine system. Briefly bqckflushed with dechlorination pucks at outfall. No issues foujnd. 13:28 Placed wells back to auto. Notified ROC of work complete. | Queensville Wells No. 1 and 2 | 2026-02-24
CENTRAL | February | On-site for a station and equipment check. No issues found Cylinder bank 2 change with J Silva Contractor on-site for generator load test Topped up oil on well pump 2 15 cylinders and 4 bags of ammonia in inventory Hot flush both silicate pumps and lines. Primed and back flushed Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@1056 G:2.82 A:2.96mg/L Effluent Free@1102 G:0.26 A:0.21mg/L Treated Free@1104 G:0.08 A:0.13mg/L Treated Total@1107 G:3.02 A:3.07mg/L | Queensville Wells No. 1 and 2 | 2026-02-02
CENTRAL | February | Onsite for station check and operational samples Recordings in PWQ sheet adjusted effluent free chlorine analyzer from 2.45 mg/L to 2.80 mg/L free ammonia was 0.00 mg/L before the effluent chlorine analyzer change, after it was reading 0.07 mg/L batched ammonia tank 1. station ok | Queensville Wells No. 1 and 2 | 2026-02-23
CENTRAL | February | On-site for a station and equipment check Noticed that silicate pump motor spins but pump does not. Locked out at panel, work order W11670454 Weekly bacti and operational samples taken Topped ammonia day tank 2 Chemical levels and systems ok 9 cylinders and 6 bags of ammonia in inventory Verified analyzers, entered all readings and grabs into PWQ sheet Influent Free@1110 G:2.94 A:2.92mg/L Effluent Free@1112 G:2.46 A:2.49mg/L Treated Free@1114 G:0.25 A:0.21mg/L Treated Total@1117 G:3.50 A:3.42mg/L Mono-2.62 FA-0.02 TA-0.53mg/L | Queensville Wells No. 1 and 2 | 2026-02-17
CENTRAL | February | -When reviewing SCADA trends, notice treated total was a flat line at 3.47mg/L since yesterday - treated total analyzer was still in cleaning mode - stopped the well and put the total analyzer back to service - verified the analyzer: grab=2.98mg/L analyzer=3.02mg/L - put wells back to auto - there is no user between the wall house and Queensville ET - reviewed trends at Queensville ET - inlet total was always above 2.30mg/L, treated free at the well house was always above 0.05mg/L which well was running, and effluent free readings were in normal operating range - CT requirement was always met | Queensville Wells No. 1 and 2 | 2026-02-12
CENTRAL | February | On site to reconnect generator with Freguson Electric | Queensville Wells No. 1 and 2 | 2026-02-10
CENTRAL | February | On-site for a station and equipment check No issues found Chemical levels and systems ok 12 cylinders and 4 bags of ammonia in inventory Took weekly bacti samples Cleaned analyzers Spanned effluent free analyzer 2.86 to 2.45 based on 3 grabs-2.48,2.46,2.42 Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@1048 G:2.52 A:2.54mg/L Effluent Free@1059 G:2.45 A:2.45 Treated Free@1101 G:0.28 A:0.23mg/L Treated Total@1109 G:3.48 A:3.53 Mono-2.84 FA-0.04 TA-0.60mg/L | Queensville Wells No. 1 and 2 | 2026-02-11
CENTRAL | February | on-site for various work orders contractors on-site as well -deep well exhaust valves inspected (both wells) -Cl2 leak detection and system inspection completed -ammonia system inspection and drawdowns completed -ammonia pump diaphragms inspected -NTU calibration verification completed -JHSC inspection completed -dechlor puck dispenser ok -Silicate pumps inspeected | Queensville Wells No. 1 and 2 | 2026-02-12
CENTRAL | February | On-site for a station and equipment check No issues found. Chemical levels and systems ok Topped up NaSi day tanks Topped up ammonia day tank 1 Changed cylinder bank B with J Zhang Changed reagents in effluent free analyzer Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@1333 G:2.72 A:2.77mg/L Effluent Free@1335 G:1.37 A:1.43mg/L Treated Free@1337 G:0.07 A:0.07mg/L Treated Total@1341 G:2.60 A:2.65mg/L | Queensville Wells No. 1 and 2 | 2026-02-13
CENTRAL | February | Station Check (no issues found) Input data to PWQ 8:35 Verified CL17s (mg/l) Influent Free: Grab 2.66, A 2.71 Effluent Free: Grab 1.86, A 1.86 Treated: Free: Grab 0.04, A 0.06 Total: Grab 2.70, A 2.71 Influent CL17 (new reagents) Silicate day tank top up Chlorine cylinder change with JZ Chlorine bulk shipment accepted | Queensville Wells No. 1 and 2 | 2026-02-20
CENTRAL | February | On site with Sean Peoples to investigate Well 2 fail to start alarms. ROC notified. Found solenoid on waste valve to be missing fastening cap. Cap for solenoid, timer relay and control relay for waste cycle have now been replaced. With assistance from Ben Hess, Well 2 operation tested. Initial run signal sent to starter before being energized, causing fail to start and uncommanded stop. After resetting, well ran without incident. Well 2 placed in Auto and returned to normal operation. ROC notified. | Queensville Wells No. 1 and 2 | 2026-02-18
CENTRAL | February | Under direction of OIC William Mather. Worked with contractors to reconnect and test station generator. Notified ROC of events. Once station was on gen power then Wel1 was commanded to run for 1hr on standby power. After testing completed ROC helped shut down the well and we transfer power back to utility. Everything was put back to remote auto. | Queensville Wells No. 1 and 2 | 2026-02-10
CENTRAL | February | On-site for a station and equipment check No issues found Topped up NaSi day tanks. Topped up ammonia day tank 2 Topped up mineral oil for both wells Changed Total Free reagents and cleaned unit Changed cylinder bank 1 with J Zhang 12 cylinders and 4 bags of ammonia in inventory Took operational sample Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@1040 G:2.98 A:2.92mg/L Effluent Free@1045 G:2.86 A:2.89mg/L Treated Free@1053 G:0.24 A:0.22mg/L Treated Total@1055 G:3.48 A3.56mg/L Mono-2.93 FA-0.02 TA-0.60 | Queensville Wells No. 1 and 2 | 2026-02-09
CENTRAL | February | On-site for a station and equipment check No issues found Contractors onsite Chemical levels and systems ok 15 cylinders and 2 bags of ammonia in inventory Topped up NaSi day tanks Topped up ammonia day tank 1 Weekly bacti samples taken PH taken Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@0809 G:3.06 A:3.01mg/L Effluent Free@0819 G:2.72 A:2.77mg/L Treated Free@0821 G:0.25 A:0.21mg/L Treated Total@0823 G:3.50 A:3.44mg/L Mono-2.83 FA-0.05 TA-0.61 PH-8.07 | Queensville Wells No. 1 and 2 | 2026-02-05
CENTRAL | February | Back onsite because of funny analyzer readings Ran well 3 in manual Put chlorine dose in manual to stabilize chlorine residual Treated chlorine analyzer still jumping around. Will notify Eric S that treated total chlorine analyzer needs more troubleshooting leaving Well 3 and 4 manual off | Queensville Wells No. 3 and 4 | 2026-02-23
CENTRAL | February | On-site for a station and equipment check No issues found Chemical levels and systems ok 15 cylinders and 15 bags of ammonia in inventory Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@1031 G:2.78 A:2.76mg/L Effluent Free@1032 G:0.91 A:0.92mg/L Treated Free@1033 G:0.08 A:0.09mg/L Treated Total@1038 G:2.84 A:2.83 mg/L | Queensville Wells No. 1 and 2 | 2026-02-06
CENTRAL | February | Attending site to continue to troubleshoot erratic readings from Total chlorine analyzer (W11685985). Replaced all internal chlorine analyzer components and issue still persists. Changed signal average from 2 to 4, and reading looks much more stable. Will check the trend on Monday and determine if we will be required to replace it with a CL17sc analyzer. Had wells placed in auto for the weekend via ROC. ROC was notified before and after maintenance activities. | Queensville Wells No. 3 and 4 | 2026-02-27
CENTRAL | February | On-site for a station and equipment check No issues found Weekly bacti samples taken Chemical levels and systems ok 15 cylinders and 6 bags of ammonia in inventory Verified analyzers, entered all readings and grabs into PWQ sheet Left wells in manual off for next day step test Influent Free@0824 G:2.82 A:2.78mg/L Effluent Free@0831 G:2.32 A:2.29mg/L Treated Free@0906 G:0.14 A:0.11mg/L Treated Total@0909 G:3.12 A:2.98mg/L | Queensville Wells No. 3 and 4 | 2026-02-25
CENTRAL | February | Restarted the Operator Interface Terminal due to Windows OS updates. The wells were off and the Remote Operations Center was notified prior to doing the work. | Queensville Wells No. 3 and 4 | 2026-02-23
CENTRAL | February | On-site for a station and equipment check No issues found. Chemical levels and systems ok 15 cylinders and 6 bags of ammonia in inventory Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@1328 G:2.82 A:2.70mg/L Effluent Free@1332 G:0.97 A:1.01mg/L Treated Free@1334 G:0.05 A:0.04mg/L Treated Total@1336 G:2.59 A:2.42mg/L | Queensville Wells No. 3 and 4 | 2026-02-27
CENTRAL | February | Onsite to troubleshoot AIT4 (Treated Total) Erratic readings Informed ROC and operations. Well was already in manual off. Replaced main board and colorimeter. Replaced reagents and tubings. Took grabs. adjusted analyzer accordingly. G = 2.34 mg/L A = 2.37 mg/L Cleared associated alarms. No issues. Informed ROC,Armed building and left site | Queensville Wells No. 3 and 4 | 2026-02-24
CENTRAL | February | On-site to aide in maintenance step test of well 3 Received diesel for generator. Cleaned, hot flushed and primed NaSi lines. | Queensville Wells No. 3 and 4 | 2026-02-26
CENTRAL | February | Attending site to check erratic readings from Total chlorine analyzer (W11685985). Tried many things to get the readings to stabilize but the only thing that had any effect was changing the tubing and buffer/reagent. ROC was notified before and after maintenance activities. | Queensville Wells No. 3 and 4 | 2026-02-25
CENTRAL | February | Onsite for station check and operational samples Recordings in PD sheet Treated total analyzer readings jumping, cleaned analyzer adjusted flow. Readings still not normal, notified Eric S. Cleaned turbidimeter | Queensville Wells No. 3 and 4 | 2026-02-23
CENTRAL | February | Attending site to check Total chlorine analyzer (W11683435). Found moisture on colorimeter circuit board. Replaced colorimeter and verified analyzer reading. No adjustments were required. ROC was notified before and after maintenance activities. | Queensville Wells No. 3 and 4 | 2026-02-23
CENTRAL | February | On-site for a station and equipment check No issues found Chemical levels are systems ok 15 cylinder and 4 bags of ammonia in inventory Hot flush silicate lines, primed and back flushed Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@1250 G:2.48 A:2.50mg/L Effluent Free@1256 G:0.70 A:0.75mg/L Treated Free@1258 G:0.03 A:0.04mg/L Treated Total@1303 G:2.38 A:2.42mg/L | Queensville Wells No. 3 and 4 | 2026-02-02
CENTRAL | February | Attending site to check Treated Free chlorine analyzer (W11621115). Push button switches were found to be inoperable. Replaced bush buttons and verified reading. ROC was notified before and after maintenance activities. | Queensville Wells No. 3 and 4 | 2026-02-02
CENTRAL | February | On-site for various work orders. Completed CL2 system inspection. Dechlor and and back flushed. Verified ammonia pumps dosing and volumes. Ok Ensured treated total is reading in signal average 2 and changed reagents. Trend is very variable, will continue to monitor remotely Trouble shooting well/generator with T Zimmerman-Jones | Queensville Wells No. 3 and 4 | 2026-02-19
CENTRAL | February | On-site for a station and equipment check No issues found Well 3 running in schedule mode Chemical levels and systems ok 15 cylinders and 6 bags of ammonia in inventory Took weekly bacti samples Topped up mineral oil well 4 Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@0909 G:2.56 A:2.54mg/L Effluent Free@0915 G:2.46 A:2.58mg/L Treated Free@0916 G:0.10 A:0.14mg/L Treated Total@0920 G:3.10 A:3.16mg/L Mono-2.55mg/L FA-0.07mg/L FA-0.57mg/L | Queensville Wells No. 3 and 4 | 2026-02-11
CENTRAL | February | Onsite to investigate influence chlorine analyzer. 13:00 free analyzer reading 0.00 mg/l. Grab matching at 0.00. Will Mather?s onsite and cleaned silicate injections points. Total reading 0.61 mg/l. Contact tank has been back flushed briefly earlier. Replaced analyzer pinch tubes. Tested chlorine system to ensure dosing is correct. Back flushed contact tank after putting dechlore pucks in outfall. Once influence grabs reaching 0.94 mg/l total chlorine completed backflush. Ran well 3 in manual at 50 L/s. 15:10 verified influence chlorine grab 2.48. Analyzer at 2.50. 15:15 Been Hess onsite to relieve me. | Queensville Wells No. 3 and 4 | 2026-02-10
CENTRAL | February | On-site for a station and equipment check No issues found Chemical levels and systems ok 15 cylinders and 6 bags of ammonia in inventory Cleaned and confirmed flow to treated total analyzer after sporadic values this weekends trends. Will monitor Took weekly bacti and operational samples Verified analyzers, entered all readings and grabs into PWQ sheet Influent Free@1421 G:2.18 A:2.12mg/L Effluent Free@1424 G:2.60 A:2.48mg/L Treated Free@1427 G:0.18 A:0.15mg/L Treated Total@1430 G:3.48 A:3.42mg/L Mono-2.56 FA-0.03 TA-0.53mg/L | Queensville Wells No. 3 and 4 | 2026-02-17
CENTRAL | February | On-site for a station and equipment check Standing water and damaged door noted in PAC room for well 3. Sent to SR Team lead Chemical levels and systems ok 15 cylinders and 6 bags of ammonia in inventory Put NaSi pump 2 back in service Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@1019 G:2.62 A:2,72mg/L Effluent Free@1021 G:0.15 A:0.14mg/L Treated Free@1024 G:0.07 A:0.06mg/L Treated Total@1028 G:2.62 A:2.74mg/L | Queensville Wells No. 3 and 4 | 2026-02-13
CENTRAL | February | -on site with total power to do the annual maintenance on generator. Placed unit in manual and notified ROC of alarms that will be present from our work (0900) finished test and placed unit back to auto and breaker closed 1500 let roc know and cleared alarms. Under direction of oic. | Queensville Wells No. 3 and 4 | 2026-02-11
CENTRAL | February | -on site to assist investigation of well 4 ESTOP alarm. As per Dan B email the Vfd panel did have a blown fuse. I replaced it and test ran it with Will m to confirm operation. We then did a gen test to see if we could replicate that problem from yesterday but had no luck in that. Both wells ran fine on generator power. Left site with both pumps in manual with Will. Under direction of oic. | Queensville Wells No. 3 and 4 | 2026-02-19
CENTRAL | February | On-site for; Silicate hot flush, prime and backflush -JHSC -Refill eyewash fluid -Deep well exhaust inspections -Flow controls flushed and cleaned -CL2 leak detection completed during generator test, unable to run well 3 switched well duties and notified Tyler Generator tested under load fuel start 950L hours start 712.43 end 714 600 volts 60.0hz oil temp160'F oil pressure 85psi coolant 160'f | Queensville Wells No. 3 and 4 | 2026-02-18
CENTRAL | February | Onsite responding to both well 3 and well 4 fail to start/OOS. Able to get Well 3 to run by pressing ?auto? on the VFD beside the motor. Well 4 has an ?emergency stop alarm? without the E-stop being pressed. On the VFD it?s error is ?Run Enable Missing? check parameter 20.12 Leaving Well 4 OOS for the night will notify electricians. Well 3 running in Auto duty-ok | Queensville Wells No. 3 and 4 | 2026-02-18
CENTRAL | February | -on site to address the generator rad leak (1200) called roc to let them know we are on site and might cause alarms during troubleshooting. Tyler smith and myself found that the rad hose was loose and causing fluid to leak. We tightened connection and monitored. We test ran unit to confirm that the unit was not continuously leaking. I also changed the breaker that feeds the block heater as that seems to have failed. Cleared alarms and placed unit back to auto. Under direction of oic. | Queensville Wells No. 3 and 4 | 2026-02-12
CENTRAL | February | On site to remove and replace Well 4 motor in response to vibration issues. Test ran to waste. | Queensville Wells No. 3 and 4 | 2026-02-10
CENTRAL | February | On site to respond to power issue with Queensville wealth for Control cabinet. Tested voltage and amp draw. Checked for correct fuse size installation. Seems to be OK now. | Queensville Wells No. 3 and 4 | 2026-02-20
CENTRAL | February | Station Check (no issues found) Input data to PWQ 10:17 Verified CL17s (mg/l) Influent Free: Grab 2.60, A 2.66 Effluent Free: Grab 0.12, A 0.14 Treated: Free Grab 0.04, A 0.06 Total: 2.58, A 2.66 | Queensville Wells No. 3 and 4 | 2026-02-20
CENTRAL | February | On site to commission well 4 with Dan boate, Kyle Rae and William Mather Updated Ethernet cards with latest firmware Tested well 4 VFD in SCADA manual and checked if PID tuning works. Tested Well 3 VFD analog data and comms, set up well 3 vfd parameters for comms Wells are back in auto and no alarms present | Queensville Wells No. 3 and 4 | 2026-02-05
CENTRAL | February | Was onsite earlier to finish up getting Wells 3 and 4 running. Put chlorine dosing into manual during startup. Had Influent and effluent free chlorine analyzers in signal average 1 on initial startup. Once system seemed balanced, put the chlorine dosing back to auto and the analyzers signal average back to 2. Leaving the well manual running until it passes through the contact tank | Queensville Wells No. 3 and 4 | 2026-02-10
CENTRAL | February | On-site for a station and equipment check No issues found Chemical levels and systems ok 15 cylinders and 4 bags of ammonia in inventory Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@1335 G:2:72 A:2.60mg/L Effluent Free@1338 G:0.41 A:0.40 mg/L Treated Free@1339 G:0.08 A:0.05mg/L Treated Total@1343 G:2.52 A:2.44mg/L | Queensville Wells No. 3 and 4 | 2026-02-05
CENTRAL | February | On site to commission new VFD for W4. Also worked with PCS to get Ethernet connection working with W3. | Queensville Wells No. 3 and 4 | 2026-02-05
CENTRAL | February | -on site with water maintenance team to investigate the vibration issues. We tested p3 for a cycle and noticed the vibration and pressure that it is pumping out. Once the ct tank had finished pumping we then ran p4 to test first test at 1300 we found that the waste valve faulted the pump. We tried putting the pump to manual speed and closing the discharge valve to see if the vibration changed but noticed no difference. We then had it test in auto speed and closing the valve but noticed change in vibration was noted. We finished our test 1430 once the ct tank finished and left the pump in manual for the weekend. We would like to do more testing Monday. I let Justin Q know and he is going to notify the oncall operator. Under direction of oic. | Queensville Wells No. 3 and 4 | 2026-02-06
CENTRAL | February | On-site for a station and equipment check No issues found Chemical levels and systems ok 15 cylinders and 6 bags of ammonia in inventory Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@0947 G:2.54 A:2.58mg/L Effluent Free@0951 G:0.16 A:0.14mg/L Treated Free@0951 G:0.05 A:0.05mg/L Treated Total@0955 G:2.34 A:2.38mg/L | Queensville Wells No. 3 and 4 | 2026-02-06
CENTRAL | February | -on site to troubleshoot well 4 vibration. With iws we tested the pump running to system (1000) called roc to inform them of work being done. We ran the well at about 70l/s for about 30mins for testing to see if we could replicate the vibration of the motor. We also ran the motor at various speeds. No major alarms were noted. Did have an hi turbidity alarm come in we acknowledged it at 1115. We did run the motor decoupled to the pump for further testing. Our tests determined we should try replacing the motor. We left the motor decoupled and in manual off for the evening. Under direction of oic. | Queensville Wells No. 3 and 4 | 2026-02-09
CENTRAL | February | On-site to collect weekly bacti samples. Will return to complete full station and equipment check after delivery of samples. | Queensville Wells No. 3 and 4 | 2026-02-05
CENTRAL | February | On-site for a station and equipment check No issues found. Chemical levels and systems ok 15 cylinders and 6 bags of ammonia in inventory Tyler and crew on-site to trouble wells. Frozen waste, managed to get thawed and flows Took operational sample Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@1313 G:2.68 A:2.73 Effluent Free@1321 G:2.58 A:2.61 Treated Free@1323 G:0.12 A:0.14 Treated Total @1324 G:3.40 A:3.34 | Queensville Wells No. 3 and 4 | 2026-02-09
CENTRAL | February | Check vibrating motor number 4 | Queensville Wells No. 3 and 4 | 2026-02-06
WEST | February | - on site to complete station check -checked trends: all ok -entered reading in PWQ: all ok -took chlorine grab 09:05 -free cl: 0.06mg/l -total cl: 1.90mg/l -man/start pump 2 -equipment all ok | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2026-02-27
WEST | February | -on site to complete station check and collect weekly bacti W11620180 -checked trends: -entered readings in PWQ -took grab and sample from east cell 14:15 -free cl: 0.04mg/l -total cl: 1.38mg/l -west cell grab 15:20 -free cl: 0.06mg/l -total cl: 1.42mg/l -equipment all ok | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2026-02-25
WEST | February | Onsite to try and repair limitorque valve actuator in resevoir pipe gallery. Could not make any progress. Valve actuator still out of service. | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2026-02-25
WEST | February | On site to repair malfunctioning actuator with replacement control board. Tested ok. Actuator back on service, left in open position in local mode. | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2026-02-26
WEST | February | Onsite for station check Checked residuals mg/l @1435 Total grab 1.82 Free grab 0.01 P1 in local oos | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2026-02-23
WEST | February | -on site for station check -checked trends: all ok -entered reading in PWQ: all ok -took chlorine grab 09:20 -free cl: 0.07mg/l -total cl: 1.75mg/l -equipment and heating all ok | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2026-02-02
WEST | February | -on site to complete station check and weekly bacti W11588844 -checked trends: all ok -entered readings in PWQ: all ok -took chlorine grab and sample east cell 14:10 -free cl: 0.0.6mg/l -total cl: 1.62mg/l - west cell grab 14:15 -free cl: 0.10mg/l -total cl: 1.60mg/l -equipment all ok | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2026-02-11
WEST | February | -on site for station check -checked trends all ok -entered reading in PWQ: all ok -took chlorine grab 13:30 -free cl: 0.07mg/l -total cl: 1.83mg/l -equipment all ok | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2026-02-18
WEST | February | -on site for station check -checked trends: all ok -entered readings in PWQ: all ok -took chlorine grab 14:05 -free cl: 0.03mg/l -total cl: 1.65mg/l -man/start to pump 2 to listen pump - minimal cavitation -will leave pump running for 30 minutes | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2026-02-20
WEST | February | -wrong entry | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2026-02-16
WEST | February | -on site attending comm fail -reservoir 4.64 M -power restored -historian heart outstanding -Ian Williams will clear -site is trending- confirmed with ROC | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2026-02-10
WEST | February | -on site for station check and weekly bacti W11605685 -checked trends: all ok -entered readings in PWQ: all ok -took chlorine grab and sample west cell 12:55 -free cl: 0.11mg/l -total cl: 1.43mg/l -east cell grab 13:00 -free cl: 0.12mg/l -total cl: 1.52mg/l -adjusted top floor heater- area was over 30C -no other issues | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2026-02-17
WEST | February | -on site to complete station check -checked trends: all ok -entered readings in PWQ: all ok -took chlorine grab 11:10 -free cl: 0.09mg/l -total cl: 1.72mg/l -ran pump 3 to check cavitation -took video- placed pump in man/off | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2026-02-13
WEST | February | Locked out pump 1 and unwired motor. This pump and motor set with be coming out for a complete refurbishment. Isolated inlet and began draining. | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2026-02-03
WEST | February | Attended station with security to investigate intrusion alarm- noticed pumping station bay doors not locked properly, lock not connected to latch causing the door to rattle. Placed a temporary lock and zip ties to prevent door from rattling- station fully secured. Will inform maintenance to fix latch. Informed ROC. No outstanding alarms onsite. | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2026-02-07
WEST | February | Tested flood alarm Deactivated Jefferson duty Ran pumps Inspected actuated valves and check calves of pumps 2&3 Reactivated duty after Tested hi/lo temp in reservoir Deactivated duty Exercised actuated valve to cell 1 Cell 2 cable faulted with no power tried flipping breaker Exercised manual valves Tested sump Completed jhsc | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2026-02-09
WEST | February | -On-site to complete reservoir station check and collect sample -reservoir level = 85%, filling -checked equipment -reviewed trends -found RES_MV1 with no power to actuator, created work order for CMS -collected grab samples: 08:34 - East Cell: Free Chlorine = 0.03 mg/L Total Chlorine = 1.53 mg/L 08:37 - West Cell: Free Chlorine = 0.02 mg/L Total Chlorine = 1.52 mg/L MCL = 1.33 mg/L TNH3 = 0.34 mg/L FNH3 = 0.08 mg/L NO2 = 0.000 mg/L temp = 7.6 08:40 - collected weekly regulatory micro. sample from West Cell - W/O # W11568536 -recorded readings in PWQ sheet -no other issues found | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2026-02-04
WEST | February | -on site to complete PS station check -pumps manual off, pump #1 OOS -checked equipment -reviewed trends -recorded readings in PWQ sheet -checked residuals: 13:36 - Grabs: Free Chlorine = 0.00 mg/L Total Chlorine = 1.78 mg/L -no issues found | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2026-02-06
CENTRAL | February | Deleted entry. This entry was intended for coons tower. | Richmond Hill Bloomington Elevated Tank | 2026-02-25
CENTRAL | February | On-site for station check and sampling. MBHP - W11620030. 13:28 Tower level 62% and filling at 78 l/s. 13:30 Verified inlet analyzer (mg/l): Free chlorine grab: 0.03. Total chlorine grab: 1.95 Analyzer: 1.95. 13:38 Verified outlet analyzer (mg/l) and collected sample. free chlorine grab: 0.04. Total chlorine grab: 1.84. analyzer: 1.87. Free ammonia: 0.09 Total ammonia: 0.41 Monochloramine: 1.64. Nitrite: 0.003. pH: 7.98. Recorded readings into PD sheets. Station and equipment: No issues identified. | Richmond Hill Bloomington Elevated Tank | 2026-02-25
CENTRAL | February | Station Check (no issues found) Input data to PWQ Verified CL17s(mg/L) 3:15 oultlet: Free: Grab 0.05 Total: Grab 1.78, A 1.82 3:20 Inlet: Free: Grab 0.06 Total: Grab 1.92, A 1.99 3:25 #11588694 bact. & operational samples Heat trace (inlet and outlet) cleared | Richmond Hill Bloomington Elevated Tank | 2026-02-11
CENTRAL | February | Informed ROC (Angelica) onsite to complete monthly Maximo workorders CL17 maintenance/cleaning in CAL mode start @ 12:55 pm Took grabs @ 1:30 pm to verify analyzers Inlet Total: 1.90 mg/l Outlet Total: 1.80 mg/l Cl17?s both back in seevice No adjustment necessary JHSC inspection - no issues Housekeeping Valve excercise Low temp alarm test - ok Heat trace inspection - ok Recirc pump excercise complete ET ops normal | Richmond Hill Bloomington Elevated Tank | 2026-02-18
CENTRAL | February | On-site for station check and sampling. MBDW - W11605549. 10:22 Tower level 69% and draining at 92 l/s. 10:24 Verified inlet analyzer (mg/l): Free chlorine grab: 0.07. Total chlorine grab: 2.05. Analyzer: 1.99. 10:34 Verified outlet analyzer (mg/l) and collected sample. (correction to add when sample was collected). free chlorine grab: 0.05. Total chlorine grab: 1.74. analyzer: 1.77 Free ammonia: 0.08 Total ammonia: 0.40. Monochloramine: 1.59. Nitrite: 0.000. Temperature: Celsius. pH: 7.99 Recorded readings into PD sheets. Station and equipment: No issues identified. | Richmond Hill Bloomington Elevated Tank | 2026-02-17
CENTRAL | February | On-site for a station and equipment check No issues found Weekly bacti sample taken while draining Verified analyzers and entered all readings and grabs into PWQ sheet Inlet Total@1304 G:1.71 A:1.79mg/L Outlet Total@1307 G:1.82 A:178mg/L | Richmond Hill Bloomington Elevated Tank | 2026-02-04
CENTRAL | February | On-site for station check and sampling. W11620030 14:17 Tower level 66% and filling at 115 l/s. 14:18 Verified inlet chlorine analyzer (mg/l): Free chlorine grab: 0.03. Total chlorine grab: 1.96. Analyzer: 2.01. 14:25 verified outlat analyzer and collected sample. free chlorine grab: 0.08. Total chlorine grab: 1.80. Analyzer: 1.81. Ph: 8.03 Free ammonia: 0.09 Total ammonia: 0.41 Monochloramine: 1.66. ?Nitrite: 0.003. Temperature: 7.0 celsius. Recorded data in process sheets. No issues found. | Richmond Hill Coon's Elevated Tank | 2026-02-25
CENTRAL | February | Onsite to complete monthly Maximo workorders Informed ROC (Carter D) of ongoings Cleaned both Inlet/Outlet CL17 analyzers in Cal mode from 9 am - 9:30 am Took grabs @ 9:30 am Inlet Total: 1.95 mg/l Outlet Total: 1.85 mg/l Standardized outlet only to match grabs Reagents ok JHSC inspection no issues found General housekeeping complete ET ops normal | Richmond Hill Coon's Elevated Tank | 2026-02-26
CENTRAL | February | Station Check (no other issues found) Input data to PWQ 13:30 Verified CL17s (mg/l) Inlet: Free Grab: 0.05 Total: Free Grab 1.92, A 1.99 Outlet: Free Grab 0.05 Total: Grab 1.88, A 1.90 13:40 # 11588694 bact. and operational samples Inlet heat trace active alarm (will monitor) | Richmond Hill Coon's Elevated Tank | 2026-02-11
CENTRAL | February | On-site for station check and sampling. MBHP - W11605549 Outstanding inlet riser heat trace low temp alarm. Cleared alarm with no issues. Heat trace is on. 09:14 Tower level 65% and draining at 89 l/s. 09:17 Verified inlet chlorine analyzer (mg/l): Free chlorine grab: 0.03. Total chlorine grab: 1.88. Analyzer: 1.96. 09:29 verified outlat analyzer and collected sample. free chlorine grab: 0.05. Total chlorine grab: 1.77. Analyzer: 1.76. Ph: 7.98 Free ammonia: 0.09 Total ammonia: 0.40 Monochloramine: 1.56 ?Nitrite: 0.003. Temperature: 5.6 Celsius. Recorded data in process sheets. No issues found. | Richmond Hill Coon's Elevated Tank | 2026-02-17
CENTRAL | February | On-site for a station and equipment check No issues found Took weekly bacti sample while draining Verified analyzers and entered all readings and grabs into PWQ sheet Inlet Total@1342 G:1.76 A:1.81mg/L Outlet Total@1444 G:1.75 A:1.75mg/L | Richmond Hill Coon's Elevated Tank | 2026-02-04
EAST | February | Under Direction of OIC Dan Zhou On Site for; - Station checks Data in PWQ Workbook Grabs @ 14:58 FCl: 0.03 mg/L TCl: 1.57 mg/L Duty active , pumps 1,4 Equipment OOS: None Facility OK | Richmond Hill Pugsley Pumping Station | 2026-02-26
EAST | February | Under Direction of OIC Dan Zhou On Site for; - Station checks Data in PWQ Workbook Grabs @ 09:13 FCl: 0.04 mg/L TCl: 1.55 mg/L Duty not active Equipment OOS: Cell 2 valve (RSR2_MV1) - refer to central team for details Facility OK | Richmond Hill Pugsley Pumping Station | 2026-02-23
EAST | February | Under Direction of OIC Dan Zhou On Site for; - Station checks Data in PWQ Workbook Grabs @ 13:55 FCl: 0.08 mg/L TCl: 1.57 mg/L Pump 1 and 4 active in duty 1 Equipment OOS: none Facility OK | Richmond Hill Pugsley Pumping Station | 2026-02-02
EAST | February | Check air pressure in check valves Add air to check valves 1 2 and 3 | Richmond Hill Pugsley Pumping Station | 2026-02-02
EAST | February | Under Direction of OIC Dan Zhou On Site for; - Station checks - Comprehensive house cleaning - Control panel lights inspection Data in PWQ Workbook Grabs @ 14:28 FCl: 0.06 mg/L TCl: 1.56 mg/L Pump 2 and 3 active in duty 1 Equipment OOS: none Facility OK | Richmond Hill Pugsley Pumping Station | 2026-02-20
EAST | February | Under direction of OIC Dan Zhou On site for; - Generator test - JHSC Health and Safety Inspection - Flood alarm test - Surge anticipator test (PRV) test - Flood Alarm test - Hoist inspection - Station check - butterfly valve exercise 1,2,3,4 Generator Test: @ 13:04 placed pump 2 in manual, and pump 1,3,4 in manual off Start hours: 377.6 Start time: 13:13 hrs. Stop Hours: 378.9 (includes cool down time) Stop Time: 14:33 hrs. Run Time: 1 hr. 20. mins. Start Fuel: 6431 L Stop Fuel: 6500 L (LIT not accurate) Pre run checks; Battery Cell Levels: NA Battery Terminals and Cables: Ok Oil Level: Ok Coolant Level: Ok Fluid Leaks: Ok Coolant Recirculating pump: Ok Faulty Gauges: Ok @ 13:39 hrs. Put pump 2 in Manual On (Active), Generator under load @ 14:09 hrs. put pump 2 in manual off Operating Current: 29 amps Operating Frequency: 60 Hz Operating Voltage: 600 Volts, Engine speed: 1798 RPM Water/coolant Temp: 160 f Oil Pressure: 65 psi kPa Oil temp: 176 f Grab Samples taken @ 13:58 hrs. FCl: 0.05 mg/L TCl: 1.57 mg/L Surge anticipators; - Discharge side surge anticipators function - Control panel for suction side surge anticipators does not function, informed lead hand Dan Zhou, and they had created a work order @ 14:34 returned pumps 1,2,3,4 to auto Pumps 3,4 active in duty 1 Equipment OOS: None Facility OK | Richmond Hill Pugsley Pumping Station | 2026-02-19
EAST | February | Under Direction of OIC Joe Mazza On Site for; - Station checks Data in PWQ Workbook Grabs @ 11:55 hrs. FCl: 0.06 mg/L TCl: 1.64 mg/L Pump 4 and 3 active in duty 1 Equipment OOS: none Facility OK | Richmond Hill Pugsley Pumping Station | 2026-02-13
EAST | February | Under Direction of OIC Dan Zhou On Site for; - Station checks Data in PWQ Workbook Grabs @ 14:38 FCl: 0.07 mg/L TCl: 1.58 mg/L Pump 2 and 3 active in duty 1 Equipment OOS: RSR2_MV1 for cell 2, contact central for details Facility OK | Richmond Hill Pugsley Pumping Station | 2026-02-09
EAST | February | Under direction fo OIC Dan Zhou On site for; - Station checks Data in PWQ workbook Grabs @ 14:46 FCl:0.08 mg/L TCl: 1.58 mg/L Duty active pumps 2,3 in duty 1 Equipment OOS: Cell 2 valve in local open due to power failure Feb. 5 2026, disregard fail to open alarm, work order has been created. Facility OK | Richmond Hill Pugsley Pumping Station | 2026-02-06
EAST | February | Vibration readings | Richmond Hill Pugsley Pumping Station | 2026-02-03
WEST | February | Trends checked and ok, equipment checked and ok All measurements are in mg/l HL - time :9:45 Free grab 0.05 Total grab 3.50 vs analyzer 3.55 Mono 2.10 Bact sample grabbed - 10:20 Reservoir - time 10:30 Free grab 0.01 Total grab 3.80 vs 3.76 analyzer Mono 3.60 Post injection time 10:45 Free grab 0.03 Total grab 2.33 vs analyzer 2.28 | Schomberg Water Treatment Plant & Wells 2-4 | 2026-02-25
WEST | February | Under the direction of Jacob Muzzin, Worked along side Network Analyst Kevin Wen, to replaced a Network switch to Cisco IE3300 inside a network panel for SHTP3 and Control panel for Well 2 building. Provided 24 VDC power to new switch from 24VDC power supply. Informed the ROC regarding possible comm fail alarm. After the replacement, checked all the ports and reset the comm alarms. | Schomberg Water Treatment Plant & Wells 2-4 | 2026-02-12
WEST | February | Changed cl2 cylinder with J. Bloye | Schomberg Water Treatment Plant & Wells 2-4 | 2026-02-26
WEST | February | Trends checked and ok, equipment checked and ok All measurements are in mg/l High lift - time: 9:57 Free grab 0.03 Total grab 3.39 vs 3.48 analyzer Mono 2.96 Reservoir - time 10:10 Free grab 0.06 Total grab 3.66 vs analyzer 3.71 Mono 3.08 Post filter - time 10:27 Free grab 0.02 Total grab 2:18 vs analyzer 2:26 Topped up KMNO tank to 82.3 cm (369 L) - 2:45 | Schomberg Water Treatment Plant & Wells 2-4 | 2026-02-23
WEST | February | Onsite for station check Checked residuals mg/l Hl @0928 Total analyzer 3.41 grab 3.42 Free grab 0.06 Mcl grab 2.91 Reservoir @1311 Total analyzer 3.79 grab 3.88 Free grab 0.10 Mcl grab 3.62 Through plant @1325 Total analyzer 2.24 grab 2.34 Free grab 0.07 | Schomberg Water Treatment Plant & Wells 2-4 | 2026-02-27
WEST | February | 09:51- ROC called regarding filter 3 turbidity being high after backwash. CMU 5 W11695345 issued. attended site, cleaned vial, flushed line and verified with std, and then replaced the vial for filter 3 turbidity meter. value remained high. Noticed flow to the analyzer was considerably low (0.35l/s) , increased the flow to 58l/s . Noticed Turbidity value coming down. | Schomberg Water Treatment Plant & Wells 2-4 | 2026-02-27
WEST | February | Hl @1224 Total analyzer 3.44 grab 3.46 Free grab 0.03 Mcl grab 2.85 Reservoir @1227 Total analyzer 3.77 grab 3.80 Free grab 0.06 Through plant @1236 Total analyzer 2.31 grab 2.24 Free grab 0.06 Topped up kmno tank Rotated reservoir cells | Schomberg Water Treatment Plant & Wells 2-4 | 2026-02-02
WEST | February | W11620255- SWO on call 08:00 -consultation call regarding Filter 3 turbidity high. 08:30- Advised ROC to initiate backwash. | Schomberg Water Treatment Plant & Wells 2-4 | 2026-02-27
WEST | February | Eat 0.14 nitrate 0.296 nitrite 0.000 ammonium 2.36 Hl 0.17 nitrate 0.172 nitrite 0.000 ammonium 2.65 F3 0.15 F2 0.09 F1 0.11 Raw 1.80 ammonium 2.96 W4 1.99 ammonium 3.33 W2 1.48 ammonium 2.66 | Schomberg Water Treatment Plant & Wells 2-4 | 2026-02-02
WEST | January | Review UV alarm monthly summary and power failure from January 6th. System appears to have interlocked and shut down normally. Flow registered for 30 seconds during shutdown while UV dose went below 40mj/cm2. Non reportable, no compliance issues. | Schomberg Water Treatment Plant & Wells 2-4 | 2026-01-06
WEST | February | On site for the scheduled PM work orders with D. Simm. Informed ROC about the work being done. W11583827 SHTP, Electric Actuated Valves Inspection, Schomberg WTP W3&4 W11583844 SHTP, Exhaust Fan Inspection, Schomberg WTP W3&4 W11583871 SHTP, Check Valves Inspection, Schomberg WTP W3&4 W11583887 SHTP, Dehumidifier Inspection, Schomberg WTP W3&4 W11591705 SHTP, Fire Pumps and Motors, Inspection, W11602054 SHTP W2, Pressure Relief Valve, Inspection Topped up KMNO4 tank 1- 16.04cm/71.72L to 81.6cm/ 365L | Schomberg Water Treatment Plant & Wells 2-4 | 2026-02-18
WEST | February | On site for step test with water resources on well 3 Started well 3 at approximately 9 L/s Reduced plant flow from 18 to 9 l/s Reduced filters in production from 2 to 1 In order to maintain level in raw water tank For the duration of step test put post uv cl2 dosage to manual Increased flow to 18l/s manipulated plant to continue flow. Increased to 26l/s hi flow alarm came in. Stopped well and plant for hour long quiet period After that placed set points back to normal and restarted plant | Schomberg Water Treatment Plant & Wells 2-4 | 2026-02-19
WEST | February | Onsite for station check Checked residuals mg/l Hl @0851 Total analyzer 3.47 grab 3.48 Free grab 0.03 Mcl grab 3.10 Reservoir @0904 Total analyzer 3.78 grab 3.74 Free grab 0.02 Mcl grab 3.41 Through plant @0912 Total analyzer 2.28 grab 2.32 Free grab 0.06 Tested well 3 at various flows in prep for step test - High flow alarm came in | Schomberg Water Treatment Plant & Wells 2-4 | 2026-02-13
WEST | February | Onsite for station check and to collect weekly micro W11605647 Hl @0920 Total analyzer 3.55 grab 3.52 Free grab 0.04 Mcl grab 3.05 Reservoir @0926 Total analyzer 3.67 grab 3.70 Free grab 0.05 Mcl grab 3.37 Through plant @0929 Total analyzer 2.29 grab 2.30 Free 0.05 Rotated reservoir cells closed north opened south Changed reagents in reservoir cl17sc analyzer | Schomberg Water Treatment Plant & Wells 2-4 | 2026-02-17
WEST | February | Responding to reservoir chlorine analyzer fault. Worked with ROC to rotate sample pumps and run both pumps to see if alarm would clear. Alarm came back in repeatedly but analyzer appeared to be trending. Found sample P2 tubing leak. Replaced tubing and primed. Reservoir analyzer reagent level low. Unable to replace, no spare reagents on site. Should last until tomorrow, will request operator bring reagents and spares to site and stock as required. Residuals: mg/L 1450 Reservoir A: tcl 3.81 G: tcl 3.64 Span calibrate reservoir Cl17sc to 3.64 from 3.81mg/L based on grabs (at 1504, value after was 3.79mg/L). Cleaned Treated NTU analyzer sample vial, clears vial clarity alarm. (Was faulted on SCADA, still trending values). Chlorine dosing is in Manual setting, will request switch to auto dosing (post-UV) once reservoir Cl17 is checked again on next station check. | Schomberg Water Treatment Plant & Wells 2-4 | 2026-02-16
WEST | February | Onsite for station check and to collect weekly micro sample W11588872 Through plant @0923 Total analyzer 2.29 grab 2.25 Free grab 0.05 Reservoir @0952 Total analyzer 3.77 grab 3.80 Free grab 0.06 Mcl grab 3.37 High lift @1031 Total analyzer 3.58 analyzer 3.50 Free grab 0.05 Rotated well duty to collect bact sample | Schomberg Water Treatment Plant & Wells 2-4 | 2026-02-11
WEST | February | -received call from ROC regarding step test interim -override stop set point adjusted 5.1m to 5.3m - pump 2 not adjusting to 17l/s adjustment - manual speed set from 70% to 92% for 17.1l/s - reservoir high level adjusted from 90% to 85% to warn ROC to activate high lift | Schomberg Water Treatment Plant & Wells 2-4 | 2026-02-18
WEST | February | Onsite to complete work orders Completed jhsc on well 2 Inspected actuated valves at well 2 no issues Inspected high lift pumps 1,2 &5 Checked check valves , added air to valves for p1&5 Topped up kmno tank 1 Started plant duty @1232 power blip occurred Ack reset most alarms to get plant going When arrived back on site Kmno p2 oos had to unplug and plug back in. Reservoir low level came but started to recover | Schomberg Water Treatment Plant & Wells 2-4 | 2026-02-10
WEST | February | Trends checked good, reagent and equipment in good levels and conditions All readings measured in mg/l HL - time: 10:08 am free grab 0.03 Total grab 3.51 vs analyzer 3.54 Mono 3.06 Reservoir - time: 10:35 Free grab 0.05 Total grab 3.59 vs analyzer 3.64 Mono 3.37 Post filter - time : 10:42 Free grab 0.03 Total grab 2.19 vs. Analyzer 2.23 | Schomberg Water Treatment Plant & Wells 2-4 | 2026-02-20
WEST | February | Respond to KMNO P1 leakage alarm. KMNO tank 2 level at 16, pump keeps switch back to duty 2 due to tank level. Replace P1 tube element, prime and test. Place back in duty 1. Fill KNNO tank 2 from 15cm to 82cm and mix. Reset run hours on KMNO P1 to track tube element changes and hours to failure. | Schomberg Water Treatment Plant & Wells 2-4 | 2026-02-15
WEST | February | Onsite to complete work orders Monthly generator run Start Fuel 83.8/83.7 cm 1614/1611 L Hrs 541.5 Ran high lifts in duty to put on load Stop Fuel 83.7/83.7 cm 1611/1589 L Hrs 543.0 Did chlorination system inspection no issues observed Changed from using chlorinator 4 in duty to chlorinator 2 Checked cl2 leaks and scrubber no issues observed Accepted cl2 cylinder delivery Received 12 12 empty taken away Noticed Kmno tank 2 filling whole tank/pump 1 in duty. Rotated duties because it was higher than the changeover level. Will continue to monitor. | Schomberg Water Treatment Plant & Wells 2-4 | 2026-02-05
WEST | February | Chris Iliohan Tyler Smith. In to complete PM on air compressor and close openings on raw water tank lid work is completed | Schomberg Water Treatment Plant & Wells 2-4 | 2026-02-11
WEST | February | -on site to complete work orders -completed Scrubber System Valves, Exercise -completed UVT lens cleaning and unit flush -completed Transfer Pump and Motor Inspection -completed Transfer Pump Air Relief Valves Inspection -replaced uv#3 lamp #1 due to being close to 5000 hour runtime, reset hours | Schomberg Water Treatment Plant & Wells 2-4 | 2026-02-03
WEST | February | Onsite to clear treated ntu fault | Schomberg Water Treatment Plant & Wells 2-4 | 2026-02-08
WEST | February | Station checks Equipment checked and ok, trends checked and ok High lift analyzer Time: 11:00 Free: grab 0.06 Total: grab 3.46 vs analyzer 3.51 Mono 2.99 Reservoir Time: 11:15 Free: grab 0.07 Total: grab 3.74 vs analyzer 3.80 Mono 3.33 Post filter Time: 11:31 Free: grab 0.03 Total: grab 2.25 vs analyzer 2.30 | Schomberg Water Treatment Plant & Wells 2-4 | 2026-02-09
WEST | February | On site to complete station check Checked residuals mg/l Hl @0802 Total analyzer 3.41 grab 3.50 Free grab 0.05 Mcl grab 3.03 Through plant @1019 Total analyzer 2.23 grab 2.19 Free grab 0.04 Reservoir @1034 Total analyzer 3.67 grab 3.70 Free grab 0.09 Mcl grab 3.33 Continued troubleshooting Kmno system Changed check valve in suction side of pump leading to tank Noticed level contributed to climb when not in duty Replaced prv Topped up kmno tank 2 Changed cl2 cylinder with J Bloye Cl2 weight 63 to 130 kg | Schomberg Water Treatment Plant & Wells 2-4 | 2026-02-06
WEST | February | Onsite for station check and to collect weekly micro sample and iron & manganese samples W11568498 W11568659 W11152974 Plant was shutting off on arrival tried to manipulate and keep wells going but didn?t start filter duty quick enough and raw water tank hihi came in Checked residuals mg/l High lift @0938 Total analyzer 3.47 grab 3.56 Free grab 0.03 Mcl grab 3.16 Through plant @1000 Total analyzer 2.38 grab 2.36 Free grab 0.03 Reservoir @1004 Total analyzer 3.71 grab 3.82 Free grab 0.06 Mcl grab 0.07 | Schomberg Water Treatment Plant & Wells 2-4 | 2026-02-04
WEST | February | Onsite to complete work orders Deactivated plant Completed Kmno injection point cleaning Completed inspection of Kmno pumps Ran to sight glass to check max flow / min P1 100% 405 50% 390 15% 370 P2 100% 385 50% 390 15% 370 Reduced p2 max flow to 395 ml/min from 405 Cleaned cl17sc analyzers Grabs before Reservoir 3.69 grab 3.50 Hl analyzer 3.41 grab 3.40 After Reservoir analyzer 3.64 grab 3.60 Hl analyzer 3.01 grab 3.04 Reactivated plant Completed monthly up sensor check | Schomberg Water Treatment Plant & Wells 2-4 | 2026-02-03
WEST | February | -on site for station check -checked trends: all ok -entered readings in PWQ: -verified pre analyzer 11:00 -analyzer free: 0.07mg/l grab: 0.06mg/l -analyzer total: 1.52mg/l grab: 1.55mg/l -reagents all ok -verified post analyzer 11:10 -analyzer free: 0.04mg/l grab: 0.06mg/l -analyzer total: 1.57mg/l grab: 1.60mg/l -reagents all ok -verified chemscan: all ok -reagents all ok -topped up ammonia tank 2 - 15-75cm -completed housekeeping | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2026-02-27
WEST | February | Onsite for station check Duty active Checked residuals mg/l Pre @1207 TCL analyzer 1.52 grab 1.54 Fcl analyzer 0.07 grab 0.07 Mcl analyzer 1.46 grab 1.46 F nh3 analyzer 0.09 grab 0.05 T nh3 analyzer 0.37 grab 0.34 Post @1215 TCL analyzer 2.10 grab 2.11 Fcl analyzer 0.08 grab 0.06 Mcl analyzer 1.99 grab 1.95 F nh3 analyzer 0.04 grab 0.07 T nh3 analyzer 0.49 grab 0.46 Topped up ammonia tank 1 | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2026-02-23
WEST | February | -on site for station check and weekly bacti W11620180 -checked trends trends: all ok -entered reading in PWQ: all ok -took sample and grab from north cell 10:50 -free cl: 0.06mg/l -total cl: 2.05mg/l -west cell grab 10:55 -free cl: 0.07mg/l -total cl: 2.08mg/l -south cell 11:00 -free cl: 0.10mg/l -total cl: 2.10mg/l -equipment all ok -completed station check of rechlor building -checked trends: all ok -entered reading in PWQ: all ok -verified pre analyzer 12:20 -analyzer free: 0.07mg/l grab: 0.08mg/l -analyzer total: 1.52mg/l grab: 1.48mg/l -reagents all ok -verified post analyzer 12:40 -analyzer free: 0.08mg/l grab: -analyzer total: 2.06mg/l grab: 2.14mg/l - adjusted -reagents all ok -verified chemscan: all ok -reagents all ok | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2026-02-25
WEST | February | -on site for station check -checked trends: all ok -entered reading in PWQ: all ok -verified pre- analyzer 10:45 -analyzer free: 0.05mg/l grab: 0.08mg/l -analyzer total: 1.53mg/l grab: 1.55mg/l -reagents all ok -verified post analyzer 10:55 -analyzer free: 0.03mg/l grab: 0.01mg -analyzer total: 1.60mg/l grab: 1.58mg/l -reagents all ok -verified chemscan: all ok -reagents all ok -topped up ammonia tank 1 15-75cm | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2026-02-02
WEST | February | -on site to receive cylinder delivery - received 14/sent 15 -no issues -troubleshooting high free post ammonia -verified chemscan 12:40 - free ammonia - 0.17mg/l grab: 0.07mg/l - adjusted (0.14 - 0.04) -changed cylinder with Benson S - 46.8kg - 114.7kg | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2026-02-19
WEST | February | Informed ROC and operations. Onsite to perform annual calibration on Chemscan analyzer. Used the calibration mode. Verified the analyzer and no adjustments made. Put everything back in service. No issues. Informed ROC, armed the building and left the site. | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2026-02-13
WEST | February | completed PM work order. informed ROC beforehand W11562858 RHRSTR, JHSC Health and Safety Inspection, East Vaughan BPS | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2026-02-19
WEST | February | Onsite to wrap up annual calibrations Informed ROC and operations Used cal mode on scada during the calibrations Completed chlorine room instruments: WIT, gas detectors and chlorinators. Also completed RES FIT Cleared associated alarms No issues Informed ROC, armed building and left site | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2026-02-17
WEST | February | -on site to complete station check -checked trends: all ok -entered readings in PWQ: all ok -verified pre analyzer 13:05 -analyzer free: 0.08mg/l grab: 0.07mg/l -analyzer total: 1.79mg/l grab: 1.80mg/l -topped up KI -verified post analyzer 13:15 -analyzer free: 0.09mg/l grab: 0.11mg/l -analyzer total: 2.64mg/l grab: 2.44mg/l - adjusted -topped up KI -verified chemscan - adjust post mono 2.12- 2.21mg/l (-0.06 - 0.03 offset) reagents all ok -electrician on site to investigate source line not available - all equipment in station and surrounding area all ok -power restored 13:35 -ammonia chemical system all ok | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2026-02-20
WEST | February | -on site for re-chlor station check -checked trends: all ok -entered readings in PWQ: all ok -verified pre analyzer 13:20 -analyzer free: 0.13mg/l grab: 0.07mg/l - adjusted -analyzer total: 1.53mg/l grab: 1.52mg/l -reagents all ok -verified post analyzer 13:40 -analyzer free: 0.08mg/l grab: 0.08mg/l -analyzer total: 2.38/l grab: 2.34mg/l -reagents all ok -chemscan verified: adjust pre ammonia .26- .35 (0- 0.09 offset) -reagents all ok -equipment all ok -topped up ammonia tank 2 - 15- 75cm | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2026-02-17
WEST | February | Onsite for annual calibrations at chemical disinfection facility Informed ROC. ROC placed Bayview pumps manual off Completed PRE and Post free and total maintenance and calibration Took grabs: Pre injection Free 0.08mg/L Total 1.59mg/L Post injection Free 0.08mg/L Total 2.16mg/L Cleared associated alarms Informed ROC. ROC placed Bayview pumps back to auto No issues Armed building and left site | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2026-02-12
WEST | February | -on site for weekly bacti W -checked trends: all ok -entered readings in PWQ: -took north cell grab 11:30 -free cl: 0.06mg/l -total cl: 2.08mg/l -west cell grab 11:35 -free cl: 0.12mg/l -total cl: 2.06mg/l -south cell grab 11:40 -free cl: 0.11mg/l -total cl: 2.05mg/l -equipment all ok -on site for re-chlorine station check -checked trends: all ok -verified pre-analyzer 12:30 -free reading: 0.06mg/l grab: 0.07mg/l -total reading: 1.66mg/l grab: 1.64mg/l -reagents all ok -verified post - analyzer 12:50 -analyzer free:0.07mg/l grab: 0.06mg/l -analyzer total: 2.30mg/l grab: 2.48mg/l - adjusted -reagents all ok -verified chemscan: all ok -reagents all ok -re-verified pre-injection 13:30 due to high alarm -analyzer 2.03mg/l grab: 1.93mg/l - adjusted | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2026-02-11
WEST | February | -on site to complete station and weekly bacti W11605685 -checked trends: all ok -entered reading in PWQ: all ok -took chlorine grab and sample north cell 10:10 -free cl: 0.03mg/l -total cl: 2.04mg/l -west cell 10:15 -free cl: 0.08mg/l -total cl: 1.92mg/l -south cell 10:20 -free cl: 0.07mg/l -total cl: 2.01mg/l -notice burning smell coming from dehumidifier/heating unit - extremely hot - turned unit off and informed team lead - turned all both block heaters | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2026-02-17
WEST | February | -on site to complete station check -checked trends: all ok -entered readings in PWQ: -verified pre analyzer 09:00 -analyzer free:0.10mg/l grab: 0.07mg/l -analyzer total: 1.56mg/l grab: 1.64mg/l - adjusted -reagents all ok -verified post analyzer 09:10 -analyzer free: 0.05mg/l grab: 0.04mg/l -analyzer total: 1.55mg/l grab: 1.65mg/l - adjusted -reagents all ok -chemscan verified: adjusted post mom 1.44 - 1.36mg/l (.02/-.06) -adjust post free ammonia 0.03 - 0.14 (0.03/0.14) -adjusted post total ammonia 0.41- 0.51 0.03/0.14 -topped up yellow reagents -topped up ammonia tank 1 -15- 75cm -replaced ammonia tubing elements on pomp 1&2 -tested and primed - all ok | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2026-02-13
WEST | February | -Responded hihi post-combined chlorine - due to the unstable power supply in Richmond Hill tonight, Bayview PS's pumps were on and off which caused sudden flow changes in the system - the chemical system didn't response to the flow change quick enough and caused hi post-combined chlorine at 19:01 to 19:05 (highest residual total=3.28mg/L free=0.15mg/L), 20:42 to 20:51 (highest residual total=3.73mg/L free=0.11mg/L), 22:38 to 22:42 (highest residual total=3.63mg/L free=0.14mg/L) - performed grab test total=2.38mg/L free=0.08mg/L analyzer total=2.43mg/L free=0.09mg/L - no user was affected - not reportable | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2026-02-17
WEST | February | On site to replace network switch with network analyst Aaron Magsakay. All pumps were in manual. Comm failure alarm was triggered due to this. Removed Old switch from RHRSTR NAC panel Wired 24 VDC power to the new switch and plugged in the ports. Powered up new IE3300 layer 3 switch and checked the comms. Removed unused cat6 cables. Checked with ROC to make sure comms are back and trends are good. Did the same process for VNPSCD PAC panel switch | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2026-02-04
WEST | February | -on site for station check and weekly bacti W -checked trends: all ok -entered reading in PWQ: all ok -took chlorine grab and sample north cell 10:25 -free cl: 0.07mg/l -total cl: 2.05mg/l -west cell 10:30 -free cl: 0.09mg/l -total cl: 2.09mg/l -south cell 10:35 -free cl:0.08mg/l -total cl: 2.11mg/l -completed station check of re chlor building -verified pre analyzer 11:30 -analyzer free: 0.05mg/l grab: 0.08mg/l -analyzer total: 1.50mg/l grab: 1.50mg/l -reagents all ok -verified post analyzer 11:45 -analyzer free: 0.05mg/l grab: 0.03mg/l -analyzer total: 2.15mgl grab: 2.14mg/l -reagents all ok -verified chemscan -reagents all ok | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2026-02-04
WEST | February | -on site to complete rechlor station check -rechlor not active -completed cylinder change -filled ammonia tank #2 231 L to 1162 L -checked equipment -reviewed trends -recorded readings in PWQ sheet -depolox reagents ok -chemscan reagents ok -verified analyzers: 09:50 - pre-injection Analyzer readings: Free Chlorine = 0.05 mg/L Total Chlorine = 1.43 mg/L TNH3 = 0.31 mg/L FNH3 = 0.07 mg/L MCL = 1.41 mg/L 09:50 - pre-injection Grabs: Free Chlorine = 0.04 mg/L Total Chlorine = 1.52/1.52/1.52 mg/L TNH3 = 0.34 mg/L FNH3 = 0.08 mg/L MCL = 1.35 mg/L 09:59 - adjusted pre injection total chlorine analyzer to 1.52 mg/L based on average of 3 grabs 10:00 - post-injection Analyzer readings: Free Chlorine = 0.03 mg/L Total Chlorine = 1.50 mg/L TNH3 = 0.43 mg/L FNH3 = 0.07 mg/L MCL = 1.47 mg/L 10:00 - post-injection Grabs: Free Chlorine = 0.03 mg/L Total Chlorine = 1.54 mg/L TNH3 = 0.34/0.36/0.35 mg/L FNH3 = 0.07 mg/L MCL = 1.39/1.38/1.37 mg/L 10:34 - adjusted post injection total ammonia reading to 0.35 mg/L based on average of 3 grabs, offset 0.09 to 0.05 10:36 - adjusted post injection monochloramine reading to 1.38 mg/L based on average of 3 grabs, offset 0.07 to 0.02 -no other issues found | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2026-02-06
WEST | February | -on site to complete station -checked trends; all ok -took reading in PWQ: all ok -verified pre analyzer and performed maintenance 09:50 -analyzer free: 0.05mg/l grab: 0.06mg/l -analyzer total: 1.58mg/l grab: 1.60mg/l -reagents/flow/pressure/motor and electrolyte all ok -verified and post analyzer and performed maintenance 10:15 -analyzer free: 0.05mg/l grab: 0.04mg/l -analyzer total: 2.16mg/l grab: 2.18mg/l -reagents/flow/pressure/motor and electrolyte all ok -verified chemscan -reagents all ok | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2026-02-09
WEST | February | -on site to complete following work order -chlorine leak test: all ok - halogen system all ok -scrubber inspection: all ok -completed cleaning and zero of chemscan -parameter 230 & 248 above 2500 and min/max values acceptable - verified unit after cleaning - pre readings 13:50 -analyzer pre- mono: 1.33mg/l grab: 1.39mg/l - adjusted (-0.03 / 0.03) -analyzer free nh: 0.07mg/l grab: 0.07mg/l -analyzer total nh: 0.33mg/l grab: 0.34mg/l -post reading 14:05 -analyzer mono: 1.94mg/l grab: 2.00mg/l - adjusted (0.01/0.06) -analyzer free nh: 0.03mg/l grab: 0.05mg/l -analyzer total nh: 0.44mg/l grab: 0.44mg/l -topped up green/grey and mutation reagents -completed chlorine inspection: all ok | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2026-02-05
LINEAR | February | AUMCBS onsite to change FIT from bidirectional to unidirectional operation as per W11611748 Made changes and left site Informed ROC of the work | Linear Water System | 2026-02-23
LINEAR | February | Worked with North Rock contractor to replace 2 air valves in chamber 691800532 on contract T9718-07 Grab chlorine test results after work was completed as follows Free- 0.05mg/l Total- 1.45mg/l All valves associated with the watermain isolation have been opened and the system is back to normal operation. | Linear Water System | 2026-02-26
WW-NORTH | February | Adjusted EGSSSC forcemain lolo pressure alarm from 45 to 40 kPa to keep consistent with ROC forcemain lolo pressure setpoint. | Newmarket Pinch Valves | 2026-02-02
WW-NORTH | February | Completed monthly PM work orders: -Flow control valve inspection -Sump pit inspection -Air valve inspection | Newmarket Pinch Valves | 2026-02-13
WW-NORTH | February | Informed ROC. Onsite to perform annual Calibration on flowmeter. Used the calibration mode. Performed calibration. Put the flowmeter back in service. All the related alarms were cleared. No issues. Informed ROC and left the site. | Newmarket Pinch Valves | 2026-02-17
WW-NORTH | February | Attended for pinch valve #1 fault Closed isolation valve and tried to open pinch valve locally on Rotork but it wouldn't move (motor stalled alarm on screen) Spoke to Brent (electrical on-call), was able to get the valve to open in local after a few tries Cleared alarm on SCADA and opened isolation valve - pinch valve #1 will stay in duty 2 for the night Notified RO?C of valve status. | Newmarket Pinch Valves | 2026-02-01
WW-WEST | February | Completed the station check and daily lab work Decanted then emptied the sludge thickening tank Added 2 bags of soda ash to each aeration tank Batch wasted 15m3 from clarifier 1 and 10m3 from clarifier 2 Cleaned up in the process building | Nobleton Water Resource Recovery Facility | 2026-02-24
WW-WEST | February | Completed the station check and daily lab work Decanted and then emptied the sludge thickening tank Added 2 bags of soda ash to each aeration tank Bled the aeration condensate line Removed rags from the aeration tanks and outlets | Nobleton Water Resource Recovery Facility | 2026-02-25
WW-WEST | February | Added two bags of soda ash each into aeration tank 1 and 2 | Nobleton Water Resource Recovery Facility | 2026-02-28
WW-WEST | February | Harie Rajamithiran(OIT) working under the direction of Daniel Hirstwood(OIC). -Supernated STT and transferred to SHT -Completed lab analysis & station check , no issues found -Started batch wasting process at 9:40 , wasting from 11:00- 13:00 for 15m^3 per train -Added 2 bags of soda ash into each aeration tank -Completed online DO probe verification with handheld , cleaned out rags from both tank 1&2 probes and cleaned sensor. A difference of approximately 1.00ppm was found between online DO probes versus handheld. -Received Alum delivery at 12:20 for 16125kg. -Alum level before filling process : 0.87 m -Alum level after filling process : 3.51 m | Nobleton Water Resource Recovery Facility | 2026-02-27
WW-WEST | February | Completed the station check and daily lab work Decanted then emptied the sludge thickening tank Added 2 bags of soda ash to each aeration tank Batch wasted 15m3 from each clarifier Received a soda ash delivery of 50 bags Inspected and greased RAS, WAS, and scum pumps | Nobleton Water Resource Recovery Facility | 2026-02-26
WW-WEST | February | Collected weekly compliance samples | Nobleton Water Resource Recovery Facility | 2026-02-25
WW-WEST | February | Completed the station check and daily lab work Decanted then emptied the sludge thickening tank Added 2 bags of soda ash to each aeration tank Batch wasted 15m3 from clarifier 1 and 10m3 from clarifier 2 Cleaned up in the RAS/WAS room | Nobleton Water Resource Recovery Facility | 2026-02-23
WW-WEST | February | On site to look at leaking plant service water, did not find a leak informed operators to monitor area, looked at return valve 4, valve is stiff will source new valve | Nobleton Water Resource Recovery Facility | 2026-02-26
WW-WEST | February | Harie Rajamithiran(OIT) working under the direction of Daniel Hirstwood(OIC). -Supernated STT and transfers to SHT -Completed lab analysis, no issues found -Completed station check, no issues found -Started batch wasting process at 11:00, wasting from 12:00-14:00 for 15m^3 per train -Added 2 bags of soda ash into each aeration tank -Prepared compliance sample bottles for weekly compliance -Took out some rags from aeration tanks | Nobleton Water Resource Recovery Facility | 2026-02-02
WW-WEST | February | Completed the station check and daily lab work Decanted then emptied the sludge thickening tank Batch wasted 15m3 from each aeration tank Added 2 bags of soda ash to each aeration tank | Nobleton Water Resource Recovery Facility | 2026-02-20
WW-WEST | February | Completed the station check and daily lab work Entered data into SharePoint Decanted then Emptied the sludge thickening tank Batch wasted 20m3 from clarifier 1 and 15m3 from clarifier 2 Added 2 bags of soda ash to each aeration tank Received an alum delivery of 16.5tonnes | Nobleton Water Resource Recovery Facility | 2026-02-10
WW-WEST | February | Completed the daily lab work and station check Decanted then emptied the sludge thickening tank Batch wasted 15m3 from both clarifiers Cleaned the do probes Removed floating solid?s from the aeration tanks | Nobleton Water Resource Recovery Facility | 2026-02-18
WW-WEST | February | - transferred sludge from the thickening tank to the sludge holding tank - Performed in-house labs and recorded readings on SharePoint. No issues - Enabled RAS batch wasting mode at 8:40. Wasted 20 m^3 from train 1 and 20 m^3 from train 2 - Notified ROC of the work being performed. Inspected clarifier 1 drive and oil for OJT. No issues - Inspected vortex 1 and 2. All okay. Greased fittings. Pumps are all good, oil level is good - Inspected travelling screen. Greased fittings. Checked oil level, all good - Inspected screening press. Heat trace is okay. Oil level is good - Inspected debris auger and grit dewatering screen, oil is all good. No issues - Inspected bypass sampling kit. Seal is still intact. No issues - Checked station and recorded readings on SharePoint. Created archibus for emergency light in RAS/WAS room due to low battery alarm - Exercised filter inlet valves. Greased fittings - Cleared UV fault alarm | Nobleton Water Resource Recovery Facility | 2026-02-19
WW-WEST | February | - Added 2 bags of soda ash each to aeration tank 1 and 2 - Removed floating solids from aeration tank 1 and 2 - Checked for condensation in the air lines for aeration tank 1 and 2. None found - Tidied up aeration tank area and blower room - Cleaned aeration tank channel - Recharged dodge ram 2118 battery | Nobleton Water Resource Recovery Facility | 2026-02-18
WW-WEST | February | Added UV Bypass alarm. Alarm will annunciate if no UV?s are active and there is plant flow for 15 min. The alarm was tested to confirm operation on the servers. No UV?s were off during test. Alarm is to be reset using reset control that appears beside the UV reactors on SCADA while the alarm is active. | Nobleton Water Resource Recovery Facility | 2026-02-13
WW-WEST | February | Harie Rajamithiran(OIT) working under the direction of Lance Johnson(OIC). -Supernated STT and transferred to SHT -Completed lab analysis and station check , no issues found -Started batch wasting process at 10:00 , wasting from 11:00-13:00 for 15m^3 per train -Added 2 bags of soda ash into each aeration tank -Completed sand filter/air lift 1-2 air compressor inspection and cleaning , no issues found | Nobleton Water Resource Recovery Facility | 2026-02-17
WW-WEST | February | Collected weekly samples | Nobleton Water Resource Recovery Facility | 2026-02-18
WW-WEST | February | Harie Rajamithiran(OIT) working under the direction of Young Jung(OIC). -Assisted Young Jung to completed work orders and recruitment video. | Nobleton Water Resource Recovery Facility | 2026-02-19
WW-WEST | February | Harie Rajamithiran(OIT) working under the direction of Daniel Hirstwood(OIC). -Supernated STT and transferred to SHT -Completed lab analysis and station check , no issues found -Started batch wasting process at 10:00, wasting from 11:00-13:00 for 15m^3 per train -Added 2 bags of soda ash into each aeration tank -Prepared weekly compliance sample bottles | Nobleton Water Resource Recovery Facility | 2026-02-13
WW-WEST | February | On site for RAS pump 2 coupling failure Found pump side of coupler deteriorated Locked out RAS pump 2 Removed two piece coupler One piece coupler in stock on site Installed new coupler and reassembled coupler. Operations put pump in service Complete | Nobleton Water Resource Recovery Facility | 2026-02-13
WW-WEST | February | Completed the station check and daily lab work Decanted and then emptied the sludge thickening tank Batch wasted 15m3 from each clarifier Added 2 bags of soda ash to each aeration tank Removed rags from the aeration outlet Bled the condensation from the aeration lines Pulled a sand filter as it was clogged and reseated it | Nobleton Water Resource Recovery Facility | 2026-02-12
WW-WEST | February | Onsite for weekend work orders. Added 2 bags of soda ash per tank. Remotely enabled batch wasting mode at 1:40pm and set auto waste for 30m3 from 3pm-5pm When wasting completed at 5pm placed WAS pumps back into manual and reset RAS | Nobleton Water Resource Recovery Facility | 2026-02-15
WW-WEST | February | Remote entry - at 6:53pm received call from ROC for alum pumps 3 and 4 uncommanded stop alarms And alum pump 5 general alarm. Alum pump 1 and 2 continue to pump to aeration tank 1 and 2. Logged in remotely and reset to clear alarms. Alarms cleared and alum pump 4 dosing alum to filter inlet as normal. Will continue to monitor. | Nobleton Water Resource Recovery Facility | 2026-02-16
WW-WEST | February | Added 2 bags of soda ash to each aeration tank | Nobleton Water Resource Recovery Facility | 2026-02-22
WW-WEST | February | - Added 2 bags of soda ash each to aeration tank 1 and 2 - Decanted the sludge thickening tank then transferred sludge from the thickening tank to the holding tank - Cleaned aeration tank outlet weir - Held outputs for DO probe. Cleaned probe. Once done, resumed outputs. DO readings good with manual probe - Notified ROC of the work being performed - Tested sanitary sump alarm. hihi alarm received - Filter inlet channel is good - Cleaned filter reject pit - Checked heat trace, display not working. No issues with heat | Nobleton Water Resource Recovery Facility | 2026-02-11
WW-WEST | February | Completed the station check and daily lab work Decanted and then emptied the sludge thickening tank Added 2 bags of soda ash to each aeration tank Batch wasted 20m3 from clarifier 1 and 15m3 from clarifier 2 | Nobleton Water Resource Recovery Facility | 2026-02-05
WW-WEST | February | Collected weekly effluent samples | Nobleton Water Resource Recovery Facility | 2026-02-11
WW-WEST | February | On site to reset process building UPS. Power cycle UPS. PAC down for short duration. Alarms cleared. | Nobleton Water Resource Recovery Facility | 2026-02-06
WW-WEST | February | On site to assist contractor Total Power with Diesel Generator 5 year PM. Completed | Nobleton Water Resource Recovery Facility | 2026-02-09
WW-WEST | February | Harie Rajamithiran(OIT) working under the direction of Gavin Walker(OIC). -Completed lab analysis, no issues found -Completed station check, no issues found -Added 2 bags of soda ash into each aeration tank -Started batch wasting process at 9:40, wasting from 11:00-13:00 for 15m^3 per train -Competed monthly Joint Health & Safety inspection, no issues found -Inspected all aeration blowers, sludge blowers and grit blowers, no issues found | Nobleton Water Resource Recovery Facility | 2026-02-03
WW-WEST | February | Collect weekly and monthly samples of raw, sludge, final effluent and domestic wells for YDSS lab submissions. | Nobleton Water Resource Recovery Facility | 2026-02-04
WW-WEST | February | Completed the station check and daily lab work Decanted and emptied the sludge thickening tank Added 2 bags of soda ash Batch wasted 15m3 from each clarifier Removed floating rags from the aeration tank Inspected the process building sump pit | Nobleton Water Resource Recovery Facility | 2026-02-09
WW-WEST | February | Completed the station check and daily lab work Emptied the sludge thickening tank Added 2 bags of soda ash to each aeration tank Batch wasted 15m3 from each clarifier Removed floating solids from the aeration tank and aeration tank outlet Cleaned the do probes in the aeration tanks | Nobleton Water Resource Recovery Facility | 2026-02-04
WW-WEST | February | Completed the station check and daily lab work Decanted and then emptied the sludge thickening tank Batch wasted 15m3 from each clarifier Added 2 bags of soda ash to each aeration tank Removed rags from the aeration tanks and plant inlet | Nobleton Water Resource Recovery Facility | 2026-02-06
WW-CEAST | February | -on site for Housekeeping, cleaning up garbage around site on various floors -running pump 1 in auto duty 1, if it trips on bearing high temp, or another alarm, WO will be created, ongoing issues with pump 1 -completed alarm investigation -W11692845- Leslie Pump 1 High Bearing Temp Alarm created -station okay, only 5 pumps in auto/duty rotation, pump 1 OOS | Markham Leslie Pumping Station | 2026-02-26
WW-CEAST | February | Station Check completed (See details on SharePoint). Checked drywell. cleaned dry well area Checked screen room, changed out rag bin. Cleaned/hose down screen room. Switched pumps duty to timed mode from all-stop. Pumps 3, 4, 5, and 6 available in timed-auto duty rotation every 4 hours. pump 1 faulted on 'stack overtemp' alarm. cleared the alarm. pump 2 seal water line has a pinhole leak. created work request W11683392 for maintenance to fix. Pump 1 & 2 taken oos. All standby power generators available in auto. Drained condensates from the surge tanks air compressors. | Markham Leslie Pumping Station | 2026-02-23
WW-CEAST | February | -ran pump 1 with maintenance, upper bearing on pump is overheating -pump is manual off but available if needed to run -wet well consolidated work order completed -pump 2 was put OOS for the seal water, but back online before end of day -all 6 pumps can run, but pump 1 is manual off for the night, but available if needed -station okay | Markham Leslie Pumping Station | 2026-02-24
WW-CEAST | February | -station check of site -reviewed SCADA -inspected site -entered data into SharePoint -rotated bins in screen room -pump 1 OOS, fault alarm, Fault 47 Stack Overtemp, notifying maintenance, WO already created, will add to it -5 pumps available in auto -station okay | Markham Leslie Pumping Station | 2026-02-27
WW-CEAST | February | -station check of site -reviewed SCADA -inspected site -entered data into sharepoint -rotated bins in screen room, and put bins out for pickup -station okay | Markham Leslie Pumping Station | 2026-02-25
WW-CEAST | February | Checked all seal water solenoid valves okay None leaking past All seats are good. Replaced copper seal water line on pump 2. Operator will reopen suction valve. | Markham Leslie Pumping Station | 2026-02-24
WW-CEAST | February | On site for media sampling with Contractor, All Round System (John Round), under RFT 2609-25. | Markham Leslie Pumping Station | 2026-02-26
WW-CEAST | February | On site to install pump 4 discharge valve. Bonnet installed will return to install rotork. | Markham Leslie Pumping Station | 2026-02-02
WW-CEAST | February | Station check complete and the readings have been entered into the sharepoint. Changed out the rag bin. Investigated bar screen 1 fault alarm. Found large amounts of rags stuck between bottom sprocket/chain which has caused the overtorque. Removed the rags from the sprocket/chain and put the unit back in service. | Markham Leslie Pumping Station | 2026-02-02
WW-CEAST | February | -station check of site -reviewed SCADA -entered data into sharepoint -inspected site -rotated bins in screen room, bins out for pickup -inspected outfall -station okay | Markham Leslie Pumping Station | 2026-02-18
WW-CEAST | February | -station check of site -reviewed SCADA -entered data into sharepoint -inspected site -rotated bins in screen room -pump 1 locked out late wednesday afternoon on a high bearing temp alarm, it was left off and OOS. Reset alarm on pump today and returned pump 1 back to auto duty rotation. All 6 pumps available. If pump 1 overheats again, we will leave it OOS for the weekend and get mechanical to investigate. Cleaned the screen on the seal water system, and opened the valve all the way to get as much seal water to pump 1 as possible. Will see if this helps. -station okay | Markham Leslie Pumping Station | 2026-02-20
WW-CEAST | February | On site to install split seal on rebuilt pump #1 | Markham Leslie Pumping Station | 2026-02-10
WW-CEAST | February | -cleaned screen room and rotated bins -cleaned up pump floor area, Housekeeping -pump 1 back to auto as per maintenance's request, all 6 pumps in auto/available -station okay | Markham Leslie Pumping Station | 2026-02-17
WW-CEAST | February | Checked station/equipments. Changed out the rag bin. Cleared comm fail alarm. All trend, equipment visible on scada Hosed down screen room floor. Pushed in empty bins back into the screen room | Markham Leslie Pumping Station | 2026-02-15
WW-CEAST | February | -on site to put pump 1 back online after repairs were completed by Christian Streef and Martin DeVries -electrical removed lockout on pump -maintenance removed their locks -LOTO on suction valve was removed, and suction valve was opened slowly, air was bled from pump -discharge valves were slowly opened and air bled from riser pipe -pump 1 was started in manual to test, seemed to run normally with no issues -mechanical was measuring the temp readings -pump 1 manual off after 45 min run test, mechanical doing further checks -pump 1 will remain manual off for the night to cool down -5 pumps in auto -station okay | Markham Leslie Pumping Station | 2026-02-12
WW-CEAST | February | -On site to complete work orders. -Completed consolidated monthly dry well pump floor inspection work order. -Sump pit inspection completed. Tested Sump Level HiHi Alarm and confirmed with ROC. -Dry well flood alarm does not exist at this site, tested sump level HiHi in its place. -High low temp alarm does not exist at this site, temperatures tracked on BAS site. -BAS check completed. -Auto dialer test completed and confirmed with ROC. -Air compressor inspection completed, checked belts, oil, filters. -Seal water strainer checks completed. -Pump 1 OOS. -Pump 6 in auto duty rotation, but discharge valve is leaking, issue already reported to maintenance team. -Bar Screen 2 fault came in at 0928 this morning, reset fault and test ran screen for multiple cycles with no issues. Left bar screen 2 running in auto. Topped up oil on both bar screens. -RS Pump and Motor Inspection completed: -Pump 1 OOS -Pump 2: 1710L/s at 100% speed. -Pump 3: 1300L/s. -Pump 4: 1290L/s. -Pump 5: 1570L/s at 100% speed. -Pump 6: 1190L/s. -Check valve inspections completed. -Air relief valve inspections completed. | Markham Leslie Pumping Station | 2026-02-10
WW-CEAST | February | -station check of site -reviewed SCADA -entered data into sharepoint -inspected site -completed consolidated surge tank inspection -ran pump 1 for an hour, pump manual off -station okay | Markham Leslie Pumping Station | 2026-02-13
WW-CEAST | February | -station check of site -entered data into sharepoint -inspected site -reviewed SCADA -notified ROC of work being performed -WAJAX on site for generator maintenance -YR maintenance and electrical on site for pump 1 repairs -generators started at 11:58 Generator 1: Start Hours:230.24 Stop Hours:231.42 Generator 2: Start Hours:117.40 Stop Hours:119.35 Generator 3: Start Hours:103.59 Stop Hours:105.54 Bulk Fuel Tank Start: 23,437L Fuel Stop: 22,572L -generator 1 went into shutdown due to low oil level, topped up oil, reset alarms, put generator 1 back to auto, generator started up and ran for remainder of 1 hour test run, sync/load shared with other generators Generator Run Time: 1.95 hrs -generators off at 13:52 -test successful, back on utility power, reset alarms -pump 1 remains OOS -all other pumps in auto and reset -Generator 1-3 Monthly Test Run -Hazard Waste Removal-no hazardous waste -Leslie Scrubber Inspection -bin replacement/screen room inspection -station okay | Markham Leslie Pumping Station | 2026-02-11
WW-CEAST | February | On site to finish assembly of rebuilt pump #1. Will return to flood pump with operator and rack pump back in to test. | Markham Leslie Pumping Station | 2026-02-11
WW-CEAST | February | Station check complete and the readings have been entered into the sharepoint. Changed out the rag bin, pushed full bin out for pick up. Filled up barscreen oil reservoirs. Shelved all pump 1 and associated discharge valve alarms for now until it gets repaired. Work in progress by CMS to repair pump 4 discharge valve. | Markham Leslie Pumping Station | 2026-02-04
WW-CEAST | February | On site completed work orders. Pump 4 ran twice after repair by CMS, discharge valve and running operation ok, no issues. Put back in service and includes in the auto duty rotation. Currently in duty 1, with a flow of around 1290 L/s at 420 kPa PIT1/520 kPa PIT2. Station Check (See details on SharePoint). All pumps available in timed auto duty rotation every 4 hours, except pump 1, which is out of service. All standby power generator available in auto. Drained condensates from surge tanks air compressors. Checked dry well, ok. Blew down bubblers. Checked bar screens. Switched rag bin. Put rag bins back inside the screen room after picked up by Miller Waste yesterday. Cleaned screen room of rags on the floor. Switched sump pump duty and ran sump pump to remove old/stagnant water/sewage inside the sump pit. Hoist inspection completed. | Markham Leslie Pumping Station | 2026-02-06
WW-CEAST | February | Weather today Clear and -16 Celsius -On site to complete work orders W11579343. -Completed station check. -Entered station readings into SharePoint. -Pumps 2, 3, 4, 5, and 6 available in timed-auto duty rotation every 4 hours. -Pumps 1 out of service. -All standby power generators available in auto. -Switched sump pump duty. -Drained condensates from the surge tanks air compressors. -Checked dry well, ok. -Checked bar screens. Switched rag bin. Cleaned/hosed down bar screen room. | Markham Leslie Pumping Station | 2026-02-09
WW-CEAST | February | On site to make sure pump 4 discharge valve is moving properly. Valve opens and closes smoothly. Set open and closed limits. Pump is ready to flood and run. | Markham Leslie Pumping Station | 2026-02-05
EAST | February | On site to complete station check. Time: 09:20 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.46 1.37 Time: 09:23 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.38 1.46 Total: 1.62 Verified analyzers with grabs. Adjusted the influent free from 1.37mg/l-1.46mg/l due to multiple grabs taken at 09:26. Adjusted the effluent free from 1.46mg/l-1.38mg/l due to multiple grabs taken at 09:27. Checked site and trends. Will leave silicate pump 2 off the priming valve is broken and needs to be replaced. | Mount Albert Wells 1 & 2 | 2026-02-26
WW-CEAST | February | -On site to respond to Wet Well Screen 1 and 2 Differential LOE and HiHi Alarms. -Upon arrival to site, checked trends and bar screen inlet channel. Trends showed there were several level fluctuations and spikes within the last two hours. Inspection of the bar screen channels showed traces of white foam in channels and on bars, which likely caused the above alarms. Foam has almost entirely dissipated and issue appears to now be resolved. | Markham Leslie Pumping Station | 2026-02-03
EAST | February | On site to complete station check. Collecting weekly Bac-t Samples. W11619936 Weekly Bac-t Samples. Also on site to top up silicate tank. Start: 19.3cm/91L Stop: 102.6cm/484L Time: 10:35 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.93 1.99 Time: 10:36 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.44 1.47 Total: 1.71 Started well 1 in local to run to waste to collect sample at 10:30. Verified analyzers with grabs. Checked site and trends. Put silicate pump 2 into manual side to starting issues. Shut down well 1 at 11:04. Entered data into PWQ sheet. | Mount Albert Wells 1 & 2 | 2026-02-25
EAST | February | On site with Travis Wyatt for on the job training and to assist in monthly maintenance: 11:45hrs: Cleaned HACH CL17 Analyzer, Verified Analyzers after cleaning @12:00hrs: Influent FCL grab residual: 1.63mg/l, Analyzer: 1.59mg/l Effluent FCL grab residual: 1.65mg/l. Analyzer: 1.67mg/l Silicate and Hypo system inspection including injection point cleaning and inspection. Inspected chemical boards. Deep well exhaust valve inspection. Low temp alarm test. | Mount Albert Wells 1 & 2 | 2026-02-24
EAST | February | On site for station check, and operational sampling (W1164413). Activated system duty. Tower level 71%. Entered data into PWQ sheets. Verified analyzers: Inffluent taken at 9:38 Free Grab: 1.78 mg/L Analyzer: 1.82 mg/L Effluent taken at 9:40 Free grab: 1.51 mg/L Analyzer: 1.52 mg/L Total grab: 1.79 mg/L Took operational sample at 9:49 Chemical systems: Hypo pump 2 running 28% speed, DP= 440 kpa Silicate pump 2 running at 37% speed, DP= 500 kpa. Reviewed SCADA trends, Outstanding alarms: gen fuel high level alarm. Station OK. | Mount Albert Wells 1 & 2 | 2026-02-23
EAST | February | On site to complete station check. Collecting PH reading Time: 13:00 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.89 1.91 Time: 3:05 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.50 1.45 Total: 1.68 Verified analyzers with grabs. At 12:30 activated duty for Mount Albert. Checked station and trends. Well 1 OOS due to WQ issues. No outstanding alarms. PH reading 8.02. | Mount Albert Wells 1 & 2 | 2026-02-02
EAST | February | On site to complete station check. Time: 13:45 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.39 1.32 Time: 13:50 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.37 1.36 Total: 1.56 Verified analyzers with grabs Well 1 OOS due to WQ issues. Gen hi tank alarm disregard. Entered data into PWQ sheet. Cleaned NTU analyzer. | Mount Albert Wells 1 & 2 | 2026-02-20
EAST | February | On site to complete station check. Collecting weekly Bac-t Samples. W11605433 Weekly Bac-t Samples. Time: 13:15 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.92 1.93 Time: 13:20 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.40 1.48 Total: 1.64 Started well 1 at 13:14 to run well to waste for sampling. Changed out effluent free CL-17 reagents. Entered data into PWQ sheet. Checked site and trends. Gen tank hi alarm disregard. Well 1 OOS due to WQ issues. only running to waste to collect raw water sample. At 13:52 shut down well 1. | Mount Albert Wells 1 & 2 | 2026-02-17
EAST | February | On site to complete station check. Collecting weekly Bac-t Samples. W11588600 Weekly Bac-t Samples. Time: 13:18 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.95 1.93 Time: 13:20 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.50 1.53 Total: 1.68 At 13:24 started up well 1 to run to waste to collect sample. Verified analyzers all ok. Well 1 OOS due to WQ issues. Gen tank hi alarm disregard. Entered data into PWQ sheet. | Mount Albert Wells 1 & 2 | 2026-02-11
EAST | February | Silicate Top Up Before: 33.4cm/158L After: 105.2cm/496L | Mount Albert Wells 1 & 2 | 2026-02-10
EAST | February | On site to complete station check. Time: 07:45 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.43 1.35 Time: 07:47 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.39 1.42 Total: 1.65 Verified analyzers with grabs. Checked station and trends. Gen hi tank alarm disregard. Well 1 OOS due to WQ issues. Entered data into PWQ Changed out reagents for the influent free CL-17 analyzer. | Mount Albert Wells 1 & 2 | 2026-02-13
EAST | February | On site for hypo delivery and completing work orders. Hypo tank fill. Start: 310/310L Stop: 608/602L Started generator at 11:15 also attached will be the generator readings. Started well at 11:17 to put generator under load. Shut well off at 12:17 while generator is being shut off. Completed JHSC inspection as well. No issues with work orders. | Mount Albert Wells 1 & 2 | 2026-02-03
EAST | February | On site to complete station check. Time: 12:30 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.46 1.40 Time: 12:35 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.50 1.47 Total: 1.68 Verified analyzers with grabs. Checked site and trends. Generator hi tank level alarm disregard. Well 1 OOS due to WQ issues. Entered data into PWQ sheets. | Mount Albert Wells 1 & 2 | 2026-02-06
EAST | February | On site to complete station check. Time: 10:05 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.49 1.41 Time: 10:07 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.42 1.47 Total: 1.62 Verified analyzers with grabs. Checked station and trends. Well 1 OOS due to WQ issues. Generator hi fuel alarm disregard. Entered data into PWQ sheet. | Mount Albert Wells 1 & 2 | 2026-02-09
EAST | February | On site to complete station check. Collecting weekly Bac-t Samples. W11568200 Weekly Bac-t Samples. W11569414 Monthly Manganese Samples. Time: 13:50 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.98 2.01 Time: 13:53 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.52 1.48 Total: 1.59 Activated duty at 13:03 to sample wells 1 and 2. Checked site and trends. Verified analyzers with grabs. Well 1 OOS for WQ issues. Diesel tank level hi alarm disregard. Stopped well 1. All flow from this well went to waste and not to system. | Mount Albert Wells 1 & 2 | 2026-02-04
EAST | February | On site to correct source of chlorine gas leak with Jack P. Cylinders already isolated, turned booster pump 2 local on to purge chlorine lines. Replaced parker fitting on outlet of the regulator on left bank cylinder. Opened chlorine cylinders and vacuum tested system for leaks. Backwashed station for a few mins, with de-chlor pucks in the catch basin. Placed chlorine system back in service and placed well back in service. Monitoring well start up. Rotated chlorinators to test both. | Mount Albert Well 3 | 2026-02-23
EAST | February | On site to complete station check. Collecting weekly Bac-t Samples. W11619936 Weekly Bac-t Samples. W11670426 Manganese Sample. Time: 11:15 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.73 1.73 Time: 11:20 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.67 1.64 Total: 1.84 Verified analyzers with grabs. Checked site and trends. No outstanding alarms. No OOS equipment. Topped up silicate tank. Start: 66.3cm/2108L Stop: 79.2cm/2518L This is silicate from Aurora wells 1-4. | Mount Albert Well 3 | 2026-02-25
EAST | February | On site to complete station check. Time: 10:10 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.75 1.77 Time: 10:12 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.83 1.81 Total: 2.09 Verified analyzers with grabs. Checked site and trends. Cleared any outstanding alarms on site. No OOS equipment on site. Cleaned NTU cell which locked out well at 10:30. Cleared interlock and restarted well at 10:37. NTU is currently 0.230 and dropping. Will monitor off site. | Mount Albert Well 3 | 2026-02-26
EAST | February | On site for Camlok wiring for generator load tests | Mount Albert Well 3 | 2026-02-27
EAST | February | On site for station check, and operational sampling (W1164413). Duty active, Tower level 77%. Entered data into PWQ sheets. Verified analyzers: Inffluent taken at 11:53 Free Grab: 1.82 mg/L Analyzer: 1.82 mg/L Effluent taken at 11:56 Free grab: 1.76 mg/L Analyzer: 1.71 mg/L Total grab: 2.01 mg/L Took operational sample at 12:00 Chemical systems: Chlorinator 2 open at 33%, BP2 running DP=1000 kpa Silicate pump 2 running at 42% speed, DP= 500 kpa. Reviewed SCADA trends, Station OK. | Mount Albert Well 3 | 2026-02-23
EAST | February | On site to complete station check. Time: Influent Grab (mg/l) Analyzer (mg/l) Free: Time: Effluent Grab (mg/l) Analyzer (mg/l) Free: Total: | Mount Albert Well 3 | 2026-02-26
EAST | February | On site to complete station check. Completing raw water PH reading Time: 13:50 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.84 1.82 Time: 13:55 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.76 1.72 Total: 1.94 Verified analyzers with grabs. Checked station and trends. No OOS equipment. No outstanding alarms on site. PH reading 8.01. Replaced CL-17 reagents for the influent and effluent analyzers. | Mount Albert Well 3 | 2026-02-02
EAST | February | On site to complete the following work orders: - Turbidity analyzer maintenance - addressed turbidity fault from earlier this morning as well - Closed chlorine leak detector test and scrubber check work orders - they were deemed to be working after chlorine leak alarm on 02/17 - Chemical system inspection Silicate: Cleaned injection points, flushed lines with hot water and verified pumps with drawdown. No issues with silicate system - Chemical system inspection chlorine: Chlorinators were tested yesterday during chlorine leak resolution. Performed visual inspection of system - Chlorine emergency kit inspection Well back to auto, station ok | Mount Albert Well 3 | 2026-02-19
EAST | February | On site to complete station check. Time: 08:25 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.61 1.54 Time: 08:30 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.57 1.53 Total: 1.87 Entered data into PWQ sheet. Verified analyzers with grabs. Checked station and trends. No outstanding alarms on site. No OOS equipment. | Mount Albert Well 3 | 2026-02-13
EAST | February | On site to fix silicate pump 1. Replaced diaphragm and purged air from the system. Tested pump and cleared alarms at 09:06. Put pump 1 into duty 1 at 09:08, system is back to normal. | Mount Albert Well 3 | 2026-02-10
EAST | February | On site to check the silicate system especially pump 1 which has a new diaphragm. No issues noticed. | Mount Albert Well 3 | 2026-02-12
EAST | February | On site with Jackie Saunders to address chlorine leak from last night Placed chlorine scrubber back to auto Purged chlorine system using booster pump #1 - Removed leaky Parker fitting, found that the grab spacer ring was cracked. Replaced fitting and threaded on. Opened chlorine cylinders and tested for leaks, none observed @08:40 - Activated system duty - MTETNL level is 65% Station ok | Mount Albert Well 3 | 2026-02-18
EAST | February | On site responding to chlorine leak alarm. Tested system and have not been able to find cause of leak. Also on site to complete station check. Time: 11:30 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.66 1.57 Time: 11:32 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.38 1.36 Total: 1.72 Verified analyzers with grabs all ok. Checked site and trends. Entered data into PWQ sheet. No outstanding alarms on site. No OOS equipment on site. tightened up vent lines on regulators to prevent leak will monitor off site and inform OCO. | Mount Albert Well 3 | 2026-02-20
EAST | February | Changed chlorine cylinder on right bank. | Mount Albert Well 3 | 2026-02-12
EAST | February | On site to respond to chlorine leak alarm. Well duty is not active upon arrival. Chlorine gas sensor is reading 0.0ppm. Reset the chlorine scrubber.? Noticed a small leak from left side cl2 regulator's Parker connection. Closed both cylinders, purged the lines. Placed well 3 to local off. Will come back during the day to replace the flex tubings and connections. Informed ROC. Well 3 is OOS for the night.? | Mount Albert Well 3 | 2026-02-22
EAST | February | On site to complete station check. Collecting weekly Bac-t Samples. W11588600 Weekly Bac-t Samples. Time: 14:10 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.77 1.73 Time: 14:12 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.70 1.64 Total: 1.93 Verified analyzers with grabs. No outstanding alarms on site. No OOS equipment on site. Checked site and trends. Entered data into PWQ sheet. | Mount Albert Well 3 | 2026-02-11
EAST | February | On site responding to chlorine gas leak / scrubber running alarms W11670914 When arrived on site @20:05 reset scrubber and it stopped. Gas detector reading 0.0 ppm . Checked for leaks using ammonia, none observed. However observed a Parker fitting on the discharge side of the regulator #1 that appears cross threaded. Will inform Team lead tomorrow, to get two operators to site to fix. Isolated cylinder #1 for the time being. Leaving chlorine scrubber running in local on overnight, just in case there was an issue with that Parker fitting. Informed ROC that would be leaving scrubber running overnight and to disregard that alarm until 07:30 tomorrow Chlorine cylinder #1 OOS Station okay | Mount Albert Well 3 | 2026-02-17
EAST | February | On site to complete station check. Collecting weekly Bac-t Samples. W11605433 Weekly Bac-t Samples. Time: 14:20 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.81 1.75 Time: 14:25 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.72 1.66 Total: 2.05 Verified analyzers with grabs. Checked site and trends. No OOS equipment No outstanding alarms. Entered data into PWQ sheet. | Mount Albert Well 3 | 2026-02-17
EAST | February | On site to complete station check. Collecting weekly Bac-t Samples. Collecting Monthly Manganese Samples. W11568200 Weekly Bac-t Samples. W11569414 Monthly Manganese Samples. Time: 14:25 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.76 1.72 Time: 14:28 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.64 1.63 Total: 2.02 Verified analyzers with grabs all ok. No OOS equipment. No outstanding alarms. | Mount Albert Well 3 | 2026-02-04
EAST | February | On site to complete station check. Time: 11:45 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.57 1.52 Time: 11:47 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.60 1.54 Total: 1.76 Verified analyzer with grabs all ok. Checked site and trends. Ruptured diaphragm on pump 1 silicate causing a fault alarm. Entered data into PWQ sheets. | Mount Albert Well 3 | 2026-02-09
EAST | February | On site to complete station check. Time: 13:35 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.49 1.51 Time: 13:38 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.48 1.51 Total: 1.88 Verified analyzers with grabs. Checked site and trends. No outstanding alarms on site. No OOS equipment. Entered data into PWQ sheet. | Mount Albert Well 3 | 2026-02-06
EAST | February | On site to complete following work orders: W11570951 Supply Fans Check W11570957 Exhaust Fans Check W11570963 Deep Well Exhaust Valve check W11570984 Facility Outfall Inspection W11571049 Standby Generator Test W11571063 Chlorine Analyzer Maintenance W11571278 JHSC Inspection Put well 3 in manual at 09:08 and informed ROC of work to be completed at 09:09. Taking grabs to verify analyzers after maintenance. Time: 10:35 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.52 1.50 Time:10:37 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.51 1.51 Verified analyzers no issues pocket colorimetre passed calibration. Started generator at 12:46 and started well in manual at 12:47. All details of generator run will be attached to this log entry. Completed silicate work and pumped hot water through system and pump. Any changes in trends or alarms created are due to work orders being completed. Stopped well at 13:43 in preparation for generator shut down. Generator shut down at 13:53. Put well into auto at 13:54 duty is active. | Mount Albert Well 3 | 2026-02-05
EAST | February | Changed the duty 1 start set point from 45% to 60% at 07:08 after a successful draw down, | Mount Albert North Elevated Tank | 2026-02-23
EAST | February | On site to complete station check. Collecting weekly Bac-t Sample. W11619936 Weekly Bac-t Sample. Time: 13:15 Grab (mg/l) Analyzer (mg/l) Free: 1.52 1.52 Total: 1.72 Verified analyzers with grabs all ok. Checked site and trends. No OOS equipment. No outstanding alarms on site. | Mount Albert North Elevated Tank | 2026-02-25
EAST | February | @03:42 - ROC called for outlet free chlorine high alarm Reviewed trends, chlorine analyzer had spiked to 5 mg/L twice in the past hour. Analyzer was reading 5 mg/L from 03:34 to 03:44, and has been steadily dropping since. Coincides with when the ROC started filling the tower @04:02 - Deactivated duty to see if the alarm comes back with the tower draining. Analyzer reading spiked slightly, but then stabilized at ~1.65 mg/L around 04:40. Requested ROC to call back if the outlet FCL goes high again, and will attend site at that point. | Mount Albert North Elevated Tank | 2026-02-17
EAST | February | At 07:42 turned off duty and changed the duty start set point from 60% to 45%. This is to deep cycle the tower for WQ. | Mount Albert North Elevated Tank | 2026-02-20
EAST | February | On site to complete station check. Collecting weekly Bac-t Sample. W11605433 Weekly Bac-t Sample. Time: 12:10 Grab (mg/l) Analyzer (mg/l) Free: 1.47 1.51 Total: 1.69 While on site took a look at the pinch plate tubing on the CL-17 analyzer. While doing this analyzer went to 0mg/l at 12:18 grabs were taken at 12:20 and are reading 1.47mg/l, same as grabs taken at 12:10. Also will be priming the CL-17 analyzer due to erratic reading that occurred over the weekend. Took another grab at 12:30 while CL-17 analyzer is priming, Time: 12:30 Grab (mg/l) Free: 1.49 Analyzer reading after prime is 1.51mg/l grab after prime is 1.48mg/l at 12:43. Activated duty at 12:44 to collect samples. | Mount Albert North Elevated Tank | 2026-02-17
EAST | February | On site for monthly maintenance: Informed ROC - JHSC health and safety inspection - Manual valves exercises - Low temperature alarm test - Sump pit inspection - Inlet / Outlet Heat trace inspections - observed a low temperature alarm as active on the inlet and outlet units - ack / reset alarms. Heaters on the heat trace are running, and current temps are okay. Informed TL to request to send an operator back to check them tomorrow - Chlorine analyzer maintenance: Started @14:14, Completed @14:33. Verified analyzer reading with grab residual @14:45 - Grab: 1.45 mg/L / Analyzer: 1.44 mg/L - Portable gasoline generator test run Station ok | Mount Albert North Elevated Tank | 2026-02-19
EAST | February | On site to complete station check. Collecting weekly Bac-t Sample. Collecting monthly manganese sample. W11568200 Weekly Bac-t Sample. W11569414 Monthly Manganese Sample. Time: 08:50 Grab (mg/l) Analyzer (mg/l) Free: 1.42 1.38 Total: 1.59 Cleared historian heart beat alarm on site at 08:56. Verified analyzer on site. Checked site and trends. Verified analyzer with grabs all ok. Entered data into PWQ sheet. No OOS equipment on site. | Mount Albert North Elevated Tank | 2026-02-04
EAST | February | On site to complete station check. Collecting weekly Bac-t Sample. W11588600 Weekly Bac-t Sample. Time: 12:40 Grab (mg/l) Analyzer (mg/l) Free: 1.41 1.39 Total: 1.54 Verified analyzers with grabs No outstanding alarms on site. No OOS equipment Activated duty at 12:48. Checked site and trends. | Mount Albert North Elevated Tank | 2026-02-11
EAST | February | On site for station check. Collected CL2 grab residual on Discharge Header: 11:20hrs: Free Cl2 grab residual: 1.36mg/l, Total Cl2 grab residual: 1.57mg/l Checked station readings. All information in PWQ sheet. Checked site and equipment. Equipment out of service: None. | Stouffville Zone 1 Booster Pumping Station | 2026-02-23
EAST | February | On site for station check. Collected CL2 grab residual on Discharge Header: 12:20hrs: Free Cl2 grab residual: 1.34mg/l, Total Cl2 grab residual: 1.50mg/l Checked station readings. All information in PWQ sheet. Checked site and equipment. Equipment out of service: None. | Stouffville Zone 1 Booster Pumping Station | 2026-02-26
EAST | February | On site for station check. Collected CL grab residual on Discharge Header: 12:45hrs: Free Cl2 grab residual: 1.54mg/l, Total Cl2 grab residual: 1.71mg/l Checked station readings. All information in PWQ sheet. Checked site and equipment. Equipment out of service: None. | Stouffville Zone 1 Booster Pumping Station | 2026-02-02
EAST | February | Placed VC_FCV1 in auto. | Stouffville Zone 1 Booster Pumping Station | 2026-02-10
EAST | February | On site for station check. Collected CL grab residual on Discharge Header: 10:32hrs: Free Cl2 grab residual: 1.44mg/l, Total Cl2 grab residual: 1.65mg/l Checked station readings. All information in PWQ sheet. Checked site and equipment. Equipment out of service: None. | Stouffville Zone 1 Booster Pumping Station | 2026-02-13
EAST | February | Conducted Generator Test Run (12:42hrs): Diesel Generator Run Monthly Test: Start Runtime: 12:42hrs (Run hrs: 514.6hrs) Fuel Start: 751L Stop Runtime: 13:58hrs (Run hrs: 515.8hrs ) Fuel Stop: 735L Generator Performance Data recorded below: Battery Cell Levels: OK Battery Terminals/Cables: Ok Oil and Coolant: Ok Amps: 64amps Volts: 594 Hertz: 61 RPM: 1800 Oil Pressure: 57psi Water temp: 176F Oil temp: 220F Pyrometer: 520F No issues during generator run test. Ran Pump 2 during run test. Valve exercise and check valve greasing Housekeeping | Stouffville Zone 1 Booster Pumping Station | 2026-02-10
EAST | February | On site for station check. Collected CL grab residual on Discharge Header: 11:10hrs: Free Cl2 grab residual: 1.81mg/l, Total Cl2 grab residual: 1.95mg/l Checked station readings. All information in PWQ sheet. Checked site and equipment. Equipment out of service: None. | Stouffville Zone 1 Booster Pumping Station | 2026-02-17
EAST | February | On site for station check. Collected CL grab residual on Discharge Header: 12:10hrs: Free Cl2 grab residual: 1.34mg/l, Total Cl2 grab residual: 1.55mg/l Checked station readings. All information in PWQ sheet. Checked site and equipment. Equipment out of service: None. | Stouffville Zone 1 Booster Pumping Station | 2026-02-20
EAST | February | On site for station check. Collected CL grab residual on Discharge Header: 11:20hrs: Free Cl2 grab residual: 1.54mg/l, Total Cl2 grab residual: 1.76mg/l Checked station readings. All information in PWQ sheet. Checked site and equipment. Equipment out of service: None. | Stouffville Zone 1 Booster Pumping Station | 2026-02-09
EAST | February | Tested FCV's auto function by placing it in auto. Activated duty and deactivated duty to for the test. It is functioning well. Left it man/off for the night and will place it in auto tomorrow. | Stouffville Zone 1 Booster Pumping Station | 2026-02-09
EAST | February | On site for station check. Collected CL grab residual on Discharge Header: 11:35hrs: Free Cl2 grab residual: 1.48mg/l, Total Cl2 grab residual: 1.66mg/l Checked station readings. All information in PWQ sheet. Checked site and equipment. Equipment out of service: None. | Stouffville Zone 1 Booster Pumping Station | 2026-02-06
EAST | February | On site with Travis Wyatt for Cylinder change on Bank 1. | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2026-02-24
EAST | February | Under Direction of OIC Dan Zhou On Site for; - Station checks Data in PWQ workbook @ 11:05 hrs. Adjusted pump speed for pump 1 to 65 % and pump 2 to 60 %, then returned speed setpoint to auto Influent Water Grab @ 11:11 hrs. TCL: 1.56 mg/L Analyzer: TCl: 1.51 mg/L Effluent Water Grab @ 11:14 hrs. FCl: 1.93 mg/L TCl: 5.00 mg/L , 1/4 dilution Analyzer: Free Chlorine FCl: 1.98 mg/L Analyzer Total Chlorine TCl: 4.95 mg/L Simulated Free Grab @ 11:24 hrs. Sim FCl: 1.76 mg/L, Analyzer: FCl: 1.70 mg/L Duty not active Equipment OOS: Pump 4 Facility OK | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2026-02-26
EAST | February | On site with Sean Peoples to investigate BP #2 outlet valve. Found actuator gearbox seal to be compromised. Oil has entered the electrical enclosure. Rotork actuator will need to be replaced. ROC notified. Replacement actuator from inventory installed. Remote control not functioning, requires further investigation. Only operable in Local Control. ROC notified. | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2026-02-23
EAST | February | Under Direction of OIC Dan Zhou On Site for; - Station checks - Receive chlorine cylinders (24), worked with OIC Joe Mazza Data in PWQ workbook Influent Water Grab @ 13:10 hrs. TCL: 1.54 mg/L Analyzer: TCl:: 1.51 mg/L Effluent Water Grab @ 13:14 hrs. FCl: 1.65 mg/L TCl: 2.40 mg/L Analyzer: Free Chlorine FCl: 1.56 mg/L Analyzer Total Chlorine TCl: 2.41 mg/L Simulated Free Grab @ 10:20 hrs. Sim FCl: 1.67 mg/L, Analyzer: FCl: 1.65 mg/L Duty not active Equipment OOS: Pump 4, pump 2 (power loss) Facility OK | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2026-02-23
EAST | February | Under Direction of OIC Dan Zhou On Site for; - Station checks - Test pump 2 and discharge valve Data in PWQ workbook @ 09:01 hrs. stopped pump 3 placed pump 2 in duty 1 with pump 1 Valve actuated and fully opened, pump 2 back in service. Influent Water Grab @ 13:10 hrs. TCL: 1.54 mg/L Analyzer: TCl: 1.51 mg/L Effluent Water Grab @ 09:37 hrs. FCl: 1.92 mg/L TCl: >4.40 mg/L Analyzer: Free Chlorine FCl: 1.96 mg/L Analyzer Total Chlorine TCl: 4.83 mg/L Simulated Free Grab @ 09:38 hrs. Sim FCl: 1.62 mg/L, Analyzer: FCl: 1.62 mg/L Duty not active Equipment OOS: Pump 4 Facility OK | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2026-02-25
EAST | February | On site with Sean Peoples to continue work on Pump #2 outlet valve actuator. ROC notified. Programming and installation completed. With assistance of ROC, actuator tested. Found that actuator timed out and ?Fail to open? alarm initiated. Tyler Zimmerman-Jones contacted and then coordinated with PCS to change the valve timer and test actuator. Valve now operates appropriately in remote. | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2026-02-24
EAST | February | Under Direction of OIC Dan Zhou On Site for; - Station checks - Chlorine cylinder change (worked with OIC Joe Mazza) Data in PWQ workbook Influent Water Grab @ 09:54 hrs. TCL: 1.54 mg/L Analyzer: TCl: 1.51 mg/L Effluent Water Grab @ 09:57 hrs. FCl: 1.95 mg/L TCl: > 4.40 mg/L Analyzer: Free Chlorine FCl: 1.99 mg/L Analyzer Total Chlorine TCl: 4.81 mg/L Simulated Free Grab @ 10:03 hrs. Sim FCl: 1.70 mg/L, Analyzer: FCl: 1.67 mg/L @10:24 hrs. Informed ROC of chlorine cylinder change, with Joe Mazza @ 10:39 placed pump 2 in manual on at 50 % to test chlorine system after cylinder change changed duty 1 from pumps 1/3 to pumps 2/3 Equipment OOS: Pump 4 Facility OK | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2026-02-02
EAST | February | On site with Travis Wyatt to change out Cl2 Cylinder Bank 1. | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2026-02-02
EAST | February | Under Direction of OIC Dan Zhou ON Site for PM's; - AIT Maintenance Informed ROC @ 13:01, and placed pumps 1 and 3 in manual off, pumps 2 and 4 currently in manual off Clean Start @ 13:03 Clean Stop @ 13:50 Low flow to Influent total analyzer, disregard alarm -> station off no flow to users Analyzer Verification: Influent Water Grab @ 14:05 hrs. TCL: 1.62 mg/L Analyzer: TCl: 1.65 mg/L Effluent Water Grab @ 14:01 hrs. FCl: 1.71 mg/ TCl: 2.72 mg/L Analyzer: Free Chlorine FCl: 1.67 mg/L Analyzer Total Chlorine TCl: 2.75 mg/L Simulated Free Grab @ 14:03 hrs. Sim FCl: 1.64 mg/L, Analyzer: FCl: 1.65 mg/L @ 14:10 placed pumps 1 and 3 in manual on, pumps 2 and 4 remain in manual off | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2026-02-12
EAST | February | Under direction of OIC Dan Zhou On site for PM?s - Actuated valve exercise and inspection - Chlorine leak detector and safety equipment test - Chlorine scrubber check - Chemical system inspection (chlorine) - Pump 4 inspection - Comprehensive cleaning - Chlorine cylinder change (worked with OIC Joe Mazza) - Install vent line to chlorine regulators vent (worked with OIC Joe Mazza) @ 12:35 informed ROC of chlorine leak detector test and pump 4 inspection @ 12:46 placed pumps 1 and 3 in manual off for jockey pump test, and chlorine leak detector test Chlorine leak detector test triggered @ 12:40: - All halogen valves actuated and closed cylinders, scrubber activated - Exhaust fan vfd fault light on at MCC panel, tried flipping breaker (no change), created work order (W11673974) Pump 4 inspection: @ 13:32 pump 4 (jockey pump) in manual on for inspection, using GC 1 to CBP 1 BP1 at 235 kpa Rotameter reading 33 PPD Pump pressure gauge 610 kpa Scada pump discharge pressure 629 kpa @ 13:41 put pump 4 in manual off MV 1,3,4 actuated, Pump 2 and MV2 OOS due to power loss. @ 13:59 placed pumps 1 and 3 in auto, active in Duty 1 | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2026-02-18
EAST | February | Under Direction of OIC Dan Zhou On Site for; - Station checks Data in PWQ workbook Influent Water Grab @ 08:48 hrs. TCL: 1.60 mg/L Analyzer: TCl:: 1.54 mg/L Effluent Water Grab @ 08:54 hrs. FCl: 1.92 mg/ TCl: > 2.20 mg/L Analyzer: Free Chlorine FCl: 1.96 mg/L Analyzer Total Chlorine TCl: 4.89 mg/L Simulated Free Grab @ 08:58 hrs. Sim FCl: 1.80 mg/L, Analyzer: FCl: 1.77 mg/L @ 8:59 hrs. Sim free sample tap disrupted flow to analyzer, disregard alarm Equipment OOS: Pump 4, pump 2 (power loss) Facility OK | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2026-02-11
EAST | February | Under Direction of OIC Joe Mazza On Site for; - Station checks Data in PWQ workbook Influent Water Grab @ 08:13 hrs. TCL: 1.61 mg/L Analyzer: TCl:: 1.60 mg/L Effluent Water Grab @ 08:20 hrs. FCl: 1.92 mg/L Using 1/4 dilution took 3 grabs TCl: 4.08 mg/L, 4.08 mg/L, 4.12 mg/L Average = 4.09 mg/L Adjusted analyzer to 4.09 mg/L @ 08:49 informed ROC of sensor warning on Effluent CL-17 @ 08:52 manually stopped pumps 1 and 3 to reset analyzer, no flow to users @ 08:54 reset effluent analyzer by turning OFF and ON -> sensor warning lifted Disregard total chlorine lolo, due to turning off and on analyzer Analyzer: Free Chlorine FCl: 1.95 mg/L Analyzer Total Chlorine TCl: 5.00 mg/L Simulated Free Grab @ 08:58 hrs. Sim FCl: 1.74 mg/L, Analyzer: FCl: 1.71 mg/L @ 09:14 returned pumps 1 and 3 back to auto (duty active) Equipment OOS: Pump 4, pump 2 (power loss) Facility OK | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2026-02-13
EAST | February | Under Direction of OIC Dan Zhou On Site for; - Station checks Data in PWQ workbook Influent Water Grab @ 08:44 hrs. TCL: 1.59 mg/L Analyzer: TCl:: 1.51 mg/L Effluent Water Grab @ 08:47 hrs. FCl: 1.70 mg/L TCl: 3 grab ave. 2.50 mg/L, 2.44 mg/L, 2.48 mg/L Ave = 2.47 mg/L Effluent Analyzer adjusted to 2.47 mg/L Analyzer: Free Chlorine FCl: 1.62 mg/L Analyzer Total Chlorine TCl: 1.99 mg/L Simulated Free Grab @ 09:00 hrs. Sim FCl: 1.71 mg/L, Analyzer: FCl: 1.65 mg/L @ 09:01 sim free lolo alarm, disregard, low flow to analyzer Equipment OOS: Pump 4, pump 2 (power loss) Facility OK | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2026-02-17
EAST | February | On site to reset P1 and P3 VFD faults. P1 had no communication msg and P3 had over current msg on ABB pad. Reset the VFDs and they are back to standby. Ack+reset alarms. P1 and P3 started in auto. Station is back to normal operation. P2 remains OOS due to MV2 issue. | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2026-02-18
EAST | February | On site for Cl2 Cylinder change and installation of vent tubing. | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2026-02-18
EAST | February | Under Direction of OIC Dan Zhou On Site for; - Station checks Data in PWQ workbook Influent Water Grab @ 10:03 hrs. TCL: 1.51 mg/L Analyzer: TCl:: 1.47 mg/L Effluent Water Grab @ 10:04 hrs. FCl: 1.94 mg/L TCl: 1/4 dilution, 1.25 mg/L x 4 = 5.00 mg/L Analyzer: Free Chlorine FCl: 2.00 mg/L Analyzer Total Chlorine TCl: 4.97 mg/L Simulated Free Grab @ 10:10 hrs. Sim FCl: 1.72 mg/L, Analyzer: FCl: 1.72 mg/L Pumps 1 and 3 active in duty 1 Equipment OOS: Pump 4 (jockey pump), pump 2 (power loss) Facility OK | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2026-02-20
EAST | February | Under direction of OIC Dan Zhou On site for; - Station checks - SL1000 Cleaning and Verification Influent Water Grab @ 12:06 hrs. TCl: 1.52 mg/L Analyzer: TCl: 1.52 mg/L Effluent Water Grab @ 12:08 hrs. FCl: 2.00 mg/L TCl: > 2.20 mg/L Analyzer FCl: 2.00 mg/L TCl: 4.71 mg/L Simulated Free Cl Grab @ 12:20 hrs. FCl: 1.80 mg/L Analyzer: FCl: 1.73 mg/L | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2026-02-06
EAST | February | Under direction of OIC Dan Zhou On site for; - generator test - JHSC health and safety inspection @ 09:07 informed ROC of generator test and JHSC inspections @ 09:09 hrs. Placed pump 1 in manual off, shut pump 2 off in manual @ 09:15 shut pump 3 off in manual Generator Test: Start hours: 461.9 Start time: 09:21 hrs. Stop Hours: 463.3 (includes cool down time) Stop Time: 10:50 hrs. Run Time: 1.2 hours Start Fuel: 2986/2284 L Stop Fuel: 2987/2214 L Pre run checks; Battery Cell Levels: Ok Battery Terminals and Cables: Ok Oil Level: Ok Coolant Level: Ok Fluid Leaks: Ok Coolant Recirculating pump: Ok Faulty Gauges: Ok @ 09:32 hrs. Put pump 2 in Manual On @ 09:38 put pump 3 in Manual On Operating Current: 185 amps Operating Frequency: 61 Hz Operating Voltage: 600 Volts, Engine speed: 1803 RPM Water/coolant Temp: 172 F Oil Pressure: 61 psi Oil Temp: 182 F @ 10:20 hrs. Placed pump 2 in manual off @ 10:25 hrs. placed pump 3 in manual off @ 10:55 hrs. Returned all pumps to auto, pumps 2,3 active in duty 1 | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2026-02-03
EAST | February | Under direction of OIC Dan Zhou On site for PM?s; - Chlorine emergency repair kit inspection - Critical air valves flush and inspection | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2026-02-03
EAST | February | Duty rotated booster pumps: Placed P1 to D1, P2 to D2 | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2026-02-09
EAST | February | Under Direction of OIC Dan Zhou On Site for; - Station checks - Investigate outlet MV for BP2 Data in PWQ workbook Influent Water Grab @ 10:33 hrs. TCL: 1.48 mg/L Analyzer: TCl:: 1.44 mg/L Effluent Water Grab @ 10:37 hrs. FCl: 1.87 mg/ TCl: 2.74 mg/L Analyzer: Free Chlorine FCl: 1.80 mg/L Analyzer Total Chlorine TCl: 2.65 mg/L Simulated Free Grab @ 10:41 hrs. Sim FCl: 1.95 mg/L, Analyzer: FCl: 1.86 mg/L Outlet MV at BP2 power loss. Flipped breaker, no change, flipped secondary power switch at valve, no change. MV at outlet for BP1 functions and is on the same breaker. Created WO for maintenance (W11649860). Valve left in local, BP2 in manual off. Duty inactive (pumps 1 and 3 in duty 1) Equipment OOS: Pump 4 Facility OK | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2026-02-09
EAST | February | Under Direction of OIC Dan Zhou On Site for; - Station checks Data in PWQ workbook Influent Water Grab @ 09:10 hrs. TCL: 1.53 mg/L Analyzer: TCl:: 1.51 mg/L Effluent Water Grab @ 09:13 hrs. FCl: 1.93 mg/L TCl: > 4.40 mg/L Analyzer: Free Chlorine FCl: 1.98 mg/L Analyzer Total Chlorine TCl: 4.75 mg/L Simulated Free Grab @ 09:17 hrs. Sim FCl: 1.72 mg/L, Analyzer: FCl: 1.77 mg/L Equipment OOS: Pump 4 Facility OK | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2026-02-04
EAST | February | On site for station check and to collect weekly micro samples (W11620016) and HAA samples (W11676368). Collected Cl2 grab residuals on Header tap @10:40hrs and Sample: FCL: 1.75mg/l Analyzer FCL: 1.75mg/l TCL: 1.97mg/l Checked station readings, verified Cl2 analyzer. All information in PWQ sheet. Equipment out of service: None. | Stouffville Zone 2 Elevated Tank | 2026-02-25
EAST | February | On site for station check and to collect weekly micro samples (W11588680) and HAA samples (W11642920). Collected in house iron samples. Collected Cl2 grab residuals on Header tap @12:00hrs and Sample: FCL: 1.72mg/l Analyzer FCL: 1.72mg/l TCL: 1.89mg/l Checked station readings, verified Cl2 analyzer. All information in PWQ sheet. Equipment out of service: None. | Stouffville Zone 2 Elevated Tank | 2026-02-11
EAST | February | On site for station check and to collect weekly micro samples (W11605521) and HAA samples (W11664457). Collected Cl2 grab residuals on Header tap @10:35hrs and Sample: FCL: 1.72mg/l Analyzer FCL: 1.70mg/l TCL: 1.91mg/l Checked station readings, verified Cl2 analyzer. All information in PWQ sheet. Equipment out of service: None. | Stouffville Zone 2 Elevated Tank | 2026-02-17
EAST | February | On site for station check and to collect weekly micro samples (W11568302) and ANSCAN sample (W11568629). Collected Cl2 grab residuals on Header tap @10:40hrs and Sample: FCL: 1.91mg/l Analyzer FCL: 1.91mg/l TCL: 2.12mg/l Checked station readings, verified Cl2 analyzer. All information in PWQ sheet. Equipment out of service: None. | Stouffville Zone 2 Elevated Tank | 2026-02-04
EAST | February | On site for monthly maintenance: 11:10hrs: Cleaned HACH CL17 Analyzer, Verified Analyzer after cleaning: FCL grab residual: 1.71mg/l, Analyzer FCL: 1.73mg/l. Sump Pit inspection, Manual valve exercise, Heat Trace System Inspection. Tested Low Temperature alarm, no issues. JHSC Inspection of STW3 and Z1 PS and this facility. | Stouffville Zone 2 Elevated Tank | 2026-02-05
EAST | February | On site for station check and to collect weekly micro samples (W11620016) and HAA sample (W11676368). Collected in house iron samples and ATP. Collected Cl2 grab residuals on Header tap @11:15hrs and Sample: FCL: 1.34mg/l Analyzer FCL: 1.31mg/l TCL: 1.50mg/l Checked station readings, verified Cl2 analyzer. All information in PWQ sheet. Equipment out of service: None. | Stouffville Zone 1 Elevated Tank | 2026-02-25
EAST | February | On site for station check and to collect weekly micro samples (W11588680) and HAA sample (W11642920). Collected in house iron samples. Collected Cl2 grab residuals on Header tap @12:35hrs and Sample: FCL: 1.41mg/l Analyzer FCL: 1.45mg/l TCL: 1.63mg/l Changed HACH Cl17 Reagents. Checked station readings, verified Cl2 analyzer. All information in PWQ sheet. Equipment out of service: None. | Stouffville Zone 1 Elevated Tank | 2026-02-11
EAST | February | Attending site to check chlorine analyzer fault (W11670776). Analyzer had a motor error. Replaced motor and optical sensor. Verified reading at 1.39 mg/L Free. ROC was notified before and after maintenance activities. | Stouffville Zone 1 Elevated Tank | 2026-02-18
EAST | February | On site for station check and to collect weekly micro samples (W11605521) and HAA sample (W11664457). Collected Cl2 grab residuals on Header tap @11:50hrs and Sample: FCL: 1.34mg/l Analyzer FCL: 1.38mg/l TCL: 1.59mg/l Checked station readings, verified Cl2 analyzer. All information in PWQ sheet. Equipment out of service: None. | Stouffville Zone 1 Elevated Tank | 2026-02-17
EAST | February | Deep cycle tower to 40% by changing the duty start setpoint from 60% to 40%. | Stouffville Zone 1 Elevated Tank | 2026-02-19
EAST | February | On site responding to low low CL2 reading (0.00mg/l). Collected Free CL2 grab residual @ 12:35hrs: 1.35mg/l. Issue with the CL2 Analyzer itself, may be related to changing the reagents during station check. Initiated priming sequence to prime new reagents. Cl2 Analyzer didn't seem as though it was priming correctly, powered off Analyzer and powered back on. Received a "Motor Error" alarm on the Display. Spoke with instrumentation Eric S who will attend site. WO issued. | Stouffville Zone 1 Elevated Tank | 2026-02-17
EAST | February | On site for station check and to collect weekly micro samples (W11568302) and ANSCAN sample (W11568629). Collected Cl2 grab residuals on Header tap @11:45hrs and Sample: FCL: 1.74mg/l Analyzer FCL: 1.73mg/l TCL: 1.95mg/l Checked station readings, verified Cl2 analyzer. All information in PWQ sheet. Equipment out of service: None. | Stouffville Zone 1 Elevated Tank | 2026-02-04
EAST | February | On site for monthly maintenance: 12:55hrs: Cleaned HACH CL17 Analyzer, Verified Analyzer after cleaning: FCL grab residual: 1.72mg/l, Analyzer FCL: 1.65mg/l. Adjusted Cl2 Analyzer to reflect grab residual based on multiple CL2 grab residuals. Portable Generator run test, Heat Trace System Inspection. JHSC Inspection. Housekeeping. | Stouffville Zone 1 Elevated Tank | 2026-02-05
EAST | February | Under direction of OIC Dan Zhou On site for; - Station checks - Regulatory sampling ( Micro, W11620058) - Operational sampling, nitrification Data in PWQ workbook Regulatory samples taken @ 10:21 from north cell South Cell Grab @ 10:07 hrs. TCl: 1.58 FCl: 0.02 Analyzer: TCl: 1.56 mg/L North Cell Grab @ 10:21 hrs. TCl: 1.51 mg/L FCl: 0.04 Analyzer: TCl: 1.56 mg/L Cells Filling Equipment OOS: none Facility OK | Markham PD6 Reservoir | 2026-02-25
EAST | February | Under direction of OIC Dan Zhou On site for; - Station checks - Regulatory sampling ( Micro, W11605563) - Operational sampling, nitrification and corrosion control, with ATP and flouride analysis Data in PWQ workbook Regulatory samples taken @ 10:00 from north cell South Cell Grab @ 09:54 hrs. TCl: 1.58 FCl: 0.04 Analyzer: TCl: 1.57 mg/L North Cell Grab @ 10:00 hrs. TCl: 1.48 mg/L FCl: 0.06 Analyzer: TCl: 1.57 mg/L Cells Draining Equipment OOS: none Facility OK | Markham PD6 Reservoir | 2026-02-17
EAST | February | On site to change buffer and indicator reagents for total chlorine analyzer. | Markham PD6 Reservoir | 2026-02-20
EAST | February | On site for; - Station checks - Regulatory sampling ( Micro, W11568358) Data in PWQ workbook Regulatory samples taken @ 10:00 from north cell. South Cell Grab @ 09:57 hrs. TCl: 1.51 FCl: 0.07 Analyzer: TCl: 1.55 mg/L North Cell Grab @ 10:00 hrs. TCl: 1.45 mg/L FCl: 0.08 Cells Draining Equipment OOS: none Facility OK | Markham PD6 Reservoir | 2026-02-04
EAST | February | Under direction of OIC Dan Zhou On site for; - Station checks - Regulatory sampling ( Micro, W11588722) - Operational sampling, nitrification Data in PWQ workbook Regulatory samples taken @ 10:00 from north cell South Cell Grab @ 09:57 hrs. TCl: 1.51 FCl: 0.07 Analyzer: TCl: 1.58 mg/L North Cell Grab @ 10:00 hrs. TCl: 1.45 mg/L FCl: 1.53 Analyzer: TCl: 1.58 mg/L Cells Draining Equipment OOS: none Facility OK | Markham PD6 Reservoir | 2026-02-11
EAST | February | Under direction of OIC Dan Zhou On site for PM's - Chlorine analyzer maintenance - Sump pump test - Dehumidifier cleaning and inspection - High/low water level alarms test - Flood alarm test - JHSC Health and Safety Inspection - External venting screens inspection - Air valve inspection - Comprehensive house cleaning Chlorine analyzer maintenance; Start Clean @ 12:25 hrs. Exited Clean @ 12:49 hrs. Post analyzer maintenance verification; Grab @ 13:00 hrs. TCl: 1.58 mg/L Analyzer: TCl: 1.54 mg/L Initiated Flood alarm @ 12:33 hrs. (OK) Flood Alarm test: Hi initiated @ 13:26 hrs. alarm in @ 13:26 hrs. (OK) Lo initiated @ 13:27 hrs. alarm in @ 13:29 hrs. (OK) | Markham PD6 Reservoir | 2026-02-05
CENTRAL | February | Call from ROC about Co2 leak detector hihi alarm active. Logged in remotely to review trends on SCADA. Observed detector reading over 5000 between the hrs of 5 to 6pm. Noticed leak detector reading started to trend downward when duty deactivated. Spoke with Area TL over the phone, we agreed to leave plant off for the night for further investigation in the morning if the alarm is not triggered again. Notified ROC. | Keswick Water Treatment Plant | 2026-02-25
CENTRAL | February | -Performed station check - logged station readings into PWQ sheet -Changed pre-free reagents -Performed filter performance review - 100% | Keswick Water Treatment Plant | 2026-02-27
CENTRAL | February | Filter performance both 100% | Keswick Water Treatment Plant | 2026-02-27
CENTRAL | February | Checked filter performance both 100% | Keswick Water Treatment Plant | 2026-02-26
CENTRAL | February | -Tested chlorine leak alarm | Keswick Water Treatment Plant | 2026-02-24
CENTRAL | February | As per workorder Filter performance review @ 4:55 pm via scada F1 and F2 100% all ok | Keswick Water Treatment Plant | 2026-02-23
CENTRAL | February | -Changed chlorine cylinder -Responded lolo fluoride - noticed fluoride pump air locked - bleaded air -Performed station check - logged station readings into PWQ sheet -Collected weekly BacT sample YD #W11620086 -Performed filter performance review - 100% | Keswick Water Treatment Plant | 2026-02-25
CENTRAL | February | -Helped raw water sample line repair 1. LOTO low lift pump at breaker & discharge valve, travelling bar screen, raw water sample pump 2. Put LLP-FCV1, PACL pumps, SETL-TK11MV1, SETL-TK2-MV1 in manual off 3. Once the repair is done - removed the temporary sample line, put the permanent line online, restarted sample pump - no leak 4. Reversed all the changes -Performed station check - logged station readings into PWQ sheet -Checked CL17 reagents - OK | Keswick Water Treatment Plant | 2026-02-23
CENTRAL | February | As per workorder Filter performance review via scada @ 3:25 pm F1 and F2 both 100% - all ok Ops normal | Keswick Water Treatment Plant | 2026-02-24
CENTRAL | February | -Performed station check - logged station readings into PWQ sheet -Checked CL17 reagents - OK -Reviewed filter performance - 100% | Keswick Water Treatment Plant | 2026-02-02
CENTRAL | February | As directed by teamlead onsite to complete workorders Changed chlorine cylinder w/ Will M General Housekeeping Reset Raw water sample pump Fault 007 Also check filter performance via scada @ 11:00 am Filter 1 and 2 both 100% - all ok Ops normal | Keswick Water Treatment Plant | 2026-02-19
CENTRAL | February | Attending site to check Finished water turbidimeter (W11658745). There were no errors in the turbidimeter display. Replaced vial compartment assembly and Operations started high lift pumps. Observed turbidity to increase for a few minutes after startup and then drop to 0.121NTU, after several minutes. Turbidimeter spikes on startup have been occurring regularly. ROC was notified before and after maintenance activities. | Keswick Water Treatment Plant | 2026-02-11
CENTRAL | February | -Helped replace 3" valve -Finished the following work orders *CL17 analyzer maintenance *High life pump 2 flow control valve test | Keswick Water Treatment Plant | 2026-02-18
CENTRAL | February | -Performed station check - logged station readings into PWQ sheet -Changed finished water free analyzer reagents -Performed filter performance review - 100% | Keswick Water Treatment Plant | 2026-02-20
CENTRAL | February | ROC called regarding settled water conduit lolo alarms, as well as CO2 adjusted pH low alarm. @15:36 - CO2 adjusted Low alarm, which stopped the low lift pumps, causing the settled water lolo alarms to follow @15:41 @15:49 when ROC called, CO2 adjusted pH had recovered. Was able to clear alarms and Low lifts restarted, filling the pretreatment / settled water conduit Monitored site remotely, everything is back to normal operations as of @16:00 | Keswick Water Treatment Plant | 2026-02-15
CENTRAL | February | Under direction of OIC Ben Hess. Notified ROC or testing level transmitter in the diesel tank. Worked with contractors to connect and test diesel LIT and generator enclosure TT. | Keswick Water Treatment Plant | 2026-02-19
CENTRAL | February | -Performed station check - logged station readings into PWQ sheet -Reviewed filter performance - 100% -Collected GLIP sample & in-house water quality samples -Performed H&S inspection | Keswick Water Treatment Plant | 2026-02-12
CENTRAL | February | -Reviewed filter performance - 100% -Tried to isolated the plant for repair 3" gate valve - the one going east was successfully closed, but the one going west was frozen - will schedule another day and coordinate with the town of Georgina to isolate from the street -Finished the following work orders *Backwash tube maintenance *Pressure relief valve test *Hoist inspection *Washwater transfer pump maintenance *Filter Top Sample Water Pump Maintenance | Keswick Water Treatment Plant | 2026-02-10
CENTRAL | February | CO2 adjusted pH alarm came in, Co2 pH dropped to 6.5 from an increase in low lift flow. Cleared alarm, and low lift pumps restarted | Keswick Water Treatment Plant | 2026-02-17
CENTRAL | February | -Topped up PACL day tank from 71.14cm to 82.28cm -Reviewed filter performance - 100% -Reset raw turbidimeter fault alarm - raw sample pump tripped - F007 - Restarted sample pump | Keswick Water Treatment Plant | 2026-02-13
CENTRAL | February | Reviewed filter performance values and trends - both filters 100% | Keswick Water Treatment Plant | 2026-02-16
CENTRAL | February | Onsite to reset raw water sample pump fault. Fault 007 overload alarm Adjusted pump to 14 Hz Adjusted flow rates to pH probe, turbidimeter sample tap and lab sample tap. All in normal range. Reset low lift turbidimeter fault | Keswick Water Treatment Plant | 2026-02-13
CENTRAL | February | Attending site to check low-lift Total Chlorine analyzer (W11679195). Cleaned colorimeter cell and calibrated but the reading went down to 0.02mg/L again. Replaced colorimeter and calibrated to 0.18mg/L, Total chlorine based on average of 3 grabs. ROC was notified before and after maintenance activities. | Keswick Water Treatment Plant | 2026-02-20
CENTRAL | February | Under the direction of Ben H Onsite for station and equipment check Take weekly BacT sample W11605591 @ 11:00 am (running) Treated Total: 1.80 mg/l Treated Free: 1.50 mg/l Topped up Fluoride day tank Topped up PACL day tank Ack/reset raw sample pump fault and turbidimeter fault due to low flow - all ok Ops normal | Keswick Water Treatment Plant | 2026-02-17
CENTRAL | February | Completed filter performance check: filter 1- 100%, filter 2- 100% | Keswick Water Treatment Plant | 2026-02-20
CENTRAL | February | -Performed filter performance review - 100% | Keswick Water Treatment Plant | 2026-02-16
CENTRAL | February | -Reviewed filter performance - 100% | Keswick Water Treatment Plant | 2026-02-17
CENTRAL | February | Chris Iliohan and Tyler Smith in with contractor to freeze supply line from main Remove old valve and install new check for leaks. No leak noticed Work complete | Keswick Water Treatment Plant | 2026-02-18
CENTRAL | February | As per workorder check filter performance via scada @ 15:40 Both F1 and F2 100% - all ok | Keswick Water Treatment Plant | 2026-02-18
CENTRAL | February | -Restarted the plant in auto - started with low lift pumps to fill the floc tank, settling tank, and conduit - when restarting high lift pump, the pump was interlocked by hi finish water turbidity - checked finish water turbidimeter - flow OK - performed a turbidimeter maintenance - turbidity still high - replaced sample cell - turbidity high - called in instrumentation on call Eric S. - Eric came in to replace the turbidimeter element - Turbidity came down - restarted high lift pump -Reviewed filter performance - 100% -Performed station check - logged station readings into PWQ sheet -Changed clear well free reagents -Collected weekly BacT sample YD #W11588750 Grab: free=1.28mg/L total=1.56mg/L Analzyer: free=1.23mg/L total=1.49mg/L | Keswick Water Treatment Plant | 2026-02-11
CENTRAL | February | Remove damaged piping on diesel cooling line and install isolation valve to stop water flowing through diesel | Keswick Water Treatment Plant | 2026-02-09
CENTRAL | February | -Performed station check - logged station readings into PWQ sheet Grab: treated free=1.51mg/L total=1.90mg/L@13:40 Analyzer: treated free=1.53mg/L total=1.92mg/L -Collected GIIP samples, weekly BacT sample YD #W11568386, algae sample YD#W11568587, & THM sample YD #W11568116 -Changed chlorine cylinder -Changed settling tank free analyzer reagents -Reviewed filter performance - 100% | Keswick Water Treatment Plant | 2026-02-05
CENTRAL | February | -Performed station check - logged station readings into PWQ sheet -Checked CL17 reagents - OK | Keswick Water Treatment Plant | 2026-02-06
CENTRAL | February | Filter performance check completed: filter 1- 100%, filter 2- 100% | Keswick Water Treatment Plant | 2026-02-04
CENTRAL | February | Onsite to complete station check. Topped up pacl day tanks. Around 10:30 found decommissioned generator water service was passing. Tightened 1? bypass valve and valve began leaking. Leaking water flowing into sanitary drain. 10:46 placed all high lifts and low lifts in manual off. Notified ROC of issues. Closed plant service isolation valve but valve continued to pass and valve housing cracked. Neither isolation valve in fluoride room are to be holding. Held off on attempting to isolate distribution plant isolation valves outside station due to extreme cold conditions and valves being very stiff. 11:30 Was able to temporarily cap leak at generator bypass. 12:00 maintenance arrived and able to install a more permanent cap. Created work order for maintenance to replace service water isolation valve. We will attempt to isolate station completely tomorrow with warmer weather. 14:02 completed filter performance review. Both filters at 100%. Verified all analyzers had reagents and correct flows. Entered data into process sheets. Outstanding settled water lolo alarm due to low lifts in manual off. Plant lab and analyzer verification unable to complete to do plant offline and service water valve issues. Will complete before placing plant online. No other issues found. | Keswick Water Treatment Plant | 2026-02-09
CENTRAL | February | Completed filter performance check: filter 1- 100%, filter 2- 100% | Keswick Water Treatment Plant | 2026-02-06
CENTRAL | February | -Finished the following work orders *Aerator maintenance *Flushed raw water sample line *Fluoride pump maintenance *Diesel generator test run -A technician from Black & McDonald came in to troubleshoot CO2 not start running - Checked heat trace to CO2 pipe - normal and working - Pressure restored to 210kPa - Low temp might cause low pressure | Keswick Water Treatment Plant | 2026-02-05
CENTRAL | February | Completed filter performance check: filter 1- 100%, filter 2- 100% | Keswick Water Treatment Plant | 2026-02-05
CENTRAL | February | Completed filter performance check: filter 1- 100%, filter 2- 100% | Keswick Water Treatment Plant | 2026-02-09
CENTRAL | February | Received call from ROC stating they received a call from Linde technician that needs access to gate to look at CO2 system. Called technician to let them know I could be there in 45 minutes and technician said they would prefer to come back tomorrow at 8am. Will inform Central Crew. Placed High lifts in manual off to keep plant offline until technician can investigate CO2 not dosing issue. | Keswick Water Treatment Plant | 2026-02-04
CENTRAL | February | -Reviewed filter performance - 100% -Finished the following work orders *Chemical pump inspection *Chlorine emergency kit inspection *Turbidimeter maintenance *Fluoride analyzer maintenance | Keswick Water Treatment Plant | 2026-02-03
EAST | February | On site for station check and weekly micro sampling (W11620769) Duty not active, tower level 62% Entered data in PWQ sheets. Verified analyzer: Inlet/Outlet at 10:32 Free Grab: 1.30 mg/L Analyzer: 1.26 mg/L Total Grab: 1.63 mg/l Collected micro sample from inlet/outlet at 10:38 Reviewed trends. Station OK | Sutton Elevated Tank | 2026-02-25
EAST | February | On site to respond to building flood alarm. Float on sump pump was faulty. Swapped out sump pump with new pump. Tested, no issues. | Sutton Elevated Tank | 2026-02-27
EAST | February | Attending site in response to the ROC calling for a building flood alarm. Sump pump had not triggered. Manually moved the float to trigger the pump. Tested the float a few more times to make sure it works. Notified ROC that the issue was corrected. | Sutton Elevated Tank | 2026-02-27
EAST | February | On site for station check and weekly micro sampling (W11606343) Duty active, tower level 56% Entered station data into PWQ sheet. Verified chlorine analyzer: Grab sample taken at 10:50 Free Grab: 1.34 mg/L Analyzer: 1.28 mg/L Total Grab: 1.69 mg/L Micro sample taken from inlet/outlet tap at 10:54 Reviewed trends, no outstanding alarms. Station OK. | Sutton Elevated Tank | 2026-02-17
EAST | February | On site with S. Baidy to to climb tower and close rooftop hatch that was blown open. | Sutton Elevated Tank | 2026-02-12
EAST | February | On site for station check, weekly micro sampling (W11569329) and VOC sampling (W11569301) Tower level - 60% and draining. Recorded station readings in PWQ sheets Verified analyzer reading: Outlet @ 10:40 Free Grab: 1.53 mg/L Analyzer: 1.47 mg/L Total Grab: 1.85 mg/L Collected micro sample @ 10:44 from inlet/outlet. Took VOC samples at 10:47. Reviewed trends, equipment ok Station ok | Sutton Elevated Tank | 2026-02-04
EAST | February | On site for station check, weekly micro sampling (W11589444) Tower level - 50% and filling. Recorded station readings in PWQ sheets Verified analyzer reading: Outlet @ 10:11 Free Grab: 1.45 mg/L Analyzer: 1.42 mg/L Total Grab: 1.80 mg/L Collected micro sample @ 10:13 from inlet/outlet. Reviewed trends, equipment ok Station ok | Sutton Elevated Tank | 2026-02-11
EAST | February | On site for monthly work orders, Notified ROC of work orders being done. Inlet/Outlet Heat Trace Inspection JHSC inspections, Chlorine analyzer maintenance, took grab sample to verify analyzer: Grab: 1.70 mg/L Analyzer: 1.66 mg/L Building low temp alarm test: alarm triggered at 13:38, reset and cleared. Manual valve exercise, Sump pit system inspection, Portable generator test run, And general housekeeping. | Sutton Elevated Tank | 2026-02-03
EAST | February | Deactivated duty 1 for sampling. | Sutton Elevated Tank | 2026-02-04
EAST | February | Informed ROC. Onsite to perform calibration/maintenance on post injection and outlet chlorine analyzer. Used the calibration mode. Took a multiple grab samples and adjusted analyzers accordingly. Post injection chlorine analyzer Free readings A- 1.00 mg/l G- 1.00 mg/l Total readings A- 1.44 mg/l G- 1.45 mg/l Outlet chlorine analyzer Free readings A-1.29 mg/l G- 1.29 mg/l Total readings A- 1.73 mg/l G- 1.73 mg/l All the related alarms cleared. No issues. Informed ROC and left the site. | Keswick Deer Park Elevated Tank | 2026-02-26
EAST | February | 14:05 chlorine grab / analyzer: (mg/l) Pre-injection free= 1.35 ?/ 1.46 Post injection free = 0.84 / 0.90 Outlet free = 0.10 / 0.01? 14:19 calibrated preinjection and outlet free according to 3 grabs' average.? Tower is isolated. | Keswick Deer Park Elevated Tank | 2026-02-27
EAST | February | On site with contractor from Syntec, Chris Scott and Dan Zhou to test operation of inlet valve. | Keswick Deer Park Elevated Tank | 2026-02-27
EAST | February | On site to assist with LCV commissioning. ET is isolated from the system. Opened the BV upstream of FCV while BV downstream remains closed. Opened the drain valve on inlet header to allow the new LCV to open. Placed dechlor pucks at outfall. Tested the LCV open/close function via SCADA. The LCV is de-energized now and will open in auto once the tower is online. ET level is 96% and remains offline. | Keswick Deer Park Elevated Tank | 2026-02-27
EAST | February | On site to flush outlet line after bacteriological sample result received. Fully opened outlet riser isolation valve and opened outlet drain valve enough to hear flow through it. Placed de-chlor pucks in outfall. Flushed between 15:50 and 16:07. Verified analyzers with grab sample at 16:14 Grab free: 1.16 mg/L Analyzer: 5.00 mg/L Total grab: 1.57 mg/L Analyzer: 1.60 mg/L Adjusted free chlorine analyzer after three grab samples. Re-isolated outlet valve due to leaking drain valve. Tower still offline and isolated. | Keswick Deer Park Elevated Tank | 2026-02-27
EAST | February | On site to check station Replaced chlorine injection lines with half inch tubing. Tested Lo alarm and flushed LIT: disregard alarms | Keswick Deer Park Elevated Tank | 2026-02-27
EAST | February | Onsite to commission the new altitude valve, had to download to the PAC to upgrade the revision. Site lost communication for about 5 minutes, Tower was offline and isolated when this occurred. | Keswick Deer Park Elevated Tank | 2026-02-27
EAST | February | Run tubing for analyzers Tuning installed just need instrumentation to connect | Keswick Deer Park Elevated Tank | 2026-02-24
EAST | February | 17:14 - Closed inlet valves to isolate tower at 96% 17:23 - took grab samples from inlet pipe: Free 1.61 mg/L, Total 1.96 mg/L 17:26 - took micro sample (W11673892) | Keswick Deer Park Elevated Tank | 2026-02-25
EAST | February | On site to flush and to start filling KSETDP. @09:05 - Opened first inlet valve on the inlet header, and opened inlet drain valve cracked to flush lines to facility outfall Added dechlor pucks to outfall Outlet analyzer is currently plumbed to the inlet header. Took grab residuals while flushing @09:40 FCL: 1.15 mg/L / Analyzer: 2.30 mg/L - Adjusted analyzer to match grabs TCL: 1.35 mg/L / Analyzer: 1.44 mg/L - Adjusted analyzers to match grabs Grab residual from outfall @09:36 - 0.0 mg/L @09:40 - Closed drain valve on inlet line Removed LOTO from second inlet valve. From 09:40 to 09:55 - Flushed inlet riser pipe multiple times, by opening second inlet valve for a short period, and then closing the first inlet valve, and opening the drain valve to drain what was flushed into the riser pipe. Started filling tank @09:57 - Flow through inlet is 105 L/s. Inspected piping with contractors - no leaks observed on the inlet side. Took grab residuals while filling: FCL Grab: 1.36 / Analyzer: 1.41 mg/L Unshelved the following alarms - pH Lo, Tower level low alarms, Site offline alarms, Chlorine system alarms. No longer any shelved alarms for site Tower level is 15% @10:32 - will monitor and return to site later | Keswick Deer Park Elevated Tank | 2026-02-25
EAST | February | Onsite to commission new pre injection analyzer Site off line Informed ROC and ops Completed the work and verified signals to PAC with PCS Calibrated A=1.46mg/L G=1.45mg/L Cleared associated alarms Informed ROC | Keswick Deer Park Elevated Tank | 2026-02-25
EAST | February | Check drain requirements Measured up drain lines | Keswick Deer Park Elevated Tank | 2026-02-02
EAST | February | I?m site for station check and assigned work orders. Notified the ROC of work being done. Station Offline - Completed visual check of station, contractors not on site today. Chlorine gas detector test - gas leak and gas HIHI alarms triggered at 10:12, and reset. Building low temp alarm test - alarm triggered at 10:32 and reset, JHSC inspections, Ventilation system inspection, Portable generator test run, Chemical system inspection - system offline, performed visual inspection, And general housekeeping. | Keswick Deer Park Elevated Tank | 2026-02-10
EAST | February | On site for station check - Landmark is on site for upgrades projects Visual inspection of site and equipment Station ok | Keswick Deer Park Elevated Tank | 2026-02-02
EAST | February | Connect water temporarily to analyzer Bleed air out of altitude valve and fully open | Keswick Deer Park Elevated Tank | 2026-02-20
EAST | February | 15:15 Returned to site. 15:18 Verified outfall chlorine residual by grab, FCL = 0.01 mg/l. 15:20 grab chlorine residual from inlet, FCL = 1.30 mg/l, TCL = 1.69 mg/l. Adjusted Outlet analyzer (temporarily plumbed to inlet sample line) to match with 3 grabs average. 15:30 Closed the drain valve. Estimated backflushing volume is to be calculated later. The tower remains isolated from the system. | Keswick Deer Park Elevated Tank | 2026-02-20
EAST | February | On site with Dan Boate, wiring altitude valve and chlorine analyzer. | Keswick Deer Park Elevated Tank | 2026-02-20
EAST | February | On site with Sean Peoples installing conduit for new analyzer and valve. | Keswick Deer Park Elevated Tank | 2026-02-12
EAST | February | On site with Jackie S to flush the watermain through drain valve to outfall. Verified all pipe gallery manual valves are in closed position. Lee F. and Kyle R. arrived on site as well. Plumbed the inlet header sample line to Outlet Analyzer temporarily since the new analyzer is not commissioned yet. Worked with Harsh to locate the valve box at Boyers/Queensway, opened the valve slowly. Worked with Lee F to slowly charge the new Singer valve, purged air out of the sensing lines and it is fully open. 11:55 crack opened the drain valve on the inlet header. Checked outfall for flow rate that it is controlled discharge. Placed dechlor pucks at outfall. 12:10 grab chlorine residual at outfall, FCL = 0.00 mg/l. 12:22 grab chlorine residual from inlet header: FCL = 0.01 mg/l, TCL = 0.11 mg/l. Will return to site to later in the afternoon. | Keswick Deer Park Elevated Tank | 2026-02-20
EAST | February | On site to work on altitude valve wiring. | Keswick Deer Park Elevated Tank | 2026-02-11
EAST | February | Install drain for analyzer | Keswick Deer Park Elevated Tank | 2026-02-04
EAST | February | On site for station check. Site Offline. Completed visual check. Station ok. | Keswick Deer Park Elevated Tank | 2026-02-11
EAST | February | On site for station check. Station Offline. Completed visual check of station. Station ok. | Keswick Deer Park Elevated Tank | 2026-02-04
EAST | February | On site to run conduits for new valve and analyser | Keswick Deer Park Elevated Tank | 2026-02-09
CENTRAL | February | Closed Inlet valve MV1 - Tower level is 87%. In order to allow KSETDP to fill quicker. Will be reopened later in the day. West park tank is isolated from distribution | Keswick West Park Reservoir | 2026-02-25
CENTRAL | February | Adjusted duty stop from 85% to 90% in order to fill KSETDP | Keswick West Park Reservoir | 2026-02-25
CENTRAL | February | -Performed station check - logged station readings into PWQ sheet -Checked CL17 reagents - OK -Calibrated free analyzer based on 3 grab tests | Keswick West Park Reservoir | 2026-02-27
CENTRAL | February | Deactivated system duty. Manual open inlet valve MV1. | Keswick West Park Reservoir | 2026-02-25
CENTRAL | February | -Tested chlorine leak alarm | Keswick West Park Reservoir | 2026-02-24
CENTRAL | February | -Performed station check - logged station readings into PWQ sheet -Checked CL17 reagents - OK | Keswick West Park Reservoir | 2026-02-24
CENTRAL | February | Station and equipment check Take weekly BacT sample W11620838 @ 8:25 am (draining) Total: 1.76 mg/l Free: 1.40 mg/l No adjustments required Changed CL2 cylinder w/ JZ (right side) Ops normal | Keswick West Park Reservoir | 2026-02-25
CENTRAL | February | Attending site to check issue with Chlorinator #1 failing to close (W11539246). Adjusted milliamp output on chlorinator and actuated chlorinator to check that it closes completely. ROC was notified before and after maintenance activities. | Keswick West Park Reservoir | 2026-02-02
CENTRAL | February | -Performed station check - logged station readings into PWQ sheet Grab: treated free=1.49mg/L total=1.82mg/L@9:00 Analyzer: treated free=1.54mg/L total=1.79mg/L -Checked CL17 reagents - OK | Keswick West Park Reservoir | 2026-02-02
CENTRAL | February | -Performed station check - logged station readings into PWQ sheet -Changed free reagents | Keswick West Park Reservoir | 2026-02-20
CENTRAL | February | Station and equipment check Take weekly BacT sample w11606488 and grabs. @ 12:50 pm Total: 1.77 mg/l Free: 1.30 mg/l Standardized total analyzer to match grabs Tank ops normal | Keswick West Park Reservoir | 2026-02-17
CENTRAL | February | -Performed station check - logged station readings into PWQ sheet -Checked CL17 reagents - OK | Keswick West Park Reservoir | 2026-02-13
CENTRAL | February | -Performed station check - logged station readings into PWQ sheet -Checked CL17 reagents - OK -Cleaned CL17 analyzers | Keswick West Park Reservoir | 2026-02-06
CENTRAL | February | -Performed station check - logged station readings into PWQ sheet -Collected weekly BacT sample YD #W11589619 -Changed treated total reagents - OK -Finished the following work orders *H&S inspection *Chemical system inspection *Test ran generator | Keswick West Park Reservoir | 2026-02-11
CENTRAL | February | -Performed station check - logged station readings into PWQ sheet Grab: free=1.53mg/L total=1.75mg/L@9:30 Analyzer: free=1.53mg/L total=1.79mg/L -Checked CL17 reagents - Ok -Collected weekly BacT sample YD #W11569728 & monthly samples YD #W11569714 | Keswick West Park Reservoir | 2026-02-04
CENTRAL | February | -Performed station check - logged station readings into PWQ sheet -Checked CL17 reagents - OK | Keswick West Park Reservoir | 2026-02-09
EAST | February | Thaw outlet pipe Thawed pipe 25 ? could not see any more ice | Musselman's Lake Elevated Tank | 2026-02-27
EAST | February | On site to complete station check. Collecting weekly Bac-t Sample. W11619922 Weekly Bac-t Sample. Time: 14:08 Grab (mg/l) Analyzer (mg/l) Free: 1.34 1.39 Total: 1.39 No outstanding alarms on site. No OOS equipment. Verified analyzers. Checked station and trends. | Musselman's Lake Elevated Tank | 2026-02-25
EAST | February | On site to complete following work orders: Chlorine analyzer maintenance. Heat trace inspection. Portable gasoline generator test. JHSC inspection. Contacted ROC at 12:56 about alarms being generated. After completing analyzer maintenance took grabs to verify analyzer. Time: 13:15 Grab (mg/l) Analyzer (mg/l) Free: 1.40 1.39 Completed calibration on pocket colorimetre passed. No issues any changes in trends are due to work orders being completed. | Musselman's Lake Elevated Tank | 2026-02-26
EAST | February | On site to complete station check. Collecting weekly Bac-t Sample. W11605419 Weekly Bac-t Sample. Time: 09:15 Grab (mg/l) Analyzer (mg/l) Free: 1.35 1.36 Total: 1.49 Verified analyzer with grabs. Started well 3 at 09:20 in manual for sampling. No outstanding alarms on site. No OOS equipment. Entered data into PWQ sheet. | Musselman's Lake Elevated Tank | 2026-02-17
EAST | February | Change duty 1 start set point from 72% to 40%. | Musselman's Lake Elevated Tank | 2026-02-19
EAST | February | On site to complete station check. Collecting weekly Bac-t Sample. W11588586 Weekly Bac-t Sample. Time: 08:45 Grab (mg/l) Analyzer (mg/l) Free: 1.36 1.38 Total: 1.48 Outfall was plugged with ice and flooded the valve room. Was able to unplug by using a pick axe which allowed the water to drain. Also replaced the CL-17 chlorine analyzer reagents. No outstanding alarms on site. No OOS equipment on site. | Musselman's Lake Elevated Tank | 2026-02-11
EAST | February | Updating PAC for upcoming well pmp4 commissioning, including duty logic, total flow calculation, PTTW code etc. | Musselman's Lake Elevated Tank | 2026-02-05
EAST | February | On site to complete station check. Collecting weekly Bac-t Sample. W11568186 Weekly Bac-t Sample. Time: 09:35 Grab (mg/l) Analyzer (mg/l) Free: 1.38 1.38 Total: 1.46 Verified analyzer on site. No outstanding alarms on site. No OOS equipment on site. Checked station and trends. | Musselman's Lake Elevated Tank | 2026-02-04
EAST | February | Incrementally increased MV1 open set point from 5% to 17%. | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2026-02-25
EAST | February | Closed tower valve MV1 @10:01 - to allow more flow to fill KSETDP. Tower is currently isolated from distribution, level is 74% | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2026-02-25
EAST | February | Changed MV1 open setpoint to 50%. Placed MV1 back in auto mode. | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2026-02-25
EAST | February | On site for station check and weekly micro sampling (W11620783) Duty active, tower level 69% Manual open recirculation valve, and manual start recirculation pump. Recorded station readings in PWQ sheets Verified analyzer readings: Header @ 9:15 Free Grab: 1.39 mg/L Analyzer: 1.31 mg/L Total Grab: 1.68 mg/L Analyzer: 1.72 mg/L Inlet @ 9:20 Free Grab: 1.62 mg/L Analyzer: 1.62 mg/L Total Grab: 2.00 mg/L Analyzer: 1.99 mg/L Outlet @ 9:06 Free Grab: 1.45 mg/L Analyzer: 1.42 mg/L Total Grab: 1.73 mg/L Analyzer: 1.66 mg/L Collected micro sample from outlet @ 9:10. 9:19 - manual stop recirculation pump, manual close recirculation valve, and place both back in auto. Chemical system: Chlorinator 1 open 13%, BP1 DP=908 kpa Noticed chlorine sysem drawing from left bank, right bank tank not empty. Found that right bank tank was closed, re-opned tank and put back in service. Reviewed trends, checked station. Station OK. | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2026-02-25
EAST | February | Tower valve MV1 placed back to auto, open 100% @14:47 - Started closing tower isolation valve MV1 to throttle down the flow to fill KSETDP faster. Monitored system pressure on woodbine ET header, and both WTPs | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2026-02-25
EAST | February | On site for station check and weekly micro sampling (W11606357) Duty not active, tower level 64% Manual open recirculation valve, and manual start recirculation pump. Recorded station readings in PWQ sheets Verified analyzer readings: Header @ 9:23 Free Grab: 1.34 mg/L Analyzer: 1.31 mg/L Total Grab: 1.70 mg/L Analyzer: 1.69 mg/L Inlet @ 9:29 Free Grab: 1.35 mg/L Analyzer: 1.17 mg/L Total Grab: 1.68 mg/L Analyzer: 1.66 mg/L Adjusted inlet free chlorine value with the avg of three grab samples. Outlet @ 9:36 Free Grab: 1.38 mg/L Analyzer: 1.42 mg/L Total Grab: 1.69 mg/L Analyzer: 1.66 mg/L Collected micro sample from header @ 9:27. 9:42 - manual stop recirculation pump, manual close recirculation valve, and place both back in auto. Reviewed trends, checked station. Station OK. | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2026-02-17
EAST | February | On site for station check, weekly micro sampling (W11589458) Duty not active - Tower level 71% and draining. Manual open recirculation valve, and manual start recirculation pump. Recorded station readings in PWQ sheets Verified analyzer reading: Header @ 8:55 Free Grab: 1.51 mg/L Analyzer: 1.46 mg/L Total Grab: 1.85 mg/L Analyzer: 1.90 mg/L Inlet @ 8:59 Free Grab: 1.50 mg/L Analyzer: 1.42 mg/L Total Grab: 1.87 mg/L Analyzer: 1.83 mg/L Outlet @ 9:04 Free Grab: 1.53 mg/L Analyzer: 1.54 mg/L Total Grab: 1.87 mg/L Analyzer: 1.86 mg/L Collected micro sample from header @ 9:07. Amish stop recirculation pump, and close recirculation valve. Place both back in auto Reviewed trends, equipment ok Station ok | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2026-02-11
EAST | February | Reviewed station trends in lieu of on site station check. Duty active, tower level 75%. Trends all okay. No outstanding alarms. | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2026-02-13
EAST | February | On site with Sean Peoples. Heater in chlorine scrubber rm replaced. | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2026-02-19
EAST | February | On site for station check. Duty not active - Tower level 71% and draining Recorded station readings in PWQ sheets Manual start re-circulation pump. Verified analyzer readings, took grab samples between 9:44-9:52 No adjustments needed. Manual stop recirculation pump. Reviewed trends, equipment ok. Outstanding alarms: N/A Station ok Header @ 9:44 Free Grab: 1.54 mg/L Analyzer: 1.59 mg/L Total Grab: 1.91 mg/L Analyzer: 1.93 mg/L Adjusted free chlorine reading after three grab residuals. Inlet @ 9:52 Free Grab: 1.54 mg/L Analyzer: 1.55 mg/L Total Grab: 1.90 mg/L Analyzer: 1.81 mg/L Adjusted free chlorine reading after three grab residuals. Outlet @ 9:47 Free Grab: 1.55 mg/L Analyzer: 1.60 mg/L Total Grab: 1.90 mg/L Analyzer: 1.88 mg/L | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2026-02-06
EAST | February | On site for station check and monthly work orders, Notified ROC of work orders being done. 9:45 - Chlorine gas detectors test: alarms triggered and were cleared. Chlorine scrubber check, Chlorine analyzer maintenance: flushed y-screens. Zero call inlet free Cl analyzer with no flow conditions. Returned all analyzers to normal operations. Verified chlorine analyzers: Header @ 10:43 Free Grab: 1.55 mg/L Analyzer: 1.58 mg/L Total Grab: 1.91 mg/L Analyzer: 1.95 mg/L Inlet @ 10:48 Free Grab: 1.90 mg/L Analyzer: 2.14 mg/L Total Grab: 2.18 mg/L Analyzer: 2.27 mg/L Outlet @ 10:52 Free Grab: 1.56 mg/L Analyzer: 1.58 mg/L Total Grab: 1.91 mg/L Analyzer: 1.88 mg/L Run recirculation pump, Inlet/outlet heat trace inspection, Manual valve exercise, Actuated valve exercise, Chlorine Scrubber media sampling, Ventilation system inspection, Dehumidifier inspection and cleaning. Entered data into PWQ sheet. Reviewed trends, equipment ok. Station ok. | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2026-02-05
EAST | February | On site for station check, weekly micro sampling (W11569343), and VOC sampling (W11569315) Tower level - 77% and draining. Recorded station readings in PWQ sheets Verified analyzer reading: Header @ 9:13 Free Grab: 1.57 mg/L Analyzer: 1.56 mg/L Total Grab: 1.90 mg/L Analyzer: 1.91 mg/L Inlet @ 9:25 Free Grab: 1.78 mg/L Analyzer: 2.11 mg/L Total Grab: 2.07 mg/L Analyzer: 2.13 mg/L Adjusted inlet free Cl analyzer after three grab samples. Outlet @ 9:28 Free Grab: 1.59 mg/L Analyzer: 1.62 mg/L Total Grab: 1.89 mg/L Analyzer: 1.74 mg/L Adjusted outlet total Cl analyzer after three grab samples. Collected micro sample from header @ 9:17, took VOC samples at 9:20 Reviewed trends, equipment ok Station ok Completed JHSC inspections. | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2026-02-04
EAST | February | Placed pumps back into "REMOTE" after Linear work was completed. | Markham Pumping Station | 2026-02-27
EAST | February | Under direction of OIC (Dan Zhou) On site for; - Station checks Analyzer verification: Grabs @ 11:35 hrs. FCl: 0.04 mg/L TCl: 1.35 mg/L Analyzer: FCl: 0.02 mg/L TCl: 1.34 mg/L Duty inactive Equipment OOS: None Facility OK | Markham Pumping Station | 2026-02-23
EAST | February | Under direction of OIC (Dan Zhou) On site for; - Station checks Analyzer verification: Grabs @ 12:53 hrs. FCl: 0.03 mg/L TCl: 1.37 mg/L Analyzer: FCl: 0.00 mg/L TCl: 1.33 mg/L Duty inactive Equipment OOS: Facility, due to isolation by linear team for valve repairs. Pumps 1,2,3 in local. Facility OK | Markham Pumping Station | 2026-02-26
EAST | February | Under direction of OIC (Dan Zhou) On site for; - Station checks Grabs @ 14:51 hrs. FCl: 0.10 mg/L TCl: 1.42 mg/L Analyzer: FCl: 0.02 mg/L TCl: 1.35 mg/L Duty inactive Equipment OOS: None Facility OK | Markham Pumping Station | 2026-02-02
EAST | February | Under Direction of OIC (Dan Zhou) On Site for PM?s - JHSC Health and Safety checks - Flood alarm test - Comprehensive cleaning - Dehumidifier cleaning and inspection - Generator test run - Hoist inspection Generator Test: Start hours: 589.0 Start time: 10:18 hrs. Stop Hours: 590.6 (includes cool down time) Stop Time: 11:55 hrs. Run Time: 1 hr. 37 mins. Start Fuel: 578/579 L Stop Fuel: 550/548 L Pre run checks; Battery Cell Levels: NA Battery Terminals and Cables: Ok Oil Level: Ok Coolant Level: Ok Fluid Leaks: Ok Coolant Recirculating pump: Ok Faulty Gauges: Ok @ 10:37 hrs. Put pump 2in Manual On (Active), Generator under load @ 11:19 hrs. put pump 2 in manual off Operating Current: 30 amps Operating Frequency: 60 Hz Operating Voltage: 600 Volts, Engine speed: 1801 RPM Water/coolant Temp: 183 f Oil Pressure: 58 psi kPa Oil temp: 197 f @ 11:57 manually triggered flood alarm | Markham Pumping Station | 2026-02-19
EAST | February | Under direction of OIC (Dan Zhou) On site for; - Station checks Grabs @ 12:35 hrs. FCl: 0.05 mg/L TCl: 1.37 mg/L Analyzer: FCl: 0.02 mg/L TCl: 1.33 mg/L Duty inactive Equipment OOS: None Facility OK | Markham Pumping Station | 2026-02-17
EAST | February | Under direction of OIC (Dan Zhou) On site for; - Station checks Grabs @ 09:53 hrs. FCl: 0.07 mg/L TCl: 1.44 mg/L Analyzer: FCl: 0.02 mg/L TCl: 1.44 mg/L Duty inactive Equipment OOS: None Facility OK | Markham Pumping Station | 2026-02-13
EAST | February | Under direction of OIC (Dan Zhou) On site for; - Station checks - Chlorine analyzer maintenance Analyzer verification: Grabs @ 11:19 hrs. FCl: 0.03 mg/L TCl: 1.31 mg/L Analyzer: FCl: 0.02 mg/L TCl: 1.29 mg/L Duty inactive Equipment OOS: None Facility OK | Markham Pumping Station | 2026-02-20
EAST | February | Under direction of OIC (Dan Zhou) On site for; - Station checks Grabs @ 11:53 hrs. FCl: 0.04 mg/L TCl: 1.09 mg/L based on 3 grab ave. Analyzer: FCl: 0.00 mg/L TCl: 0.68-1.25 mg/L ? Trial isolation by linear affecting flow/pressure to analyzer, inaccurate readings by analyzer. Analyzer OOS until isolation valve is reopened. Duty inactive Equipment OOS: None Facility OK | Markham Pumping Station | 2026-02-09
EAST | February | Under direction of OIC Dan Zhou On site for; - station checks - regulatory sampling, (Micro, W11620058) - Operational sampling; nitrification - Actuated valve exercise and inspection (draining during inspection, @ 77 %) Data in PWQ workbook Regulatory sample taken @ 12:58 hrs. Grabs @ 12:58 hrs. FCl: 0.07 mg/L TCl: 1.68 mg/L Analyzer: FCl: 0.03 mg/L TCl: 1.68 mg/L Tower at 83 % (Filling, during sampling) Equipment OOS: none Facility OK | Markham Milliken Elevated Tank | 2026-02-25
EAST | February | On site to investigate network connections. | Markham Milliken Elevated Tank | 2026-02-25
EAST | February | Under direction of OIC Dan Zhou On site for; - station checks - regulatory sampling none, (Micro, W11588722) - operational sampling, nitrification Data in PWQ workbook Regulatory sample taken @ 12:44 hrs. Grabs @ 12:44 hrs. FCl: 0.07 mg/L TCl: 1.82mg/L Analyzer: FCl: 0.02 mg/L TCl: 1.78 mg/L Tower at 80 % (Filling) Equipment OOS: none Facility OK | Markham Milliken Elevated Tank | 2026-02-11
EAST | February | Under direction of OIC Dan Zhou On site for; - station checks - regulatory sampling none, (Micro, W11605563) - Operational sampling; nitrification and corrosion control, ATP Data in PWQ workbook Regulatory sample taken @ 12:44 hrs. Grabs @ 12:44 hrs. FCl: 0.07 TCl: 1.61 Analyzer: FCl: 0.02 TCl: 1.66 Tower at 72 % (Filling) Equipment OOS: none Facility OK | Markham Milliken Elevated Tank | 2026-02-17
EAST | February | Under direction of OIC Dan Zhou On Site for PM?s; - Inlet/outlet Heat trace system Inspection - Low temp alarm test - Sump pit system inspection - Chlorine analyzer maintenance - Comprehensive cleaning - JHSC health and safety inspection - Dehumidifier inspection and cleaning Analyzer verification; Grabs @ 11:48 hrs. FCl: 0.05 mg/L TCl: 1.72 mg/L Analyzer: FCl: 0.02 mg/L TCl: 1.76 mg/L HI/LO Water level Alarms: HI water level alarm triggered @ 12:00 hrs. LO water level alarm triggered @ 12:03 hrs. | Markham Milliken Elevated Tank | 2026-02-12
EAST | February | Onsite to respond to building smoke alarm. Smoke alarm active after power blip on site and ROC was able to clear it first time and alarm became active again and ROC could not clear and reset this time, Arrived onsite, went into the valve room, conducted visual inspection no issues. logged into the OIT cleared building alarm. During time of visit there was a mobile generator (trailer) running with blowers and heaters supplying heat and light into the reservoir. the valve room had a burning smell or looks like hot work was done before my arrival. there was dust in the building, There was no body onsite as it was after hours, I talked to area supervisor, and will call him back if alarm comes in again for further action. Notified ROC before leaving site. | Markham PD5 Reservoir | 2026-02-27
EAST | February | Under direction of OIC Dan Zhou On site for; - station checks - Regulatory sampling ( Micro, W11588722) - Operational sampling, nitrification Data in PWQ workbook Regulatory sample taken from west cell @ 11:01 hrs. West Cell Grabs @ 11:01 hrs. FCl: 0.07 TCl: 1.49 Analyzer: FCl: 0.03 TCl: 1.55 Equipment OOS: East Cell Facility OK | Markham PD5 Reservoir | 2026-02-11
EAST | February | Under direction of OIC Dan Zhou On site for; - station checks - Regulatory sampling ( Micro, W11620058) - Operational sampling, nitrification Data in PWQ workbook Regulatory sample taken @ 11:07 hrs. from west cell West Cell Grabs @ 11:07 hrs. FCl: 0.07 mg/L TCl: 1.46 mg/L Analyzer: FCl: 0.03 mg/L TCl: 1.50 mg/L Equipment OOS: East Cell Facility O | Markham PD5 Reservoir | 2026-02-25
EAST | February | Under direction of OIC Dan Zhou On site for; - station checks - Regulatory sampling ( Micro, W11605563) - Operational sampling, nitrification and corrosion control, with ATP - Interconnect valve between PD5-PD6 inspection Data in PWQ workbook Regulatory sample taken @ 10:58 hrs. from west cell West Cell Grabs @ 10:58 hrs. FCl: 0.07 TCl: 1.51 Analyzer: FCl: 0.03 TCl: 1.52 Equipment OOS: East Cell (under construction) Facility OK | Markham PD5 Reservoir | 2026-02-17
EAST | February | Under direction of OIC Dan Zhou On site for; - station checks - Regulatory sampling ( Micro, W11568358) - Inspect interconnect valve between east/west cell Data in PWQ workbook Regulatory sample taken @ 10:43 hrs. West Cell Grabs @ 10:43 hrs. FCl: 0.05 TCl: 1.44 Analyzer: FCl: 0.03 TCl: 1.45 Equipment OOS: East Cell Facility OK | Markham PD5 Reservoir | 2026-02-04
EAST | February | Under direction of OIC Dan Zhou On site for PM?s; - High/low water level alarm - JHSC health and safety inspection - External venting screens inspection - Chlorine analyzer maintenance - Comprehensive housekeeping Chlorine analyzer verification: Grabs @ 12:37 hrs. From west cell FCl: 0.06 mg/L TCl: 1.42 mg/L Analyzer FCl: 0.03 mg/L TCl: 1.47 mg/L Hi/Lo water level alarms functioning East Cell OOS | Markham PD5 Reservoir | 2026-02-03
EAST | February | On site for station check. Collected in house iron samples. Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 2.60mg/l FCL Analyzer: 2.58mg/l 10:25hrs: Effluent Free Cl2 grab residual: 2.62mg/l FCL Analyzer: 2.58mg/l Effluent Total Cl2 grab residual: 2.85mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: Chlorinator #2 out of service, sourcing new rotameter. | Stouffville Well 3 | 2026-02-23
EAST | February | On site for station check and to collect weekly micro samples (W11620016). Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 2.56mg/l FCL Analyzer: 2.52mg/l 09:42hrs: Effluent Free Cl2 grab residual: 2.56mg/l FCL Analyzer: 2.52mg/l Effluent Total Cl2 grab residual: 2.80mg/l Raw collected @ 09:42hrs. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: Chlorinator #2 out of service. | Stouffville Well 3 | 2026-02-25
EAST | February | On site for station check. Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 2.56mg/l FCL Analyzer: 2.57mg/l 10:55hrs: Effluent Free Cl2 grab residual: 2.44mg/l FCL Analyzer: 2.50mg/l Effluent Total Cl2 grab residual: 2.84mg/l Silicate system inspection. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: Chlorinator #2 out of service, sourcing new rotameter. | Stouffville Well 3 | 2026-02-26
EAST | February | On site for station check. Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 2.46mg/l FCL Analyzer: 2.42mg/l 11:25hrs: Collected Raw PH: 7.27 11:25hrs: Effluent Free Cl2 grab residual: 2.34mg/l FCL Analyzer: 2.33mg/l Effluent Total Cl2 grab residual: 2.60mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: Chlorinator #2 out of service. | Stouffville Well 3 | 2026-02-02
EAST | February | On site with Travis Wyatt for Chlorine Cylinder change. Conducted monthly maintenance: 10:00hrs: Cleaned HACH CL17 Analyzer, Verified Analyzers after cleaning @10:25hrs: Influent FCL grab residual: 2.46mg/l, Analyzer: 2.44mg/l Effluent FCL grab residual: 2.40mg/l. Analyzer: 2.34mg/l Turbidimeter Calibration and maintenance Chlorine Leak Detector Test Silicate system inspection, injection point cleaning and pump dosage checks. Replaced diaphragm on Pump 2. Chlorine system inspection. Chlorinator #2 OOS for rotameter installation. Housekeeping | Stouffville Well 3 | 2026-02-12
EAST | February | On site with Travis Wyatt for Cylinder change. | Stouffville Well 3 | 2026-02-24
EAST | February | On site for station check. Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 2.52mg/l FCL Analyzer: 2.55mg/l 12:45hrs: Effluent Free Cl2 grab residual: 2.50mg/l FCL Analyzer: 2.53mg/l Effluent Total Cl2 grab residual: 2.86mg/l Changed Influent and Effluent Analyzer reagents. Decreased Chlorine Influent dosage setpoint from 2.60mg/l to 2.50mg/l due to middle of winter. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: Chlorinator #2 out of service, sourcing new rotameter. | Stouffville Well 3 | 2026-02-20
EAST | February | On site for station check and to collect weekly micro samples (W11605521). Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 2.58mg/l FCL Analyzer: 2.55mg/l 09:55hrs: Effluent Free Cl2 grab residual: 2.60mg/l FCL Analyzer: 2.54mg/l Effluent Total Cl2 grab residual: 2.92mg/l Raw collected @ 09:55hrs. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: Chlorinator #2 out of service. | Stouffville Well 3 | 2026-02-17
EAST | February | On site for station check and to collect weekly micro samples (W11588680). Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 2.60mg/l FCL Analyzer: 2.63mg/l 09:40hrs: Effluent Free Cl2 grab residual: 2.62mg/l FCL Analyzer: 2.60mg/l Effluent Total Cl2 grab residual: 3.00mg/l Raw collected @ 09:40hrs. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: Chlorinator #2 out of service. | Stouffville Well 3 | 2026-02-11
EAST | February | On site for Silicate delivery from 33.93cm to 65.8cm. | Stouffville Well 3 | 2026-02-18
EAST | February | On site for station check. Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 2.55mg/l FCL Analyzer: 2.45mg/l 09:50hrs: Effluent Free Cl2 grab residual: 2.55mg/l FCL Analyzer: 2.45mg/l Effluent Total Cl2 grab residual: 2.72mg/l Adjusted Influent Cl17 Analyzer from 2.45mg/l to 2.55mg/l based on multiple Cl2 grab residuals. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: Chlorinator #2 out of service, sourcing new rotameter. | Stouffville Well 3 | 2026-02-13
EAST | February | On site for station check and to collect weekly micro samples (W11568302). Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 2.68mg/l FCL Analyzer: 2.66mg/l 09:35hrs: Effluent Free Cl2 grab residual: 2.64mg/l FCL Analyzer: 2.57mg/l Effluent Total Cl2 grab residual: 2.80mg/l Raw collected @ 09:35hrs. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: Chlorinator #2 out of service. | Stouffville Well 3 | 2026-02-04
EAST | February | On site for station check. Operational iron samples collected. Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 2.84mg/l FCL Analyzer: 2.91mg/l 10:40hrs: Effluent Free Cl2 grab residual: 2.86mg/l FCL Analyzer: 2.78mg/l Effluent Total Cl2 grab residual: 3.10mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: Chlorinator #2 out of service, sourcing new rotameter. | Stouffville Well 3 | 2026-02-09
EAST | February | On site with Travis Wyatt to change CL2 Cylinder. | Stouffville Well 3 | 2026-02-05
EAST | February | On site for station check. Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 2.60mg/l FCL Analyzer: 2.60mg/l 11:00hrs: Effluent Free Cl2 grab residual: 2.58mg/l FCL Analyzer: 2.52mg/l Effluent Total Cl2 grab residual: 2.84mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: Chlorinator #2 out of service, sourcing new rotameter. | Stouffville Well 3 | 2026-02-06
EAST | February | On site for station check and to collect weekly micro samples (W11620016). Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 3.42mg/l FCL Analyzer: 3.48mg/l 08:45hrs: Effluent Free Cl2 grab residual: 1.98mg/l FCL Analyzer: 1.92mg/l Effluent Total Cl2 grab residual: 2.66mg/l Well 1 Raw collected @ 08:45hrs. Well 2 Raw collected @ 09:17hrs. Switched Well duties: W1 to D2, W2 to D1. Isolated Hypo Tank #2 to drawdown Hypo Tank #1 for replacement due to leak midway up the tank. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Stouffville Well 1 & 2 | 2026-02-25
EAST | February | On site for station check. Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 3.40mg/l FCL Analyzer: 3.44mg/l 12:45hrs: Effluent Free Cl2 grab residual: 1.88mg/l FCL Analyzer: 1.93mg/l Effluent Total Cl2 grab residual: 2.54mg/l Hypo Pump Diaphragms swapped out in both pumps. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Stouffville Well 1 & 2 | 2026-02-26
EAST | February | On site for station check. Collected in house iron samples. Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 3.42mg/l FCL Analyzer: 3.48mg/l 12:15hrs: Effluent Free Cl2 grab residual: 1.95mg/l FCL Analyzer: 1.91mg/l Effluent Total Cl2 grab residual: 2.44mg/l Silicate system maintenance. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Stouffville Well 1 & 2 | 2026-02-23
EAST | February | On site for station check. Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 3.50mg/l FCL Analyzer: 3.60mg/l 09:15hrs: Effluent Free Cl2 grab residual: 1.82mg/l FCL Analyzer: 1.88mg/l Effluent Total Cl2 grab residual: 2.34mg/l Switched Duties on Well Pumps: W1 to D2, W2 to D1. Collected raw PH values: 09:30hrs: Well 1: 7.97 09:45hrs: Well 2: 8.00 Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Stouffville Well 1 & 2 | 2026-02-02
EAST | February | On site receiving Silicate delivery. Bulk Tank start: 50.33cm, Bulk tank finish: 96.35cm. | Stouffville Well 1 & 2 | 2026-02-18
EAST | February | Received 1000L hypo. 200L to BL12. | Stouffville Well 1 & 2 | 2026-02-18
EAST | February | On site for station check. Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 3.62mg/l FCL Analyzer: 3.55mg/l 09:15hrs: Effluent Free Cl2 grab residual: 1.96mg/l FCL Analyzer: 1.94mg/l Effluent Total Cl2 grab residual: 2.46mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Stouffville Well 1 & 2 | 2026-02-13
EAST | February | On site for station check and to collect weekly micro samples (W11605521). Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 3.72mg/l FCL Analyzer: 3.75mg/l 08:32hrs: Effluent Free Cl2 grab residual: 1.74mg/l FCL Analyzer: 1.70mg/l Effluent Total Cl2 grab residual: 2.26mg/l Well 1 Raw collected @ 09:30hrs. Well2 Raw collected @ 08:35hrs. Ran Well #1 in manual to collect raw sample and to also investigate erratic flow issues noticed by ROC. Did not notice any flow fluctuations, however, as recommended by Team Lead Dan Z, we will increase the flow rates to both wells from 23L/S to 27 L/S. Placed Well #1 into Duty 1 and Well #2 to Duty #2. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Stouffville Well 1 & 2 | 2026-02-17
EAST | February | On site for monthly maintenance: 09:15hrs: Cleaned HACH CL17 Analyzer, Verified Analyzer after cleaning @09:55hrs: Influent FCL grab residual: 1.89mg/l, Analyzer: 1.86mg/l Effluent FCL grab residual: 1.64mg/l. Analyzer: 1.61mg/l. Received 1250L of Hypo from Glen Chemicals. Conducted Generator Test Run (10:00hrs): Diesel Generator Run Monthly Test: Start Runtime: 10:00hrs (Run hrs: 661.4) Fuel Start: 978L Stop Runtime: 11:15hrs (Run hrs: 662.7) Fuel Stop: 964L Generator Performance Data recorded below: Battery Cell Levels: OK Battery Terminals/Cables: Ok Oil and Coolant: Ok Amps: 60amps Volts: 595 Hertz: 61 RPM: 1750 Oil Pressure: 25psi Water temp: 150F Oil temp: 180F No issues during generator run test. Ran Well 2 during run test. Turbidimeter maintenance and calibration completed. Conducted chemical system inspection including injection points. | Stouffville Well 1 & 2 | 2026-02-10
EAST | February | On site for station check. Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 3.42mg/l FCL Analyzer: 3.52mg/l 11:05hrs: Effluent Free Cl2 grab residual: 1.97mg/l FCL Analyzer: 2.00mg/l Effluent Total Cl2 grab residual: 2.64mg/l Changed influent and effluent CL17 Analyzers Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Stouffville Well 1 & 2 | 2026-02-20
EAST | February | On site for station check and to collect weekly micro samples (W11588680). Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 3.40mg/l FCL Analyzer: 3.35mg/l 10:45hrs: Effluent Free Cl2 grab residual: 1.97mg/l FCL Analyzer: 1.92mg/l Effluent Total Cl2 grab residual: 2.42mg/l Well 1 Raw collected @ 11:13hrs. Well2 Raw collected @ 10:45hrs. Switched Pump duties: W1 to D1, W2 to D2. Silicate dose slightly low, checked Silicate Calibration columns, dosing close to what it should be. Made slight adjustment to Silicate P1, Max Flow from 88 to 95ml/min. Will monitor dosage on next station check. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Stouffville Well 1 & 2 | 2026-02-11
EAST | February | On site for station check. Operational iron samples collected. Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 3.60mg/l FCL Analyzer: 3.55mg/l 09:55hrs: Effluent Free Cl2 grab residual: 1.82mg/l FCL Analyzer: 1.82mg/l Effluent Total Cl2 grab residual: 2.18mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Stouffville Well 1 & 2 | 2026-02-09
EAST | February | Changed well 2 percentage decline hi alarm set point from 30% to 35%, as requested by Tanya K. | Stouffville Well 1 & 2 | 2026-02-11
EAST | February | On site for station check. Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 3.42mg/l FCL Analyzer: 3.49mg/l 12:45hrs: Effluent Free Cl2 grab residual: 2.03mg/l FCL Analyzer: 2.07mg/l Effluent Total Cl2 grab residual: 2.84mg/l Conducted JHSC Inspection and Housekeeping. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Stouffville Well 1 & 2 | 2026-02-06
EAST | February | On site for station check and to collect weekly micro samples (W11568302). Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 3.96mg/l FCL Analyzer: 3.93mg/l 08:40hrs: Effluent Free Cl2 grab residual: 2.46mg/l FCL Analyzer: 2.46mg/l Effluent Total Cl2 grab residual: 3.26mg/l Well 1 Raw collected @ 08:40hrs. Well2 Raw collected @ 08:40hrs. Inspected Hypo Pumps and Hypo chemical board. No issues. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Stouffville Well 1 & 2 | 2026-02-04
EAST | February | On site to accept diesel fuel delivery Start: 64cm/626L Stop: 100.7cm/1007L No issues with delivery on site. | Ballantrae Well 1 & 2 | 2026-02-27
EAST | February | On site to check station and equipment, as well as collect samples. Well 1 is running in duty 1. 08:33 Collected well1 raw. YD W11619922. 08:38 grab chlorine residual on treated sample: FCL = 1.85 mg/l, Total = 2.09 m/g. Effluent Analyzer free = 1.88 mg/l. 08:38 Collected treated sample. 08:41 influent grab free = 1.98 mg/l, analyzer free = 1.99 mg/l. 08:43 switched duty 1 well to Well 2. Rotated hypo pump duty at the same time. 09:03 collected well 2 raw. Station readings are entered in PWQ sheet. Reviewed trends, station is under normal operation. | Ballantrae Well 1 & 2 | 2026-02-25
EAST | February | On site to receive hypo delivery | Ballantrae Well 1 & 2 | 2026-02-24
EAST | February | On site to complete station check. Time: 11:50 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.66 1.74 Time: 11:52 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.74 1.70 Total: 1.80 Verified analyzers with grabs all ok. Checked station and trends. No outstanding alarms on site. No OOS equipment. | Ballantrae Well 1 & 2 | 2026-02-26
EAST | February | On site for station check, and operational sampling (W11614421). Duty active, Tower level 80%. Entered data into PWQ sheets. Verified analyzers: Inffluent taken at 14:08 Free Grab: 1.99 mg/L Analyzer: 1.97 mg/L Effluent taken at 14:10 Free grab: 1.96 mg/L Analyzer: 1.90 mg/L Total grab: 2.38 mg/L Took operational sample at 14:17 Chemical systems: Hypo pump 1 running at 22% speed, DP=780 kpa Silicate pump 1 running at 43% speed, DP= 760 kpa. Reviewed SCADA trends, Station OK. | Ballantrae Well 1 & 2 | 2026-02-23
EAST | February | On site to complete station check. Recording raw water PH monitoring. Time: 10:10 Influent Grab (mg/l) Analyzer (mg/l) Free: 2.04 2.00 Time: 10:13 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.78 1.72 Total: 2.01 Verified analyzers with grabs all ok. Raw water PH 8.04. Entered data into PWQ sheet. Checked station and trends. No OOS equipment. No outstanding alarms on site. At 10:25 put BLW3 to manual to sample raw water PH. | Ballantrae Well 1 & 2 | 2026-02-02
EAST | February | On site to complete station check. Collecting weekly Bac-t Samples. W11588586 Weekly Bac-t Samples. Time: 09:50 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.98 2.01 Time: 09:55 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.61 1.69 Total: 1.72 Entered data into PWQ sheet. Verified analyzers with grabs. Between 10:00 and 10:35 shut down well 1 ran well 2, then shut down well 2 and put well 1 in auto and everything back to normal. Checked station and trends. No OOS equipment. No outstanding alarms. | Ballantrae Well 1 & 2 | 2026-02-11
EAST | February | 7:42am Man/Start well 1 for sampling. | Ballantrae Well 1 & 2 | 2026-02-18
EAST | February | Check hose bib for leaks Install new hose bib old one leaking badly Needs a new garden hose will notify operator | Ballantrae Well 1 & 2 | 2026-02-10
EAST | February | Placed well 1&2 man/off for planned shut down. | Ballantrae Well 1 & 2 | 2026-02-17
EAST | February | -on site to assist with power down of station transferred pac panel to the portable unit and turned generator off called roc (0830) to warn them of the alarms that would be generated. Once electrical contractor and hydro reconnected we confirmed rotation and voltage at the breaker. Closed station back to utility and cleared alarms (1715). Retuned pac panel to normal power. Called roc to activate duty and confirmed that pump was running. Under direction of oic. | Ballantrae Well 1 & 2 | 2026-02-17
EAST | February | On site to complete station check. Time: 09:25 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.60 1.55 Time: 09:27 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.44 1.49 Total: 1.76 Verified analyzers with grabs all ok. Checked station and trends. No outstanding alarms on site. No OOS equipment. | Ballantrae Well 1 & 2 | 2026-02-20
EAST | February | On site to complete following work orders: W11590524 Hypo System Maintenance W11590555 CL-17 Analyzer Maintenance W11590585 Diesel Generator Test Run W11590632 CL-17 Analyzer Maintenance W11590719 NTU Maintenance W11592847 Silicate System Inspection W11592871 Dechlorination Puck Dispenser Inspection On site to help with hypo delivery. Start: 275L Stop: 425L Well 1 and 2 put in manual at 10:02. Started generator at 12:46. Attached to this entry will be the generator stats. Any changes in trends or alarms created re due to work orders being completed. After analyzer cleaning verifying analyzers with grabs. Time: 14:00 Influent Grab (mg/l) Analyzer (mg/l) Free: 2.04 2.00 Time: 14:02 Effluent Grab (mg/l) Analyzer (mg/l) Free: 2.03 1.98 After verifying analyzers no issues calibration on pocket colorimetre passed with standard viles. I issues with work orders. | Ballantrae Well 1 & 2 | 2026-02-18
EAST | February | On site to complete hypo top up from Glen Chemicals certificate of analysis is attached to log entry. Start: 56.44 Stop: 80.76 No issues with top up. | Ballantrae Well 1 & 2 | 2026-02-10
EAST | February | On site to complete station check. Time: 10:10 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.91 1.95 Time: 10:12 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.83 1.69-1.83 Total: 2.01 Verified analyzers with grabs. Adjusted the effluent free after multiple grabs were taken from a 1.69mg/l to a 1.83mg/l at 10:15. Replaced reagents in both the influent and effluent free CL-17 analyzers. Checked site and trends. No outstanding alarms on site. No OOS equipment. Entered data into PWQ. | Ballantrae Well 1 & 2 | 2026-02-13
EAST | February | On site to complete station check. Collecting weekly Bac-t Samples. W11638986 Weekly Bac-t Samples. Time: 08:10 Influent Grab (mg/l) Analyzer (mg/l) Free: 2.17 2.26 Time: 08:13 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.75 1.80 Total: 1.80 Verified analyzers with grabs all ok. Stopped well 1 at 08:16. Started well 2 at 08:17. No outstanding alarms on site. No OOS equipment. At 08:52 shut down well 2 and put it to auto. At 08:53 put well 1 back to auto duty 1. | Ballantrae Well 1 & 2 | 2026-02-18
EAST | February | -on site to address Vfd fault. Found unit in overcurrent alarm. Reset the Vfd on the keypad and cleared alarms on scada. Motor started and currently monitoring to confirm operation. Well has been running for 15 minutes no issues current output of drive all within spec. Called Patrick F to let him know what happened. Under direction of oic. | Ballantrae Well 1 & 2 | 2026-02-17
EAST | February | On site to complete station check. Collecting weekly Bac-t Samples. W11568186 Weekly Bac-t Samples. Time: 11:38 Influent Grab (mg/l) Analyzer (mg/l) Free: 2.00 2.04 Time: 11:41 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.72 1.64 Total: 1.93 Verified analyzers with grabs. Checked station and trends. Stopped well 1 at 11:45 and started well 2 in manual at 11:46. Stopped well 2 at 12:10 and put all wells back to auto and restarted well 1 at 12:11. No outstanding alarms on site. No OOS equipment. | Ballantrae Well 1 & 2 | 2026-02-04
EAST | February | On site to place both wells local off for electrical shutdown today. Contractors conducting electrical upgrades to facility and will require electricity to be shutdown until 3pm. Generator will be offline and unavailable during this time. ROC notified of shutdown. Hypo delivery received 200L. | Ballantrae Well 1 & 2 | 2026-02-03
EAST | February | On site to complete station check. Time: 13:15 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.87 1.87 Time: 13:17 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.85 1.77 Total: 2.09 Verified analyzers with grabs. Checked station and trends. Entered data into PWQ sheets. No outstanding alarms on site. No OOS equipment. | Ballantrae Well 1 & 2 | 2026-02-09
EAST | February | On site to complete station check. Time: 09:20 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.80 1.84 Time: 09:23 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.75 1.66 Total: 1.87 Verified analyzers with grabs all ok. Checked site and trends. No outstanding alarms on site. No OOS equipment on site. Entered data into PWQ sheet. | Ballantrae Well 1 & 2 | 2026-02-06
EAST | February | -on site to assist with site shut down 0930 got pac ups on the temp gen contractor brought. We confirmed power was disconnected and contractor completed work. We returned power at 1320 and confirmed no issues. PAC returned to normal power and placed pumps back to auto. Under direction of oic. | Ballantrae Well 1 & 2 | 2026-02-03
EAST | February | On site to verify silicate pump 1 operation. Placed it in duty 1 and enabled silicate pump duty rotation. Enable chlorine system duty rotation. Activated well duty. System is running normally. Equipment OOS: silicate bulk tank. | Ballantrae Well 3 | 2026-02-26
EAST | February | WRONG BOOK MTW3 On site to correct source of chlorine gas leak with Jack P. Cylinders already isolated, turned booster pump 2 local on to purge chlorine lines. Replaced parker fitting on outlet of the regulator on left bank cylinder. Opened chlorine cylinders and vacuum tested system for leaks. Backwashed station for a few mins, with de-chlor pucks in the catch basin. Placed chlorine system back in service and placed well back in service. Monitoring well start up. | Ballantrae Well 3 | 2026-02-23
EAST | February | On site to complete station check. Time: 11:03 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.69 1.63 Time: 11:05 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.66 1.74 Total: 1.83 Verified analyzers with grabs. No outstanding alarms on site. Silicate level is 140cm. No OOS equipment. Checked site and trends. | Ballantrae Well 3 | 2026-02-26
EAST | February | On site for station check, and operational sampling (W11614421). Activated system duty, Tower level 73%. Entered data into PWQ sheets. Verified analyzers: Inffluent taken at 13:10 Free Grab: 2.46 mg/L Analyzer: 2.38 mg/L Effluent taken at 13:12 Free grab: 1.56 mg/L Analyzer: 1.65 mg/L Total grab: 1.89 mg/L Took operational sample at 13:19 Chemical systems: Chlorinator 2 open at 56%, BP2 running DP=1450 kpa Silicate pump 2 running at 22% speed, DP= 680 kpa. Noticed silicate pump 1 was air locked, rotated to pump 2 and deactivated duty rotation and SCADA. Was unable to correct pump 1 while on site. Reviewed SCADA trends, Station OK. | Ballantrae Well 3 | 2026-02-23
EAST | February | Check leaking backflow preventer Replaced 1st check disc debris on disc cleaned and retested Passed | Ballantrae Well 3 | 2026-02-26
EAST | February | On site to check station and equipment, as well as collect samples. Well 3 is running in duty 1. 09:25 Collected well 3 raw. YD W11619922. 09:30 grab chlorine residual on treated sample: FCL = 1.69 mg/l, Total = 2.01 m/g. Effluent Analyzer free = 1.71 mg/l. 09:30 Collected treated sample. 09:33 influent grab free = 2.07 mg/l, analyzer free = 2.18 mg/l. 09:36 standardized influent analyzer reading according to 3 grabs? average. 09:43 Switched chlorine duty to run #1 Chlorinator #1 is dosing at 28 ppd, which is the same of #2. #1 vacuum is at -100mbar. Chlorine booster pump 1 discharge pressure is 205 psi, which is similar to #2?s discharge pressure of 210 psi. No noticeable issue with chlorine #1. Leaving chlorine #1 running in lead duty. Trouble shoot silicate pump 1 issue. Foot valve needs cleaning. Will return to site to perform more testing on silicate pump 1 system. It is OOS for now. Station readings are entered in PWQ sheet. Reviewed trends, station is under normal operation. | Ballantrae Well 3 | 2026-02-25
EAST | February | On site to complete station check. Collecting raw water PH samples. Time: 11:15 Influent Grab (mg/l) Analyzer (mg/l) Free: 2.05 2.11 Time: 11:18 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.41 1.40 Total: 1.61 Verified analyzers with grabs all ok. Checked site and trends. No outstanding alarms on site. Chlorinator 1 OOS due to issues with dosing will troubleshoot tomorrow. Raw water PH is 8.13. At 11:26 put well 3 into auto which shut down the well. | Ballantrae Well 3 | 2026-02-02
EAST | February | Disabled well 3 percent decline master alarm. It is not setup by Water Resources yet. | Ballantrae Well 3 | 2026-02-17
EAST | February | Silicate top up: Before: 120L After: 200L | Ballantrae Well 3 | 2026-02-10
EAST | February | Update software/PAC/SCADA with new updates for contract. Dan onsite for the duration of the update. Well was OFF for the complete update time period. Started Well, commissioned new software, confirmed data capture as required. All work for preparation of contract development occurring. | Ballantrae Well 3 | 2026-02-10
EAST | February | Switched chlorinator 2 to chlorinator 1 to see if the chlorinator causes any issues. Will monitor remotely. | Ballantrae Well 3 | 2026-02-12
EAST | February | On site to complete station check. Collecting weekly Bac-t Samples. W11588586 Weekly Bac-t Samples. Time: 11:00 Influent Grab (mg/l) Analyzer (mg/l) Free: 2.12 2.21 Time: 11:03 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.46 1.55 Total: 1.69 Verified analyzers with grabs. Entered data into PWQ sheet. No OOS equipment on site. | Ballantrae Well 3 | 2026-02-11
EAST | February | On site to complete following work orders: W11600561 Cl2 Emergency Repair Kit Inspection. W11600571 Low Temperature Alarm Test W11600582 Exhaust Fan Check W11600588 Supply Fan 1 Check W11600594 Chlorine Leak Detector Test W11600612 Chlorine Scrubber Check W11600622 Diesel Generator Test W11592057 Housekeeping Attached to this entry is the information for the generator test. At 09:46 informed ROC of work orders to be completed. At 09:46 put well 3 in manual and shut it down. No issues with generator run while generator was running on load. Any changes in trends are due to work orders being completed, any alarms created are also due to work orders being done. | Ballantrae Well 3 | 2026-02-12
EAST | February | On site to complete the following work orders: W11600663 Well Pump Oil Drip System Inspection. W11600668 Chlorine Analzyer Maintenance W11602115 JHSC Inspection W11602138 NTU Calibration and Maintenance W11602493 Dechlorination Puck Dsicpenser Inspection W11602606 Chemical System Inspection Silicate W11602630 Chemical System Inspection Chlorine. Informed ROC of work to be completed at 10:24. Leaving site to top up BLW1/2 with hypo delivery. Back on site to continue completing work orders. Testing chlorintor 1 and troubleshooting to see if we get any lolo influent. Going to start generator shutting well 3 off at 13:15. Will not be running generator today will finish this work order later this week. Time: 14:25 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.5. 1.55 Time: 14:26 Effluent Grab (mg/l) Analyzer (mg/l) Free: 2.07 2.09 Verified analyzers with grabs no issues. No issues with work orders. Any changes in trends or alarms created are due to work orders being completed. | Ballantrae Well 3 | 2026-02-10
EAST | February | On site to complete station check. Time: 09:33 Influent Grab (mg/l) Analyzer (mg/l) Free: 2.20 2.28 Time: 09:35 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.66 1.63 Total: 1.86 Verified analyzers with grabs all ok. Checked site and trends. No outstanding alarms on site. No OOS equipment. Entered data into PWQ sheet. | Ballantrae Well 3 | 2026-02-13
EAST | February | On site to complete station check. Time: 09:50 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.48 1.49 Time: 09:42 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.27 1.32 Total: 1.49 Verified analyzers with grabs all ok. Chlorinator 1 is still off for the weekend due to issues on start up and shut down. No outstanding alarms on site. Entered data into PWQ sheet. | Ballantrae Well 3 | 2026-02-20
EAST | February | On site to complete station check. Collecting weekly Bac-t Samples. W11605419 Weekly Bac-t Samples. Time: 10:15 Influent Grab (mg/l) Analyzer (mg/l) Free: 2.10 2.18 Time: 10:20 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.58 1.56 Total: 1.70 Verified analyzers with grabs all ok. Checked site and trends. Percent decline alarm acknowledged not Abel to reset. Lowered flow from 30l/s to 25l/s and switched to chlorinator 1 to test and see if there is any issue with influent free. Entered data into PWQ sheet. Put flow back to 30l/s to see if there is a change will monitor off site. Shut well 3 off due to sample being collected and more troubleshooting needing to be done. Put chlorinator 1 in manual off. | Ballantrae Well 3 | 2026-02-17
EAST | February | Silicate bulk tank (SILC_TK1_LIT1) is reading 55cm. Confirmed with on site consultant (Adil M.), it is coming from contractors' activity. There is no chemical/liquid in side the tank. Ask consultant to submit request to power off the LIT until the bulk tank is in placed in service. Disregards the LIT reading until then. | Ballantrae Well 3 | 2026-02-11
EAST | February | On site with Kyle C to test new software. Tested AIT1, AIT2, PIT1 interlocks and alarms. Tested silicate pump operation in manual. 11:37 ? 11:54 Man/start well 3. 12:04 ? 12:24 Run Well 3 in auto. 12:30 ? 13:36 Run well 3 in auto. 14:00 ? 15:03 Man/Start well 3 a few times to test and start/stop sequence. New software commissioning is complete. Disabled Master Alarms on silicate day tank LIT, silicate bulk tank LIT as they are not commissioned. Well 4 is visible on SCADA, however, it is not commissioned. Well 3 is back to auto duty standby. Silicate system is drawing from the temporary day tank. | Ballantrae Well 3 | 2026-02-10
EAST | February | On site responding to Influent Chlorine Lolo lockout that occurred overnight @03:42 CMU5 #W11664802 Arrived on site @11:35 and analyzer is reading 0.05 mg/L. Verified analyzer reading with grab residual 0.07 mg/L Connected 2 lengths of discharge hosing to the waste man hole at back of building. Started backflushing @11:50. Added dechlorination pucks to chamber. Stopped backflushing @12:18. Disconnected backflushing hose. Influent residual is 1.25 mg/L Tested chlorinator #1 while backflushing. Did not observe any issues while running it. Will leave OOS for remainder on weekend, but is available if needed. Started well #3 in manual @12:30, with chlorinator #2 in D1. Well is running okay, no issues with chlorine dosing. Also investigated the well #3 percent decline Lolo alarms tat have been coming in. Observed that after an hour of well #3 running the value for well performance spikes above 100%. Will inform Team lead/supervisor next week. Station ok, no further issues on site | Ballantrae Well 3 | 2026-02-15
EAST | February | On site to complete station check. Collecting weekly Bac-t Samples. W11568200 Weekly Bac-t Samples. W11569414 Monthly Manganese Samples. Time: 13:50 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.98 2.01 Time: 13:53 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.52 1.48 Total: 1.59 Activated duty at 13:03 to sample wells 1 and 2. Checked site and trends. Verified analyzers with grabs. Well 1 OOS for WQ issues. Diesel tank level hi alarm disregard. Stopped well 1. All flow from this well went to waste and not to system. | Ballantrae Well 3 | 2026-02-04
EAST | February | Activate duty. | Ballantrae Well 3 | 2026-02-09
EAST | February | On site to complete station check. Time: 10:15 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.53 1.52 Time: 10:20 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.51 1.53 Total: 1.70 Entered data into PWQ sheet. Verified analyzers on site. Checked site and trends. No outstanding alarms on site. Chlorinator 1 still OOS. | Ballantrae Well 3 | 2026-02-06
EAST | February | On site with Kyle C to test new software. Man/Stop well 3 and placed W3 to local off. Informed ROC. Well 3 is to remain OOS and Local OFF for the night. Informed ROC and team. | Ballantrae Well 3 | 2026-02-09
EAST | February | On site to complete station check. Collecting weekly Bac-t Samples. W11568186 Weekly Bac-t Samples. Time: 12:30 Influent Grab (mg/l) Analyzer (mg/l) Free: 2.07 2.12 Time: 12:33 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.49 1.48 Total: 1.70 Verified analyzers with grabs all ok. Checked site and trends. Chlorinator 1 still OOS. No outstanding alarms on site. Entered info into PWQ sheet. | Ballantrae Well 3 | 2026-02-04
EAST | February | Scratch last entry it was meant for MTW1/2. | Ballantrae Well 3 | 2026-02-04
EAST | February | On site for station check and to collect weekly micro samples (W11620016). Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 1.97mg/l FCL Analyzer: 1.98mg/l 12:35hrs: High Lift Effluent Free Cl2 grab residual: 1.79mg/l FCL Analyzer: 1.83mg/l Effluent Total Cl2 grab residual: 1.97mg/l Well 5 collected @ 12:20hrs. Well 6 collected @ 12:17hrs. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Stouffville Reservoir and Wells 5 & 6 | 2026-02-25
EAST | February | On site for station check. Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 1.87mg/l FCL Analyzer: 1.90mg/l 09:05hrs: High Lift Effluent Free Cl2 grab residual: 1.77mg/l FCL Analyzer: 1.76mg/l Effluent Total Cl2 grab residual: 1.96mg/l Changed Influent Discharge from West Cell to East Cell and Sample pumps. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None | Stouffville Reservoir and Wells 5 & 6 | 2026-02-23
EAST | February | On site for station check. Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 1.93mg/l FCL Analyzer: 1.94mg/l 09:05hrs: High Lift Effluent Free Cl2 grab residual: 1.87mg/l FCL Analyzer: 1.79mg/l Effluent Total Cl2 grab residual: 1.97mg/l Tested Cl2 leak alarm. No issues. Switched High Lift Pump duties: P1 to D1, P2 to D2. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None | Stouffville Reservoir and Wells 5 & 6 | 2026-02-26
EAST | February | On site for station check and to collect weekly micro samples (W11605521). Well 5 collected @ 12:20hrs. Well 6 collected @ 12:15hrs. Had to leave site to respond to low CL2 at Bethesda Tower. | Stouffville Reservoir and Wells 5 & 6 | 2026-02-17
EAST | February | Conducted monthly maintenance: 12:20hrs: Cleaned Influent HACH CL17 Analyzer, Verified Analyzers after cleaning @12:45hrs: Influent FCL grab residual: 1.76mg/l, Analyzer: 1.65mg/l Adjusted CL2 Analyzer from 1.65mg/l to 1.76mg/l based on multiple Cl2 grab residuals. Chlorine Cylinder repair kit inspection. Chlorine Scrubber inspection | Stouffville Reservoir and Wells 5 & 6 | 2026-02-18
EAST | February | On site for station check and to collect weekly micro samples (W11605521). Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 1.97mg/l FCL Analyzer: 1.98mg/l 13:30hrs: High Lift Effluent Free Cl2 grab residual: 1.82mg/l FCL Analyzer: 1.82mg/l Effluent Total Cl2 grab residual: 1.91mg/l Well 5 collected @ 12:20hrs. Well 6 collected @ 12:15hrs. Switched reservoir influent cell from EAST to WEST and sample pump suction line. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Stouffville Reservoir and Wells 5 & 6 | 2026-02-17
EAST | February | Repair leak high lift pump 2 Back in auto | Stouffville Reservoir and Wells 5 & 6 | 2026-02-10
EAST | February | On site for station check. Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 1.90mg/l FCL Analyzer: 1.94mg/l 08:15hrs: High Lift Effluent Free Cl2 grab residual: 1.82mg/l FCL Analyzer: 1.82mg/l Effluent Total Cl2 grab residual: 1.95mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None | Stouffville Reservoir and Wells 5 & 6 | 2026-02-13
EAST | February | On site for station check. Travis Wyatt on site for Chlorine Cylinder change. Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 1.78mg/l FCL Analyzer: 1.80mg/l 09:45hrs: High Lift Effluent Free Cl2 grab residual: 1.77mg/l FCL Analyzer: 1.75mg/l Effluent Total Cl2 grab residual: 1.87mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None | Stouffville Reservoir and Wells 5 & 6 | 2026-02-20
EAST | February | On site for station check and to collect weekly micro samples (W11588680). Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 2.00mg/l FCL Analyzer: 2.04mg/l 08:45hrs: High Lift Effluent Free Cl2 grab residual: 1.85mg/l FCL Analyzer: 1.84mg/l Effluent Total Cl2 grab residual: 1.99mg/l Well 5 collected @ 08:30hrs. Well 6 collected @ 08:25hrs. Switched duties on High lift Pumps: P1 to D2, P2 to D1. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Stouffville Reservoir and Wells 5 & 6 | 2026-02-11
EAST | February | Acknowledged and reset a High Lift P1 failed to stop alarm on Duty Stop. On Scada, pump had actually stopped but may have took longer than normal to stop when the command was given. Will need to investigate further as to why pump is stopping slightly longer than it should. | Stouffville Reservoir and Wells 5 & 6 | 2026-02-06
EAST | February | Conducted monthly maintenance: 09:35hrs: Cleaned HACH CL17 High Lift Effluent Analyzer, Verified Analyzers after cleaning @09:50hrs: Effluent FCL grab residual: 1.77mg/l. Analyzer: 1.75mg/l. Changed Effluent HACH Cl17 Analyzer reagents. Changed Influent HACH Cl17 Analyzer reagents. Conducted Generator Test Run (09:24hrs): Diesel Generator Run Monthly Test: Start Runtime: 09:24hrs (Run hrs: 14.25hrs) Fuel Start: 3107L Stop Runtime: 10:30hrs (Run hrs: 15.35hrs ) Fuel Stop: 3091L Generator Performance Data recorded below: Battery Cell Levels: OK Battery Terminals/Cables: Ok Oil and Coolant: Ok Amps: 50amps Volts: 596 Hertz: 61 RPM: 1800 Oil Pressure: 37psi Water temp: 170F No issues during generator run test. Ran HLP2 during run test. Turbidimeter maintenance and calibration completed. Conducted chemical system inspection. Housekeeping. | Stouffville Reservoir and Wells 5 & 6 | 2026-02-19
EAST | February | On site for station check. Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 1.88mg/l FCL Analyzer: 1.89mg/l 12:30hrs: High Lift Effluent Free Cl2 grab residual: 1.83mg/l FCL Analyzer: 1.82mg/l Effluent Total Cl2 grab residual: 1.95mg/l Changed Reservoir inlet from West to East and Sampling pumps. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: High Lift P1 offline for flow control valve repair. | Stouffville Reservoir and Wells 5 & 6 | 2026-02-09
EAST | February | On site for station check. Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 1.79mg/l FCL Analyzer: 1.78mg/l 09:40hrs: High Lift Effluent Free Cl2 grab residual: 1.81mg/l FCL Analyzer: 1.81mg/l Effluent Total Cl2 grab residual: 1.95mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Stouffville Reservoir and Wells 5 & 6 | 2026-02-06
EAST | February | On site for station check and to collect weekly micro samples (W11568302). Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 2.03mg/l FCL Analyzer: 2.10mg/l 12:50hrs: High Lift Effluent Free Cl2 grab residual: 1.91mg/l FCL Analyzer: 1.92mg/l Effluent Total Cl2 grab residual: 2.04mg/l Well 5 collected @ 12:26hrs. Well 6 collected @ 12:18hrs. Adjusted Target influent from 2.10mg/l to 2.00mg/l. Changed Influent feed from East to West and Sampling Pump feed. Collected RAW Water PH @12:57hrs: Well 5: 7.45 Well 6: 7.43 Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Stouffville Reservoir and Wells 5 & 6 | 2026-02-04
EAST | February | On site for Cl2 Cylinder change with Travis Wyatt. | Stouffville Reservoir and Wells 5 & 6 | 2026-02-05
EAST | February | On site for station check. 09:35hrs: Verified FCL Cl2 Analyzer: FCL grab residual: 1.80mg/l Analyzer: 1.81mg/l TCL grab residual: 1.95mg/l Verified HACH Cl17 Analyzer and checked site and equipment. All readings in PWQ sheet. Equipment out of service: No | Stouffville Highway 48 Booster Pumping Station | 2026-02-23
EAST | February | On site for station check. 10:10hrs: Verified FCL Cl2 Analyzer: FCL grab residual: 1.70mg/l Analyzer: 1.69mg/l TCL grab residual: 1.85mg/l Verified HACH Cl17 Analyzer and checked site and equipment. All readings in PWQ sheet. Equipment out of service: None. | Stouffville Highway 48 Booster Pumping Station | 2026-02-26
EAST | February | Conducted monthly maintenance: 13:40hrs: Cleaned HACH CL17 Analyzer, Verified Analyzers after cleaning @13:50hrs: FCL grab residual: 1.70mg/l. Analyzer: 1.73mg/l. JHSC conducted on site. | Stouffville Highway 48 Booster Pumping Station | 2026-02-19
EAST | February | On site for station check. 10:30hrs: Verified FCL Cl2 Analyzer: FCL grab residual: 1.70mg/l Analyzer: 1.69mg/l TCL grab residual: 1.87mg/l Verified HACH Cl17 Analyzer and checked site and equipment. All readings in PWQ sheet. Equipment out of service: None. | Stouffville Highway 48 Booster Pumping Station | 2026-02-20
EAST | February | On site for station check. 08:35hrs: Verified FCL Cl2 Analyzer: FCL grab residual: 1.74mg/l Analyzer: 1.71mg/l TCL grab residual: 1.88mg/l Verified HACH Cl17 Analyzer and checked site and equipment. All readings in PWQ sheet. Equipment out of service: None. | Stouffville Highway 48 Booster Pumping Station | 2026-02-13
EAST | February | On site for station check. 14:00hrs: Verified FCL Cl2 Analyzer: FCL grab residual: 1.53mg/l Analyzer: 1.57mg/l TCL grab residual: 1.65mg/l Changed HACH CL17 Analyzer reagents. Verified HACH Cl17 Analyzer and checked site and equipment. All readings in PWQ sheet. Equipment out of service: None. | Stouffville Highway 48 Booster Pumping Station | 2026-02-17
EAST | February | On site for station check. 13:30hrs: Verified FCL Cl2 Analyzer: FCL grab residual: 1.59mg/l Analyzer: 1.62mg/l TCL grab residual: 1.72mg/l Verified HACH Cl17 Analyzer and checked site and equipment. All readings in PWQ sheet. Equipment out of service: None. | Stouffville Highway 48 Booster Pumping Station | 2026-02-04
EAST | February | On site for station check. 10:20hrs: Verified FCL Cl2 Analyzer: FCL grab residual: 1.79mg/l Analyzer: 1.77mg/l TCL grab residual: 1.91mg/l Verified HACH Cl17 Analyzer and checked site and equipment. All readings in PWQ sheet. Equipment out of service: None. | Stouffville Highway 48 Booster Pumping Station | 2026-02-06
EAST | February | On site for station check. 13:05hrs: Verified FCL Cl2 Analyzer: FCL grab residual: 1.82mg/l Analyzer: 1.82mg/l TCL grab residual: 1.90mg/l Ran air compressor to regulate pressure tank levels. Verified HACH Cl17 Analyzer and checked site and equipment. All readings in PWQ sheet. Equipment out of service: None. | Stouffville Highway 48 Booster Pumping Station | 2026-02-09
WEST | February | On site for station check. Site offline. Doors locked. | King City Wells 3 & 4 | 2026-02-13
WEST | February | On site for station check. Site offline. Doors locked. | King City Wells 3 & 4 | 2026-02-20
WEST | February | On site for station check. Site offline. Doors locked. W11574343- JHSC inspection complete. | King City Wells 3 & 4 | 2026-02-06
WEST | February | On site for station check and micro sampling W11620283 Check Trends- All okay Ran Well 3 and 4 in local 11:20-Verified Treated Free & Total Analyzer Free cl2 Grab- 0.01 mg/L, Analyzer - 0.01 mg/L Total Cl2 Grab- 1.85 mg/L, Analyzer - 1.89 mg/L 11:16-Verified Effluent Free Analyzer Free cl2 Grab- 0.04 mg/L, Analyzer - 0.04 mg/L 11:16-Verified Influent Free Analyzer Free cl2 Grab- 0.02 mg/L, Analyzer - 0.07 mg/L Topped up KI reagent. Entered Values in PWQ sheet Samples taken stopped wells Equipment oaky. | Kleinburg Wells 3 and 4 | 2026-02-25
WEST | February | On site for station check and micro sampling W11605699 Check Trends- All okay Ran Well 3 and 4 in local 13:44-Verified Treated Free & Total Analyzer Free cl2 Grab- 0.03 mg/L, Analyzer - 0.01 mg/L Total Cl2 Grab- 1.96 mg/L, Analyzer - 1.98 mg/L 13:48-Verified Effluent Free Analyzer Free cl2 Grab- 0.03 mg/L, Analyzer - 0.04 mg/L 13:48-Verified Influent Free Analyzer Free cl2 Grab- 0.03 mg/L, Analyzer - 0.06 mg/L Topped up Acetate. Entered Values in PWQ sheet Samples taken stopped wells Equipment oaky. | Kleinburg Wells 3 and 4 | 2026-02-17
WEST | February | On site for station check and to collect bacti sample W11605699 ran wells to waste - distribution valve locked out. Checked residuals Total Analyzer 1.99mg/L Grab 1.95mg/L Free Analyzer 0.01mg/L Grab 0.03mg/L Reagents all okay Wells back offline after sampling No known issues | Kleinburg Wells 3 and 4 | 2026-02-11
WEST | February | Ran well 3 and 4 locally to collect raw water resampling 11:30- collected samples | Kleinburg Wells 3 and 4 | 2026-02-13
WEST | February | On site for station check and micro sampling W11568550 Check Trends- All okay Ran Well 3 and 4 in local 11:15-Verified Treated Free & Total Analyzer Free cl2 Grab- 0.03 mg/L, Analyzer - 0.01 mg/L Total Cl2 Grab- 2.01 mg/L, Analyzer - 2.00 mg/L 13:58-Verified Effluent Free Analyzer Free cl2 Grab- 0.05 mg/L, Analyzer - 0.04 mg/L 10:55-Verified Inffluent Free Analyzer Free cl2 Grab- 0.04 mg/L, Analyzer - 0.06 mg/L Reagents All good Entered Values in PWQ sheet Samples taken stopped wells Equipment oaky. | Kleinburg Wells 3 and 4 | 2026-02-04
WEST | February | Onsite for the following PM Work orders. Informed ROC about the works being done. W11562248 KLW34, Diesel Generator Test Run Pre check Battery okay- 26.5V Coolant- Okay Oil - Okay Before Start Start time- 10:00 Run time- 416.1 hr Fuel level-1987L/38.5cm KLPSWL pump 4 running Local. After Stop Stop time- 11:14 Run time- 417.3 hr Fuel level-1953L/37.8 cm W11562437-Chlorine Analyzer, Maintenance 13:50-Verified Treated Free & Total Analyzer Free cl2 Grab- 0.02 mg/L, Analyzer - 0.04 mg/L Total Cl2 Grab- 2.07 mg/L, Analyzer - 2.07 mg/L 13:53-Verified Effluent Free Analyzer Free cl2 Grab- 0.05 mg/L, Analyzer - 0.04 mg/L 13:55-Verified Inffluent Free Analyzer Free cl2 Grab- 0.02 mg/L, Analyzer - 0.06 mg/L W11562403-Turbidimeter Maintenance- Display not showing any options after vail cleaning and verification. Value still in hold output mode. CMU created-W11634370 W11562289-Pressure Relief Valve, Inspection W11563441- Ammonia System, Inspection W11563465-Deep Well Exhaust Valve, Maintenance W11563510- Chlorine Leak Detector, Test W11562826-JHSC Health and Safety Inspection W11564230-Chemical System Inspection - Chlorine W11564270- Chemical System Inspection - Silicate W11563405- Ventilation System - Exhaust Fans W11563325- Chlorine Scrubber, Check W11563395-Chlorine Cylinder Emergency Repair Kit Inspection | Kleinburg Wells 3 and 4 | 2026-02-03
WEST | February | Attending site to check Turbidimeter screen issue (W11634370). Cycled power on transmitter and device rebooted normally. ROC was notified before and after maintenance activities. | Kleinburg Wells 3 and 4 | 2026-02-06
WEST | February | Trends checked and ok, equipment checked and ok All measurement are in mg/l Tower draining Common inlet/outlet - time : 11:35 Free 0.05 Total grab 3.49 vs analyzer 3.52 Mono 2.90 Post injection - time : 11:42 Free 0.04 Total grab 4.08 vs analyzer 4.14 | Schomberg Elevated Tank | 2026-02-23
WEST | February | Onsite for station check Tower filling Post inj @1106 Total analyzer 3.67 grab 3.72 Free grab 0.00 Deactivated duty Pre inj @1128 Total analyzer 3.54 grab 3.56 Free grab 0.04 Mcl grab 3.00 Topped up hypo tank | Schomberg Elevated Tank | 2026-02-27
WEST | February | Onsite for station check Tower draining Checked residuals mg/l Common @1047 Total grab 3.44 grab 3.36 Free grab 0.03 Post inj @1051 Total analyzer 3.25 grab 3.10 Free grab 0.06 Reagents ok | Schomberg Elevated Tank | 2026-02-02
WEST | February | Attending site to replace failed hypo pump#2 (W11497370). Replaced pump and corroded connection cables. Primed pump and adjusted valves so it is ready to run from SCADA, if needed. Operations were notified so that they can test the pump next time they are on site. A spare pump will be available from the inventory at 145 HWP. ROC was notified before and after maintenance activities. | Schomberg Elevated Tank | 2026-02-10
WEST | February | Equipment checked and ok, trends checked and ok Tower draining Common inlet time: 11:45 Free grab 0.04 Total grab 3.60 vs analyzer 3.62 Mono 2.94 Bact Sample grabbed time 12:16 Post injection time 12:10 Free grab 0.06 Total grab 4.28 vs analyzer 4.22 | Schomberg Elevated Tank | 2026-02-25
WEST | February | Tower filling Trends checked and ok, equipment checked and ok All readings are in mg/l Common inlet/outlet -time 11:35 Free grab 0.08 Total grab 3.10 vs analyzer 3.16 Mono 2.74 Post injection- time: 11:50 Free grab 0.10 Total grab 3.81 vs analyzer 3.78 | Schomberg Elevated Tank | 2026-02-20
WEST | February | Onsite for station check and to collect weekly micro W11605647 Tower filling Post inj @1136 Total analyzer 3.69 grab 3.60 Free grab 0.02 Deactivated duty Pre inj @1153 Total analyzer 3.54 grab 3.52 Free grab 0.03 Mcl grab 2.98 Changed reagents in post injection analyzer | Schomberg Elevated Tank | 2026-02-17
WEST | February | Onsite for station check Tower draining Checked residuals mg/l Common / pre @0953 Total analyzer 3.54 grab 3.46 Free grab 0.09 Mcl grab 2.90 Post inj @1006 Total analyzer 4.33 grab 4.26 | Schomberg Elevated Tank | 2026-02-13
WEST | February | Onsite to complete work orders Cleaned cl17sc analyzers grabs before @1200 Post inj Total analyzer 3.38 grab 3.10 Free grab 0.04 @1206 Common Total analyzer 3.29 grab 3.02 Free grab 0.06 Completed monthly generator run Completed jhsc Change reagents in common cl17sc Closed common inlet to work in hypo injection point feed system through bypass, resulting in loss of flow to analyzer Compliance alarm came in @1407 Common Grab Total grab 3.26 Free grab 0.03 Opened valve back to normal operation @ 1418 Cleaned common inlet analyzer again @1423 High spike came in due to adjusting flow and maintenance Checked residuals mg/l @1454 Common Total analyzer 3.32 grab 3.28 Free grab 0.01 Started high lift to get flow to post inj Grabs @1516 Total analyzer 3.44 grab 3.30 Hypo pump 2 drawdown 150 ml/min Hypo pump 1 drawdown 140 ml/min Topped up hypo tank | Schomberg Elevated Tank | 2026-02-12
WEST | February | Onsite for station check and to collect weekly micro sample W11588872 Tower filling Checked residuals mg/l @1112 Post inj Total analyzer 3.60 grab 3.70 Free grab 0.06 Deactivated hl duty Common/ Pre inj @1128 Total analyzer 3.36 grab 3.28 Free grab 0.05 | Schomberg Elevated Tank | 2026-02-11
WEST | February | Attending site to check display on Hypo Tank Level (W11621184). Cycled power to display and it booted up normally. ROC was notified before and after maintenance activities. | Schomberg Elevated Tank | 2026-02-03
WEST | February | Tower draining Equipment checked and ok, trends checked and ok Common inlet/ outlet Time 1:21 pm Free: grab 0.08 Total: grab 3.42 vs analyzer 3.44 Mono 2.93 Post injection Time 1:27 pm Free: grab 0.09 Total: grab 4.40 vs 4.50 | Schomberg Elevated Tank | 2026-02-09
WEST | February | Onsite for station check and to collect weekly micro sample W11568498 Tower draining Checked residuals mg/l Common @1143 Total analyzer 3.51 grab 3.54 Free grab 0.06 Mcl grab 2.97 Post inj @ 1151 Total analyzer 4.31 grab 4.00 Free grab 0.13 | Schomberg Elevated Tank | 2026-02-04
WEST | February | Tower draining Equipment inspected ok, trends ok Post injection free 0.09, total 3.03 vs analyzer 3.05 - 11:15 am Pre injection free 0.08, total 3.51 vs analyzer 3.46 Monochloramine 3.03 - 11:25 am | Schomberg Elevated Tank | 2026-02-06
EAST | February | ROC informed of train 3, 6 shut down. Backpulse flow lolo and pumps OOS. Reviewed SCADA, noticed the backpulse fill valves are man/off. Placed them to auto and Tank 2 valve is in duty 1. Ack+Reset alarms, initiated train 3 and train 6 backwash. Initiated rest of trains' backwashes to stagger recovery percentage. Changed the backwash tank fill rate from 65 l/s to 75 l/s. Enabled backup power selection for all types of cleans. Changed Train 1 and 2 permeate pumps' VFD speed from 65% to 60%. All trains are available and plant is under normal operation. | Georgina Water Treatment Plant | 2026-02-24
EAST | February | On site to respond to High Lift CL2 free analyzer HIHI alarm. Was reading in excess of 3.20mg/l. Collected CL2 grab residual @ 14:25hrs: 1.57mg/l. Zero calibrated the CL2 Analyzer and Cal spanned the analyzer to reflect Cl grab residual values. | Georgina Water Treatment Plant | 2026-02-27
EAST | February | ROC called about hi lift header FCL hi alarm logged in remotely, duty active and tower level at 55% and filling. @ 1710 hrs: Hi lift header 2.66 mg/l with hi hi alarm active. keswick header -FCL= 1.59 mg/l Sutton header - FCL= 1.57 mg/l Contact tanks and clear-wells residuals are trending normal No chlorine issues based on trends 1910 hrs: Hi lift header analyzer still trending upward (2.87 mg/l) but analyzer downstream and upstream all reading normal, changes. Directed ROC to ignore Hi lift header reading for the night and will be attended to tomorrow morning, if ROC notice any changes in chlorine analyzers at the clearwells or contact tanks to notify me right away. Also, train 5 experiencing TMP issues, reduced HL flow from 200 down to 190 l/s | Georgina Water Treatment Plant | 2026-02-26
EAST | February | Onsite for station check and lab analysis, entered data into PWQ sheets. Reviewed MIT and daily filter performance on all membrane trains - all passed and within range - recorded data in PWQ sheets. 11:00 - Adjusted high lift pump duty to duty 1 - P3, duty 2 - P1, duty 3 - P2. | Georgina Water Treatment Plant | 2026-02-26
EAST | February | Change out 24 inch butterflyUV south line Filled and ready to be put back in service | Georgina Water Treatment Plant | 2026-02-24
EAST | February | On site for UV maintenance support for CMS UV1 and UV2 manual off, BKPL_TK_PV3, BKPL_TK1_PV1, BKPL_TK2_PV1 manual closed, Train 7 and Train 8 OFF, 9:50 Initiated backpulse on Train 1, 9:53 UV1 and UV2 influent and effluent valves manual closed, 10:01 Initiated backpulse on Train 2, requested Central Water run KSTP to support UV maintenance on site at GWTP. KSTP high lift pump 3 placed manual on by Jerry Zhang, 10:02 BKPL_TK2_PV1 backpulse tank fill valve manual open, closed handwheel valve to UV2, 10:06, to drain the permeate header Permeate header drained. Electrician Dan Boate cut power to UV2 influent and effluent valves. Operator - UV2 effluent valve local closed, locked and tagged out. Operator - UV2 local off, locked and tagged out. Remote Operator Carter Dunn informed of work and directed to disregard alarms, 10:35 Primed permeate header and UV2 line after UV2 MV1 valve was replaced. Electrician, Dan Boate, powered the influent and effluent UV valves and Operators removed the locked on the UV2 effluent valve and UV2 breaker. Reset train turbidity faults after priming permeate header. Placed all equipment back to auto, placed Trains 1-8 ON. High common permeate turbidity, 15:00 and 15:22, shut down trains, flushed line and reset. High common permeate turbidity and Trains 5-8 in shutdown on high turbidity, 15:52. Initiated backpulse on Train 8. Remained on site for supervised start up. | Georgina Water Treatment Plant | 2026-02-24
EAST | February | Informed ROC. Onsite to perform annual calibration at low lift GWTP building. Calibration mode was used during the work. All the PITs and LITs completed. Put everything back in service. All the related alarms were cleared. No issues . Informed ROC, armed the building and left the site. | Georgina Water Treatment Plant | 2026-02-27
EAST | February | Attended site and completed MIT and membrane performance review - all good. Recorded observations in the shared PWQ sheet | Georgina Water Treatment Plant | 2026-02-23
EAST | February | Verified CT & CW, Keswick Header, and Sutton Header analyzers. Entered data into PWQ sheets. Adjusted Keswick header free analyzer with the average of three grab samples. Adjusted Post Clear well free chlorine analyzer with the average of three grab samples. | Georgina Water Treatment Plant | 2026-02-25
EAST | February | On site for preventative maintenance work orders Completed MIT review and membrane performance review - all okay Chlorine analyzer maintenance sed tanks to lake Low lift pump and motor inspection PSW line injection point maintenance Treated header chlorine analyzer maintenance Chlorine scrubber check Low lift housekeeping Membrane and permeate room housekeeping Chlorine system overhaul - inspected Station and equipment okay | Georgina Water Treatment Plant | 2026-02-26
EAST | February | Inspected low lift pump 3 flow control valve. Replaced O-rings on indicator shaft. No other issues to report, unit can return to service. | Georgina Water Treatment Plant | 2026-02-23
EAST | February | On site for station check and sampling work orders W11620072, 9:00 Sutton header turbidity fault - found analyzer in low flow state, increased sample flow from 0.25L/min to 0.5L/min and cleared alarm, 9:30 UV1 reactor minor fault, UV reactor 1 lamp #1-1 lo UV irradiance - UV dosage 32.75 mJ/cm2 and UV intensity 17% okay. Will investigate lamp 1-1 when the plant is off, 9:58 Completed MIT and filter performance review and log, 10:31 Completed lab and station rounds and recorded observations in the shared lab sheet and PWQ sheet, 12:15 Collected raw and treated micro samples, W11620072 Raw water sample collected at 11:20 Treated water sample collected at 12:10 Treated FCl 2.13 mg/L; Treated TCl 2.26 mg/L Completed low lift inspection, 13:30 UV Reactor 3-1 lo UV irradiance - PERM_SV2 and SV3 valves were left manual open from last night. Must leave these valves manual open until the plant shuts off to ensure the plant doesn't lock out from a false turbidity spike while KSETDP fills, 14:30. Station and equipment okay, Jackie Saunders and Patrick Fobert on site | Georgina Water Treatment Plant | 2026-02-25
EAST | February | Completed MIT review and membrane performance check - all okay | Georgina Water Treatment Plant | 2026-02-27
EAST | February | ZW6 permeate turbidity fault, turbidity out of range - directed RO Carter to place OFF and reduced plant setpoint to 180 L/s | Georgina Water Treatment Plant | 2026-02-01
EAST | February | On site for station check, lab analysis and equipment verifications Reviewed MIT and daily filter performance on all membrane trains - Train #2 MIT had failed overnight, will troubleshoot. All other trains passed MIT and filter performance is within range - Recorded data in PWQ sheets Jack P addressed train #6 turbidity fault from over the weekend. Cleaned vial and cleared alarms. Train back in service Initiated MIT on train #2 @09:48 - MIT passed: High: 6.12 kpa / Low: 4.49 kpa Placed train #2 back in service @10:27 Train #4 Air inlet valve failed to close @13:22. Second time this has occurred today. Adjusted the speed setpoint on the aeration valve, will monitor. Placed train back in service. Completed in-house lab analysis on Raw and treated waters Verified analyzer readings - Contact tanks, clearwells, treated, residual management. Made the following adjustments: - Post clearwell adjusted from 1.70 to 1.87 mg/L based on multiple grabs Completed lab reagents, inventory and replace WO Reviewed trends, equipment OOS: Sludge P3, Bisulfite P2 Station ok | Georgina Water Treatment Plant | 2026-02-02
EAST | February | Initiated MIT on train #6 @07:49 - it was left off for the weekend due to NTU fault. | Georgina Water Treatment Plant | 2026-02-02
EAST | February | On site for station check and lab Cleaned train 6 turbidimeter and cleared bubbles in cuvette, cleared turbidity fault alarm, and returned to service 9:00 Rotated air compressor duty - Kaiser in lead, 11:20 Rotated raw water sample pump duty, P2 to duty 3, P1 to duty 1, 11:21 Rotated post-chlorination and clearwell ejector solenoid valves - valve 2 OFF, valve 1 to duty 1, 11:23 Rotated backpulse fill valve from tank 2 to tank 1, 11:26 Chris Iliohan completed work strapping down the clearwell backpulse line and BKPL_TK_PV3 was cycled for testing, 11:38. BKPL_TK_PV3 placed back to auto after backpulse tank level of 1.76 M achieved. AER_FMB4_PV1B failed to close (11:57) reset and initiated M-clean, will monitor AER_FMB_P1VB failed to close (14:10) - adjusted speed to open and speed to close, attempted to seat. Monitoring. Completed station rounds and lab, 14:11 Station and equipment okay | Georgina Water Treatment Plant | 2026-02-02
EAST | February | Reviewed monthly and daily filter performance criteria. All values within range. | Georgina Water Treatment Plant | 2026-02-02
EAST | February | Chris Iliohan Tyler Smith in to add pipe support To back pulse piping also adjusted opening speed on supply valve . Check operation couple time no further pipe movement | Georgina Water Treatment Plant | 2026-02-02
EAST | February | On site for station check and sampling work orders, W11588736 Collected GLIP and Bac-T micro samples, 11:46 Treated chlorine residuals, in mg/L FCl 1.95 TCl 2.23 Completed lab Completed JHSC inspection Completed SBS pump inspection Completed low lift housekeeping Verified fluoride, clearwell, contact tank and Keswick treated and Sutton treated chlorine analyzers. Recorded observations in the shared PWQ sheet. Treated chlorine analyzers, grab/analyzer, mg/L Keswick: FCl: 1.81/1.78, TCl: 2.07/2.13 Sutton: FCl: 1.85/1.87, TCl: 2.07/2.18 Station and equipment okay | Georgina Water Treatment Plant | 2026-02-17
EAST | February | On site for preventative maintenance work orders Placed GLIP samples out for pickup Completed 2 ton and 5 ton crane inspections, high lift crane, membrane crane and chlorine tonner crane Completed wash water and sludge transfer pump inspection and rotation. Rotated sludge transfer pump duty to: P1 in duty for tank 2, Pump 3 in duty for tank 1, Pump 2 OFF Wash water transfer pump 3 still OOS for maintenance - currently isolated. Wash water transfer pump 1 in duty for tank 1, P2 in duty for tank 2, P3 OFF Completed SO2 emergency repair kit inspection Station and equipment okay | Georgina Water Treatment Plant | 2026-02-12
EAST | February | On site for station check, equipment verifications, and weekly micro sampling (W11588736) Reviewed MIT and daily filter performance on all membrane trains - all passed and within range - recorded values in PWQ sheets, no issues observed. Manual backwash on GAC #1: - Placed filter OOS and began draining to clearwell through filter effluent valve @08:15 - Filter drained to 3.01 m @08:35, and started backwash sequence in manual - @09:06 - Stopped backwash pump, allowing filter to rest for 10 minutes - @09:17 - Started filter to waste, by opening inlet valve and FTW valve UV 2 has started with one train to fill the GAC inlet channel. Placed trains 3, 4 and 8 to demand override to fill channel, backwash clearwell and allow for filter to waste. Disabled the demand overrides @10:17 - UV dosage high and UV intensity low alarms - Alarms are due to lower than normal flow through the UVs, okay to disregard - Closed BKWS_MV1 backwash clearwell fill valve @09:55, level is 4.93 m, will finish filling later Activated Duty 1 @09:58 - KSTKWP Level - 58% - Stopped GAC 1 filter to waste @10:25 - Placed GAC 1 back in service - NTU is 0.239 - Completed PWQ sheets plant rounds and data collection, chemical dosage verifications Operations and Adjustments - Duty rotated air compressors - placed KAESER compressor in lead duty - Deactivated Zebra mussel control chlorination @14:03 - Increased Clearwell dosage factors by 2% each: Chlorinator #5 50 to 52%, Chlorinator #6 51 to 53% - Made minor adjustment to clearwell chlorination diffusers, in order to better balance the clearwell chlorine residuals Reviewed trends, Equipment OOS: Sludge Pump #3, Low lift pump #3 Station ok | Georgina Water Treatment Plant | 2026-02-17
EAST | February | Initiated Hypo Recovery clean on train #8 @09:22 Collected grab sample from train #8 hypo R-clean @12:50 - 440 mg/L cl2, pH = 10.01 Troubleshooted with train #2 MIT fail overnight and with the TMP alarms that have came in this afternoon. - Manually added pressure to the low side of train #2 to test for leaks @13:28 - Observed leaking camlock fittings on cassette F - Replaced gaskets and re-installed. - Manually added pressure to low side again to test membranes after gasket replacement. - Placed train #2 back in service @14:14 Collected grab sample from train #8 hypo R-clean @15:05 - 430 mg/L cl2, pH = 9.96 | Georgina Water Treatment Plant | 2026-02-11
EAST | February | On site for station check. Reviewed MIT and daily filter performance on all membrane trains - all passed and within range - recorded data in PWQ sheets. Reviewed trends in lieu of performing full station check, recorded data in PWQ sheets. Trends for filters, and treated headers OK. Station OK. | Georgina Water Treatment Plant | 2026-02-20
EAST | February | On site for monthly maintenance - informed ROC of work to be completed - Reviewed MIT and daily filter performance on all membrane trains - All passed and within range - recorded readings in PWQ sheets - Completed UV system cleaning on UVs 1 and 2 - UV sensor calibration - Completed UV 1 from 11:00 to 11:35. Completed UV 2 from 14:00 to 14:30. Placed both UVs back to auto - UVT analyzer dehumidifier element change out - Activated Keswick system duty @14:43, and activated Sutton duty @15:07 | Georgina Water Treatment Plant | 2026-02-12
EAST | February | On site for station check and sampling work orders GLIP sampling, raw water, W11588975 Operational sampling, raw water algae monitoring, W11568744 Micro sampling, raw and treated water, W11605577 Train 2 low pressure MIT failure - placed Train 2 OFF and initiated MIT, 8:32 Train 7 Recirc inlet V failed to close alarm - reset recirculation valve alarm, 8:37 Train 7 neutralization exceeded dur alarm - verified neutralization with a grab sample, pH 7.35. Returned to service, ON, 8:44 Train 7 recirculation valve not closing when commanded in manual. Train 7 OFF, 8:50 Train 7 recirculation valve - adjusted the limit and cycled the valve in manual, returned to auto, cleared alarm and placed back into service. Train 7 ON, 9:10 Train 7 MIT initiated, 9:10 Initiated Train 8 hypo R clean and activated Keswick duty 1, 9:23 Train 2 ON, 9:30 Collected raw and treated water samples, 10:05 Treated water chlorine residuals: FCl 1.98, TCl 2.08 mg/L Completed MIT and daily filter performance review - all passed, 10:22 Verified Treated water chlorine analyzers, grab/analyzer, in mg/L Keswick FCl, 10:44, 1.65/1.52 - adjusted to match average of grabs Keswick TCl, 10:44, 1.95/1.93 Sutton FCl, 10:50, 1.69/1.80 - adjusted to match average of grabs Sutton TCl, 10:50, 1.97/2.06 - adjusted to match average of grabs Verified treated water fluoride analyzers, grab/analyzer, in mg/L Keswick, 10:49, 0.768/0.65 - increased offset from 0.00 to 0.10 Sutton, 10:49, 0.81/0.59 - increased offset from 0.01 to 0.14 Recorded observations in the station shared PWQ sheet and lab sheet Station and equipment okay | Georgina Water Treatment Plant | 2026-02-11
EAST | February | Reviewed MIT and daily filter performance on all membrane trains - all passed and within range - recorded data in PWQ sheets @09:40 - activated system duty | Georgina Water Treatment Plant | 2026-02-16
EAST | February | Train #8 shutdown on Hihi turbidity @08:07 - first run cycle after recovery clean. Reviewed trends, turbidity back to normal levels. Placed train to backwash and back in service | Georgina Water Treatment Plant | 2026-02-12
EAST | February | ROC called regarding MIT fail on Train 2. Directed ROC to leave Train 2 in off position for the night. Directed ROC to deactivate duty since tower was almost full. | Georgina Water Treatment Plant | 2026-02-11
EAST | February | Reviewed MIT and daily filter performance on all membrane trains - all passed and within range - recorded data in PWQ sheets Deactivated system duty @10:00 - Informed ROC that we would be performing maintenance on turbidity analyzers for Trains, GACs, Treated - Train / Permeate header turbidity analyzer maintenance from 10:00 to 11:15 - GAC 1-4 analyzer maintenance from 11:15 to 12:00 - Treated turbidity analyzer maintenance from 13:00 to 13:30 Manual backwash on GAC #3: Placed GAC 3 OOS on the setpoints page - @12:25 Closed Inlet valve, and opened effluent valve to drain GAC to clearwell - @13:07 Started backwash pump 2 - @13:34 Backwash is complete, allowing filter to rest - Started Filter to waste @13:48, by opening inlet valve, and filter to waste valve. UV had started to fill the GAC inlet channel @13:28 - Causing UV dosage high alarms - Completed housekeeping of common areas - Wash water transfer pump maintenance and duty rotation Activated system duty @14:24 - KSTKWP Level - 50% GAC #3 continuing filter to waste - NTU is still elevated. Will inform on call OIC to place GAC back in service around 16:00 Alarms cleared, station ok | Georgina Water Treatment Plant | 2026-02-18
EAST | February | Enabled following SCADA alarms on both UV1 and UV2: UV Transmittance lo, lolo UV Intensity hihi, hi, lo, lolo, OOR | Georgina Water Treatment Plant | 2026-02-11
EAST | February | ROC called regarding Train 7 neutralization exceeded alarm followed by Train 7 Recirc inlet valve failed to close alarm. Logged into Scada, Neutralization did end up completing without any issues. Still an outstanding inlet valve failed to close alarm. Unable to exercise or reset. Train 7 will be offline for the night. No scheduled M-Cleans tomorrow so can leave this Recirc inlet valve in open status for the night. | Georgina Water Treatment Plant | 2026-02-10
EAST | February | Reviewed MIT and daily filter performance on all membrane trains - all passed and within range - recorded data in PWQ sheets. Common Permeate turbidity fault alarm (triggered 06:50) active upon arrival, wiped down vial exterior and cleared alarm. Manual backwash on GAC4: 9:58 - Called ROC to notify of backwash on GAC 4 to be performed. 9:59 - Manual opened backwash clearwell fill valve 10:06 - Placed GAC4 OOS on the setpoints page 10:36 - Common Perm turbidity HIHI alarm, and ZW3 shutdown alarm. Discovered the permeate turbidity vial exterior was wet, wiped down to dry, returned to service, and cleared alarms. 10:38 - Manual closed backwash clearwell fill valve. 10:42 - UV reactor 1 shutdown alarms due to low flow. 10:44 - Changed train three status to off and back on (M-Clean pending) 10:47 - Cleared UV alarms, UV reactor 1 start/stop sequnce fault alarm. UV 1 interlocked. Rotated UV duty to UV reactor 2, to let UV 1 cool down. Monitoring Permeate turbidity while UV 2 runs. 11:33 - Placed GAC4 back in service. Will resume backwash when backwash clearwell can be filled at a later time. Placed UV reactor 1 back in auto. 11:48 - Examined Permeate turbidimeter again - dampness on the interior of the analyzer created turbidity spikes. Wiped down and returned to service. 12:00 - 13:20 Received SBS chemical delivery. 14:00 - 15:00 Completed chlorine analyzer maintenance for Permeate, CIP, Clearwell, CT Tanks, and Post CW analyzers. | Georgina Water Treatment Plant | 2026-02-19
EAST | February | Placed train #8 to Standby @18:45. Recovery clean has been completed | Georgina Water Treatment Plant | 2026-02-11
EAST | February | On site for station checks, lab analysis and data collection Reviewed MIT and daily filter performance on all membrane trains - all passed and within range - recorded data in PWQ sheets @08:42 - Activated system duty - KSTKWP level - 67% Completed PWQ sheets plant rounds and data collection Completed in-house lab for raw and treated waters Verified chlorine analyzer readings with grab residuals - Made the following adjustments to average of 3 grabs Clearwell #2 - Grab: 1.55 / Analyzer: 1.47 mg/L Post clearwell - Grab: 1.44 / Analyzer: 1.61 mg/L Train #7 CIP Cleaning inlet valve failed to open @10:38. Exercised valve and it was very sticky trying to open. Increased open speed setpoint, and it opened. Also adjusted the close limit on the valve. Exercised valve a few times after, and it seems to actuate better. Will monitor @11:10 - Observed that raw water chlorinator #8 was not dosing. Booster pump is running, but the rotameter is at 0 kg/day. Duty rotated to chlorinator #7, and it is dosing normally at 8 kg/day. Reviewed trends Equipment OOS: Low lift pump #3, Sludge pump #3, Chlorinator #8 Station ok | Georgina Water Treatment Plant | 2026-02-13
EAST | February | 15:37 Closed GAC3 filter to waste valve. Placed GAC3 in service. GAC3 turbidity = 0.146 and trending down. | Georgina Water Treatment Plant | 2026-02-18
EAST | February | Activated Duty 1 - KSTKWP level - 57% | Georgina Water Treatment Plant | 2026-02-15
EAST | February | On site for preventative maintenance Completed fluoride probe calibration with a 1.0 mg/L standard, UVs manual off Keswick - 9:41 - reduced offset from 0.12 to 0.01 Sutton - 9:53 - manual closed Sutton PRV for fluoride probe calibration - 9:59 reduced fluoride offset from 0.13 to 0.00 10:28 Sutton PRV returned to auto Completed aeration blower maintenance Completed emergency chlorine repair kit inspection Completed clearwell drain pump inspection Completed clearwell drain valve exercise Completed fluoride pump maintenance - inspection Completed MIT and daily filter performance review and log Station and equipment okay | Georgina Water Treatment Plant | 2026-02-10
EAST | February | On site for monthly PM's - Informed ROC of work to be completed Initiated MIT on train #7 @08:45 - It was left off overnight after recovery clean Reviewed MIT and daily filter performance on all membrane trains - all passed and within range - recorded data in PWQ sheets Initiated acid Recovery clean on train #7 @09:30 Manual closed Sutton PRV @09:53 for fluoride probe calibration. No alarms caused - Triggered containment leak alarms @10:28 - Hypo, Fluoride and SBS Took grab on train #7 Recovery clean acid - pH = 3.19 @10:30 - Triggered chlorine leak alarms @11:15 - Tonner room and Chemical room Took second grab on train #7 acid clean - pH = 2.96 - Sodium hypo pumps inspection - Caustic soda pumps inspection - Sodium bisulfite pumps inspection - High lift FCV Inspections - High lift pump and motor inspections Train #7 remains in R-clean Equipment OOS: Sludge P3, Low lift P3 | Georgina Water Treatment Plant | 2026-02-10
EAST | February | Increased Fluoride P1 dosage factor from 105 to 110 due to low Sutton header alarm while feeding Sutton (0.45mg/l). Keswick header in the 0.50 range. | Georgina Water Treatment Plant | 2026-02-07
EAST | February | ROC called regarding Backpulse Valve failed to close alarm. Directed ROC to ack and reset. Aldso had backpulse tank HIHI alarm, most likely related to this valve not closing fully. Will inform GWTP operator tomorrow. | Georgina Water Treatment Plant | 2026-02-04
EAST | February | Completed MIT and membrane review - all okay | Georgina Water Treatment Plant | 2026-02-03
EAST | February | Completed low lift station check: - Observed leak on Low lift pump 3 Flow control valve - on the rising stem to the limit switch / indicator. Attempted to tighten the top nut on the stem, could not resolve leak. Placed low lift pump 3 to local off OOS, and isolated pump from the discharge header by closing the pump 3 discharge valve. Created WO for maintenance to address. - Pre chlorination system - chlorine system remains active, with the new chlorine analyzers online and linked to SCADA. Isolated old chlorine analyzers from the sample lines, so that flow is now only going through the new analyzers. Will monitor. | Georgina Water Treatment Plant | 2026-02-06
EAST | February | ROC called regarding low fluoride on Sutton Header (0.40mg/l). Keswick header reading 0.52mg/l. Directed ROC to increase dose on P1 (D1) from 1.00 to 1.05. Will monitor. | Georgina Water Treatment Plant | 2026-02-07
EAST | February | On site for monthly maintenance: Informed ROC - Low lift JHSC inspection - Low lift FCV inspections - Low lift turbidity analyzer maintenance - Low lift chlorine analyzer maintenance - Lift chlorine gas detector test: Triggered @10:04. After triggering the alarm, the sensor is stuck at 5.12 ppm, with a fault, OOR and high alarms active. Suspect that the sensor is not working and may need replacement. Will create WO for instrumentation - Received hypo delivery: 1000 L - Troubleshooted train #4 aeration valve B. Train shutdown during backwash @14:14. Observed that the air pressure to the valve was lower than usual. Increased air pressure to the valve from 40 to 60 psi - which is standard to the aeration valves - Troubleshooted train #7 CIP inlet valve - which had failed to open during train #7 M-clean. Had instructed ROC to ack and reset and it reopened it. Made adjustments to close limit on the valve. Will monitor Reviewed trends Equipment OOS: Sludge P3, Bisulfite P2 Disregarding low lift CL2 gas alarms for the night. Work order to be created for instrumentation Station ok | Georgina Water Treatment Plant | 2026-02-03
EAST | February | On site for station check and lab Activated Keswick (KSTKWP) and Georgina (SUETDR) duty 1, 9:05 Fluoride pump 1 running at, 11:25, 60% speed Verified fluoride probes, 11:25, (grab/analyzer), mg/L Keswick: 0.78/0.63 Sutton: 0.71/0.45 - Increased analyzer offset from -0.12 to 0.00 Continuing to monitor to match the analyzers with the average of grabs Rotated from fluoride pump 1 to fluoride pump 2, 11:45 Completed air compressor inspection, 12:30 14:05 - Keswick fluoride in mg/L: grab: 0.85, analyzer: 0.65 - increased offset to 0.12 to match average of grabs 14:05 - Sutton fluoride in mg/L: grab: 0.85, analyzer: 0.61 - increased offset to 0.13 to match average of grabs Completed lab and station rounds, 14:10 Station and equipment okay | Georgina Water Treatment Plant | 2026-02-09
EAST | February | On site for sampling and station check Sampling work orders Algae (raw) W11568573 VOC (raw and treated) W11568102 MBTEB and MBHP (Raw and treated micro sample) W11568372 GEOMIB (raw and treated) W11568573 Mixed citric acid tank and ensured priming tanks were filled and initiated Acid R clean on Train 6, 8:50 Completed MIT and daily filter performance review and log - all okay, 8:51 Low lift chlorine gas detector hi, gas detector hi hi, gas detector OOR alarms outstanding - work order created for Instrumentation Sodium hypo tank level hi hi alarm outstanding from hypo tank top up yesterday, okay to disregard Increased high lift plant flow from 180 to 200 L/s, 11:47 Completed station rounds, sampling, lab, 13:15 Recorded observations in the shared PWQ and station spreadsheets Collected raw and treated samples. Raw sample collected at 9:30. Treated sample collected at 11:40. Treated chlorine grabs as follows: FCl - 2.05 mg/L TCl - 2.36 mg/L Station and equipment okay | Georgina Water Treatment Plant | 2026-02-04
EAST | February | On site for preventative maintenance Received fluoride delivery Tank level start: 0.46 M, stop: 1.25 M Performed two point calibration on Keswick and Sutton fluoride probes. Plant was off, UVs manual off, ROC informed. Verified fluoride probes with the average of grabs and adjusted offset to match. Keswick: 0.38 mg/L, Sutton: 0.38 mg/L, 11:50 Total Power contractor, Jeremy, inspected diesel generator and reproduced the re-occurring overcrank issue. He and Sean Peoples (CMS Electrician) replaced the speed pot and test ran the generator with no issues. Initiated generator test on load. Generator test run Hours Start 514.55 Stop 515.93 Fuel Start 0.73 M Stop 0.68 M Run statistics 60 Hz 600 V 440 kW 325 A Increased fluoride dosage factor, 13:03 Pump 1 from 0.95 to 1.00 Pump 2 from 0.50 to 0.55 Compressed air receiver B Pressure switch low - disregard. Exercising standby compressor Station and equipment okay | Georgina Water Treatment Plant | 2026-02-05
EAST | February | Train #6 was left off overnight after acid clean. Initiated MIT on train #6 @10:12 - MIT passed - High: 3.16 / Low: 1.82 kpa Reviewed MIT and daily filter performance on all membrane trains - All passed and within range - recorded values in PWQ sheets Completed the following WO's: - Air compressor maintenance and inspection - ran emergency compressor #3 - no issues - Air dryer inspection - Compressed air system inspection, no leaks observed | Georgina Water Treatment Plant | 2026-02-05
EAST | February | On site for station check and equipment verifications Reviewed MIT and daily filter performance on all membrane trains - all passed and within range - recorded data in PWQ sheets Initiated Recovery clean Hypo on Train #7 @10:15 Operations and adjustments: - Duty rotated air compressors - Placed BOGE to Lead D1, and Kaeser to Standby D2 - Created WO for maintenance to service Kaeser air compressor, there is a maintenance prompt on the screen. Kaeser compressor remains available in Standby if needed - Primed and tested Sodium bisulfite pump #2 during a neutralization sequence. No leaks observed, pump is now in auto back in service - @11:00 duty rotated clearwell chlorinators - placed chlorinator #6 to D1 - @11:05 duty rotated clearwell solenoid valves, placed valve #2 to D1. Performed visual inspection of chlorination system and lines. Chlorinator #6 is dosing 45 kg/day, with adequate vacuum - @11:22 duty rotated low lift chlorinators (Mussel control) Placed chlorinator #8 in D1 Collected grab sample on train #7 R-clean @13:45 - 400 mg/L cl2, pH = 9.96 Completed PWQ sheets plant rounds, verified dosages all okay. Reviewed trends, equipment OOS: Low lift P3, Sludge P3 Station ok | Georgina Water Treatment Plant | 2026-02-09
EAST | February | On site for station check, 08:00 Activated SUETDR duty 1, 08:18 Completed MIT and daily filter performance review and log - all okay, 08:24 Activated Keswick duty 1, 9:40 Increased fluoride pump 2 dosage factor 0.55 to 0.60, at 10:31 Fluoride analyzer readings: Keswick 0.41 and Sutton 0.38 prior to change with fluoride pump 2 running Increased fluoride pump 2 dosage factor 0.60 to 0.65, 11:11 Verified chlorine analyzers (grab/analyzer) in mg/L Contact tank 1 FCl, 13:06, 1.88/1.91 Contact tank 2 FCl, 13:09, 2.17/2.21 Clearwell 1 FCl, 13:05, 1.91/1.85 Clearwell 2 FCl, 13:10, 1.93/1.84 Post clearwell FCl, 13:12, 1.93/2.15 Adjusted to match average of grabs Keswick header FCl, 13:23, 1.89/1.76 Adjusted to match average of grabs Keswick header TCl, 13:23, 2.12/2.26 Sutton header FCl, 13:04, 1.84/1.97 Sutton header TCl, 13:04, 2.09/2.29 Adjusted Keswick fluoride analyzer, 13:30 Grab: 0.76, Analyzer: 0.51 -- adjusted to 0.61. Continuing to monitor Station and equipment okay | Georgina Water Treatment Plant | 2026-02-06
EAST | February | ROC called regarding Make Up Air Unit low temp alarm. Will disregard till Monday. | Georgina Water Treatment Plant | 2026-02-08
EAST | February | On site with total power for generator issue | Georgina Water Treatment Plant | 2026-02-05
WW-CEAST | February | Satnam and Chris Iliohan in to get pump 3 up running. Discharge valve faulty. Removed actuator from pump 4 since it out of service Install on pump 3 discharge valve had to reprogram actuator due to left have operation being moved to right hand valve configuration Tested local and remote. No issues noticed at this time | Aurora Henderson Sewage Pumping Station | 2026-02-23
WW-CEAST | February | On site to assist for wet well scum removal. Put station on pac mode around 9.30am. Wessuc was able to clean scum off cell 1 in the wet well. They will be back again to clean the remainder of the wet well. Station put back to auto mode from pac mode at 3.00pm. station back to normal operations. | Aurora Henderson Sewage Pumping Station | 2026-02-26
WW-CEAST | February | Station readings taken. Data entered on sharepoint. Reviewed SCADA, trends. All pumps available in all-stop auto duty rotation. Station running normal. Standby power generator available in auto. | Aurora Henderson Sewage Pumping Station | 2026-02-23
WW-CEAST | February | On site for media sampling with Contractor, All Round System (John Round), under RFT 2609-25. | Aurora Henderson Sewage Pumping Station | 2026-02-26
WW-CEAST | February | Station readings taken. Data entered on sharepoint. Reviewed SCADA, trends. All pumps available in all-stop auto duty rotation. Station running normal. JHSC Health and Safety Inspection completed. Dry Well Flood Alarm Test, High/Low Temperature Alarm Test completed Hazardous Waste Collection and Removal Standby Power Generator Test Run - pre-test checked, ok. Generator started and stopped running without problem. Gen Start time: 80.3, Stop time: 81.6, Run time: 1:3hrs. Cleared/reset all alarms. Generator back in auto and available. | Aurora Henderson Sewage Pumping Station | 2026-02-02
WW-CEAST | February | Station check complete and the readings have been entered into the sharepoint | Aurora Henderson Sewage Pumping Station | 2026-02-13
WW-CEAST | February | Station readings taken. Data entered on sharepoint. Reviewed SCADA, trends. All pumps available in all-stop auto duty rotation. Station running normal. Odour control scrubber system inspection completed. Standby power generator available in auto. | Aurora Henderson Sewage Pumping Station | 2026-02-27
WW-CEAST | February | Station readings taken. Data entered on sharepoint. Reviewed SCADA, trends. All pumps available in all-stop auto duty rotation. Station running normal. RS Pump inspection. Pump 1 - @ 50% speed, 54 L/s, 329 kPa, 57 A, 551 V, 58 Hz, 1710 Rpm; @100% speed, 65 L/s, 352 kPa, 66 A, 572 V, 60 Hz, 1783 Rpm Pump 2 - @ 50% speed, 50 L/s, 325 kPa, 56 A, 551 V, 58 Hz, 1711 Rpm; @100% speed, 62 L/s, 347 kPa, 65 A, 575 V, 60 Hz, 1783 Rpm Pump 3 - @ 50% speed, 54 L/s, 323 kPa, 57 A, 551 V, 58 Hz, 1711 Rpm; @100% speed, 63 L/s, 349 kPa, 67 A, 545 V, 60 Hz, 1782 Rpm Pump 4 - @ 50% speed, 53 L/s, 330 kPa, 57 A, 551 V, 58 Hz, 1711 Rpm; @100% speed, 64 L/s, 352 kPa, 65 A, 575 V, 60 Hz, 1784 Rpm RS Pump Discharge Valves Actuator Inspection and Exercise Manual Valves Exercise Check valve inspection. Air Relief Valve inspection. | Aurora Henderson Sewage Pumping Station | 2026-02-20
WW-CEAST | February | Station check complete and the readings have been entered into the sharepoint. | Aurora Henderson Sewage Pumping Station | 2026-02-09
WW-CEAST | February | Station check complete and the readings have been entered into the sharepoint | Aurora Henderson Sewage Pumping Station | 2026-02-06
WW-CEAST | February | -station check of site -reviewed SCADA -inspected site -entered data into SharePoint -armed site, and locked gate -station okay | Oak Ridges Air Management Facility | 2026-02-24
WW-CEAST | February | On site for station check. Entered station readings to sharepoint. Fans 1 and 2 running in auto. Nutrient tank batch mixing completed. Unit 1 recirculation pump #2 OOS. Unit 2 recirculation pump #1 OOS. Standby power generator available in auto | Oak Ridges Air Management Facility | 2026-02-02
WW-CEAST | February | On site to investigate recirc pump flow issues. Got an approval from Dave(NAC) prior to coming on site for investigation. Found system 1 recirc 1 and system 2 recirc 2 pumps have been isolated with both suction/discharge closed. Talked to Dave(NAC) and he confirmed all valves should have been open and all pumps should have been in service. Opened all valves for above pumps, bled the air out from the pump, and then put it back in service. Noticed 2 different types of pump motors mounted/installed on recirc pumps. Inquired to NAC/Aecom as to why we have 2 different motors. | Oak Ridges Air Management Facility | 2026-02-19
WW-CEAST | February | On site for station check & Support for EATON VFD Programming. EATON VFD Programming completed successfully. Tested out new recirculation pump for train 1. Entered station readings to sharepoint. Fans 1 and 2 running in auto. Nutrient tank batch mixing completed. Unit 1 recirculation pump #1 OOS. Standby power generator available in auto | Oak Ridges Air Management Facility | 2026-02-17
WW-CEAST | February | Shelved Estop/communication loss alarms for all recirc pumps as requested by Graham.B/ROC | Oak Ridges Air Management Facility | 2026-02-04
WW-CEAST | February | -Received call from ROC regarding power failure on site. Utility power has now been restored, but multiple alarms on site. Cleared alarms related to power failure, but Fan 1 VFD Fault will not clear. Contacted team lead, who is following up with NAC regarding Fan 1 fault. | Oak Ridges Air Management Facility | 2026-02-03
WW-CEAST | February | Station check complete and the readings have been entered into the sharepoint. System 2 recirc pump 2 overload alarm outstanding. Informed NAC and Jim(NAC) on his way to troubleshoot. Filled nutrient tank. Increased blowdown for both trains in response to low recirc pH | Oak Ridges Air Management Facility | 2026-02-09