## Operational Issues
PERSONGROUP | LOGBOOK_MONTH | LDTEXT | DESCRIPTION | EVENTDATE
WW-NORTH | March | decant and transfer sludge tank 1 complete lab and enter data into SharePoint pump scum down batch waste into tank 1 plant checks completed Rake bar screen Level grit bin Clean train three turbidity meter | Keswick Water Resource Recovery Facility | 2026-03-30
WW-NORTH | March | Performed station check Decanted/transferred sludge thickening tanks Batch wasted into tank 1, topped up tank 2, then directed WAS to tank 3 Completed lab and entered readings into ACE sheet Collected weekly regulatory samples and delivered to Newmarket Delivered spent UV bulbs to Newmarket Completed scheduled work orders Inspected OCU and recorded readings in binder Received citric acid delivery Satnam (electrical) was here to investigate train 2 permeate pump issue - now running in auto. | Keswick Water Resource Recovery Facility | 2026-03-31
WW-NORTH | March | Decanted Sludge holding tanks: 2 & 3 Transferred Sludge holding tanks: 2 & 3 Directed WAS to tank 2 Pumped down scum chambers Rotated UV duties: Duty 1 = Channel 2 Duty 2 = Channel 1 Rotated Headworks screening channel: Duty 1 = Channel 2 Duty 2 = Channel 1 Channel 1 bin is full Overhead door to channel 2 bin room is not working; cycled breaker in an attempt to resolve issue- no success. Will create a followup work order | Keswick Water Resource Recovery Facility | 2026-03-15
WW-NORTH | March | Performed station check Decanted/transferred sludge thickening tanks Topped up tank 3, then directed WAS to tank 2 Completed lab and entered readings into ACE sheet Collected weekly regulatory samples and delivered to Newmarket Made process adjustment as a result of high flows - lowered aeration tank alum dosages (50 to 20 mg/L), switched bar screen to continuous mode, disabled M-cleans for trains 3-5, and lowered plant recovery from 93 to 90% Completed scheduled work orders Inspected and greased online clarifiers Performed housekeeping around aeration blowers Cleaned TSS probe. | Keswick Water Resource Recovery Facility | 2026-03-11
WW-NORTH | March | Train 4 shut down on hihi turbidity which came in on start up; cleared alarm and placed train back in service and observed start up- turbidity did not immediately drop but gradually reduced below 1 NTU. Will schedule a turbidimeter cleaning tomorrow. | Keswick Water Resource Recovery Facility | 2026-03-11
WW-NORTH | March | Performed station check Decanted/transferred sludge thickening tanks Topped up tank 3, then directed WAS to tank 2 Completed lab and entered readings into ACE sheet Lowered RAS return rate from 50 to 40% Scheduled hypo R-cleans for trains 2, 3, and 5 to start at 18:00 Worked on UV 1A - replaced intensity probe sleeve and rack 9, bulb 5 sleeve Found membrane air compressor 2 auto drain passing air continuously - isolated the drain and created a WO for maintenance Cleaned train 2 turbidimeter and returned to service Completed scheduled work orders Exercised outfall gates Inspected microscreen actuators and valves Honeywell was here to fix various arming/disarming issues around plant and Ferguson Electric was here working in generator building. | Keswick Water Resource Recovery Facility | 2026-03-13
WW-NORTH | March | Started decanting S.T.T's 2 and 3 | Keswick Water Resource Recovery Facility | 2026-03-01
WW-NORTH | March | Replaced batteries on generator | Keswick Water Resource Recovery Facility | 2026-03-10
WW-NORTH | March | Performed station check Decanted/transferred sludge thickening tanks Batch wasted into tank 1, fed tank 3 until full, then directed WAS to tank 2 Completed lab and entered readings into ACE sheet Reset sludge blower/channel blower/membrane MUA alarms Scheduled a heated hypo/acid R-clean on train 2 for 19:00 Worked on membrane turbidimeters Completed scheduled work orders Topped up caustic tank (no delivery today) Inspected OCU and recorded readings in binder Performed portable Honda generator test runs Performed H&S inspection Checked for hazardous waste. | Keswick Water Resource Recovery Facility | 2026-03-02
WW-NORTH | March | Performed station check Decanted/transferred sludge thickening tanks Batch wasted into tank 1, topped up tank 3, then directed WAS to tank 2 Completed lab and entered readings into ACE sheet Collected weekly regulatory samples and delivered to Newmarket Checked membrane air compressors and dryers Checked membrane turbidimeters Scheduled a heated hypo/acid R-clean on train 3 for 19:00. | Keswick Water Resource Recovery Facility | 2026-03-04
WW-NORTH | March | Performed station check Decanted/transferred sludge thickening tanks Batch wasted into tank 1, topped up tank 2, then directed WAS to tank 3 Completed lab and entered readings into ACE sheet Adjusted aeration tank alum dosages from 60 to 50 mg/L Topped up hypo and caustic tanks Completed scheduled work orders and notified ROC of work being completed Flushed alum lines to aeration tanks Checked aeration tank DO probes Investigate diesel containment flood alarm - contractors working on containment. | Keswick Water Resource Recovery Facility | 2026-03-10
WW-NORTH | March | Performed station check Decanted/transferred sludge thickening tanks Batch wasted into tank 1, topped up tank 2, then directed WAS to tank 3 Completed lab and entered readings into ACE sheet Topped up hypo tank Completed scheduled work orders Inspected OCU and recorded readings in binder Inspected sludge holding pumps Anchor Experts was here to inspect fall arrest equipment. | Keswick Water Resource Recovery Facility | 2026-03-05
WW-NORTH | March | Performed station check Decanted/transferred sludge thickening tanks Batch wasted into tank 1, topped up tank 3, then directed WAS to tank 2 Completed lab and entered readings into ACE sheet Investigated train 2 permeate pump showing in local on SCADA - hour meter on MCC doesn't have power and train 2 won't run in remote Completed scheduled work orders Cleaned TSS probe Inspected and cleaned membrane turbidimeters Exercised alum chemical panel valves Cleaned DO probes Pumped down scum chambers Inspected OCU and recorded readings in binder Performed housekeeping around plant. | Keswick Water Resource Recovery Facility | 2026-03-23
WW-NORTH | March | Test backflow preventers All 6 tested passed | Keswick Water Resource Recovery Facility | 2026-03-18
WW-NORTH | March | Performed station check Decanted/transferred sludge thickening tanks Topped up tank 2, then directed WAS to tank 3 Replaced tank 2 and 3 decant pumps Completed lab and entered readings into ACE sheet Replaced train 1 turbidimeter vial Completed scheduled work orders Inspected OCU and recorded readings in binder Pumped down scum chambers. | Keswick Water Resource Recovery Facility | 2026-03-26
WW-NORTH | March | 1150hrs switched WAS feed from STT2 to STT1 checked scada | Keswick Water Resource Recovery Facility | 2026-03-21
WW-NORTH | March | Performed station check Decanted/transferred sludge thickening tanks Batch wasted into tank 1, topped up tank 3, then directed WAS to tank 2 Completed lab and entered readings into ACE sheet Completed scheduled work orders and notified ROC of work being completed Inspected scum pumps Cleaned DO probes Hosed membrane trains 2-5 and collected sample of initial hypo solution during train 1 R clean (470 mg/L) Placed generator in local for the day while contractors worked on silencers. | Keswick Water Resource Recovery Facility | 2026-03-17
WW-NORTH | March | Test backflow preventers All passed | Keswick Water Resource Recovery Facility | 2026-03-17
WW-NORTH | March | Performed station check Decanted/transferred sludge thickening tanks Topped up tank 2, then directed WAS to tank 3 Completed lab and entered readings into ACE sheet Made process adjustments - increased aeration tank alum dosages (20 to 40 mg/L), switched bar screen to intermittent mode, enabled M-cleans for trains 3-5 Completed scheduled work orders Pumped down scum chambers Cleaned membrane turbidimeters Tested headworks gas detectors Inspected grit vortexes Inspected headworks sump pump Inspected dewatering pump. | Keswick Water Resource Recovery Facility | 2026-03-12
WW-NORTH | March | Performed station check Decanted/transferred sludge thickening tanks Fed tank 2 until full, then directed WAS to tank 3 Completed lab and entered readings into ACE sheet Hosed scum buildup in grit classifier 1 Worked on train 5 turbidimeter flowmeter Completed scheduled work orders and notified ROC of work being completed Performed standby generator test run and recorded readings in rounds sheet Start: 369.1 h Stop: 370.2 h Run time: 1.1 h Started effluent pumps after diesel transfer (both in duty 1 but not running) Cleaned DO probes Checked chlorine analyzer Inspected hoists in membrane building Received caustic delivery Inspected air compressors Hosed membrane trains 4&5. | Keswick Water Resource Recovery Facility | 2026-03-03
WW-NORTH | March | Performed station check Decanted/transferred sludge thickening tanks Topped up tank 3, then directed WAS to tank 2 Completed lab and entered readings into ACE sheet Scheduled heated hypo/acid R-cleans on train 4/5 for 18:00 Completed scheduled work orders Checked membrane sump pit and tested high level alarm Tested chemical containment flood alarms Replaced aeration blower 1, 3, and 4 filters Received captor delivery Chris (PCS) was here to replace SCADA UPS in admin building. | Keswick Water Resource Recovery Facility | 2026-03-06
WW-NORTH | March | Directed WAS to sludge thickening tank 1 | Keswick Water Resource Recovery Facility | 2026-03-14
WW-NORTH | March | Performed station check Decanted/transferred sludge thickening tanks Batch wasted into tank 1, topped up tank 3, then directed WAS to tank 2 Replaced decant pump 2 handle and hose connection, and hosed sludge pad Completed lab and entered readings into ACE sheet Scheduled a hypo/acid R-clean on train 1 for 18:00 Rotated effluent pump duties Completed scheduled work orders Inspected membrane and generator air compressors Inspected OCU, RAS/WAS, and admin sump pumps and tested high level alarm Inspected sludge transfer pumps Inspected supernatant pumps Pumped down scum tanks. | Keswick Water Resource Recovery Facility | 2026-03-09
WW-NORTH | March | Performed station check Decanted/transferred sludge thickening tanks Batch wasted into tank 1, topped up tank 3, then directed WAS to tank 2 Completed lab and entered readings into ACE sheet Collected weekly regulatory samples and delivered to Newmarket Worked on UV bank 1A - replaced intensity probe but still reading low Scheduled a heater hypo/acid R-clean for train 2 @ 18:00 Lowered alum dosage to aeration tanks from 40 to 35 mg/L Rotated headworks channel 1 into service after bin was emptied Completed scheduled work orders Hosed membrane train 1 Received alum delivery Pumped north flowmeter chamber Placed generator in local for the day while contractors worked on silencers. | Keswick Water Resource Recovery Facility | 2026-03-18
WW-NORTH | March | Test backflow preventers B1 water meter failed 2nd check installed repair kit retested Passed The others both passed | Keswick Water Resource Recovery Facility | 2026-03-23
WW-NORTH | March | Remove broken auto drain from compressor. | Keswick Water Resource Recovery Facility | 2026-03-18
WW-NORTH | March | On site to replace the auto drain on compressor 1 Also took the Ginie lift battery to get a replacement | Keswick Water Resource Recovery Facility | 2026-03-23
WW-NORTH | March | on site 0712hrs sludge handling. out 0720hrs to KeswickPS back 0900hrs. | Keswick Water Resource Recovery Facility | 2026-03-22
WW-NORTH | March | Plant checks completed Sludge handling Batch waste into tank 1 Alum delivery received Check OCU Top up hypo day tank Check and grease micro screens Check RAS/WAS pumps and sumps Check crane in RAS/WAS building Competed lab and enter data into SharePoint Program R clean on train 1&4 Clean train 3 turbidity meter Check air compressors | Keswick Water Resource Recovery Facility | 2026-03-16
WW-NORTH | March | Performed station check Decanted/transferred sludge thickening tanks Topped up tank 3, then directed WAS to tank 2 Completed lab and entered readings into ACE sheet Increased alum dosages to aeration tanks from 35 to 50 mg/L Topped up hypo tank. | Keswick Water Resource Recovery Facility | 2026-03-27
WW-NORTH | March | Performed weekend sludge work. Decanted and transferred STT 2 and 3 - Investigated where sodium bisulfite containment spill alarm was coming from but could not find source. All other containments are dry. - While in membrane building noticed that the braided water line feeding micro screen 1 was leaking. Removed damaged hose and replaced with new line. Micro screen 1 back online running in auto. | Keswick Water Resource Recovery Facility | 2026-03-08
WW-NORTH | March | Performed station check Decanted/transferred sludge thickening tanks Topped up tank 3, then directed WAS to tank 2 Completed lab and entered readings into ACE sheet Scheduled heated hypo+acid R-cleans on trains 3 & 5 for 18:00 and topped up chemical tanks Adjusted citric acid tank level alarms (lo from 0.3 to 0.2 m, lolo from 0.2 to 0.15 m). | Keswick Water Resource Recovery Facility | 2026-03-20
WW-NORTH | March | Fuel tank 1 vacuum is 14 inches Hg Fuel tank 2 vacuum is 18.5 inches Hg Day tank is new and contractors are plumbing fittings into it Containment is recently epoxied for bulk and day tanks. | Keswick Water Resource Recovery Facility | 2026-03-26
WW-NORTH | March | Performed station check Decanted/transferred sludge thickening tanks Batch wasted into tank 1, topped up tank 2, then directed WAS to tank 3 Completed lab and entered readings into ACE sheet Topped up caustic tank Cleaned up oil puddle under compressor 1 Performed housekeeping in RAS/WAS basement. | Keswick Water Resource Recovery Facility | 2026-03-24
WW-NORTH | March | Performed station check Decanted/transferred sludge thickening tanks Batch wasted into tank 1, topped up tank 3, then directed WAS to tank 2 Completed lab and entered readings into ACE sheet Recorded monthly meter readings in rounds sheet Collected weekly regulatory samples and delivered to Newmarket Returned caustic lo and lolo setpoints to 0.3 and 0.2 m Initiated M-clean on train 2 during scheduled time (cleans not running remotely while train is interlocked) Performed housekeeping around plant. | Keswick Water Resource Recovery Facility | 2026-03-25
WW-NORTH | March | Performed station check Decanted/transferred sludge thickening tanks Topped up tank 2, then directed WAS to tank 3 Completed lab and entered readings into ACE sheet Replaced cable to UV intensity probe - intensity still reading low Completed scheduled work orders Inspected OCU and recorded readings in binder Pumped down scum tanks Received hypo delivery Inspected bar screens Total Lift was here to inspect AWP. | Keswick Water Resource Recovery Facility | 2026-03-19
WW-NORTH | March | station checks health and safety | Holland Landing Lagoons | 2026-03-02
WW-NORTH | March | site checks | Holland Landing Lagoons | 2026-03-26
WW-NORTH | March | checked site. | Holland Landing Lagoons | 2026-03-09
WW-NORTH | March | time in 1100hrs station checks lagoon berm inspection. out 1200 | Holland Landing Lagoons | 2026-03-20
WW-NORTH | March | station checks sharepoint data entry Diesel containment inspected. | Holland Landing Sewage Pumping Station | 2026-03-09
WW-NORTH | March | Under direction of OIC Chris Colangelo Worked with CMS, David Dougherty, Martin DeVries, Christian Streef. Impeller on RSP_PMP3 was changed. VFD #3 Max Frequency adjusted to 57Hz. Scada speed SP remained the same 85% which reduced the operating speed to 53Hz from 56Hz. Ran flow and speed testing on PMP3 with Maint and Supplier contractors. Everything was put back in Auto after the testing. No outstanding Issues remaining. | Holland Landing Sewage Pumping Station | 2026-03-30
WW-NORTH | March | on site for OCU media sampling. Drywell condensed inspection | Holland Landing Sewage Pumping Station | 2026-03-11
WW-NORTH | March | station checks diesel generator test run health and safety OCU inspection drywell flood alarm test , appx1045hrs. Received by cpo | Holland Landing Sewage Pumping Station | 2026-03-05
WW-NORTH | March | Attended for investigation into abnormal wetwell overflow flowmeter readings Observed water from river has backed up to facility outfall pipe Opened hatch in wetwell to check overflow trough and found some water pooled below the overflow transmitter - no active flow is occurring. | Holland Landing Sewage Pumping Station | 2026-03-10
WW-NORTH | March | on site 1030hrs station checks sharepoint data entry diesel containment inspection house cleaning | Holland Landing Sewage Pumping Station | 2026-03-19
WW-NORTH | March | Onsite to verify WWEL_FIT1 configuration as requested Informed ROC Placed device into cal mode on scada then connected via HART Found that the flow totalizer had not been configured correctly. Corrected the issue and saved the parameters Removed device from cal mode and cleared associated alarms Informed ROC, armed building and left site | Holland Landing Sewage Pumping Station | 2026-03-24
WW-NORTH | March | station checks security car on site , with gate open on arrival. Honeywell working on door. sharepoint data entry diesel containment inspection | Holland Landing Sewage Pumping Station | 2026-03-26
WW-NORTH | March | station checks sharepoint data entry Diesel containment inspection overflow kit inspection. dropped off davit and winch | Holland Landing Sewage Pumping Station | 2026-03-16
WW-NORTH | March | station checks sharepoint data entry | Holland Landing Sewage Pumping Station | 2026-03-02
WW-NORTH | March | While checking SCADA I noticed that WWEL_FIT1 was showing a flow of approx 25L/s. This reading on SCADA is for the overflow to the river. Based on the SCADA trends this flow started to creep up from 0 L/s on March 7. The trends did not indicate the wetwell level getting to an elevation that would cause an overflow event. At 1113HRS I contacted Kevin Kerek to notify him of the findings. He confirmed that he will dispatch an operator to check out the station and confirm the overflow weir is dry and follow-up as needed with instrumentation. | Holland Landing Sewage Pumping Station | 2026-03-10
WW-NORTH | March | Responding to inlet channel hihi, caused by channel grinder fault from earlier this morning. Ran grinder locally in reverse and then forward. Placed back to auto and observed start up and brief run period- no issues | Holland Landing Sewage Pumping Station | 2026-03-12
WW-NORTH | March | On site for PM on odour control system. Checked out motor and fan. Direct coupled no issues with noise or vibration. | Holland Landing Sewage Pumping Station | 2026-03-12
WW-NORTH | March | Changed Overflow Hi from 250 to 10l/s and HiHi from 280 to 25l/s. | Holland Landing Sewage Pumping Station | 2026-03-25
WW-NORTH | March | Onsite to check station Review scada/trends Enter data in sharepoint No alarms Check river level - water from river has backed up to facility outfall pipe Opened hatch in wetwell to check overflow trough and found water still pooled below the overflow transmitter - verified there is no active flow occurring. | Holland Landing Sewage Pumping Station | 2026-03-12
WW-NORTH | March | on site 0845hrs station check reset RSP2 at MCC, tripped out on power failure. Ran in duty 1. | Holland Landing Sewage Pumping Station | 2026-03-23
WW-NORTH | March | On site to add grease wip to channel grinder to make easier access for greasing | Holland Landing Sewage Pumping Station | 2026-03-04
WW-NORTH | March | Onsite to check station Review scada/trends Enter data in sharepoint Cpd onsite with ghd contractor | East Gwillimbury 2nd Concession Sewage Pumping Station | 2026-03-12
WW-NORTH | March | station checks sharepoint data entry Diesel containment dry. | East Gwillimbury 2nd Concession Sewage Pumping Station | 2026-03-09
WW-NORTH | March | on site for OCU media sampling. | East Gwillimbury 2nd Concession Sewage Pumping Station | 2026-03-11
WW-NORTH | March | on site 1000hrs station checks sharepoint data entry diesel containment inspection ( dry ) out 1050hrs | East Gwillimbury 2nd Concession Sewage Pumping Station | 2026-03-23
WW-NORTH | March | on site for OCU media sampling | Queensville West Sewage Pumping Station | 2026-03-11
WW-NORTH | March | station checks van 3081-24 on site ( electrical ), GHD car246-72 on site, 0n arrival. Diesel containment flood alarm from feb 28 @02:37 will not clear, checked containment and is dry. sharepoint data entry 09:05 hrs driller with Thurburn on site to drill one hole in conjunction with GHD. | East Gwillimbury 2nd Concession Sewage Pumping Station | 2026-03-02
WW-NORTH | March | WO's Generator test run OCU inspection drywell flood alarm test, CPO received appx 0924hrs drywell and hoist inspections Recirc valves and actuators exercise health and safety inspection | East Gwillimbury 2nd Concession Sewage Pumping Station | 2026-03-03
WW-NORTH | March | station checks sharepoint data entry diesel containment inspection ( dry) | East Gwillimbury 2nd Concession Sewage Pumping Station | 2026-03-26
WW-NORTH | March | station checks sharepoint data entry overflow kit inspection Diesel containment inspection (dry) dropped off davit base and winch | East Gwillimbury 2nd Concession Sewage Pumping Station | 2026-03-16
WW-NORTH | March | Onsite to enter wetwell - consolidated work order Alert roc Wetwell overflow came in on scada at 0941hrs Clear and reset alarms | Queensville West Sewage Pumping Station | 2026-03-06
WW-NORTH | March | Complete pump PM?s No unusual noise, heat , or vibration. Pumps ran well. No slamming of check valves. Pump 3 discharge pressure gauge is broken. Pump 2 discharge 72 L/sec Pump 3 discharge 64 L/sec | Queensville West Sewage Pumping Station | 2026-03-12
WW-NORTH | March | Responding to sewage pump 2 VFD fault - reset VFD on MCC and cleared alarm on SCADA | Queensville West Sewage Pumping Station | 2026-03-08
WW-NORTH | March | Responding to pump 1 vfd fault (32 fan cooling T1->T16); reset fault and ran pump in manual- no issues. Left pump in duty 1 | Queensville West Sewage Pumping Station | 2026-03-11
WW-NORTH | March | Onsite to check station Review scada/trends Enter data in sharepoint Clear info alarms Diesel containment check | Queensville West Sewage Pumping Station | 2026-03-12
WW-NORTH | March | station checks sharepoint data entry | Queensville West Sewage Pumping Station | 2026-03-02
WW-NORTH | March | station checks sharepoint data entry Diesel containment is dry. alarm will not clear. | East Gwillimbury 2nd Concession Sewage Pumping Station | 2026-03-05
WW-NORTH | March | WO's generator test run ocu inspection actuators exercise consolidated drywell/hoist inspections. drywell flood alarm test on scada @1037hrs. health and safety | Queensville West Sewage Pumping Station | 2026-03-04
WW-NORTH | March | on site 0945hrs station checks sharepoint data entry diesel conatinment inspection out 1030hrs | East Gwillimbury 2nd Concession Sewage Pumping Station | 2026-03-19
WW-NORTH | March | station checks sharepoint data entry Diesel conatainment alarm. Found water in containment as snow had been plowed over and melted. Vacuumed out containment. Cleared alarm on scada | Queensville West Sewage Pumping Station | 2026-03-05
WW-NORTH | March | station checks sharepoint data entry | Queensville West Sewage Pumping Station | 2026-03-09
WW-NORTH | March | station checks sharepoint data entry dropped off davit and winch | Queensville West Sewage Pumping Station | 2026-03-16
WW-NORTH | March | WO's station checks blower inspection fanbody inspection recirculation system inspection | Morton Avenue Air Management Facility | 2026-03-12
WW-NORTH | March | 1117hrs on site station checks sharepoint data entry diesel containment inspection | Queensville West Sewage Pumping Station | 2026-03-19
WW-NORTH | March | on site 1056hrs station checks out 1209hrs | Queensville West Sewage Pumping Station | 2026-03-23
WW-NORTH | March | station check sharepoint data entry diesel containment inspection. | Queensville West Sewage Pumping Station | 2026-03-26
WW-NORTH | March | Onsite to check station Review scada Enter data in sharepoint Flush blowdown Swap blower duties. Blower 1 in duty 1 Drain flex hose JHSC inspection | Morton Avenue Air Management Facility | 2026-03-02
WW-NORTH | March | Onsite to check station Review scada Enter data in sharepoint Flush blowdown Swap blower duties. Blower 2 in duty 1 | Morton Avenue Air Management Facility | 2026-03-09
WW-NORTH | March | Onsite to check station Review scada - no alarms Enter data in sharepoint Flush blowdown Swap blower duty - blower 2 in d1 | Morton Avenue Air Management Facility | 2026-03-23
WW-NORTH | March | Rotate blowers Enter data into SharePoint Drain condensation in media unit | Morton Avenue Air Management Facility | 2026-03-16
WW-NORTH | March | Onsite to check station Review scada Enter data in sharepoint Flush blowdown | Morton Avenue Air Management Facility | 2026-03-26
WW-NORTH | March | Onsite to check station Review scada Enter data in sharepoint Flush blowdown | Morton Avenue Air Management Facility | 2026-03-05
WW-NORTH | March | Test backflow preventer | Morton Avenue Air Management Facility | 2026-03-11
WW-NORTH | March | Onsite to check station Review scada Enter data in sharepoint Flush blowdown | Morton Avenue Air Management Facility | 2026-03-19
WW-NORTH | March | Performed facility station check Completed Lab analysis: Data in Sharepoint Decanted Sludge thickening tank Transferred Sludge holding tank Inspected headworks: replaced grit bins and raked manual bar screen Equipment OOS: Mechanical bar screen | Sutton Water Resource Recovery Facility | 2026-03-30
WW-NORTH | March | Diverted Woodriver Bend to lagoon @ 08:56 hrs Adjusted Flow bias max: 10 L/s --> 15 L/s Performed facility station check Completed Lab analysis: Data in Sharepoint Collected Weekly Samples: Sewage (W11705266) Raw @ 09:30 / Effluent @ 09:35 Decanted Sludge thickening tank Transferred Sludge holding tank Inspected headworks: leveled grit bin and raked manual bar screen GFL hauled sludge = 38 m3 Diverted Woodriver Bend to lagoon at 08:56 hrs Adjusted Flow bias max: 10 L/s --> 15 L/s Filter B-F3 airlift not throwing sand- pulled and is now functioning Filter A-F1 airlift not throwing sand and unable to pull up airlift. Lanced with air but still unable to budge. Will continue troubleshooting tomorrow Equipment OOS: Mechanical bar screen | Sutton Water Resource Recovery Facility | 2026-03-31
WW-NORTH | March | Performed facility station check Completed Lab analysis: Data in Sharepoint Decanted Sludge holding tank Transferred Sludge thickening tank Inspected headworks: leveled grit bin and raked bar screen Total Power LTD on site to perform semi annual generator maintenance Completed monthly PM work orders: -Generator test run Date: March 05, 2026 Start time: 11:26 Start hours: 601 Stop Hours: 602.2 Run Time hours: 1.02 Start Fuel: 674 L (23.0 cm) Stop Fuel: 642 L (21.9 cm) Pre run checks: Battery Cell Levels: Ok Battery Terminals and Cables: Ok Oil Level: Ok Coolant Level: Ok Fluid Leaks: Ok Coolant Recirculating pump: Ok Faulty Gauges: Ok Operating Current: 122 Amps Operating Frequency: 60.0 Hz Operating Voltage: 600 Volts Engine speed: 1803 RPM Water/coolant Temp: 184 F Pyrometer: 864 F Oil Pressure: 42 psi Oil Temp: 212 F | Sutton Water Resource Recovery Facility | 2026-03-05
WW-NORTH | March | Performed station check Decanted and transferred STT Cleaned bar screen area Completed lab analysis and entered readings into SharePoint Pushed out rag and grit bins Checked sand filters | Sutton Water Resource Recovery Facility | 2026-03-03
WW-NORTH | March | Performed station check Decanted and transferred STT GFL took sludge load 51m3 Completed lab analysis and entered readings into SharePoint Worked on sand filters AF3 and BF3 to get them operating Changed 3 bulbs on UV bank 2A (1-2, 1-4, 2-2) Inspected blower air relief Inspected and cleared inlet channel Test ran South River temp diesel for 15min | Sutton Water Resource Recovery Facility | 2026-03-13
WW-NORTH | March | Onsite for ocu media sampling with omar and contractor | Sutton Water Resource Recovery Facility | 2026-03-11
WW-NORTH | March | Performed station check Decanted and transferred STT GFL took sludge load 51m3 Completed lab analysis and entered into SharePoint Checked sand filters | Sutton Water Resource Recovery Facility | 2026-03-10
WW-NORTH | March | 07:34 Diverted High St SPS to lagoon and returned Woodriver SPS to plant and placed lagoon pumps to manual off\ 11:36 Placed lagoon pumps back to auto Performed facility station check Completed Lab analysis: Data in Sharepoint Collected Weekly Samples: Sewage (W11656781) Raw @ 09:25 / Effluent @ 0920 Decanted Sludge holding tank Transferred Sludge thickening tank Inspected headworks: leveled grit bin and raked manual bar screen GFL hauled sludge = 51m3 Adjusted Lagoon hydrostatic level Lo alarm: 0.70 m ==> 0.30 m Equipment OOS: Mechanical bar screen | Sutton Water Resource Recovery Facility | 2026-03-11
WW-NORTH | March | On site for the broken screen auger and meet green frog. A quote was requested for a new auger | Sutton Water Resource Recovery Facility | 2026-03-13
WW-NORTH | March | Decanted sludge thickening tank Transferred sludge holding tank Raked manual bar screen | Sutton Water Resource Recovery Facility | 2026-03-15
WW-NORTH | March | Started decanting S.T.T Checked and leveled grit and rag bins Cleaned bar screen equipment Finished decanting and raised gate back to top position Started transfer from S.H.T | Sutton Water Resource Recovery Facility | 2026-03-01
WW-NORTH | March | Attending site to commission and verify the Lagoon Flowmeter - SUSP_SUSPLG_LGN_FIT1 (W11479921). Configured device, added asset number and verified function. ROC was notified before and after maintenance activities. | Sutton Water Resource Recovery Facility | 2026-03-04
WW-NORTH | March | Performed weekend sludge work - Decanted and transferred STT | Sutton Water Resource Recovery Facility | 2026-03-08
WW-NORTH | March | Performed station check Decanted and transferred STT Skimmed SBRs GFL took sludge load 50m3 Cleaned bar screen Completed lab analysis and entered readings into SharePoint | Sutton Water Resource Recovery Facility | 2026-03-06
WW-NORTH | March | Performed station check Decanted and transferred STT Completed lab analysis and entered readings into SharePoint GFL took sludge load 51m3 Upon arrival noticed dewatering screw press hopper, which is fed from the bar screen, was full. - Inspected screw press and found it to be sheered in half. - Switched bar screen and screw press to local off. - Pulled gate to manual bar screen and placed it into channel feeding offline bar screen. Maintenance on site to begin repairs on screw press. | Sutton Water Resource Recovery Facility | 2026-03-09
WW-NORTH | March | Performed station check Decanted and transferred STT Completed lab analysis and entered readings into SharePoint Cleaned bar screen | Sutton Water Resource Recovery Facility | 2026-03-02
WW-NORTH | March | Performed facility station check Completed Lab analysis: Data in Sharepoint Decanted Sludge thickening tank Transferred Sludge holding tank Inspected headworks: leveled grit bin and raked manual bar screen GFL hauled sludge = 50 m3 Cleaned DO probe SBR2 Adjusted SBR Common Setpoints: Post DO Low Setpoint = 3.00 PPM --> 3.20 PPM Equipment OOS: Mechanical bar screen | Sutton Water Resource Recovery Facility | 2026-03-24
WW-NORTH | March | Performed facility station check Completed Lab analysis: Data in Sharepoint Decanted Sludge thickening tank Transferred Sludge holding tank Inspected headworks: leveled grit bin and raked manual bar screen Adjusted WAS Total Cycle time SBR#1: 450 sec --> 430 sec SBR#2: 420 sec --> 380 sec Equipment OOS: Mechanical bar screen | Sutton Water Resource Recovery Facility | 2026-03-26
WW-NORTH | March | Performed facility station check Completed Lab analysis: Data in Sharepoint Decanted Sludge thickening tank Transferred Sludge holding tank Inspected headworks: leveled grit bin and raked manual bar screen Adjusted filter feed pump duty start: 1.10 m ==> 1.30 m Adjusted UV priorities: LEAD = Channel 2: BANKS- LEAD = A / LAG = B LAG = Channel 1: BANKS- LEAD = A / LAG = B Replaced ballast on UV Bank 1B: lamps 1/2- replaced with an allegedly rebuilt ballast. Ballast failed on start up. Will replace with a brand new ballast tomorrow. Adjusted UV priorities: LEAD = Channel 1: BANKS- LEAD = B / LAG = A LAG = Channel 2: BANKS- LEAD = A / LAG = B Filter B-F3: airlift has started throwing sand. Will continue to monitor. GFL hauled sludge = 51 m3 Equipment OOS: Mechanical bar screen | Sutton Water Resource Recovery Facility | 2026-03-19
WW-NORTH | March | Performed facility station check Completed Lab analysis: Data in Sharepoint Decanted Sludge thickening tank Transferred Sludge holding tank Inspected headworks: leveled grit bin and raked manual bar screen Replaced ballast on UV Bank 1B: lamps 1/2- replaced with new ballast. Cleaned effluent sample jug and lines Equipment OOS: Mechanical bar screen and building effluent pump 2 | Sutton Water Resource Recovery Facility | 2026-03-20
WW-NORTH | March | On site to install new effluent pumps. Pump installed but leaking at flange, leaving 1 pump off until Monday when flange can be corrected. | Sutton Water Resource Recovery Facility | 2026-03-20
WW-NORTH | March | Changed filter feed start duty from 1.0m to 0.9m to match level bias minimum. | Sutton Water Resource Recovery Facility | 2026-03-10
WW-NORTH | March | 12:50 Stopped diverting High St SPS to lagoon. All flow going to plant Adjusted SBR Common Setpoints, Post DO low Setpoint: 2.1 ppm ==> 3.0 ppm DO is remaining high and causing the blowers to stay off during the on air cycle. Will continue to monitor and make further changes if required Cleaned DO probes Performed facility station check Completed Lab analysis: Data in Sharepoint Decanted Sludge holding tank Transferred Sludge thickening tank Inspected headworks: leveled grit bin and raked manual bar screen Filter 1a; filter and reject water line clogged. Cleared obstruction from reject line but filter requires further maintenance. 14:33 UV Channel 2A multiple lamp failure and not enough healthy bulbs available. Adjusted UV priorities. Channel 1= LEAD / Bank 1 = LEAD / Bank 2 = LAG Channel 2 = LAG / Bank 1 = LAG / Bank 2 = LEAD Will replace bulbs tomorrow. Equipment OOS: Mechanical bar screen | Sutton Water Resource Recovery Facility | 2026-03-12
WW-NORTH | March | Test backflow preventers All passed | Sutton Water Resource Recovery Facility | 2026-03-03
WW-NORTH | March | Began diverting Woodriver bend SPS flows to the lagoon to alleviate load on plant. | Sutton Water Resource Recovery Facility | 2026-03-07
WW-NORTH | March | Performed facility station check Completed Lab analysis: Data in Sharepoint Decanted Sludge thickening tank Transferred Sludge holding tank Inspected headworks: screenings bin swap & replacement and raked manual bar screen GFL hauled sludge = 51 m3 Filter B-F3 airlift isn't throwing sand, only bubbling up air. Removed airlift and lanced the bottom of the filter; was extremely clogged- black water and rags were coming up. Reinstalled airlift and placed module back in operation. It was only temporarily functioning, but then failed again. Will continue troubleshooting tomorrow Equipment OOS: Mechanical bar screen | Sutton Water Resource Recovery Facility | 2026-03-16
WW-NORTH | March | Performed facility station check Completed Lab analysis: Data in Sharepoint Collected Weekly Samples: Sewage (W11690050) Raw @ 09:20 / Effluent @ 09:15 Decanted Sludge thickening tank Transferred Sludge holding tank Inspected headworks: leveled grit bin and raked manual bar screen GFL hauled sludge = 50 m3 Rotated UV priorities: LEAD = Channel 1: BANKS- LEAD = A / LAG = B LAG = Channel 2: BANKS- LEAD = A / LAG = B Equipment OOS: Mechanical bar screen | Sutton Water Resource Recovery Facility | 2026-03-25
WW-NORTH | March | on site 0800hrs sludge handling checked site. wracked barscreen out 0845hrs | Sutton Water Resource Recovery Facility | 2026-03-22
WW-NORTH | March | Performed facility station check Completed Lab analysis: Data in Sharepoint Collected Weekly Samples: Sewage (W11672667) Raw @ 08:45 / Effluent @ 09:00 Received ALUM delivery: 2167 L ==> 15'274L Decanted Sludge thickening tank Transferred Sludge holding tank Inspected headworks: leveled grit bin and raked manual bar screen Adjusted filter "Flow bias maximum": 16 L/s ==> 14 L/s Investigated filter B airlift supply air solenoid valve passing; solenoid requires replacing (burnt out). Breaker for the sand filters has been switched off. Supply air solenoid valves are in manual bypass- air will continuously run, when filter feed pumps are off. Maintenance team lead has been notified and parts have been ordered. UV channel 1 bank B, ballast fail and multiple lamp fault. Will replace ballast tomorrow. Adjusted UV Channel 1 priorities: 1A = LEAD / 1B = LAG Filter B-F3- continued troubleshooting; air lanced again from the side, with the airlift still installed- more rags came up and began throwing sand again. It was only temporarily functioning, but then failed again. Will continue troubleshooting tomorrow GFL hauled sludge = 51 m3 Completed monthly PM work orders: -EQ tank line flush -Decant arms 1 & 2 maintenance -SBR and Sludge blowers air relief inspection -Consolidated headworks inspection Equipment OOS: Mechanical bar screen | Sutton Water Resource Recovery Facility | 2026-03-18
WW-NORTH | March | Performed facility station check Completed Lab analysis: Data in Sharepoint Decanted Sludge thickening tank Transferred Sludge holding tank Inspected headworks: leveled grit bin and raked manual bar screen GFL hauled sludge = 51 m3 Equipment OOS: Mechanical bar screen | Sutton Water Resource Recovery Facility | 2026-03-17
WW-NORTH | March | Performed facility station check Completed Lab analysis: Data in Sharepoint Decanted Sludge thickening tank Transferred Sludge holding tank Inspected headworks: swapped out bar screen bins and raked manual bar screen GFL hauled sludge = 50 m3 Equipment OOS: Mechanical bar screen | Sutton Water Resource Recovery Facility | 2026-03-23
WW-NORTH | March | Performed facility station check Completed Lab analysis: Data in Sharepoint Decanted Sludge thickening tank Transferred Sludge holding tank Inspected headworks: leveled grit bin and raked manual bar screen Equipment OOS: Mechanical bar screen | Sutton Water Resource Recovery Facility | 2026-03-27
WW-NORTH | March | On site to finish install of effluent pump. Ran tested and put back in service. | Sutton Water Resource Recovery Facility | 2026-03-23
WW-NORTH | March | UV 1A low intensity alarm came in again. Adjusted UV channel 1 priorities 1A = LAG / 1B = LEAD | Sutton Water Resource Recovery Facility | 2026-03-12
WW-NORTH | March | Found sewage p.2 running at 100% with no flow Ran all pumps @ 100% and notified ROC of work being completed Obtained flow greater than 205 L/s on all pumps except sewage p.1 (160 L/s). | Keswick Sewage Pumping Station | 2026-03-13
WW-NORTH | March | Ran pump 3 at 100% in manual to clear slight blockage. Put other 3 pumps in manual. All back in auto and pump 3 discharged 215l/s | Keswick Sewage Pumping Station | 2026-03-12
WW-NORTH | March | On site to verify backup panel set-points. Removed obsolete backup panel elevation charts left current operating chart on PAC panel door. Cleaned toilet | Keswick Sewage Pumping Station | 2026-03-12
WW-NORTH | March | Onsite to check station Review scada/trends Enter data in sharepoint Hazardous waste removal check Heat trace inspection OCU maintenance | Keswick Sewage Pumping Station | 2026-03-05
WW-NORTH | March | Onsite to check station Review scada/trends Enter data in sharepoint ROC call regarding p2 and p3 lolo flow alarms Test both pumps at 100% manual speed - no flow Manually backflush p2 and p3 Try to run again at 100% speed - no flow Consolidated drywell work orders - panel did mot receive drywell flood, will return later to retest P3 clog cleared remotely Back onsite to flush p2 and try drywell flood again Bleed air on p2 - pump runs at 100% 215L/s. Back in service Panel did not receive drywell flood. Will try again later date | Keswick Sewage Pumping Station | 2026-03-09
WW-NORTH | March | Attended for sewage p.1 low flow Notified ROC of work being completed Backflushed p.1 and tested @ 100% - 208 L/s. | Keswick Sewage Pumping Station | 2026-03-13
WW-NORTH | March | Onsite to check station and run generator Alert roc Transfer station to diesel power at 11:26hrs Review scada/trends Enter data in sharepoint Transfer station back to diesel power at 12:26hrs Diesel data in sharepoint | Keswick Sewage Pumping Station | 2026-03-23
WW-NORTH | March | Attended for station check Recorded station readings in rounds sheet Checked dry well - p.1 running in duty Checked generator building - assisted Toromont tech with his investigation into generator issue from 12/24/2025 @ 00:51 Reviewed SCADA/trends - p.2 had no flow @ 100% speed, bled air and ran @ 100% (flow above 210 L/s for all). | Keswick Sewage Pumping Station | 2026-03-16
WW-NORTH | March | on site 0730hrs Responding to both channel grinder faults at 0644hrs ( VFD faults ). reset at MCC and then on scada. Both running now. 0739hrs while on site. Ultrasonic Hi and HI HI level alarms came in. RSP 1 and 2 now running at 272 l/s. Cleared ultrasonic alarms. cmu11750026. out 0745hrs | Keswick Sewage Pumping Station | 2026-03-22
WW-NORTH | March | Onsite to check station Review scada/trends Enter in sharepoint Clear outstanding alarms | Keswick Sewage Pumping Station | 2026-03-26
WW-NORTH | March | house keeping found water on floor in boiler room coming from condensate box behind boiler. mopped up . | Keswick Sewage Pumping Station | 2026-03-27
WW-NORTH | March | Onsite to check station Review scada/trends Enter data in sharepoint No outstandingp alarms | Keswick Sewage Pumping Station | 2026-03-19
WW-NORTH | March | Onsite to check station Review scada/trends Enter data in sharepoint Clear outstanding alarms - p2 lo flow Provide access to building for Eaton and Lexsan contractors to investigate OCU vfd issue Find p2 check valve leaking at the stem. Disable p2 from duty rotation and in manual off Eaton finds ocu drive is not operational and will be replaced JHSC inspection | Keswick Sewage Pumping Station | 2026-03-02
WW-NORTH | March | Onsite to complete consolidated wetwell work order Alert roc 10:20hrs station overflow and wetwell mezzanine flood alarm came in on scada. Clear and reset Alert roc work complete | Keswick Sewage Pumping Station | 2026-03-06
WW-NORTH | March | On site responding to Channel Grinder 2 overload fault. - Upon arrival the VFD was showing an OL fault - Reset alarm and attempted to run in auto but alarm came back in - Placed grinder in local and ran in reverse briefly - Reset alarm and placed back into Auto Channel Grinder 2 is now back running in auto | Keswick Sewage Pumping Station | 2026-03-07
WW-NORTH | March | Performed facility station check Data in sharepoint Equipment OOS: none | Sutton Woodriver Bend Sewage Pumping Station | 2026-03-30
WW-NORTH | March | Performed station check Entered readings into SharePoint Ran diesel generator Completed JHS inspection | Sutton Woodriver Bend Sewage Pumping Station | 2026-03-05
WW-NORTH | March | Performed station check Entered readings into SharePoint Reviewed trends | Sutton Woodriver Bend Sewage Pumping Station | 2026-03-09
WW-NORTH | March | Performed station check Entered readings into SharePoint | Sutton Woodriver Bend Sewage Pumping Station | 2026-03-02
WW-NORTH | March | Performed station check Entered readings into SharePoint | Sutton Woodriver Bend Sewage Pumping Station | 2026-03-16
WW-NORTH | March | Performed station check Entered readings into SharePoint | Sutton Woodriver Bend Sewage Pumping Station | 2026-03-23
WW-NORTH | March | Performed station check' Entered readings into SharePoint | Sutton Woodriver Bend Sewage Pumping Station | 2026-03-12
WW-NORTH | March | Performed station check Entered readings into SharePoint Completed JHS inspection | Sutton South River Sewage Pumping Station | 2026-03-12
WW-NORTH | March | Performed facility station check Data in sharepoint Equipment OOS: none | Sutton South River Sewage Pumping Station | 2026-03-30
WW-NORTH | March | Performed station check Entered readings into SharePoint | Sutton South River Sewage Pumping Station | 2026-03-09
WW-NORTH | March | Performed station check Entered readings into SharePoint | Sutton South River Sewage Pumping Station | 2026-03-02
WW-NORTH | March | Performed station check Entered readings into SharePoint | Sutton South River Sewage Pumping Station | 2026-03-19
WW-NORTH | March | Performed station check Entered readings into SharePoint | Sutton South River Sewage Pumping Station | 2026-03-23
WW-NORTH | March | Performed station check Entered readings into SharePoint | Sutton South River Sewage Pumping Station | 2026-03-05
WW-NORTH | March | Performed station check Entered readings into SharePoint | Sutton South River Sewage Pumping Station | 2026-03-16
WW-NORTH | March | Performed facility station check Data in sharepoint Equipment OOS: none | Sutton High Street Sewage Pumping Station | 2026-03-30
WW-NORTH | March | Performed station check Entered readings into SharePoiunt | Sutton South River Sewage Pumping Station | 2026-03-26
WW-NORTH | March | Onsite for ocu media sampling with omar and contractor | Sutton High Street Sewage Pumping Station | 2026-03-11
WW-NORTH | March | Performed station check Entered readings into SharePoint Reviewed trends | Sutton High Street Sewage Pumping Station | 2026-03-09
WW-NORTH | March | Placed pump #1 in local off to inspect suction check valve as a potential cause of pump issues. Isolated discharge valve and opened drain in order to open inspection port. - Wiped off checked and rinsed with hose. - Closed inspection port and opened discharge valve to place pump back online. - Ran pump #1 in auto manual 100% for first start up to purge any air. - Placed pump #1 in auto duty 1 - Pump #1 ran normal with no alarms Will monitor the next few cycles to make sure pump continues to run properly. | Sutton High Street Sewage Pumping Station | 2026-03-27
WW-NORTH | March | Performed station check Entered readings into SharePoint Checked pump room and reviewed trends | Sutton High Street Sewage Pumping Station | 2026-03-23
WW-NORTH | March | Responding to CMU5 W11760566 P1 VFD fault Alarm came in at 00:00hrs vfd fault and no flow alarm. Ack reset vfd and pump Run pump 100% speed - wetwell level trending down. Place p1 in duty 1 - will monitor pump cycle P1 ran full pump cycle in auto no apparent issues | Sutton High Street Sewage Pumping Station | 2026-03-26
WW-NORTH | March | Onsite to check station Review scada/trends Enter data in sharepoint Overflow kit inspection | Keswick Joe Dales Sewage Pumping Station | 2026-03-12
WW-NORTH | March | Performed station check Entered readings into SharePoint Reviewed SCADA trends | Sutton High Street Sewage Pumping Station | 2026-03-02
WW-NORTH | March | Performed station check Pump #2 air relief was leaking, isolated air relief and notified maintenance. Completed assigned EZMax work orders: - Test ran diesel generator - JHS inspection Entered readings into SharePoint | Sutton High Street Sewage Pumping Station | 2026-03-12
WW-NORTH | March | Performed station check Entered readings into SharePoint Collected davit arm for inspection | Sutton High Street Sewage Pumping Station | 2026-03-05
WW-NORTH | March | Changed pump duty levels back to original levels adjusted from December 10th 2025 to scour forcemain. High level influent alarm keeps coming in at the WRRF. Duty 1 was 1.85 start back to 1.65 stop was 1.0 now back to 1.3. Duty 2 start was 1.95 back to 1.85 and stop was 1 now back to 1.4m. Also minimum speed % on pumps was 100 now 0% | Sutton High Street Sewage Pumping Station | 2026-03-13
WW-NORTH | March | Performed station check Entered readings into SharePoint Checked pump room and reviewed trends | Sutton High Street Sewage Pumping Station | 2026-03-19
WW-NORTH | March | Performed station check Entered readings into SharePoint Checked pump room - ok | Sutton High Street Sewage Pumping Station | 2026-03-26
WW-NORTH | March | Performed station check Entered readings into SharePoint Checked pump room - ok | Sutton High Street Sewage Pumping Station | 2026-03-16
WW-NORTH | March | Replaced broken 1? fitting from air relief on pump 2. Found connection leaking at union. Adjusted connection and checked during next run cycle okay. Complete. | Sutton High Street Sewage Pumping Station | 2026-03-18
WW-NORTH | March | Completed vibration readings on both pumps and motors. | Sutton High Street Sewage Pumping Station | 2026-03-18
WW-NORTH | March | Responding to W11762134 p1 vfd fault. Alarm came in at 00:07hrs loss of prime no flow alarm vfd fault Reset all, check pump room Run pump 1 at 100% speed. Clear blockage and place in duty 1 Monitor full pump cycle in auto with pump speed set to manual 20% - no issues | Sutton High Street Sewage Pumping Station | 2026-03-27
WW-NORTH | March | Onsite to check station Review scada/trends Enter data in sharepoint TSSA contractors onsite working on generator | Keswick Joe Dales Sewage Pumping Station | 2026-03-05
WW-NORTH | March | on site for OCU media sampling | Keswick Joe Dales Sewage Pumping Station | 2026-03-11
WW-NORTH | March | Onsite to check station Review scada/trends Enter data in sharepoint No alarms | Keswick Joe Dales Sewage Pumping Station | 2026-03-23
WW-NORTH | March | Onsite to complete work orders Alert roc Review scada/trends hazardous waste removal OCU maintenance Consolidated drywell work order Diesel test run Transfer station to diesel power at 10:59hrs JHSC inspection Heat exchanger Radiator inspection Hi/low temp - came in on scada 11:12hrs Sump high level - came in on scada 11:35hrs Transfer station back to hydro power at 11:55hrs Hoist inspection Clear all alarms and reset dialer Diesel data in sharepoint Alert roc work complete | Keswick Joe Dales Sewage Pumping Station | 2026-03-04
WW-NORTH | March | Onsite to check station Review scada/trends Enter data in sharepoint | Keswick Joe Dales Sewage Pumping Station | 2026-03-02
WW-NORTH | March | Onsite to check station Review scada/trends Enter data in sharepoint | Keswick Joe Dales Sewage Pumping Station | 2026-03-09
WW-NORTH | March | station checks sharepoint data entry | Keswick Joe Dales Sewage Pumping Station | 2026-03-16
WW-NORTH | March | Onsite to check station Review scada/trends Enter data in sharepoint | Keswick Joe Dales Sewage Pumping Station | 2026-03-19
WW-NORTH | March | Onsite to check station Review scada/trends No alarms Enter data in sharepoint | Keswick Joe Dales Sewage Pumping Station | 2026-03-26
WW-NORTH | March | Onsite to check station Review scada/trends Enter data in sharepoint | Georgina No. 4 Sewage Pumping Station | 2026-03-02
WW-NORTH | March | Onsite to check station Review scada/trends Enter data in sharepoint | Georgina No. 4 Sewage Pumping Station | 2026-03-05
WW-NORTH | March | Onsite for ocu media sampling with Omar and contractor | Georgina No. 4 Sewage Pumping Station | 2026-03-11
WW-NORTH | March | Responding again to bar screen over torque fault alarm. Reset alarm and watched bar screen run a full cycle in auto. Due to higher flows adjusted run time of bar screen to run every 45 min rather than 1.5 hours. | Georgina No. 4 Sewage Pumping Station | 2026-03-10
WW-NORTH | March | Performed station check Entered readings into SharePoint Checked bar screen and bin | Georgina No. 4 Sewage Pumping Station | 2026-03-16
WW-NORTH | March | Onsite to check station Review scada/trends Enter data in sharepoint | Georgina No. 4 Sewage Pumping Station | 2026-03-19
WW-NORTH | March | Attended for wet well high level alarms Opened forcemain 1 to allow for greater flow out of wetwell - station flow increased from 150 L/s to 250 L/s and forcemain 2 pressure dropped from ~555 to ~485 kPa (forcemain 1 also ~485 kPa) Checked bar screen for overload alarm and tightened bolts on scraper blade, reset alarms and ran. | Georgina No. 4 Sewage Pumping Station | 2026-03-11
WW-NORTH | March | Onsite to complete work orders Alert roc Diesel test run - 10:08hrs transfer station to diesel power Jhsc Consolidated drywell work order -drywell flood - came in on dialer and scada 10:20hrs Building hi low temp - came in on scada 10:19hrs Check valve inspection RSP inspection Sump pit inspection Dialer test Hoist inspection Hazardous waste removal OCU maintenance Transfer station back to hydro power at 11:26hrs Diesel data in sharepoint Alert roc station back to normal operation Clear alarms/ reset dialer | Georgina No. 4 Sewage Pumping Station | 2026-03-03
WW-NORTH | March | Onsite to check station Review scada/trends Enter data in sharepoint Change barscreen run time back to every 1.5hrs from every 45 mins. Found p3 had been running continuously since yesterday. Manually swap pump duties - p1 - d1 Overflow kit inspection | Georgina No. 4 Sewage Pumping Station | 2026-03-12
WW-NORTH | March | Onsite to check station Review scada/trends Enter data in sharepoint No alarms Barscreen and screw press maintenance | Georgina No. 4 Sewage Pumping Station | 2026-03-27
WW-NORTH | March | Responding to bar screen over torque fault - reset alarm and ran manually for a full cycle - placed back in auto and watched it run in auto | Georgina No. 4 Sewage Pumping Station | 2026-03-09
WEST | March | Test | Ansnorveldt Wells 2, 3 & Reservoir | 2026-03-31
WW-NORTH | March | Onsite to check station Review scada/trends Enter data in sharepoint P1 run time higher than other pumps and running in duty 1 on arrival. Switch pump duties - p1-d3 | Georgina No. 4 Sewage Pumping Station | 2026-03-23
WW-NORTH | March | Onsite to check station Review scada/trends Enter data in sharepoint Rake barscreen | Georgina No. 4 Sewage Pumping Station | 2026-03-09
WEST | March | In to Complete Station Check and to collect bacti sample w11705480 Residuals Treated Free Grab: 1.52mg/L, Analyzer 1.48mg/L Treated total 1.89mg/L Post Reservoir Free grab 1.56mg/L, Analyzer 1.60mg/L Pre Reservoir free grab 3.50mg/L, Analyzer 3.53mg/L No issues on site | Ansnorveldt Wells 2, 3 & Reservoir | 2026-03-31
WEST | March | Test entry - IT investigation | Ansnorveldt Wells 2, 3 & Reservoir | 2026-03-31
WEST | March | -on site to respond to discharge pressure LOLO alarm, treated water free chlorine LOLO and fault alarms, and post reservoir free chlorine LOLO and fault alarms -arrived on site and found all high lifts interlocked due to max # of starts -ran pump #1 in local, once pressure was restored chlorine analyzers began reading again -PCS disabled the high lift pump max # of starts interlock, reset alarms and pumps began running in auto -discharge pressure was low from 10:43 to 11:01, informed King on call operator -verified analyzers: 11:05 - treated water FCL analyzer = 1.61 mg/L Grab = 1.55 mg/L 11:13 - post reservoir FCL analyzer = 1.40 mg/L Grab = 1.53/1.58/1.56 mg/L 11:19 - adjusted post reservoir analyzer to 1.56 mg/L based on average of 3 grabs -reviewed trends, system appears to be experiencing unusually high demand which caused high number of pump starts, put two pumps into duty 3 to reduce amount of pump starts and stops -site back to normal operation, will continue to monitor | Ansnorveldt Wells 2, 3 & Reservoir | 2026-03-05
WEST | March | In to check bladder tank pneumatic pressure. Notify ROC of running HLPs in local to maintain reasonable pressures while tanks isolated from system. Drain water from tanks, confirm pneumatic pressure: Tank 2 250kpa Tank 1 210kpa Manufacturer install instructions: set air pressure to 2psi below cut in (duty 1 start). Fill tanks to 296kPa. Place back in service and monitor. Clean Treated NTU analyzer vial (vial clarity alarm). NTU may spike due to pneumatic tank draining and running HLPs without tanks. HLP cycles appear to be 6-7 minute intervals, up from 3 minutes. No other issues. | Ansnorveldt Wells 2, 3 & Reservoir | 2026-03-12
WEST | March | In to Complete Station Check and to collect bacti sample w11637320 Residuals Treated Free Grab: 1.56mg/L, Analyzer 1.34-1.56mg/L Total 1.76mg/L Adjusted treated free from 1.34-156mg/L after multiple grabs Post Reservoir Free grab 1.50mg/L, Analyzer 1.42mg/L Pre Reservoir Free grab 3.04mg/L, Analyzer 3.36mg/L No other issues on site | Ansnorveldt Wells 2, 3 & Reservoir | 2026-03-04
WEST | March | -on site to complete station check -checked trends: all ok -entered readings in PWQ: all ok -verified inlet analyzer 08:55 -analyzer: 3.48mg/l grab: 2.78mg/l - adjusted -verified post res analyzer 09:00 -analyzer: 1.55mg/l grab: 1.40mg/l - adjusted -verified treated analyzer 09:05 -analyzer: 1.59mg/l grab: 1.36mg/l - adjusted -total grab: 1.57mg/l -cleaned NTU analyzer -equipment all ok | Ansnorveldt Wells 2, 3 & Reservoir | 2026-03-02
WEST | March | In to Complete Station Check Residuals Treated Free Grab: 1.42mg/L, Analyzer 1.48mg/L Post Reservoir Free grab 1.43mg/L, Analyzer 1.39mg/L No other issues on site | Ansnorveldt Wells 2, 3 & Reservoir | 2026-03-16
WEST | March | -on site for station check -checked trends: all ok -entered readings in PWQ: all ok -verified analyzer -inlet 08:25: 2.63mg/l grab: 2.80mg/l - adjusted -post res 08:30: 1.41mg/l grab: 1.39mg/l -treated free 08:35: 1.38mg/l grab: 1.36mg/l -total grab: 1.52mg/l -equipment all ok | Ansnorveldt Wells 2, 3 & Reservoir | 2026-03-20
WEST | March | In to Complete Station Check Residuals Treated Free Grab: 1.42mg/L, Analyzer 1.49mg/L Post Reservoir Free grab 1.46mg/L, Analyzer 1.52mg/L Pre Reservoir free grab 3.42mg/L, Analyzer 3.33mg/L No issues on site | Ansnorveldt Wells 2, 3 & Reservoir | 2026-03-27
WEST | March | In to Complete Station Check and complete weekly BacT sample - W1165875 Residuals Treated Free Grab: 1.34 mg/L, Analyzer 1.37mg/L Post Reservoir Free grab 1.33mg/L, Analyzer 1.39mg/L Pre Reservoir free grab 2.90 mg/L, Analyzer 2.90mg/L Topped up hypo tanks, 33 -> 52 L No other issues on site | Ansnorveldt Wells 2, 3 & Reservoir | 2026-03-11
WEST | March | -on site to complete work orders -informed ROC of work -completed Pumps 2 and 3 Strainer Inspection -completed Turbidity Analyzer TU5300 Maintenance and Calibration -cleaned turbidimeter vial, verified analyzer - passed -completed Siemens Depolox 5/Micro 2000 Chlorine Analyzer Maintenance -cleaned analyzers, checked electrolyte and grit sand -verified analyzers after maintenance: 10:00 - post reservoir FCL analyzer = 1.46 mg/L Grab = 1.46 mg/L 10:07 - reservoir inlet FCL analyzer = 3.43 mg/L Grab = 3.24/3.20/3.16 mg/L 10:14 - adjusted reservoir inlet analyzer to 3.20 mg/L based on average of 3 grabs 10:16 - treated water FCL analyzer = 1.40 mg/L Grab: = 1.45 mg/L -completed Pressure Regulating Valve Maintenance -completed JHSC Health and Safety Inspection -cleaned and tested well # 2 discharge air valve -power systems contractor on site for annual generator maintenance, performing load test on generator 10:32 - contractor started generator, generator hours = 312 hours 18 minutes -reservoir inlet chlorine hihi alarm came in, verified analyzer: 11:51 - reservoir inlet FCL analyzer = 4.13 mg/L Grab = 3.28/3.20/3.16 mg/L 12:05 - adjusted reservoir inlet analyzer to 3.21 mg/L based on average of 3 grabs 12:08 - generator hours = 313 hours 54 minutes -CMS on site to continue generator maintenance | Ansnorveldt Wells 2, 3 & Reservoir | 2026-03-03
WEST | March | In to Complete Station Check Residuals Treated Free Grab: 1.41mg/L, Analyzer 1.40mg/L Post Reservoir Free grab 1.35mg/L, Analyzer 1.40mg/L No other issues on site | Ansnorveldt Wells 2, 3 & Reservoir | 2026-03-06
WEST | March | In to Complete Station Check Residuals Treated Free Grab: 1.25mg/L, Analyzer 1.38mg/L Post Reservoir Free grab 1.19mg/L, Analyzer 1.32mg/L No other issues on site | Ansnorveldt Wells 2, 3 & Reservoir | 2026-03-09
WEST | March | On site for annual generator pm. | Ansnorveldt Wells 2, 3 & Reservoir | 2026-03-03
WEST | March | Disable the Max No Starts for High Lift PMP1-PMP3 based on request from OIC. (Setting was 20/hr - something in the field may be causing surplus of starts - will leave disabled until told otherwise) | Ansnorveldt Wells 2, 3 & Reservoir | 2026-03-04
WEST | March | -on site for station check -checked trends: all ok -entered reading in PWQ -verified analyzer -inlet 08:50: 2.77mg/l grab: 3.12mg/l - adjusted -post res08:45: 1.64mg/l grab: 1.54mg/l - adjusted -treated free 08:40: 1.56mg/l grab: 1.52mg/l - adjusted -total grab: 1.76mg/l -equipment all ok | Ansnorveldt Wells 2, 3 & Reservoir | 2026-03-23
WEST | March | -on site to complete station check and weekly bacti W11672769 -checked trends: all ok -entered reading in PWQ : all ok -verified analzyser -inlet 08:40: 2.58mg/l grab 2.62mg/l -post res 08:45: 1.34mg/l grab: 1.31mg/l -treated free: 08:50: 1.48 grab: 1.33mg/l - adjusted -total grab: 1.53mg/l -increased dosage factor 150 -155% -cleaned NTU analyzer -equipment all ok | Ansnorveldt Wells 2, 3 & Reservoir | 2026-03-18
CENTRAL | March | System testing NOT real please ignore Revision 1 | Aurora (East) First Commerce Elevated Tank | 2026-03-30
WEST | March | In to Complete Station Check and to collect bacti sample w11690144 Residuals Treated Free Grab: 1.53mg/L, Analyzer 1.53mg/L Total 1.81mg/L Post Reservoir Free grab 1.54mg/L, Analyzer 1.53mg/L Pre Reservoir Free grab 3.12mg/L, Analyzer 3.03mg/L No other issues on site | Ansnorveldt Wells 2, 3 & Reservoir | 2026-03-25
WEST | March | In to Complete Station Check Residuals Treated Free Grab: 1.36 mg/L, 1.43 Analyzer mg/L Treated total grab 1.53 mg/L Post Reservoir Free grab 1.40 mg/L, Analyzer 1.38mg/L Pre Reservoir free grab mg/L, Analyzer mg/L | Ansnorveldt Wells 2, 3 & Reservoir | 2026-03-13
CENTRAL | March | Onsite for station check/collect sample- WO# W11657608: Sample results (08:10): Free- 0.03, Total- 2.72 * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Aurora (East) First Commerce Elevated Tank | 2026-03-11
CENTRAL | March | This is a test | Aurora (East) First Commerce Elevated Tank | 2026-03-31
CENTRAL | March | Onsite for station check/collect sample- WO# W11690776: Sample results (11:22): Free- 0.09, Total- 2.76 * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Aurora (East) First Commerce Elevated Tank | 2026-03-25
CENTRAL | March | Onsite to complete assigned work orders- informed ROC: H/S inspection Low temp alarms Ventilation inspection Heat trace system inspection Portable generator test/inspection Manual valve exercise/inspection Depolox analyzer maintenance Dehumidifier inspection Performed station housekeeping Station/equipment- Ok | Aurora (East) First Commerce Elevated Tank | 2026-03-19
CENTRAL | March | Onsite for station check/collect sample- WO# W11673476: Treated sample results (08:20): Free- 0.08, Total- 2.84 * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Aurora (East) First Commerce Elevated Tank | 2026-03-18
CENTRAL | March | Restarted the Operator Interface Terminal due to Windows Operating System software updates. | Aurora (East) Wellington Pumping Station | 2026-03-30
CENTRAL | March | Onsite for station check/collect samples- WO# W11638288, W11638258: Sample results (08:12): Free- 0.06, Total- 2.80 * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Aurora (East) First Commerce Elevated Tank | 2026-03-04
CENTRAL | March | On site for station check. 14:33 activated Aurora east zone duty. Well 5 forward low flow alarm triggered on start up but checkvalve opened during pump ramp up and alarm cleared. Pumps 5 running at 154.9 l/s and P4 in standby. Rotated to pump 4 in duty to compare electrical draw between both pumps. Found sump pumps in manual off. Placed back in auto and tested with no issues. Entered data into process sheets. No issues found. | Aurora (East) Wellington Pumping Station | 2026-03-02
CENTRAL | March | Vibration readings | Aurora (East) Wellington Pumping Station | 2026-03-12
CENTRAL | March | Onsite to complete work orders: 08:40 hrs. Generator inspection and test run. Run hours: 373.3 to 374.8. Fuel level: 1761 L to 1726 L. Pre- inspection. Oil level ok. Coolant level ok. Recirculation pump ok. Battery ok. 08:59 Placed pump 4 and 5 in manual off and notified ROC of work being done. 09:01 Initiated generator test. 09:21 Ran well 5 in manual. Pump and motor inspection ok. Sump pit inpsection ok. Building flood alarm remains OOS with previous work order created W11692965 09:37 Low building temp alarm. Triggered and cleared alarm. JHSC inspection ok. 10:20 placed pump 5 manual off. 10:30 completed generator run with no issues. Ventillation system inspection. Generator room ef-1 tripped after generator run. Reset. No other issues found on site. | Aurora (East) Wellington Pumping Station | 2026-03-10
CENTRAL | March | On site for station check. Pump 4 running in duty at 165 l/s. Pump 5 in standby. Entered data into process sheets. No issues found. | Aurora (East) Wellington Pumping Station | 2026-03-06
CENTRAL | March | On site for station check. Pump 4 and 5 in standby. Entered data into process sheets. No issues found. | Aurora (East) Wellington Pumping Station | 2026-03-13
CENTRAL | March | On site for station check. Pump 4 and 5 in standby. Entered data into process sheets. No issues found. | Aurora (East) Wellington Pumping Station | 2026-03-09
CENTRAL | March | On site for station check. 07:38 Pump 5 running at 164 l/s. Pump 4 in standby. Entered data into process sheets. No other issues found. | Aurora (East) Wellington Pumping Station | 2026-03-27
CENTRAL | March | On site for station check. Pump 4 and 5 in standby. Entered data into process sheets. No other issues found. | Aurora (East) Wellington Pumping Station | 2026-03-23
CENTRAL | March | Check leaking backflow Backflow preventer passed, flushed water out of the dump port Not leaking | Aurora (East) Wellington Pumping Station | 2026-03-23
CENTRAL | March | On site for station check. Pump 4 and 5 in standby. Entered data into process sheets. Found small drip on backflow prevention assembly. Created W11737138. No other issues found. | Aurora (East) Wellington Pumping Station | 2026-03-16
CENTRAL | March | On site for station check. Pump 4 and 5 in standby. Entered data into process sheets. No other issues found. | Aurora (East) Wellington Pumping Station | 2026-03-20
CENTRAL | March | Informed ROC. Onsite to install and setup ultrasonic flowmeter. Informed ROC, armed the building and left the site. | Aurora (North) Orchard Heights Elevated Tank | 2026-03-30
CENTRAL | March | On site to investigate malfunctioning building flood alarm. ROC notified. Found float switch to be faulty. Replaced float and tested with assistance from Ian Williams from PCS. Building flood alarm now functional. Work completed. Building flood alarm acknowledged and reset. ROC notified. | Aurora (East) Wellington Pumping Station | 2026-03-16
CENTRAL | March | Onsite for station check/collect samples- WO# W11706313, W11706283: Sample results (13:28): Free- 0.09, Total- 2.84 * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Aurora (North) Orchard Heights Elevated Tank | 2026-03-31
CENTRAL | March | Comprehensive House Cleaning PM: completed | Aurora (North) Orchard Heights Elevated Tank | 2026-03-18
CENTRAL | March | Onsite for station check/collect samples- WO# W11638288, W11638258: Sample results (13:12): Free- 0.07, Total- 3.02 * Adjusted total analyzer from 2.80 to 3.02 based on multiple grabs (3.02, 3.02, 3.04) * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Aurora (North) Orchard Heights Elevated Tank | 2026-03-04
CENTRAL | March | Onsite to complete assigned work orders- informed ROC: H/S inspection Low/high temp test Sump system inspection Depolox analyzer maintenance Manual valve exercise/inspection Drain valve exercise/inspection Station/equipment- Ok | Aurora (North) Orchard Heights Elevated Tank | 2026-03-12
CENTRAL | March | Onsite for station check/collect sample- WO W11673476: Sample results (13:45): Free- 0.08, Total- 2.90 * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Aurora (North) Orchard Heights Elevated Tank | 2026-03-18
CENTRAL | March | Onsite for station check/collect sample- WO# W11690776: Sample results (09:00): Free- 0.09, Total- 2.82 * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Aurora (North) Orchard Heights Elevated Tank | 2026-03-25
CENTRAL | March | Onsite for station check/collect sample- WO# W11657608: Treated sample results (14:10): Free- 0.04, Total- 2.90 * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Aurora (North) Orchard Heights Elevated Tank | 2026-03-11
CENTRAL | March | Restarted the Operator Interface Terminal due to Windows Operating System software updates. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2026-03-30
CENTRAL | March | TESTING NEW MAXIMO SYSTEM NOT REAL ENTRY PLEASE IGNORE REVISION 1 REVISION 2 | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2026-03-28
CENTRAL | March | Onsite to complete work orders: Notified ROC of work being done. Topped up ammonia tank 2 from 222 L to 1270L. Joint health and safety inspection. Found ammonia room, chlorine vestibule and reservoir basement emergency lights OOS. Notified team lead. Sump pit inspection. Dehumidifier cleaning and inpsection. Ammonia peristaltic pump 1 and pump 2 inspection. Pump 1 max pump rate 1520 ml/min. P2 max pump rate 1460 ml/min. Adjusted SCADA setpoints to match. 11:22 deactivated chloramine dosing system. 11:41 Chlorine leak detection test. Gas leak Alarm triggered using tester. Halogen shut off system actuated. Bank 2 actuators B shorted and D timed out. D failed to close. Retested and all acutators worked without issues. 11:47 Repopened chlorine cylinders and placed chemical systems back in auto. No issues remain. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2026-03-05
CENTRAL | March | On site for station check and reservoir sampling. W117705787 and W11705378. Reservoir flow at 358 l.s and rechloramination boosting is on. Reservoir level at 46%. Topped up ammonia tank 1. Replaced chemscan Ammonia reagent. Verified residuals (mg/l): 10:12 Pre-injection/outlet grabs: Free grab: 0.08. Depolox 5: 0.05. Total grab: 1.64 Micro2000: 1.61 Chemscan: 1.61. Monochloramine grab: 1.51. Chemscan: 1.59. Free ammonia grab: 0.07. Chemscan: 0.08. Total ammonia grab: 0.37. Chemscan: 0.39. Nitrite: 0.003. temperature: 6.6 celsius. 10:23 Post-injection chlorine grabs. Free grab: 0.03. Depolox 5: 0.0\3. Total grab: 3.26 Micro2000: 3.26. Chemscan: 3.09. Monochloramine grab: 2.73. Chemscan: 2.91. Adjsuted chemscan to match grab. Free ammonia grab: 0.04. Chemscan: 0.02. Total ammonia grab: 0.58. Chemscan: 0.56. Recorded data into process sheets. No issues found on site. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2026-03-31
CENTRAL | March | #NAME? | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2026-03-05
CENTRAL | March | On site for station check and sampling. W11656795. 11:36 outlet flow at 414 L/s. Rechloramination boosting on. Reservoir level at 51%. Verified residuals (mg/l): 11:45 Pre-injection/outlet grabs. Collected sample. Free grab: 0.08. Depolox 5: 0.06. Total grab: 1.64. Micro2000: 1.54 Chemscan: 1.60. Monochloramine grab: 1.54. Chemscan: 1.58. Free ammonia grab: 0.07. Chemscan: 0.08. Total ammonia grab: 0.37. Chemscan: 0.39. 11:55 Post-injection chlorine grabs. Free grab: 0.02. Depolox 5: 0.04. Total grab: 3.26 Micro2000: 3.19. Chemscan: 3.31. Monochloramine grab: 2.76. Chemscan: 2.90. Free ammonia grab: 0.01. Chemscan: 0.04. Total ammonia grab: 0.56. Chemscan: 0.58. Calculated ammonia dosage is since March 9th is 0.18 mg/l. Total ammonia dose calculated on SCADA is 0.29. Post injection ammonia grab: 0.01 while ammonia pump 2 is running. 12:10 rotated to ammonia pump 1. Disabled duty auto rotate. 12:30 retested free ammonia on post injection. Grab: 0.05. Chemscan: 0.05. Completed drawdowns for both pumps. p1 max drawdown 1490 ml/min. Adjusted SCADA to match from 1520 ml/min. Will re-evaluate next station check. Ammonia tank mixer 1 switch remains OOS. No other new issues found on site. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2026-03-11
CENTRAL | March | On site for station check. 10:29 outlet flow at 0 L/s. Rechloramination boosting off. Reservoir level at 64%. Topped up ammonia tank 2. Topped up micro2000 pre injection total analyzer acetate reagent. Verified residuals (mg/l): 10:50 Pre-injection/outlet grabs. Collected sample. Free grab: 0.03. Depolox 5: 0.06. Total grab: 1.65 Micro2000: 1.58 Chemscan: 1.65. Monochloramine grab: 1.55. Chemscan: 1.59. Free ammonia grab: 0.07. Chemscan: 0.07. Total ammonia grab: 0.37. Chemscan: 0.44. 11:02 Post-injection chlorine grabs. Free grab: 0.03. Depolox 5: 0.04. Total grab: 3.24 Micro2000: 3.20. Chemscan: 3.32. Monochloramine grab: 2.85. Chemscan: 3.03. Adjusted to match grab. Free ammonia grab: 0.08. Chemscan: 0.07. Total ammonia grab: 0.64. Chemscan: 0.59. With ammonia p1 in duty calculated ammonia dosage is 0.28 mg/l. SCADA Ammonia dose is 0.29 mg/l. Rotated to ammonia pump 2 in duty 1 and will evaluate ammonia p2 performance on next sation check . Ammonia tank mixer 1 switch remains OOS. No other new issues found on site. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2026-03-13
CENTRAL | March | On site for station check. 12:23 outlet flow at 329 L/s. Rechloramination boosting on. Reservoir level at 48%. Verified residuals (mg/l): 12:25 Pre-injection/outlet grabs. Collected samples. Free grab: 0.02 Depolox 5: 0.06. Total grab: 1.57. Micro2000: 1.59 Chemscan: 1.61. Monochloramine grab: 1.49 Chemscan: 1.58. Free ammonia grab: 0.07. Chemscan: 0.09. Total ammonia grab: 0.37. Chemscan: 0.41. 12:30 Post-injection chlorine grabs. Free grab: 0.04/0.04/0.05. Depolox 5: 0.16. Adjusted to match grab average Total grab: 3.30/3.26/3.26. Micro2000: 3.18. Chemscan: 3.29. adjusted to match grab average. Monochloramine grab: 2.80 Chemscan: 2.78. Free ammonia grab: 0.05. Chemscan: 0.07. Total ammonia grab: 0.60. Chemscan: 0.61. Ammonia tank mixer 1 switch remains OOS. No other new issues found on site. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2026-03-06
CENTRAL | March | On site for station check. 11:16 outlet flow at 0 L/s. Rechloramination boosting off. Reservoir level at 87%. Topped up ammonia tank 1. Generated W11700364 to replaced the ammonia mixer switch as its no longer working to turn off the mixer. Unplugged the mixer from recepticle once mixing was completed. received 20 chlorine cylinders and removed 20 empty cylinders. Verified residuals (mg/l): 11:35 Pre-injection/outlet grabs. Free grab: 0.09 Depolox 5: 0.06. Total grab: 1.62/1.61/1.62 Micro2000: 1.70 Chemscan: 1.62. Adjusted micro2000 to match grab averages. Monochloramine grab: 1.54 Chemscan: 1.60. Free ammonia grab: 0.10. Chemscan: 0.06. Total ammonia grab: 0.41. Chemscan: 0.35. 11:42 Post-injection chlorine grabs. Rechloramination has stopped dosing. Free grab: 0.06. Depolox 5: 0.01. Total grab: 1.62. Micro2000: 1.67. Chemscan: 1.67 Monochloramine grab: 1.57 Chemscan: 1.58. Free ammonia grab: 0.07. Chemscan: 0.11. Total ammonia grab: 0.38. Chemscan: 0.50. No other new issues found on site. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2026-03-02
CENTRAL | March | On site for station check and sampling. W11637647 and W11637218. 10:14 outlet flow at 400 L/s. Rechloramination boosting on. Reservoir level at 49%. Verified residuals (mg/l): 10:18 Pre-injection/outlet grabs. Collected samples. Free grab: 0.07 Depolox 5: 0.06. Total grab: 1.75. Micro2000: 1.68 Chemscan: 1.71. Monochloramine grab: 1.58 Chemscan: 1.64. Free ammonia grab: 0.08. Chemscan: 0.07. Total ammonia grab: 0.39. Chemscan: 0.37. 10:38 Post-injection chlorine grabs. Free grab: 0.03. Depolox 5: 0.07. Total grab: 3.30. Micro2000: 3.23. Chemscan: 3.29. Monochloramine grab: 2.86 Chemscan: 2.95. Free ammonia grab: 0.04. Chemscan: 0.05. Total ammonia grab: 0.61. Chemscan: 0.59. Ammonia tank mixer 1 switch remains OOS. No other new issues found on site. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2026-03-04
CENTRAL | March | On site for station check. Replaced chlorine cylinder bank B with Joe DeMarco. Topped up ammonia tank 1, 222L to 12767 L. 13:53 outlet flow at 412 L/s. Rechloramination boosting on. Reservoir level at 55%.. Verified residuals (mg/l): 13:54 Pre-injection/outlet grabs. Collected samples. Free grab: 0.10 Depolox 5: 0.06. Total grab: 1.63. Micro2000: 1.66 Chemscan: 1.60. Monochloramine grab: 1.55. Chemscan: 1.58. Free ammonia grab: 0.07. Chemscan: 0.08. Total ammonia grab: 0.37. Chemscan: 0.40. 14:02 Post-injection chlorine grabs. Free grab: 0.03. Depolox 5: 0.04. Total grab: 3.24 Micro2000: 3.29. Chemscan: 3.31. Monochloramine grab: 2.82. Chemscan: 2.79. Free ammonia grab: 0.03. Chemscan: 0.05. Total ammonia grab: 0.59. Chemscan: 0.59. Ammonia tank mixer 1 switch remains OOS. No other new issues found on site. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2026-03-09
CENTRAL | March | On site for station check and to collect sample. W11672681. 12:28 outlet flow at 450 L/s. Rechloramination boosting on. Reservoir level at 54%. Verified residuals (mg/l): 12:41 Pre-injection/outlet grabs. Collected sample. Free grab: 0.03. Depolox 5: 0.05. Total grab: 1.62 Micro2000: 1.63 Chemscan: 1.61. Monochloramine grab: 1.51. Chemscan: 1.57. Free ammonia grab: 0.12. Chemscan: 0.10. Total ammonia grab: 0.41. Chemscan: 0.40. 12:53 Post-injection chlorine grabs. Free grab: 0.06. Depolox 5: 0.04. Total grab: 3.26 Micro2000: 3.28. Chemscan: 3.31. Monochloramine grab: 2.77. Chemscan: 2.70 Free ammonia grab: 0.02. Chemscan: 0.06. Total ammonia grab: 0.57. Chemscan: 0.62. Adjusted chlorine/ammonia ratio from 4.8 to 4.7. No issues found on site. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2026-03-18
CENTRAL | March | Replaced left chlorine cylinder bank with Kyle Rae. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2026-03-16
CENTRAL | March | On site for station check. 10:20 outlet flow at 389 L/s. Rechloramination boosting off. Reservoir level at 55%. Topped up ammonia tank 1. Topped up chemscan sulphuric acid and potassium iodine reagent. Verified residuals (mg/l): 11:07 Pre-injection/outlet grabs. Collected sample. Free grab: 0.03. Depolox 5: 0.06. Total grab: 1.62 Micro2000: 1.67 Chemscan: 1.59. Monochloramine grab: 1.51. Chemscan: 1.59. Free ammonia grab: 0.08. Chemscan: 0.07. Total ammonia grab: 0.37. Chemscan: 0.40. 11:20 Post-injection chlorine grabs. Free grab: 0.04. Depolox 5: 0.04. Total grab: 3.24 Micro2000: 3.23. Chemscan: 3.10. Monochloramine grab: 2.79. Chemscan: 2.82 Free ammonia grab: 0.11. Chemscan: 0.06 Adjusted to match grabs. Total ammonia grab: 0.66. Chemscan: 0.57. Adjusted to match grabs. Adjusted chlorine/ammonia ratio from 4.7 to 4.8. With ammonia p2 in duty calculated ammonia dosage is 0.28 mg/l. SCADA Ammonia dose is 0.29 mg/l. No issues found with ammonia pumps. Placed ammonia pump duty back to all stop rotate setting. Kyle Rae on site to repair ammonia tank mixer 1 switch. No other new issues found on site. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2026-03-16
CENTRAL | March | 21:34 ROC informed me that chlorine booster pump 2 failed to start. Roc attempted to restart with no luck. 21:42 remotely restarted chlorine train 2 with no issues. Dosing appears normal. Notified Roc.. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2026-03-21
CENTRAL | March | On site for station check. 07:38 outlet flow at 0 L/s. Rechloramination boosting of. Reservoir level at 87%. Aurora Duty has just activated and station flow will be starting shortly once vavle opens. Topped up ammonia tank 2. Topped up micro2000 KI and acetate reagents for pre and post injection analyzers. Verified residuals (mg/l): 07:41 Pre-injection/outlet grabs. Collected sample. Free grab: 0.07. Depolox 5: 0.06. Total grab: 1.60 Micro2000: 1.52 Chemscan: 1.61. Monochloramine grab: 1.45. Chemscan: 1.54. Free ammonia grab: 0.08. Chemscan: 0.06. Total ammonia grab: 0.36. Chemscan: 0.38. 08:38 Post-injection chlorine grabs. Free grab: 0.05. Depolox 5: 0.04. Total grab: 3.24 Micro2000: 3.26. Chemscan: 3.31. Monochloramine grab: 2.84. Chemscan: 2.90. Free ammonia grab: 0.06. Chemscan: 0.09. Adjusted to match grab. Total ammonia grab: 0.66. Chemscan: 0.66. No issues found on site. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2026-03-20
CENTRAL | March | on site to troubleshoot the uncommanded starts and the pumps inability to start locally. initially we found that the contactor was making a very audible buzzing noise. i took the contactor out and found that there was a damaged part inside it and binding the movement of the contactor and not allowing it to close. i repaired the part and tested it with Donny. no issues were present during our testing and pump has run for approximately 20mins. under direction of oic | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2026-03-27
CENTRAL | March | Onsite to receive delivery of ammonia sulphate. 48 bags delivered. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2026-03-17
CENTRAL | March | Onsite to test chlorine booster pump 2. Unconnected stop alarm triggered trying to run pump remotely. Pump won?t start locally. 11:50 Put chlorine pump 1 back in service and notified roc. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2026-03-26
CENTRAL | March | Onsite you complete work orders: 13:17 Placed chlorine/ammonia dosing system offline. Aurora central duty is currently not active and outlet flow is 0 l/s. Siemens depolox 5 and micro2000 inspection. chemscan analyzer maintenance. No issues found. 13:40 verified analyzers: Pre injection free: 0.02. Analyzer: 0.06. Pre injection total: 1.65. Micro2000: 1.68. Chemscan: 1.67. 13:45 Post injection free: 0.02. Analyzer: 0.01. Post injection total: 1.66. Micro2000: 1.65. Chemscan: 1.65. 13:57 Chemical storage tank inspection. Tested flood alarm. Chlorine system inspection. Tested vacuum. Placed all systems back to auto once complete. No new issues found. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2026-03-05
CENTRAL | March | On site for station check. 10:20 outlet flow at 0 L/s. Rechloramination boosting of. Reservoir level at 51%. Topped up ammonia tank 1. Changed chlorine cylinder bank 2 with Ben Hess. 11:00 With Ben Hess and Chris scott tested chlorine dosing system and lo vaccum alarms. Found alarms failing to trigger. Ran chlorine sytem to storm and not into system after placing dechlorination pucks at outlet. Off gassing at outlet triggerd chlorine briefly triggered chlorinel leak detection hihi alarm with detector spiking at 2.90 PPM. Verified chlorine booster pump 2 running with no issues. Verified residuals (mg/l): 12:05 Pre-injection/outlet grabs. Collected sample. Free grab: 0.03. Depolox 5: 0.05. Total grab: 1.62 Micro2000: 1.52 Chemscan: 1.65. Monochloramine grab: 1.56. Chemscan: 1.61. Free ammonia grab: 0.06.. Chemscan: 0.07. Total ammonia grab: 0.37 Chemscan: 0.37. 12:15 Post-injection chlorine grabs. Free grab: 0.04. Depolox 5: 0.00. Total grab: 1.63 Micro2000: 1.65. Chemscan: 1.65 Monochloramine grab: 1.54. Chemscan: 1.56. Free ammonia grab: 0.08. Chemscan: 0.12. Total ammonia grab: 0.38. Chemscan: 0.53. adjusted to match grab. No issues found on site. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2026-03-23
CENTRAL | March | 13:52 received call from roc (Christian). Chlorine pump 2 failed to start. Station unable to chlorine boost. 13:58 attempted to start remotely. Failed again. 13:59 placed chlorine train 1 back in service. Lowered chlorine target setpoint to 3.00 mg/L as chlorinate is smaller. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2026-03-25
CENTRAL | March | On site for station check and reservoir sampling. W11690064 08:16 outlet flow at 456 L/s. Rechloramination boosting on. Reservoir level at 44%. Verified residuals (mg/l): 08:35 Pre-injection/outlet grabs. Collected sample. Free grab: 0.05. Depolox 5: 0.05. Total grab: 1.68 Micro2000: 1.72 Chemscan: 1.66. Monochloramine grab: 1.54. Chemscan: 1.59. Free ammonia grab: 0.0. Chemscan: 0.07. Total ammonia grab: 0.37 Chemscan: 0.38. 08:45 Post-injection chlorine grabs. Free grab: 0.07. Depolox 5: 0.03. Total grab: 3.24/3.26/3.26 Micro2000: 3.06. Chemscan: 3.20 Adjusted micro2000 to match grab. Monochloramine grab: 2.80. Chemscan: 2.60. Adjusted chemscan to match grab. Free ammonia grab: 0.02. Chemscan: 0.08. Adjusted chemscan to match grab. Total ammonia grab: 0.58. Chemscan: 0.56. No issues found on site. Recorded readings in process sheets. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2026-03-25
CENTRAL | March | On site for station check and to collect sample. W11672681. 12:28 outlet flow at 450 L/s. Rechloramination boosting on. Reservoir level at 54%. Topped up ammonia tank 2. Verified residuals (mg/l): 12:41 Pre-injection/outlet grabs. Collected sample. Free grab: 0.03. Depolox 5: 0.05. Total grab: 1.62 Micro2000: 1.63 Chemscan: 1.61. Monochloramine grab: 1.51. Chemscan: 1.57. Free ammonia grab: 0.12. Chemscan: 0.10. Total ammonia grab: 0.41. Chemscan: 0.40. 12:53 Post-injection chlorine grabs. Free grab: 0.06. Depolox 5: 0.04. Total grab: 3.26 Micro2000: 3.28. Chemscan: 3.31. Monochloramine grab: 2.77. Chemscan: 2.70 Free ammonia grab: 0.02. Chemscan: 0.06. Total ammonia grab: 0.57. Chemscan: 0.62. Adjusted chlorine/ammonia ratio from 4.8 to 4.7. No issues found on site. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2026-03-18
CENTRAL | March | 14:20 onsite to respond to chlorine booster pump 1 failing to start. Stopped all chemical dosing. Valved chlorinator 2 to chlorine booster pump 1. Changed SCADA chlorine cfg: to booster pump 1 to chlorinator 2 and restarted dosing. Adjusted chlorine target setpoint to 3.30. Placed chlorine booster p2 in local. Created work order for maintenance to investigate chlorine booster pump 2. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2026-03-25
CENTRAL | March | On site for station check and sampling. W117705787 and W11705378.. 15:00 Tower level at 46% and draining at 0 l/s. 15:01 Verified chlorine analyzer (mg/l) and collected sample. Free chlorine grab: 0.04. Analyzer: 0.05. Total chlorine grab: 1.98. Analyzer: 1.91. Monochloramine: 1.93. Free ammonia: 0.06. Total ammonia: 0.44. Nitrite: 0.004. Replaced micro 2000 analyzer acetate reagent. No issues on site. | Aurora (Southwest) Allenvale Elevated Tank | 2026-03-31
CENTRAL | March | On site to investigate ammonia mixer switch. Found switch cover plate to be damaged. Replaced cover plate and tested operation. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2026-03-16
CENTRAL | March | On site for station check and chlorine booster pump 2 testing with Tyler Z. 09:26 Notified ROC to place bathurst/wellington valve manual off. Set chlorine train and valving back to normal ops mode to allow tyler to test/repair chlorine pump 2. No flow from reservoir and rechloramination boosting is off. Reservoir level at 52%. Topped up ammonia tank 2. Verified residuals (mg/l): 10:15 Pre-injection/outlet grabs: Free grab: 0.06. Depolox 5: 0.05. Total grab: 1.65 Micro2000: 1.65 Chemscan: 1.58. Monochloramine grab: 1.53. Chemscan: 1.61. Free ammonia grab: 0.08. Chemscan: 0.07. Total ammonia grab: 0.38 Chemscan: 0.40. 10:30 Post-injection chlorine grabs. Free grab: 0.02. Depolox 5: 0.00. Total grab: 1.65 Micro2000: 1.69. Chemscan: 1.65. Monochloramine grab: 1.53. Chemscan: 1.62. Free ammonia grab: 0.07. Chemscan: 0.09. Total ammonia grab: 0.37. Chemscan: 0.48. Adjusted to match grab. 10:52 placed Bathurst/wellington valve back to auto, placed chlorine train 1 back in service. Set chlorine dosage point to 2.85 mg/l. 11:22 hours. Tyler repaired contactor to chlorine booster pump 2. Placed back in servcie. Chlorine train 1 back to manual off in standby. Chlorine train dosing in normal mode. Chlorine dosage setpoint back to 3.30 mg/l. No issues found on site. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2026-03-27
CENTRAL | March | -Finished the following work orders *Tested low temp alarm *Valve exercises *Depolox analyzer maintenance *Tested portable generator *Heat trace inspection *H&S inspection | Aurora (Southwest) Allenvale Elevated Tank | 2026-03-05
CENTRAL | March | On site for station check and sampling. W11637647 and W11637218.. 11:28 Tower level at 56% and draining. 11:34 Verified chlorine analyzer (mg/l) and collected samples. Free chlorine grab: 0.05. Analyzer: 0.01. Total chlorine grab: 2.16 analyzer: 2.19. Nitrite grab: 0.003 Free ammonia: 0.07 Total ammonia: 0.46. Monochloramine: 1.98. Temperature: 4.3 celsius. pH: 8.03. No issues on site. | Aurora (Southwest) Allenvale Elevated Tank | 2026-03-04
CENTRAL | March | On site for station check and sampling. W11656795. 13:38 Tower level at 60% and draining. 11:42 Verified chlorine analyzer (mg/l) and collected sample. Free chlorine grab: 0.03. Analyzer: 0.00. Total chlorine grab: 2.17. Analyzer: 2.12. No issues on site. | Aurora (Southwest) Allenvale Elevated Tank | 2026-03-11
CENTRAL | March | On site for station check and sampling. W11690064. 11:03 Tower level at 63% and draining at 0 l/s. 11:10 Verified chlorine analyzer (mg/l) and collected sample. Free chlorine grab: 0.03. Analyzer: 0.05. Total chlorine grab: 2.12. Analyzer: 2.09. Monochloramine: 1.94. Free ammonia: 0.06. Total ammonia: 0.44. No issues on site. | Aurora (Southwest) Allenvale Elevated Tank | 2026-03-25
CENTRAL | March | On site for station check and sampling. W11672681. 09:27 Tower level at 60% and draining at 5.2 l/s. 09:35 Verified chlorine analyzer (mg/l) and collected sample. Free chlorine grab: 0.08. Analyzer: 0.07. Total chlorine grab: 2.13. Analyzer: 2.13. Monochloramine: 1.97. Free ammonia: 0.06. Total ammonia: 0.45. Nitrite: 0.004 pH: 7.99 Temp: 3.8 celsius. No issues on site. | Aurora (Southwest) Allenvale Elevated Tank | 2026-03-18
CENTRAL | March | Onsite for station check/collect samples- WO# W11706313, W11706283: Sample results (12:25): Free- 0.09, Total- 3.00 * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Aurora Orchard Heights Pumping Station & Reservoir | 2026-03-31
CENTRAL | March | Onsite for station check: Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Aurora Orchard Heights Pumping Station & Reservoir | 2026-03-02
CENTRAL | March | Restarted the Operator Interface Terminal due to Windows Operating System software updates. | Aurora Orchard Heights Pumping Station & Reservoir | 2026-03-30
CENTRAL | March | Onsite for station check: Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Aurora Orchard Heights Pumping Station & Reservoir | 2026-03-06
CENTRAL | March | Onsite to complete assigned work orders- informed ROC: H/S inspection Low/high temp test Ventilation inspection Depolox analyzer maintenance Pump and motor inspection Manual valve exercise/inspection Dehumidifier inspection Generator test: Start time- 09:46 Stop time- 10:53 Start hours- 205.8 Stop hours- 206.9 Start fuel- 2,460 L (85cm) Stop fuel- 2,450 L (84cm) Pre inspection completed prior to generator test run- no abnormalities * Generator operating stats (under load P4): 1798 rpm 603 V 60 Hz 58 A 444 kpa- oil pressure 87 C- coolant temp Placed generator back into auto once test run completed- no abnormalities during test/inspection * Station/equipment- Ok | Aurora Orchard Heights Pumping Station & Reservoir | 2026-03-12
CENTRAL | March | Onsite for station check/collect samples- WO# W11638288, W11638258: Sample results (12:30): Free- 0.09, Total- 2.90 * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Aurora Orchard Heights Pumping Station & Reservoir | 2026-03-04
CENTRAL | March | Onsite for station check: Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Aurora Orchard Heights Pumping Station & Reservoir | 2026-03-13
CENTRAL | March | Onsite for station check/collect sample- WO# W11657608: Treated sample results (13:34): Free- 0.06, Total- 3.04 * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Aurora Orchard Heights Pumping Station & Reservoir | 2026-03-11
CENTRAL | March | Onsite for station check: Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Aurora Orchard Heights Pumping Station & Reservoir | 2026-03-27
CENTRAL | March | Onsite for CMU5. Free AIT loosing electrolyte rapidly Informed ROC Put AITs to cal mode on scada Removed electrode holder and found membrane to have popped out of socket causing the leak. Replaced membrane and filled holder with new electrolyte Replaced assembly and put back in service Found very low flow to Free AIT. Grit not swirling in sample cell and very low flow to drain. Flushed main sample line. Lots of flow and pressure. Removed pressure reducing valve, disassembled and cleaned. Returned to service and adjusted. Flow much better now. Took multiple grabs for Free AIT and adjusted G =0.07mg/L A =0.07mg/L Removed AITs from cal mode Informed ROC, armed building and left site | Aurora Orchard Heights Pumping Station & Reservoir | 2026-03-20
CENTRAL | March | Onsite for station check/collect sample- WO# W11690776: Sample results (08:28): Free- 0.05, Total- 2.96 * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Aurora Orchard Heights Pumping Station & Reservoir | 2026-03-25
CENTRAL | March | On site for station check. W117705787 and W11705378. 12:58 reservoir inlet at 59 l/s. Rechloramination dosing on. Zone 3 pumps 1 and 2 in standby. Topped up ammonia tank 2. Verified analyzer residuals (mg/l): 13:25 Pre-injection grabs: Free chlorine grab: 0.04. Analyzer: 0.03. Total Chlorine grab: 1.85 CL17: 1.88. Chemscan: Monochloramine grab: 1.69 Chemscan: 1.70 Free ammonia grab: 0.11. Chemscan: 0.10 Total ammonia: 0.45. Chemsca: 0.46. 13:30 Post-injection grabs. Free chlorine grab: 0.03. Analyzer: 0.06. Total Chlorine grab: 2.68 CL17: 2.61. Chemscan: 2.66. 13:40 Outlet grab Free chlorine grab: 0.02. Analyzer: 0.04. Total Chlorine grab: 2.30 Analyzer: 2.37 Monochloramine grab: 2.08 Free ammonia grab: 0.05 Total ammonia: 0.45 Nitrite: 0.003. 13:40 Zone 3 grab: Free chlorine: 0.02. Analyzer: 0.04. Total Chlorine: 2.30. Analyzer: 2.31 Station and equipment ok. No issues found. Entered readings into process sheets. | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2026-03-31
CENTRAL | March | Onsite for station check: Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Aurora Orchard Heights Pumping Station & Reservoir | 2026-03-09
CENTRAL | March | Onsite for station check: Replaced depolox KI reagent * Verified analyzers Depolox reagents- Ok Performed station housekeeping Noticed potential crack in depolox free probe- electrolyte gel draining quickly after filling. Informed instrumentation- will create work order to further investigate | Aurora Orchard Heights Pumping Station & Reservoir | 2026-03-20
CENTRAL | March | Onsite for station check/collect sample- WO# W11673476: Sample results (13:05): Free- 0.01, Total- 3.18 * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Aurora Orchard Heights Pumping Station & Reservoir | 2026-03-18
CENTRAL | March | Onsite for station check: Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Aurora Orchard Heights Pumping Station & Reservoir | 2026-03-16
CENTRAL | March | Onsite for station check: Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Aurora Orchard Heights Pumping Station & Reservoir | 2026-03-23
CENTRAL | March | Restarted the operator interface terminal due to windows operating system updates. | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2026-03-31
CENTRAL | March | On site for station check. 09:10 reservoir outlet at 32 l/s. Rechloramination dosing off. Zone 3 pumps 1 and 2 in standby. Replaced outlet total chlorione analyzer reagent. Verified analyzer residuals (mg/l): 09:36 Pre-injection grabs: Free chlorine grab: 0.03. Analyzer: 0.04. Total Chlorine grab: 2.26 CL17: 2.33. Chemscan: 2.41. Monochloramine grab: 2.06 Chemscan: 2.02 Free ammonia grab: 0.06. Chemscan: 0.03. Total ammonia: 0.47. Chemscan: 0.49 09:41 Post-injection grabs. Free chlorine grab: 0.04. Analyzer: 0.04. Total Chlorine grab: 2.36 CL17: 2.39. Chemscan: 2.50 Monochloramine grab: 2.05 Chemscan: 2.04 Free ammonia grab: 0.07. Chemscan: 0.02 Total ammonia: 0.47. Chemscan: 0.51. 09:45 Outlet grab and sample collected. Free chlorine grab: 0.03. Analyzer: 0.03. Total Chlorine grab: 2.38. Analyzer: 2.35. 09:50 Zone 3 grab: Free chlorine: 0.03. Analyzer: 0.04. Total Chlorine: 2.38. Analyzer: 2.30. Found EF-1 remains faulted with work order previously made. Station and equipment ok. No issues found. Entered readings into process sheets. | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2026-03-13
CENTRAL | March | On site for station check/ 07:45 Reservoir draining at 30 l/s. Rechloramination dosing off. Zone 3 pumps 1 and 2 in standby. Topped up ammonia tank 1. Verified analyzer residuals (mg/l): 08:36.Pre-injection grabs: Free chlorine grab: 0.07. Analyzer: 0.04. Total Chlorine grab: 2.40 CL17: 2.36. Chemscan: 2.46. Monochloramine grab: 2.09. Chemscan: 2.04 Free ammonia grab: 0.06. Chemscan: 0.04. Total ammonia: 0.48. Chemscan: 0.47. 09:06 Post-injection grabs. Chloriamination dosing system now running. Free chlorine grab: 0.05. Analyzer: 0.06. Total Chlorine grab: 2.66. CL17: 2.56. Chemscan: 2.47. Monochloramine grab: 2.28. Chemscan: 2.24 Free ammonia grab: 0.07. Chemscan: 0.02. Total ammonia: 0.52. Chemscan: 0.60. 09:09 Outlet grab: Free chlorine grab: 0.07. Analyzer: 0.04. Total Chlorine grab: 2.32. Analyzer: 2.38. 09:13 Zone 3 grab: Free chlorine: 0.07. Analyzer: 0.04. Total Chlorine: 2.32. Analyzer: 2.33 Station and equipment ok. No issues found. Entered readings into process sheets. | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2026-03-06
CENTRAL | March | Onsite to complete work orders: Notified roc of work. 13:56 placed all chemical dosing systems offline. 13:59 tested chlorine emergency shut off valves. Ok. 14:00 tested Chlorine leak detection. Ok 14:04 turned dosing system back online. No issues found. | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2026-03-10
CENTRAL | March | On site for station check and sampling. W11637647 and W11637218. 08:25 Reservoir filling at 71 l/s. Rechloramination dosing on. Zone 3 pumps both in standby. Verified analyzer residuals (mg/l): 08:35.Pre-injection grabs: Free chlorine grab: 0.02. Analyzer: 0.04. Total Chlorine grab: 1.83 CL17: 1.86. Chemscan: 1.88. 08:42 Post-injection grabs: Free chlorine grab: 0.04. Analyzer: 0.06. Total Chlorine grab: 2.56 CL17: 2.61. Chemscan: 2.69. 08:57 Outlet grab: Free chlorine grab: 0.02. Analyzer: 0.03 Total Chlorine grab: 2.36. Analyzer: 2.39 monochloramine grab: 2.08. Free ammonia grab: 0.04. Total Ammonia: 0.45. Nitirite: 0.002. Temperature: 4.9 Celsius. pH: 7.98. 09:13 Zone 3 grab: Free chlorine: 0.02 Analyzer: 0.04 Total Chlorine: 2.36. Analyzer: 2.39 Station and equipment ok. No issues found. Entered readings into process sheets. | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2026-03-04
CENTRAL | March | On site for station check. 07:52 Reservoir filling at 48 l/s. Zone 3 Pump 1 and 2 in standby. Chemical boosting active. Reservoir level at 73%. EF-01 overload tripped. Reset with no issues. Verified analyzer residuals (mg/l): 08:50 Pre-injection grabs: Free chlorine grab: 0.05. Analyzer: 0.03. Total Chlorine grab: 1.81 CL17: 1.87. Chemscan: 1.89. Monochloramine grab: 1.65 Chemscan: 1.69. Free ammonia grab: 0.08. Chemscan: 0.06. Total Ammonia: 0.41. Chemscan: 0.45. 09:00 Post-injection grabs: Free chlorine grab: 0.04. Analyzer: 0.06. Total Chlorine grab: 2.54 CL17: 2.52. Chemscan: 2.57. monochloramine grab: 2.18. Chemscan: 2.17. Free ammonia grab: 0.05. Chemscan: 0.02. Total Ammonia: 0.48. Chemscan: 0.52. 09:13 Outlet grab: Free chlorine grab: 0.02. Analyzer: 0.03 Total Chlorine grab: 2.36. Analyzer: 2.39 09:13 Zone 3 grab: Free chlorine: 0.02 Analyzer: 0.04 Total Chlorine: 2.36. Analyzer: 2.39 Station and equipment ok. No issues found. Entered readings into process sheets. | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2026-03-02
CENTRAL | March | On site for station check. 10:30 reservoir filling at 37 l/s. Rechloramination dosing on. Zone 3 pumps 1 running at 69.9 l/s. Pump 3 in standby. replaced post injection total chlorine analyzer reagent. Verified analyzer residuals (mg/l): 10:42 Pre-injection grabs: Free chlorine grab: 0.04. Analyzer: 0.04. Total Chlorine grab: 1.83 CL17: 1.85. Chemscan: 1.87. Monochloramine grab: 1.66. Chemscan: 1.66 Free ammonia grab: 0.09. Chemscan: 0.13. Total ammonia: 0.42. Chemscan: 0.46. 10:56 Post-injection grabs. Rechloramination boosting off now. Free chlorine grab: 0.06. Analyzer: 0.03. Total Chlorine grab: 1.84. CL17: 1.89. Chemscan: 1.9. Monochloramine grab: 1.66. Chemscan: 1.71 Free ammonia grab: 0.11. Chemscan: 0.07. Total ammonia: 0.44. Chemscan: 0.51. 11:08 Outlet grab: Free chlorine grab: 0.07. Analyzer: 0.04. Total Chlorine grab: 2.42. Analyzer: 2.37. 11:10 Zone 3 grab: Free chlorine: 0.07. Analyzer: 0.03. Total Chlorine: 2.42. Analyzer: 2.37 Found EF-1 faulted again. Created work order for maintenance to investigate. Station and equipment ok. No issues found. Entered readings into process sheets. | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2026-03-09
CENTRAL | March | On site for station check. 07:40 reservoir filling at 24 l/s. Rechloramination dosing off. Zone 3 pumps 1 running at 70 l/s. Pump 2 in standby. Verified analyzer residuals (mg/l): 07:47 Pre-injection grabs: Free chlorine grab: 0.02. Analyzer: 0.05. Total Chlorine grab: 2.32 CL17: 2.31. Chemscan: 2.40. 07:58 Post-injection grabs. Rechloramination boosting off now. Free chlorine grab: 0.02. Analyzer: 0.04. Total Chlorine grab: 2.34 CL17: 2.37. Chemscan: 2.47 08:04 Outlet grab and sample collected. Free chlorine grab: 0.05. Analyzer: 0.04. Total Chlorine grab: 2.32. Analyzer: 2.37. Monochloramine grab: 2.06 Free ammonia grab: 0.06. Total ammonia: 0.47. Nitrite: 0.003. pH: 8.00. Temperature: 5.9 08:15 Zone 3 grab: Free chlorine: 0.05. Analyzer: 0.04. Total Chlorine: 2.44. Analyzer: 2.35. Found EF-1 remains faulted with work order previously made. Station and equipment ok. No issues found. Entered readings into process sheets. | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2026-03-11
CENTRAL | March | On site for station check. 08:56 reservoir inlet at 72 l/s. Rechloramination dosing on. Zone 3 pumps 2 running at 70.1 l/s. P1 in standby. Replaced zone 3 CL17 free analzyer reagent. Topped up chemscan distilled water. Verified analyzer residuals (mg/l): 09:13 Pre-injection grabs: Free chlorine grab: 0.04. Analyzer: 0.03. Total Chlorine grab: 1.85 CL17: 1.87. Chemscan: 1.93 Monochloramine grab: 1.68 Chemscan: 1.66. Free ammonia grab: 0.10. Chemscan: 0.09. Total ammonia: 0.43. Chemscan: 0.46. 09:44 Post-injection grabs. Free chlorine grab: 0.05. Analyzer: 0.06. Total Chlorine grab: 2.60 CL17: 2.63. Chemscan: 2.67. Monochloramine grab: 2.25. Chemscan: 2.18.. Free ammonia grab: 0.05. Chemscan: 0.02. Total ammonia: 0.50. Chemscan: 0.54.. 09:49 Outlet grab: Free chlorine grab: 0.02. Analyzer: 0.04. Total Chlorine grab: 2.32 Analyzer: 2.34 09:49 (corrected time typo) Zone 3 grab: Free chlorine: 0.02. Analyzer: 0.04. Total Chlorine: 2.32. Analyzer: 2.35. . Found EF-1 remains faulted with work order previously made. Station and equipment ok. No issues found. Entered readings into process sheets. | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2026-03-23
CENTRAL | March | Onsite to adjust metro flow control valve Adjusted speed pilots on valve, both now set to 3 turns from fully closed. | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2026-03-16
CENTRAL | March | Onsite to complete CL17 analyzer maintenance. Topped up chemscan sulphuric acid reagent. Replaced outlet free cl17 analyzer reagent. 09:45 Notified ROC, placed free analyzers in calibration mode and completed all free cl17 analyzer maintenance. 10:28 Verified zone 3 analyzer (mg/l): 0.05. Analyzer 0.04. 10:30 Outlet free grab: 0.03. Analyzer: 0.07. 10:32 Preinjection free grab: 0.05. Analyzer: 0.04. 10:34 Post injection free grab: 0.08. Analyzer: 0.04. completed site cleaning. No issues found. Topped up No issues found. | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2026-03-26
CENTRAL | March | On site for station check. 10:15 reservoir inlet at o l/s. Rechloramination dosing off. Reservoir outlet 18 l/s. Zone 3 pumps 1 and 2 in standby. Verified analyzer residuals (mg/l): 10:38 Pre-injection grabs: Free chlorine grab: 0.02. Analyzer: 0.04. Total Chlorine grab: 2.34 CL17: 2.34. Chemscan 2.35. Monochloramine grab: 2.01 Chemscan: 1.99 Free ammonia grab: 0.08. Chemscan: 0.14. Analyzers next reading 0.03 with grab 0.06. Adjusted analyzer offset up to match grab. Total ammonia: 0.47. Chemscan: 0.50. 10:48 Post-injection grabs. Free chlorine grab: 0.03. Analyzer: 0.04. Total Chlorine grab: 2.36 CL17: 2.39. Chemscan: 2.51. Adjusted chemscan to match grabs. Monochloramine grab: 2.05. Chemscan: 2.10. Free ammonia grab: 0.07. Chemscan: 0.02. Adjusted to match grab. Total ammonia: 0.47. Chemscan: 0.50. 10:57 Outlet grab and sample collected. Free chlorine grab: 0.07. Analyzer: 0.04. Total Chlorine grab: 2.40 Analyzer: 2.35 10:57 Zone 3 grab: Free chlorine: 0.07.. Analyzer: 0.04. Total Chlorine: 2.40. Analyzer: 2.35. . Found EF-1 remains faulted with work order previously made. Station and equipment ok. No issues found. Entered readings into process sheets. | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2026-03-20
CENTRAL | March | Onsite to complete work orders and to adjust metro valve speed setpoints. 10:50 Notified ROC of work being performed. Adjusted closing and opening speed pilots from 3 turns opened from close to 4.5 turns open. Exercised speed pilots. Tested valve and opened with no issues. Placed valve back into auto. Valve flow trend initially appears less erratic. JHSC inspection ok. Visual chemical injection point inspection. ok. No issues found. | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2026-03-17
CENTRAL | March | Onsite for chlorine cylinder change. Changed left chlorine cylinder with Alex B. 13:45 Notified roc and ran diesel generator under load. Fuel level: 2158 to 2137L. Run hours: 240.53 to 241.57. Preinspection: Oil level ok. Coolant level ok. Battery terminals ok. Recirculaiton pump ok. 14:48 completed generator run. No new issues found. | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2026-03-17
CENTRAL | March | On site for station check and sampling. W11672681 13:58 reservoir inlet at 61 l/s. Rechloramination dosing on. Zone 3 pumps 1 and 2 in standby. Replaced pre-injection cl17sc total analyzer reagent. Verified analyzer residuals (mg/l): 14:21 Pre-injection grabs: Free chlorine grab: 0.05. Analyzer: 0.03. Total Chlorine grab: 1.87 CL17: 1.85. Chemscan: 1.88 14:25 Post-injection grabs. Free chlorine grab: 0.06. Analyzer: 0.09. Total Chlorine grab: 2.68 CL17: 2.62. Chemscan: 2.79. 14:30 Outlet grab and sample collected. Free chlorine grab: 0.03. Analyzer: 0.03. Total Chlorine grab: 2.40. Analyzer: 2.38. Monochloramine grab: 2.14 Free ammonia grab: 0.06. Total ammonia: 0.49. Nitrite: 0.000 pH: 8.06. Temperature: 4.6 celsius. 14:30 Zone 3 grab: Free chlorine: 0.03. Analyzer: 0.04. Total Chlorine: 2.40. Analyzer: 2.38 . Found EF-1 remains faulted with work order previously made. Station and equipment ok. No issues found. Entered readings into process sheets. | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2026-03-18
CENTRAL | March | On site for station check and sampling of reservoir. W11690064. 13:00 reservoir outlet at 52 l/s. Rechloramination dosing off. Zone 3 pumps 1 and 2 in standby. Verified analyzer residuals (mg/l): 13:05 Pre-injection grabs: Free chlorine grab: 0.03. Analyzer: 0.03. Total Chlorine grab: 2.28 CL17: 2.32. Chemscan: 2.38. 13:11 Post-injection grabs. Free chlorine grab: 0.07. Analyzer: 0.04. Total Chlorine grab: 2.30 CL17: 2.38. Chemscan: 2.32. 13:15 Outlet grab and sample collected. Free chlorine grab: 0.06. Analyzer: 0.03. Total Chlorine grab: 2.36 Analyzer: 2.33. Monochloramine grab: 2.07 Free ammonia grab: 0.05. Total ammonia: 0.45. 13:15 Zone 3 grab: Free chlorine: 0.06. Analyzer: 0.04. Total Chlorine: 2.36. Analyzer: 2.29. . Found EF-1 remains faulted with work order previously made. Station and equipment ok. No issues found. Entered readings into process sheets. | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2026-03-25
CENTRAL | March | Onsite to complete Chemscan and cl17sc maintenance. 13:54 notified roc of work and shut down all chemical dosing pumps. Placed analyzers in calibration mode and performed Chemscan maintenance and clean flush. Cleaned all cl17sc total chlorine analyzers. Verified analyzers. 14:18 zone 3 outlet total: 2.38. Analyzer: 2.35. 14:21 outlet total: 2.30. Analyzer: 2.34. 14:27 pre injection total: 1.83. Analyzer: 1.88 14:30 post injection total: 1.86. Analyzer: 1.91. 14:41 placed all analyzers systems back in service. No issues found. | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2026-03-19
CENTRAL | March | On site for station check. 12:28 reservoir inlet at 62 l/s. Rechloramination dosing on. Zone 3 pumps 1 and 2 in standby. Verified analyzer residuals (mg/l): 12:36 Pre-injection grabs: Free chlorine grab: 0.02. Analyzer: 0.03. Total Chlorine grab: 1.84 CL17: 1.89. Chemscan: 1.96. Adjusted chemscan to match grabs. Monochloramine grab: 1.69 Chemscan: 1.70 Free ammonia grab: 0.11. Chemscan: 0.10 Total ammonia: 0.45. Chemsca: 0.46. 12:43 Post-injection grabs. Free chlorine grab: 0.04. Analyzer: 0.06. Total Chlorine grab: 2.70 CL17: 2.72. Chemscan: 2.90. Chemscan dropped next reading to 2.74. Monochloramine grab: 2.28. Chemscan: 2.31 Free ammonia grab: 0.04. Anlayzer: 0.02. Adjusted to match grab. Total ammonia: 0.49. Chemscan: 0.54. 12:52 Outlet grab Free chlorine grab: 0.02. Analyzer: 0.03. Total Chlorine grab: 2.34 Analyzer: 2.30 12:52 Zone 3 grab: Free chlorine: 0.02. Analyzer: 0.04. Total Chlorine: 2.34. Analyzer: 2.31 13:14 stopped dosing to complete chlorine to perform chlorine system inspectino. Notified ROC. Triggered a high vaccum switch alarm during vacuum test. 13:34 No issues found. Placed chemical dosing systems back in auto . Station and equipment ok. No issues found. Entered readings into process sheets. | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2026-03-27
CENTRAL | March | On site to respond to chlorine room exhaust fan, EF1, reports of it tripping. Found exhaust fan tripped on MCC. Inspected motor fan belt and blower wheel. Found all to be in good working order. Inspected motor nameplate current draw and compared that to the overload on the motor starter in the MCC. Found that the trip setting on the overload was set too low. Adjusted setting and tested for proper operation. Chlorine room exhaust fan should be working correctly now. | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2026-03-26
CENTRAL | March | On site for station check. 09:01 reservoir inlet at 68 l/s. Rechloramination dosing on. Zone 3 pumps 1 running at 70 l/s and P2 in standby. Replaced pre injection free chlorione analyzer reagent. Verified analyzer residuals (mg/l): 09:10 Pre-injection grabs: Free chlorine grab: 0.04. Analyzer: 0.04. Total Chlorine grab: 1.85 CL17: 1.88. Chemscan: 1.91 Monochloramine grab: 1.67 Chemscan: 1.64 Free ammonia grab: 0.11. Chemscan: 0.10. Total ammonia: 0.44. Chemscan: 0.47 09:22 Post-injection grabs. Free chlorine grab: 0.05. Analyzer: 0.07. Total Chlorine grab: 2.58 CL17: 2.66. Chemscan: 2.81 Monochloramine grab: 2.26 Chemscan: 2.29 Free ammonia grab: 0.06. Chemscan: 0.04 Total ammonia: 0.50. Chemscan: 0.57. 09:33 Outlet grab and sample collected. Free chlorine grab: 0.06. Analyzer: 0.03. Total Chlorine grab: 2.34. Analyzer: 2.36. 09:33 Zone 3 grab: Free chlorine: 0.06. Analyzer: 0.04. Total Chlorine: 2.34. Analyzer: 2.36. Found EF-1 remains faulted with work order previously made. Station and equipment ok. No issues found. Entered readings into process sheets. | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2026-03-16
CENTRAL | March | Restarted the Operator Interface Terminal due to Windows Operating System software updates. Well was not running during the work. | Aurora Well 5 | 2026-03-30
CENTRAL | March | Attending site to check chlorinator#2 (W11714177). Replaced broken 1/4" tubing section. This was repaired earlier this week but broke again. Left a loop in the tubing this time to reduce stress on the tubing. Joe DeMarco called to advise that the dosing required adjustment after the repair which he performed remotely. Influent Free residual is back within normal limits. ROC was notified before and after maintenance activities. | Aurora Well 5 | 2026-03-06
CENTRAL | March | silicate top up: before 1805L after 2315L | Aurora Well 5 | 2026-03-03
CENTRAL | March | Onsite for station check: Changed CL2 cylinders: 0/48 kg to 68/48 kg * Adjusted treated total analyzer from 3.17 to 2.88 based on multiple grabs (2.86, 2.88, 2.88) * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok | Aurora Well 5 | 2026-03-09
CENTRAL | March | Onsite for station check: Collected enhanced operational sample * Adjusted influent free analyzer from 2.74 to 2.60 based on multiple grabs (2.60, 2.60, 2.58) * Adjusted effluent free analyzer from 2.38 to 2.20 based on multiple grabs (2.20, 2.20, 2.20) * Replaced effluent free CL17 reagents * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok Changed CL2 cylinders: 58/0 kg to 58/68 kg * | Aurora Well 5 | 2026-03-02
CENTRAL | March | Adjusted ammonia startup dosage setpoint from 42.76 mL/min to 44.00 mL/min | Aurora Well 5 | 2026-03-09
CENTRAL | March | Onsite to repair ammonia mixer pump 2 Replaced propeller on shaft Mixed ammonia tank 2, back in service Investigate Silicate pump 1 fault ?Ruptured diaphragm? Will get new from inventory and replace, remains OOS Ops normal | Aurora Well 5 | 2026-03-12
CENTRAL | March | Onsite for station check: Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok Silicate P1 man/off OOS- will replace diaphragm | Aurora Well 5 | 2026-03-13
CENTRAL | March | Onsite for station check/collect samples- WO# W11657608: Treated sample results (09:58): Free- 0.14, Total- 2.96 * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok | Aurora Well 5 | 2026-03-11
CENTRAL | March | Onsite for station check/collect samples- WO# W11673476: Treated sample results (12:04): Free- 0.09, Total- 3.08 * Adjusted treated total analyzer from 2.83 to 3.08 based on multiple grabs (3.08, 3.04, 3.08) * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok | Aurora Well 5 | 2026-03-18
CENTRAL | March | Onsite for station check: Changed CL2 cylinders: 0/56 kg to 68/56 kg * Replaced influent free CL17 reagents * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok | Aurora Well 5 | 2026-03-20
CENTRAL | March | Attending site to check silicate pump#2 (W11737102). When operated, pump stops after a few strokes then displays power supply error. Pump was removed for evaluation my the manufacturer's representative. | Aurora Well 5 | 2026-03-24
CENTRAL | March | Onsite to troubleshoot chlorine booster/chlorinator #2- informed ROC: Tried running chlorine booster #2 and chlorinator #2- no flow to chlorinator. Placed well 5 in man/off. Locally ran chlorine booster pump #2 and manually opened chlorinator #2- still no flow to chlorinator. Placed chlorine booster #2 and chlorinator #2 in local/off- Informed Eric S. Chlorine system will require further troubleshooting. Well 5 placed back into auto once investigation completed | Aurora Well 5 | 2026-03-05
CENTRAL | March | Onsite for station check/complete assigned WO: H/S inspection Placed chlorine booster #2 and chlorinator #2 back into auto duty 1. Further investigation completed by Eric S. Placed back into normal operation and will monitor performance during next run cycle. Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok | Aurora Well 5 | 2026-03-06
CENTRAL | March | Onsite to complete assigned work orders: Deep well exhaust inspection Exhaust fan/damper inspection CL17 analyzer maintenance Turbidimeter maintenance Silicate system inspection - Adjusted silicate P1 max flow from 150 to 140 based on multiple drawdown attempts * - Adjusted silicate P2 max flow from 150 to 140 based on multiple drawdown attempts * Ammonia system inspection Chlorine system inspection CL2 leak alarm test Performed station housekeeping Work order created for ammonia tank #2 mixer damaged propeller * Jason G onsite filling silicate tank * Station/equipment- Ok | Aurora Well 5 | 2026-03-10
CENTRAL | March | Attending site to check issue with chlorinator #2 (W11692934). Found broken 1/4" tubing where the local vacuum gauge is bypassed. Replaced broken tubing and tested. Could not put back to Auto due to SCADA communication issue. Wil notify Operations. ROC was notified before and after maintenance activities. | Aurora Well 5 | 2026-03-03
CENTRAL | March | Onsite for station check/collect samples- WO# W11638288: Treated sample results (11:32): Free- 0.06, Total- 3.04 * Replaced treated total CL17 reagents * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok | Aurora Well 5 | 2026-03-04
CENTRAL | March | Onsite for station check/complete assigned work orders: Changed CL2 cylinders: 34/0 kg to 34/68 kg * Eyewash cleaning/inspection Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok | Aurora Well 5 | 2026-03-27
CENTRAL | March | Onsite for station check: Received multiple high FA readings during operational sampling (0.13, 0.11, 0.12)- Adjusted CL2/AMM ratio from 3.7 to 3.9. Once adjustments made FA reading 0.08. Performed ammonia drawdowns during monthly maintenance, no abnormalities. Will continue to monitor changes * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok | Aurora Well 5 | 2026-03-23
CENTRAL | March | Onsite for station check and troubleshoot silicate pump fault alarms: Silicate pump 1 diaphragm rupture alarm- replaced diaphragm and primed lines. Completed a drawdown to verify pump output. Pump placed back into auto duty 1. Silicate pump 2 diaphragm rupture alarm- replaced diaphragm but unable to prime lines. Pump display reading power error- will create work order for pump to be further investigated. Pump placed OOS. Changed CL2 cylinders: 41/0 kg to 41/68 kg Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok | Aurora Well 5 | 2026-03-16
CENTRAL | March | Silicate top up (44 to 52cm) | Aurora Well 5 | 2026-03-24
CENTRAL | March | Onsite for station check/collect samples- WO# W11690776: Sample results (13:00): Free- 0.07, Total- 3.08 * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok | Aurora Well 5 | 2026-03-25
CENTRAL | March | Onsite for station check: Station offline * Station/equipment- Ok | Aurora Well 6 | 2026-03-31
CENTRAL | March | Onsite to ?borrow? ammonia pump Ops normal Well 6 OOS | Aurora Well 6 | 2026-03-12
CENTRAL | March | Restarted the Operator Interface Terminal due to Windows Operating System software updates. Well was off. | Aurora Well 6 | 2026-03-30
CENTRAL | March | Onsite for station check: Station offline * Station/equipment- Ok | Aurora Well 6 | 2026-03-11
CENTRAL | March | Onsite for station check/complete assigned work orders: H/S inspection Performed station housekeeping Station/equipment- Ok | Aurora Well 6 | 2026-03-03
CENTRAL | March | Onsite for station check: Station offline * Station/equipment- Ok | Aurora Well 6 | 2026-03-18
CENTRAL | March | Station and equipment check Well remains OOS as per normal ops All ok | Aurora Well 6 | 2026-03-23
CENTRAL | March | Received 24 chlorine cylinders. Returned 24 empties. | Aurora Wells 1-4 Water Treatment Plant | 2026-03-31
CENTRAL | March | Onsite to complete assigned work orders- informed ROC: H/S inspection Performed station housekeeping Generator test run: Start hours- 92.50 Stop hours- 93.75 Start fuel- 6,750 L (25.5 cm) Stop fuel- Start time- 12:36 Stop time- 13:53 Generator pre test inspection completed- no abnormalities * Generator operating stats (under load P2/P3): 1800 rpm 600 V 60 Hz 962 A Oil pressure- 79 psi Oil temp- 187 F Coolant temp- 177 F Fuel pressure- 103 psi Fuel temp- 68 F No abnormalities during generator test run- returned generator and station pumps back to auto once test run completed * Station/equipment- Ok | Aurora Wells 1-4 Water Treatment Plant | 2026-03-05
CENTRAL | March | Fuel inspection | Aurora Wells 1-4 Water Treatment Plant | 2026-03-09
CENTRAL | March | Onsite for raw station check/collect samples- WO# W11657608: Station/equipment- Ok Onsite for station check/collect sample- WO# W11657608: Treated sample results (11:45): Free- 0.12, Total- 2.90 * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok | Aurora Wells 1-4 Water Treatment Plant | 2026-03-11
CENTRAL | March | Onsite for treated station check/collect samples- WO# W11638288: Treated sample results (09:40): Free- 0.06, Total- 2.92 * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok Onsite for raw station check/collect samples- WO# W11638288: Station/equipment- Ok | Aurora Wells 1-4 Water Treatment Plant | 2026-03-04
CENTRAL | March | Onsite to complete assigned work orders- informed ROC: H/S inspection CL17 analyzer maintenance Turbidimeter maintenance CL2 leak alarm test Silicate system inspections Ammonia system inspections Chlorine system inspections Eyewash cleaning/solution replacement (treated building) Performed cleaning/maintenance on chemical boards Station/equipment- Ok | Aurora Wells 1-4 Water Treatment Plant | 2026-03-03
CENTRAL | March | Onsite for treated station check: Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok Onsite for raw station check: Station/equipment- Ok | Aurora Wells 1-4 Water Treatment Plant | 2026-03-09
CENTRAL | March | Onsite for treated station check: Changed CL2 cylinders: 0/59 kg to 68/59 kg * Replaced effluent free CL17 reagents * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok Onsite for raw station check/complete WO: Air relief valve inspection Station/equipment- Ok | Aurora Wells 1-4 Water Treatment Plant | 2026-03-06
CENTRAL | March | Onsite for treated station check: Collected enhanced operational sample * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok | Aurora Wells 1-4 Water Treatment Plant | 2026-03-02
CENTRAL | March | Onsite for station check: Replaced treated free CL17 reagents * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok Onsite for raw station check/complete WO: Eyewash cleaning/inspection Station/equipment- Ok | Aurora Wells 1-4 Water Treatment Plant | 2026-03-13
CENTRAL | March | Received silicate delivery. Bulk tank 41.7 ¦ 40.7cm -> 83.0 ¦ 81.7cm | Aurora Wells 1-4 Water Treatment Plant | 2026-03-17
CENTRAL | March | Onsite for station check: Changed CL2 cylinders: 45/0 kg to 45/68kg (Donald M and Ben H) Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok | Aurora Wells 1-4 Water Treatment Plant | 2026-03-16
CENTRAL | March | Onsite for treated station check: Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok Onsite for raw station check: Station/equipment- Ok | Aurora Wells 1-4 Water Treatment Plant | 2026-03-20
CENTRAL | March | Onsite to change CL2 cylinders: 0/53 kg to 68/53 kg * | Aurora Wells 1-4 Water Treatment Plant | 2026-03-23
CENTRAL | March | Onsite to perform ammonia pump maintenance- informed ROC: Replaced ammonia pump diaphragms, primed ammonia pumps once completed Station/equipment- Ok | Aurora Wells 1-4 Water Treatment Plant | 2026-03-26
CENTRAL | March | Received ammonia delivery with Donny M. | Aurora Wells 1-4 Water Treatment Plant | 2026-03-17
CENTRAL | March | Onsite for treated station check: Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok Onsite for raw station check: Station/equipment- Ok | Aurora Wells 1-4 Water Treatment Plant | 2026-03-27
CENTRAL | March | Onsite for raw station check/collect raw samples- WO# W11673476: Station/equipment- Ok Onsite for treated station check/collect treated samples- WO# W11673476: Treated sample results (10:40): Free- 0.14, Total- 3.06 * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok Noticed burning smell coming from electrical room- informed Ben H and Tyler Z- electrician will attend station to further investigate * | Aurora Wells 1-4 Water Treatment Plant | 2026-03-18
CENTRAL | March | Onsite for treated station check/collect sample- WO# W11690776: Sample results (09:45): Free- 0.10, Total- 2.90 * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok Onsite for raw station check/collect samples- WO# W11690776: Station/equipment- Ok | Aurora Wells 1-4 Water Treatment Plant | 2026-03-25
CENTRAL | March | Onsite for treated station check: Replaced influent free CL17 reagents * Replaced treated total CL17 reagents * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok Onsite for raw station check: Station/equipment- Ok | Aurora Wells 1-4 Water Treatment Plant | 2026-03-23
CENTRAL | March | On site to transfer silicate.? Before level: 0.84 / 0.86cm After level: 0.80 / 0.81 cm | Aurora Wells 1-4 Water Treatment Plant | 2026-03-04
EAST | March | SYSTEM TESTING - PLEASE IGNORE | Bayview Pumping Station | 2026-03-28
EAST | March | SYSTEM TESTING - PLEASE IGNORE | Bayview Pumping Station | 2026-03-28
EAST | March | Attended site for preventative maintenance with Phil DeGroot. Tested discharge surge valves Exercised Sycamore chamber PRV Station and equipment okay | Bayview Pumping Station | 2026-03-30
EAST | March | On site to complete station check. Time: 11:40 Grab (mg/l) Analyzer (mg/l) Free: 0.05 0.01 Total: 1.47 1.49 Verified analyzer with grabs. Checked station and trends. Pump 2 OOS due to it being rebuilt. All alarms on site are due to pump 2 being offline. | Bayview Pumping Station | 2026-03-30
EAST | March | On site to facilitate Diesel load test with generator contractor. | Bayview Pumping Station | 2026-03-30
EAST | March | Duty rotated pumps - Placed pump #3 in duty 1, pump #4 to duty 2. Duty is currently not active. | Bayview Pumping Station | 2026-03-11
EAST | March | On site to wire up temperature sensors on pump two. Also facilitate generator fluid maintenance with generator contractor. Transfer test to test for proper operation of the standby power system. | Bayview Pumping Station | 2026-03-31
EAST | March | On site to respond to Pump #3 suction valve not open interlock, and the chlorine / temperature analyzer OOR / Low alarms Electrical is on site for generator service / load test with Total Power. Chlorine analyzer dropped to 0.00 mg/L @13:41, and recovered @13:46. Was caused during station power transfer to generator. Between the power transfer, an alarm came up on the generator, causing a delay to the transfer. During that period, the chlorine analyzer lost power, causing the OOR alarms. No further issues with Chlorine analyzer Pump #3 discharge valve was backed off by about half a turn from fully open, causing the position indicator to send a signal to SCADA to interlock Pump #3. Fully opened valve, and the interlock on pump #3 cleared Activated system duty to test pumps while on generator power @14:15 Deactivated system duty @14:32 | Bayview Pumping Station | 2026-03-31
EAST | March | On site for facility station check and equipment verifications Duty is active - RHRSTR Level - 82% Pumps 1 and 4 running, 1245 L/s Recorded station readings in PWQ sheets Verified analyzer readings @11:50 (Grab / Analyzer mg/L) Free: 0.05 / 0.03 Total: 1.58 / 1.63 Reviewed trends - observed that trending on the electrical room OIT (upstairs). Lower OIT is trending okay, as well as remote SCADA trends. Informed TL to create WO for PCs Equipment OOS: Pump #2 for rebuild Station operation ok | Bayview Pumping Station | 2026-03-09
EAST | March | On site for facility station check and equipment verifications Duty is active - RHRSTR Level - 80% Pumps 1 and 3 running in D1 - 1277 L/s, 644 kpa discharge pressure Recorded data in PWQ sheets Verified analyzer readings with grab residuals: @14:00 Grab free: 0.07 mg/L / Analyzer: 0.04 mg/L Grab total: 1.48 mg/L / Analyzer: 1.55 mg/L Observed water leaking from grease nipple on check valve for pump #1. Was able to slow the leak, but will need mechanical support to fix. Pump is still able to run. Created W11733142 to address the issue Reviewed trends Equipment OOS: Pump #2 for rebuild Station ok | Bayview Pumping Station | 2026-03-13
EAST | March | On site for facility station check and equipment verifications Duty is active - RHRSTR Level - 77% Pumps 1 and 4 running in D1 - 1265 L/s, Discharge pressure - 634 kpa Verified chlorine analyzer readings: @11:55 Grab free: 0.05 mg/L / Analyzer: 0.03 mg/L Grab total: 1.51 mg/L / Analyzer: 1.49 mg/L Reviewed trends Equipment OOS: Pump #2 for rebuild Station ok | Bayview Pumping Station | 2026-03-06
EAST | March | On site for facility station check and equipment verifications Duty is active - RHRSTR level - 73% Pumps 1 and 3 running in D1, 1285 L/s, 638 kpa discharge pressure Recorded data in PWQ sheets Verified analyzer readings @13:48 Grab FCL: 0.06 / Analyzer: 0.04 mg/L Grab TCL: 1.47 / Analyzer: 1.53 mg/L Reviewed trends, equipment OOS: Pump 2 for rebuild Station operations normal | Bayview Pumping Station | 2026-03-16
EAST | March | Vibration readings | Bayview Pumping Station | 2026-03-16
EAST | March | On site for installation of rtd?s, conduit and wiring for pump #2 rebuild. | Bayview Pumping Station | 2026-03-26
EAST | March | Station Check (no issues found) Input data to PWQ 11:40 Verified Depolox (mg/l) Free: Grab 0.04, A 0.02 Total: Grab 1.51, A 1.46 | Bayview Pumping Station | 2026-03-20
EAST | March | On site to check station and equipment. P1 and P4 are running in duty 1. 14:13 chlorine residuals grab/analyzer in mg/l: Total: 1.51/1.53 Free: 0.04/0.03 Other station readings are in PWQ sheets. Reviewed trends, Station is under normal operation. Equipment OOS: Pump 2. | Bayview Pumping Station | 2026-03-02
EAST | March | On site for station check, equipment verifications, and to complete monthly PMs - Diesel generator test run and hours log Duty is not active - RHRSTR level is 78% Pre checks: Oil Level - Ok Coolant Level - Ok Battery Terminals / cables - Ok Battery Cell levels - N/A Coolant Recirculation pump - Ok Fluid leaks - None Start hours: 138.8 hours Start Fuel: 4081 / 4092 L (152 / 153 cm) Start time: @11:43 Activated system duty while generator running to test station operation under generator power Generator readings while running: @12:50 Voltage: 4.16 kV Current: 165 amps Frequency: 60 hz Engine speed: 1800 RPM Oil pressure: 65.5 psi Oil temperature: 210 F Coolant temperature: 190 F Exhaust: 612 C / 624 C Deactivated system duty @12:59 - pumps 1 and 3 stopped in auto Stop Hours: 140.4 hours Stop time: 13:18 Stop Fuel: 3888 / 3950 (145 / 147 cm) No issues with generator test run or transfer test Verified analyzer readings @12:55 (Grab/analyzer mg/L) FCL: 0.06 / 0.00 TCL: 1.50 / 1.43 No adjustments needed Recorded station data in PWQ sheets @13:43 / 13:45 tested Surge relief valves - pumps are all off. No issues with test, cleared alarms Reviewed trends, equipment OOS: Pump #2 for rebuild Station operation normal | Bayview Pumping Station | 2026-03-23
EAST | March | On site for monthly PMs - Informed ROC while on site Station is currently off - duty is not active - Completed Pressure gauge test WO - Pumps 1-4 centrifugal pumps inspection - Ventilation system inspection - Dehumidifier inspection - Check valves inspections / maintenance - Manual valves exercises - Discharge valve actuators exercise to test check valve function with pumps off. When exercising pump #3 discharge valve, the check valve slammed closed aggressively. Created WO to maintenance to look at the check valve. (W11746694) - Flood alarms test (tested high and hihi) Suction and discharge valves closed when triggered flood alarms, and reopened in auto after alarms cleared - JHSC Health and safety inspection - 5 tonne hoist system inspection - Chlorine analyzer maintenance (Depolox) Verified analyzer with grab residuals after maintenance (mg/L) Free Grab: 0.06 mg/L / Analyzer: 0.03 Total Grab: 1.53 / Analyzer: 1.59 Adjusted TCL analyzer to average of 3 grabs Duty activated at 12:30 - Pumps 1 and 3 in duty 1. Completed facility station check and equipment verifications - Readings in PWQ sheets Equipment OOS: Pump #2 for rebuild Station operation normal | Bayview Pumping Station | 2026-03-19
WEST | March | On site for station check Check trends: All okay 11:30- Verified analyzer Grab free CL2- 0.04 mg/L Analyzer Free Cl2- 0.02 mg/L Grab Total CL2- 2.05 mg/L Analyzer Total CL2- 2.10 mg/L Reagents all good Entered values in PWQ sheet. Equipment okay. | East Vaughan Teston Pumping Station | 2026-03-09
WEST | March | On site for station check Check trends: All okay 14:40- Verified analyzer Grab free CL2- 0.05 mg/L Analyzer Free Cl2- 0.05 mg/L Grab Total CL2- 2.16 mg/L Analyzer Total CL2- 2.08 mg/L Reagents all good. Entered values in PWQ sheet. Equipment okay. | East Vaughan Teston Pumping Station | 2026-03-30
WEST | March | On site for station check Check trends: All okay 12:50- Verified analyzer Grab free CL2- 0.04 mg/L Analyzer Free Cl2- 0.04 mg/L Grab Total CL2- 2.09 mg/L Analyzer Total CL2- 2.13 mg/L Reagents all good Entered values in PWQ sheet. Equipment okay. | East Vaughan Teston Pumping Station | 2026-03-02
WEST | March | Reset Sanitary sump pump alarms. W11633103- Charlatte Surge tanks. Isolated both tanks. Tank 1- pressure v/s level looks good before draining. After drain, pressure dropped down below 54 psi, added compressed air to make it 54 psi. Tank 2- pressure v/s level looks good before draining. pressure v/s level looks good after draining. Put both tanks back to service. Informed ROC before and after the work. | East Vaughan Teston Pumping Station | 2026-03-12
WEST | March | Station Check (no issues found) Input data to PWQ 11:00 Verified Depolox (mg/l) Free: Grab 0.04, A 0.00 (adjusted to match grabs) Total: Grab 2.07, A 2.05 | East Vaughan Teston Pumping Station | 2026-03-23
WEST | March | On site for station check Check trends: All okay 09:20- Verified analyzer Grab free CL2- 0.06 mg/L Analyzer Free Cl2- 0.03 mg/L Grab Total CL2- 2.09 mg/L Analyzer Total CL2- 2.07 mg/L Reagents all good. Entered values in PWQ sheet. Equipment okay. | East Vaughan Teston Pumping Station | 2026-03-16
WEST | March | On site for Scheduled PM workorders, Informed ROC about the works being done. W11632905 VNPS, PD7/PD8 VFD Air Filter Change, East Vaughan Pumping Station (3M) W11632945 VNPS, Process Mechanical Lubrication - PD8, East Vaughan Pumping Station (6M) W11632874 VNPS, Process Mechanical Air valve flush and inspection - PD7, East Vaughan Pumping Station(1M) W11632890 VNPS, Process Mechanical Air valve flush and inspection - PD8, East Vaughan Pumping Station(1M) W11632834 VNPS, Chlorine Analyzer maintenance 14:30-Verified Analyzer Grab Free CL2-0.06mg/L; Analyzer- 0.02 mg/L Grab Total Cl2- 2.04mg/L; Analyzer- 2.05 mg/L W11632860 VNPS, Standby Power Generator Test Run and Run Hours log, East Vaughan Pumping Station(1M) Pre check Battery okay- 26.9V Coolant- Okay Oil - Okay Before Start Start time- 10:45 Run time- 237.6 hr Fuel level Bulk Tank- 12763.2L/85.6% Day Tank- 2229L/89.9% Put one pump on load from PD7 and PD8 After Stop Stop time- 12:30 Run time- 239.2 hr Fuel level Bulk Tank- 12659L/84.9% Day Tank- 1937L/76.7% | East Vaughan Teston Pumping Station | 2026-03-17
WEST | March | On site for station check Check trends: All okay 13:30- Verified analyzer Grab free CL2- 0.02 mg/L Analyzer Free Cl2- 0.01 mg/L Grab Total CL2- 2.15 mg/L Analyzer Total CL2- 2.10 mg/L Reagents all good. Entered values in PWQ sheet. Equipment okay. W11749626- VNPS pd8 pump 2 not avaliable - CMU created. Sanitary pit flush complete | East Vaughan Teston Pumping Station | 2026-03-20
WEST | March | On site to respond to outstanding fault on PD8 pump 4 VFD. Found F 25 watchdog fault. Manufacturers troubleshooting guide indicates that this is a micro processor overload fault. The troubleshooting guide recommends that if this is not a persistent problem, which it has not been, to just go ahead and try a reset and see if the problem goes away. Reset the drive and the fault is clear. If the problem persists we will have to look further at the main control board. Also, installed vibration dampening screws on fuel system outside, and inside, audible alarms in an effort to reduce the volume from these alarm horns. | East Vaughan Teston Pumping Station | 2026-03-05
WEST | March | On site for station check Check trends: All okay 11:15- Verified analyzer Grab free CL2- 0.03 mg/L Analyzer Free Cl2- 0.04 mg/L Grab Total CL2- 2.02 mg/L Analyzer Total CL2- 2.03 mg/L Reagents all good Entered values in PWQ sheet. Equipment okay. | East Vaughan Teston Pumping Station | 2026-03-06
WEST | March | On site for station check Check trends: All okay 09:55- Verified analyzer Grab free CL2- 0.05 mg/L Analyzer Free Cl2- 0.02 mg/L Grab Total CL2- 2.03 mg/L Analyzer Total CL2- 2.07 mg/L Reagents all good. Entered values in PWQ sheet. Equipment okay. W11663655- Sanitary pit flush complete | East Vaughan Teston Pumping Station | 2026-03-13
WEST | March | On site for station check Check trends: All okay Zero calibrated free cl2 analyzer 12:00- Verified analyzer Grab free CL2- 0.05 mg/L (Avg:0.03,0.07,0.05) Analyzer Free Cl2- 0.15 mg/L Adjusted the value to 0.05 mg/L Grab Total CL2- 2.04 mg/L Analyzer Total CL2- 2.06 mg/L Reagents all good. Entered values in PWQ sheet. Equipment okay. Sanitary pit flush complete | East Vaughan Teston Pumping Station | 2026-03-27
WEST | March | On site for station check Site offline all ok | Holland Landing East Elevated Tank | 2026-03-11
WEST | March | -on site to complete following work order -JHSC inspection: all ok -chamber inspection: tested flood and temp alarm - tower still double isolated -generator run: no issues - topped up gas - low temp alarm: all ok | Holland Landing East Elevated Tank | 2026-03-19
WEST | March | -on site for station check -tower isolated -no issues | Holland Landing East Elevated Tank | 2026-03-23
WEST | March | On site for station check Site offline all ok | Holland Landing East Elevated Tank | 2026-03-05
WEST | March | On site to complete station check. Site offline all ok | Holland Landing East Elevated Tank | 2026-03-16
WEST | March | On site to complete station check. Free Chlorine 0.06mg/L Total Chlorine 1.10mg/L No issues on site | Holland Landing Sherwood Pumping Station | 2026-03-13
WEST | March | On site to complete station check. Free Chlorine 0.08mg/L Total Chlorine 1.36mg/L No issues on site | Holland Landing Sherwood Pumping Station | 2026-03-09
WEST | March | -on site for station check -checked trends: all ok -entered readings in PWQ: all ok -took chlorine grab 11:45 -free cl: 0.11mg/l -total cl: 1.45mg/l -equipment all ok | Holland Landing Sherwood Pumping Station | 2026-03-02
WEST | March | On site to complete station check. Free Chlorine 0.06mg/L Total Chlorine 1.41mg/L No issues on site | Holland Landing Sherwood Pumping Station | 2026-03-16
WEST | March | On site for the following work orders Diesel test run - elec and contractor on site to run generator for annual inspection Gen start hrs 1431.6 stop 1433.7 Gen start fuel 667L stop 623L Valve exercise Prv Y screen House keeping Low temp alarm Jhsc inspection No issues on site | Holland Landing Sherwood Pumping Station | 2026-03-17
WEST | March | On site to facilitate the load testing of the generator. Test complete. System back to normal with no outstanding alarms. | Holland Landing Sherwood Pumping Station | 2026-03-17
WEST | March | -on site for station check -checked trends: all ok -entered reading in PWQ: all ok -took chlorine grab 14:10 -free cl: 0.04mg/l -total cl: 1.14mg/l -equipment all ok | Holland Landing Sherwood Pumping Station | 2026-03-23
WEST | March | Details: -on site for station check -checked trends: all ok -entered readings in PWQ: all ok -took chlorine grab 10:10 -free cl: 0. 07 mg/l -total cl: 1.46 mg/l -equipment all ok | Holland Landing Sherwood Pumping Station | 2026-03-06
WEST | March | -on site for station check -checked trends: all ok -took reading in PWQ: all ok -took chlorine grab 13:05 -free cl: 0.07mg/l -total cl: 1.67mg/l -equipment all ok | Holland Landing Sherwood Pumping Station | 2026-03-20
WEST | March | Silicate top up: (from 0.469/0.447 to 0.816/0.855cm) | Holland Landing Well No. 1 | 2026-03-30
WEST | March | On site for hypo delivery | Holland Landing Sherwood Pumping Station | 2026-03-10
WEST | March | - on site to troubleshoot ammonia pump 1 and silicate pump 1 - replaced element in silicate pump 1 and cleaned silicate system -cleaned injection points, tested check valves and reprimed pumps - ammonia pump 1 airlocked - purged air the relief line and adjusted relief valve - | Holland Landing Well No. 1 | 2026-03-30
WEST | March | -on site for station check -checked trends: all ok -entered reading in PWQ: all ok -verified analyzer -influent 10:05: 2.92mg/l grab:2.92mg/l -effluent 10:35: 2.74mg/l grab: 2.78mg/l -treated free 10:10: 0.14mg/l grab: 0.16mg/l -treated total 10:15: 3.28mg/l grab: 3.24mg/l -reagents all ok -topped up ammonia tank 1 16cm - 76cm | Holland Landing Well No. 1 | 2026-03-02
WEST | March | On site responding to low treated analyzers Verified analyzers started back flushing at 14:10hrs placed dechlor in chamber. Well was off and not directing to user during this time. | Holland Landing Well No. 1 | 2026-03-31
WEST | March | On site for station check Residuals Treated Total Grab: 2.84mg/L Analyzer: 3.04mg/L Treated Free Grab: 0.15mg/L, Analyzer: 0.34mg/L Effluent Free Grabs: 2.82mg/L, Analyzer: 2.79mg/L Influent Free Grabs: 2.56mg/L, Analyzer: 2.45mg/L Unable to adjust analyzer as buttons aren?t working will create workorder for inst Site in manual off after sampling for main break | Holland Landing Well No. 1 | 2026-03-31
WEST | March | On site for station check Residuals Treated Total Grab: 3.30mg/L Analyzer: 3.26mg/L Treated Free Grab: 0.2mg/L, Analyzer: 0.19mg/L Effluent Free Grabs: 2.54mg/L, Analyzer: 2.61mg/L Influent Free Grabs: 2.75mg/L, Analyzer: 2.81mg/L Performed advanced monitoring (SL1000) Total Chlorine 3.30mg/L Mono 2.69mg/L FA 0.04mg/L TA 0.57mg/L found leak on ammonia pump 1, repaired leak and adjusted pump stroke from 85 to 100 | Holland Landing Well No. 1 | 2026-03-11
WEST | March | Details: On site for station check Residuals Treated Total Grab: 3.20 mg/L Analyzer: 3.28mg/L Treated Free Grab: 0.14mg/L, Analyzer: 0.15mg/L Effluent Free Grabs: 2.82 mg/L, Analyzer: 2.74mg/L Influent Free Grabs: 2.94 mg/L, Analyzer: 2. 83mg/L Performed advanced monitoring (SL1000) Total Chlorine 3.55mg/L Mono 2.93mg/L FA 0.09mg/L TA 0.67mg/L No issues on site | Holland Landing Well No. 1 | 2026-03-06
WEST | March | On site for station check Residuals Treated Total Grab: 2.62mg/L Analyzer: 2.55mg/L Treated Free Grab: 0.20mg/L, Analyzer: 0.14mg/L Effluent Free Grabs: 2.12mg/L, Analyzer: 2.03mg/L Influent Free Grabs: 2.78mg/L, Analyzer: 2.78mg/L Performed advanced monitoring (SL1000) Total Chlorine 2.68mg/L Mono 2.10mg/L FA 0.05mg/L TA 0.42mg/L Found leak on ammonia p1 discharge - changed out fitting and pressure tested all seemed ok - placed pump in duty 1 will monitor No issues on site | Holland Landing Well No. 1 | 2026-03-13
WEST | March | On site for the following HLW1, JHSC Health and Safety Inspection, Holland Landi HLW1, Flow Control Valve, Test, Holland Landing W1 (1M) HLW1, Chlorine Scrubber, Check, Holland Landing W1 (1M) HLW1, Chlorine Gas Detector, Test, Holland Landing W1 (1M) HLW1, Chlorine Analyzer, Maintenance, Holland Landing W1 (1M) HLW1, Chlorinator, Inspection, Holland Landing, Well 1 (6M) HLW1, Turbidity Analyzer TU5300, Maintenance and Calibration, Holland Landing W1 (1M) HLW1, Chemical System Inspection - Chlorine , Holland Landing W1 (1M) HLW1, Chemical System Inspection - Silicate, Holland Landing W1 (1M) HLW1, CIZ Emergency Repair Kit Inspection, Holland Landing W1 (1M) HLW1, Chemical System Inspection - Ammonia, Holland Landing Well 1 (1M) Changed chlorine cylinder 1 with Tim Hudson from 0-68kg | Holland Landing Well No. 1 | 2026-03-10
WEST | March | On site for station check Residuals Treated Total Grab: 3.42mg/L Analyzer: 3.36mg/L Treated Free Grab: 0.11mg/L, Analyzer: 0.15mg/L Effluent Free Grabs: 2.68mg/L, Analyzer: 2.73mg/L Influent Free Grabs: 2.90mg/L, Analyzer: 2.82mg/L Performed advanced monitoring (SL1000) Total Chlorine 3.51mg/L Mono 2.94mg/L FA 0.12mg/L TA 0.70mg/L Changed out treated free reagents No issues on site | Holland Landing Well No. 1 | 2026-03-09
WEST | March | **Disregard the following entry meant for hlw2** On site for station check Residuals Treated Total Grab: 1.50mg/L Analyzer: 1.45mg/L Treated Free Grab: 0.05mg/L, Analyzer: 0.03mg/L Effluent Free Grabs: 0.93mg/L, Analyzer: 0.83mg/L Influent Free Grabs: 2.58mg/L, Analyzer: 2.57mg/L No issues on site | Holland Landing Well No. 1 | 2026-03-16
WEST | March | -on site to complete station check -checked trends: all ok -entered readings in PWQ: all ok -verified analyzer -influent 10:05: 2.93mg/l grab: 2.80mg/l - adjusted -effluent 10:10: 2.53mg/l grab: 2.50mg/l -treated free 10:15: 0.14mg/l grab: 0.15mg/l -treated total 10:20: 3.17mg/l grab: 3.10mg/l -adjusted -reagents all ok -investigated ammonia pump 1 - airlocked - adjusted air relief and purged air -man/started well -completed general housekeeping and washroom inspection -equipment all ok | Holland Landing Well No. 1 | 2026-03-23
WEST | March | Details: On site for station check and to collect bacti sample w11637907 Residuals Treated Total Grab: 3.36mg/L Analyzer: 3.41mg/L Treated Free Grab: 0.13mg/L, Analyzer: 0.15mg/L Effluent Free Grabs: 2.52mg/L, Analyzer: 2.64mg/L Influent Free Grabs: 2.84mg/L, Analyzer: 2.79mg/L Performed advanced monitoring (SL1000) Total Chlorine 3.35mg/L Mono 2.81mg/L FA 0.09mg/L TA 0.65mg/L No issues on site | Holland Landing Well No. 1 | 2026-03-04
WEST | March | -on site for station check -checked trends: all ok -entered reading in PWQ: silicate dose low - placed Nasi pump 1 man/off -verified analyzer -influent 11:30: 2.74mg/l grab: 2.70mg/l -effluent 11:35: 2.56mg/l grab: 2.54mg/l -treated free 11:40: 0.19mg/l grab: 0.16mg/l -treated total 11:45: 3.11mg/l grab: 3.08mg/l -reagents all ok -installed air relief line on ammonia pump 1 -ammonia pump 2 max flow set 145ml/min -ammonia pump 1 max flow 110ml/min | Holland Landing Well No. 1 | 2026-03-20
WEST | March | On site for station check Residuals Treated Total Grab: 3.30mg/L Analyzer: 3.12mg/L Treated Free Grab: 0.15mg/L, Analyzer: 0.21mg/L Effluent Free Grabs: 2.82mg/L, Analyzer: 2.79mg/L Influent Free Grabs: 2.80mg/L, Analyzer: 2.82mg/L Performed advanced monitoring (SL1000) Total Chlorine 3.30mg/L Mono 2.45mg/L FA 0.00mg/L TA 0.47mg/L Changed out effluent reagents Primed ammonia p1 as it?s air locked No issues on site | Holland Landing Well No. 1 | 2026-03-27
WEST | March | -on site to complete station check and collect weekly bacti W11673099 -checked trends: all ok -entered readings in PWQ -verified analyzer -influent 11.50: 2.84mg/l grab: 2.88mg/l -effluent 11.55: 2.54mg/l grab: 2.64mg/l - adjusted -treated free 12:00: 0.16mg/l grab: 0.14mg/l -treated total 12:05: 3.04mg/l grab: 3.06mg/l -reagents all ok -topped up ammonia tank 2 17cm - 77cm -ammonia pump 1 airlock when tank switch over - purged air -equipment all ok | Holland Landing Well No. 1 | 2026-03-18
WEST | March | On site for station check and to collect bacti sample w11690350 Residuals Treated Total Grab: 3.14mg/L Analyzer: 3.15mg/L Treated Free Grab: 0.13mg/L, Analyzer: 0.15mg/L Effluent Free Grabs: 2.76mg/L, Analyzer: 2.78mg/L Influent Free Grabs: 2.84mg/L, Analyzer: 2.84mg/L Performed advanced monitoring (SL1000) Mono 2.79mg/L FA 0.04mg/L TA 0.59mg/L No issues on site | Holland Landing Well No. 1 | 2026-03-25
WEST | March | On site for station check Residuals Treated Total Grab: 3.20mg/L Analyzer: 3.28mg/L Treated Free Grab: 0.11mg/L, Analyzer: 0.16mg/L Effluent Free Grabs: 2.58mg/L, Analyzer: 2.65mg/L Influent Free Grabs: 2.78mg/L, Analyzer: 2.81mg/L Performed advanced monitoring (SL1000) Total Chlorine 3.11mg/L Mono 2.80mg/L FA 0.01mg/L TA 0.56mg/L Changed out influent reagents No issues on site | Holland Landing Well No. 1 | 2026-03-16
WEST | March | Silicate top up (Before: 23.8cm), (after still equalizing) | Holland Landing Well No. 2 | 2026-03-30
WEST | March | On site for station check and to collect bacti sample w1170616 Residuals Treated Total Grab: 3.08mg/L Analyzer: 3.04mg/L Treated Free Grab: 0.11mg/L, Analyzer: 0.15mg/L Effluent Free Grabs: 2.52mg/L, Analyzer: 2.45mg/L Influent Free Grabs: 2.70mg/L, Analyzer: 2.68mg/L No issues on site. site in manual off for main break. | Holland Landing Well No. 2 | 2026-03-31
WEST | March | -on sit to change cylinder and troubleshoot silicate leak alarm - changed cylinder - 43kg-97.3kg - silicate pump 1 check valve was passing - cleaned check valves/replaced tubing element/ tested check valves and reprimed both pumps/reset alarms -cleaned water out of room | Holland Landing Well No. 2 | 2026-03-30
WEST | March | -on site to complete station -checked trends: all ok -entered reading in PWQ: all ok -verified analyzers -influent 13:35: 2.69mg/l grab: 2.60mg/l - adjusted -effluent 13.30: 2.40mg/l grab 2.34mg/l - adjusted -treated free 13:35: 0.12mg/l grab: 0.13mg/l -treated total 13:40: 3.06mg/l grab: 3.06mg/l -reagents all ok -topped up ammonia tank 1 16 -76cm -equipment all ok | Holland Landing Well No. 2 | 2026-03-02
WEST | March | On site to top up ammonia tank 2 from 20-80cm Installed knew check on ammonia p1 suction | Holland Landing Well No. 2 | 2026-03-31
WEST | March | On site to complete chlorinator overhaul (annual). Rebuilt chlorinators 1 and 2 with annual kits, rotameter stoppers, and orifice. Completed 11 point calibration on chlorinators. Tested for vacuum and capacity, all appears good. Backflush small volume with dechlor in outfall chamber, to remove highly chlorinated slugs from influent (purging and calibration). Run HLW2 manual on to test chlorination. Used backwash reset button to account for distribution water in CT after backflush. Residuals: mg/L 1354 Effluent Cl G: FCl 0.30 tcl 1.71 A: FCl 0.31 (Confirming distribution water at effluent after backflush). | Holland Landing Well No. 2 | 2026-03-13
WEST | March | On site for station check Residuals Treated Total Grab: 1.54 mg/L Analyzer: 1.53 mg/L Treated Free Grab: 0.01 mg/L, Analyzer: 0.03mg/L Effluent Free Grabs: 1.72mg/L, Analyzer: 1.79mg/ L Sl1000 readings - time: 2:43 pm Nitrite 0.005mg/L Total ammonia 0.40 mg/L Free ammonia 0.09 mg/L Mono 1.56 mg/L | Holland Landing Well No. 2 | 2026-03-13
WEST | March | On site for station check and bacti sample w11637907 Residuals Treated Total Grab: 3.18mg/L Analyzer: 3.09mg/L Treated Free Grab: 0.13mg/L, Analyzer: 0.15mg/L Effluent Free Grabs: 2.48mg/L, Analyzer: 2.45mg/L Influent Free Grabs: 2.62mg/L, Analyzer: 2.65mg/L Performed advanced monitoring (SL1000) Total Chlorine 3.28mg/L Mono 2.32mg/L FA 0.00mg/L TA 0.45mg/L Sharon Valve grab Total Chlorine 2.09mg/L Changed out influent free reagents | Holland Landing Well No. 2 | 2026-03-04
WEST | March | -on site to complete station check -check trends all ok -entered readings in PWQ: all ok -verified analyzer -influent 10:00: 2.69mg/l grab: 2.70mg/l -effluent 10:05: 1.92mg/l grab: 1.95mg/l -treated free 10:10: 0.16mg/l grab: 0.14mg/l -treated total 10:15: 2.64mg/l grab: 2.62mg/l -changed treated free reagents -troubleshoot ammonia pump 1 - tried new check valve - did not fit - informed team lead - installed air relief line on pump head - completed draw down 80ml/min -topped up ammonia tank 1 16-76cm -man/started well -no other issues | Holland Landing Well No. 2 | 2026-03-20
WEST | March | -on site for station check -checked trends: all ok -entered reading in PWQ: all ok -verified analyzer -influent 10:55: 2.66mg/l grab: 2.56mg/l - adjusted -effluent 11:00: 2.38mg/l grab: 2.38mg/l -treated free 11:05: 0.15mg/l grab: 0.15mg/l -treated total 11:10: 3.12mg/l grab: 3.10mg/l -reagents all ok -Sharon grab 11:15: 1.39mg/l -equipment all ok | Holland Landing Well No. 2 | 2026-03-23
WEST | March | On site to change chlorine cylinder. | Holland Landing Well No. 2 | 2026-03-17
WEST | March | On site for station check Residuals Treated Total Grab: 3.32mg/L Analyzer: 3.20mg/L Treated Free Grab: 0.16mg/L, Analyzer: 0.16mg/L Effluent Free Grabs: 2.58mg/L, Analyzer: 2.62mg/L Influent Free Grabs: 2.76mg/L, Analyzer: 2.74mg/L Performed advanced monitoring (SL1000) Total Chlorine 3.38mg/L Mono 2.59mg/L FA 0.00mg/L TA 0.51mg/L No issues on site | Holland Landing Well No. 2 | 2026-03-27
WEST | March | -on site to investigate chlorinated to opening to 100% -checked trends - appeared influent dropped causing unit to run to 100% -switched chlorinator and observed switch over no issues -no issues with regulators as well - purged air from ammonia pump 1 | Holland Landing Well No. 2 | 2026-03-26
WEST | March | -on site for station check and weekly bacti W11673090 -checked trends: all ok -entered readings in PWQ: all ok -verified analyzer -influent 13:45 : 2.68mg/l grab: 2.64mg/l -effluent 13:50: 2.44mg/l grab: 2.42mg/l -treated free 13:55: 0.14mg/l grab: 0.12mg/l -treated total: 14:00: 3.14mg/l grab: 3.12mg/l -reagents all ok -investigated ammonia pump 1 - airlocks - purged air -investigated ammonia pump 2 - found air relief valve passing - cleaned check valves and stop leaking | Holland Landing Well No. 2 | 2026-03-18
WEST | March | On site for station check Residuals Treated Total Grab: 2.68mg/L Analyzer: 2.71mg/L Treated Free Grab: 0.12mg/L, Analyzer: 0.11mg/L Effluent Free Grabs: 0.22mg/L, Analyzer: 0.19mg/L Influent Free Grabs: 3.16mg/L, Analyzer: 3.18mg/L Sharon Valve grab Total Chlorine 1.83mg/L | Holland Landing Well No. 2 | 2026-03-09
WEST | March | -on site to change cylinder -32.2kg -100.2kg | Holland Landing Well No. 2 | 2026-03-10
WEST | March | On site for the following HLW2, JHSC Health and Safety Inspection, Holland Landing Well 2 (1M) HLW2, Chlorine Gas Detector, Test, Holland Landing, Well 2 (1M) HLW2, Chlorine Analyzer Maintenance, Holland Landing, Well 2 (1M) HLW2, Silicate Peristaltic Pump Inspection, Holland Landing Well 2 (1200 Hrs.) HLW2, Chemical System Inspection - Chlorine, Holland Landing W2 (1M) HLW2, Pressure Relief Valve, Maintenance, Holland Landing, Well 2 (1M) HLW2, Chlorine Scrubber, Check, Holland Landing, Well 2 (1M) HLW2, Low/High Temperature Alarm, Test, Holland Landing Well 2 (1M) HLW2, Turbidimeter, Maintenance, Holland Landing, Well 2 (1M) HLW2, HLW2 Chemical System Inspection - Silicate, Holland Landing W2 (1M) HLW2, Chemical System Inspection - Ammonia, Holland Landing Well 2 (1M) HLW2, Pressure Relief Valve, Maintenance, Holland Landing, Well 2 (1M) HLW2, Eye Wash, Cleaning & Solution Replacement, Holland Landing Well 2 (6M) HLW2, Ammonia Diaphragm Pump Inspection, Holland Landing W2 (1200 Hrs.) Changed out effluent free reagents. No issues on site | Holland Landing Well No. 2 | 2026-03-12
WEST | March | On site for station check Residuals Treated Total Grab: 3.04mg/L Analyzer: 2.95mg/L Treated Free Grab: 0.15mg/L, Analyzer: 0.13mg/L Effluent Free Grabs: 2.38mg/L, Analyzer: 2.32mg/L Influent Free Grabs: 2.44mg/L, Analyzer: 2.51mg/L Performed advanced monitoring (SL1000) Mono 2.32mg/L FA 0.00mg/L TA 0.44mg/L Sharon Valve grab Total Chlorine 2.02mg/L | Holland Landing Well No. 2 | 2026-03-06
WEST | March | **entrys not remote just was put in hlw1 elog by mistake** On site for station check Residuals Treated Total Grab: 1.50mg/L Analyzer: 1.45mg/L Treated Free Grab: 0.05mg/L, Analyzer: 0.03mg/L Effluent Free Grabs: 0.93mg/L, Analyzer: 0.83mg/L Influent Free Grabs: 2.58mg/L, Analyzer: 2.57mg/L No issues on site | Holland Landing Well No. 2 | 2026-03-17
WEST | March | On site for station check Residuals Treated Total Grab: 2.68mg/L Analyzer: 2.71mg/L Treated Free Grab: 0.13mg/L, Analyzer: 0.13mg/L Effluent Free Grabs: 2.30mg/L, Analyzer: 2.37mg/L Influent Free Grabs: 2.52mg/L, Analyzer: 2.59mg/L Sharon Valve grab | Holland Landing Well No. 2 | 2026-03-11
WEST | March | - change chlorine cylinder 35.6kg - 103.6kg | Holland Landing Well No. 2 | 2026-03-03
WEST | March | Onsite to troubleshoot Post Injection AIT. Informed ROC. Noticed the Post Injection AIT lost the program. Cycled the power, reprogrammed the AIT and Enabled analog outputs. Readings came back to normal. No issues. Noticed there was minimal flow to the Post-free AIT. removed the diaphragm and cleaned it. put it back in service. Flow much better. AL Post total AIT - 2.32 mg/l AL POST free AIT - 0.08 mg/l Put the POST AIT back in service. No issues. Informed ROC, Armed the building and left the site. | Holland Landing West Elevated Tank | 2026-03-31
WEST | March | Respond to site power failure, comm failures. Unable to access electrical room, ekey is validated. Re-validated ekey and gained access 0450. All breakers in HLPSYS, HLETYS pipe gallery and electrical room are in closed positions, no obvious signs of tripped equipment (LPA, fed from LPB, all appears normal). Communicated with on call electrician, currently responding to multiple power outages and priority calls. There is a manual transfer switch that can be used with portable generator if necessary (requires electrician for transfer). Power restored approximately 0540. Outstanding historian heartbeat alarm, and post-inj analyzer value on SCADA is OOR. Analyzer is powered on and appears to be working. Cycled power to analyzer. Unable to calibrate Post Depolox Cl analyzer; -calibration menu shows ?bias? set at 7.50mg/L instead of span calibrate option. Grabs: mg/L Post 0558 Grab: FCl 0.04 tcl 2.36 Analyzer: FCl 0.06 tcl 3.60 Pre 0604 G: FCl 0.05 tcl 2.30 A: FCl 0.08 tcl 2.38 Request INST troubleshoot post-injection chlorine analyzer (CMU to be issued). Request w-MAINT inspect issue with site power out while generator was running. | Holland Landing West Elevated Tank | 2026-03-31
WEST | March | On site to complete station checks and collect bacti sample w11706016 Verified analyzers @09:15 Pre-injection Free chlorine Grab: 0.05mg/L Analyzer: 0.08mg/L Total chlorine Grab: 2.36mg/L Analyzer: 2.35mg/L Post-Injection - inst on site to fix analyzer Free chlorine Grab: 0.05mg/L Analyzer: 0.08mg/L Total chlorine Grab: 2.32mg/L Analyzer 2.35mg/L No other issues on site - wells off unable to do advanced monitoring | Holland Landing West Elevated Tank | 2026-03-31
WEST | March | On site to complete station checks Verified analyzers @ 11:27 Pre-injection Free chlorine Grab: 0.04mg/L Analyzer: 0.04mg/L Total chlorine Grab: 1.71mg/L Analyzer: 1.77mg/L Mono 0.37mg/L FA 0.28mg/L TA 0.35mg/L Nitrite 0.009mg/L Post-Injection Free chlorine Grab: 0.04mg/L Analyzer: 0.02mg/L SL1000 Total chlorine Grab: 2.64mg/L Analyzer 2.77mg/L Mono 1.62mg/L FA 0.19mg/L TA 0.50mg/L Nitrite 0.000mg/L Tank TCL 1.61mg/L Mono 0.42mg/L Nitrite 0.009mg/L FA 0.30mg/L TA 0.38mg/L Nitrate 0.066mg/L | Holland Landing West Elevated Tank | 2026-03-13
WEST | March | 14:47-logged in remotely to investigate pre injection low cl2 After discussion with ORO, decided to run the system till pre total cl2 go below 0.45 mg/L or Post total cl2 goes above 4.00 mg/L and hold the value for more than 2 minutes. | Holland Landing West Elevated Tank | 2026-03-01
WEST | March | On site to complete station check and to collect w11637907 Verified analyzers @0830 Pre-injection while draining Free chlorine Grab: 0.04mg/L Analyzer: 0.05mg/L Total chlorine Grab: 2.40mg/L Analyzer: 2.44mg/L SL1000 while filling as of 08:39hrs Mono 0.44mg/L FA 0.10mg/L TA 0.18mg/L Nitrite 0.004mg/L Post-Injection Free chlorine Grab: 0.08mg/L Analyzer: 0.06mg/L Total chlorine Grab: 2.57mg/L Analyzer 2.88mg/L SL1000 Mono 1.35mg/L FA 0.00mg/L TA 0.26mg/L Nitrite 0.000mg/L Tank TCL 1.70mg/L Mono 0.45mg/L Nitrite 0.004mg/L FA 0.13mg/L TA 0.22mg/L Nitrate 0.128mg/L Reran, post injection ammonia @09:45hrs Mono 1.80mg/L FA 0mg/L TA 0.30mg/L Reagents all ok | Holland Landing West Elevated Tank | 2026-03-04
WEST | March | -on site to complete station check -checked trends: all ok -entered reading in PWQ: all ok -verified post injection 11:55 -analyzer free: 0.06mg/l grab: 0.07mg/l -analyzer total: 2.58mg/l grab: 2.54 mg/l -reagents all ok -verified pre injection 12:05 -analyzer free: 0.05mg/l grab: 0.03mg/l -analyzer total: 2.77mg/l grab: 2.74mg/l -reagents all ok -completed water quality lab | Holland Landing West Elevated Tank | 2026-03-02
WEST | March | On site to complete station check and complete BacT sampling, W11658071 Verified analyzers @ 10:35 Pre-injection Free chlorine Grab: 0.08mg/L Analyzer: 0.05mg/L Total chlorine Grab: 1.88mg/L Analyzer: 1.78mg/L Mono 0.38mg/L FA 0.17mg/L TA 0.24mg/L Nitrite 0.005mg/L Post-Injection Free chlorine Grab: 0.04mg/L Analyzer: 0.03mg/L SL1000 Total chlorine Grab: 2.95mg/L Analyzer 3.13mg/L Mono 1.76mg/L FA 0.07mg/L TA 0.42mg/L Nitrite 0.002mg/L Tank TCL 1.69mg/L Mono 0.43mg/L Nitrite 0.003mg/L FA 0.23mg/L TA 0.32mg/L Nitrate 0.093mg/L | Holland Landing West Elevated Tank | 2026-03-11
WEST | March | On site to respond to fault on tank mixer VFD panel. Upon inspection found burnt wire connections inside VFD control panel. Assessed that a temporary repair could be made and executed said repair. Documented findings and repair for possible warranty claim. | Holland Landing West Elevated Tank | 2026-03-04
WEST | March | On site to complete station check Verified analyzers @0900hrs Pre-injection Free chlorine Grab: 0.03mg/L Analyzer: 0.03mg/L Total chlorine Grab: 1.35mg/L Analyzer: 1.40mg/L Mono 0.26mg/L FA 0.21mg/L TA 0.24mg/L Nitrite 0.000mg/L Post-Injection Free chlorine Grab: 0.05mg/L Analyzer: 0.03mg/L SL1000 Total chlorine Grab: 3.13mg/L Analyzer 2.12mg/L Mono 2.01mg/L FA 0.10mg/L TA 0.49mg/L Nitrite 0.002mg/L Tank TCL 1.60mg/L Mono 0.48mg/L Nitrite 0.002mg/L FA 0.13mg/L TA 0.23mg/L Nitrate 0.099mg/L Reagents all ok | Holland Landing West Elevated Tank | 2026-03-06
WEST | March | On site to complete the following: HLETYS, High & Low Water Level Alarm, Test, Holland Landing West ET (2M) HLETYS, Sensing Line Heat Trace System, Maintenance, Holland Landing West, ET [WINTER] (1M) HLETYS, Low Temperature Alarm, Test, Holland Landing West, ET (1M) HLETYS, Ammonia System Inspection, Holland Landing West ET (1M) HLETYS, Sodium Hypochlorite System Inspection, Holland Landing West ET (1M) HLETYS, Siemens Depolox 5/Micro 2000, Chlorine Analyzer, Maintenance, Holland Landing West ET (1M) HLETYS, Sump Pit System Inspection, Holland Landing West ET (1M) HLETYS, Comprehensive Housekeeping, Holland Landing West ET (1M) No issues found Replaced acetate in post analyzer | Holland Landing West Elevated Tank | 2026-03-05
WEST | March | -on site to respond to mixer uncommanded stop / fault alarms -found mixer with F021 output phase loss fault -tried to reset but fault immediately comes back in -informed CMS to investigate | Holland Landing West Elevated Tank | 2026-03-03
WEST | March | On site to complete station check Verified analyzers @1005hrs Pre-injection Free chlorine Grab: 0.03mg/L Analyzer: 0.03mg/L Total chlorine Grab: 1.52mg/L Analyzer: 1.63mg/L Mono 0.39mg/L FA 0.23mg/L TA 0.30mg/L Nitrite 0.005mg/L Post-Injection Free chlorine Grab: 0.05mg/L Analyzer: 0.02mg/L SL1000 Total chlorine Grab: 1.68mg/L Analyzer 1.88mg/L Mono 0.40mg/L FA 0.24mg/L TA 0.32mg/L Nitrite 0.006mg/L * chemical dosing turned off as flow was less than 20L/s going into the tower Tank TCL 1.75mg/L Mono 0.48mg/L Nitrite 0.004mg/L FA 0.18mg/L TA 0.27mg/L Nitrate 0.118mg/L Reagents all ok | Holland Landing West Elevated Tank | 2026-03-09
WEST | March | On site to complete station checks and collect bacti sample w11690350 Verified analyzers @09:40 Pre-injection Free chlorine Grab: 0.05mg/L Analyzer: 0.04mg/L Total chlorine Grab: 1.78mg/L Analyzer: 1.98mg/L Post-Injection Free chlorine Grab: 0.05mg/L Analyzer: 0.02mg/L SL1000 Total chlorine Grab: 2.84mg/L Analyzer 3.08mg/L All Readings entered into pwq sheet | Holland Landing West Elevated Tank | 2026-03-25
WEST | March | -on site to re-verify pre total reading 14:20 -analyzer 2.84mg/l - grab: 2.46mg/l - adjusted | Holland Landing West Elevated Tank | 2026-03-23
WEST | March | -on site for station check and weekly bacti W11673909 -checked trends: all ok -entered reading in PWQ: all ok -verified analyzer -post analyzer 09:45 -free: 0.03mg/l grab: 0.06mg/l -total: 2.56mg/l grad 2.60mg/l -topped up reagents -pre analyzer 10:00 -free: 0.06mg/l grab: 0.05mg/l -total: 2.28mg/l grab: 2.48mg/l - adjusted -topped up reagents -equipment all ok -will follow up with team lead regarding water quality results | Holland Landing West Elevated Tank | 2026-03-18
WEST | March | On site for station check Verified analyzers Readings in pwq sheet - adjusted inlet free ammonia from 0.30-0.25mg/L as post ammonia grabs were low Reagents all okay | Holland Landing West Elevated Tank | 2026-03-27
WEST | March | -on site for station check -checked trends: all ok -entered reading in PWQ: all ok -verified pre analyzer 12:20 -analyzer free: 0.02mg/l grab: 0.03mg/l -analyzer total: 1.13mg/l grab: 1.30mg/l -reagents all ok -verified post analyzer 12:40 -analyzer free: 0.01mg/l grab: 0.03mg/l -analyzer total: 2.83mg/l grab: 2.80mg/l -reagents all ok -made following adjustments - hypo pump 1 195- 175ml/min -hypo pump 2 195 - 185ml/min -inlet free ammonia 0.25mg/l - .30mg/l -topped up hypo tank - 249-304L -no other issues | Holland Landing West Elevated Tank | 2026-03-23
WEST | March | On site to complete station checks Verified analyzers @ 10:30 Pre-injection Free chlorine Grab: 0.05mg/L Analyzer: 0.04mg/L Total chlorine Grab: 1.79mg/L Analyzer: 1.70mg/L Mono 0.42mg/L FA 0.24mg/L TA 0.32mg/L Nitrite 0.006mg/L Post-Injection Free chlorine Grab: 0.05mg/L Analyzer: 0.03mg/L SL1000 Total chlorine Grab: 3.14mg/L Analyzer 3.29mg/L Mono 1.69mg/L FA 0.0.03mg/L TA 0.0.36mg/L Nitrite 0.000mg/L Tank TCL 1.85mg/L Mono 0.48mg/L Nitrite 0.004mg/L FA 0.24mg/L TA 0.33mg/L Nitrate 0.134mg/L Adjusted pre free ammonia on scada from 0.28-0.25mg/L based off the pre and post results above. Topped up ammonia tank from 38-68cms | Holland Landing West Elevated Tank | 2026-03-16
WEST | March | -on site to complete station check -checked trends: all ok -entered readings in PWQ -verified analyzer -pre injection 13.20 -analyzer free: 0.03mg/l grab: 0.04mg/l -analyzer total: 1.20mg/l grab: 1.28mg/l- adjusted -reagents all ok -post injection 13:30 -analyzer free 0.02mg/l grab: 0.04mg/l -analyzer total: 3.02mg/l grab: 3.00mg/l -reagents all ok -due to high incoming ammonia adjusted hypo pump 2 195ml/min to 185ml/min - will monitor -equipment all ok | Holland Landing West Elevated Tank | 2026-03-20
WEST | March | -on site to meet hypo delivery -290 - 600 - top up level bouncing due to high level | Holland Landing West Elevated Tank | 2026-03-24
WEST | March | conducted station check checked trends: all ok Station duty active; Pump 1 and 4 running. 11:50- Grabs taken Grab free Cl2: 0.08mg/l Grab total Cl2: 2.00mg/l equipment all ok | Jefferson Pumping Station & Reservoir | 2026-03-30
WEST | March | On site to complete station check, operational sample and weekly bacti W11705742 Checked trends: all ok Took chlorine grab and sample West cell 14:45 Free CL2: 0.06mg/l Total CL2: 2.02mg/l East cell 14:50 Free CL2: 0.05mg/l Total CL2: 2.10 mg/l Equipment all ok Entered reading PWQ: all ok | Jefferson Pumping Station & Reservoir | 2026-03-31
WEST | March | -Responded P1,P2, P3 fault alarm -P1 control voltage low, P2 &P3 valve fail to open - reset alarms in MCC - P1 started in auto duty 1 | Jefferson Pumping Station & Reservoir | 2026-03-31
WEST | March | -reset power alarms -generator currently -pump 3 fail to start - will attend | Jefferson Pumping Station & Reservoir | 2026-03-03
WEST | March | On site for the following PM work orders. Informed ROC about the works being done. W11650338 JFPS, Standby Power Generator Test Run and Run Hours log Pre check Battery okay- 26.52V Coolant- Okay Oil - Okay Before Start Start time- 09:45 Run time- 671.1 hr Fuel level-9023L/167.2cm JFPS pump 3 running manual. After Stop Stop time- 11:00 Run time- 672.6 hr Fuel level-8963L/165.9 cm W11651916 JFPS, Dehumidifier Inspection & Cleaning, W11650352 JFPS, Sump Pit System Inspection W11650887 JFPS, Manual Valves Exercise W11650901 JFPS, Actuated Valves Exercise & Inspection, W11651273 JFPS, Pump & Motor Inspection W11651760 JFPS, Ventilation System Inspection W11651770 JFPS, Low Temperature Alarm Test W11651781 JFPS, Hoist System Inspection W11650643 JFRS, Sump Pit System Inspection W11650656 JFRS, Ventilation System Inspection W11651841 JFRS, Dehumidifier Inspection & Cleaning, W11651235 JFRS, JHSC Health and Safety Inspection, W11652030 JFRS, External Venting Screens Inspection, W11651245 JFRS, Sump Pit System Inspection, ValveHouse W11651258 JFRS, Actuated Valve Exercise & Inspection,ValveHouse W11651722 JFRS, Flood Alarm Test Jefferson Valve House, ValveHouse W11651732 JFRS, Manual Valves Exercise, Jefferson, ValveHouse W11651746 JFRS, Dehumidifier Inspection & Cleaning,ValveHouse | Jefferson Pumping Station & Reservoir | 2026-03-10
WEST | March | -on site to complete station check and weekly bacti W11637582 -checked trends: all ok -entered readings in PWQ: all ok -took chlorine grab and sample from west cell 14:15 -free cl: 0.08mg/l -total cl: 2.01mg/l -east cell chlorine grab 14:20 -free cl: 0.11mg/l -total cl: 1.95mg/l -equipment all ok | Jefferson Pumping Station & Reservoir | 2026-03-04
WEST | March | On site for station check Check trends; All okay Station duty active; Pump 3 & 4 running 14:05 grabs taken Free cl2- 0.07 mg/l total cl2- 1.84 mg/l entered values in PWQ sheet. equipment okay | Jefferson Pumping Station & Reservoir | 2026-03-06
WEST | March | On site for station check Check trends; All okay Station duty active; Pump 3 & 4 running 14:44 grabs taken Free cl2- 0.04 mg/l total cl2- 1.79 mg/l entered values in PWQ sheet. equipment okay | Jefferson Pumping Station & Reservoir | 2026-03-09
WEST | March | -on site for station check -checked trends: all ok -entered readings in PWQ: all ok -took chlorine grab 10:00 -free cl: 0.07mg/l -total cl: 2.05mg/l -equipment all ok | Jefferson Pumping Station & Reservoir | 2026-03-03
WEST | March | Vibration readings | Jefferson Pumping Station & Reservoir | 2026-03-17
WEST | March | On site to complete station check and weekly bacti W11657067 Checked trends: all ok Took chlorine grab and sample East cell 14:00 Free CL2: 0.05mg/l Total CL2: 2.04mg/l West cell 14:00 Free CL2: 0.03mg/l Total CL2: 2.00 mg/l Equipment all ok Entered reading PWQ: all ok | Jefferson Pumping Station & Reservoir | 2026-03-11
WEST | March | Chris Iliohan Tyler Smith into take Pump 2 out of service. Rebuild is required | Jefferson Pumping Station & Reservoir | 2026-03-20
WEST | March | Station Check (pumping station) (no issues found) Input data to PWQ 14:00 Chlorine grab (mg/l) Free: 0.04, Total 1.99 | Jefferson Pumping Station & Reservoir | 2026-03-23
WEST | March | On site for station check Check trends; All okay Station duty active; Pump 3 & 4 running 14:45 grabs taken Free cl2- 0.06 mg/l total cl2- 2.03 mg/l entered values in PWQ sheet. equipment okay | Jefferson Pumping Station & Reservoir | 2026-03-27
WEST | March | Vibration readings and grease pump 1 and two | Jefferson Pumping Station & Reservoir | 2026-03-27
WEST | March | Vibration readings 3 and 4 Help with pump 2 | Jefferson Pumping Station & Reservoir | 2026-03-24
WEST | March | On site to complete station check, operational sample and weekly bacti W11672961 Checked trends: all ok Took chlorine grab and sample West cell 14:45 Free CL2: 0.01mg/l Total CL2: 1.88mg/l East cell 14:40 Free CL2: 0.07mg/l Total CL2: 1.95 mg/l Equipment all ok Entered reading PWQ: all ok | Jefferson Pumping Station & Reservoir | 2026-03-18
WEST | March | On site for station check Check trends; All okay Station duty active; Pump 1 & 4 running 14:22 grabs taken Free cl2- 0.00 mg/l total cl2- 2.17 mg/l entered values in PWQ sheet. equipment okay | Jefferson Pumping Station & Reservoir | 2026-03-20
WEST | March | On site to complete station check and weekly bacti W11690336 Checked trends: all ok Took chlorine grab and sample East cell 14:50 Free CL2: 0.02mg/l Total CL2: 2.06mg/l West cell 14:55 Free CL2: 0.05mg/l Total CL2: 2.06 mg/l Equipment all ok Entered reading PWQ: all ok | Jefferson Pumping Station & Reservoir | 2026-03-25
WEST | March | On site for station check Check trends; All okay Station duty active; Pump 3 & 4 running 14:00 grabs taken Free cl2- 0.07 mg/l total cl2- 2.07 mg/l entered values in PWQ sheet. equipment okay | Jefferson Pumping Station & Reservoir | 2026-03-16
WEST | March | - on site to reconnect pump 2. connected and tested to confirm rotation. left pump in manual off for the time being and let Cole W know that we should put an interm procedure in to run that pump an hour a day for a week to break in the bearings. under direction of oic | Jefferson Pumping Station & Reservoir | 2026-03-25
WEST | March | Restarted the Operator Interface Terminal due to Windows Operating System software updates. | King City Dufferin Booster Pumping Station | 2026-03-30
WEST | March | On site for station check and bacti sample w11690350 Residuals Treated Total Grab: 2.98mg/L Analyzer: 3.07mg/L Treated Free Grab: 0.13mg/L, Analyzer: 0.16mg/L Effluent Free Grabs: 2.35mg/L, Analyzer: 2.28mg/L Influent Free Grabs: 3.52mg/L, Analyzer: 3.39mg/L Performed advanced monitoring (SL1000) Mono 2.34mg/L FA 0.05mg/L TA 0.51mg/L Changed out chlorine cylinder 1 with Tim Hudson from 0-68kg Changed out treated total reagents Treated total analyzer climbing took another grab at 13:35hrs of 3.44mg/L adjusted analyzer from 3.65-3.44mg/L after multiple grabs | Holland Landing Well No. 2 | 2026-03-25
WEST | March | On site to investigate pre injection low cl2 - CMU W11697567. Up on initial assessment, identified the pre injection analyzer ran out of acetate buffer solution. Topped the acetate buffer solution and waited for the value to climb up naturally. 17:30- verified post injection analyzer Grab free Cl2- 0.04 mg/L Analyzer free Cl2- 0.06 mg/L Grab Total Cl2- 2.56 mg/L Analyzer Total Cl2- 2.55 mg/L 17:38- verified pre injection analyzer Grab free Cl2- 0.05 mg/L (Avg 0.04,0.05,0.06) Analyzer free Cl2- 0.06 mg/L Adjusted analyzer down to 0.05 mg/l Grab Total Cl2- 2.50 mg/L Analyzer Total Cl2- 2.55 mg/L Activated duty. Cl2 pump kicked on, post injection total values climbing. Everything looks normal. Pre inj Low cl2 was due to analyzer malfunction. | Holland Landing West Elevated Tank | 2026-03-01
WEST | March | Station check (no issues found) entered data to PWQ 10:00 Chlorine Residual Grab (mg/L) Free 0.03, Total 1.70 | King City Dufferin Booster Pumping Station | 2026-03-13
WEST | March | -on site to complete station check -system duty not active -checked equipment -reviewed trends -recorded readings in PWQ sheet -checked residuals: 14:05 - Grabs: Free Chlorine = 0.00 mg/L Total Chlorine = 1.80 mg/L -no issues found | King City Dufferin Booster Pumping Station | 2026-03-06
WEST | March | -on site to complete station check -system duty not active -checked equipment -reviewed trends -recorded readings in PWQ sheet -checked residuals: 09:43 - Grabs: Free Chlorine = 0.00 mg/L Total Chlorine = 1.82 mg/L -no issues found | King City Dufferin Booster Pumping Station | 2026-03-09
WEST | March | Check no hot water 600 V sending electrician to service unit | King City Dufferin Booster Pumping Station | 2026-03-19
WEST | March | -on site to complete station check -system duty active -checked equipment -reviewed trends -recorded readings in PWQ sheet -checked residuals: 09:41 - Grabs: Free Chlorine = 0.00 mg/L Total Chlorine = 1.74 mg/L -no issues found | King City Dufferin Booster Pumping Station | 2026-03-20
WEST | March | On site to troubleshoot and repair tankless water heater. Found flow switch out of adjustment. Corrected and tested for proper operation. | King City Dufferin Booster Pumping Station | 2026-03-23
WEST | March | -on site for station check -check trends: -entered reading in PWQ: all ok -took chlorine grab:08:30 -free cl: 0.08mg/l -total cl: 1.52mg/l -started sump pump at KCETDS to clear flood alarm -no other issues | King City Dufferin Booster Pumping Station | 2026-03-27
WEST | March | In to complete station check. Enter data into PWQ. No issues. | King City Dufferin Booster Pumping Station | 2026-03-23
WEST | March | -On-site to complete station check and collect sample -system duty not active, tower = 75 % -checked equipment -reviewed trends -CL17 reagents ok -verified chlorine analyzers: 13:36 - Analyzer readings: Free Chlorine = 0.05 mg/L Total Chlorine = 1.74 mg/L 13:36 - Grabs: Free Chlorine = 0.04 mg/L Total Chlorine = 1.68 mg/L MCL = 1.53 mg/L TNH3 = 0.36 mg/L FNH3 = 0.06 mg/L NO2 = 0.004 mg/L temp = 6.9 C 13:43 - collected weekly regulatory micro. sample - W/O # W11705494 -recorded readings in PWQ sheet -no issues found -ran meter chamber sump pump in local | King City Dufferin Elevated Tank | 2026-03-31
WEST | March | -on site to complete station check -system duty not active -found pump 2 discharge valve stuck open, closed valve and returned to auto -tested both pumps due to multiple fail to start alarms, no issues observed -checked equipment -reviewed trends -recorded readings in PWQ sheet -pump #1 hours = 6991.1 -pump #2 hours = 6621.8 -checked residuals: 09:12 - Grabs: Free Chlorine = 0.00 mg/L Total Chlorine = 1.85 mg/L -no issues found | King City Dufferin Booster Pumping Station | 2026-03-02
WEST | March | Responded to Meter chamber flood alarm. Pump not running in auto, ran in hand and verified flow, pumped below flood level and placed back in auto | King City Dufferin Booster Pumping Station | 2026-03-13
WEST | March | -on site to complete work orders -completed JHSC Health and Safety Inspection -found water heater not producing tempered water for eyewash, created work order for CMS -completed Critical Air Valve Flush and Inspection | King City Dufferin Booster Pumping Station | 2026-03-12
WEST | March | -on site to complete station check -system duty not active -checked equipment -reviewed trends -recorded readings in PWQ sheet -checked residuals: 13:19 - Grabs: Free Chlorine = 0.00 mg/L Total Chlorine = 1.78 mg/L -no issues found | King City Dufferin Booster Pumping Station | 2026-03-16
WEST | March | -On-site to complete station check and collect sample -deactivated system duty, tower = 67 % -checked equipment -reviewed trends -CL17 reagents ok -verified chlorine analyzers: 13:16 - Analyzer readings: Free Chlorine = 0.03 mg/L Total Chlorine = 1.65 mg/L 13:16 - Grabs: Free Chlorine = 0.05 mg/L Total Chlorine = 1.68 mg/L MCL = 1.59 mg/L TNH3 = 0.36 mg/L FNH3 = 0.05 mg/L NO2 = 0.004 mg/L temp = 7.0 C 13:21 - collected weekly regulatory micro. sample - W/O # W11657053 -recorded readings in PWQ sheet -no issues found | King City Dufferin Elevated Tank | 2026-03-11
WEST | March | On site to replace UPS batteries inside PAC panel. Site was offline due to planned maintenance, After the batteries were replaced, UPS was tested for 10 min on battery worked ok. | King City Dufferin Elevated Tank | 2026-03-23
WEST | March | -On-site to complete station check and collect sample -system duty not active, tower = 47 % -checked equipment -reviewed trends -CL17 reagents ok -verified chlorine analyzers: 13:31 - Analyzer readings: Free Chlorine = 0.02 mg/L Total Chlorine = 1.59 mg/L 13:31 - Grabs: Free Chlorine = 0.02 mg/L Total Chlorine = 1.62 mg/L MCL = 1.47 mg/L TNH3 = 0.36 mg/L FNH3 = 0.07 mg/L NO2 = 0.004 mg/L temp = 5.4 C 13:35 - collected weekly regulatory micro. sample - W/O # W11672783 -recorded readings in PWQ sheet -no issues found -ran meter chamber sump pump in local while on site -completed Eye Wash Cleaning & Solution Replacement | King City Dufferin Elevated Tank | 2026-03-18
WEST | March | In to start filling of KCETDS for sampling following condition assessment, cleaning, and disinfection. IAM / Landmark spray disinfected 200mg/L chlorine solution to storage at 1232. Flushed riser / drain piping and started filling 1310. Isolated ET at 1430, will continue filling tomorrow morning. | King City Dufferin Elevated Tank | 2026-03-23
WEST | March | -On-site to complete station check -tower currently isolated awaiting sample results post inspection -checked equipment -reviewed trends -CL17 reagents ok -verified chlorine analyzers: 13:13 - Analyzer readings: Free Chlorine = 0.07 mg/L Total Chlorine = 2.11 mg/L 13:13 - Grabs: Free Chlorine = 0.04 mg/L Total Chlorine = 1.65/1.62/1.63 mg/L 13:23 - adjusted total chlorine analyzer to 1.63 mg/L based on average of 3 grabs -recorded readings in PWQ sheet -no issues found -ran meter chamber sump pump in local | King City Dufferin Elevated Tank | 2026-03-25
WEST | March | -on site to isolate tower for inspection -closed inlet valve -put altitude valve into manual and isolated stem ball valve to pin closed -monitored system pressures -switched controlling tower to KCETFS and adjusted duty 60 - 80% 08:45 - tower level = 35%, open KCETFS isolation valve and close KCETDS outlet valve 08:46 - placed dechlorination pucks at tower outfall and began draining tower to waste at 10 l/s 09:20 - collected grab from drainage pond outlet, total chlorine = 0.00 mg/L -put site offline and powered off chlorine analyzers -added dechlorination pucks to tower outfall -leaving tower draining at 10 l/s, will monitor remotely | King City Dufferin Elevated Tank | 2026-03-20
WEST | March | On site to respond to reports of inlet line heat trace low temperature alarm. Found no active alarms. Verified proper operation of heat trace system. Verified proper unit configuration including set points. | King City Dufferin Elevated Tank | 2026-03-17
WEST | March | -on site to fill the tower to overflow and collect sample W11753096 -man/started pump at 100% at KCPSDs -opened altitude valve 100% -opened inlet isolation valve -no flow to system -flushed all sample taps and cleaned -turned on analyzer verified at 08:30 -analyzer total: 1.27mg/l grab: 1.67mg/l -primed analyzers -verified analyzer 10:15 -analyzer total: -analyzer free: -reagents all ok -added dechlor to pond for overflow -tower hit overflow at 10:15 -closed inlet valve/open tie valve - placed KCPSDS in auto -verified analyzer at 10:20 -analyzer free: 0mg/l grab: 0.03mg/l - unable to adjust analyzer -analyzer total: 1.51mg/l grab: 1.83mg/l - adjusted -reagents all ok - | King City Dufferin Elevated Tank | 2026-03-24
WEST | March | -on site to complete work orders -informed ROC of work -completed CL17 Chlorine Analyzer, Maintenance 10:04 - analyzers in clean mode -cleaned analyzers, flushed sample lines -replaced tubing in TCL analyzer and primed 11:02 - collected grab: FCL = 0.00 mg/L TCL = 1.82 mg/L 11:43 - analyzers back online -verified analyzers after maintenance: 11:47 - Analyzer readings: Free Chlorine = 0.03 mg/L Total Chlorine = 1.69 mg/L 11:47 - Grabs: Free Chlorine = 0.05 mg/L Total Chlorine = 1.65 mg/L -tested isolation of tower in preparation for taking tower offline for inspection/ maintenance -opened bypass valve and isolated inlet and outlet valves -monitored system pressures - ok -set KCETFS as controlling tower and activated system duty -no system issues observed running on KCETFS -completed Inlet/Outlet Heat Trace System, Inspection -completed JHSC Health and Safety Inspection -completed Actuated Valve, Exercise & Inspection -completed Low Temperature Alarm Test -completed Ventilation System, Inspection -completed High & Low Water Level Alarm, Test -completed Drain Valve Exercise -completed Dehumidifier, Cleaning & Inspection -returned tower valving to normal operation and set KCETDS to controlling tower -site back to normal operation | King City Dufferin Elevated Tank | 2026-03-12
WEST | March | -on site to put tower back online after passing resultsW11753096 -verified analyzer 14:40 -analyzer free: 0.06mg/l grab: 0.08mg/l -analyzer total: 1.58mg/l grab: 1.68mg/l - adjusted -opened inlet and outlet isolation valves -close the tie valve -no issues -informed control panel | King City Dufferin Elevated Tank | 2026-03-26
WEST | March | -On-site to complete station check and collect sample -system duty active, tower = 64 % -checked equipment -reviewed trends -depolox reagents ok -verified chlorine analyzers: 12:28 - Analyzer readings: Free Chlorine = 0.04 mg/L Total Chlorine = 1.52 mg/L 12:28 - Grabs: Free Chlorine = 0.03 mg/L Total Chlorine = 1.63/1.61/1.63 mg/L SL1000 Readings: MCL = 1.49 mg/L TNH3 = 0.35 mg/L FNH3 = 0.06 mg/L NO2 = 0.004 mg/L temp = 7.1 C 12:35 - collected weekly regulatory micro. sample - W/O # W11705494 12:38 - adjusted total chlorine analyzer to 1.62 mg/L based on average of 3 grabs -recorded readings in PWQ sheet -no other issues found | King City Fisher Elevated Tank | 2026-03-31
WEST | March | -on site to respond to meter chamber flood alarm -ran sump pump in local -cleared alarm -pump back in auto | King City Dufferin Elevated Tank | 2026-03-16
WEST | March | -On-site to complete station check and collect samples -system duty not active, tower = 46 % -checked equipment -reviewed trends -replaced CL17 reagents -verified chlorine analyzers: 13:54 - Analyzer readings: Free Chlorine = 0.02 mg/L Total Chlorine = 1.60 mg/L 13:54 - Grabs: Free Chlorine = 0.03 mg/L Total Chlorine = 1.66 mg/L MCL = 1.54 mg/L TNH3 = 0.36 mg/L FNH3 = 0.06 mg/L NO2 = 0.003 mg/L temp = 6.2 C 13:59 - collected weekly regulatory micro. sample - W/O # W11637334 -collected operational ATP sample -recorded readings in PWQ sheet -no issues found | King City Dufferin Elevated Tank | 2026-03-04
WEST | March | On site to complete monthly work orders including: -portable generator test run -valve exercising -prv inspection -low temperature alarm -housekeeping -analyzer maintenance -health and safety inspection -heat trace system inspection Station operation normal, no issues on site. | King City Fisher Elevated Tank | 2026-03-17
WEST | March | -On-site to complete station check and collect sample -system duty not active, tower = 47 % -checked equipment -reviewed trends -depolox reagents ok -verified chlorine analyzers: 12:15 - Analyzer readings: Free Chlorine = 0.03 mg/L Total Chlorine = 1.63 mg/L 12:15 - Grabs: Free Chlorine = 0.05 mg/L Total Chlorine = 1.51/1.49/1.52 mg/L SL1000 Readings: MCL = 1.43 mg/L TNH3 = 0.35 mg/L FNH3 = 0.07 mg/L NO2 = 0.004 mg/L temp = 5.4 C 12:22 - collected weekly regulatory micro. sample - W/O # W11672783 12:24 - adjusted total chlorine analyzer to 1.51 mg/L based on average of 3 grabs -recorded readings in PWQ sheet -no issues found -closed tower isolation valve to test in preparation for KCETDS isolation, no issues | King City Fisher Elevated Tank | 2026-03-18
WEST | March | -On-site to complete station check and collect samples -system duty not active, tower = 44 % -checked equipment -reviewed trends -depolox reagents ok -verified chlorine analyzers: 13:21 - Analyzer readings: Free Chlorine = 0.03 mg/L Total Chlorine = 1.58 mg/L 13:21 - Grabs: Free Chlorine = 0.01 mg/L Total Chlorine = 1.57 mg/L SL1000 Readings: MCL = 1.49 mg/L TNH3 = 0.36 mg/L FNH3 = 0.07 mg/L NO2 = 0.003 mg/L temp = 5.0 C 13:25 - collected weekly regulatory micro. sample - W/O # W11637334 -collected operational ATP sample -recorded readings in PWQ sheet -no issues found | King City Fisher Elevated Tank | 2026-03-04
WEST | March | -On-site to complete station check and collect sample -system duty active, tower = 39 % -checked equipment -reviewed trends -replaced KI solution -verified chlorine analyzers: 11:46 - Analyzer readings: Free Chlorine = 0.03 mg/L Total Chlorine = 1.40 mg/L 11:46 - Grabs: Free Chlorine = 0.03 mg/L Total Chlorine = 1.53/1.52/1.55 mg/L SL1000 Readings: MCL = 1.45 mg/L TNH3 = 0.36 mg/L FNH3 = 0.07 mg/L NO2 = 0.003 mg/L temp = 7.4 C 11:52 - collected weekly regulatory micro. sample - W/O # W11657053 11:55 - adjusted total chlorine analyzer to 1.53 mg/L based on average of 3 grabs -recorded readings in PWQ sheet -no other issues found | King City Fisher Elevated Tank | 2026-03-11
WEST | March | -On-site to complete station check and collect sample -system duty not active, tower = 64 % -checked equipment -reviewed trends -depolox reagents ok -verified chlorine analyzers: 12:43 - Analyzer readings: Free Chlorine = 0.04 mg/L Total Chlorine = 1.51 mg/L 12:43 - Grabs: Free Chlorine = 0.03 mg/L Total Chlorine = 1.49 mg/L SL1000 Readings: MCL = 1.48 mg/L TNH3 = 0.37 mg/L FNH3 = 0.08 mg/L NO2 = 0.004 mg/L 12:48 - collected weekly regulatory micro. sample - W/O # W11690322 -recorded readings in PWQ sheet -no issues found | King City Fisher Elevated Tank | 2026-03-25
WEST | March | On site responding to power fail (Hydro one planned power shut down). Transferred power to portable generator. W11756686. 03:45 utility power restored, shut down generator and returned site to utility power. Freedom mobile on site inspecting equipment. | King City Fisher Elevated Tank | 2026-03-25
WEST | March | -On-site to complete station check and collect sample -deactivated system duty, tower = 76 % -checked equipment -reviewed trends 08:57 - collected grab sample: Free Chlorine = 0.03 mg/L Total Chlorine = 1.97 mg/L MCL = 1.88 mg/L TNH3 = 0.42 mg/L FNH3 = 0.05 mg/L NO2 = 0.003 mg/L temp = 7.4 C 09:01 - collected weekly regulatory micro. sample - W/O # W11705756 -recorded readings in PWQ sheet -no issues found | Kleinburg Elevated Tank | 2026-03-31
WEST | March | -On-site to complete station check and collect sample -deactivated system duty, tower = 68 % -checked equipment -reviewed trends 08:02 - collected grab sample: Free Chlorine = 0.05 mg/L Total Chlorine = 1.88 mg/L MCL = 1.89 mg/L TNH3 = 0.46 mg/L FNH3 = 0.08 mg/L NO2 = 0.003 mg/L temp = 7.3 C 08:06 - collected weekly regulatory micro. sample - W/O # W11657170 -recorded readings in PWQ sheet -no issues found | Kleinburg Elevated Tank | 2026-03-11
WEST | March | -On-site to complete station check and collect sample -deactivated system duty, tower = 73 % -checked equipment -reviewed trends 09:12 - collected grab sample: Free Chlorine = 0.04 mg/L Total Chlorine = 1.90 mg/L MCL = 1.86 mg/L TNH3 = 0.42 mg/L FNH3 = 0.05 mg/L NO2 = 0.004 mg/L temp = 6.6 C 09:17 - collected weekly regulatory micro. sample - W/O # W11637596 -collected operational ATP sample -recorded readings in PWQ sheet -no issues found | Kleinburg Elevated Tank | 2026-03-04
WEST | March | On site to complete monthly work orders. -low temp alarm -valve exercising -standby generator test run -health and safety inspection. | Kleinburg Elevated Tank | 2026-03-10
WEST | March | -On-site to complete station check and collect sample -deactivated system duty, tower = 79 % -checked equipment -reviewed trends 08:52 - collected grab sample: Free Chlorine = 0.05 mg/L Total Chlorine = 1.83 mg/L MCL = 1.92 mg/L TNH3 = 0.42 mg/L FNH3 = 0.04 mg/L NO2 = 0.004 mg/L 08:57 - collected weekly regulatory micro. sample - W/O # W11690439 -recorded readings in PWQ sheet -no issues found | Kleinburg Elevated Tank | 2026-03-25
WEST | March | -on site to complete station check -system duty active -checked equipment -reviewed trends -recorded readings in PWQ sheet -replaced KI reagent -pump #1 hours = 17888.5 -pump #2 hours = 17983.7 -pump #3 hours = 18646.2 -verified chlorine analyzers: 12:53 - Analyzer readings: Free Chlorine = 0.03 mg/L Total Chlorine = 1.86 mg/L 12:53 - Grabs: Free Chlorine = 0.03 mg/L Total Chlorine = 1.97/1.96/1.95 mg/L 13:02 - adjusted total chlorine analyzer to 1.96 mg/L based on average of 3 grabs -no other issues found | Kleinburg HWY 27 Booster Pumping Station | 2026-03-02
WEST | March | Under the direction of David Tarascio, Worked along side Network Analyst Kevin Wen, to replaced a Network switch to Cisco IE3300 inside a Network panel. All three Booster Pumps were in manual off. There was a historian hrbt alarm due to OIT comm fail Provided 24 VDC power to new switch. There is a trend gap on SCADA between 12:16 PM to 12:47 PM due to this work. After the replacement, checked all the ports and reset the comm alarms. | Kleinburg Elevated Tank | 2026-03-04
WEST | March | -On-site to complete station check and collect sample -deactivated system duty, tower = 69 % -checked equipment -reviewed trends 08:41 - collected grab sample: Free Chlorine = 0.04 mg/L Total Chlorine = 1.85 mg/L MCL = 1.84 mg/L TNH3 = 0.42 mg/L FNH3 = 0.06 mg/L NO2 = 0.004 mg/L temp = 5.7 C 08:45 - collected weekly regulatory micro. sample - W/O # W11672975 -recorded readings in PWQ sheet -no issues found | Kleinburg Elevated Tank | 2026-03-18
WEST | March | Under the direction of David Tarascio, Worked along side Network Analyst Kevin Wen, to replaced a Network switch to Cisco IE3300 inside a Network panel. All three Booster Pumps were in manual off. There was a historian hrbt alarm due to OIT comm fail Provided 24 VDC power to new switch. There is a trend gap on SCADA between 11:31 AM to 11:51 AM due to this work. After the replacement, checked all the ports and reset the comm alarms. | Kleinburg HWY 27 Booster Pumping Station | 2026-03-04
WEST | March | -on site to complete station check -system duty active -checked equipment -reviewed trends -recorded readings in PWQ sheet -analyzer reagents ok -verified chlorine analyzers: 11:15 - Analyzer readings: Free Chlorine = 0.02 mg/L Total Chlorine = 2.00 mg/L 11:15 - Grabs: Free Chlorine = 0.04 mg/L Total Chlorine = 2.01 mg/L -no issues found | Kleinburg HWY 27 Booster Pumping Station | 2026-03-06
WEST | March | Station Check (no issues found) Input data to PWQ 11:05 Verified Depolox (mg/l) Free: Grab 0.04, A 0.02 Total: Grab 1.88, A 1.91 (Acetate, & distilled/Ki top up) | Kleinburg HWY 27 Booster Pumping Station | 2026-03-13
WEST | March | -on site for station check -checked trends: all ok -entered readings in PWQ: all ok -verified analyzer 11:50 -analyzer free: 0.02mg/l grab: 0.03mg/l -analyzer total: 2.06mg/l grab: 2.04mg/l -reagents all ok -equipment all ok | Kleinburg HWY 27 Booster Pumping Station | 2026-03-27
WEST | March | -on site to complete station check -system duty not active -checked equipment -reviewed trends -recorded readings in PWQ sheet -analyzer reagents ok -verified chlorine analyzers: 10:44 - Analyzer readings: Free Chlorine = 0.03 mg/L Total Chlorine = 1.94 mg/L 10:44 - Grabs: Free Chlorine = 0.03 mg/L Total Chlorine = 1.89 mg/L -no issues found | Kleinburg HWY 27 Booster Pumping Station | 2026-03-16
WEST | March | -on site to complete station check -system duty active, pumps 1 and 2 running -checked equipment -reviewed trends -recorded readings in PWQ sheet -analyzer reagents ok -verified chlorine analyzers: 12:01 - Analyzer readings: Free Chlorine = 0.02 mg/L Total Chlorine = 2.01 mg/L 12:01 - Grabs: Free Chlorine = 0.06 mg/L Total Chlorine = 2.02 mg/L -no issues found | Kleinburg HWY 27 Booster Pumping Station | 2026-03-23
WEST | March | -on site to complete station check -system duty not active -checked equipment -reviewed trends -recorded readings in PWQ sheet -analyzer reagents ok -verified chlorine analyzers: 13:28 - Analyzer readings: Free Chlorine = 0.03 mg/L Total Chlorine = 2.08 mg/L 13:28 - Grabs: Free Chlorine = 0.03 mg/L Total Chlorine = 2.04 mg/L -no issues found | Kleinburg HWY 27 Booster Pumping Station | 2026-03-20
WEST | March | On site to complete monthly work orders. -pump and motor maintenance -chlorine analyzer maintenance -sump pit inspection -health and safety inspection -check valve inspection -prv inspection -low temp alarm | Kleinburg HWY 27 Booster Pumping Station | 2026-03-10
WEST | March | -on site to complete station check -system duty not active -checked equipment -reviewed trends -recorded readings in PWQ sheet -analyzer reagents ok -verified chlorine analyzers: 13:24 - Analyzer readings: Free Chlorine = 0.02 mg/L Total Chlorine = 1.93 mg/L 13:24 - Grabs: Free Chlorine = 0.05 mg/L Total Chlorine = 1.96 mg/L -no issues found | Kleinburg HWY 27 Booster Pumping Station | 2026-03-09
WEST | March | -on site to complete work orders -informed ROC of work -completed High/Low Temperature Alarm Test -completed Flood Alarm, Test -completed Pump and Motor, Inspection -completed Eye Wash, Solution Replacement -completed Pressure Relief Valve, Inspection -completed Siemens Depolox 5/Micro 2000, Chlorine Analyzer, Maintenance -filled grit sand and electrolyte -flushed sample lines, checked flow rates -verified analyzers after maintenance: 13:26 - Analyzer readings: Free Chlorine = 0.10 mg/L Total Chlorine = 2.02 mg/L 13:26 - Grabs: Free Chlorine = 0.04/0.03/0.03 mg/L Total Chlorine = 2.00 mg/L 13:33 - adjusted free chlorine analyzer to 0.03 mg/L based on average of 3 grabs -site back to normal operation | Kleinburg Whisper Lane Booster Pumping Station | 2026-03-10
WEST | March | -on site to complete station check -checked equipment -reviewed trends -analyzer reagents ok -recorded readings in PWQ sheet -verified chlorine analyzers: 11:34 - Analyzer readings: Free Chlorine = 0.06 mg/L Total Chlorine = 1.93 mg/L 11:34 - Grabs: Free Chlorine = 0.05 mg/L Total Chlorine = 1.92 mg/L -no issues found | Kleinburg Whisper Lane Booster Pumping Station | 2026-03-06
WEST | March | Station Check (no issues found) input data to PWQ 11:45 Verified Depolox (mg/l) Free: Grab 0.07, A 0.05 Total: Grab 1.76, A 1.78 (Acetate top up) | Kleinburg Whisper Lane Booster Pumping Station | 2026-03-13
WEST | March | -on site for station check -checked trend: all ok -entered readings in PWQ: all ok -verified analyzer 12:30 -analyzer free: 0.06mg/l grab: 0.04mg/l -analyzer total: 1.97mg/l grab: 1.95mg/l -reagents all ok -locally ran pump 1 &2: no issues | Kleinburg Whisper Lane Booster Pumping Station | 2026-03-27
WEST | March | Check mechanical seal Seal leaking. Locating a replacement seal | Kleinburg Whisper Lane Booster Pumping Station | 2026-03-19
WEST | March | -on site to complete station check -ran pump #3 in manual -checked equipment -reviewed trends -analyzer reagents ok -recorded readings in PWQ sheet -verified chlorine analyzers: 11:35 - Analyzer readings: Free Chlorine = 0.06 mg/L Total Chlorine = 1.84 mg/L 11:35 - Grabs: Free Chlorine = 0.04 mg/L Total Chlorine = 1.83 mg/L -no issues found | Kleinburg Whisper Lane Booster Pumping Station | 2026-03-23
WEST | March | -on site to complete station check -checked equipment -analyzer reagents ok -recorded readings in PWQ sheet -verified chlorine analyzers: 11:03 - Analyzer readings: Free Chlorine = 0.06 mg/L Total Chlorine = 1.87 mg/L 11:03 - Grabs: Free Chlorine = 0.05 mg/L Total Chlorine = 1.84 mg/L -no issues found | Kleinburg Whisper Lane Booster Pumping Station | 2026-03-16
WEST | March | Station Check (no issues found) Input data to PWQ 10:00 Verified Depolox (mg/l) Free: Grab 0.05, A 0.06 Total: Grab 1.82, A 1.88 Depolox (new KI/distilled) | Kleinburg Whisper Lane Booster Pumping Station | 2026-03-20
WEST | March | -on site to complete station check -ran pump #4 in manual -checked equipment -reviewed trends -analyzer reagents ok -recorded readings in PWQ sheet -verified chlorine analyzers: 12:56 - Analyzer readings: Free Chlorine = 0.06 mg/L Total Chlorine = 1.83 mg/L 12:56 - Grabs: Free Chlorine = 0.05 mg/L Total Chlorine = 1.88 mg/L -small leak from pump #4 shaft seal, created work order for CMS -no other issues | Kleinburg Whisper Lane Booster Pumping Station | 2026-03-09
WEST | March | -on site to complete station check -ran pumps 1 and 2 in local -checked equipment -reviewed trends -analyzer reagents ok -recorded readings in PWQ sheet -pump hours: #1 = 3976.0 #2 = 4499.2 #3 = 5566.7 #4 = 5449.4 -verified chlorine analyzers: 11:55 - Analyzer readings: Free Chlorine = 0.06 mg/L Total Chlorine = 1.96 mg/L 11:55 - Grabs: Free Chlorine = 0.04 mg/L Total Chlorine = 1.93 mg/L -no issues found | Kleinburg Whisper Lane Booster Pumping Station | 2026-03-02
W-MAINT | March | Totalizer: 4906177 m3 Discharge pressure: 24.5 kPa Flow Rate: 10.6L/s Monitoring well: 219.4masl Well 8 RPM: 2349 AMP: 5.3 %: 36 Level: 208.4 masl Well 13 RPM: 2043 AMP: 4.9 %: 18 Level: 206.4 masl | Major MacKenzie and Newkirk Road Dewatering Wells | 2026-03-11
W-MAINT | February | Totalizer: 4888666m3 Discharge pressure: 27.18Kpa Flow Rate: 10.5 L/s Monitoring well: 219.2 masl Well 8 RPM: 2350 AMP: 5.3 %: 36 Level: 208.5 masl Well 13 RPM: 2043 AMP: 4.9 %: 17 Level: 206.6 masl | Major MacKenzie and Newkirk Road Dewatering Wells | 2026-02-19
W-MAINT | March | Attended site to top up generator fuel. Fuel level at 5/8 of a tank on arrival. Fuel level full Generator took approximately 100L of fuel. Complete. | Major MacKenzie and Newkirk Road Dewatering Wells | 2026-03-08
W-MAINT | March | On site due to a power failure | Major MacKenzie and Newkirk Road Dewatering Wells | 2026-03-07
W-MAINT | March | On site due to power failure | Major MacKenzie and Newkirk Road Dewatering Wells | 2026-03-07
W-MAINT | February | Totalizer: 4883206m3 Discharge pressure: 25.11Kpa Flow Rate: 11.2 L/s Monitoring well: 219.1 masl Well 8 RPM: 2450 AMP: 5.5 %: 42 Level: 207.6 masl Well 13 RPM: 2112 AMP: 4.6 %: 21 Level: 205.6 masl On site adjusted the combined flow rate to 10.5L/s as per Tanya kampherns request. Changed the speed of well 8 to 37% speed and well 8 to 17%. New values below Totalizer: 4883212m3 Discharge pressure: 25.18Kpa Flow Rate: 10.5 L/s Monitoring well: 219.1 masl Well 8 RPM: 2365 AMP: 5.3 %: 37 Level: 208.2 masl Well 13 RPM: 2043 AMP: 4.9 %: 17 Level: 206.6 masl | Major MacKenzie and Newkirk Road Dewatering Wells | 2026-02-13
W-MAINT | March | On site for weekly Station check. Also replaced malfunctioning unit heater. Totalizer: 4916973 m3 Discharge pressure: 30.24 kPa Flow Rate: 10.2 L/s Monitoring well: 219.4 masl Well 8 RPM: 2349 AMP: 5.3 %: 36 Level: 208.6 masl Well 13 RPM: 2060 AMP: 4.9 %: 18 Level: 206.4 masl | Major MacKenzie and Newkirk Road Dewatering Wells | 2026-03-23
W-MAINT | March | On site to switch power from temporary generator back to Hydro power. Reset any alarms and started pumps 13 and eight in manual mode as normal. Totalizer: 4907870m3 Discharge pressure: 24.52Kpa Flow Rate: 10.5 L/s Monitoring well: 219.4 masl Well 8 RPM: 2349 AMP: 5.3 %: 36 Level: 208.4 masl Well 13 RPM: 2060 AMP: 4.9 %: 18 Level: 206.4 masl | Major MacKenzie and Newkirk Road Dewatering Wells | 2026-03-13
W-MAINT | March | Totalizer: 4901980 m3 Discharge pressure: 27.81 kPa Flow Rate: 10.3 L/s Monitoring well: 219.2 masl Well 8 RPM: 2349 AMP: 5.3 %: 36 Level: 208.5 masl Well 13 RPM: 2043 AMP: 4.9 %: 17 Level: 206.6 masl | Major MacKenzie and Newkirk Road Dewatering Wells | 2026-03-06
W-MAINT | March | Details: Totalizer: 4912364 m3 Discharge pressure: 30.15 kPa Flow Rate: 10.3 L/s Monitoring well: 219.3 masl Well 8 RPM: 2349 AMP: 5.3 %: 36 Level: 208.6 masl Well 13 RPM: 2060 AMP: 4.9 %: 18 Level: 206.4 masl | Major MacKenzie and Newkirk Road Dewatering Wells | 2026-03-18
WEST | March | -on site to collect weekly bacti W11637582 -checked trends: all ok -entered reading in PWQ: all ok -took sample and chlorine grab 09:35 -free cl: 0.08mg/l -total cl: 1.63mg/l -west cell grab 09:40 -free cl: 0.08mg/l -total cl: 1.62mg/l -equipment all ok | Maple North Reservoir | 2026-03-04
WEST | March | On site for station check, operational sampling and weekly bacti W11705742 Checked trends: all ok 10:30-Took sample and chlorine grab from west cell Free cl: 0.05mg/l Total cl: 1.70 mg/l 10:35-East cell chlorine grab Free cl: 0.03mg/l Total cl: 1.60 mg/l Entered readings in PWQ: all ok equipment all okay Equipment all ok | Maple North Reservoir | 2026-03-31
WEST | March | -on site to complete following station check -outside sump pit inspection: all ok | Maple North Reservoir | 2026-03-19
WEST | March | on site for station check and weekly bacti W -checked trends: all ok -entered readings in PWQ: all ok -took sample and chlorine grab east cell 09:52 -free cl: 0.07mg/l -total cl: 1.48mg/l -west cell chlorine grab 10:37 -free cl: 0.04 mg/l -total cl: 1.47mg/l -equipment all ok | Maple North Reservoir | 2026-03-18
WEST | March | On site for station check, operational sampling and weekly bacti W11672961 Checked trends: all ok 10:37-Took sample and chlorine grab from west cell Free cl: 0.04mg/l Total cl: 1.47 mg/l 09:52-East cell chlorine grab Free cl: 0.07mg/l Total cl: 1.48 mg/l Entered readings in PWQ: all ok Equipment all ok | Maple North Reservoir | 2026-03-18
WEST | March | On site for station check and weekly bacti W11690336 Checked trends: all ok 10:25-Took sample and chlorine grab from East cell Free cl: 0.05mg/l Total cl: 1.64 mg/l 10:30-west cell chlorine grab Free cl: 0.03mg/l Total cl: 1.63 mg/l Entered readings in PWQ: all ok Equipment all ok | Maple North Reservoir | 2026-03-25
WEST | March | Restarted the Operator Interface Terminal due to Windows OS memory. | Maple North Reservoir | 2026-03-23
WEST | March | -on site to complete following work orders -JHSC inspection: all ok -general housekeeping- notice water on floor - pushed water into sump pit -sump pit inspection: all ok -main cross over valve: all ok | Maple North Reservoir | 2026-03-12
WEST | March | on site for station check and weekly bacti W11657067 -checked trends: all ok -entered readings in PWQ: all ok -took sample and chlorine grab east cell 09:10 -free cl: 0.03mg/l -total cl: 1.59mg/l -west cell chlorine grab 09:15 -free cl: 0.03mg/l -total cl: 1.62mg/l -equipment all ok | Maple North Reservoir | 2026-03-11
WEST | March | conducted station check checked trends: all ok verified PD7 analyzer 10:40 Grab free Cl2: 0.07mg/l; Analyzer: 0.02mg/l Grab total Cl2: 1.70mg/l Analyzer: 1.68mg/l PD8 analyzer offline entered readings in PWQ equipment all ok | Maple Pumping Station | 2026-03-30
WEST | March | Station Check (no issues found) Input data to PWQ 14:15 Verified Depolox (mg/l) Free: Grab 0.04, A 0.03 Total: Grab 1.77, A 1.78 | Maple Pumping Station | 2026-03-13
WEST | March | -on site to complete following work orders -JHSC inspection: no high voltage on PD8 MCC room -screen inspection: all ok - | Maple Pumping Station | 2026-03-05
WEST | March | -on site to complete following work orders -screen inspection: all ok -sump inspection: all ok -general housekeeping main floor: all ok -diesel run -diesel start: 484/497.7 -diesel stop: 485/498.8 -diesel level: 38436 - 371/508L -diesel ventilation inspection: all ok -tested containment alarm: all ok -diesel transfer pumps: all ok -chlorine analyzer maintenance -verified PD7 analyzer 13:40 -analyzer free: 0.02mg/l grab: 0.05mg/L -analyzer total: 1.90mg/l grab: 1.88mg/l -flow/electrolyte/pressure and sand all ok -PD8 analyzer offline | Maple Pumping Station | 2026-03-05
WEST | March | conducted station check checked trends: all ok verified PD7 analyzer 10:04 Grab free: 0.04mg/l Analyzer: 0.03mg/l Grab total: 1.72mg/l Analyzer: 1.67mg/l PD8 analyzer offline entered readings in PWQ equipment all ok | Maple Pumping Station | 2026-03-09
WEST | March | #NAME? | Maple Pumping Station | 2026-03-03
WEST | March | W11695012- Site access for fire system contractor and building inspector Assisted contractor and inspector. conducted station check checked trends: all ok verified PD7 analyzer 11:00 analyzer free: 0.03mg/l grab: 0.02mg/l analyzer total: 1.71mg/l grab: 1.68mg/l PD8 analyzer offline entered readings in PWQ equipment all ok | Maple Pumping Station | 2026-03-02
WEST | March | on site for the following work order. W11668087- Process sump pump and drain valve exercise Unable to enter the chamber due to the ongoing construction. sump pumps started manually, listened pumps starting and made sure its running. However, level did not go down in LIT. will investigate later. W11641379- MWPS comprehensive house keeping, pump room | Maple Pumping Station | 2026-03-19
WEST | March | -on site to complete station check -checked equipment -reviewed trends -recorded readings in PWQ sheet -PD8 analyzer out of service due to PD8 suction line isolation Verified analyzers: 09:24 - PD7 Analyzer readings: Free Chlorine = 0.02 mg/L Total Chlorine = 1.69 mg/L 09:24 - PD7 Grabs: Free Chlorine = 0.01 mg/L Total Chlorine = 1.69 mg/L -no issues found | Maple Pumping Station | 2026-03-23
WEST | March | conducted station check checked trends: all ok verified PD7 analyzer 10:40 Grab free: 0.06mg/l Analyzer: 0.02mg/l Grab total: 1.69mg/l Analyzer: 1.69mg/l PD8 analyzer offline entered readings in PWQ equipment all ok | Maple Pumping Station | 2026-03-20
WEST | March | conducted station check checked trends: all ok verified PD7 analyzer 09:54 Grab free: 0.01mg/l Analyzer: 0.03mg/l Grab total: 1.60mg/l Analyzer: 1.67mg/l PD8 analyzer offline entered readings in PWQ equipment all ok | Maple Pumping Station | 2026-03-06
WEST | March | On site to complete hard wiring for PD8 VFD remote reset signal upgrade. Tested fault signals and resetting from the PLC panel. | Maple Pumping Station | 2026-03-05
WEST | March | conducted station check checked trends: all ok verified PD7 analyzer 10:20 Grab free Cl2: 0.04mg/l; Analyzer: 0.02mg/l Grab total Cl2: 1.70mg/l Analyzer: 1.67mg/l PD8 analyzer offline entered readings in PWQ equipment all ok | Maple Pumping Station | 2026-03-27
WEST | March | conducted station check checked trends: all ok verified PD7 analyzer 09:35 Grab free: 0.04mg/l Analyzer: 0.03mg/l Grab total: 1.65mg/l Analyzer: 1.65mg/l PD8 analyzer offline entered readings in PWQ equipment all ok | Maple Pumping Station | 2026-03-16
WEST | March | -on site to complete station check, following work orders and weekly bacti W -checked trends: all ok -entered readings in PWQ: all ok -took chlorine grab and sampl north cell 08:30 -free cl: 0.08mg/l -total cl: 1.61mg/l -cleaned and verified metro analyzer 08:35 -analyzer free:0.02mg/l grab: 0.04mg/l -analyzer total: 1.66mg/l grab: 1.68mg/l -flow/pressure/electrolyte: all ok -cleaned and verified peel analyzer 08:45 -analyzer: 1.80mg/l grab: 1.76mg/l - adjusted -changed reagents -tested high and low level alarms: all ok -sump pump inspection: all ok -construction on going | Maple South Reservoir | 2026-03-11
WEST | March | on site for station check, operational sampling and weekly bacti W11705742 checked trends: all ok 09:20-took sample and chlorine grab north cell Free Cl2: 0.03 mg/l Total Cl2: 1.67mg/l 09:30-verified peel analyzer Grab Total Cl2: 1.69mg/l Analyzer Total Cl2: 1.67 mg/L Reagents all ok 09:35-verified metro analyzer Grab Free CL2- 0.05 mg/L Analyzer free CL2- 0.02mg/L Grab Total CL2- 1.66 mg/L Analyzer Total CL2- 1.69 mg/L entered readings in PWQ Site under construction | Maple South Reservoir | 2026-03-31
WEST | March | on site for station check, operational sampling and weekly bacti W11672961 checked trends: all ok 09:50-verified peel analyzer Grab Total Cl2: 1.63mg/l Analyzer Total Cl2: 1.67 mg/L Reagents all ok 09:55-verified metro analyzer Grab Free CL2- 0.02 mg/L Analyzer free CL2- 0.02mg/L Grab Total CL2- 1.60 mg/L Analyzer Total CL2- 1.63 mg/L 09:40-took sample and chlorine grab north cell Free Cl2: 0.02 mg/l Total Cl2: 1.65mg/l entered readings in PWQ Site under construction | Maple South Reservoir | 2026-03-18
CENTRAL | March | Elog was down this morning March 31, 2026 Jason Garnett onsite from 7:45 am - 8:15 am Completed station and equipment check and weekly BacT sample W11705420 Took sample and grabs @ 7:55 am Total: 2.70 mg/l Free: 0.02 mg/l Analyzer matched grabs, reagents ok All other readings on PD sheets shared online folder ET Filling @ 20 l/s ET ops normal | Newmarket (East) Harry Walker Elevated Tank | 2026-03-31
WEST | March | on site for station check, operational sampling and weekly bacti W11690336 checked trends: all ok 09:40-verified peel analyzer Grab Total Cl2: 1.70mg/l Analyzer Total Cl2: 1.71 mg/L Reagents all ok 09:45-verified metro analyzer Grab Free CL2- 0.03 mg/L Analyzer free CL2- 0.02mg/L Grab Total CL2- 1.70 mg/L Analyzer Total CL2- 1.67 mg/L 09:38-took sample and chlorine grab north cell Free Cl2: 0.04 mg/l Total Cl2: 1.64mg/l entered readings in PWQ Site under construction | Maple South Reservoir | 2026-03-25
WEST | March | -on site for station check and weekly bacti W11637582 -checked trends: all ok -entered readings in PWQ: -verified peel analyzer 08:25: 1.68mg/l grab: 1.67mg/l -reagents all ok -took sample and chlorine grab north cell 08:30 -free cl: 0.10mg/l -total cl: 1.65mg/l -verified metro analyzer 08:40 -analyzer free: 0.02mg/l grab: 0.05mg/l -analyzer total: 1.63mg/l grab: 1.67mg/l -site under construction | Maple South Reservoir | 2026-03-04
CENTRAL | March | Station Check (no issues found) Input data to PWQ 3:00 Verified Depolox (mg/L) Free: Grab 0.04, A 0.02 Total: Grab 2.52, A 2.56 Samples #11637661, #11637260 & operational | Newmarket (East) Harry Walker Elevated Tank | 2026-03-04
CENTRAL | March | Station Check (no issues found) Input data to PWQ 10:10 Verified Depolox (mg/l) Free: Grab 0.04, A 0.01 Total: Grab 2.48, A 2.52 10:20 #11690790 bact. | Newmarket (East) Harry Walker Elevated Tank | 2026-03-25
CENTRAL | March | Station Check (no issues found) Input data to PWQ 13:30 Verfied Depolox (mg/l) Free: Grab 0.04, A 0.02 Total: Grab 2.62, A 2.41 (adjusted to match grabs) 13:40 Sample #11657622 Depolox (acetate topped up) | Newmarket (East) Harry Walker Elevated Tank | 2026-03-11
CENTRAL | March | Onsite to complete monthly Maximo workorders Telecom crew onsite No alarms created ET ops normal | Newmarket (East) Harry Walker Elevated Tank | 2026-03-24
CENTRAL | March | Station Check (no issues found) Input data to PWQ 14:35 Verified Depolox (mg/l) Free: Grab 0.05, A 0.02 Total: Grab 2.66, A 2.60 3:00 #11672723 bact. and operational samples | Newmarket (East) Harry Walker Elevated Tank | 2026-03-18
CENTRAL | March | onsite to receive hypo delivery, aprox 380 L Also station check and take weekly BacT sample W1111705420 from sample tap Total: 1.70 mg/l Free: 0.04 mg/l All other readings on PD sheets Top up hypo day tanks 1 and 2 reagents ok Ops normal | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2026-03-31
CENTRAL | March | Station and equipment check Reservoir filling at time of check Took grabs from Inlet @ 10:00 am (post) Total: 2.60 mg/l Free: 0.03 mg/l All other readings on PD sheets *adjusted offset for header total ammonia from -0.03 to - 0.08 Topped up both Hypo day tanks Changed CL17 reagent ?inlet free? Ops normal | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2026-03-13
CENTRAL | March | Station and equipment check Tank filling Took grabs @ 11:05 am from post (inlet) Total: 2.38 mg/l Free: 0.04 mg/l Also took grabs from Pre (header) @ 10:35 am, readings input to PD sheets *adjusted offset on header FA from 0.00 to -0.07 to match grabs Top up both Hypo day tanks Chemicals/reagents ok Ops normal | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2026-03-06
CENTRAL | March | Station Check (no issues found) Input data to PWQ Verified CL17s (mg/L) 13:00 Pre (outlet): Free: Grab 0.04, A 0.01 Total: Grab 1.82, A 1.89 13:15 Post (header) Free: Grab 0.06, A 0.07 Total: Grab 3.10, A 3.15 Header Free CL17 (new reagents) #11649044 (hot water flush of chemscan sample lines (chemical pumps manual off during work)) Ammonia tank (transfer of #1 into #2) Hypo tank #2 top up | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2026-03-09
CENTRAL | March | Received hypo delivery and topped up tanks 1 and 2. W11652297 | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2026-03-10
CENTRAL | March | Station Check (no issues found) Input data to PWQ Verified CL17s (mg/L) 10:50 Pre (Inlet/Draining) Free: Grab 0.04, A 0.01 Total: Grab 1.80, A 1.80 10:55 Post (header/draining): Free: Grab 0.06, A 0.05 Total: Grab 3.20, A 3.25 11:00 Sample #11657622 Chemscan (distilled, distilled/muriatic top up) | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2026-03-11
CENTRAL | March | Station Check (no other issues found) Input data to PWQ Verified CL17s (mg/l) 12:35 PRE Free: Grab 0.03, A 0.01 Total: Grab 1.65, A 1.66 12:45 Post (header) Free: Grab 0.07, A 0.04 Total: Grab 3.16, A 3.20 13:00 Samples #11637260, #11637661 & operational Ammonia pump 1 in manual off due to "fail to start" alarms | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2026-03-04
CENTRAL | March | Hypo Delivery Before: Tank 1 280L, Tank 2 234L, bulk tank 0L After: Tank 1 280L, Tank 2 283L , bulk tank 330L Total delivered 379L Ammonia pump 1 "fail to start" cleared and started in duty 1 Chemscan (new yellow reagent ) | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2026-03-03
CENTRAL | March | Station Check (no issues found) Input data to PWQ #11667608 Chemscan sample line hot flush (chemical pumps manual off, chemscan off-line durin flush) Verified CL17s (mg/L) 13:30 Pre (draining/ Outlet): Free: Grab 0.03, A 0.02 Total: Grab 1.80, A 1.77 12:40 Post (draining/ Header): Free: Grab 0.05, A 0.05 Total: Grab 3.20, A 3.20 Cl17 (Inlet total) reagents changed Chemscan (green & grey reagent top up) Hypo tank 2 top up Ammonia Tank 2 top up (transferred from tank 1 (ammonia pump 1 oos)) | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2026-03-16
CENTRAL | March | Station Check (no issues found) Input data to PWQ Verified CL17s(mg/l)(draining) 12:05 Pre (inlet/outlet) Free: Grab 0.03, A 0.02 Total: Grab 1.79, A 1.83 12:35 #11672723 bact. & operational samples 12:15 Post (header) Free: Grab 0.04, A 0.05 Total: Grab 3.12, A 3.20 | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2026-03-18
CENTRAL | March | Onsite for station check Contractors cutting lower door into VC1 wall, have tarpped off chemscan. Reset breaker 6 for chlorine room electrical plug. Changed header total cl17 reagent. Station ok | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2026-03-27
CENTRAL | March | Station Check (no issues found) Input data to PWQ Verified CL17s (mg/l) (Draining): 12:22 PRE (inlet/outlet): Free: Grab 0.04, A 0.02 Total: Grab 1.91, A 2.00 12:35 POST(Header): Free: Grab 0.05, A 0.05 Total: Grab 3.20, 3.22 12:45 #11690790 bact. sample Chemscan (top up distilled, KI sol'n) | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2026-03-25
CENTRAL | March | Onsite to assist with the relocation of the chemscan unit, all chemical pumps placed in manual and off Tank 2 remained filling as work being completed PCS/Instrumentation also on site Received Hypo delivery aprox 520 L Batched ammonia tank 1 Instrumentation also investigating am P1 fault an startup, left manual OFF for now Will monitor system via scada | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2026-03-19
CENTRAL | March | Trained with Ben H. on operation of site. On site to complete station check. Verified analyzers: Header Free Chlorine @ 11:10 Grab: 0.03 mg/L Analyzer: 0.03 mg/L Header Total Chlorine @ 11:10 Grab: 1.78 mg/L Analyzer: 1.77 mg/L Inlet Free Chlorine @ 11:17 Grab: 0.06 mg/L Analyzer: 0.04 mg/L Inlet Total Chlorine @ 11:17 Grab: 2.00 mg/L Analyzer: 2.08 mg/L Adjusted chemscan header free ammonia reading from 0.05 to 0.18 mg/L based on grabs -Ended duty | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2026-03-20
CENTRAL | March | Onsite to top up ammonia tank 1. Deactivated chlorine boosting system while batch tank. Placed back in service at 14:32 No issues found | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2026-03-23
CENTRAL | March | Onsite to witness Lexsan relocate the Chem Scan coordinated Connor from ROC, only the power was turned off none of the wires were removed. Jason Garnett is onsite site to witness the relocation Instrumentation were also onsite to verify the Chem Scan after power was turned back on. Site left under normal condition | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2026-03-19
CENTRAL | March | On site to complete station check. Verified chemscan outlet readings. Entered data into PD sheets | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2026-03-20
CENTRAL | March | Work orders: #11669068 CL17 maint. Verified(mg/L): 10:15 Pre (header/Fill) Free: Grab 0.03, A 0.03 Total: Grab 1.98, A 1.97 10:30 Post (inlet/fill) Free: Grab 0.03, A 0.03 Total: Grab 1.98, A 1.97 #11669663 flood Hypo pump draw down (no changes made): #11670012 , #11675940, #11676221 Ammonia pump 1 (oos) unable to perform draw down) | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2026-03-17
CENTRAL | March | Station and equipment check Informed ROC (Carter D) will be completing Maximo workorder hot water flush of all analyzer supply lines 9:30-10:45 am All chemical systems placed off and analyzers in cal mode, reservoir filling Returned system to normal w/ no issues Took grabs @ 11:15 am Post (inlet) Total: 2.30 mg/l Free: 0.05 mg/l All other readings on PD sheets Topped up both hypo day tanks Am P1 OOS Ops normal | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2026-03-23
CENTRAL | March | Attending site to check ammonia pump#1 (W11707116). Found internal pump relay not functioning to provide running status back to SCADA. Replaced internal relay and tested to function correctly after repair. ROC was notified before and after maintenance activities. | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2026-03-24
CENTRAL | March | Onsite to verify Chemscan analyzer after relocation. Informed ROC. Turned on the Chemscan analyzer after relocation. Took a multiple grab samples. All readings back to normal and matched SCADA. All the associated alarms were cleared. No issues. Troubleshoot ammonia pump #1. Replaced the start/stop relay. Alarms still intermittently present. Ammonia pump #1 in manual off for now. Informed ROC, armed the building and left the site. | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2026-03-19
CENTRAL | March | Onsite to receive hypo delivery 330 L Ops normal Top up hypo day tanks to make room in bulk tank | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2026-03-24
CENTRAL | March | #11668904 Hypo pump maint (cleaned all hypo inj. pts. and draw down) #11668956 Ammonia (due to ammonia pump having alarm issues) -Transferred ammonia tank 1 into tank 2 -ammonia tank 1 (new batch) #11669036 Chemscan -header Free Ammonia offset adjusted from -0.06 to 0.00 to match grab #11668939 chem tanks | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2026-03-05
CENTRAL | March | On site to perform station check No issues found | Newmarket (London) Yonge Street Elevated Tank | 2026-03-31
CENTRAL | March | Station Check (no issues found) Input data to PWQ CL17/Chemscan sample line hot water flush (Hypo& Ammonia chemical pumps manual off during flush) Verified CL17s (mg/L)(Draining) 13:30 Pre (Inlet) Free: Grab 0.04, A 0.01 Total: Grab 1.69, A 1.74 13:40 Post (header) Free: Grab 0.03, A 0.05 Total: Grab 3.10, A 3.19 Hypo tank 2 top up Ammonia Pump #1 had a "fail to start" on Friday and went to Duty 2, No issues found with pump and returned to Duty 1, ran without issue Chemscan (Grey & Green top up, Muratic/distilled new batch) | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2026-03-02
CENTRAL | March | On site to complete station check. Site offline and secure. | Newmarket (London) Yonge Street Elevated Tank | 2026-03-09
CENTRAL | March | Station Check Responding to security issue (outer door not secure (can be manually pulled open) however the inner door is secure, no signs of tampering) (ROC notified) Site off-line | Newmarket (London) Yonge Street Elevated Tank | 2026-03-02
CENTRAL | March | On site to complete station check. Site offline and secure. | Newmarket (London) Yonge Street Elevated Tank | 2026-03-16
CENTRAL | March | On site for PMs. -Completed JHSC inspection. All good -Notified ROC that tower pressure sensor (PIT) would be reading inaccurately while drawing water from the line for replacing the eyewash solution. Replaced eyewash solution | Newmarket (London) Yonge Street Elevated Tank | 2026-03-19
CENTRAL | March | On site to complete station check. Site offline and secure. | Newmarket (London) Yonge Street Elevated Tank | 2026-03-25
CENTRAL | March | Station and equipment check Complete maximo workorders Low temp alarm in "hut", turned portable heater back on Flushed w/m with dechlor in place starting @ 10:40 am - 11:20 am aprox. 14 l/s (22 m3) Fixed leaking hose bib in old well 14 building JHSC inspection complete no issues Ops normal | Newmarket (Northeast) Davis Drive Elevated Tank | 2026-03-24
CENTRAL | March | Onsite to refuel portable gas generator. | Newmarket (Southeast) Ivsbridge Elevated Tank | 2026-03-20
CENTRAL | March | Station and equipment check Take weekly BacT sample W11705420 and grabs @ 8:55 am Total: 2.78 mg/l Free: 0.03 mg/l Analyzer matched, reagents ok Mono: 2.33 mg/l Free Ammonia: 0.06 mg/l Total Ammonia: 0.52 mg/l Nitrite: 0.003 mg/l ET in delivery mode ET ops normal | Newmarket (Southeast) Ivsbridge Elevated Tank | 2026-03-31
CENTRAL | March | On site to complete PMs. Notified ROC of relevant alarms. -Altitude valve inspection: all good -Heat trace system inspection: all good -Portable generator test: all good, coordinated with Donny M. to top up fuel -JHSC inspection: all good -Flood alarm test: all good | Newmarket (Southeast) Ivsbridge Elevated Tank | 2026-03-27
CENTRAL | March | Station and equipment check Take weekly BacT sample W11705420 and grabs @ 10:20 am from outlet sample tap Total: 2.69 mg/l Free: 0.04 mg/l Analyzer matched and reagents ok all other readings on PD sheets Ops normal | Newmarket (West) Bathurst Tank | 2026-03-31
CENTRAL | March | Station Check (no issues found) Input data to PWQ 11:00 Verified Depolox (mg/L) Free: Grab 0.04, A 0.06 Total: Grab 2.88, A 3.08 (adjusted to match grabs) Samples #11637260, #11637661, & operational Depolox (new KI/distilled) | Newmarket (Southeast) Ivsbridge Elevated Tank | 2026-03-04
CENTRAL | March | Station Check (no issues found) Input data to PWQ 9:55 Verified Depolox (mg/l) Free: Grab 0.04, A 0.04 Total: Grab 2.92, A 2.91 10:00 Sample #11657622 | Newmarket (Southeast) Ivsbridge Elevated Tank | 2026-03-11
CENTRAL | March | Station Check (no issues found) Input data to PWQ 11:00 Verified Depolox (mg/L) Free: Grab 0.03, A 0.05 Total: Grab 2.62, A 2.67 Depolox (topped up electrolyte) 11:18 #11690790 bact. | Newmarket (Southeast) Ivsbridge Elevated Tank | 2026-03-25
CENTRAL | March | Onsite to perform monthly chlorine analyzer maintenance. | Newmarket (Southeast) Ivsbridge Elevated Tank | 2026-03-27
CENTRAL | March | Station Check (no issues found) Input data to PWQ 9:55 Verified Depolox (mg/l) Free: Grab 0.06, A 0.04 Total: Grab 3.14, A 3.10 (topped up Acetate & KI/distilled) 9:05 #11672723 bact. & operational samples | Newmarket (Southeast) Ivsbridge Elevated Tank | 2026-03-18
CENTRAL | March | Station Check (no issues found) Input data to PWQ 8:50 Verified Depolox (mg/L) Free: Grab 0.05, A 0.05 Total: Grab 2.60, A 2.62 Depolox (topped up electrolyte) 9:15 #11690790 bact. | Newmarket (West) Bathurst Tank | 2026-03-25
CENTRAL | March | :Station Check (no issues found) Input data to PWQ 10:00 Verified Depolox (mg/l) Free: Grab 0.05, A 0.05 Total: Grab 2.86. A 2.78 10:15 #11672723 bact. & operational samples | Newmarket (West) Bathurst Tank | 2026-03-18
CENTRAL | March | On site to complete station check Entered data into PD sheet No issues found | Newmarket Kirby Pumping Station | 2026-03-31
CENTRAL | March | Station Check (no issues found) Input data to PWQ 8:36 Verified Depolox (mg/l) Free: Grab 0.08, A 0.05 Total: Grab 2.76, A 2.76 Depolox (acetate, distilled/KI , electrolyte top up) 8:45 Sample #11657622 | Newmarket (West) Bathurst Tank | 2026-03-11
CENTRAL | March | Station Check (no issues found) Input data to PWQ 9:20 Verified Depolox (mg/L) Free: Grab 0.04, A 0.05 Total: Grab 2.70, A2.72 9:50 Samples #11637260, 11637661, operational Depolox (topped up acetate & electrolyte | Newmarket (West) Bathurst Tank | 2026-03-04
CENTRAL | March | Workorders: #11674409 Depolox Maint.: electrolyte top up 13:40 Verified (mg/l) Free: Grab 0.06, A 0.05 Total: Grab 2.70, A 2.76 #1167504 jhs #11675382 hi/lo test #11675664 dechlor. | Newmarket (West) Bathurst Tank | 2026-03-17
CENTRAL | March | Station and equipment check FCV: 0% Flow: 0 l/s suction pressure: 47 kPa discharge pressure: 340 kPa All pumps available Ops normal | Newmarket Kirby Pumping Station | 2026-03-06
CENTRAL | March | Station Check (no issues found) Input data to PWQ | Newmarket Kirby Pumping Station | 2026-03-02
CENTRAL | March | Station Check (no issues found) Input data to PWQ | Newmarket Kirby Pumping Station | 2026-03-09
CENTRAL | March | Station and equipment check Ops normal | Newmarket Kirby Pumping Station | 2026-03-13
CENTRAL | March | Station and equipment check All ok Ops normal | Newmarket Kirby Pumping Station | 2026-03-23
CENTRAL | March | Onsite for station check Recordings in PD sheet station ok | Newmarket Kirby Pumping Station | 2026-03-27
CENTRAL | March | Station Check (no issues found) Input data to PWQ Jhs inspection | Newmarket Kirby Pumping Station | 2026-03-16
CENTRAL | March | On site to complete station check. Station off. No issues found. Completed PD sheet | Newmarket Kirby Pumping Station | 2026-03-20
CENTRAL | March | On site to complete station check and weekly bacti sample W11706327 Ben put wells 1 and 2 into manual on for duration of station check -Verified analyzers: Influent Free Chlorine @ 10:06 Grab: 2.68mg/L Analyzer: 2.70 mg/L Effluent Free Chlorine @ 10:13 Grab: 2.60 mg/L Analyzer: 2.55mg/L Treated Free Chlorine @ 10:16 Grab: 0.09 mg/L Analyzer: 0.14 mg/L Treated Total Chlorine @ 10:19 Grab: 2.84 mg/L Analyzer: 2.88 mg/L - Changed treated free and effluent free reagents - Entered data into PD Sheet - Checked trends - Filled ammonia tank 1 | Newmarket Well 1 & 2 | 2026-03-31
CENTRAL | March | Onsite to complete monthly Maximo workorders Informed ROC (Angelica) of ongoings Found no issues Ops normal | Newmarket Kirby Pumping Station | 2026-03-26
CENTRAL | March | On site to complete station check. -Verified analyzers: Influent Free Chlorine @ 10:18 Grab: 2.68 mg/L Analyzer: 2.68 mg/L Effluent Free Chlorine @ 10:14 Grab: 2.56 mg/L Analyzer: 2.57 mg/L Treated Free Chlorine @ 10:10 Grab: 0.12 mg/L Analyzer: 0.13 mg/L Treated Total Chlorine @ 10:10 Grab: 2.90 mg/L Analyzer: 2.94 mg/L -Based on SL1000 grabs taken for ammonia pump 1 and 2, adjusted chlorine:ammonia ratio from 3.8 to 3.9 -Entered data into PD Sheet -Checked trends | Newmarket Well 1 & 2 | 2026-03-13
CENTRAL | March | Silicate top up 686 L -1089 L | Newmarket Well 1 & 2 | 2026-03-10
CENTRAL | March | On site with Alex B to complete station check and operator samples -Verified analyzers: Influent Free Chlorine @ 10:20 Grab: 2.60 mg/L Analyzer: 2.63 mg/L Effluent Free Chlorine @ 10:24 Grab: 2.62 mg/L Analyzer: 2.53 mg/L Treated Free Chlorine @ 10:29 Grab: 0.09 mg/L Analyzer: 0.14 mg/L Treated Total Chlorine @ 10:32 Grab: 2.90 mg/L Analyzer: 2.95 mg/L - Entered data into PD Sheet - Checked trends - Topped up well 2 mineral oil - Alex put well 13 into manual | Newmarket Well 1 & 2 | 2026-03-09
CENTRAL | March | Silicate top up: Before 671L After 1069L | Newmarket Well 1 & 2 | 2026-03-03
CENTRAL | March | On site to complete station check. -Verified analyzers: Influent Free Chlorine @ 14:42 Grab: 2.50 mg/L Analyzer: 2.53 mg/L Effluent Free Chlorine @ 14:39 Grab: 0.28 mg/L Analyzer: 0.32 mg/L Treated Free Chlorine @ 14:36 Grab: 0.12 mg/L Analyzer: 0.07 mg/L Treated Total Chlorine @ 14:36 Grab: 2.42 mg/L Analyzer: 2.52 mg/L -Entered data into PD Sheet -Checked trends | Newmarket Well 1 & 2 | 2026-03-20
CENTRAL | March | On site to complete station check -Verified analyzers: Influent Free Chlorine @ 12:12 Grab: 2.44 mg/L Analyzer: 2.42mg/L Effluent Free Chlorine @ 12:15 Grab: 0.15 mg/L Analyzer: 0.15 mg/L Treated Free Chlorine @ 12:18 Grab: 0.09 mg/L Analyzer: 0.8mg/L Treated Total Chlorine @ 12:21 Grab: 2.56 mg/L Analyzer: 2.48 mg/L - Entered data into PD Sheet - Checked trends - performed PM on silicate pumps: all good | Newmarket Well 1 & 2 | 2026-03-27
CENTRAL | March | On site with Alex B to complete station check and bacti samples (W11656837). -Verified analyzers: Influent Free Chlorine @ 10:12 Grab: 2.70 mg/L Analyzer: 2.61 mg/L Effluent Free Chlorine @ 10:15 Grab: 2.30 mg/L Analyzer: 2.31 mg/L Treated Free Chlorine @ 10:18 Grab: 0.11 mg/L Analyzer: 0.13 mg/L Treated Total Chlorine @ 10:21 Grab: 2.70 mg/L Analyzer: 2.81 mg/L - Changed Influent free analyzer reagents - Entered data into PD Sheet - Checked trends - Alex returned well 1 and 2 to auto - Alex put well 15 to manual on | Newmarket Well 1 & 2 | 2026-03-11
CENTRAL | March | NMW12 On site with Alex B to complete station check and weekly bacti samples W11638302 Alex B put wells into manual off -Verified analyzers: Influent Free Chlorine @ 9:47 Grab: 2.54 mg/L Analyzer: 2.60 mg/L Effluent Free Chlorine @ 9:50 Grab: 2.48 mg/L Analyzer: 2.56 mg/L Treated Free Chlorine @ 10:02 Grab: 0.09 mg/L Analyzer: 0.13 mg/L Treated Total Chlorine @ 9.57 Grab: 2.90 mg/L Analyzer: 2.94 mg/L - Entered data into PD Sheet - Checked trends - Alex put wells 1 and 2 back into auto - Alex put well 15 into auto | Newmarket Well 1 & 2 | 2026-03-04
CENTRAL | March | On site to complete PMs Informed ROC of relevant alarms Did chlorine leak detector test: all good Alex cleared alarms Calibrated and performed maintenance on turbidimeter: all good, reading 0.032 NTU Performed cleaning of chlorine analyzers: all good Verified analyzers: Influent free chlorine @ 14:34 Grab: 2.60 mg/L Analyzer: 2.52mg/L Effluent Free Chlorine @ 14:37 Grab: 0.15 mg/L Analyzer: 0.12 mg/L Treated Free Chlorine @ 14:40 Grab: 0.03 mg/L Analyzer: 0.06 mg/L Treated Total Chlorine @ 14:46 Grab: 2.08 mg/L Analyzer: 2.08 mg/L -Alex returned Newmarket wells 1 and 2 to auto | Newmarket Well 1 & 2 | 2026-03-04
CENTRAL | March | On site with Alex B to complete station check -Verified analyzers: Influent Free Chlorine @ 11:09 Grab: 2.70 mg/L Analyzer: 2.69 mg/L Effluent Free Chlorine @ 11:12 Grab: 2.52 mg/L Analyzer: 2.56 mg/L Treated Free Chlorine @ 11:15 Grab: 0.13 mg/L Analyzer: 0.13 mg/L Treated Total Chlorine @ 11:18 Grab: 2.82 mg/L Analyzer: 2.94mg/L - Entered data into PD Sheet - Checked trends - Filled ammonia tank 2 - Alex put Newmarket Well 15 into manual | Newmarket Well 1 & 2 | 2026-03-06
CENTRAL | March | On site to complete station check and collect operational samples. -Changed reagents for treated total analyzer -Verified analyzers: Influent Free Chlorine @ 10:30 Grab: 2.56 mg/L Analyzer: 2.64 mg/L Effluent Free Chlorine @ 10:27 Grab: 2.58 mg/L Analyzer: 2.62 mg/L Treated Free Chlorine @ 10:24 Grab: 0.16 mg/L Analyzer: 0.13 mg/L Treated Total Chlorine @ 10:24 Grab: 2.94 mg/L Analyzer: 3.01 mg/L -Entered data into PD Sheet -Checked trends | Newmarket Well 1 & 2 | 2026-03-02
CENTRAL | March | Changed chlorine cylinder bank B with Joe Williams. | Newmarket Well 1 & 2 | 2026-03-02
CENTRAL | March | Attending site to repair Influent Free chlorine analyzer push buttons (W11688098). ROC shut off well near end of cycle so that work could proceed. Calibration mode was used to reduce alarms from this equipment. Replaced all switches on analyzer circuit board. ROC was notified before and after maintenance activities. | Newmarket Well 1 & 2 | 2026-03-03
CENTRAL | March | Silicate top up: (76.3 to 114.3cm) | Newmarket Well 1 & 2 | 2026-03-24
CENTRAL | March | Received 9 full and gave 9 empty for chlorine delivery. | Newmarket Well 1 & 2 | 2026-03-12
CENTRAL | March | On site to complete station check and collect operational samples. -Placed wells in manual-on for duration of station check -Verified analyzers: Influent Free Chlorine @ 10:43 Grab: 2.80 mg/L Analyzer: 2.76 mg/L Effluent Free Chlorine @ 10:36 Grab: 2.56 mg/L Analyzer: 2.46 mg/L Treated Free Chlorine @ 10:33 Grab: 0.11 mg/L Analyzer: 0.13 mg/L Treated Total Chlorine @ 10:33 Grab: 2.80 mg/L Analyzer: 2.80 mg/L -Topped up ammonia tank 2 -Topped up well 2 mineral oil -Returned wells 1&2 to auto -Placed well 13 in manual-on -Entered data into PD Sheet -Checked trends | Newmarket Well 1 & 2 | 2026-03-23
CENTRAL | March | On site to complete station check and collect weekly bacti samples (W11673490). -Verified analyzers: Influent Free Chlorine @ 9:48 Grab: 2.56 mg/L Analyzer: 2.56 mg/L Effluent Free Chlorine @ 9:44 Grab: 2.56 mg/L Analyzer: 2.48 mg/L Treated Free Chlorine @ 9:41 Grab: 0.10 mg/L Analyzer: 0.13 mg/L Treated Total Chlorine @ 9:41 Grab: 2.82 mg/L Analyzer: 2.86 mg/L -Entered data into PD Sheet -Checked trends | Newmarket Well 1 & 2 | 2026-03-18
CENTRAL | March | On site to complete PMs with Alex B Informed ROC of relevant alarms Performed deep well exhaust valve maintenance for both wells: all good Performed PM for silicate system: - Put wells and chlorine boosters into manual off - Put dechlor in waste chamber - Hot flushed silicate pumping system - Hot flushed silicate injection points - Isolated raw main from contact tank and depressurized raw main. Pulled injection points and performed maintenance - Ran to waste while priming silicate lines - Performed drawdowns on silicate system - Changed max flow scada silicate set points from 220ml/L to 230ml/L for both silicate pumps - Places chlorine boosters into auto - Placed wells in auto and started duty Performed PM for ammonia system - performed drawdowns on ammonia pump one and two: all good Performed JHSC Inspection: all good - Tested silicate dosing: all good for both pumps | Newmarket Well 1 & 2 | 2026-03-05
CENTRAL | March | On site to complete station check and collect weekly bacti samples (W11690106) -Verified analyzers: Influent Free Chlorine @ 9:33 Grab: 2.54 mg/L Analyzer: 2.57 mg/L Effluent Free Chlorine @ 9:30 Grab: 2.62 mg/L Analyzer: 2.53 mg/L Treated Free Chlorine @ 9:27 Grab: 0.11 mg/L Analyzer: 0.13 mg/L Treated Total Chlorine @ 9:27 Grab: 2.84 mg/L Analyzer: 2.87 mg/L -Entered data into PD Sheet -Checked trends | Newmarket Well 1 & 2 | 2026-03-25
CENTRAL | March | On site to complete station check and collect operational samples. -Changed chlorine cylinder bank A with Joe W. -Topped up ammonia tank 1 -Verified analyzers: Influent Free Chlorine @ 9:42 Grab: 2.50 mg/L Analyzer: 2.51 mg/L Effluent Free Chlorine @ 9:38 Grab: 2.58 mg/L Analyzer: 2.58 mg/L Treated Free Chlorine @ 9:34 Grab: 0.16 mg/L Analyzer: 0.14 mg/L Treated Total Chlorine @ 9:34 Grab: 3.00 mg/L Analyzer: 2.92 mg/L -Entered data into PD Sheet -Checked trends | Newmarket Well 1 & 2 | 2026-03-16
CENTRAL | March | On site to complete PMs. Notified ROC of relevant alarms. -Completed chlorine inspection: added dechlor to waste chamber and started backflushing slightly while completing work. Closed waste valve when finished. All good -Completed bank B chlorine cylinder change with Ben H. | Newmarket Well 1 & 2 | 2026-03-27
CENTRAL | March | Station Check (no issues found) site off-line | Newmarket Well 14 | 2026-03-09
CENTRAL | March | Flush water main for 1 hour @ aprox 13 L/S Flow meter reading after 46 m3 Ops normal | Newmarket Well 14 | 2026-03-13
CENTRAL | March | Visual inspection | Newmarket Well 14 | 2026-03-16
CENTRAL | March | Onsite to respond to loss of power alarms at 12:24. Found power pole breaker tripped on phase C outside of site. No issues found in facility. Notified ROC an on call electrician Tyler Z. 14:54. Electrician and electrical company on route route for repair. Station is offline, only lost communication to EGmCDD. | Newmarket Well 14 | 2026-03-21
CENTRAL | March | On site to complete station check -Verified analyzers: Influent Free Chlorine @ 13:43 Grab: 3.12mg/L Analyzer: 3.06 mg/L Effluent Free Chlorine @ 13:45 Grab: 0.19 mg/L Analyzer: 0.16 mg/L Treated Free Chlorine @ 13:48 Grab: 0.08 mg/L Analyzer: 0.8 mg/L Treated Total Chlorine @ 13:51 Grab: 2.98 mg/L Analyzer: 3.00 mg/L - Entered data into PD Sheet - Checked trends - Changed Influent free reagents - Completed work order W11633920 | Newmarket Well No. 15 | 2026-03-27
CENTRAL | March | Station Check No issues found Station Offline | Newmarket Well 14 | 2026-03-02
CENTRAL | March | On site to complete station check and weekly bacti sample W11706327 Ben put well 15 in manual on for duration of station check -Verified analyzers: Influent Free Chlorine @ 12:18 Grab: 3.00 mg/L Analyzer: 2.90 mg/L Effluent Free Chlorine @ 12:21 Grab: 2.88 mg/L Analyzer: 2.87 mg/L Treated Free Chlorine @ 12:24 Grab: 0.13 mg/L Analyzer: 0.14 mg/L Treated Total Chlorine @ 12:31 Grab: 3.38 mg/L Analyzer: 3.50 mg/L - Entered data into PD Sheet - Checked trends - Topped up well mineral oil | Newmarket Well No. 15 | 2026-03-31
CENTRAL | March | On site to complete station check and collect operational samples. -Verified analyzers: Influent Free Chlorine @ 11:21 Grab: 3.06 mg/L Analyzer: 3.00 mg/L Effluent Free Chlorine @ 11:15 Grab: 2.90 mg/L Analyzer: 2.80 mg/L Treated Free Chlorine @ 11:11 Grab: 0.17 mg/L Analyzer: 0.14 mg/L Treated Total Chlorine @ 11:11 Grab: 3.48 mg/L Analyzer: 3.41 mg/L -Entered data into PD Sheet -Checked trends | Newmarket Well No. 15 | 2026-03-02
CENTRAL | March | Received chlorine delivery. 6 full, gave 6 empty. | Newmarket Well No. 15 | 2026-03-12
CENTRAL | March | On site to complete station check. -Placed well in manual for duration of station check -Verified analyzers: Influent Free Chlorine @ 8:46 Grab: 2.82 mg/L Analyzer: 2.71 mg/L Effluent Free Chlorine @ 8:41 Grab: 0.11 mg/L Analyzer: 0.14 mg/L Treated Free Chlorine @ 8:38 Grab: 0.10 mg/L Analyzer: 0.07 mg/L Treated Total Chlorine @ 8:38 Grab: 2.84 mg/L Analyzer: 2.85 mg/L -Topped up well 15 mineral oil. Noticed debris in reservoir, created WO W11732814 for maintenance to address it -Entered data into PD Sheet -Checked trends -Returned well to auto | Newmarket Well No. 15 | 2026-03-13
CENTRAL | March | On site with Alex B to complete station check and weekly bacti samples W11656837 -Verified analyzers: Influent Free Chlorine @ 12:21 Grab: 2.94 mg/L Analyzer: 2.90 mg/L Effluent Free Chlorine @ 12:24 Grab: 2.84 mg/L Analyzer: 2.84 mg/L Treated Free Chlorine @ 12:27 Grab: 0.13 mg/L Analyzer: 0.14 mg/L Treated Total Chlorine @ 12:38 Grab: 3.30 mg/L Analyzer: 3.38 mg/L - Entered data into PD Sheet - Checked trends - Alex put well 15 back into auto | Newmarket Well No. 15 | 2026-03-11
CENTRAL | March | Silicate top up: Before 275.6L After 378L | Newmarket Well No. 15 | 2026-03-03
CENTRAL | March | NMW15 On site with Alex B to complete station check -Verified analyzers: Influent Free Chlorine @ 12:40 Grab: 2.98 mg/L Analyzer: 2.93 mg/L Effluent Free Chlorine @ 12:44 Grab: 2.88 mg/L Analyzer: 2.84 mg/L Treated Free Chlorine @ 12:47 Grab: 0.14 mg/L Analyzer: 0.15 mg/L Treated Total Chlorine @ 12:51 Grab: 3.34 mg/L Analyzer: 3.43 mg/L - Entered data into PD Sheet - Checked trends - Alex B and Jay G changed chlorine cylinder bank B - Created W11714356 to quick report assessment of ammonia pump 1 dosing - Changed max flow set point from 98 to 102 for ammonia pump one: all good | Newmarket Well No. 15 | 2026-03-06
CENTRAL | March | On site with Alex B to complete station check and operator samples - Alex put well 13 back into auto - Alex put well 15 into manual for duration of station check -Verified analyzers: Influent Free Chlorine @ 13:33 Grab: 2.86 mg/L Analyzer: 2.84 mg/L Effluent Free Chlorine @ 13:36 Grab: 2.76 mg/L Analyzer: 2.79mg/L Treated Free Chlorine @ 13:39 Grab: 0.10 mg/L Analyzer: 0.14 mg/L Treated Total Chlorine @ 13:45 Grab: 3.26 mg/L Analyzer: 3.37 mg/L - Entered data into PD Sheet - Checked trends - Mixed and filled ammonia tank one - Alex returned well 15 to auto | Newmarket Well No. 15 | 2026-03-09
CENTRAL | March | NMW15 On site with Alex B to complete station check and weekly bacti samples W11638302 -Verified analyzers: Influent Free Chlorine @ 11:04 Grab: 2.80 mg/L Analyzer: 2.79 mg/L Effluent Free Chlorine @ 11:07 Grab: 2.80 mg/L Analyzer: 2.84 mg/L Treated Free Chlorine @ 11:10 Grab: 0.15 mg/L Analyzer: 0.15 mg/L Treated Total Chlorine @ 11:14 Grab: 3.26 mg/L Analyzer: 3.36 mg/L - Entered data into PD Sheet - Checked trends - Alex returned well 15 to auto - Performed drawdown on ammonia pump one - Alex placed ammonia pump one in manual - Exercised ammonia valve one locally, Alex returned to auto | Newmarket Well No. 15 | 2026-03-04
CENTRAL | March | Discussed with Ben H, returned well to auto | Newmarket Well No. 15 | 2026-03-02
CENTRAL | March | 08:20 Notified roc of work. Locked out well 15. Emptied and Cleaned silicate tank with Alex Bell. Cleaned silicate foot valves. Replace silicate pump 1 pump tube. Joe Williams topped up silicate tank from empty to 376.6 L. Changed left chlorine cylinder. Primed both silicate pumps. Adjusted p1 max pump rate from 205 to 244 ml/min. Adjusted silicate concentration SCADA setpoint from 27 to 38%. 13:50 Placed silicate pumps and well 15 back to auto. | Newmarket Well No. 15 | 2026-03-24
CENTRAL | March | On site to complete station check and collect operational samples. -Verified analyzers: Influent Free Chlorine @ 13:45 Grab: 2.98 mg/L Analyzer: 2.96 mg/L Effluent Free Chlorine @ 13:38 Grab: 2.84 mg/L Analyzer: 2.81 mg/L Treated Free Chlorine @ 13:34 Grab: 0.13 mg/L Analyzer: 0.14 mg/L Treated Total Chlorine @ 13:34 Grab: 3.48 mg/L Analyzer: 3.42 mg/L -Entered data into PD Sheet -Checked trends -Returned well to auto | Newmarket Well No. 15 | 2026-03-23
CENTRAL | March | Returned well 15 to auto. | Newmarket Well No. 15 | 2026-03-19
CENTRAL | March | On site to complete station check, collect weekly bacti samples (W11690106), and reinstall silicate injection point 2. -Notified ROC of relevant alarms. Added dechlor to waste chamber. Isolated raw main via valve on influent side of contact tank and depressurized raw main via waste valve. Reinstalled silicate injection point 2. Primed line while backflushing well slightly. -Placed well in manual-on -Verified analyzers: Influent Free Chlorine @ 12:37 Grab: 3.02 mg/L Analyzer: 2.93 mg/L Effluent Free Chlorine @ 12:42 Grab: 2.98 mg/L Analyzer: 2.91 mg/L Treated Free Chlorine @ 12:46 Grab: 0.14 mg/L Analyzer: 0.15 mg/L Treated Total Chlorine @ 12:46 Grab: 3.52 mg/L Analyzer: 3.50 mg/L -Confirmed both injection points functional. Left silicate injection point 2 in use -Returned well to auto -Entered data into PD Sheet -Checked trends | Newmarket Well No. 15 | 2026-03-25
CENTRAL | March | Attending site to check 'motor error' on Total chlorine analyzer (W11761894). Replaced motor and verified reading. Analyzer reading 2.83mg/L, and average of 3 dpd grabs was 2.81mg/L. ROC was notified before and after maintenance activities. | Newmarket Well No. 15 | 2026-03-26
CENTRAL | March | On site to complete PMs. Notified ROC. -Completed JHSC inspection, all good -Performed maintenance on and calibrated turbidimeter, analyzer read 0.060 NTU afterwards | Newmarket Well No. 15 | 2026-03-19
CENTRAL | March | Returned well to auto once maintenance finished with the mineral oil pot. Added ammonia to and mixed ammonia tank 2, returned ammonia valve 2 to auto. | Newmarket Well No. 15 | 2026-03-20
CENTRAL | March | Clean drip oiler and refill with new mineral oil | Newmarket Well No. 15 | 2026-03-20
CENTRAL | March | On site to troubleshoot treated free hi and hihi alarm and ammonia pumps with Donny M. Notified ROC of relevant alarms. Added dechlor to drain chamber and began backflushing. Verified analyzer: Treated Free Chlorine @ 9:32 Grab: 2.40 mg/L Analyzer: 1.20 mg/L Analyzer read 2.40 mg/L after adjustment. 9:43 Combined lolo alarm came in while backflushing. There was a free chlorine analyzer reading of 1.68 mg/L. Replaced diaphragm in ammonia pump 2. Cleaned foot valves for both pumps. Performed drawdowns. Placed well in manual-on. Placed chlorine dosing in manual for ammonia dosage tuning. Treated Free Chlorine @ 14:12 Grab: 0.13 mg/L Analyzer: 0.25 mg/L Analyzer read 0.13 mg/L after adjustment. Returned well to auto, returned chlorine dosing to auto. | Newmarket Well No. 15 | 2026-03-03
CENTRAL | March | On site to complete station check and collect weekly bacti samples (W11673490). -Placed well in manual for duration of station check -Verified analyzers: Influent Free Chlorine @ 11:25 Grab: 3.04 mg/L Analyzer: 2.93 mg/L Effluent Free Chlorine @ 11:16 Grab: 2.90 mg/L Analyzer: 2.89 mg/L Treated Free Chlorine @ 11:10 Grab: 0.12 mg/L Analyzer: 0.15 mg/L Treated Total Chlorine @ 11:10 Grab: 3.40 mg/L Analyzer: 3.46 mg/L -Entered data into PD Sheet -Checked trends -Returned well to auto | Newmarket Well No. 15 | 2026-03-18
CENTRAL | March | On site to complete PMs. Notified ROC. -Completed ammonia inspection: all good Ammonia pump 1 max flow setpoint changed from 102 to 99 mL/min based on drawdowns Ammonia pump 2 max flow setpoint changed from 98 to 102 mL/min based on drawdowns -Completed deep well exhaust valve maintenance -Completed maintenance on CL17 chlorine analyzers, verified afterwards: Influent Free Chlorine @ 12:34 Grab: 3.16 mg/L Analyzer: 3.23 mg/L Effluent Free Chlorine @ 12:42 Grab: 0.18 mg/L Analyzer: 0.20 mg/L Treated Free Chlorine @ 12:31 Grab: 0.10 mg/L Analyzer: 0.10 mg/L Motor error issue persistent with treated total analyzer. Analyzer offline for now. Leaving well in manual-off, contacted Eric S. to come replace the motor and had ROC create CMU. | Newmarket Well No. 15 | 2026-03-26
CENTRAL | March | On site to complete PMs. Notified ROC. -Completed chlorine leak detection test: all good -Replaced reagents for treated total and free chlorine analyzers | Newmarket Well No. 15 | 2026-03-18
CENTRAL | March | On site to complete station check. -Placed well in manual-off for duration of station check -Verified analyzers: Influent Free Chlorine @ 7:48 Grab: 2.72 mg/L Analyzer: 2.69 mg/L Effluent Free Chlorine @ 7:45 Grab: 0.09 mg/L Analyzer: 0.12 mg/L Treated Free Chlorine @ 7:42 Grab: 0.08 mg/L Analyzer: 0.06 mg/L Treated Total Chlorine @ 7:42 Grab: 2.56 mg/L Analyzer: 2.51 mg/L -Filled ammonia tank 2 with water; did not add ammonia yet, placed valve 2 into manual-closed -Performed silicate pump drawdowns. Changed pump 1 max flow SCADA setpoint from 280 to 240 mL/min. Changed pump 2 SCADA max flow setpoint from 270 to 250 mL/min. Adjusted PSV and PRV on chemical board to higher settings. -Pump 1 appears to be pumping a small amount of air which may have caused previous dosing issues. Will address next week during silicate work; for now, silicate pump 1 remains manual-off but may be used with partial efficacy if needed. -Entered data into PD Sheet -Checked trends -Kept well in manual off for maintenance to perform work on mineral oil pot | Newmarket Well No. 15 | 2026-03-20
CENTRAL | March | On site to complete PMs. Notified ROC. -Completed chlorine inspection: all good. Added dechlor to waste chamber and backflushed slightly during work. Chlorinator 1 v-notch passes slightly under heavy vacuum; no corrective action currently needed -Eric S. on site to continue maintenance on treated total analyzer, well remains in manual-off | Newmarket Well No. 15 | 2026-03-26
CENTRAL | March | On site to complete station check and collect operational samples. -Placed well in manual-on for duration of station check -Verified analyzers: Influent Free Chlorine @ 13:12 Grab: 2.98 mg/L Analyzer: 2.86 mg/L Effluent Free Chlorine @ 13:09 Grab: 2.86 mg/L Analyzer: 2.73 mg/L Treated Free Chlorine @ 12:58 Grab: 0.11 mg/L Analyzer: 0.14 mg/L Treated Total Chlorine @ 12:58 Grab: 3.30 mg/L Analyzer: 3.34 mg/L -Change chlorine cylinder B with Joe W. -Entered data into PD Sheet -Checked trends -Returned well to auto -Cleaned foot valve for silicate pump 1 | Newmarket Well No. 15 | 2026-03-16
CENTRAL | March | Silicate top up 211 L - 380 L | Newmarket Well No. 15 | 2026-03-10
CENTRAL | March | Placed well 15 in manual-off after switching ammonia pumps did not remedy hihi free chlorine spike. | Newmarket Well No. 15 | 2026-03-03
CENTRAL | March | Onsite to troubleshoot silicate issues Silicate tank filling while well is off, water was passing through injection point, into the calibration column and back feeding into the silicate tank. Using C1V1/V2 = C2 I adjusted silicate concentration from 38% to 27%. Pulled injection points, both had silicate in chunks in check valves, disassembled and cleaned with hot water. Able to get injection point 1 back into service, injection point 2 check valve failed (leaving OOS) when discharge header was recharged. Hand pump had to be disassembled and cleaned as it was seized, causing power failure to chlorine room tripping the breaker. Silicate tank needed to be mixed, used hand pump onsite to mix the tank. Silicate P1 pulling in air, cut suction line and added new parker fitting, cleared air bubbles out of line Performed drawdowns on silicate P1 and P2 adjusted silicate P1 from 240 ml/min to 205 ml/min. Put everything back to auto. Facility ok | Newmarket Well No. 15 | 2026-03-20
CENTRAL | March | On site with Ben H to complete PMs. Alex on site to complete silicate PM. - Performed chlorine inspection: all good - Performed chlorine analyzer maintenance: all good - Performed pressure relief valve test on well 13: all good - Performed terbidimeter cleaning: all good - Performed H&S inspection: all good Alex verified analyzers: Influent Free Chlorine @ 14:52 Grab: 2.34 mg/L Analyzer: 2.37 mg/L Effluent Free Chlorine @ 14:59 Grab: 0.53 mg/L Analyzer: 0.53 mg/L Treated Free Chlorine @ 14:56 Grab: 0.07 mg/L Analyzer: 0.07 mg/L Treated Total Chlorine @ 14:53 Grab: 2.18 mg/L Analyzer: 2.25 mg/L | Newmarket Wells 13-16 | 2026-03-12
CENTRAL | March | NMW136 On site to complete station check and weekly bacti sample W11706327 Ben H. put well 13 in manual on for duration of station check -Verified analyzers: Influent Free Chlorine @ 8:05 Grab: 2.90 mg/L Analyzer: 2.92 mg/L Effluent Free Chlorine @ 8:08 Grab: 2.48mg/L Analyzer: 2.60 mg/L Treated Free Chlorine @ 8:11 Grab: 0.15 mg/L Analyzer: 0.11 mg/L Treated Total Chlorine @ 8:18 Grab: 3.14 mg/L Analyzer: 3.01 mg/L - Entered data into PD Sheet - Checked trends - Changed treated total reagents | Newmarket Wells 13-16 | 2026-03-31
CENTRAL | March | On site with Alex B to complete station check and weekly bacti samples (W11656837). Alex put well 13 into manual on for duration of the station check -Verified analyzers: Influent Free Chlorine @ 8:53 Grab: 2.60 mg/L Analyzer: 2.68 mg/L Effluent Free Chlorine @ 8:56 Grab: 2.38 mg/L Analyzer: 2.30 mg/L Treated Free Chlorine @ 9:00 Grab: 0.08 mg/L Analyzer: 0.12 mg/L Treated Total Chlorine @ 9:03 Grab: 2.72 mg/L Analyzer: 2.76 mg/L - Entered data into PD Sheet - Checked trends - -Topped up well 13 mineral oil - Alex put well 13 back in auto - Alex put well 1 and 2 into manual-on | Newmarket Wells 13-16 | 2026-03-11
CENTRAL | March | Silicate top up: Before 2044L After 2352L | Newmarket Wells 13-16 | 2026-03-03
CENTRAL | March | Onsite to respond to treated free high alarm- informed by ROC: Took grab to verify analyzer (09:58): Treated free grab: 0.10 Treated free analyzer: 0.12 Treated free analyzer onsite not matching up with treated free scada reading- informed Ben H, and Eric S. Work order has been created. Instrumentation team will respond to site to further investigate. | Newmarket Wells 13-16 | 2026-03-10
CENTRAL | March | Received 8 full chlorine cylinders in delivery exchange for 8 empties. | Newmarket Wells 13-16 | 2026-03-02
CENTRAL | March | Silicate top up 1929 L - 3481 L Also exhaust fan in well 13 building very loud, turned off Will create workorder for maintenance to service or replace Ops normal | Newmarket Wells 13-16 | 2026-03-10
CENTRAL | March | Returned well 13 to auto. | Newmarket Wells 13-16 | 2026-03-02
CENTRAL | March | NMW136 On site with Alex B to complete station check -Verified analyzers: Influent Free Chlorine @ 9:56 Grab: 2.64 mg/L Analyzer: 2.73 mg/L Effluent Free Chlorine @ 10:01 Grab: 2.52 mg/L Analyzer: 2.43 mg/L Treated Free Chlorine @ 10:04 Grab: 0.15 mg/L Analyzer: 0.12 mg/L Treated Total Chlorine @ 10:07 Grab: 2.82 mg/L Analyzer: 2.80 mg/L - Entered data into PD Sheet - Checked trends - Alex B. and Jay G. changed chlorine cylinder bank B | Newmarket Wells 13-16 | 2026-03-06
CENTRAL | March | Wel_AIT3 R1S13:Ch0 reading inaccurate based on Eric's testing. Move to R1S13:Ch02 temporarily until card is either replaced or drawings and literature updated. Eric will create a WO to initiate. | Newmarket Wells 13-16 | 2026-03-10
CENTRAL | March | On site to complete station check and collect operational samples. -Verified analyzers: Influent Free Chlorine @ 9:41 Grab: 2.70 mg/L Analyzer: 2.76 mg/L Effluent Free Chlorine @ 9:30 Grab: 2.32 mg/L Analyzer: 2.36 mg/L Treated Free Chlorine @ 9:26 Grab: 0.10 mg/L Analyzer: 0.11 mg/L Treated Total Chlorine @ 9:26 Grab: 2.82 mg/L Analyzer: 2.72 mg/L -Placed well 13 in manual-on to draw down chlorine cylinder bank B -Entered data into PD sheet -Checked trends | Newmarket Wells 13-16 | 2026-03-02
CENTRAL | March | On site with Alex B to complete station check and operational samples -Verified analyzers: Influent Free Chlorine @ 11:51 Grab: 2.70 mg/L Analyzer: 2.73 mg/L Effluent Free Chlorine @ 11:54 Grab: 2.48 mg/L Analyzer: 2.40mg/L Treated Free Chlorine @ 11:57 Grab: 0.15 mg/L Analyzer: 0.12 mg/L Treated Total Chlorine @ 12:00 Grab: 2.78 mg/L Analyzer: 2.74 mg/L - Entered data into PD Sheet - Checked trends | Newmarket Wells 13-16 | 2026-03-09
CENTRAL | March | On site to complete station check -Verified analyzers: Influent Free Chlorine @ 9:14 Grab: 2.88 mg/L Analyzer: 2.98 mg/L Effluent Free Chlorine @ 9:17 Grab: 2.62 mg/L Analyzer: 2.63 mg/L Treated Free Chlorine @ 9:20 Grab: 0.09mg/L Analyzer: 0.12 mg/L Treated Total Chlorine @ 9:34 Grab: 2.94 mg/L Analyzer: 3.06 mg/L - Entered data into PD Sheet - Checked trends - Changed treated free reagents | Newmarket Wells 13-16 | 2026-03-27
CENTRAL | March | Onsite for station check recordings in PD sheet adjust effluent free chlorine analyzer adjust silicate p2 max flow from 225 ml/min to 255 ml/min based on drawdowns adjusted well 13 drip oiler to ~4-5 drips/min station ok | Newmarket Wells 13-16 | 2026-03-20
CENTRAL | March | On site to complete station check and collect operational samples. -Topped up ammonia tank 2 -Verified analyzers: Influent Free Chlorine @ 11:00 Grab: 2.86 mg/L Analyzer: 2.84 mg/L Effluent Free Chlorine @ 10:55 Grab: 2.50 mg/L Analyzer: 2.50 mg/L Treated Free Chlorine @ 10:47 Grab: 0.07 mg/L Analyzer: 0.11 mg/L Treated Total Chlorine @ 10:47 Grab: 2.84 mg/L Analyzer: 2.86 mg/L -Adjusted mineral oil pot on well 13 to 1-2 drops per minute from <1 drops per minute -Entered data into PD sheet -Checked trends | Newmarket Wells 13-16 | 2026-03-16
CENTRAL | March | On site to complete PMs. Notified ROC of relevant alarms. -Performed silicate hot flush: added dechlor to well 13 waste chamber. Flushed silicate chemical boards with hot water. Performed drawdowns. Pump 2 max flow setpoint changed from 225 to 240 mL/min. Backflushed for a short period via well 13 PRV to get rid of any excess silicate from work. -Worked with Joe D. to tighten pigtail on bank B chlorine cylinder with halogen 2B. | Newmarket Wells 13-16 | 2026-03-19
CENTRAL | March | On site to complete PMs. Notified ROC of relevant alarms. -Performed ammonia inspection: Adjusted pump 2 max flow setpoint from 220 to 230 mL/min based on drawdowns.Otherwise all good. | Newmarket Wells 13-16 | 2026-03-27
CENTRAL | March | Silicate top up (57.5 to 65.3 cm) | Newmarket Wells 13-16 | 2026-03-24
CENTRAL | March | On site to complete station check and collect operational samples. -Verified analyzers: Influent Free Chlorine @ 11:49 Grab: 2.74 mg/L Analyzer: 2.83 mg/L Effluent Free Chlorine @ 11:46 Grab: 2.54 mg/L Analyzer: 2.57 mg/L Treated Free Chlorine @ 11:40 Grab: 0.09 mg/L Analyzer: 0.12 mg/L Treated Total Chlorine @ 11:40 Grab: 2.94 mg/L Analyzer: 3.06 mg/L -Entered data into PD sheet -Checked trends -Returned well 13 to auto -Placed well 15 in manual-on | Newmarket Wells 13-16 | 2026-03-23
CENTRAL | March | On site to complete station check and collect weekly bacti samples (W11673490). -Verified analyzers: Influent Free Chlorine @ 8:18 Grab: 2.90 mg/L Analyzer: 2.97 mg/L Effluent Free Chlorine @ 8:22 Grab: 2.30 mg/L Analyzer: 2.41 mg/L Treated Free Chlorine @ 8:08 Grab: 0.13 mg/L Analyzer: 0.09 mg/L Treated Total Chlorine @ 8:08 Grab: 2.48 mg/L Analyzer: 2.57 mg/L -Adjusted mineral oil pot on well 13 to 2-3 drops per minute from <1 drops per minute. Will continue to monitor -Entered data into PD sheet -Checked trends | Newmarket Wells 13-16 | 2026-03-18
CENTRAL | March | On site to complete station check. -Placed well 13 in manual for duration of station check -Verified analyzers: Influent Free Chlorine @ 12:55 Grab: 2.68 mg/L Analyzer: 2.66 mg/L Effluent Free Chlorine @ 12:44 Grab: 2.42 mg/L Analyzer: 2.19 mg/L Adjusted analyzer based on average of 3 grabs. Analyzer read 2.42 mg/L afterwards. Treated Free Chlorine @ 12:34 Grab: 0.12 mg/L Analyzer: 0.11 mg/L Treated Total Chlorine @ 12:51 Grab: 2.74 mg/L Analyzer: 2.53 mg/L Adjusted analyzer based on average of 3 grabs. Analyzer read 2.74 mg/L afterwards. -Placed well in manual-off -Performed maintenance on well 13 deep well exhaust valve -Calibrated turbidimeter; analyzer read 0.043 NTU afterwards -Entered data into PD sheet -Checked trends | Newmarket Wells 13-16 | 2026-03-13
CENTRAL | March | Onsite to troubleshoot treated free reading discrepancy between analyzer and SCADA reading. Informed ROC and asked them to put well in manual off. Based on the troubleshooting we found issues with the analog input. Reached out to oncall PCS person (Kyle Carlen). He informed us to move the input from I11300 to I11302. Verified the analyzer reading. No issues. Treated Free chlorine reading spiked few times during the troubleshooting, well was in manual off during that period. Informed ROC, armed the building and no issues. | Newmarket Wells 13-16 | 2026-03-10
CENTRAL | March | On site to complete PMs. Notified ROC of relevant alarms. -Placed well 13 in manual-off then local -Added dechlor to waste chamber, isolated contact tank on influent side in order to depressurize raw main. Depressurized via well 13 PRV. Pulled injection points, opened influent side valve slightly (STILL MOSTLY CLOSED) to repressurize in order to run hot water through chemical boards and injection points. -Leaving site early to receive chlorine deliveries at other Newmarket well sites. Well 13 left in local, silicate pumps in manual-off. Injection points still removed from system and influent side valve still mostly closed. Notified ROC site would remain in local. | Newmarket Wells 13-16 | 2026-03-12
CENTRAL | March | NMW136 On site with Alex B to complete station check and weekly bacti samples W11638302 -Verified analyzers: Influent Free Chlorine @ 8:38 Grab: 2.74 mg/L Analyzer: 2.70 mg/L Effluent Free Chlorine @ 8:41 Grab: 2.58 mg/L Analyzer: 2.52 mg/L Treated Free Chlorine @ 8:44 Grab: 0.11mg/L Analyzer: 0.13 mg/L Treated Total Chlorine @ 8:47 Grab: 2.86mg/L Analyzer: 2.92mg/L - Entered data into PD Sheet - Checked trends - topped up ammonia tank one - Topped up well 13 mineral oil | Newmarket Wells 13-16 | 2026-03-04
CENTRAL | March | Returned to site to continue work on silicate system. Christian B and Ben H on site to complete other PMs. -Cleaned injection points. Depressurized raw main via isolation on influent side of contact tank and opening well 13 PRV in order to put injection points back in place. Repressurized system and fully opened isolation valve. Primed silicate lines while backflushing slightly through well 13 PRV. Performed drawdowns on both silicate pumps. Changed max flow SCADA setpoint from 265mL/min to 225mL/min for silicate pump 2. -Replaced eyewash solution in silicate room -Returned well 13 to auto once PMs completed | Newmarket Wells 13-16 | 2026-03-12
CENTRAL | March | On site to complete PMs. Notified ROC of relevant alarms. -Completed chlorine leak detection test: all good -Created CMU W11744100 to replace pigtail on bank B cylinder 2nd from right (with halogen 2B) -Cleaned influent free chlorine analyzer to try and reduce trend ?jaggedness?. Verified analyzer afterward: Influent Free Chlorine @ 13:51 Grab: 2.42 mg/L Analyzer: 2.40 mg/L | Newmarket Wells 13-16 | 2026-03-18
CENTRAL | March | Change oil well 13 motor and drain drip oiler and clean Fill with new mineral oil Placed back in auto | Newmarket Wells 13-16 | 2026-03-04
CENTRAL | March | On site to complete station check and collect weekly bacti samples (W11690106) -Placed well 15 in manual-off. Started area duty 1 -Changed reagents for effluent free chlorine analyzer -Verified analyzers: Influent Free Chlorine @ 8:10 Grab: 2.86 mg/L Analyzer: 2.87 mg/L Effluent Free Chlorine @ 8:20 Grab: 2.22 mg/L Analyzer: 2.18 mg/L Treated Free Chlorine @ 8:24 Grab: 0.12 mg/L Analyzer: 0.10 mg/L Treated Total Chlorine @ 8:24 Grab: 2.60 mg/L Analyzer: 2.68 mg/L -Topped up well 13 mineral oil -Entered data into PD sheet -Checked trends | Newmarket Wells 13-16 | 2026-03-25
WEST | March | Onsite for station check Pump running Chamber secure and dry No issues observed | Nobleton Booster Pumping Station | 2026-03-09
WEST | March | Onsite for station check Pump running Chamber secure and dry No issues observed | Nobleton Booster Pumping Station | 2026-03-06
WEST | March | Onsite for station check Pump on Site secure Chamber dry | Nobleton Booster Pumping Station | 2026-03-16
WEST | March | Onsite for station check Pump appears to be running | Nobleton Booster Pumping Station | 2026-03-23
WEST | March | Onsite for station check Pump on Site secure Chamber dry | Nobleton Booster Pumping Station | 2026-03-20
WEST | March | Onsite for station check and to collect weekly micro sample W11637120 Tower draining Checked residuals mg/l @0921 Free analyzer 1.07 grab 1.52 Total analyzer 1.54 grab 1.69 Adjusted both analyzers | Nobleton North Elevated Tank | 2026-03-04
WEST | March | Onsite for station check Pump on Site secure Chamber dry | Nobleton Booster Pumping Station | 2026-03-27
WEST | March | On site for station check and to collect weekly micro sample W11690158 Tower draining Check residuals mg/l @0914 Free analyzer 1.52 grab 1.33 Total analyzer 1.62 grab 1.64 Adjusted free analyzer | Nobleton North Elevated Tank | 2026-03-25
WEST | March | On site for station check and to collect weekly micro sample W11672653 Tower draining Check residuals mg/l @0907 Free analyzer 1.62 grab 1.59 Total analyzer 2.32 grab 1.87 Adjusted total analyzer | Nobleton North Elevated Tank | 2026-03-18
WEST | March | On site to complete work orders Completed maintenance on chlorine analyzer Reduced flow, resulting in a lower free chlorine residual Added grit Added electrolyte Grabs after Free analyzer 1.62 grab 1.42 Total analyzer 1.71 grab 1.71 Adjusted free analyzer Ran portable generator with no issues Completed jhsc | Nobleton North Elevated Tank | 2026-03-17
WEST | March | Onsite for station check and to collect weekly micro sample W1165889 Tower draining Checked residuals mg/l @0905 Free analyzer 1.53 grab 1.42 Total analyzer 1.45 grab 1.65 Adjusted both analyzers based on average of multiple grabs Reagents ok | Nobleton North Elevated Tank | 2026-03-11
WEST | March | Onsite to complete work orders Tower draining Completed maintenance on depolox analyzer Reagents ok Grit ok Added electrolyte to both free and total analyzers Grabs before @1229 Free analyzer 1.50 grab 1.52 Total analyzer 1.78 grab 1.74 Grabs after @1247 Free analyzer 1.49 grab 1.47 Total analyzer 1.72 grab 1.71 Completed monthly portable run , no issues Exercised manual valves Completed jhsc | Nobleton South Elevated Tank | 2026-03-05
WEST | March | Onsite for station check and to collect weekly micro sample W11705252 Checked residuals mg/l @1020 Free analyzer 1.33 grab 1.54 Total analyzer 1.66 grab 1.70 Adjusted free analyzer Reagents ok | Nobleton South Elevated Tank | 2026-03-31
WEST | March | Onsite for station check and to collect weekly micro sample W11656889 Checked residuals mg/l @1000 Free analyzer 1.52 grab 1.53 Total analyzer 1.69 grab 1.80 Reagents ok Adjusted total analyzer | Nobleton South Elevated Tank | 2026-03-11
WEST | March | On site for station check and to collect weekly micro sample W11690158 Tower draining Check residuals mg/l @0958 Free analyzer 1.40 grab 1.44 Total analyzer 1.65 grab 1.70 | Nobleton South Elevated Tank | 2026-03-25
WEST | March | On site for station check and to collect weekly micro sample W11672653 Tower draining Check residuals mg/l @1015 Free analyzer 1.74 grab 1.59 Total analyzer 1.75 grab 1.71 Adjusted free analyzer Reagents ok | Nobleton South Elevated Tank | 2026-03-18
WEST | March | Onsite for station check and to collect weekly micro sample W11637120 Tower draining Checked residuals mg/l @1004 Free analyzer 1.24 grab 1.53 Total analyzer 1.82 grab 1.78 Adjusted free analyzer Reagents ok | Nobleton South Elevated Tank | 2026-03-04
WEST | March | Silicate top up (-0.33 to 41.91cm) | Nobleton Well 2 | 2026-03-30
WEST | March | Onsite for station check and to collect weekly micro sample W11705252 Well running Checked residuals mg/l Influent @1103 Free analyzer 1,98 grab 1.96 Total grab 2.74 Effluent @1108 Free analyzer 1.65 grab 1.66 Total grab 1.91 Reagents ok Nasi P1 39% Chlorinator 2 , 23ppd, 86% DF | Nobleton Well 2 | 2026-03-31
WEST | March | Onsite to assist GFL contractor with cleaning silicate tank Placed well and silicate pumps in local to prevent start up Disinfected with hypo solution before putting back to service Placed everything back to remote Started well in manual and had NTU spike due to chemical board valving issues , adjusted and turbidity dropped. | Nobleton Well 2 | 2026-03-30
WEST | March | Silicate top up: ( 40.6 to 82.05cm) | Nobleton Well 2 | 2026-03-31
WEST | March | Onsite for station check and to collect weekly micro sample W11656889 Well running in manual Checked residuals mg/l Influent @1318 Free analyzer 1.92 grab 1.95 Total grab 2.60 Effluent @1322 Free analyzer 1.70 grab 1.72 Total grab 2.20 Placed well back to auto | Nobleton Well 2 | 2026-03-11
WEST | March | On site to complete work orders Stopped well in manual Completed jhsc, no issues observed Cleaned cl17 analyzers Grabs Before Effluent free Analyzer 1.73 grab 1.68 Influent free Analyzer 1.81 grab 1.76 After Effluent free Analyzer 1.71 grab 1.70 Influent free Analyzer 1.72 grab 1.71 Calibrated ntu analyzer with 20 ntu vial Exercised prv Tested cl2 leak detection, no issues Changed cl2 cylinder with T Hudson Cl2 weight 35 to 103 kg Worked on silicate injection points Broke lance in infection point for p2 left in local Tested cl2 system Started well in manual | Nobleton Well 2 | 2026-03-03
WEST | March | Onsite for station check Well running in auto Historian heartbeat shut down well restarted after Checked residuals mg/l Effluent @1403 Free analyzer 1.71 grab 1.80 Total grab 2.10 Influent @1408 Free analyzer 1.86 grab 1.92 Total grab 2.30 | Nobleton Well 2 | 2026-03-09
WEST | March | Onsite for station check Well running in manual Checked residuals mg/l Influent @1353 Free analyzer 1.96 grab 1.90 Total grab 2.44 Effluent @1348 Free analyzer 1.64 grab 1.65 Total grab 2.08 Put silicate p2 back in duty and primed Historian heartbeat alarm stopped well | Nobleton Well 2 | 2026-03-06
WEST | March | Repair injection line Re and re silicates line injection shut off valve | Nobleton Well 2 | 2026-03-06
WEST | March | Onsite for station check Remotely started well Checked residuals mg/l Influent @1217 Free analyzer 1.88 grab 1.87 Total grab 2.90 Effluent @1210 Free analyzer 1.63 grab 1.66 Total grab 1.86 | Nobleton Well 2 | 2026-03-02
WEST | March | Onsite for station check Well running in manual Checked residuals mg/l Influent @1303 Free analyzer 1.88 grab 2.00 Total grab 2.36 Effluent @1309 Free analyzer 1.66 grab 1.79 Total grab 2.07 Primed silicate p2 Changed reagents on both cl17 analyzers | Nobleton Well 2 | 2026-03-13
WEST | March | On site to meet GFL contractor for quote to clean out silicate tank. Temporary day tank does not fit in site facility doors. Will have silicate tank topped up prior to clean so facility can be used in auto. | Nobleton Well 2 | 2026-03-23
WEST | March | Onsite to monitor silicate system Added flushing connector to bottom of chemical board To get rid of air in suction side of p1 Replaced o rings in ball valve Disconnected and reinstalled fitting to go from pvc to pump suction ball valve De pressurized main Cleaned injection point of silicate p2 Due to high discharge pressure Repressurized main Completed drawdown of p1 117 ml/min Started well P1 suction appeared to stay charged Swapped duties to check p2 pressure, appeared normal but started to increase as runtime increased Rotated duties back to p1 Deactivated all stop rotate Flushed ntu analyzer Ran silicate p1 in manual speed setpoint | Nobleton Well 2 | 2026-03-24
WEST | March | Onsite for station check and to collect weekly micro sample Well running Checked residuals mg/l Influent @1230 Free analyzer 1.87 grab 1.83 Effluent @1221 Free analyzer 1.80 grab 1.79 Total grab 2.19 Flushed ntu analyzer | Nobleton Well 2 | 2026-03-18
WEST | March | Onsite to investigate silicate issues Changed ball valves on silicate chemical board Re plumbed connections for pump tube element Changed tube element in p2 Drawdown to system 117 ml/ min Left well in man off available in emergency Silicate tank lit not showing correct level Due to build up | Nobleton Well 2 | 2026-03-19
WEST | March | Onsite to check on silicate LIT and chlorinator #1 Informed ROC ROC placed well manual off Viewed silicate trends. Found LIT signal to be a little noisy. Removed LIT transducer and flange to inspect. Transducer is clean but a lot of solids build up below it. Opened tank lid and found a massive amount of solids build up. Tank needs to be cleaned out. Uneven solids surface interfering with ultrasonic signal. Found chlorinator #1 showing 1% open when closed. Adjusted zero position very slightly and exercised actuator. Zero is good now. Ops onsite for silicate work Informed ROC. Ops and ROC to coordinate well back to AUTO Left site | Nobleton Well 2 | 2026-03-19
WEST | March | Onsite to complete station check and collect weekly micro sample Well running Checked residuals mg/l Influent @1320 Free analyzer 1.86 grab 1.89 Total grab 2.80 Effluent @1317 Free analyzer 1.79 grab 1.78 Total grab 2.06 Stopped well in manual To continue troubleshooting silicate pump two issues Depressurized the main and put in new injection point Started well and manual | Nobleton Well 2 | 2026-03-25
WEST | March | Onsite for station check Well in manual off Checked residuals mg/l Effluent @1305 Free analyzer 1.47 grab 1.52 Total grab 1.70 Influent @1308 Free analyzer 1.60 grab 1.66 Total grab 1.81 Earlier in day changed cl2 cylinder with J.Williams Replumbed the fittings on the tube element on p1 | Nobleton Well 2 | 2026-03-20
WEST | March | In to work on silicate system. Removed silicate tank mixer from tank lid. Requested quote from contractor, will have tank cleaned out (solids buildup in tank, overdue for clean. Interfering with LIT). Replaced all asahi ball valves on silicate board. Replaced tubing element and compression fittings on Si P2. Changed to PE tubing, Parker fittings, asahi ball valves for fpt unions to tube element. Changed cal column vent line to 1:2 PE tubing and ran back to silicate tank. Will change Si P1 lines on another date. Performed drawdowns on Si P2 to system. W2 manual off, available as backup well (until tank is cleaned or temporary day tank is set up). | Nobleton Well 2 | 2026-03-19
WEST | March | Onsite for station check Started well in manual Checked residuals mg/l Effluent @1014 Free analyzer 1.71 grab 1.75 Total grab 1.97 Influent @1022 Free analyzer 1.87 grab 1.87 Total grab 2.20 Nasi P2 38% Chlorinator 1 22.5 ppd, 84%df | Nobleton Well 2 | 2026-03-27
WEST | March | Onsite for station check Checked residuals mg/l Influent @1217 Free analyzer 1.62 grab 1.61 Total grab 1.73 Effluent @1220 Free analyzer 1.91 grab 1.92 Total grab 2.13 Topped up silicate tank to 77cm Primed sillicate pumps Draw down to system p1 105ml/min Started well in manual with silicate p1 in duty, ntu climbed Rotated duty and ntu came down | Nobleton Well 2 | 2026-03-23
WEST | March | Onsite for station check and to collect weekly micro sample W11637120 Well duty active Checked residuals mg/l Influent @1403 Free analyzer 1.95 grab 1.94 Total grab 2.42 Effluent @1355 Free analyzer 1.74 grab 1.71 Total grab 2.18 | Nobleton Well 2 | 2026-03-04
WEST | March | Silicate top up (42.11 to 75.98cm) | Nobleton Wells 3 & 7 | 2026-03-30
WEST | March | Onsite to respond to well locking out due to low influent cl2 and to complete station check and collect weekly micro sample W11705252 Checked residuals Influent @1145 Free analyzer 0.62 grab 0.85 Started back flush @1146 Influent @1152 Free analyzer 1.50 grab 1.45 Stopped backflush @1153 Restarted well Influent @1226 Free analyzer 2.17 grab 2.13 Effluent @1232 Free analyzer 1.78 grab 1.75 Total grab 1.92 | Nobleton Wells 3 & 7 | 2026-03-31
WEST | March | Tried to prime hypo p2 Interlocked the well Ack reset and restarted well | Nobleton Wells 3 & 7 | 2026-03-09
WEST | March | @1300 activated duty remotely Well interlocked due to influent lolo alarm @1313 ack reset alarm, when value came back up and well restarted | Nobleton Wells 3 & 7 | 2026-03-05
WEST | March | Onsite for station check well running Checked residuals mg/ Influent @0914 Free analyzer 2.19 grab 2.18 Total grab 2.88 Effluent @0918 Free analyzer 1.75 grab 1.73 Total grab 1.99 Reagents ok Stopped well Noticed leak on silicate p2 Cleaned and tried to solace pump head New pump head did not appear to work Cleaned old one and put back on Primed pump Primed both hypo pumps Topped up hypo tanks | Nobleton Wells 3 & 7 | 2026-03-06
WEST | March | Onsite to complete work orders Generator run Start 372.3 hrs Fuel 80.3 cm 842 L Stop 373.4 hrs Fuel Completed jhsc Exercised prv Cleaned injection points Sillicate to sight glass P1 120 ml/min P2 125 ml/min Hypo P1 355 ml/min P2 350 ml/min P2 making noise when off left in manual off Cleaned pump suction check valves | Nobleton Wells 3 & 7 | 2026-03-12
WEST | March | Onsite for station check and to collect weekly micro sample w11637120 Well running Checked residuals mg/l Influent @1253 Free analyzer 2.16 grab 2.15 Total grab 2.70 Effluent @1257 Free analyzer 1.57 grab 1.54 Total grab 1.80 Topped up hypo tanks Primed hypo p2 and put into duty Lolo influent caused well to lock out Ack reset and restarted well | Nobleton Wells 3 & 7 | 2026-03-04
WEST | March | Onsite for station check and to collect weekly micro sample W11656889 Well running Checked residuals mg/l Influent @1244 Free analyzer 2.34 grab 2.32 Total grab 3.80 Effluent @1247 Free analyzer 1.74 grab 1.73 Total grab 2.02 Rotated hypo pump duty | Nobleton Wells 3 & 7 | 2026-03-11
WEST | March | Onsite for station check Well duty active Checked residuals mg/l Effluent @1106 Free analyzer 1.79 grab 1.62 Total grab 1.88 Influent @1114 Free analyzer 2.15 grab 2.20 Total grab 3.40 Silicate p2 63% Hypo p1 26% | Nobleton Wells 3 & 7 | 2026-03-09
WEST | March | Onsite for station check Duty active Checked residuals mg/l Influent @0945 Free analyzer 2.22 grab 2.19 Total grab 3.44 Effluent @0943 Free analyzer 1.76 grab 1.66 Total grab 1.95 | Nobleton Wells 3 & 7 | 2026-03-16
WEST | March | Onsite for station check Well running in manual Checked residuals mg/l Effluent @0944 Free analyzer 1.58 grab 1.57 Total grab 1.73 Influent @0956 Free analyzer 2.05 grab 2.02 Total grab 3.40 Sillicate p1 85% , 81.32 ml/min Hypo p1 25%, 61.55 ml/min , 56.5%df Deactivated well Noticed leak on fittings of inlet to effluent cl17 Closed valve resulting in no flow to analyzer an low residual readings Changed tubing and fittings Opened valve to regain flow Primed hypo 2 and place back to auto Primed both silicate pumps @1040 Influent grab Free analyzer 1.36 grab 1.51 Adjusted analyzer Some how analyzer went to 3.25 and then read 0.00 mg.l Tried brief prime cycle | Nobleton Wells 3 & 7 | 2026-03-20
WEST | March | Onsite for station check and to collect weekly micro sample W11672653 Well running Checked residuals mg/l Influent @1353 Free analyzer 2.28 grab 2.24 Effluent @1350 Free analyzer 1.80 grab 1.76 Total 2.06 | Nobleton Wells 3 & 7 | 2026-03-18
WEST | March | Checked/troubleshoot hypo pump #2 and power receptacle, did not find any problems. | Nobleton Wells 3 & 7 | 2026-03-19
WEST | March | Onsite to complete work orders Cleaned ntu analzyer and calibrated with 20 ntu vial Cleaned cl17 analyzers Grabs after Effluent Free analyzer 1.57 grab 1.58 Influent Free analyzer 1.46 grab 1.49 Started well hypo p1 fail to start alarm interlocked well Restarted well | Nobleton Wells 3 & 7 | 2026-03-17
WEST | March | Onsite for station check Well running in. Schedule mode, placed in manual to keep it on Effluent @1343 Free analyzer 1.61 grab 1.63 Total grab 1.87 Influent @1345 Free analyzer 2.10 grab 2.05 Total 2.90 Tried troubleshooting hypo p1 Caused well to interlocking by having both hypo pumps in manual Low influent interlock came in Checked residuals mg/l Influent @1421 Free analyzer 0.37 grab 0.39 Started to backlash Influent @1433 Free analyzer 1.53 grab 1.54 Stopped back flush approximately 10m3 Restarted well | Nobleton Wells 3 & 7 | 2026-03-02
WEST | March | Onsite for station check Checked residuals Influent @1255 Free analyzer 1.55 grab 1.32 Total grab 1.57 Adjusted free analyzer Effluent @1303 Free analyzer 1.48 grab 1.42 Total 1.68 Changed reagents in cl17 analyzers | Nobleton Wells 3 & 7 | 2026-03-27
WEST | March | Macnamarra fuel inspection | Nobleton Wells 3 & 7 | 2026-03-10
WEST | March | Onsite for station check Well running in manual Checked residuals mg/l Influent @1359 Free analyzer 2.12 grab 2.05 Total grab 3.40 Effluent @1354 Free analyzer 1.74 grab 1.73 Total grab 1.93 | Nobleton Wells 3 & 7 | 2026-03-13
WEST | March | On site for station check and to collect weekly micro sample W11690158 Well running Checked residuals mg/l Influent @1136 Free analyzer 2.22 grab 2.16 Effluent @1115 Free analyzer 1.57 grab 1.44 Total grab 1.72 Adjusted effluent analyzer Hypo p1 25%, 60.58ml/min, 55.25%df Nasi p1 68%, 81.68ml/min | Nobleton Wells 3 & 7 | 2026-03-25
WEST | March | Onsite for station check Well duty active Checked residuals mg/l Effluent @1005 Free analyzer 1.46 grab 1.40 Total grab 1.65 Influent @1008 Free analyzer 2.13 grab 2.06 Primed hypo p2 Hypo p1 24%, 59.52 ml/min, 54,75%df Nasi p1 67% , 80.94 ml/min | Nobleton Wells 3 & 7 | 2026-03-23
WEST | March | Silicate top up (45.53 to 76.73cm) | Nobleton Wells 5 & 6 | 2026-03-31
WEST | March | -on site to complete chlorinator rebuilds -rebuilt and calibrated both chlorinators -backflushed during calibrations -started well and tested both chlorinators in auto -no issues | Nobleton Wells 5 & 6 | 2026-03-30
WEST | March | Onsite for station check Well running in manual Checked residuals mg/l Influent @1227 Free analyzer 2.74 grab 2.70 Total grab 3.72 Effluent @1230 Free analyzer 2.01 grab 1.92 Total grab 2.38 Primed silicate p1 Reduced p2 max flow from 90 to 85 ml/min | Nobleton Wells 5 & 6 | 2026-03-06
WEST | March | Onsite to complete station check and collect weekly micro sample Well running Checked residuals mg/L Influent @1344 Free analyzer 2.90 grab 2.84 Effluent @1348 Free analyzer 1.84 grab 1.88 Total grab 2.48 Nasi P1 30%,47,1 ml/min Chlrntr 2 59%,154%DF | Nobleton Wells 5 & 6 | 2026-03-31
WEST | March | Flushed ntu analyzer Ran silatze pumps to sight glass P1 160 ml/min/ P2 200 ml/,min Started well Uncommanded stop, shut well down T.Hudson onsite | Nobleton Wells 5 & 6 | 2026-03-11
WEST | March | -man/start well to test silicate system -primed silicate pumps | Nobleton Wells 5 & 6 | 2026-03-12
WEST | March | -remotely monitor station NTU -pump 1 was able to bring down station NTU to 0.08 NTU - at max flow 50ml/min (96%) dosage still low on with pump 1 running -pump 2 speed set to 75 (73%) - will monitor | Nobleton Wells 5 & 6 | 2026-03-12
WEST | March | Onsite to complete station check and to collect weekly micro sample Well running Checked residuals mg/l Influent @1132 Free analyzer 2.77 grab 2.88 Total grab 3.84 Effluent @1135 Free analyzer 2.02 grab 1.94 Total grab 2.30 Flushed ntu analyzer sample line causing spike Primed silicate pumps 1&2, noticed air in lines Uncommanded stop came in shutting down well Ack reset and it came in again Ack reset and started well Adjusted well flow from 25 to 28 L/s Changed reagents in both cl17 analyzers Cl2 appeared to be dosing ineffective reduced flow back to 25l/s | Nobleton Wells 5 & 6 | 2026-03-04
WEST | March | -on site to replace chlorine ejector #1 -replaced ejector and vacuum tested chlorine system - ok -started well in manual and tested chlorinator #1 in auto, adjusted dosage factor down due to high influent residual -will monitor -primed silicate pump 2 | Nobleton Wells 5 & 6 | 2026-03-06
WEST | March | Onsite for station check Well duty active Checked residuals mg/l Influent @1228 Free analyzer 2.79 grab 2.88 Total grab 2.72 Effluent @1230 Free analyzer 2.02 grab 2.01 Total grab 2.58 Stopped well to clean ntu analyzer Primed both dislocated pumps and restarted well | Nobleton Wells 5 & 6 | 2026-03-09
WEST | March | Attending site to check issues with silicate pump speed feedback not matching speed setpoint (W11726510). Reset parameters so that pump displays are in set to show RPM, and performed drawdown testing on both pumps with Jacob and Tim. Operations will monitor and advise is any other issues arise. ROC was notified before and after maintenance activities. | Nobleton Wells 5 & 6 | 2026-03-11
WEST | March | Onsite to investigate Lo influent Checked residual mg/l @0935 Free analyzer 0.98 grab 0.92 @0936 started backflush @1000 Influent free analyzer 1.10 grab 1.11 @1002 stopped backflush Approximately 19m3 Restarted well in manual at 23l/s Influent hihi alarm came in Reduced dosage factor until residual stabilized Checked residuals mg/l Influent free @1111 Analyzer 2.79 grab 2.88 Effluent free @1115 Analyzer 2.26 grab 2.15 | Nobleton Wells 5 & 6 | 2026-03-05
WEST | March | Onsite for station check Well running in manual @1117 Influent analyzer 2.83 grab 3.12 Total grab 3.76 @1124 Effluent free analyzer 2.26 grab 2.42 Total grab 2.94 Adjusted both cl17 analyzers | Nobleton Wells 5 & 6 | 2026-03-02
WEST | March | Onsite for station check Well running in manual Checked residuals mg/l Effluent @1142 Free analyzer 1.62 grab 1.72 Total 2.13 Influent @1147 Free analyzer 2.71 grab 2.62 Total grab 4.13 Sillicate p2 29% , 47.4 ml/min Chlorinator 1 54%, 140% df, 30 ppd Earlier in day changed cl2 cylinder with J.Williams | Nobleton Wells 5 & 6 | 2026-03-20
WEST | March | Onsite for station check Well running in manual Checked residuals mg/l Influent @1015 Free analyzer 2.87 grab 2.90 Total grab 3.46 Effluent @1018 Free analyzer 1.69 grab 1.77 Total grab 2.03 | Nobleton Wells 5 & 6 | 2026-03-16
WEST | March | Onsite to complete station check and to collect weekly micro sample W11672653 Well duty active Checked residuals Influent @1124 Free analyzer 2.86 grab 3.28 Effluent @1130 Free analyzer 2.33 grab 2.34 Total grab 2.64 Adjusted influent analyzer | Nobleton Wells 5 & 6 | 2026-03-18
WEST | March | Onsite for station check Well running in manual Checked residuals mg/l Influent @1220 Free analyzer 2.80 grab 2.94 Effluent @1228 Free analyzer 1.86 grab 1.85 Total grab 2.14 | Nobleton Wells 5 & 6 | 2026-03-27
WEST | March | Onsite for station check Well running Checked residuals mg/l Effluent @1055 Free analyzer 2.09 grab 2.17 Total grab 2.64 Influent @1058 Free analyzer 2.77 grab 2.88 Total grab 3.72 Chlorinator 1 59%, 154%df , 32 ppd Nasi p2 30%, 48 ml/mib | Nobleton Wells 5 & 6 | 2026-03-23
WEST | March | Onsite for station check and to collect weekly micro sample W11690158 Well running Checked residuals mg/l Influent @1247 Free analyzer 2.74 grab 3.10 Total grab 3.80 Adjusted free analyzer Effluent @1249 Free analyzer 2.09 grab 2.06 Total grab 2.42 Chlorinator 1 32ppd, 58% Nasi p2 30%, 47.3 ml/min | Nobleton Wells 5 & 6 | 2026-03-25
WEST | March | On site to investigate silicate issues Ran draw down on pump one When checking silicate injection point lines for air in advertently bumped into chlorine injection point line and broke the lance Shut down well Isolated the pipe Took out broken injection point and isolated corps stop Placed chlorinator one in booster pump, one in manual and out of service | Nobleton Wells 5 & 6 | 2026-03-12
WEST | March | -on site to troubleshoot silicate pumps -notice issue with pump speed on chemical pumps - informed Erik S - will attend -man/started well 5 with both silicate pull at 100% -verified analyzer -influent 13:05: 2.80mg/l grab: 2.58mg/l - adjusted -effluent 13:10: 1.91mg/l grab -treated total grab: -reagents all ok | Nobleton Wells 5 & 6 | 2026-03-11
WEST | March | Macnamarra fuel inspection | Nobleton Wells 5 & 6 | 2026-03-10
WEST | March | On site to complete work orders Completed jhsc Back on site to investigate diesel spill sump Emergency shower was left dripping, resulting in filling the sump pit Pumped pit out until the alarm cleared Well started an auto Noticed chlorinator 2 did not appear to be dosing tried to open chlorinator further , interlocked the well due to chlorinator being in local Restarted well with chlorinator 1 duty But well shut down due to low influent residual Took influent grab Analyzer 0.06 grab 2.20 Next reading residual recovered and alarm was reset Restart restarted well with chlorinator 2 Appeared to be dosing fine | Nobleton Wells 5 & 6 | 2026-03-17
WEST | March | In to troubleshoot silicate system. Replace tube element and roller on Si P1 (roller changed from ?super? to regular roller with 2 active/ 2 passive rollers. -poor performance at lower speeds. Replaced suction / discharge tubing and fittings to PE tubing and Parker fittings 1/2 from 3/8 and tested. Replaced calibration column blow off line with 1/2 connection and ran to drain conduit. Tested Si P2 to system pressure: -drawdowns and 25 and 40% speeds = 168ml/min -changed Si P1 max pump capacity SP to 160ml/min and rotated into duty. Install replacement injector lance and 3/4 corp stop for chlorinator 1 discharge line and tested. Replaced turbidimeter sample line back to 1/4 and ran to sample sink. Run W5 in auto with chlorinator 1 and silicate P1 to test dosing and performance after maintenance. | Nobleton Wells 5 & 6 | 2026-03-16
WEST | March | -on site to troubleshoot silicate system -replaced silicate pump 2 element -returned silicate pump 2 to pvc suction line -started well and performed drawdowns into system, pump 2 max flow = 175 ml/min -set pump 2 scada max flow setpoint to 160 ml/min, will monitor dosage calculation | Nobleton Wells 5 & 6 | 2026-03-16
CENTRAL | March | Onsite for station check and weekly Bacti sample Recordings in PWQ sheet Residuals (mg/L) Inlet Grab @ 15:00 Free: 0.03 Total: 2.96 Inlet Analyzer @ 15:00 Free: 0.03 Total: 2.84 Outlet Grabs @ 14:55 Free: 0.03 Total: 2.4 Mono: 1.98 FA: 0.09 TA: 0.48 NO2: 0.005 Temp: 10.8 Outlet Analyzer @ 14:55 Analyzer Free: 0.10 Analyzer Total: 2.17 adjusted to 2.40 Station ok | Queensville Elevated Tank | 2026-03-31
WEST | March | Onsite to complete work orders Diesel Start 85.1/82.9 cm 880/ 856 L 261:10 hrs Stop 84.0 / 81.9 cm 868/ 845 L 262:29 hrs Tested cl2 leak detection Completed subsection of silicate system Cleaned injection points Ran hot water through lines Adjusted fittings Primed both pumps Exercised manual valves Exercised prv Cleaned cl17 analyzers Grabs before Influent Free analyzer 2.04 grab 1.93 Effluent Free analyzer 2.00 grab 2.05 Calibrated ntu analyzer with 20 ntu vial and flushed sample lines out Grabs after Influent Free analyzer 2.00 grab 1.99 Effluent Free analyzer 2.01 grab 1.96 Completed cl2 system inspection No issues observed Started well in manual | Nobleton Wells 5 & 6 | 2026-03-10
CENTRAL | March | On-site for a station and equipment check No issues found Weekly bacti and operational samples taken Verified analyzers, readings and grabs entered into PWQ sheet Inlet Free@1440 G:0.05 A:0.01mg/L Inlet Total@1444 G:2.70 A:2.67mg/L Outlet Free@1445 G:0.06 A0.08mg/L Outlet Total@1448 G:2.46 A:2.41mg/L | Queensville Elevated Tank | 2026-03-04
CENTRAL | March | On-site for a station and equipment check No issues found Weekly bacti and operational samples taken Verified analyzers and entered all readings and grabs into PWQ sheet Verified analyzers and entered all readings and grabs into PWQ sheet Inlet Free@1103 G:0.07 A:0.10mg/L Inlet Total@1105 G:2.78 A:2.85mg/L Outlet Free@1107 G:0.07 A:0.11mg/L Outlet Total@1110 G:2.20 A:2.23mg/L | Queensville Elevated Tank | 2026-03-25
CENTRAL | March | On-site due to an inlet free hi hi alarm. Inlet analyzer reading 0,33mg/L on arrival. Average of three grabs, 0.09, 0.11, 0.15mg/L. Adjusted inlet free to 0.11mg/L Will continue to monitor remotely | Queensville Elevated Tank | 2026-03-09
CENTRAL | March | On-site for various work orders: Dechlor puck dispenser inspected, cleaned and filled JHSC inspection completed Manual valve exercised Generator test completed Inlet/Outlet heat trace system inspection general housekeeping Analyzer maintenance and verification | Queensville Elevated Tank | 2026-03-05
CENTRAL | March | On-site for a station and equipment check No issues found Weekly bacti sample taken Verified analyzers and entered all readings and grabs into PWQ sheet Inlet Free@1110 G:0.06 A:0.10mg/L Inlet Total@1112 G:2.18 A:2.13mg/L Outlet Free@1118 G:0.10 A: 0.09mg/L Outlet Total@1120 G:2.10 A:2.14mg/L | Queensville Elevated Tank | 2026-03-11
CENTRAL | March | On-site for a station and equipment check No issues found Changed inlet reagents (both) Adjusted inlet total to 2.78mg/L based on avg of three grabs, from 2.62mg/L Verified analyzers and entered all readings and grabs into PWQ sheet Inlet Free@1036 G:0.05 A:0.07mg/L Inlet Total@038 G:2.78 A:2.78mg/L Outlet Free@1052 G:0.07 A:0.08mg/L Outlet Total@1045 G:2.28 A:2.23mg/L | Queensville Elevated Tank | 2026-03-18
CENTRAL | March | On-site for station check, weekly BACTI and iron monitoring samples Recordings in PD sheet Influent @ 09:29 Free Grab: 3.04 mg/L Analyzer Free: 2.92 mg/L adjusted to grab Effluent @ 09:32 Free Grab: 2.80mg/L Analyzer Free 2.58 mg/L adjusted to grab Treated @ 09:45 Free Grab: 0.12 mg/L Total Grab: 3.44 mg/L Analyzer Free: 0.21 mg/L Analyzer Total: 3.55 mg/L adjusted to grab SL1000 grabs FA; 0.05 TA; 0.62 Mono; 2.88 Nitrite; Temp; 9.7 Adjusted chlorine to ammonia ratio from 4.0 to 4.1 because of higher effluent free chlorine analyzer readings after adjustment. Station ok | Queensville Wells No. 1 and 2 | 2026-03-31
CENTRAL | March | 16:04. Onsite to respond to wells interlocked due to low influent. Well 1 started 3 times starting at 14:41 but shortly intlerocked on low influent residual. The contact tank has not been cleared (at 79 m3). Treated water total chlorine reading 2.74 mg/l. 16:22 verified analyzers: Influent free grab: 0.03. Analyzer: 0.03. Treated total grab: 2.74. Analyzer: 2.73. Treated free grab: 0.19. Analyzer: 0.14. 16:27 placed dechlorination pucks at outfall and initiated a backflush of contact chamber. 16:30 Tested chlorine dosing system. Found booster pump 2 fully air locked, likely occured ealier during isolation and repair work on the waste valve. Purged booster pumps of air. No issues remaining with chlorine system. 17:42 Influent free grab: 0.53. Analyzer: 0.50 mg/l. Completed backflush and reset CT timer on SCADA. 17:45 placed wells back in auto. 17:50 Found chlorine system again not functioning and shut off well. Booster pump 1 air locked again. Backflushed well briefly to remove any water in contact chamber that was not dosed. Bleeded off air from both booster pumps again and started well again at 18:11. 18:55 Verfied treated free grab: 0.10. Analyzer: 0.10. Total grab: 1.30 . Analzyer: 1.24. No issues remain. Notifed ROC work complete and to place well 1 back to auto | Queensville Wells No. 1 and 2 | 2026-03-06
CENTRAL | March | Onsite for chlorinator rebuilds and calibration. Informed ROC. ROC placed wells manual off Informed OIC Purged chlorine system and isolated. Rebuilt chlorinators and performed vacuum test. All good, no leaks. Put chlorine gas back in service and performed 11pt calibration. Verified calibration using scada. All ok Maximum gas flow is 70 (#1) and 75% (#2) Informed operations. Operations will come to site and back flush the system Informed ROC. Left site | Queensville Wells No. 1 and 2 | 2026-03-03
CENTRAL | March | Macnamarra fuel inspection | Queensville Wells No. 1 and 2 | 2026-03-10
CENTRAL | March | On-site for a station and equipment check CL2 2 booster pump locked out. Unable to reset and return to service Work order created. Chemical levels and systems ok 15 cylinders and 2 bags of ammonia in inventory Operational sample taken Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@1111 G:2.78 A:2.68mg/L Effluent Free@1117 G:0.13 A:0.10mg/L Treated Free@1121 G:0.10 A:0.09mg/L Treated Total@1122 G:2.76 A:2.71mg/L | Queensville Wells No. 1 and 2 | 2026-03-09
CENTRAL | March | On-site for a station and equipment check No issues found Topped mineral oil well 1 Chemical levels and systems ok 15 cylinders and 2 bags of ammonia in inventory Operational sample taken Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@1030 G:3.12 A:3.03mg/L Effluent Free@1032 G;0.25 A:0.20mg/L Treated Free@1034 G:3.32 A:3.25mg/L Treated Total@1040 G:3.32 A:3,25mg/L | Queensville Wells No. 1 and 2 | 2026-03-02
CENTRAL | March | Rebuild queensville well 1 wasting valve installed rubber repair kit | Queensville Wells No. 1 and 2 | 2026-03-06
CENTRAL | March | On-site for a station and equipment check No issues found Topped up ammonia day tank 2 Topped up both NaSi day tanks. Took weekly bacti samples Chemical levels and systems ok 15 cylinders and 4 bags of ammonia in inventory Verified analyzers, entered all readings and grabs into PWQ sheet Influent Free@1104 G:3.02 A:2.99mg/L Effluent Free@1106 G:2.68 A:2.73mg/L Treated Free@1107 G:0.16 A:0.21mg/L Treated Total@1111 G:3.38 A:3.38 Mono-2.81 FA-0.06 TA-0.56 | Queensville Wells No. 1 and 2 | 2026-03-04
CENTRAL | March | On-site to perform a number of PM's -CL2 gas detector test completed -Cylinder change with JZ, bank B -Deep well exhaust inspection and maintenance, both wells completed -JHSC inspection completed -Dechlor puck dispenser inspected -General Housekeeping -Cleaned and inspected flow control valve well 2 | Queensville Wells No. 1 and 2 | 2026-03-10
CENTRAL | March | On-site for a station and equipment check No issues found Chemical levels and systems ok 9 cylinders and 8 bags of ammonia in inventory Took weekly bacti samples Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@1253 G:3.06 A: 2.91mg/L Effluent Free@1300 G:2.46 A:2.51mg/L Treated Free@1303 G:0.20 A:0.21mg/L Treated Total@1307 G:3.48 A:3.40mg¦L Mono-2.72 FA-0.02 TA-0.56mg/L | Queensville Wells No. 1 and 2 | 2026-03-11
CENTRAL | March | Onsite with Cole W to respond to CL2 leak alarm- station interlocked, informed by ROC Upon arrival, found leak coming from one of the empty chlorine cylinders- cylinder not fully closed. Fully closed cylinder- no leak outstanding. Re-opened all chlorine cylinders and ack/reset all alarms via scada- informed ROC. Station placed back into auto. Station/equipment- Ok | Queensville Wells No. 1 and 2 | 2026-03-27
CENTRAL | March | Station and equipment check Took grabs @ 10:00 am (duty not active) Treated Total: 2.60 mg/l Treated Free: 0.05 mg/l Chemicals/reagents ok Receive and return 12 chlorine cylinders Ops normal | Queensville Wells No. 1 and 2 | 2026-03-20
CENTRAL | March | On site with Total Power for annual load test | Queensville Wells No. 1 and 2 | 2026-03-12
CENTRAL | March | On-site for a station and equipment check NaSi pump 2 OOS Chemical levels and systems ok 15 cylinders and 2 bags of ammonia in inventory Weekly bacti and operational samples taken Adjusted ammonia pump 1 max to 205mL/min from 218mL/min. First FA grab was 0.01, after adjusting FA grab 0.03mg/L Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@0906 G:2.64 A:2.59mg/L Effluent Free@0909 G:2.44 A:2.54mg/L Treated Free@0905 G:0.20 A:0.23mg/L Treated Total@0914 G:3.48 A:3.54mg/L | Queensville Wells No. 1 and 2 | 2026-03-25
CENTRAL | March | On-site for a station and equipment check No issues found NaSi pump 2 back in service. New check valve installed at injector Cylinder change with JZ bank 1 Topped up ammonia day tank 2 Topped up NaSi day tanks Changed Influent reagents Verified analyzers and entered all readings and grabs into PWQ sheet Influent free@0850 G:2.96 A:2.9mg/L Effluent free@0855 G:0.19 A:0.17mg/L Treated free@0858 G:0.18 A:0.13mg/L Treated Total@0900 G:2.86 A;2.94mg/L | Queensville Wells No. 1 and 2 | 2026-03-27
CENTRAL | March | On-site for a station and equipment check. No issues found. Chemical levels and systems ok NaSi pump 2 still OOS 15 cylinders and 2 bags of ammonia in inventory New rebuild kit left in ammonia room for pumps. Topped ammonia day tank 1 Topped up NaSi day tanks. Topped up mineral oil pot well 1 Changed cylinders with A Bell bank 2 Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@0918 G:2.74 A:2.81mg/L Effluent Free@0923 G:0.12 A:0.11mg/L Treated Free@0924 G:0.07 A:0.08mg/L Treated Total@0927 G:2.78 A:2.84mg/L | Queensville Wells No. 1 and 2 | 2026-03-23
CENTRAL | March | On site to help Kyle Rae with control wiring | Queensville Wells No. 1 and 2 | 2026-03-17
CENTRAL | March | Find treated total chlorine hi alarm triggered at 15:24 during SCADA review. Placed chlorine dosing system to automatic mode. Dosage factor should drop until target influence is reached. | Queensville Wells No. 1 and 2 | 2026-03-24
CENTRAL | March | On-site for chemical systems testing. Drawdowns completed on ammonia Hot flushed and primed both NaSi lines. NaSi 2 is OOS | Queensville Wells No. 1 and 2 | 2026-03-17
CENTRAL | March | On site to change well one manual speed potentiometer. Dan and I replaced and tested to confirmed operation. Cleared alarms and left well one in manual off. Under direction of oic | Queensville Wells No. 1 and 2 | 2026-03-03
CENTRAL | March | Onsite with Donny M to replace chlorine lines and regulators. Purged chlorine system. replaced the chlorine parts tested vacuum-ok tested for leaks-ok back flushed, added dechlor to outfall ran well 1 and tested both chlorinators. adjusted dosing factors for both chlorinators. site ok | Queensville Wells No. 1 and 2 | 2026-03-03
CENTRAL | March | 16:00 Onsite to respond to wells interlocked due to low influent on start up. Found localized flooding up to due to recent rain and snowmelt in storm ditch on east side of building. Notified ROC. Tested chlorine booster pump 2. Found it air locked. Bleed off air. Retested and booster pump will not start. Placed oos. Booster pump 1 ran ok with no air lock issues. 16:15 began back flushing contact chamber after placing declination pucks at outfall. 16:54 completed back flush. Reset contact tank calculations on SCADA with backflush completed. Verified influent free gab: 1.54. Analyzer: 1.62 mg/l. 17:00 started well 1 in manual. Waste valve is open at start up but found well not wasting. Found waste line isolation valve closed. Opened valve and shut down well 1. Briefly backflushed again. 17:28 started well 1 in manual with no further issues. Chlorine booster pump 2 remains oos. Notified roc system back in operation. | Queensville Wells No. 1 and 2 | 2026-03-07
CENTRAL | March | On site to replace pilot illumination and contacts on well pump 2 starter. With assistance from Will Mather and ROC, well placed in manual, taken out of service and de-energized. Work completed. ROC notified, well placed in remote and returned to operation. | Queensville Wells No. 1 and 2 | 2026-03-19
CENTRAL | March | On-site due to a call from ROC about a potential CL2 leak. Upon arrival sensor reading 0.0. Reset halogen system, tightened up valves. Cleared interlock on OIT panel. Will continue to monitor remotely | Queensville Wells No. 1 and 2 | 2026-03-27
CENTRAL | March | On-site for a station and equipment check No issues found Chemical levels and systems ok 9 cylinders and 6 bags of ammonia in inventory Changed effluent free analyzer reagents Topped up mineral pots Operational sample taken Adjust ammonia dosage on pump 2 to increase FA. First grab was 0.01mg/L after adjustment to 203mL/min from 207mL/min grab was 0.04mg/L Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@1221 G:2.76 A:2.88mg/L Effluent Free@1229 G:2.56 A:2.52mg/L Treated Free@1231 G:0.26 A:0.23mg/L Treated Total@1233 G:3.30 A:3.42mg/L Mono-2.74 FA-0.04 TA-0.57mg/L | Queensville Wells No. 1 and 2 | 2026-03-16
CENTRAL | March | On-site for a station and equipment check No issues found Chemical levels and systems ok 15 cylinders and 4 bags of ammonia in inventory Verified analyzers and entered all readings and grabs into PWQ sheet Adjusted effluent free based on an average of 3 grabs. 2.54 from 2.77mg/L Influent Free@1230 G:2.66 A:2.7mg/L Effluent Free@1234 G:2.54 A:2.54mg/L Treated Free@1240 G:0.18 A:0.22mg/L Treated Total@1243 G:3.44 A:3.47mg/L Mono-2.79 FA-0.04 TA-0.59mg/L | Queensville Wells No. 1 and 2 | 2026-03-06
CENTRAL | March | See photos/paper log book | Queensville Wells No. 3 and 4 | 2026-03-30
CENTRAL | March | On site to investigate chlorine booster pump #2 and work on well pump #2. Well pump #2 de-energized. ROC notified. Found chlorine booster pump 2 to have opened fuse feeding starter. Confirmed motor in good condition with megger. Replaced fuse, tested operation with operator Will Mather and returned to service. Well pump 2 control illumination and terminals replaced. With assistance from Ben Hess and ROC, well pump 2 placed in auto and returned to normal operation. | Queensville Wells No. 1 and 2 | 2026-03-17
CENTRAL | March | On-site for a station and equipment check No issues found Chemical levels and systems ok NaSi pump 2 still OOS Topped up ammonia day tank 2 9 cylinders and 4 bags of ammonia in inventory Took weekly bacti samples Analyzer maintenance completed NTU verification completed Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@0849 G:3.00 A:2.90mg/L Effluent Free@0854 G:2.68 A:2.67mg/L Treated Free@0856 G:0.19 A:0.23mg/L Treated Total@0900 G:3.42 A:3.53mg/L Mono-2.87 FA-0.04 TA-0.60mg/L | Queensville Wells No. 1 and 2 | 2026-03-18
CENTRAL | March | On-site for station check, weekly BACTI and iron monitoring samples Recordings in PD sheet Influent @ 13:40 Free Grab: 3.02 mg/L Analyzer Free: 2.97 mg/L Effluent @ 13:42 Free Grab: 2.90 mg/L Analyzer Free: 2.90 mg/L Treated @ 13:48 Free Grab: 0.07 mg/L Total Grab: 3.50 mg/L Analyzer Free: 0.16 mg/L Analyzer Total: 3.56 mg/L SL1000 grabs FA; 0.06 TA; 0.63 Mono; 2.87 Nitrite: Temp; 9.4 Station ok | Queensville Wells No. 3 and 4 | 2026-03-31
CENTRAL | March | On-site for a station and equipment check No issues found Placed well 3 back into auto and rotated duties Chemical systems and levels ok 15 cylinders and 6 bags of ammonia in inventory Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@1315 G:1.93 A:2.02mg/L Effluent Free@1319 G:0.17 A:0.22mg/L Treated Free@1320 G:0.02 A:0.04mg/L Treated Total@1324 G:2.12 A:2.21mg/L | Queensville Wells No. 3 and 4 | 2026-03-09
CENTRAL | March | Macnamarra fuel inspection | Queensville Wells No. 3 and 4 | 2026-03-10
CENTRAL | March | Attending site to continue investigating erratic readings from Total chlorine analyzer (W11685985). Replaced entire analyzer again. Well was in manual off during maintenance work. Well 3 was started in manual before leaving site, via ROC. ROC was notified before and after maintenance activities. | Queensville Wells No. 3 and 4 | 2026-03-02
CENTRAL | March | Onsite with D Moses and A Morvin (OJT) performed various work orders including all chemical systems inspections and drawdowns and testing flow control inspection exercise and cleaning Cl2 system inspection and leak test completed | Queensville Wells No. 3 and 4 | 2026-03-12
CENTRAL | March | Onsite to commission treated total AIT (CL17sc) Informed ROC Maintenance onsite Commissioned and configured new AIT. Took grabs G=2.19mg/l A=2.17mg/l Issue with LoLo switch alarm. Input on PAC changes but no change on SCADA. Will discuss with PCS Wells are LOCAL OFF Informed operations and ROC. Wells are available to run Armed building and leftsbite | Queensville Wells No. 3 and 4 | 2026-03-12
CENTRAL | March | On-site for a station and equipment check CMP work order created for well 4 motor oil Topped up oil pot well 4 Weekly bacti samples taken Chemical levels and systems ok 15 cylinders and 6 bags of ammonia in inventory Verified analyzers, entered all readings and grabs into PWQ sheet Influent Free@0831 G:2.54 A:2.65mg/L Effluent Free@0834 G:2.56 A:2.64mg/L Treated Free@0835 G:0.09 A:0.14mg/L Treated Total@0840 G:3.08 A:3.16mg/L Mono-2.53 FA-0.07 TA-0.57mg/L | Queensville Wells No. 3 and 4 | 2026-03-04
CENTRAL | March | On-site for a station and equipment check No issues found Chemical levels and systems ok 15 cylinders and 6 bags of ammonia in inventory Operational sample taken Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@0845 G:2.60 A:2.6g/L Effluent Free@0850 G:2.58 A:2.64mg/L Treated Free@0851 G:0.09 A:.13mg/L Treated Total@0907 G:3.18 A:3.19mg/L | Queensville Wells No. 3 and 4 | 2026-03-02
CENTRAL | March | QVW34- CT Not Achieved Alarm. Notified Will M. He is running to waste. Directed to disregard. | Queensville Wells No. 3 and 4 | 2026-03-11
CENTRAL | March | Changed/replaced chlorine analyzer with new model. | Queensville Wells No. 3 and 4 | 2026-03-12
CENTRAL | March | On-site for a station and equipment check Well 3 in manual on after backlash of contact tank. Started back flush with dechlor at 0800 completed at 0819 with two Influent total grabs of 2.90 mg/L and 3.16mg/L Reset QV duties Chemical levels and systems ok 15 cylinders and 6 bags of ammonia in inventory Took treated bacti sample. Changed Influent and effluent reagents Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@1110 G:2.48 A:2.58mg/L Effluent Free@1112 G:2.64 A:2.54mg/L Treated Free@1114 G:0.11 A:0.14mg/L Treated Total@1117 G3.02 A:3.07mg/L | Queensville Wells No. 3 and 4 | 2026-03-13
CENTRAL | March | -Collected weekly BacT sample YD #W11672737 Grab: Influent free=2.62mg/L effluent free=2.08mg/L treated free=0.18mg/L total=2.52mg/L@16:10 Analyzer: Influent free=2.63mg/L effluent free=2.15mg/L treated free=0.13mg/L total=2.57mg/L | Queensville Wells No. 3 and 4 | 2026-03-18
CENTRAL | March | On-site for a station and equipment check No issues found Chemical levels and systems ok. 15 cylinders and 6 bags of ammonia in inventory Topped up mineral oil pot well 4 Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@1116 G:2.76 A: 2.70mg/L Effluent Free@1118 G:2.62 A:2.74mg/L Treated Free@1119 G:0.10 A:0.14mg/L Treated Total@1122 G:3.18 A:3.18mg/L Mono-2.61 FA-0.08 TA-0.60mg/L | Queensville Wells No. 3 and 4 | 2026-03-23
CENTRAL | March | On-site for a station and equipment check No issues found. Chemical levels and systems ok 15 cylinders and 6 bags of ammonia in inventory Weekly bacti and operational samples taken Verified all analyzers and entered all readings and grabs into PWQ sheet Influent Free@1221 G:2.30 A:2.38mg/L Effluent Free@1224 G:2.72 A:2.73mg/L Treated Free@1226 G:0.14 A:0.14mg/L Treated Total@1218 G:3.12 A:3.15mg/L | Queensville Wells No. 3 and 4 | 2026-03-25
CENTRAL | March | On-site for a station and equipment check No issues found Chemical levels and systems ok. 15 cylinders and 6 bags of ammonia in inventory Topped up both mineral pots Run generator while under load of well 3 Generator hours start: 714h 34min End: 715h33m Fuel start 1759L. End 1724L 60Hz 601v coolant temp 160?f Oil Temp 169?F Oil pressure 89psi Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@1001 G:2.74 A:2.80mg/L Effluent Free@1004 G:2.58 A:2.69mg/L Treated Free@1009 G:0.10 A:0.14mg/L Treated Total@1013 G:3.08 A:3.12mg/L | Queensville Wells No. 3 and 4 | 2026-03-16
CENTRAL | March | On-site for a station and equipment check Wells locked out due to low Influent free Not dosing due to closed valve. Back flushed with dechlor. Restarted wells. Chemical systems and levels ok 15 cylinders and 6 bags of ammonia in inventory Verified analyzers JZ will take bacti samples | Queensville Wells No. 3 and 4 | 2026-03-18
CENTRAL | March | On site with Dan Boate to finish cleanup work on Well #4 vfd cabinet and complete Well 3 and 4 PM?s. | Queensville Wells No. 3 and 4 | 2026-03-25
CENTRAL | March | On-site for a station and equipment check Installed new check valve on NaSi 2 injection point verified function Chemical levels and systems ok Topped up mineral pot well 3 Verified analyzers and entered all readings and grabs into PWQ sheet Influent free@1141 G:2.78 A:2.74mg/L Effluent free@1143 G:0.13 A:0.12mg/L Treated Free@1138 G:0.03 A:0.06mg/L Treated Total@1138 G:2.46 A:2.41mg/L | Queensville Wells No. 3 and 4 | 2026-03-27
CENTRAL | March | Changed treated free reagents | Queensville Wells No. 3 and 4 | 2026-03-02
CENTRAL | March | On site with operator Will Mather to investigate Well Pump #3 fail to start. Conducted test run of well 3 in remote without incident. Pump ran for approximately 60 mins. Well 3 then placed in manual and run to waste. Pump was started and stopped 4 times to test operation. Fail to start could not be replicated. Well pump 3 returned to normal operation. | Queensville Wells No. 3 and 4 | 2026-03-19
CENTRAL | March | Attending site to check push button issues on Influent chlorine analyzer (W11744080). Replaced all push buttons and verified reading. ROC was notified before and after maintenance activities. | Queensville Wells No. 3 and 4 | 2026-03-24
CENTRAL | March | Station and equipment check Well duty not active during check Took grabs @ 8:40 am Treated Total: 2.20 mg/l Treated Free: 0.05 mg/l Chemicals/reagents ok Ops normal | Queensville Wells No. 3 and 4 | 2026-03-20
CENTRAL | March | on_site for various work orders -JHSC inspection completed -Comprehensive housekeeping -Deep well exhaust maintenance/inspection both wells -Dechlor puck dispenser inspected - | Queensville Wells No. 3 and 4 | 2026-03-24
CENTRAL | March | On-site for a station and equipment check No new issues found Verified wells isolated from system Ran wells to waste, in hand, in order to get weekly raw bacteria samples. Contact time not met alarm came in as a result It can be disregarded because of previous actions. Chemical levels and systems ok 15 cylinders and 6 bags of ammonia in inventory Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@1007 G:1.80 A:1.74mg/L Effluent Free@1010 G:0.11 A:0.09mg/L Treated Free@1011 G:0.05 A:0.04mg/L Treated Total@1014 G:2.18 A2.20mg/L | Queensville Wells No. 3 and 4 | 2026-03-11
CENTRAL | March | On-site for a station and equipment check No issues found. Chemical levels and systems ok Topped up ammonia day tank 1 15 cylinders and 4 bags of ammonia in inventory Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@1002 G:2.78 A:2.70mg/L Effluent Free@1003 G:0.16 A:0.16mg/L Treated Free@1009 G:0.07 A:0.06mg/L Treated Total@1012 G:2.60 A:2.57mg/L | Queensville Wells No. 3 and 4 | 2026-03-06
WEST | March | On site for station check Check trends All okay station duty off 12:15- Grabs taken Free CL2-0.04 mg/L Total CL2- 2.01 mg/L entered values in PWQ sheet Equipment okay | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2026-03-30
WEST | March | On site to complete station check and weekly bacti W11657067 Checked trends: all ok Took chlorine grab and sample East cell 13:10 Free CL2: 0.06mg/l Total CL2: 1.46mg/l West cell 13:14 Free CL2: 0.03mg/l Total CL2: 1.42mg/l Equipment all ok Entered reading PWQ: all ok | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2026-03-11
WEST | March | On site to complete station check, operational sample and weekly bacti W11705742 Checked trends: all ok Took chlorine grab and sample West cell 14:10 Free CL2: 0.06mg/l Total CL2: 1.56mg/l East cell 14:15 Free CL2: 0.04mg/l Total CL2: 1.60 mg/l Equipment all ok Entered reading PWQ: all ok | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2026-03-31
WEST | March | Onsite for the following pm work orders. Informed ROC about the works being done. W11640420 RHPSWA, JHSC Health and Safety Inspection W11640701 RHPSWA, Ventilation System Inspection W11640724 RHPSWA, PRV Valve Inspection W11640863 RHPSWA, Pump & Motor Inspection, W11642274 RHPSWA, Comprehensive Housekeeping W11640981 RHPSWA, Flood Alarm Test W11641081 RHPSWA, Discharge Valve & Actuator Exercise & Inspection Station check Check trends All okay station duty off 13:00- Grabs taken Free CL2-0.03 mg/L Total CL2- 1.90 mg/L W11640747 RHRSWA, High/Low Temperature Alarm Test W11639808 RHRSWA, Dehumidifier Inspection & Cleaning W11639629 RHRSWA, Actuated Valve Exercise & Inspection W11641140 RHRSWA, External Venting Screens Inspection W11639852 RHRSWA, Sump Pit System Inspection W11640737 RHRSWA, Flood Alarm Test, | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2026-03-03
WEST | March | - reset power alarms -all ok | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2026-03-03
WEST | March | On site for station check Check trends All okay station duty off 13:40- Grabs taken Free CL2-0.05 mg/L Total CL2- 1.91 mg/L entered values in PWQ sheet Equipment okay | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2026-03-06
WEST | March | -on site to complete station check and weekly bacti W11637582 -checked trends: all ok -entered reading PWQ: all ok -took chlorine grab and sample west cell 13:15 -free cl: 0.08mg/l -total cl: 1.38mg/l -east cell 13:25 -free cl: 0.08mg/l -total cl: 1.42mg/l -equipment all ok | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2026-03-04
WEST | March | wrong log entry. this log belongs to JFRS. See JFRS | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2026-03-11
WEST | March | Station Check (pumping station) (no issues found) Input data to PWQ 12:35 Chlorine residual grab: (Free 0.04mg/l, Total 1.97mg/l) | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2026-03-23
WEST | March | On site for station check Check trends All okay station duty off 14:15- Grabs taken Free CL2-0.02 mg/L Total CL2- 1.98 mg/L entered values in PWQ sheet Equipment okay | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2026-03-09
WEST | March | On site to complete station check and weekly bacti W11690336 Checked trends: all ok Took chlorine grab and sample East cell 14:00 Free CL2: 0.06mg/l Total CL2: 1.57mg/l West cell 14:05 Free CL2: 0.05mg/l Total CL2: 1.60 mg/l Equipment all ok Entered reading PWQ: all ok | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2026-03-25
WEST | March | On site for station check Check trends All okay station duty off 13:15- Grabs taken Free CL2-0.06 mg/L Total CL2- 1.78 mg/L entered values in PWQ sheet Equipment okay | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2026-03-16
WEST | March | On site for station check Check trends All okay station duty off 14:00- Grabs taken Free CL2-0.05 mg/L Total CL2- 2.023 mg/L entered values in PWQ sheet Equipment okay | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2026-03-27
WEST | March | On site to complete station check, operational sample and weekly bacti W11672961 Checked trends: all ok Took chlorine grab and sample West cell 14:10 Free CL2: 0.06mg/l Total CL2: 1.44mg/l East cell 14:05 Free CL2: 0.05mg/l Total CL2: 1.48 mg/l Equipment all ok Entered reading PWQ: all ok | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2026-03-18
WEST | March | On site for station check Check trends All okay station duty off 13:54- Grabs taken Free CL2-0.00 mg/L Total CL2- 2.03 mg/L entered values in PWQ sheet Equipment okay | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2026-03-20
CENTRAL | March | On-site for station check and sampling. W11705550 14:16 Deactivated PD9 duty. Tower level 69% and draining at 12 l/s. 14:30 Verified inlet analyzer (mg/l): Free chlorine grab: 0.08 Total chlorine grab: 2.08 Analyzer: 2.06 14:35 Verified outlet analyzer (mg/l) and collected sample. free chlorine grab: 0.03. Total chlorine grab: 1.83. analyzer: 1.88. Free ammonia: 0.11 Total ammonia: 0.44 Monochloramine: 1.66 Nitrite: 0.004. Recorded readings into PD sheets. Station and equipment: No issues identified. | Richmond Hill Bloomington Elevated Tank | 2026-03-31
CENTRAL | March | On-site for station check and sampling. W11637390. 13:26 Deactived PD9 duty. 13:30 Tower level 69% and draining at 10 l/s. 13:31 Verified inlet chlorine analyzer (mg/l): Free chlorine grab: 0.06. Total chlorine grab: 1.94. Analyzer: 2.01. 13:38 verified outlet analyzer and collected sample. free chlorine grab: 0.06. Total chlorine grab: 1.81. Analyzer: 1.85. Ph: 7.98. Free ammonia: 0.11 Total ammonia: 0.43 Monochloramine: 1.62. ?Nitrite: 0.000. Temperature: 4.9 celsius. Recorded data in process sheets. No issues found. | Richmond Hill Bloomington Elevated Tank | 2026-03-04
CENTRAL | March | On-site for station check and sampling. MBHP - W11656917. 10:05 Tower level 67% and filling at 87 l/s. 10:08 Verified inlet analyzer (mg/l): Free chlorine grab: 0.11 Total chlorine grab: 1.96 Analyzer: 2.01. 10:16 Verified outlet analyzer (mg/l) and collected sample. free chlorine grab: 0.02. Total chlorine grab: 1.80. analyzer: 1.85. Free ammonia: 0.11 Total ammonia: 0.43 Monochloramine: 1.61. Nitrite: 0.004. pH: 8.0. temperature: 6.4 celsius. Recorded readings into PD sheets. Station and equipment: No issues identified. | Richmond Hill Bloomington Elevated Tank | 2026-03-11
CENTRAL | March | On-site for station check and sampling. MBDW - W11672825. 10:13 Deactivated PD9 duty. 10:16Tower level 66% and draining at 10 l/s. 10:37 Verified outlet analyzer (mg/l) and collected sample. free chlorine grab: 0.02. Total chlorine grab: 1.81. analyzer: 1.83. Free ammonia: 0.11 Total ammonia: 0.44 Monochloramine: 1.68. Nitrite: 0.003. pH: 8.2. temperature: 6.4 celsius. 10:49 Verified inlet analyzer (mg/l): Free chlorine grab: 0.10 Total chlorine grab: 1.94 Analyzer: 1.97. Recorded readings into PD sheets. Station and equipment: No issues identified. | Richmond Hill Bloomington Elevated Tank | 2026-03-18
CENTRAL | March | On-site for station check and sampling. W11705550 08:16 Tower level 68% and draining at 93 l/s. 08:25 verified outlet analyzer and collected sample. free chlorine grab: 0.05. Total chlorine grab: 1.89. Analyzer: 1.85. Free ammonia: 0.11. Total ammonia: 0.45. Monochloramine: 1.71. ?Nitrite: 0.003. Temperature: 5.8 celsius. 08:40 Verified inlet chlorine analyzer (mg/l): Free chlorine grab: 0.08. Total chlorine grab: 1.87. Analyzer: 1.88. Recorded data in process sheets. No issues found. | Richmond Hill Coon's Elevated Tank | 2026-03-31
CENTRAL | March | Onsite to replace chlorine analyzer reagents. No issues found. | Richmond Hill Bloomington Elevated Tank | 2026-03-02
CENTRAL | March | On-site for station check and sampling. W11690186 09:29 Tower level 68% and draining at 88 l/s. 09:32 Verified inlet analyzer (mg/l): Free chlorine grab: 0.08 Total chlorine grab: 1.92Analyzer: 1.86. 09:47 Verified outlet analyzer (mg/l) and collected sample. free chlorine grab: 0.04. Total chlorine grab: 1.85. analyzer: 1.85. Free ammonia: 0.10 Total ammonia: 0.44 Monochloramine: 1.70 Nitrite: 0.005. Temperature: 5.2 celsius. Recorded readings into PD sheets. Station and equipment: No issues identified. | Richmond Hill Bloomington Elevated Tank | 2026-03-25
CENTRAL | March | Onsite to complete assigned work orders- informed ROC: H/S inspection Low temp tests ET Hi/Low level test Heat trace inspection Ventilation inspection CL17 analyzer maintenance Recirculation pump test Actuated valve inspection Drain valve inspection PRV inspection Performed station housekeeping Station/equipment- Ok | Richmond Hill Bloomington Elevated Tank | 2026-03-24
CENTRAL | March | On-site for station check and sampling. W11637390. 14:11 Tower level 67% and draining at 147 l/s. 14:14 Verified inlet chlorine analyzer (mg/l): Free chlorine grab: 0.03. Total chlorine grab: 1.95. Analyzer: 1.99. 14:18 verified outlat analyzer and collected sample. free chlorine grab: 0.04. Total chlorine grab: 1.76. Analyzer: 1.74 Ph: 8.03 Free ammonia: 0.06 Total ammonia: 0.38 Monochloramine: 1.65. ?Nitrite: 0.003. Temperature: 4.8 celsius. Recorded data in process sheets. No issues found. | Richmond Hill Coon's Elevated Tank | 2026-03-04
CENTRAL | March | Onsite to replace chlorine analyzer reagents for both inlet and outlet. No issues found. | Richmond Hill Coon's Elevated Tank | 2026-03-02
CENTRAL | March | Check altitude valve Installed two new solenoid valves on altitude and had control put back in controlling towe | Richmond Hill Coon's Elevated Tank | 2026-03-27
CENTRAL | March | On-site for station check and sampling. W11690186 07:00 Tower level 68% and draining at 88 l/s. 07:00 Verified inlet chlorine analyzer (mg/l): Free chlorine grab: 0.03. Total chlorine grab: 1.90. Analyzer: 1.94. 07:20 verified outlet analyzer and collected sample. free chlorine grab: 0.05. Total chlorine grab: 1.85/1.86/1.84. Analyzer: 1.76. Adjusted analyzer to match grabs. Free ammonia: 0.10. Total ammonia: 0.44. Monochloramine: 1.62. ?Nitrite: 0.004. Temperature: 5.4 celsius. Recorded data in process sheets. No issues found. | Richmond Hill Coon's Elevated Tank | 2026-03-25
CENTRAL | March | Onsiter to complete work orders: 10:34 notified ROC of work and placed chlorine analyzers in calibration mode. Chlorine analyzer maintenance - ok. 11:18 Verified analyzers: Inlet: 1.78. Analyzer: 1.75. outlet: 1.89. Analyzer: 1.89. Inlet/outlet heat trace inspection - ok. Circulation pump test - ok. chlorine scrubber check - ok. drain valve exercise- ok. JHSC inspection- ok. Actuated valve exercise and inspection: ok. PRV valve inspection: ok 11:27-11:38 triggered Low building temperature alarms of electrical, ammonia, chlorine and valve rooms. ok Ventillation system inspection:ok Site cleaning. No issues found. | Richmond Hill Coon's Elevated Tank | 2026-03-19
CENTRAL | March | On-site for station check and sampling. W11656917. 08:48 Tower level 64% and draining at 83 l/s. 09:00 Verified inlet chlorine analyzer (mg/l): Free chlorine grab: 0.03. Total chlorine grab: 1.95. Analyzer: 1.99. 09:07 verified outlet analyzer and collected sample. free chlorine grab: 0.02. Total chlorine grab: 1.79. Analyzer: 1.73 Free ammonia: 0.09. Total ammonia: 0.42. Monochloramine: 1.67. ?Nitrite: 0.004. Temperature: 5.4 celsius. Recorded data in process sheets. No issues found. | Richmond Hill Coon's Elevated Tank | 2026-03-11
CENTRAL | March | On-site for station check and sampling. W11672825 11:26 Tower level 60% and draining at 92 l/s. 11:33 verified outlet analyzer (mg/l) and collected sample. Free chlorine grab: 0.02. Total chlorine grab: 1.72. Analyzer: 1.73 Free ammonia: 0.13. Total ammonia: 0.45. Monochloramine: 1.62. ?Nitrite: 0.005. Temperature: 4.8 celsius. Ph: 8.01 11:43 Verified inlet chlorine analyzer (mg/l): Free chlorine grab: 0.06. Total chlorine grab: 1.87. Analyzer: 1.91. Work order previously created for Alltitude valve solenoide which is letting some water leak to drain. Recorded data in process sheets. No issues found. | Richmond Hill Coon's Elevated Tank | 2026-03-18
EAST | March | Vibration readings | Richmond Hill Pugsley Pumping Station | 2026-03-12
EAST | March | On site to complete station check. Time: 12:45 Grab (mg/l) Free: 0.05 Total: 1.50 No outstanding alarms. No OOS equipment. Checked station and trends. | Richmond Hill Pugsley Pumping Station | 2026-03-30
EAST | March | On site for facility station check and equipment verifications Duty is active - 330 L/s, 740 kpa Pumps 2 and 3 running in duty Grab sample from discharge: @13:00 Free: 0.02 mg/L Total: 1.61 mg/L Pump #2 and #3 system inspection and maintenance Reviewed trends, equipment OOS: None Station ok | Richmond Hill Pugsley Pumping Station | 2026-03-09
EAST | March | On site for facility station check and equipment verifications Recorded readings in PWQ sheets Duty is active - Pumps 2 and 3 running in D1, 320 L/s, discharge pressure - 740 kpa Chlorine residual grabs from discharge @14:33 Grab free: 0.03 mg/L Grab total: 1.48 mg/L Reviewed trends Equipment OOS: None Station ok | Richmond Hill Pugsley Pumping Station | 2026-03-06
EAST | March | On site to check station and equipment. P1 and P4 are running in duty 1. 14:50 chlorine residuals grab in mg/l: Total: 1.55 Free: 0.04 Other station readings are in PWQ sheets. Reviewed trends, Station is under normal operation. Generator warning alarm was outstanding from last night. Checked generator, no alarms lit at the control board. Both heaters are on. Able to ack+reset the warning alarm. Equipment OOS: none. | Richmond Hill Pugsley Pumping Station | 2026-03-02
EAST | March | Station Check (no issues found) Input data to PWQ 13:50 Chlorine Grab Residual (mg/l) Free: 0.04, Total 1.58 | Richmond Hill Pugsley Pumping Station | 2026-03-20
EAST | March | On site for monthly PMs - Informed ROC of work to be completed - Diesel generator test run and hours log Start Hours: 378.9 Start Fuel: 6447 L Pre checks: - Oil Level: Ok - Coolant Level: Ok - Battery cell levels: Ok - Battery Terminals and cables: Ok - Coolant recirc pump: Ok - Fluid Leaks: N/A @10:50 - Started generator: Ran pumps 1 and 4 during test run, to test station under generator power @11:22 - Readings while generator running Current: 196 amps Voltage: 600 V Frequency: 60.0 hz Engine speed: 1798 RPMs Oil pressure: 64 psi Oil temp: 160 F Generator stopped @12:05 Stop hours: 380.2 Stop Fuel: 6507 L No issues with generator run or transfer test - Pump #1 system inspection - Pump #4 system inspection - Flood alarm test @13:45 - Sump pumps inspection / maintenance - Suction valves exercise (Hand valves) - Discharge valve exercise (Hand valve) - Surge valves test - Housekeeping Placed all pumps back to auto Station operation okay | Richmond Hill Pugsley Pumping Station | 2026-03-17
EAST | March | Onsite to replace PSL switch on pump #3. Informed ROC and they put the pump #3 in manual off. Replaced the PSL switch and verified calibration. Put it back in service. All the related alarms were cleared. No issues. Informed ROC and left the site. | Richmond Hill Pugsley Pumping Station | 2026-03-24
EAST | March | Assisted Dan B and Ernie H with the surge valve system. They were on site to address the discharge surge valves electrical panel not working. When they tested the surge valves on discharge, valve #1 got stuck open Got to site with Jack P and we adjusted the needle valve for the close speed, and serviced the valve, flushed the strainer. The valve opened and closed okay. Tested multiple times, surge system is back to normal. | Richmond Hill Pugsley Pumping Station | 2026-03-19
EAST | March | On site to remove surge tank sump pumps as requested. | Richmond Hill Pugsley Pumping Station | 2026-03-18
EAST | March | On site for facility station check and equipment verifications Duty is active - RHRSWA Level -76% Flow: 390 L/s, Discharge pressure: 757 kpa Recorded station readings in PWQ sheets Grab sample from discharge (mg/L) Free: 0.02 Total: 1.58 Reviewed trends, equipment OOS: None Station ok | Richmond Hill Pugsley Pumping Station | 2026-03-16
EAST | March | On site to investigate surge receiving tank pump system.Investigate and found pump shorted to ground. Also found incorrect system logic with drain line motorized actuator valve and PLC programming. Will write a report and see if we can get that changed. Will need to return to replace pump. | Richmond Hill Pugsley Pumping Station | 2026-03-06
EAST | March | On site to respond to work order reporting discharge header surge relief valve system not working during recent test. Found batteries needing replacement. Replaced batteries and tested. Found upper surge relief valve sticking open. Ops cleaned y strainer and adjusted close speed pilot. Valve working well now. | Richmond Hill Pugsley Pumping Station | 2026-03-19
EAST | March | On site for station check and equipment verifications Readings in PWQ sheets Grab residuals from discharge @14:50 Free: 0.07 Total: 1.50 Reviewed trends Station operation normal | Richmond Hill Pugsley Pumping Station | 2026-03-23
WEST | March | - on site to finish station check and collect weekly bacti W11705704 - Jen Silva collected highlift sample at 11:20 - analyzer: 3.45mg/l grab: 3.50mg/l - free grab: 0.06mg/l - all other analyzer verification in PWQ -reagents all ok -topped up KMnO4 tank 1 16 -81cm -equipment all ok | Schomberg Water Treatment Plant & Wells 2-4 | 2026-03-31
WEST | March | - on site to repsond to highlift ntu fault, filter 3 Ntu alarm and UV minor faults - UV minor faults caused by power blip 28/03/2026 at 06:56 - reset alarms - turned plant off and cleaned NTU analyzers and adjust flows -topped up KMnO4 tank 2 16cm - 81cm -received post filter low chlorine alarms - verified at 14:10: 1.75mg/l grab; 1.79mg/l -checked chlorine system: all ok - adjust chlorinator 1 dosage factor 144% to 148% - on call operator | Schomberg Water Treatment Plant & Wells 2-4 | 2026-03-30
WEST | March | - on site for cylinder change 53kg - 121kg | Schomberg Water Treatment Plant & Wells 2-4 | 2026-03-31
WEST | March | Respond to UVT Transmittance Fault, OOR alarms. UVT sensor has low flow alarm active, started unit again to monitor. Triggered UVT sample flow warning again and interlocked filters on UVT Transmittance fault. Appears to be ample sample flow to analyzer (less flow / pressure on startup of plant). Sample flow warning on 30 second delay, but warning triggers SCADA fault alarm and interlocks plant. Changed UVT ?flow alarm output? setting from YES to NO temporarily to start up plant. Changed low flow warning delay from 30s to 0s - this disables flow warning and should prevent UVT fault on plant startup due to ?low sample flow? Monitored startup, no issues. | Schomberg Water Treatment Plant & Wells 2-4 | 2026-03-28
WEST | March | UV interlocked due to power failure. System appears to have shutdown normally. UV dose less than 40mj/cm2 while filter discharge flow registered for approximately 1 minute. Within compliance. | Schomberg Water Treatment Plant & Wells 2-4 | 2026-03-28
WEST | March | On site to collect weekly bact samples from raw and treated sample taps (W11657095). @09:30 tested treated chlorine residuals via hach field kit. Free: 0.04 mg/L Total: 3.66 mg/L Entered readings into PWQ sheet. Switched reservoir valving to north cell. | Schomberg Water Treatment Plant & Wells 2-4 | 2026-03-11
WEST | March | On site to collect weekly bact (W11705704) and iron (W11664712) samples. Completed in house lab and entered readings into PWQ sheet. Treated free grab: 0.06 mg/L Treated total grab: 3.50 mg/L | Schomberg Water Treatment Plant & Wells 2-4 | 2026-03-31
WEST | March | Respond to site to reset tripped OOS equipment due to power failure during storm event. Reset compressor 1, 2 (E0821 short circuit) Reset HLP1 (9 undervoltage) Reset HLP5 fire pump (phase reversal) UV system appears to have interlocked normally at 0224. Filter discharge flow registered for less than one minute during shutdown when UV dose below 40mj/cm2. Offsite 0347 during start up, responding to HLETYS comm, power failure | Schomberg Water Treatment Plant & Wells 2-4 | 2026-03-31
WEST | March | On site to collect weekly bact samples from raw and treated sample taps (w11637544). Collected MET samples (W11637705). Treated grab residual @ 08:53 Free: 0.04 mg/L Total: 3.71 mg/L Completed in house lab analyses and entered readings into PWQ sheet. | Schomberg Water Treatment Plant & Wells 2-4 | 2026-03-04
WEST | March | onsite to perfom the following WOs: - Filter turbidity analyzers - Finished water turbidity analyzer - Switched chlorinator duties, placed chlorinator 4 in lead duty and chlorinator 2 in off/ standby Reviewed Scada, duty active, deactivated duty ~ Dave T Notified ROC before and after completion of WOs - Did chlorine cylinder change with DT, tested for vacuum switch and tested leak no issues. Dave T activated duty after completion of WOs monitored station operation before leaving site no issues | Schomberg Water Treatment Plant & Wells 2-4 | 2026-03-05
WEST | March | On site responding to turbidity fault. Cleaned turbidimeter all seems okay. Checked UVT analyzer all ok. No new issues on site | Schomberg Water Treatment Plant & Wells 2-4 | 2026-03-13
WEST | March | On site to top up permangenate tanks 1 and 2 from 12/13-77/78cm | Schomberg Water Treatment Plant & Wells 2-4 | 2026-03-15
WEST | March | On site to complete monthly work orders including UV sensor check, well 2 valve exercising, prv inspection, compressor inspection and low temp alarm. | Schomberg Water Treatment Plant & Wells 2-4 | 2026-03-12
WEST | March | On site to inspect facility and complete in house lab analysis. Entered readings into PWQ sheet - no issues on site. | Schomberg Water Treatment Plant & Wells 2-4 | 2026-03-02
WEST | March | -on site to reset high lift pump 4 fault -topped up kmno4 tank 1 16- 81cm | Schomberg Water Treatment Plant & Wells 2-4 | 2026-03-10
WEST | March | -on site to meet Honeywell at SHW2 for hydro meter replacement -placed well in man/off and put SHW3 in auto -no issues - station back to normal | Schomberg Water Treatment Plant & Wells 2-4 | 2026-03-10
WEST | February | Review facility and trending for UV event occurring February 23 1533. Plant appears to have interlocked and shut down normally due to a power blip. UV dose registered below 40mj/cm2 for less than 30 seconds while filter discharge flow registered flow during shutdown. No issues. | Schomberg Water Treatment Plant & Wells 2-4 | 2026-02-23
WEST | March | All trends checked and ok, all equipment checked and ok All measurements are in mg/l Highlights - 10:00 am Total grab 3.48 vs analyzer 3.52 Free grab 0.08 Monochloramine 2.98 Post filter - 10:20 am Total grab 2.09 vs 2.15 analyzer Free 0.04 Reservoir - 10:40 am Total grab 3.59 vs analyzer 3.69 Free grab 0.05 Monochloramine 3.26 | Schomberg Water Treatment Plant & Wells 2-4 | 2026-03-09
WEST | March | On site to inspect facility. Completed in house lab analysis. Entered readings into PWA. Changed post filtration chlorine analyzer reagents. | Schomberg Water Treatment Plant & Wells 2-4 | 2026-03-06
WEST | March | -power blip caused UV minor fault alarms, plant was off at the time -reset alarms -no further issues | Schomberg Water Treatment Plant & Wells 2-4 | 2026-03-07
WEST | March | On site to work with operations, PCS and manufacturer's site technician to remove, replace and test new ultraviolet transmittance instrument panel. | Schomberg Water Treatment Plant & Wells 2-4 | 2026-03-24
WEST | March | On site to complete monthly work orders including: -Surve tank isolation valve exercise -transfer pumps inspection -PRV inspection -scrubber inspection -transfer pump air relief valve inspection No issues on site. | Schomberg Water Treatment Plant & Wells 2-4 | 2026-03-24
WEST | March | -on site to investigate filter 3 NTU trend -no issues with unit - cleaned -placed back into service | Schomberg Water Treatment Plant & Wells 2-4 | 2026-03-18
WEST | March | On site to complete monthly preventative maintenance work orders including: -health and safety inspection -high lift pumps inspection -high lift actuated valves inspection -changed chlorine cylinder bank 2 | Schomberg Water Treatment Plant & Wells 2-4 | 2026-03-19
WEST | March | On site to inspect facility. Completed in house lab analysis. Entered readings into PWQ sheet. Topped up KMNO4 tank 1. Tested chlorine residuals via hach field kit. High lift total analyzer: 3.61 mg/L High lift total chlorine grab: 3.69 mg/L Free grab: 0.04 mg/L | Schomberg Water Treatment Plant & Wells 2-4 | 2026-03-20
WEST | March | On site responding to reservoir total chlorine lolo alarm. Replaced damaged tubing barb and primed unit. Completed station check and lab analyses. Entered readings into PWQ sheet. Changed post filter chlorine analyzer reagents - found unit leaking and created follow up work order. Station operation normal, no issues on site. | Schomberg Water Treatment Plant & Wells 2-4 | 2026-03-23
WEST | March | On site to collect weekly bact samples from raw and treated sample taps (W11672923). Tested chlorine residuals via hach field kit. Free: 0.06 mg/L Total: 3.60 mg/L Analyzer: 3.58 mg/L Entered readings into PWQ sheet. | Schomberg Water Treatment Plant & Wells 2-4 | 2026-03-18
WEST | March | On site to complete annual Chlorine system overhaul (regulators, ejectors, pigtails, manifold, tubing, fittings). Replaced / rebuilt all of the above. Switched vacuum gauges for chlorinators 1 and 2 to pull from chlorinator instead of ejector heads. Adjusted chlorinator 1 and 2 vacuum gauge low range alarms to match operating vacuum from chlorinators. Vacuum tested system and tested regulator switch over. Chlorinators all holding at or above -800mmHg. Placed SHTP back in service and monitored, no issues. SHETCS duty 1 start / stop returned to 15/45%. | Schomberg Water Treatment Plant & Wells 2-4 | 2026-03-26
WEST | March | -on site to respond to filter 3 repeatedly triggering post rinse ntu high alarm -initiated rinse, turbidity reading 0.38 -replaced turbidimeter vial, turbidity decreased to 0.287 -filter 3 back in service | Schomberg Water Treatment Plant & Wells 2-4 | 2026-03-05
WEST | March | Macnamarra fuel inspection | Schomberg Water Treatment Plant & Wells 2-4 | 2026-03-10
WEST | March | Macnamarra fuel inspection | Schomberg Water Treatment Plant & Wells 2-4 | 2026-03-10
WEST | March | -on site to complete work orders -informed ROC of work -completed cylinder change -completed Check Valves Inspection, Schomberg WTP W3&4 -completed Pump and Motor Inspection, Schomberg WTP W3&4 -completed Exhaust Fan Inspection, Schomberg WTP W3&4 -completed Dehumidifier Inspection, Schomberg WTP W3&4 -completed Electric Actuated Valves Inspection, Schomberg WTP W3&4 -completed Fire Pumps and Motors, Inspection -completed Backwash Sump Tank System, Inspection -completed Low/High Temperature Alarm, Test -rotated chlorinator 4 duty into post UV dosing and tested | Schomberg Water Treatment Plant & Wells 2-4 | 2026-03-05
WEST |  | On site to complete monthly work orders including: -Surve tank isolation valve exercise -transfer pumps inspection - | Schomberg Water Treatment Plant & Wells 2-4 | 2026-03-25
WEST | March | -on site for station check, water quality lab -checked trends: all ok -entered readings in PWQ: all ok -verified analyzer -highlift 09:55: 3.70mg/l grab: 3.74mg/l -free cl grab: 0.05mg/l -post filter 10:05: 2.22mg/l grab: 2.20mg/l -reservoir 10:15: 3.05mg/l grab: 3.06mg/l -all reagents ok -switch to south cell - swapped sample lines -cleaned highlight NTU - flushed NTU sample line - caused highlift chlorine analyzer to spike to 4.15mg/l 09:50 - took total chlorine grab: 3.74mg/l - not adverse -reset UV minor faults -isolated reactor to investigate the failed sensor issue -sleeves all out but found water in sensor rod 2/3 -informed team lead -restarted plant: all ok -cleaned NTU analyzer filter 3 | Schomberg Water Treatment Plant & Wells 2-4 | 2026-03-16
WEST | March | On site to replace halogen system battery, replace Rotork batteries, replace VFD air filters, and infrared scan electrical equipment. | Schomberg Water Treatment Plant & Wells 2-4 | 2026-03-16
WEST | March | On site to complete station check. Entered readings into PWQ sheet. Verified online chlorine analyzers. Completed in house lab. | Schomberg Water Treatment Plant & Wells 2-4 | 2026-03-27
WEST | March | On site to complete monthly preventative maintenance work orders. Changed tubing elements in both reservoir analyzer sample pumps. Completed chlorine chemical system check. Performed chlorine analyzer maintenance. Completed monthly diesel generator test run. Start hours: 543.1 Stop hours: 544.5 Fuel used: 8 L | Schomberg Water Treatment Plant & Wells 2-4 | 2026-03-03
WEST | March | Rechlore building Attended Cl2 leak alarm No leak identified, reset halogen system and alarms, restarted cl2 gas dosing system, monitored site from scada for any gas buid up. everything look normal. Reservoir:- On site to complete station check, operational sample and collect weekly bacti W11705742 Checked trends: all ok 13:10-Took sample and chlorine grab from cell 1 (North) Free Cl2: 0.06mg/L Total Cl2: 2.07mg/L 13:15- cell 2 grab(East) Free Cl2: 0.08mg/L Total Cl2: 2.08mg/L 13:17-Cell 3 grab (West) Free Cl2: 0.04 mg/L Total Cl2: 2.13mg/L Entered reading in PWQ: all ok Equipment Okay | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2026-03-31
WEST | March | #NAME? | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2026-03-03
WEST | March | On site for Station check Check Trends: All okay 13:30-Verified pre- injection Analyzer Grab Free CL2-0.06mg/L; Analyzer- 0.06 mg/L Grab Total Cl2- 1.55mg/L; Analyzer- 1.48 mg/L 13:50-Verified post- injection Analyzer Grab Free CL2-0.06mg/L; Analyzer- 0.09 mg/L Grab Total Cl2- 2.54mg/L (Avg-2.52,2.54,2.58); Analyzer- 2.15 mg/L Adjusted analyzer up to 2.30 mg/L Reagents all good Verified Chem Scan- All okay Reagent all good entered values in PWQ sheet Topped up ammonia tank 1- 15.20 cm -to 75.46 cm equipment okay. | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2026-03-30
WEST | March | Reservoir:- On site to complete station and collect weekly bacti W11657067 Checked trends: all ok Took sample and chlorine grab north cell 10:25 Free Cl2: 0.05mg/L Total Cl2: 2.05mg/L South cell grab - 10:29 Free Cl2: 0.03mg/L Total Cl2: 2.09mg/L West cell grab- 10:33 Free Cl2: 0.02mg/L Total Cl2: 2.12mg/L Entered reading in PWQ: all ok Equipment Okay Rechloramination:- On site for Station check Check Trends: All okay 11:05-Verified pre- injection Analyzer Grab Free CL2-0.04mg/L; Analyzer- 0.07 mg/L Grab Total Cl2- 1.55mg/L; Analyzer- 1.49 mg/L 11:12-Verified post- injection Analyzer Grab Free CL2-0.04mg/L; Analyzer- 0.09 mg/L Grab Total Cl2- 2.19mg/L; Analyzer- 2.21 mg/L Reagents all good Verified Chem Scan- All okay topped up grey and green Reagents Topped up Ammonia tank 1 :15.03 cm- 75.22 cm entered values in PWQ sheet equipment okay. | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2026-03-11
WEST | March | On site for Station check Check Trends: All okay 10:40-Verified pre- injection Analyzer Grab Free CL2-0.02mg/L; Analyzer- 0.07 mg/L Grab Total Cl2- 1.50mg/L; Analyzer- 1.46 mg/L 10:50-Verified post- injection Analyzer Grab Free CL2-0.08mg/L; Analyzer- 0.09 mg/L Grab Total Cl2- 2.24mg/L; Analyzer- 2.24 mg/L Reagents all good Verified Chem Scan- All okay topped up DI water entered values in PWQ sheet equipment okay. | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2026-03-13
WEST | March | -on site to complete station and collect weekly bacti W11637582 -checked trends: all ok -entered reading in PWQ: all ok -took sample and chlorine grab north cell 10:15 -free cl: 0.06/l -total cl: 2.01mg/l -west cell grab 10:15 -free cl: 0.08mg/l -total cl: 2.13mg/l -south cell grab 10:20 -free cl: 0.07mg/l -total cl: 2.10mg/l -complete re chlorine building station check -checked trends: all ok -entered reading in PWQ: -verified pre analyzer 11:50 -analyzer free: 0.07mg/l grab: 0.10mg/l -analyzer total: 1.53mg/l grab: 1.52mg/l -reagents all ok -verified post analyzer 12:00 -analyzer free: 0.05mg/l grab: -analyzer total: 1.60mg/l grab: 1.67mg/l - adjusted -reagents all ok -chemscan verified -reagents all ok -equipment all ok | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2026-03-04
WEST | March | On site for Station check Check Trends: All okay 13:25-Verified pre- injection Analyzer Grab Free CL2-0.02mg/L; Analyzer- 0.06 mg/L Grab Total Cl2- 1.55mg/L; Analyzer- 1.50 mg/L 13:30-Verified post- injection Analyzer Grab Free CL2-0.04mg/L; Analyzer- 0.09 mg/L Grab Total Cl2- 2.13mg/L; Analyzer- 2.15 mg/L Reagents all good Topped up Ammonia Tank 1- 15.04 cm to 75.31 cm entered values in PWQ sheet equipment okay. | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2026-03-02
WEST | March | On site for Station check Check Trends: All okay 11:55-Verified pre- injection Analyzer Grab Free CL2-0.01mg/L; Analyzer- 0.06 mg/L Grab Total Cl2- 1.54mg/L; Analyzer- 1.51 mg/L 11:55-Verified post- injection Analyzer Grab Free CL2-0.03mg/L; Analyzer- 0.07 mg/L Grab Total Cl2- 2.24mg/L; Analyzer- 2.20 mg/L Reagents all good Verified Chem Scan- All okay topped up grey and green Reagents Topped up Ammonia tank 2 :15.04 cm- 75.52 cm entered values in PWQ sheet equipment okay. | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2026-03-09
WEST | March | Reset sump pump power failure trip for Rechlor building and sanitary sump pit at pumping station. Receive chlorine cylinder delivery. No issues. | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2026-03-10
WEST | March | On site for Station check Check Trends: All okay 12:45-Verified pre- injection Analyzer Grab Free CL2-0.02mg/L; Analyzer- 0.07 mg/L Grab Total Cl2- 1.42mg/L; Analyzer- 1.46 mg/L 12:52-Verified post- injection Analyzer Grab Free CL2-0.02mg/L; Analyzer- 0.08 mg/L Grab Total Cl2- 2.19mg/L; Analyzer- 2.16 mg/L Reagents all good Verified Chem Scan- All okay Reagent all good entered values in PWQ sheet equipment okay. | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2026-03-27
WEST | March | Station Check (no issues found) Input data to PWQ Verified Depoloxs (mg/L) 9:25 PRE: Free: Grab 0.04, A 0.07 Total: Grab 1.53, A 1.50 9:35 POST: Free: Grab 0.05, A 0.08 Total: Grab 2.32, A 2.27 Chemscan: (topped up distilled, distilled/muratic) Depolox: (topped up acetate for both) | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2026-03-23
WEST | March | On site for Station check Check Trends: All okay 11:05-Verified pre- injection Analyzer Grab Free CL2-0.02mg/L; Analyzer- 0.07 mg/L Grab Total Cl2- 1.48mg/L; Analyzer- 1.42 mg/L 11:13-Verified post- injection Analyzer Grab Free CL2-0.05mg/L; Analyzer- 0.08 mg/L Grab Total Cl2- 2.06mg/L; Analyzer- 2.04 mg/L Reagents all good Verified Chem Scan Post inj FNH3 Grab- 0.12 mg/L Post inj FNH3 Analyzer- 0.07 mg/L Adjusted Post Inj FNH3 slope from 0.04 to 0.06 New Post inj FNH3 analyzer reading- 0.09 mg/L Reagents all good. entered values in PWQ sheet equipment okay. | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2026-03-16
WEST | March | On site for Station check Check Trends: All okay Topped up Ammonia Tank 1- 15.23 cm to 75.48 cm 11:20-Verified pre- injection Analyzer Grab Free CL2-0.04mg/L; Analyzer- 0.08 mg/L Grab Total Cl2- 1.80mg/L; Analyzer- 1.88 mg/L 11:40-Verified post- injection Analyzer Grab Free CL2-0.06mg/L; Analyzer- 0.09 mg/L Grab Total Cl2- 2.30mg/L; Analyzer- 2.34 mg/L Reagents all good Verified Chem Scan- All okay topped up grey Reagent entered values in PWQ sheet equipment okay. | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2026-03-20
WEST | March | Reservoir:- On site to complete station check and collect weekly bacti W11690336 Checked trends: all ok 11:38-Took sample and chlorine grab from cell 1 (North) Free Cl2: 0.04mg/L Total Cl2: 2.16mg/L 11:40- cell 2 grab(East) Free Cl2: 0.03mg/L Total Cl2: 2.14mg/L 11:45-Cell 3 grab (West) Free Cl2: 0.03 mg/L Total Cl2: 2.15mg/L Entered reading in PWQ: all ok Equipment Okay Rechloramination:- On site for Station check Check Trends: All okay 12:42-Verified pre- injection Analyzer Grab Free CL2-0.03mg/L; Analyzer- 0.08 mg/L Grab Total Cl2- 1.92 mg/L; Analyzer- 1.87 mg/L 13:10-Verified post- injection Analyzer Grab Free CL2-0.05mg/L; Analyzer- 0.07 mg/L Grab Total Cl2- 2.18mg/L; Analyzer- 2.16 mg/L Reagents all good Verified Chem Scan- All okay Reagents all good entered values in PWQ sheet Topped up ammonia tank 2- 15.07 cm to 75 cm equipment okay. | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2026-03-25
WEST | March | -on site to complete following work orders -adjusted san marko van 54psi to 48psi -placed metro valve and pumps back into auto - tested flood alarm: all ok -tested sump pit: all ok -hoist inspection: all ok -heating inspection: all ok -check valve inspection: all ok -dehumidifier check: all ok | Woodbridge East Booster Pumping Station | 2026-03-31
WEST | March | Onsite responding to multiple alarms due to power blip CMU5 W11702361 Reset halogen system to get chloramination chemical system up and running reservoir at beginning of fill cycle Silenced diesel fuel tank outdoor alarm (very loud outdoors can hear from outside of the gate) Silenced generator diesel pump panel inside generator room Reset PD8 pump 2 soft starter fault -control volt low fault- ZC voltage lost- Had RO Connor turn BVPS pumps off until I was able to reset chlorine and ammonia systems. | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2026-03-03
WEST | March | On site for Station check Check Trends: All okay 11:45-Verified pre- injection Analyzer Grab Free CL2-0.03mg/L; Analyzer- 0.06 mg/L Grab Total Cl2- 1.48mg/L; Analyzer- 1.44 mg/L 11:55-Verified post- injection Analyzer Grab Free CL2-0.04mg/L; Analyzer- 0.09 mg/L Grab Total Cl2- 2.30mg/L; Analyzer- 2.24 mg/L Reagents all good Verified Chem Scan- All okay Reagents all good entered values in PWQ sheet equipment okay. | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2026-03-06
WEST | March | On site for Scheduled PM workorders, Informed ROC about the works being done. W11631734 RHRSTR, Separation Valve Exercise, South Richmond Hill RES (3M) W11631751 RHRSTR, West and East Hatch Clean Up, South Richmond Hill RES (3M) W11632526 RHRSTR, External Venting Screens Inspection, South Richmond Hill RES (6M) W11632026 RHRSTR, JHSC Health and Safety Inspection, East Vaughan BPS, South Richmond Hill RES | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2026-03-17
WEST | March | Reservoir:- On site to complete station and collect weekly bacti W11672961 Checked trends: all ok 11:43-Took sample and chlorine grab north cell Free Cl2: 0.06mg/L Total Cl2: 1.98mg/L 11:45- cell 2 grab Free Cl2: 0.02mg/L Total Cl2: 2.15mg/L 11:50-Cell 3 grab Free Cl2: 0.04mg/L Total Cl2: 2.15mg/L Entered reading in PWQ: all ok Equipment Okay Rechloramination:- On site for Station check Check Trends: All okay 12:50-Verified pre- injection Analyzer Grab Free CL2-0.06mg/L; Analyzer- 0.07 mg/L Grab Total Cl2- 1.56mg/L; Analyzer- 1.53 mg/L 13:09-Verified post- injection Analyzer Grab Free CL2-0.05mg/L; Analyzer- 0.09 mg/L Grab Total Cl2- 2.57mg/L; Analyzer- 2.53 mg/L Reagents all good Verified Chem Scan- All okay Reagents all good entered values in PWQ sheet equipment okay. | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2026-03-18
WEST | March | -on site to complete work orders -informed ROC of work -completed Chemscan Analyzer Maintenance -completed manual clean and manual zero 230 = 2571 248 = 3537 Min = -0.0016 Max = 0.0022 -completed Ammonia Peristaltic Pump Inspection 1200 hour service -replaced both pump elements -completed drawdowns on pumps: Pump #1 max flow = 433 ml/min Pump #2 max flow = 433 ml/min -completed Ammonia Feed and Storage Inspection -completed Chlorine Scrubber Inspection -completed Chlorine Leak Detector Test -completed Chlorine System Inspection -ran ejectors to waste and completed vacuum test -no issues -completed chlorine cylinder change -received ammonia delivery -completed Chlorine Analyzer Maintenance -checked electrolyte and grit sand -verified sample flows -verified analyzers after maintenance: 13:08 - pre-injection Analyzer readings: Free Chlorine = 0.08 mg/L Total Chlorine = 1.72 mg/L 13:08 - pre-injection Grabs: Free Chlorine = 0.04 mg/L Total Chlorine = 1.77 mg/L 13:18 - post-injection Analyzer readings: Free Chlorine = 0.09 mg/L Total Chlorine = 1.88 mg/L 13:18 - post-injection Grabs: Free Chlorine = 0.06 mg/L Total Chlorine = 1.85 mg/L -duty active, tested all chemical systems in auto -no issues, site back to normal operation | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2026-03-17
WEST | March | -on site to complete station check -system duty not active, activated duty for station check -checked equipment -reviewed trends -recorded readings in PWQ sheet -verified chlorine analyzers: 11:01 - Analyzer readings: Free Chlorine = 0.04 mg/L Total Chlorine = 1.47 mg/L 11:01 - Grabs: Free Chlorine = 0.05 mg/L Total Chlorine = 1.52 mg/L -no issues found | Woodbridge East Booster Pumping Station | 2026-03-02
WEST | March | -on site to complete station check -system duty active, pump 1 running -checked equipment -reviewed trends -recorded readings in PWQ sheet -verified chlorine analyzers: 11:29 - Analyzer readings: Free Chlorine = 0.04 mg/L Total Chlorine = 1.55 mg/L 11:29 - Grabs: Free Chlorine = 0.03 mg/L Total Chlorine = 1.57 mg/L -no issues found | Woodbridge East Booster Pumping Station | 2026-03-09
WEST | March | -on site to complete station check -system duty not active -checked equipment -reviewed trends -recorded readings in PWQ sheet -verified chlorine analyzers: 10:30 - Analyzer readings: Free Chlorine = 0.02 mg/L Total Chlorine = 1.45 mg/L 10:30 - Grabs: Free Chlorine = 0.04 mg/L Total Chlorine = 1.50 mg/L -no issues found | Woodbridge East Booster Pumping Station | 2026-03-23
WEST | March | Station Check (no issues found) Input data to PWQ 13:15 Verified Depolox (mg/L) Free: Grab 0.05, A 0.04 Total: Grab 1.65, A 1.60 | Woodbridge East Booster Pumping Station | 2026-03-13
WEST | March | -on site to complete station check -system duty active -checked equipment -reviewed trends -recorded readings in PWQ sheet -verified chlorine analyzers: 11:49 - Analyzer readings: Free Chlorine = 0.03 mg/L Total Chlorine = 1.57 mg/L 11:49 - Grabs: Free Chlorine = 0.06 mg/L Total Chlorine = 1.59 mg/L -no issues found | Woodbridge East Booster Pumping Station | 2026-03-20
WEST | March | -on site for station check -checked trends: all ok -entered reading in PWQ: -verified analyzer 10:00 -analyzer free: 0.02mg/l grab: 0.03mg/l -analyzer total: 1.29mg/l grab: 1.37mg/l - adjusted -place station valve local close due to weekend isolation | Woodbridge East Booster Pumping Station | 2026-03-27
WEST | March | -on site to complete station check -system duty active, pump 1 running -checked equipment -reviewed trends -recorded readings in PWQ sheet -verified chlorine analyzers: 11:54 - Analyzer readings: Free Chlorine = 0.03 mg/L Total Chlorine = 1.55 mg/L 11:54 - Grabs: Free Chlorine = 0.04 mg/L Total Chlorine = 1.56 mg/L -no issues found | Woodbridge East Booster Pumping Station | 2026-03-16
WEST | March | -on site to complete work orders -informed ROC of work -completed Manual Valve, Exercise -completed Low Temperature Alarm, Test -completed Sump Pit System, Inspection -completed Flood Alarm, Test -completed Siemens Depolox 5 Maintenance -checked electrolyte and grit sand -verified flow -verified analyzers after maintenance: 11:31 - Analyzer readings: Free Chlorine = 0.03 mg/L Total Chlorine = 1.53 mg/L 11:31 - Grabs: Free Chlorine = 0.03 mg/L Total Chlorine = 1.52 mg/L -completed Motorized Valve Actuator Inspection & Exercise -completed JHSC Health and Safety Inspection -completed Pump & Motor, Inspection -no issues, site back to normal operation | Woodbridge East Booster Pumping Station | 2026-03-19
WEST | March | -On-site to complete station check and collect sample -system duty not active, tower = 65 % -checked equipment -reviewed trends 11:25 - collected grab sample: Free Chlorine = 0.02 mg/L Total Chlorine = 1.71 mg/L 11:29 - collected weekly regulatory micro. sample - W/O # W11706785 SL1000 readings: MCL = 1.64 mg/L TNH3 = 0.39 mg/L FNH3 = 0.06 mg/L NO2 = 0.004 mg/L temp = 7.1 C -collected operational ATP and phosphorous samples -recorded readings in PWQ sheet -no issues found | Woodbridge East Elevated Tank | 2026-03-31
WEST | March | -on site to complete station check -system duty active -checked equipment -reviewed trends -recorded readings in PWQ sheet -verified chlorine analyzers: 13:04 - Analyzer readings: Free Chlorine = 0.05 mg/L Total Chlorine = 1.40 mg/L 13:04 - Grabs: Free Chlorine = 0.03 mg/L Total Chlorine = 1.49/1.49/1.49 mg/L 13:14 - adjusted total chlorine analyzer to 1.49 mg/L based on average of 3 grabs -no other issues found | Woodbridge East Booster Pumping Station | 2026-03-06
WEST | March | -on site to complete work orders -informed ROC of work -completed Manual Valve, Exercise -completed Actuated Valve, Exercise & Inspection -completed Portable Gasoline Generator, Test -transferred site to generator power, no issues -completed Sump Pit System, Inspection -tested flood alarm -completed Low Temperature Alarm, Test -completed Dehumidifier, Inspection & Cleaning -completed JHSC Health and Safety Inspection -no issues, site back to normal operation | Woodbridge East Elevated Tank | 2026-03-19
WEST | March | -adjust high level alarm 82-75% | Woodbridge East Elevated Tank | 2026-03-25
WEST | March | -On-site to complete station check and collect sample -system duty not active, tower filling due to San Marco valve work, tower = 58 % -checked equipment -reviewed trends 11:27 - collected grab sample: Free Chlorine = 0.04 mg/L Total Chlorine = 1.89 mg/L 11:30 - collected weekly regulatory micro. sample - W/O # W11690893 SL1000 readings: MCL = 1.79 mg/L TNH3 = 0.41 mg/L FNH3 = 0.06 mg/L NO2 = 0.006 mg/L -recorded readings in PWQ sheet -no issues found | Woodbridge East Elevated Tank | 2026-03-25
WEST | March | -adjusted PRV at chancellor and San Marko at 09:45 am -48- 55psi -tower began to fill at 60l/s at 52% 09:45 - tower filling at 10l/s at 66% at 15:15 | Woodbridge East Elevated Tank | 2026-03-25
WEST | March | -On-site to complete station check and collect samples -system duty not active, tower = 73 % -checked equipment -reviewed trends 11:59 - collected grab sample: Free Chlorine = 0.02 mg/L Total Chlorine = 1.67 mg/L 12:03 - collected weekly regulatory micro. sample - W/O # W11638725 SL1000 readings: MCL = 1.54 mg/L TNH3 = 0.36 mg/L FNH3 = 0.05 mg/L NO2 = 0.003 mg/L temp = 6.8 C -collected operational ATP and phosphorus samples -recorded readings in PWQ sheet -no issues found | Woodbridge East Elevated Tank | 2026-03-04
WEST | March | -On-site to complete station check and collect sample -deactivated system duty, tower = 78 % -checked equipment -reviewed trends 10:27 - collected grab sample: Free Chlorine = 0.02 mg/L Total Chlorine = 1.69 mg/L 10:31 - collected weekly regulatory micro. sample - W/O # W11657772 SL1000 readings: MCL = 1.54 mg/L TNH3 = 0.36 mg/L FNH3 = 0.06 mg/L NO2 = 0.004 mg/L temp = 6.9 C -recorded readings in PWQ sheet -no issues found | Woodbridge East Elevated Tank | 2026-03-11
WEST | March | -On-site to complete station check and collect sample -deactivated system duty, tower = 80 % -checked equipment -reviewed trends 10:43 - collected grab sample: Free Chlorine = 0.03 mg/L Total Chlorine = 1.47 mg/L 10:47 - collected weekly regulatory micro. sample - W/O # W11706785 SL1000 readings: MCL = 1.29 mg/L TNH3 = 0.31 mg/L FNH3 = 0.06 mg/L NO2 = 0.003 mg/L temp = 7.5 C -collected operational ATP and phosphorous samples -recorded readings in PWQ sheet -no issues found | Woodbridge West Elevated Tank | 2026-03-31
WEST | March | -On-site to complete station check and collect sample -deactivated system duty, tower = 77 % -checked equipment -reviewed trends 11:02 - collected grab sample: Free Chlorine = 0.02 mg/L Total Chlorine = 1.67 mg/L 11:07 - collected weekly regulatory micro. sample - W/O # W11673653 SL1000 readings: MCL = 1.55 mg/L TNH3 = 0.36 mg/L FNH3 = 0.05 mg/L NO2 = 0.004 mg/L temp = 6.0 C -collected operational ATP and phosphorous samples -recorded readings in PWQ sheet -no issues found | Woodbridge East Elevated Tank | 2026-03-18
WEST | March | -On-site to complete station check and collect samples -deactivated system duty, tower = 64% -checked equipment -reviewed trends 11:05 - collected grab sample: Free Chlorine = 0.02 mg/L Total Chlorine = 1.48 mg/L 11:09 - collected weekly regulatory micro. sample - W/O # W11638725 SL1000 readings: MCL = 1.30 mg/L TNH3 = 0.30 mg/L FNH3 = 0.04 mg/L NO2 = 0.004 mg/L temp = 4.4 C -collected operational ATP and phosphorous samples -recorded readings in PWQ sheet -no issues found | Woodbridge West Elevated Tank | 2026-03-04
WEST | March | -On-site to complete station check and collect sample -system duty not active, tower = 52% -checked equipment -reviewed trends 09:51 - collected grab sample: Free Chlorine = 0.02 mg/L Total Chlorine = 1.41 mg/L 09:55 - collected weekly regulatory micro. sample - W/O # W11657772 SL1000 readings: MCL = 1.21 mg/L TNH3 = 0.30 mg/L FNH3 = 0.06 mg/L NO2 = 0.004 mg/L temp = 6.2 C -recorded readings in PWQ sheet -no issues found | Woodbridge West Elevated Tank | 2026-03-11
WEST | March | -on site to complete work orders -informed ROC of work -completed Sensing Line Heat Trace System, Inspection -completed Low Temperature Alarm, Test -completed Sump Pit System Inspection -completed Flood Alarm Test -completed Air Valve Inspection -completed Manual Valve, Exercise -completed JHSC Health and Safety Inspection -completed High & Low Water Level Alarm, Test -completed Actuated Valve, Exercise -completed Portable Gasoline Generator, Test -transferred PAC power to portable generator -no issues -site back to normal operation | Woodbridge West Elevated Tank | 2026-03-24
WEST | March | -On-site to complete station check and collect sample -system duty not active, tower = 74 % -checked equipment -reviewed trends 10:20 - collected grab sample: Free Chlorine = 0.02 mg/L Total Chlorine = 1.47 mg/L 10:24 - collected weekly regulatory micro. sample - W/O # W11673653 SL1000 readings: MCL = 1.29 mg/L TNH3 = 0.30 mg/L FNH3 = 0.05 mg/L NO2 = 0.003 mg/L temp = 5.6 C -collected operational ATP and phosphorous samples -recorded readings in PWQ sheet -no issues found | Woodbridge West Elevated Tank | 2026-03-18
WEST | March | -On-site to complete station check and collect sample -deactivated system duty, tower = 58 % -checked equipment -reviewed trends 10:50 - collected grab sample: Free Chlorine = 0.04 mg/L Total Chlorine = 1.45 mg/L 10:54 - collected weekly regulatory micro. sample - W/O # W11690893 SL1000 readings: MCL = 1.28 mg/L TNH3 = 0.31 mg/L FNH3 = 0.05 mg/L NO2 = 0.005 mg/L -recorded readings in PWQ sheet -no issues found | Woodbridge West Elevated Tank | 2026-03-25
WW-WEST | March | Onsite to add soda ash to aeration tanks. added 2 bags of soda ash per train | Nobleton Water Resource Recovery Facility | 2026-03-29
WW-WEST | March | Received call from ROC for Mech. bar screen OOS alarm. (ongoing issue) Arrived onsite at 3:15am, Inlet channel hi level alarm present due to channel backing up. Reset bar screen and cleared alarms. Bar screen running operationally with no issues found - will continue to monitor. | Nobleton Water Resource Recovery Facility | 2026-03-30
WW-WEST | March | Received bar screen alarm. Upon inspection, the screen faulted in the lower position as it was pulling up rags. Small chunk of rags built up. Changed barscreen start level setpoint from 150 mm to 140 mm to clear rags before large buildup occurs. Will create a work order if the issue occurs again overnight. | Nobleton Water Resource Recovery Facility | 2026-03-30
WW-WEST | March | - GFL on site to take a load of sludge. - Transferred sludge from the thickening tank to the holding tank - Enabled RAS batch wasting mode at 9:15. Wasted 18 m^3 from train 1 and 18 m^3 from train 2 then reset RAS batch wasting mode once done - Performed inhouse lab and recorded readings on SharePoint. No new issues - Added 1 bag of soda ash each to aeration tank 1 and 2 - Checked station and recorded readings on SharePoint. No new issues - Prepared sampling bottles for the sampling day | Nobleton Water Resource Recovery Facility | 2026-03-30
WW-WEST | March | Checked station and recorded readings on SharePoint. No new issues | Nobleton Water Resource Recovery Facility | 2026-03-31
WW-WEST | March | - Collected weekly regulatory samples - Performed inhouse lab and recorded readings on SharePoint. No issues | Nobleton Water Resource Recovery Facility | 2026-03-31
WW-WEST | March | - Added 1 bag of soda ash each to aeration tank 1 and 2 - GFL on site to take a load of sludge. Transferred sludge from the thickening tank to the holding tank - Enabled RAS batch wasting mode at 8:03. Wasted 15 m^3 from train 1 and 15 m^3 from train 2 then reset RAS batch wasting mode once done - Inspected and cleaned DO probe. No new issues - No condensation in aeration air lines. all okay - Removed rags from aeration tank inlet sluice gate and surface | Nobleton Water Resource Recovery Facility | 2026-03-31
WW-WEST | March | - Checked station and recorded readings on SharePoint - added 2 bags of soda ash each to aeration tank 1 and 2 - assisted maintenance with troubleshooting effluent pump pressure decrease - maintenance worked on RAS valve 4. Killed power to the rotork unit to be removed tomorrow to install a new RAS valve - performed partial lab due to attending contractor coordination at Janet SPS for sewer clean out - Performed JHSC inspection. Tested eyewash. Eyewash alarms received. No issues | Nobleton Water Resource Recovery Facility | 2026-03-09
WW-WEST | March | Collected regulatory samples | Nobleton Water Resource Recovery Facility | 2026-03-11
WW-WEST | March | In to Monitor Station During High Flow Event. Placed Bar-screen in Continuous Cycle Mode. Found Filter Air Lift Clogged. Cleared Obstructions and Returned to Service. | Nobleton Water Resource Recovery Facility | 2026-03-11
WW-WEST | March | On site to investigate reoccurring low DO alarms on Aeration Tank 2. Cleaned probe and removed rags from inlet stems on both sides. High flows from snow melting and rain all day. Instruct ROC to monitor and turn on second blower as required. Added 2x 25kg bags of soda ash to each aeration basin. | Nobleton Water Resource Recovery Facility | 2026-03-07
WW-WEST | March | - Supernated sludge thickening tank. - Transferred sludge from the thickening tank to the sludge holding tank - Completed in-house lab and recorded readings on SharePoint. No issues. - Added 2 bags of soda ash each to aeration tank 1 and 2. - Checked station and recorded readings on SharePoint. - Enabled RAS batch wasting mode at 09:08. - Set auto wasting for 15 m^3 from train 1 and 15 m^3 from train 2 between 10:00 and 12:00. - Wasted another 5 m^3 from train 1. Then reset RAS batch wasting mode at 11:57. - Created W11714307 for alum pump 5. Pump works well in manual but displays error when analogue signal cable is plugged in. - Reduced air lift flow rates for both grit vortexes. Found the water was flowing too quickly over the weir. Flows slower and carries fewer solids over at the lower flow rate. | Nobleton Water Resource Recovery Facility | 2026-03-06
WW-WEST | March | In to Complete Scheduled WOs. Received Alum Delivery. Reviewed and Signed Documentation. Alum Tank Level: 0.57 ?> 3.10m. Enabled Batch Waste Set-point. RAS Pumps Auto Off in Preparation for Wasting @ 09:35. WAS Valves #2 and 3 Manual Open. Added Soda Ash to Both Aer. Tanks ?> 2 Bags Each. WAS Pumps #1 and 2 Manual On and Off Intermittently for Wasting. Wasting Complete, Reset Batch Wasting Set-point. Wasted 20 m3 from Clarifier #1 and 15 m3 from Clarifier #2. Returned WAS Valves #2 and 3 to Manual Closed. Inspected Bar-screen Influent and Effluent Sensors. Cleaned Sensor Heads and Adjusted Signal Pathway, Trends Restored. | Nobleton Water Resource Recovery Facility | 2026-03-13
WW-WEST | March | In to Complete Scheduled WOs. Enabled Batch Waste Set-point. RAS Pumps Auto Off in Preparation for Wasting @ 08:55. WAS Valves #2 and 3 Manual Open. Maintenance (Mech.) On-site for RAS Valve Replacement. Placed RAS Pumps #1-3 in Manual Off and Isolated Manual Suction and Discharge Valves in Preparation. Lowered and Activated Decant Pump. Added Soda Ash to Both Aer. Tanks ?> 2 Bags Each. Maintenance (Mech.) Unable to Complete Valve Replacement due to Isolation Issues. Returned RAS System to Service. Decant Complete. Raised and Deactivated Decant Pump. Sludge Transfer Valve Local Open, Transferred Thickened Sludge. Transfer Valve Returned to Manual Closed. WAS Pumps #1 and 2 Manual On and Off Intermittently for Wasting. Adjusted Aer. Train #1 and 2 Alum Dosage Set-points Based on In-House Laboratory Results: 225.00 ?> 220.00 mg/L. Verified Sand Filter Air Lift Function and Performance. Flushed Reject Wash Boxes, Weirs and Air Lifts. Wasting Complete, Reset Batch Wasting Set-point. Wasted 15 m3 from Clarifier #1 and 10 m3 from Clarifier #2. Returned WAS Valves #2 and 3 to Manual Closed. Returned Sand Filter #2 to Service Based on High Influent Flows. Verified Air Lift Function and Performance. Completed Consolidated Headworks Building Inspections with No Issues. Returned to Service. Cleared Associated Alarms. | Nobleton Water Resource Recovery Facility | 2026-03-10
WW-WEST | March | - Collected regulatory samples - Performed in-house lab and recorded readings on SharePoint. No new issues | Nobleton Water Resource Recovery Facility | 2026-03-04
WW-WEST | March | Remotely changed alum pumps 1, 3, 4 back to auto speex | Nobleton Water Resource Recovery Facility | 2026-03-12
WW-WEST | March | - Performed in-house lab and recorded readings on SharePoint. No issues - Added 2 bags of soda ash each to aeration tank 1 and 2 - Checked station and recorded readings on SharePoint - Enabled RAS batch wasting mode at 10:08. Wasted 15 m^3 from train 1 and 15 m^3 from train 2 then reset RAS batch wasting mode at 13:47 - Plant water booster pump is cycling too much. This eventually causes pumps to fault on high and low pressure. This issue seems to have been going on for a while. Upon inspection, it seems RT1 and RT2 temperature protection relay faulted and is showing red. In addition, the discharge side fails to maintain adequate pressure while the plant water demand is low (vortex water scour not active at the time, no plant water usage from hydrant, etc). This is causing the pump to cycle on constantly to boost the pressure. The pressure tank seems to be okay with no leaks. Pressure switch differential settings seem okay. The check valve seems to be the culprit. I?ve tried to isolate the lead pump, pump 1, and the hissing sound stopped but the system still loses pressure fast. Therefore, it seems to be leaking on both sides. Created work order for maintenance and notified team - Received soda as delivery at 14:50. Received 250 bags. Signed all papers | Nobleton Water Resource Recovery Facility | 2026-03-05
WW-WEST | March | Reduce alum from 215mg/L to 200mg/L on both post aeration dosing points. Reduce filter inlet alum from 19.5mg/L to 15mg/L due to high flows from rain and snow melt. | Nobleton Water Resource Recovery Facility | 2026-03-11
WW-WEST | March | Checked heat trace. digi span shows correct readings and confirmed heat production. No issues | Nobleton Water Resource Recovery Facility | 2026-03-10
WW-WEST | March | - Added 2 bags of soda ash each to aeration tank 1 and 2 - Enabled RAS batch wasting mode at 8:55. Placed valves and was pumps to auto. Set automatic batch wasting mode to waste 19 m^3 from train 1 and 14 m^3 from train 2. Reset RAS batch wasting mode at 12:30. Placed valves and was pumps back to manual off. - performed in-house lab. No issues - Notified ROC of the work being performed - Inspected the generator and fuel level, all okay. Started the generator at 13:25. Recorded readings on SharePoint after 30 minutes, no issues. Ran for approximately one hour. Runtime for generator 1 from 314 hrs to 315.06 hrs. Fuel level from 19.5 inch to inch 19.25 inch - Checked station and recorded readings on SharePoint - HVAC panel in generator room shows smoke detector tripped and HVAC tripped | Nobleton Water Resource Recovery Facility | 2026-03-02
WW-WEST | March | On site for ras pump valve 4 stiff. Electrical unwired will return to remove and install new plug valve. Also looked at effluent prv?s. Isolated pumps and prvs suspect leaking further down line as line pressure decreases. | Nobleton Water Resource Recovery Facility | 2026-03-09
WW-WEST | March | Harie Rajamithiran(OIT) working under the direction of Young Jung(OIC). -Completed sand filter valve exercise -Completed scum pumps 1&2 inspections, no issues found -Completed filter inlet channel cleaning | Nobleton Water Resource Recovery Facility | 2026-03-12
WW-WEST | March | In to Complete Scheduled WO. Corporate IT Staff On-site Upon Arrival. Added Soda Ash to Both Aer. Tanks ?> 2 Bags Each. Completed Filter Air Lift Inspection, Performance and Function OK. | Nobleton Water Resource Recovery Facility | 2026-03-15
WW-WEST | March | On site to troubleshoot RAS VL V4. Disconnected power and outputs from PAC panel. Unwired power and control wires for actuator removal. Mechanics are replacing valve. | Nobleton Water Resource Recovery Facility | 2026-03-09
WW-WEST | March | - Cleaned filter inlet channel - Gave OJT on the plant hvac system controllers, rooftop hvac system and generator radiator. Changed two rooftop 24x24x2 sized filters. Ordered smaller 12x24x2 filters. | Nobleton Water Resource Recovery Facility | 2026-03-12
WW-WEST | March | - Transferred sludge from the thickening tank to the sludge holding tank - Enabled RAS batch wasting mode at 9:06. Wasted 20 m^3 from train 1 and 20 m^3 from train 2 then reset RAS batch wasting mode once done - Checked station and recorded readings on SharePoint. No new issues - Removed lots of rags from aeration tank 1 and 2 outlet - Inspected and cleaned DO probe. No issues - Checked airlines for condensation. None found | Nobleton Water Resource Recovery Facility | 2026-03-04
WW-WEST | March | Completed daily lab and added data into SharePoint. Completed station check - effluent pump still cycling on and off with high pressure, known issue with WO. Filter cell 4 plugged - unplugged and working normally. Other filter cells working well. Decanted sludge thickening tank. Placed WAS pumps and valves into auto and Enabled batch wasting at 830am and set auto waste for 30m3 from 10am to 12pm. Placed WAS pumps and valves back in manual upon wasting completion. Bled condensation from aeration condensation lines. Added 2 bags of soda ash to aeration tanks per train. Assisted Young and Harie with sludge pump PMs | Nobleton Water Resource Recovery Facility | 2026-03-12
WW-WEST | March | Harie Rahamithiran(OIT) working under the direction of Young Jung(OIC). -Completed lab analysis & station check , no issues found -Added 2 bags of soda ash per each aeration tank -Started batch wasting process at 09:40 , wasting from 11:00-13:00 for 19m^3 per train -Transferred STT to SHT without supernate process -Cleaned UV channel & banks -Turned WAS pumps 1&2 to manuel off | Nobleton Water Resource Recovery Facility | 2026-03-20
WW-WEST | March | - Performed in-house lab and recorded readings on SharePoint - Added 2 bags of soda ash each to aeration tank 1 and 2 - Enabled RAS batch wasting mode at 9:30. Wasted 10 m^3 from train 1 and 10 m^3 from train 2 then reset RAS batch wasting mode once done - Assisted with sanitary sump pit high high float test. Alarm received - Flows still elevated due to snow melt and rain. Due to high alum usage (flow paced), changed alum pump manual speed from 37% down to 15% - Checked station and recorded readings on SharePoint. No new issues - Cleaned aeration inlet channel - Notified ROC of the work being performed. - Inspected aeration blower 1-3. Oil was good. Belt was good. Changed filter for aeration blower 2. Washed the used mesh filter with soap and placed it back on the shelf for future use | Nobleton Water Resource Recovery Facility | 2026-03-19
WW-WEST | March | High flows caused bad readings on bar screen differential level. This caused bar screen to fault. Inlet channel back-fed sludge thickening tank and filled it with raw sewage. Can be pumped out tomorrow. Reset screen. Adjusted differential level from 200mm to 150mm. Monitored. Looks okay for now. | Nobleton Water Resource Recovery Facility | 2026-03-22
WW-WEST | March | - Checked station and recorded readings on SharePoint. No new issues - Added 2 bags of soda ash each to aeration tank 1 and 2 - Enabled RAS batch wasting mode at 8:08. Wasted 20 m^3 from train 1 and 20 m^3 from train 2 then reset RAS batch wasting mode at 11:10 - Removed rags at aeration outlet - No condensation at airlines - Inspected DO probe. No issues - Inspected WAS pumps 1 and 2. Checked belt, motor and oil. No issues - Inspected RAS pumps 1~3. Checked coupling, oil and motor. No issues - Reset RAS and WAS alarms - Received a call from ROC about mechanical screen fault. Local panel shows overtorque. Upon examination, there was a huge ball of rags stuck to the screen and was not able to remove it. Placed the screen and screw to OOS and locked out. Once the rag was removed, placed the screen and screw back in service and in auto. Reset alarms and ran the screen couple times with no issues | Nobleton Water Resource Recovery Facility | 2026-03-18
WW-WEST | March | In to Complete Scheduled WOs. Notified ROC. Assisted with Aer. Tank Inlet Channel Cleaning. Completed Vortex and Sludge Blower Inspections. Oil Reservoirs and Belts OK. Greased Bearings and Replaced Air Filters Where Necessary. Returned to Service and Cleared Associated Alarms. | Nobleton Water Resource Recovery Facility | 2026-03-19
WW-WEST | March | In to Complete Scheduled WOs. Lowered and Activated Decant Pump. Added Soda Ash to Both Aer. Tanks ?> 2 Bags Each. Enabled Batch Waste Set-point. RAS Pumps Auto Off in Preparation for Wasting @ 08:25. WAS Valves #2 and 3 Manual Open. Removed Rags and Debris from Bar-screen Influent Channel. Returned Bar-screen to Differential Level Set-point Operation. Decant Complete. Raised and Deactivated Decant Pump. Sludge Transfer Valve Manual Open, Transferred Thickened Sludge. Transfer Valve Returned to Manual Closed. WAS Pumps #1 and 2 Manual On and Off Intermittently and Sequentially for Wasting. Completed Filter Air Lift Inspection, Performance and Function OK. Wasting Complete, Reset Batch Wasting Set-point. Wasted 20 m3 from Each Clarifier. Returned WAS Valves #2 and 3 to Manual Closed. Removed Rags and Debris from Aer. Tanks #1 and 2 Inlet Gates and Effluent Weirs. | Nobleton Water Resource Recovery Facility | 2026-03-16
WW-WEST | March | - Removed supernatant back into the front of the process - Performed in-house lab and recorded readings on SharePoint. Flows coming into the plant is still elevated due to rainfall and snowmelt. No issues with lab numbers, tss is good. Adjusted alum manual pump speed from 18% to 22% - Enabled RAS batch wasting mode at 9:40. Wasted 12.5 m^3 from train 1 and 12.5 m^3 from train 2 then reset RAS batch wasting mode at 13:38 - Added 2 bags of soda ash each to aeration tank 1 and 2 - Checked station and recorded readings on SharePoint. No new issues - Unplugged filter 1, east side - Changed the smaller 12x24x2 filter on the hvac rooftop | Nobleton Water Resource Recovery Facility | 2026-03-23
WW-WEST | March | Received delivery of alum. Reviewed and signed bill of lading and certificate of analysis. Filled tank from 0.75 m to 3.56 m. | Nobleton Water Resource Recovery Facility | 2026-03-25
WW-WEST | March | Harie Rajamithiran(OIT) working under the direction of Daniel Hirstwood(OIC). -Completed online DO probe verification , both aeration tank DO probes within approximately 0.70mg/L range when compared with handheld probe -Completed aeration outlet weir cleaning , valve stems and probes are clean -Completed filter inlet cleaning -Completed aeration blower room , aeration MCC & building stairs comprehensive housekeeping | Nobleton Water Resource Recovery Facility | 2026-03-26
WW-WEST | March | On site to troubleshoot Alum pump 5. Found analogue fault on pump display. Checked control and power wiring. Tightened all connections. Fault has been resolved. Tested analogue signal and measured correct reading from Scada command. Tested pump in manual with help of operations. Ok. Alum Pump 5 is back in service. | Nobleton Water Resource Recovery Facility | 2026-03-25
WW-WEST | March | Onsite for scheduled PMs. Called ROC to inform of hi level alarms being triggered from sump pit inspections. Inspected sump pit in process building basement - hi level alarm triggered and both pumps activate with floats. Inspected sanitary sump pit in headworks - hi level alarm triggered and pumps activated with floats. Cleared alarms. Placed filter air compressors into off and LOTO for inspection. Drained water from lines and tank. Checked and cleaned air filters, checked belts all ok. Placed compressors back into auto and confirmed operation. Cleaned filter building, swept floors and cleaned bathroom. Assisted with aeration tank channel clean. | Nobleton Water Resource Recovery Facility | 2026-03-19
WW-WEST | March | - wasted 12 m^3 from train 1 and 12 m^2 from train 2 then reset RAS batch wasting mode at 13:06 - checked station and recorded readings on SharePoint. No new issues - due to high flows coming in from snow melt. Placed alum pump 1, 3, 4 into manual speed at 37% to reduce alum dosage. Notified TL we need alum delivery next Friday | Nobleton Water Resource Recovery Facility | 2026-03-17
WW-WEST | March | Reset barscreen over tork. Watched screen run. No visible issues. Reset scada alarms. Screen operating in auto. | Nobleton Water Resource Recovery Facility | 2026-03-20
WW-WEST | March | Checked barscreen okay Adjusted torque sensor. Ran okay. | Nobleton Water Resource Recovery Facility | 2026-03-20
WW-WEST | March | Had ops add another bad of soda ash per aeration tank due to lower pH. Reduced alum to post aeration further from 220mg/L to 215mg/L. | Nobleton Water Resource Recovery Facility | 2026-03-10
WW-WEST | March | - Performed in-house lab and recorded readings on SharePoint. Higher effluent TSS and RAS/WAS TSS due to high flow event. - Added 2 bags of soda ash each to aeration tank 1 and 2 - Removed rags from aeration outlet - Checked station and recorded readings on SharePoint. No issues - Cleaned clarifier inlet channel - Changed alum pumps 1, 3 and 4 into manual speed at 25% to reduce the alum usage for high flow event. Changed alum setpoint back to 225 mg/L from 200 mg/L for aeration train 1 and 2. Changed filter inlet alum setpoint from 15 mg/L to 19.5 mg/L Update: Enabled RAS batch wasting mode. Wasted 25 m^3 from train 1 and 15 m^3 from train 2 then reset RAS batch wasting mode | Nobleton Water Resource Recovery Facility | 2026-03-11
WW-WEST | March | Added 2 bags soda ash to each train. | Nobleton Water Resource Recovery Facility | 2026-03-22
WW-WEST | March | - Added 2 bags of soda ash to each aeration tank - Performed in-house lab and recorded readings on SharePoint - Enabled RAS batch wasting mode at 9:30 - Transferred sludge from the thickening tank to the holding tank | Nobleton Water Resource Recovery Facility | 2026-03-17
WW-WEST | March | Performed in-house lab and recorded readings on SharePoint Collected weekly regulatory samples | Nobleton Water Resource Recovery Facility | 2026-03-18
WW-WEST | March | - Performed in-house lab and recorded readings on SharePoint. No issues - Added 2 bags of soda ash per aeration tank - Checked station and recorded readings on SharePoint. No new issues - Enabled RAS batch wasting mode at 8:40. - Set autowasting for 15 m^3 from train 1 and 15 m^3 from train 2 then reset RAS batch wasting mode at 12:05. - Picked rags out of aeration train 1 outlet and headworks inlet. | Nobleton Water Resource Recovery Facility | 2026-03-27
WW-WEST | March | - Performed in-house lab and recorded readings on SharePoint. No issues - Added 2 bags of soda ash per aeration tank - Checked station and recorded readings on SharePoint. No new issues - Enabled RAS batch wasting mode at 9:00. Wasted 15 m^3 from train 1 and 15 m^3 from train 2 then reset RAS batch wasting mode at 12:05 | Nobleton Water Resource Recovery Facility | 2026-03-26
WW-WEST | March | Collected weekly regulatory samples Performed in-house lab and recorded readings on SharePoint | Nobleton Water Resource Recovery Facility | 2026-03-25
WW-WEST | March | - Checked station and recorded readings on SharePoint. No new issues - Enabled RAS batch wasting mode at 8:44. Wasted 19 m^2 from train 1 and wasted 19 m^2 from train 2 then reset RAS batch wasting mode at 12:34 - assisted with clarifier area housekeeping. Picked up some soda ash bags from the perimeter of the facility | Nobleton Water Resource Recovery Facility | 2026-03-24
WW-WEST | March | - Performed in-house lab and recorded readings on SharePoint. No issues with number - Added 1 bag of soda ash to each aeration tank | Nobleton Water Resource Recovery Facility | 2026-03-24
WW-WEST | March | - Added 2 bags of soda ash each to aeration tank 1 and 2 - Enabled RAS batch wasting mode at 8:57. Placed WAS valves and pumps to auto. Auto batch wasting from 10-12, set to waste 11 m^3 from train 1 and 11 m^3 from train 2 - Performed daily in-house lab and recorded readings on SharePoint. No new issues - Checked station and recorded readings on SharePoint. No new issues | Nobleton Water Resource Recovery Facility | 2026-03-03
WW-WEST | March | - Added 1 bag of soda ash each to aeration tank 1 and 2 - Enabled RAS batch wasting mode at 8:50. Wasted 17.5 m^3 from train 1 and 17.5 m^3 from train 2 then reset RAS batch wasting mode once done - Performed station check and recorded readings on SharePoint - Performed DO probe inspection and cleaning. No issues - Removed floating solids. Removed rags from aeration inlet sluice gate and the outlet | Nobleton Water Resource Recovery Facility | 2026-03-25
WW-CEAST | March | -On site to complete work orders. -Station check completed, readings entered into SharePoint. -Checked screen room, changed out rag bin, flushed screw press drain lines, replaced bins following pick up. -Monthly JHSC H&S inspection completed, no issues noted. -Consolidated Dry Well Pump Floor Inspection completed. -RS pump & motor inspection completed. -Pump 1: 1310L/s. -Pump 2: 975L/s at 0% speed, 1230L/s at 25%, 1460L/s at 50%, 1860L/s at 100%. -Pump 3: 1310L/s. -Pump 4: 1290L/s. -Pump 5 OOS. -Pump 6: 1165L/s. -Check valve inspections completed. -Sump pit inspection completed. -Dry well flood alarm completed, Sump High High Level Alarm confirmed by ROC. -Air relief valve inspection completed. -Seal water strainer inspection completed. -Air compressor inspection completed. -BAS check completed. -Ran Pump 1 in auto duty 1 again until it failed again on Motor/Bearing High Temp Alarm. -Pumps 1 and 5 remain OOS. | Markham Leslie Pumping Station | 2026-03-06
WW-CEAST | March | Station check complete and the readings have been entered in the sharepoint. Changed out the rag bin. | Markham Leslie Pumping Station | 2026-03-30
WW-CEAST | March | -On site to complete work orders. -Station check completed, readings entered into SharePoint. -Checked screen room, changed out rag bin, hosed down floor, repositioned screw press to better align with floor drain. -Bar screen bin removal completed. -Monthly diesel generator test run completed, readings entered into SharePoint. -1058 - Transferred site to generator power. -1241 - Transferred site back to utility power. -Gen. 1: Start hours: 231:42, Stop hours: 233:41, Run time: 1hr, 59min. -Gen. 2: Start hours: 119:35, Stop hours: 121:33, Run time: 1hr, 58min. -Gen. 3: Start hours: 105:54, Stop hours: 107:52, Run time: 1hr, 58min. -Hazardous waste collection and removal completed. -Overflow kit inspection completed. -Ran Pump 1 in auto, duty 1. Pump ran from 12:55-1450 before faulting again on Motor/Bearing High Temp Alarms. Left pump faulted and OOS for the night. -Pump 5 OOS with VFD Fault following generator testing. Work request created for issue. | Markham Leslie Pumping Station | 2026-03-04
WW-CEAST | March | -On site to complete work orders. -Station check completed, readings entered into SharePoint. -Reset Earth Fault on AHU1. -Reset Fault 47, Stack Overtemp Fault on Pump 1. -Test ran Pump 1 in auto, duty 1. Pump 1 ran for just under two hours before faulting again. Fault 47, Overtemp Fault back on Pump 1 MCC panel and SCADA is showing Fault Alarm, Motor/Bearing High Temp Alarm, and Motor/Bearing High Temp Trip Alarm. -Left Pump 1 in manual off, OOS for the night. -Hoist inspections completed on site, no issues noted. -Checked screen room, flushed screw press drain lines, replaced bins, cleaned floor in screen room. -Pump 1 OOS. | Markham Leslie Pumping Station | 2026-03-02
WW-CEAST | March | -On site to complete consolidated wet well inspection work order. -Wet well high level alarm test completed and confirmed by ROC. -Wet well inspection and cleaning completed. -Wet well valve exercises completed. -Bar screen cleaning and lubrication completed. -Screw conveyor cleaning and lubrication completed. -Maintenance team able to clear faults on Generator 3 and Pump 5. Both are now back in service. -Pump 1 remains OOS. | Markham Leslie Pumping Station | 2026-03-10
WW-CEAST | March | LSSS - Pump 1 fault alarm. Checked site, pump duty rotated to pump 5. Phil R logged into the facility logbook to complete work orders. Will monitor site. *Wong book, should be in ROC wastewater* | Markham Leslie Pumping Station | 2026-03-02
WW-CEAST | March | -On site to complete work orders. -Cleared fault on Pump 1 and ran in auto, duty 1 for close to two hours before pump faulted again. -Pump 1 back OOS for the weekend. -Station check completed, readings entered into SharePoint. -Checked screen room, changed out rag bin, replaced bins following pick up, flushed screw press drain lines, topped up bar screen oil. -Consolidated dry well valve exercise work order completed. -Pump discharge valves are automatically exercised each day as pumps cycle through duty rotation. -Pump isolation valves all fully exercised. -Forcemain header and tie valves all fully exercised. -Forcemain drain valve exercised. -Cleared all alarms following work. -Pump 1 OOS. | Markham Leslie Pumping Station | 2026-03-13
WW-CEAST | March | On site to check automatic phone dialer. No dial tone on line. Need Bell technician | Markham Leslie Pumping Station | 2026-03-19
WW-CEAST | March | On site for pump PM?s LOTO before PM?s with electricians Completed pump PM?s on pumps 4,5, and 6. Greased pumps Greased driveshafts Checked oil levels on pumps 5 and 6 Lower bearings need to be topped up on pumps 5-6 | Markham Leslie Pumping Station | 2026-03-27
WW-CEAST | March | -station check of site -reviewed SCADA -inspected site -entered data into sharepoint -bins out for pickup, screen room clean, bins rotated -Housekeeping -pump 1 remains OOS, 5 pumps available in auto -station okay | Markham Leslie Pumping Station | 2026-03-18
WW-CEAST | March | -On site to complete work orders. -Station check completed, readings entered into SharePoint. -Checked drywell. -Checked screen room, changed out rag bin, flushed screw press drain lines, topped up bar screen oil. -Consolidated monthly surge tank inspection completed. Exercised valves and flushed transmission lines. -Pump 1 OOS. | Markham Leslie Pumping Station | 2026-03-16
WW-CEAST | March | Run pump 1 Greased during run. Temp stabilized a few times Pump shut down Allowed to cool Started pump and regressed upper bearing. | Markham Leslie Pumping Station | 2026-03-27
WW-CEAST | March | On site with total Lift for annual inspections | Markham Leslie Pumping Station | 2026-03-19
WW-CEAST | March | -On site to perform a station check. -Entered station readings into SharePoint. -Checked drywell. -Reset fault on Pump 1 and test run pump for maintenance team. -Checked screen room, changed out rag bin for the weekend, replaced bins following pick up, flushed screw press drain lines, bar screen oil topped up. -Assisted maintenance team with pump testing and maintenance activities. -Pump 1 is currently still running, but if it faults again it will remain OOS for the weekend. | Markham Leslie Pumping Station | 2026-03-27
WW-CEAST | March | -On site to perform a station check. -Entered station readings into SharePoint. -Checked drywell, drained condensate from air compressor tanks. -Ran Pump 1 in auto, duty 1 until pump faulted again. -Pump 1 remains OOS. -Rag bins placed out for pickup. | Markham Leslie Pumping Station | 2026-03-25
WW-CEAST | March | -On site to complete work orders. -Entered station readings into SharePoint. -Checked drywell. -Checked screen room, changed out rag bin, replaced bins following pick up, flushed screw press drain lines, topped up bar screen oil, cleaned rags off floor. -Completed cleaning tasks around yard and doorways. -Pump 1 OOS. | Markham Leslie Pumping Station | 2026-03-20
WW-CEAST | March | On site for odour control PM. Completed. | Markham Leslie Pumping Station | 2026-03-23
WW-CEAST | March | -On site to perform a station check. -Entered station readings into SharePoint. -Checked drywell. -Checked screen room, changed out rag bin, topped up bar screen oil, flushed screw press drain lines. -Placed rag bins out for pick up. -Ran Pump 1 in auto, duty 1 until Pump Fault came back in with Motor/Bearing High Temp Alarm. -Pump 1 OOS. | Markham Leslie Pumping Station | 2026-03-11
WW-CEAST | March | On site to check pump 5 VFD. Found auxiliary power fault. Was able to reset fault. Suspect it happened during power transfer last week. Operations tested pump 5 in manual. Pump is working ok. Pump 5 back in auto duty rotation. Also onsite to check generator 3. Local control panel screen was off. Found loose fuse holder on front of panel. Repaired. Screen is back on. No more issues. | Markham Leslie Pumping Station | 2026-03-10
WW-CEAST | March | -On site to complete work orders. -Washed Bayview Steeles OCF mist eliminator filters in screen room and left filters out to dry. -Checked screen room, changed out rag bin, flushed screw press drain lines, hosed down floor. -Odour control scrubber system inspection completed. Inspected filters, greased fan shaft in screen room OCU. -Station check completed, readings entered into SharePoint. -Bypass sampling kit inspection completed. -Ran Pump 1 in auto, duty 1 until Motor/Bearing High Temp Alarms came back in. -At 1132, Generator 3 Warning Alarm and Generator 3 DGC Not in Auto Alarm came in. Inspected Generator 3, found generator screen/panel blank, appears as though their is no power to Gen. 3 panel. Unable to reset alarms locally on generator or at GMCP panel. Work request created for issue. -Pump 1 and 5 OOS, Generator 3 OOS. | Markham Leslie Pumping Station | 2026-03-09
WW-CEAST | March | On site completed work orders. Station Check (See details on SharePoint) All pumps available in timed auto duty rotation every 4 hours, except, pump 1, which is in manual/off out of service. Standby power generators available in auto. Switch sump pump duty from pump 1 to 2. Ran sump pump 2 for several minutes to removed stagnant water/sewage from the sump pit. Drained condensates from the surge tanks air compressors. Blew down bubblers. Cleared/reset alarms. Checked dry well, ok. Checked bar screens. Found screw press drain clog. Unclogged said drain, afterwards, cleaned/hosed down bar screen room. Switched rag bin. Added oil on the screen chain oil reservoir. Both are almost empty. Adjusted dripping port to a minimal opening. | Markham Leslie Pumping Station | 2026-03-23
WW-CEAST | March | On site completed bar screen rag bin removal and replacement. Switched rag bin Pushed out rag bins for pick up by Miller Waste tomorrow. Cleaned screen room. | Markham Leslie Pumping Station | 2026-03-25
EAST | March | Under direction of OIC Dan Zhou Started well pump 2 in manual on @ 08:49 hrs. for sampling | Mount Albert Wells 1 & 2 | 2026-03-31
EAST | March | On Site for; - Station checks - Regulatory sampling micro (W11705406) Data in PWQ Workbook Regulatory samples of well 2 taken @ 09:34 hrs. Influent Grab @ 09:33 hrs. FCl: 1.87 mg/L Analyzer FCl: 1.95 mg/L Effluent Grabs @ 09:34 hrs. FCl: 1.26 mg/L TCL: 1.56 mg/L Analyzer FCl: 1.32 mg/L @ 09:42 hrs. placed well pump 2 back in auto Equipment OOS: None Facility: OK | Mount Albert Wells 1 & 2 | 2026-03-31
EAST | March | Under direction of OIC Dan Zhou On site for; - Regulatory sampling, micro (11705406) Data in PQW workbook @ 14:10 hrs. placed well pump 2 in manual off, silicate pumps 1/2 and hypo pumps 1/2 in manual/manual speed 0%. Verified flow path of well pump 1 is valved to waste @ 14:12 started well pump 1 in local Regulatory sample taken for well 1 @ 14:42 hrs. @ 14:43 placed well pump 1 in local off @ 14:44 returned silicate pumps 1/2 and hypo pumps 1/2 to auto, auto speed | Mount Albert Wells 1 & 2 | 2026-03-31
EAST | March | On site to accept hypo delivery Start 45cm Stop 88cm | Mount Albert Wells 1 & 2 | 2026-03-03
EAST | March | On site to top up silicate tank.? Before level: 61.6cm After level: 120 cm | Mount Albert Wells 1 & 2 | 2026-03-04
EAST | March | Under direction of OIC Dan Zhou On Site for; - Station checks Data in PWQ Workbook Influent Grab @ 14:16 hrs. FCl: 1.42 mg/L Analyzer FCl: 1.44 mg/L Effluent Grabs @ 14:27 hrs. FCl: 1.31 mg/L TCL: 1.74 mg/L Analyzer FCl: 1.33 mg/L Checked valving for silicate system and water flush line. Tested silicate pump 2. Placed back in service on auto duty rotate. Quick report made (W11733156) Duty inactive Equipment OOS: None Facility: OK | Mount Albert Wells 1 & 2 | 2026-03-13
EAST | March | On Site for; - Station checks - Operational sampling, iron Data in PWQ Workbook Influent Grab @ 11:28 hrs. FCl: 1.86 mg/L Analyzer FCl: 1.89 mg/L Effluent Grabs @ 11:30 hrs. FCl: 1.35 mg/L TCL: 1.73 mg/L Analyzer FCl: 1.30 mg/L @ 11:43 returned well pump 2 to auto Duty inactive Equipment OOS: Silicate pump 2 Facility: OK | Mount Albert Wells 1 & 2 | 2026-03-09
EAST | March | On Site for; - Station checks - Turbidity analyzer maintenance Data in PWQ Workbook Influent Grab @ 10:29 hrs. FCl: 1.33 mg/L Analyzer FCl: 1.37 mg/L Effluent Grabs @ 10:31 FCl: 1.42 mg/L TCL: 1.74 mg/L Analyzer FCl: 1.33 mg/L Turbidity analyzer maintenance: @ 10:39 placed well pump 2 in manual off, no flow directed to users Start clean @ 10:43 hrs. Stop clean @ 10:53 hrs. Turbidity spike due to new vial installation retaining static (formed bubbles), re cleaned new vial, once any remaining bubbles leave vial, NTU should stabilize. Informed on call OIC Jack Palmer. @ 11:18 returned pump 2 to auto Duty inactive Equipment OOS: Silicate pump 2 Facility: OK | Mount Albert Wells 1 & 2 | 2026-03-06
EAST | March | Macnamarra fuel inspection | Mount Albert Wells 1 & 2 | 2026-03-10
EAST | March | Silicate top up: Before: 360L (76.5) After: 493L (104.7) | Mount Albert Wells 1 & 2 | 2026-03-12
EAST | March | On Site for; - Station checks - JHSC Health and Safety inspection Data in PWQ Workbook Influent Grab @ 10:38 FCl: 1.35 mg/L Analyzer FCl: 1.32 mg/L Effluent Grabs @ 10:42 FCl: 1.28 mg/L TCL: 1.55mg/L Analyzer FCl: 1.22 mg/L Duty Inactive Equipment OOS: Silicate pump 2 Station running nominally | Mount Albert Wells 1 & 2 | 2026-03-02
EAST | March | Under direction of OIC Dan Zhou @ 10:45 hrs. Placed well pump 2 in manual on for operational sampling. | Mount Albert Wells 1 & 2 | 2026-03-09
EAST | March | Under direction of OIC Dan Zhou On Site for; - Station checks - Regulatory sampling micro (W11637246), manganese sampling (W11638464) Data in PWQ Workbook Regulatory samples taken @ 10:42 hrs. @ 10:05 well pump 2 interlock due to manual switch of hypo and silicate pumps @ 10:20 manually stated well pump 2 @ 10:25 placed hypo pump2 in manual speed 25 % and silicate pump 1 in manual speed 35 % Verified well pump 1 is valved to waste @ 10:27 started well pump 1 Influent Grab @ 10:43 FCl: 1.90 mg/L Analyzer FCl: 1.97 mg/L Effluent Grabs @ 10:42 FCl: 1.52 mg/L TCL: 1.91 mg/L Analyzer FCl: 1.42 mg/L @ 10:55 placed well pump 1 back in local off, and well pump 2 in auto, returned silicate pump 1 and hypo pump 2 speed setpoints back in auto Equipment OOS: Silicate pump 2 Facility: OK | Mount Albert Wells 1 & 2 | 2026-03-04
EAST | March | Station Check (no issues found) Input data to PWQ 11:41 Verified CL17s (mg/l) Influent Free: Grab 1.36, A 1.39 Effluent Free: Grab 1.20, A 1.26 Effluent Total: Grab 1.37 Silicate top up (70.8 to 107.4cm) Hypo tank transfer (preparation for small leak repair): Tank #1 (60.0 to 87.3cm) (placed in service) Tank #2 (50.4 to 23.2 cm) (placed out of service) Instrumentation on site for "loss of heartbeat" repair Diesel fuel Lo alarm adjusted from 21.0cm to 22.0 cm | Mount Albert Wells 1 & 2 | 2026-03-26
EAST | March | Under Direction of OIC Patrick Fobert On site for PM's; - Turbidity analyzer maintenance - Influent and Effluent AIT maintenance - Deep well exhaust valve test - Sodium hypochlorite panel boards inspection - Silicate pumps maintenance - Sodium hypochlorite pumps maintenance - High/low temp alarm test - Butterfly valve exercise - Sodium hypochlorite system maintenance - Well 2 bore hole inspection - Generator test run Chlorine analyzer maintenance: Start clean @ 09:22 hrs. Stop clean @ 09:59 hrs. Analyzer verification: Effluent grab @ 10:30 hrs. FCl: 1.34 mg/L Analyzer: FCl: 1.34 mg/L Influent grab @ 10:40 hrs. FCl: 1.42 mg/L Analyzer: FCl: 1.42 mg/L Turbidity meter maintenance: Start @ 09:28 hrs. Stop @ 09:47 hrs. Pre clean NTU: 0.043 Post clean NTU: 0.038 Building Low temp alarm manually triggered @ 10:08 hrs. , alarm in @ 10:10 hrs. Building High temp alarm manually triggered @ 10:18 hrs. , alarm in @ 10:22 hrs. *Replaced pump dosing head on silicate pump 2 (pump head cavity is msaller than pump 1). New max flow is 100 mL/min. Adjusted max flow silicate dosing setpoint on SCADA to 100 mL/min.* Generator test run: Start Fuel: 1486 L Stop Fuel: 1454 L Start Hours: 208.85 Stop Hours: 210.25 Start Time: 13:18 hrs. Pre run checks; Battery Cell Levels: Ok Battery Terminals and Cables: Ok Oil Level: Ok Coolant Level: Ok Fluid Leaks: NO Coolant Recirculating pump: Ok Faulty Gauges: NO @ 13:18 hrs. Switched ATS to Test for generator power @ 13:28 hrs. Placed generator under facility load, Well pump 2 in Manual ON @ 13:50 hrs. placed well pump1 in manual on local, valved to waste *under load* Operating Current: 69 Amps Operating Frequency: 60.05 Hz Operating Voltage: 602.85 Volts Engine speed: 1798 RPM Water/coolant Temp: 88.68 C Oil Pressure: 392 kpa Oil Temperature: 83.00 C @ 14:14 hrs. well pump 1 in local off for ATS switch @ 14:18 placed well pump 2 in manual off for ATS switch @ 14:22 hrs. Toggled ATS to normal @ 14:32 power switched to station power @ 14:42 cooldown stopped @ 14:44 placed well pump 2 back in auto | Mount Albert Wells 1 & 2 | 2026-03-17
EAST | March | Silicate top up | Mount Albert Wells 1 & 2 | 2026-03-19
EAST | March | Under direction of OIC Patrick Fobert On site for; - Station checks Data in PWQ Workbook Influent Grab @ 14:32 hrs. FCl: 1.53 mg/L Analyzer FCl: 1.59 mg/L Effluent Grabs @ 14:34 hrs. FCl: 1.40 mg/L TCL: 1.74 mg/L Analyzer FCl: 1.31 mg/L Changed buffer and analyzer reagents for influent and effluent AIT's. Silicate pump 2 fault alarm on March 14 due to air releif valve plug being compromised. Threading in pump head will not hold plug in place. Informed acting team lead Patrick Fobert, (part being sourced). Duty inactive Equipment OOS: Silicate Pump 2 Facility: OK | Mount Albert Wells 1 & 2 | 2026-03-16
EAST | March | @ 08:52 started well pump 2 for sampling. | Mount Albert Wells 1 & 2 | 2026-03-25
EAST | March | On Site for; - Station checks - Regulatory sampling micro (W11690092) Data in PWQ Workbook Regulatory samples taken well 2 taken @ 09:48 hrs. , well 1 raw sample taken @ 10:22 hrs. Influent Grab @ 09:32 hrs. FCl: 1.88 mg/L Analyzer FCl: 1.95 mg/L Effluent Grabs @ 09:48 hrs. FCl: 1.28 mg/L TCL: 1.56 mg/L Analyzer FCl: 1.24 mg/L NTU: 0.068 NTU @ 10:01 placed well pump 2 in manual off Verified well pump 1 is valved to waste @ 10:07 hrs. placed hypo pumps 1/2 in manual speed 0 % and silicate pumps 1/2 in manual speed 0 % @ 10:12 hrs. started well pump 1 in local, valved to waste Disregard fail to start silicate and hypo pump alarms, due to not dosing raw well water, valved to waste @ 10:22 placed well pump 1 back in local off, returned silicate pumps 1/2 and hypo pumps 1/2 speed setpoints back in auto @ 10:24 hrs. placed well pump 2 back in auto Equipment OOS: None Facility: OK | Mount Albert Wells 1 & 2 | 2026-03-25
EAST | March | Under direction of OIC Partrick Fobert Started well pump 2 for regulatory sampling. | Mount Albert Wells 1 & 2 | 2026-03-18
EAST | March | On site to complete station check. Collecting weekly Bac-t Samples. W11656823 Weekly Bac-t Samples. Time: 14:04 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.93 2.01 Time: 14:07 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.30 1.29 Total: 1.56 At 14:00 started up well 1 to run to waste to collect raw water sample. Verified analyzers with grabs. Checked site and trends. Gen tank 1 hi alarm disregard. Silicate pump 2 OOS till part can be replaced. At 14:38 stopped well 1. | Mount Albert Wells 1 & 2 | 2026-03-11
EAST | March | On Site for; - Station checks - Regulatory sampling micro (W11672709) Data in PWQ Workbook Regulatory samples taken well 2 taken @ 09:33 hrs. , well 1 raw sample taken @ 09:55 hrs. Influent Grab @ 09:24 hrs. FCl: 1.88 mg/L Analyzer FCl: 1.96 mg/L Effluent Grabs @ 09:33 hrs. FCl: 1.36 mg/L TCL: 1.76 mg/L Analyzer FCl: 1.30 mg/L Verified well pump 1 is valved to waste @ 09:39 placed hypo pumps 1/2 in manual speed 0 % and silicate pumps 1/2 in manual speed 0 % *Disregard fail to start silicate and hypo pump alarms, due to not dosing raw well water, valved to waste @ 09:39 placed well pump 2 in manual off and well pump 1 in local on for raw well 1 sample @ 09:54 placed well pump 1 back in local off, returned silicate pump 1/2 and hypo pump 1/2 speed setpoints back in auto @ 10:00 hrs. placed well pump 2 back in auto Equipment OOS: None Facility: OK | Mount Albert Wells 1 & 2 | 2026-03-18
EAST | March | On Site for; - Station checks - Turbidity analyzer maintenance Data in PWQ Workbook Influent Grab @ 12:53 hrs. FCl: 1.45 mg/L Analyzer FCl: 1.44 mg/L Effluent Grabs @ 12:57 hrs. FCl: 1.38 mg/L TCL: 1.72 mg/L Analyzer FCl: 1.35 mg/L @ 13:11 placed well pump 2 in manual off for turbidity analyzer maintenance Clean start @ 13:12 hrs. Clean stop @ 13:20 hrs. Noticed slow drip leak on interconnect valve on hypo tank 2 side. Created work order for W-Maint (W11749660) @ 13:35 placed well pump 2 in auto. Duty inactive Equipment OOS: None Facility: OK | Mount Albert Wells 1 & 2 | 2026-03-20
EAST | March | Changed well 2 flow setpoint from 22 l/s to 27 l/s. | Mount Albert Wells 1 & 2 | 2026-03-25
EAST | March | On Site for; - Station checks Data in PWQ Workbook Duty inactive during grabs Influent Grab @ 11:55 hrs. FCl: 1.28 mg/L Analyzer FCl: 1.31 mg/L Effluent Grabs @ 11:59 hrs. FCl: 1.40 mg/L TCL: 1.71 mg/L Analyzer FCl: 1.32 mg/L Isolated hypo tank 1 to drain hypo tank 2 for interconnect valve repair. Duty active Equipment OOS: None Facility: OK | Mount Albert Wells 1 & 2 | 2026-03-23
EAST | March | Under direction of OIC Dan Zhou On site for; - clean silicate containment area Cleaned silicate containment area and surrounding area plus sprayed down piping gallery room. During clean, ROC called that eyewash flow alarm is going off. Can't clear alarm remotely or on site at OIT. Attempted to resolve the issue at the eyewash and cannot. Made work order # W11768770 and informed team Lead Dan Zhou | Mount Albert Well 3 | 2026-03-30
EAST | March | Under Direction of OIC Dan Zhou @ 12:52 hrs. placed well pump 3 in manual on for sampling. | Mount Albert Well 3 | 2026-03-31
EAST | March | Silicate top up | Mount Albert Well 3 | 2026-03-12
EAST | March | Under direction of OIC Dan Zhou On site for; - Station checks - Regulatory sampling, micro (W11705406) Data in PQW Workbook Regulatory samples taken @ 13:47 hrs. Influent Grabs @ 13:46 hrs. FCl: 1.75 mg/L Analyzer: FCl: 1.77 mg/L Effluent Grabs @ 13:47 hrs. FCl: 1.72 mg/L TCl: 1.95 mg/L Analyzer: FCl: 1.71 mg/L NTU: 0.065 NTU @ 13:52 placed well pump 3 back in auto Duty inactive Equipment OOS: None Facility: OK | Mount Albert Well 3 | 2026-03-31
EAST | March | Under direction of OIC Dan Zhou On site for; - Station checks - Operational sampling, iron Data in PQW Workbook @ 09:56 hrs. placed well pump 3 in manual on for operational sampling Influent Grabs @ 10:25 hrs. FCl: 1.73 mg/L Analyzer: FCl: 1.75 m,g/L Effluent Grabs @ 10:28 hrs. FCl: 1.83 mg/L TCl: 1.89 mg/L Analyzer: 1.88 mg/L NTU: 0.56 NTU @ 10:40 hrs. returned well pump 3 to auto Duty inactive Equipment OOS: None Facility: OK | Mount Albert Well 3 | 2026-03-09
EAST | March | Under direction of OIC Dan Zhou On site for; - Station checks Data in PQW Workbook Influent Grabs @ 09:43 FCl: 1.59 mg/L TCl: 1.78 mg/L Analyzer: FCl: 1.53 m,g/L Effluent Grabs @ 09:49 FCl: 1.49 mg/L TCl: 1.76 mg/L Analyzer: 1.52 mg/L NTU: 0.67 NTU Changed influent and Effluent analyzer buffer and reagents Duty Inactive Equipment OOS: None Facility: OK | Mount Albert Well 3 | 2026-03-02
EAST | March | Under direction of OIC Dan Zhou On site for PM's - Chemical system inspection (silicate) - Supply fans check - Exhaust fans check - Chlorine leak detector test - Dechlorination puck dispenser inspection and cleaning - Chlorine scrubber media sampling - Standby power generator test run - JHSC Health and safety inspection - Deep well exhaust valve check - Turbidity analyzer maintenance and calibration - Chlorine analyzer maintenance - Chlorine scrubber check - Chlorine cylinder emergency repair kit inspection @ 09:17 hrs. informed ROC about PM's @ 09:19 hrs. placed well pump 3 in manual off for PM's Chlorine analyzer maintenance: Influent analyzer: Clean start @ 09:32 hrs. Clean stop @ 09:15 hrs. Post clean verification: Grab @ 12:28 hrs. FCl: 1.42 mg/L Analyzer: FCl: 1.47 mg/L Effluent analyzer: Clean start @ 09:32 hrs. Clean stop @ 09:15 hrs. Post clean verification: Grab @ 12:31 hrs. FCl: 1.47 mg/L Analyzer: FCl: 1.48 mg/L Turbidity meter maintenance and calibration: Clean start @ 09:47 hrs. Clean stop @ 10:05 hrs. Pre clean/calibration NTU: 0.081 Post clean/calibration NTU: 0.058 Chlorine leak detector triggered @ 12:19 hrs. Generator test run: Start Fuel: 882.8 L/ 876.6 L Stop Fuel: 876.7 L/868.4 L Start Hours: 379:33 Stop Hours: 380:45 Start Time: 12:43 hrs. Stop Time (including cool down): 13:58 hrs. Pre run checks; Battery Cell Levels: Ok Battery Terminals and Cables: Ok Oil Level: Ok Coolant Level: Ok Fluid Leaks: NO Coolant Recirculating pump: Ok Faulty Gauges: NO @ 12:43 hrs. Switched ATS to Test for generator power @ 12:55 hrs. Placed generator under facility load Well pump 3 in Manual ON *under load* Operating Current: 41 Amps Operating Frequency: 60.1 Hz Operating Voltage: 605 Volts Engine speed: 1800 RPM Water/coolant Temp: 181 f Oil Pressure: 56 kpa @ 13:47 hrs. placed well pump 3 in manual off for ATS switch @ 13:48 hrs. Toggled ATS to normal @ 13:52 hrs. power switched to station power @ 13:58 hrs. cooldown finished @ 14:17 hrs. returned well pump 3 to auto. | Mount Albert Well 3 | 2026-03-12
EAST | March | Macnamarra fuel inspection | Mount Albert Well 3 | 2026-03-10
EAST | March | Under direction of OIC Dan Zhou On site for; - Station checks - Regulatory sampling, micro (W11637246), manganese sampling (W11638464) Data in PQW Workbook Regulatory samples taken @ 09:32 hrs. @ 08:50 hrs. started well pump3 in manual for sampling Influent Grabs @ 09:33 FCl: 1.68 mg/L Analyzer: FCl: 1.68 m,g/L Effluent Grabs @ 09:32 FCl: 1.66 mg/L TCl: 1.88 mg/L Analyzer: 1.74 mg/L NTU: 0.78 NTU @ 09:48 returned well pump 3 to auto Equipment OOS: None Facility: OK | Mount Albert Well 3 | 2026-03-04
EAST | March | Under direction of OIC Dan Zhou On site for; - Station checks - Turbidity analyzer maintenance Data in PQW Workbook @ 09:20 informed ROC of turbidity analyzer maintenance, placed well pump3 in manual off, no water directed to users Turbidity Analyzer maintenance: Start clean @ 09:33 hrs. Stop clean @ 09:45 hrs. @ 09:45 disregard turbidity out of range alarm, due to improper flow to instrument Influent Grabs @ 09:50 hrs. FCl: 1.61 mg/L Analyzer: FCl: 1.65 m,g/L Effluent Grabs @ 09:52 hrs. FCl: 1.55 mg/L TCl: 1.89 mg/L Analyzer: 1.65 mg/L NTU: 0.50 NTU @ 10:01 hrs. returned well pump 3 to auto Equipment OOS: None Facility: OK | Mount Albert Well 3 | 2026-03-06
EAST | March | Under direction of OIC Dan Zhou On site for; - Station checks - Regulatory sampling, micro (W11656823) Data in PQW Workbook Regulatory samples taken @ 14:36 hrs. Influent Grabs @ 14:36 hrs. FCl: 1.73 mg/L Analyzer: FCl: 1.73 m,g/L Effluent Grabs @ 14:36 hrs. FCl: 1.71 mg/L TCl: 1.96 mg/L Analyzer: FCl: 1.68 mg/L mg/L NTU: 0.078 NTU @ 14:26 hrs. deactivated MTETNL tower duty Equipment OOS: None Facility: OK | Mount Albert Well 3 | 2026-03-11
EAST | March | Under direction of OIC Dan Zhou @ 10:17 hrs. Started well pump 3 in manual on for sampling. | Mount Albert Well 3 | 2026-03-25
EAST | March | Under direction of OIC Dan Zhou On site for; - Station checks - Turbidity analyzer maintenance Data in PQW Workbook Influent Grabs @ 11:03 hrs. (duty active for grabs) FCl: 1.69 mg/L Analyzer: FCl: 1.75 mg/L Effluent Grabs @ 11:06 hrs. FCl: 1.65 mg/L TCl: 1.98 mg/L Analyzer: FCl: 1.68 mg/L NTU: 0.065 NTU Turbidity analyzer maintenance: @ 11:40 hrs. placed well pump 3 in manual off for turbidity analyzer maintenance Start clean @ 11:42 hrs. Stop clean @ 11:55 hrs. Post clean NTU: 0.053 @ 12:08 placed well pump 3 back in auto Duty inactive Equipment OOS: None Facility: OK | Mount Albert Well 3 | 2026-03-20
EAST | March | Under direction of OIC Dan Zhou On site for; - Station checks - Regulatory sampling, micro (W11690092) - Operational sampling, (iron, NTU, FCl, TCl, temp) Data in PQW Workbook Regulatory samples taken @ 10:59 hrs. Influent Grabs @ 10:58 hrs. FCl: 1.85 mg/L Analyzer: FCl: 1.89 mg/L Effluent Grabs @ 10:59 hrs. FCl: 1.66 mg/L TCl: 1.92 mg/L Analyzer: FCl: 1.67 mg/L NTU: 0.072 NTU @ 11:13 placed well pump 3 back in auto Duty inactive Equipment OOS: None Facility: OK | Mount Albert Well 3 | 2026-03-25
EAST | March | @ 09:56 Started well pump 3 in manual on for regulatory sampling. | Mount Albert Well 3 | 2026-03-18
EAST | March | On site to complete chlorine cylinder change. Start: 0.0/64kg Stop: 68/64kg Also completed chlorine system inspection tested vacuum. No leaks detected. Cleared alarms that were from this inspection. Any changes in trends are due to work order being completed. System back to normal. | Mount Albert Well 3 | 2026-03-23
EAST | March | Under direction of OIC Dan Zhou On site for; - Station checks - Chlorine gas system inspection (worked with Phill De Groot) - Silicate system hot water flush and inspection - Chlorine cylinder change (worked with Pill De Groot) - Comprehensive housekeeping Data in PQW Workbook @ 09:36 hrs. informed ROC of chlorine gas system inspection @ 09:36 placed well in auto for gas chlorine system inspection, and silicate system flush Influent Grabs @ 11:16 hrs. FCl: 1.56 mg/L Analyzer: FCl: 1.60 mg/L Effluent Grabs @ 11:18 hrs. FCl: 1.53 mg/L TCl: 1.83 mg/L Analyzer: FCl: 1.61 mg/L NTU: 0.058 NTU @ 11:25 placed well pump 3 back in auto Duty inactive Equipment OOS: None Facility: OK | Mount Albert Well 3 | 2026-03-23
EAST | March | Under direction of OIC Patrick Fobert On site for; - Station checks - Regulatory sampling, micro (W11672709) Data in PQW Workbook Regulatory samples taken @ 11:02 hrs. Influent Grabs @ 10:59 hrs. FCl: 1.68 mg/L Analyzer: FCl: 1.70 mg/L Effluent Grabs @ 11:02 hrs. FCl: 1.62 mg/L TCl: 1.84 mg/L Analyzer: FCl: 1.66 mg/L mg/L NTU: 0.058 NTU @ 11:10 placed well pump 3 back in auto Equipment OOS: None Facility: OK | Mount Albert Well 3 | 2026-03-18
EAST | March | On site with Ernesto hidalgo to work on BAS system. | Mount Albert Well 3 | 2026-03-24
EAST | March | Under direction of OIC Patrick Fobert On site for; - Station checks Data in PQW Workbook Influent Grabs @ 11:41 hrs. FCl: 1.59 mg/L Analyzer: FCl: 1.58 mg/L Effluent Grabs @ 12:57 hrs. FCl: 1.56 mg/L TCl: 1.81 mg/L Analyzer: FCl: 1.59 mg/L NTU: 0.053 NTU Duty inactive Equipment OOS: None Facility: OK | Mount Albert Well 3 | 2026-03-16
EAST | March | Station Check (no issues found) Input data to PWQ 14:10 Verified CL17s (mg/l) Influent Free: Grab 1.54, A 1,52 Effluent Free: Grab 1.48, A 1.50 Effluent Total Grab 1.58 #11696586 Turb maint. Silicate pump #1 performed draw down (ok) and verified no leak Silicate top up (90.7 to 109.4cm) | Mount Albert Well 3 | 2026-03-26
EAST | March | Silicate top up (79.1 to 96.0cm) | Mount Albert Well 3 | 2026-03-19
EAST | March | Under direction of OIC Dan Zhou On site for; - Station checks - Regulatory sampling, micro (W11705406) - Operational sampling, (iron, FCl, TCl, temp, ATP) Data in PQW workbook Regulatory sample taken @ 08:35 hrs. Grabs @ 08:35 hrs. FCl: 1.31 mg/L TCl: 1.57 mg/L Analyzer: FCl: 1.33 mg/L Changed buffer and analyzer reagents. Tower draining for sampling Facility: OK | Mount Albert North Elevated Tank | 2026-03-31
EAST | March | On site to remove extra parts from camlok installation | Mount Albert Well 3 | 2026-03-06
EAST | March | Under direction of OIC Dan Zhou. Initiated deep cycle - Duty 1 band changed to 42-85 %. | Mount Albert North Elevated Tank | 2026-03-09
EAST | March | On site to check station and equipment.? Tower is filling.? 10:51 grab chlorine residual from outlet: FCL= 1.39 mg/l, TCL= 1.64 mg/l.? Analyzer free = 1.37 mg/l.? 10:51 collected micro sample, YD 11637264. And MN sample, W11638464. 10:52 collected in house samples. Replaced CL17 reagents. Reviewed trends, no major concerns. | Mount Albert North Elevated Tank | 2026-03-04
EAST | March | On site to complete station check. Collecting weekly Bac-t Sample. W11656823 Weekly Bac-t Sample. Time: 13:40 Grab (mg/l) Analyzer (mg/l) Free: 1.44 1.37 Total: 1.59 Entered data into PWQ sheet. Verified analyzer with grabs. Checked site and trends. No outstanding alarms on site. No OOS equipment on site. Activated duty at 13:45. | Mount Albert North Elevated Tank | 2026-03-11
EAST | March | Changed tower duty 1 start setpoint to 60 %. | Mount Albert North Elevated Tank | 2026-03-13
EAST | March | Under direction of OIC Patrick Fobert On site for; - Station checks - Regulatory sampling, Micro (W11672709) Regulatory samples taken @ 08:18 hrs. Grabs Talken @ 08:18 hrs. FCl: 1.34 mg/L TCl:1.54 mg/L Analyzer: FCl: 1.37 mg/L Equipment OOS: none Tower Draining Facility OK | Mount Albert North Elevated Tank | 2026-03-18
EAST | March | Under direction of OIC Patrick Fobert On site for PM's; - Portable generator test run - Chlorine analyzer maintenance - JHSC Health and safety inspections - Sump pit system inspection - Heat trace system inspection - Low temp alarm test - Comprehensive cleaning Ran portable generator for 15 mins, no issues observed Sump pit system working Heat trace system operational Low temp alarm triggered @ 10:09 hrs. Chlorine analyzer maintenance: Tower draining, pre grab verification; Grab @ 09:59 hrs. FCl: 1.33 mg/L Analyzer: FCl: 1.36 mg/L Start clean @ 10:03 hrs. Stop clean @ 10:33 hrs. Post clean Analyzer verification: Grab @ 11:02 hrs. FCl: 1.38 mg/L Analyzer: FCl: 1.37 mg/L | Mount Albert North Elevated Tank | 2026-03-19
EAST | March | Attended site for station check Collected grab samples and recorded results and observations in the shared PWQ sheet Station and equipment okay | Stouffville Zone 1 Booster Pumping Station | 2026-03-09
EAST | March | On site to check station and equipment. Pump 2 is running in duty 1. Station readings entered in PWQ sheet. Reviewed trends, no issues. | Stouffville Zone 1 Booster Pumping Station | 2026-03-13
EAST | March | Macnamarra fuel inspection | Stouffville Zone 1 Booster Pumping Station | 2026-03-09
EAST | March | Attended site for station check Collected grabs from the header, 14:13, in mg/L FCl 1.85; TCl 2.01 Inspected pumps, pipes, valves, equipment, all okay. Recorded observations in the shared station PWQ sheet | Stouffville Zone 1 Booster Pumping Station | 2026-03-02
EAST | March | Changed the duty 1 start setpoint from 60% to 40% to deep cycle zone 1 ET. Changed the FCV flow setpoint from 25 to 50 l/s. | Stouffville Zone 1 Booster Pumping Station | 2026-03-26
EAST | March | Under the direction of Patrick Fobert, Worked along side Network Analyst Kevin Wen, to replaced a Network switch to Cisco IE3300 inside PAC panel. ROC is informed and all Well and high lift pumps in ST area were in manual off before commencing the work This included STW3, STW12, STRS48 High Lift pumps, STPSMR Pumps, STPSTL pumps Historian hrbt alarm and Comm fail alarms were triggered Provided 24 VDC power to new switch. There is a trend gap on SCADA between 09:18 AM to 10:30 AM due to this work. After the switch replacement, checked all the ports and reset the comm alarms. New switch model is Cisco IE3300-8T2S. | Stouffville Zone 1 Booster Pumping Station | 2026-03-19
EAST | March | Attended site for generator test run and silicate delivery Received sodium silicate. Levels: Start 20.98 cm Stop 89.37 cm Fuel Start 725 L Stop 692 L Hours Start 516.7 Stop 518.3 Run statistics Current 69.5 A Frequency 60 Hz Power 620 kW Speed 1800 RPM Coolant temp 180 F Exhaust temp 580 F Oil pressure 55 PSI Oil temp 230 F Loaded generator with well 3 and one pump at the pump station Reviewed station trends and checked equipment - okay | Stouffville Zone 1 Booster Pumping Station | 2026-03-17
EAST | March | On site for station check Recorded observations and grabs in the shared PWQ sheet, 10:45 FCl grab 1.78 mg/L TCl grab 1.95 mg/L Station and equipment okay | Stouffville Zone 1 Booster Pumping Station | 2026-03-20
EAST | March | Attended site for preventative maintenance Completed valve exercise Completed housekeeping | Stouffville Zone 1 Booster Pumping Station | 2026-03-24
EAST | March | On site for station check Recorded observations in the shared PWQ sheet Station and equipment okay | Stouffville Zone 1 Booster Pumping Station | 2026-03-23
EAST | March | Attended site for station check Recorded observations in the shared PWQ sheet Station and equipment okay | Stouffville Zone 1 Booster Pumping Station | 2026-03-06
EAST | March | On site to complete station check. Time: 14:08 Influent Total: Grab (mg/l) Analyzer (mg/l) Total: 1.40 1.47 Time: 14:10 SIM Free Grab (mg/l) Analyzer (mg/l) Free: 1.67 1.74 Time: 14:12 Effluent Free Grab (mg/l) Analyzer (mg/l) Free: 1.57 1.56 Time: 14:14 Effluent Total Grab (mg/l) Analyzer (mg/l) Total: 2.28 2.34 verified analyzers with grabs. Checked station and trends. No OOS equipment. No outstanding alarms on site. | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2026-03-30
EAST | March | On site for facility station check and equipment verifications Duty is active - STETTL Level - 60% Pumps 1 and 3 running in duty 1 - 110 L/s Chlorinator #2 dosing at 25%, 37 kg/day, DF = 59%, chlorine booster pump pressure - 245 psi Recorded data in PWQ sheets Verified chlorine analyzer readings: 09:06 to 09:16 (Grab/Analyzer mg/L) Influent TCL: 1.38 / 1.43 Effluent FCL: 1.93 / 1.96 Effluent TCL: 4.40 / 4.34 Sim FCL: 1.64 / 1.69 Reviewed trends, equipment OOS: None Station and equipment okay | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2026-03-31
EAST | March | On site for facility station check and equipment verifications Duty is active - STETTL Level - 85% Pumps 1 and 2 running in D1, 110 L/s flow, Discharge pressure - 725 kpa Chlorinator #1 dosing at 32%, 39 kg/D, cl2 booster pump pressure ~ 245 psi (1690 kpa), DF = 77% Verification of chlorine analyzers @09:30 to 09:40 Grabs / Analyzers (mg/L) Influent TCL: 1.47 / 1.44 Effluent FCL: 1.94 / 1.99 Effluent TCL: 4.66 / 4.60 Simulated FCL: 1.69 / 1.74 No adjustments needed to analyzers Reagent levels ok Equipment OOS: None Reviewed trends, no abnormalities observed Station operation normal | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2026-03-06
EAST | March | On site for facility station check and equipment verifications Duty is active - STETTL Level - 67% Manual stopped pumps @08:58, in order to start diesel generator. Duty rotated pumps - Placed P2 and 3 to D1, placed P1 to D2 Start Hours: 463.3 Start Fuel: 114 / 57 cm / 4817 / 2211 L Started generator @09:02, no issues with power transfer. Started pumps @09:08 to test station under generator power. Collected generator readings @09:35 Stopped pumps @10:30, switched generator back to auto Generator stopped @10:50 Stop Hours: 465.1 Stop Fuel: 4817 / 2216 L No issues with generator run or transfer test - See attached run sheet in Elog attachments for full data Verification of chlorine analyzers @10:35 to @10:43 Grabs / Analyzers (mg/L) Influent TCL: 1.53 / 1.48 Effluent FCL: 1.71 / 1.69 Simulated FCL: 1.77 / 1.69 No adjustments needed to analyzers Changed right bank chlorine cylinders with Jack Palmer - tested for leaks, no issues Reagent levels ok Equipment OOS: None Pumps back in auto @10:50 Reviewed trends, no abnormalities observed Station operation normal | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2026-03-09
EAST | March | On site for monthly maintenance PM's - Chlorine leak detector test, and halogen valve test, all okay - Chlorine scrubber inspection - JHSC Health and safety inspection - Critical air valve flush / inspect - Chlorine emergency kit inspection Alarms cleared, station ok | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2026-03-05
EAST | March | On site for facility station check, and equipment verifications: Duty is active - STETTL Level is 80% Pumps 1 and 2 running in D1 - 110 L/s Chlorinator #1 dosing at 32%, 39 kg/day, booster pump pressure ~ 240 psi Verification of chlorine analyzers from 08:52 to 09:02 (mg/L) Influent TCL: Grab: 1.45 / Analyzer: 1.46 Effluent FCL: Grab: 1.97 / Analyzer: 2.02 Effluent TCL: Grab: 4.71 / Analyzer: 4.67 Sim FCL: Grab: 1.66 / Analyzer: 1.74 No adjustments needed to AITs Deactivated duty @09:06 to allow operator more time to sample the Stouffville wells Reviewed trends, equipment OOS: None Station ok | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2026-03-04
EAST | March | On site for monthly PMs. Informed ROC - Pump #4 (Jockey) monthly maintenance and test run @13:50 - Started pump #4 for monthly test run (Jockey pump) @13:55 - Observed that chlorinator #3 (The chlorinator tied to pump #4 was not dosing. Found that the discharge valve from the chlorinator was closed. Opened valve. Immediately stopped pump #4. @14:00 - Started backflushing to waste, added dechlor pucks to outfall @14:02 - Effluent free chlorine lolo alarm came in (Pumps are already off) @14:07 - Free chlorine residual analyzer is reading 1.86 mg/L. It did not take long to backflush as the jockey pump was only running at 30 L/s for less than 5 minutes. Stopped backflushing @14:10 @14:13 - restarted pump #4 with chlorinator #3 properly dosing now @15:00 - stopped pump #4, left in manual off as per normal Closed valves on chlorinator #3 as they were found before. Will inquire as to why they are closed. Station operation normal | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2026-03-12
EAST | March | On site to check station and equipment. Duty is active upon arrival. 11:40 chlorine residuals on grab/analyzer in mg/l: Influent Total: 1.52/1.48 Effluent Free: 1.97/1.97 Effluent Total: 4.65/4.74 (Standardized according to 3 grabs? average) Sim. Free: 1.70/1.68 Replaced reagents for Influent total and effluent free analyzers. Other station readings are in PWQ sheets. Reviewed trends, Station is under normal operation. Equipment OOS: none. | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2026-03-02
EAST | March | On site to respond to a work order for exhaust fans 6 and 7 tripped. Found both VFDs faulted with some sort of previous under voltage event. Like Could've been caused by a power outage or even a generator test. Pushing the stop button on the VFD keypad reset the fault. | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2026-03-11
EAST | March | On site for station check and equipment verifications Duty is active on arrival - STETTL Level - 64% Pumps 2 and 3 running in Duty, 110 L/s, 690 kpa discharge pressure Chlorinator #1 dosing at 31%, 39 kg/day, DF = 75% Verified chlorine analyzer readings: (Grab/Analyzer mg/L) Influent TCL: 1.53 / 1.48 Effluent FCL: 2.15 / 2.08 Effluent TCL: 4.47 / 4.62 Sim FCL: 1.70 / 1.73 No adjustments needed to analyzers Installed new pressure gauge on pump #3 discharge Reviewed trends, equipment OOS: None Station operation normal | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2026-03-13
EAST | March | Under direction of OIC Dan Zhou On site for; - Diesel receiving Tank 1; Start V: 2987 L Start cm: 73 cm Stop V: 4797 L Stop cm: 113 cm Tank 2; Start V: 2209 L Start cm: 57 cm Stop V: 2209 L Stop cm: 57 cm *note: tank 2 did not equalize or uptake fuel, LIT remained the same on tank. informed team lead Dan Zhou. *note 2: overfill device stopped fueling at 113 cm. Total received: 1832 L | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2026-03-03
EAST | March | On site for station check and equipment verifications Duty is active - STETTL Level - 78% Pumps 2 and 3 running in D1 - 110 L/s Chlorinator #2 dosing at 25 %, 38 kg/day Verified chlorine analyzers with grab residuals (Grab/Analyzer mg/L) @14:30 to 14:40 Influent TCL: 1.55 / 1.49 Effluent FCL: 1.99 / 2.05 Effluent TCL: 4.51 / 4.49 Sim FCL: 1.75 / 1.77 No adjustments needed to analyzers Reviewed trends, equipment OOS: None Station ok | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2026-03-11
EAST | March | On site to check station and equipment. Duty is not active upon arrival. Switched pump duty so that P1 and P3 are in duty 1. P2 = duty 2. Reviewed trends, no issue. Chlorine train 1 is man/off. Further testing will be done next week. | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2026-03-26
EAST | March | On site for station check and equipment verifications Duty is not active - STETTL Level - 62% - Activated system duty @10:05 Pumps 2 and 3 running in Duty, 110 L/s, 692 kpa discharge pressure Chlorinator #1 dosing at 32%, 40 kg/day, DF = 77%, booster pump pressure ~ 240 psi Verified chlorine analyzer readings: (Grab/Analyzer mg/L) @10:25 to 10:37 Influent TCL: 1.52 / 1.46 Effluent FCL: 2.07 / 2.10 Effluent TCL: 4.45 / 4.78 Sim FCL: 1.71 / 1.68 Adjusted effluent TCL analyzer based on grab sample Reviewed trends, equipment OOS: None Station operation normal | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2026-03-16
EAST | March | On site for facility station check and equipment verifications Duty is active - STETTL Level - 70% Pumps 2 and 3 running in D1 - 110 L/s, 694 kpa discharge pressure Chlorinator #1 dosing at 30%, DF = 75%, 38 kg/day, Chlorine booster pump pressure ~240 psi Recorded data in PWQ sheets Verified analyzer readings @12:25 - 12:35 (Grab / analyzer mg/L) Influent TCL: 1.48 / 1.45 Effluent FCL: 2.11 / 2.06 Effluent TCL: 4.40 / 4.51 Sim FCL: 1.73 / 1.68 No adjustments needed to analyzers Reviewed trends, equipment OOS: None Station operation normal | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2026-03-18
EAST | March | Attended site for CMU5 W11749627 effluent and sim free chlorine lo and lo lo. Appears that chlorine cylinder bank 2 regulator failed to open during chlorine bank switchover. Initiated backflush at 11:38, at approximately 24 L/s, following dechlorination protocol. Effluent free chlorine grab collected at 11:48, 0.13 mg/L Replaced chlorine cylinder bank 1 and tested chlorine regulators on bank 1 and 2 Completed backflush at 13:08 for a total of 90 minutes. Estimated water loss is 129.6 cubic meters. Reported water loss in CMU5 W11749627 Verified chlorine analyzers, 13:42, in mg/L Effluent free chlorine - G 1.62; A 1.68 Sim free chlorine - G 1.62; 1.56 Placed station pumps 1-3 back in auto for supervised start up, 13:50 Station and equipment okay | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2026-03-20
EAST | March | Vibration readings | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2026-03-16
EAST | March | On site for station check and equipment verifications: Duty is active - STETTL level 68% Recorded data in PWQ sheets Pumps 2 and 3 running in D1 - 110 L/s, 707 kpa discharge pressure Verified chlorine analyzer readings - no adjustments needed. Tested chlorinator #1 line while running station, observed an audible noise coming from ejector #1. Suspect it may have been the cause of the effluent Lolo lockout yesterday. Left Chlorinator #1 OOS again. Chlorinator #2 is dosing in auto. Reviewed trends, equipment OOS: Chlorinator #1 Station operation okay | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2026-03-25
EAST | March | On site responding to Effluent free chlorine Lolo and Simulated free Lolo alarms CMU5 #W11756650 Arrived on site @19:10. STETTL duty is active - tower level is 60% and floating at duty start. Took grab residuals on effluent Free Chlorine: @19:15 to 19:21 0.07, 0.09, 0.07 mg/L Analyzer reading: 0.04 mg/L 3 grab residuals indicate a free chlorine residual greater than 0.05 mg/L, therefore it is not a reportable incident. Also took grab residual on Simulated free analyzer @19:22 - 0.17 mg/L Free chlorine Started backflushing @19:25 at approximately 23 L/s. Added dechlor pucks to facility outfall. Reviewed trending - Observed that chlorinator #1 was dosing at the time of the incident, the same chlorinator that was running when a similar issue occured on 03/20/2026. Tested chlorinator #1 in local with chlorine booster pump running, and it seems to be functioning normally, vacuum and booster pump pressure are within regular range. Placed chlorinator / booster pump #1 to manual off and disabled duty rotation. Stopped backflushing @20:28 - Effluent free residual is 1.57 mg/L. Total water loss is approx 86.94 m3 after back flushing for 63 minutes. Effluent free residual grabs @20:36 Grabs: 1.76, 1.77 mg/L Analyzer: 1.70 mg/L @20:40 - Cleared alarms, and pumps 2 and 3 started in auto. Chlorinator #2 is dosing in Duty 1 Simulated free chlorine residual analyzer is recovering - reading 0.99 mg/L @21:08 Equipment OOS: Chlorinator #1 / Chlorine booster pump #1 Informed ROC site is back to normal operation Station ok | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2026-03-24
EAST | March | On site for station check and equipment verification, and to complete chlorine analyzer maintenance Tower level - 63%, and duty is not active. Placed pumps to manual off Completed chlorine analyzer maintenance @09:30 to @10:10. Completed on all analyzers, Influent TCL, Effluent FCL / TCL, Sim FCL Verified analyzer readings @10:20 to 10:30 (Grabs/Analyzer mg/L) Influent TCL: 1.45 / 1.47 Effluent FCL: 1.69 / 1.67 Effluent TCL: 2.46 / 2.47 Sim FCL: 1.73 / 1.71 Placed pumps to auto @10:33 - system duty is now active Recorded data in PWQ sheets Reviewed trends, equipment OOS: None Station operation normal | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2026-03-23
EAST | March | Attended site for sampling and station check Sampling MBHP W11656903 Sodium W11722238 Collected samples and verified free chlorine analyzer, 11:22, in mg/L FCl - G 1.69; A 1.64 TCl - G 1.90 Recorded observations in the shared PWQ sheet Station and equipment okay | Stouffville Zone 2 Elevated Tank | 2026-03-11
EAST | March | Attended site for station check and sampling Bac-T: W11705508 ANSCAN: W11705815 Verified free chlorine analyzer and collected samples while draining, 8:30, in mg/L FCl - G 1.63; A 1.64 TCl - G 1.86 Recorded observations in the shared PWQ sheet Station and equipment okay | Stouffville Zone 2 Elevated Tank | 2026-03-31
EAST | March | On site for station check and sampling work orders MBDW - W11637348 HAA - W11692878 ANSCAN - W11637675 Collected samples and verified free chlorine analyzer while draining, 10:43, in mg/L Free chlorine: G 1.62; A 1.63 Total chlorine: G 1.81 Recorded observations in the shared PWQ sheet Station and equipment okay | Stouffville Zone 2 Elevated Tank | 2026-03-04
EAST | March | ROC notified me about sodium exceedance at 11am. March 04, 2026 sample showed 62.3 mg/l sodium. 13:50 Verbal notification to YR Health Connection, Eugenia Huk 1-800-361-5653 x4, case# 4367316. 14:03 Verbal notification to SAC, Julian Aristizabal, AWQI171786. Will complete form 4444E later. | Stouffville Zone 2 Elevated Tank | 2026-03-10
EAST | March | Attended site for preventative maintenance Completed housekeeping Completed chlorine analyzer maintenance Completed lo temp alarm test Completed heat trace inspection Completed sump pit inspection | Stouffville Zone 2 Elevated Tank | 2026-03-24
EAST | March | Under the direction of Patrick Fobert, Worked along side Network Analyst Kevin Wen, to replaced a Network switch to Cisco IE3300 inside NAC panel. ROC is informed and all Well and high lift pumps in ST area were in manual off before commencing the work This included STW3, STW12, STRS48 High Lift pumps, STPSMR Pumps, STPSTL pumps Comm fail alarm was triggered Provided 24 VDC power to new switch. There is a trend gap on SCADA between 10:45 AM to 11:04 AM due to this work. After the switch replacement, checked all the ports and reset the comm alarms. New switch model is Cisco IE3300-8T2S. | Stouffville Zone 2 Elevated Tank | 2026-03-19
EAST | March | On site for sampling W11672797 and station check Collected sample while draining, 9:08, and verified free chlorine analyzer, in mg/L FCl - G 1.58; A 1.57 TCl - G 1.77 Recorded observations in the shared PWQ sheet. Station and equipment okay | Stouffville Zone 2 Elevated Tank | 2026-03-18
EAST | March | On site for station check and sampling W11690172 Collected sample while draining, 11:05, and verified free chlorine analyzer (mg/L) FCl - G 1.64; A 1.64 TCl - 1.76 Replaced chlorine analyzer reagents Recorded observations in the shared PWQ sheet Station and equipment okay | Stouffville Zone 2 Elevated Tank | 2026-03-25
EAST | March | On site for sampling W11637348 and station check Verified free chlorine analyzer and collected samples, 14:07, mg/L FCl G 1.34; A 1.32 TCl G 1.57 Recorded observations in the shared PWQ sheet Station and equipment okay | Stouffville Zone 1 Elevated Tank | 2026-03-04
EAST | March | On site for station check and sampling BacT - W11705508 ANSCAN - W11705815 Collected samples while draining and verified free chlorine analyzer, 14:05, in mg/L FCl - G 1.29; A 1.24 TCl - 1.50 Recorded observations in the shared PWQ sheet Station and equipment okay | Stouffville Zone 1 Elevated Tank | 2026-03-31
EAST | March | On site for station check and sampling W11672797 Collected sample, 14:45, and verified free chlorine analyzer (mg/L) FCl - G 1.40; A 1.43 TCl - G 1.60 Recorded observations in the shared PWQ sheet Station and equipment okay | Stouffville Zone 1 Elevated Tank | 2026-03-18
EAST | March | Under the direction of Patrick Fobert, Worked along side Network Analyst Kevin Wen, to replaced a Network switch to Cisco IE3300 inside NAC panel. ROC is informed and all Well and high lift pumps in ST area were in manual off before commencing the work This included STW3, STW12, STRS48 High Lift pumps, STPSMR Pumps, STPSTL pumps Comm fail alarms was triggered Provided 24 VDC power to new switch. There is a trend gap on SCADA between 09:18 AM to 10:30 AM due to this work. After the switch replacement, checked all the ports and reset the comm alarms. New switch model is Cisco IE3300-8T2S. | Stouffville Zone 1 Elevated Tank | 2026-03-19
EAST | March | On site for station check, and weekly micro sampling (W11705564) Reservoir level - 49% and on drain cycle Recorded station readings in PWQ sheets Verification of chlorine analyzer @10:05 Grab samples (mg/L) North cell: @10:05 FCL: 0.07 TCL: 1.51 South Cell: @10:10 FCL: 0.03 TCL: 1.56 Analyzer reading: 1.53 mg/L - no adjustment needed Collected micro sample @10:12 from North cell Collected in-house operational monitoring samples for ATP and Phosphorus Completed advanced monitoring with SL1000 / Nitrification control monitoring Mono: 1.34 mg/L Free NH: 0.07 mg/L Total NH: 0.34 mg/L NO2: 0.003 mg/L Temp: 3.7 C pH: 8.03 Reviewed trends, equipment OOS: None Station operation normal | Markham PD6 Reservoir | 2026-03-31
EAST | March | On site for station check and sampling W11690172 Collected sample and verified free chlorine analyzer, 13:15, in mg/L FCl - G 1.29; A 1.30 TCl - G 1.50 Replaced free chlorine analyzer reagents Recorded observations in the shared PWQ sheet Reviewed station trends Station and equipment okay | Stouffville Zone 1 Elevated Tank | 2026-03-25
EAST | March | On site for station check, and weekly micro sampling (W11656945) Reservoir level - 51% and on drain cycle Recorded station readings in PWQ sheets Verification of chlorine analyzer @08:50 Grab samples (mg/L) North cell: @08:48 FCL: 0.02 TCL: 1.50 South Cell: @08:53 FCL: 0.03 TCL: 1.56 Analyzer reading: 1.54 mg/L - no adjustment needed Collected micro sample @08:55 from North cell Collected in-house operational monitoring samples for ATP and Phosphorus Completed advanced monitoring with SL1000 / Nitrification control monitoring Mono: 1.27 mg/L Free NH3: 0.07 mg/L Total NH3: 0.32 mg/L NO2: 0.004 mg/L pH: 8.04 Temp: 4.1 C Reviewed trends, equipment OOS: None Station operation normal | Markham PD6 Reservoir | 2026-03-11
EAST | March | On site for monthly maintenance: Informed ROC - High / Low water level alarms test - Reservoir is on a drain cycle, ROC requested Toronto to place their pumps man/off while testing. Tested low alarms @10:13, and high alarms @10:16. Placed all alarm setpoints back to original values after testing - Dehumidifier inspection and test - 2 tonne hoist inspection (3M) Upper Level - Overhead hoist inspection (3M) Lower level - JHSC Health and safety inspection - Building flood alarm test @10:38 - Sump pit inspections - Mainline valves exercises - MV100 to MV600 from 10:45 to 11:40. Ensured there was always a flow path for reservoir draining to system. No issues with valves - External venting screens inspections - Chlorine analyzer maintenance from 11:50 to 12:35 - Cleaned and primed analyzer. Verified analyzer reading after maintenance with grab residual @12:30 Grab: 1.48 mg/L / Analyzer: 1.52 mg/L Alarms cleared, informed ROC, station ok | Markham PD6 Reservoir | 2026-03-05
EAST | March | On site for station check and weekly micro sampling (W11637404) Reservoir level - 60% and draining Reviewed trends - no concerns observed Recorded data in PWQ sheets Grab samples (mg/L) North cell @09:43 FCL: 0.04 TCL: 1.45 South Cell @09:49 FCL: 0.03 TCL: 1.53 Analyzer: 1.51 mg/L Collected micro sample from North cell @09:53 Collected in-house operational monitoring samples for ATP / Phosphorus Advanced Monitoring using SL1000 / Nitrification control monitoring: Mono: 1.21 mg/L Free / Total NH3: 0.10 / 0.34 mg/L NO2: 0.004 mg/L pH: 8.03 Temp: 4.8 C Station operation normal | Markham PD6 Reservoir | 2026-03-04
EAST | March | On site for station check, and weekly micro sampling (W11672839) Reservoir level - 47% and on drain cycle Recorded station readings in PWQ sheets Verification of chlorine analyzer @08:45 Grab samples (mg/L) North cell: @08:45 FCL: 0.03 TCL: 1.48 South Cell: @08:49 FCL: 0.02 TCL: 1.53 Analyzer reading: 1.51 mg/L - no adjustment needed Collected micro sample @08:52 from North cell Collected in-house operational monitoring samples for ATP and Phosphorus Completed advanced monitoring with SL1000 / Nitrification control monitoring Mono: 1.25 mg/L Free NH3: 0.10 mg/L Total NH3: 0.35 mg/L NO2: 0.00 mg/L Temp: 4.5 C Reviewed trends, equipment OOS: None Station operation normal | Markham PD6 Reservoir | 2026-03-18
EAST | March | Under direction of OIC Joe Mazza. Notified ROC of the work. Performed battery maintenance on UPS in the PAC panel. Charged new batteries and tested drawdown. Applied new service sticker. No operations affected by this work. | Markham PD6 Reservoir | 2026-03-17
EAST | March | On site for station check, and weekly micro sampling (W11690214) Reservoir level - 43% and on drain cycle Recorded station readings in PWQ sheets Verification of chlorine analyzer @09:40 Grab samples (mg/L) North cell: @09:43 FCL: 0.06 TCL: 1.48 South Cell: @09:40 FCL: 0.05 TCL: 1.60 Analyzer reading: 1.52 mg/L - no adjustment needed Collected micro sample @09:45 from North cell Collected in-house operational monitoring samples for ATP and Phosphorus Completed advanced monitoring with SL1000 / Nitrification control monitoring Mono: 1.31 mg/L NO2: 0.003 mg/L Temp: 3.8 C pH: 8.06 Reviewed trends, equipment OOS: None Station operation normal | Markham PD6 Reservoir | 2026-03-25
CENTRAL | March | This is an entry for March/29/2026. Received call from ROC at 08:07 about filter 2 back wash interlocked and OOS. When signed into SCADA found that both filter 1 and 2 were going to have a backwash at the same time. Also found that low lift pump 3 was having un-commanded stops, so put pump 3 to manual off at 08:24. Filter 2 will not be able to do its backwash till the backwash tank level drops down low enough for it to start. Will inform ROC of what is happening. | Keswick Water Treatment Plant | 2026-03-30
CENTRAL | March | Completed filter performance check: filter 1- 100%, filter 2- 100% | Keswick Water Treatment Plant | 2026-03-31
CENTRAL | March | -Performed station check - logged station readings into PWQ sheet Grab: free=1.71mg/L total=1.98mg/L@12:00 Analyzer: free=1.69mg/L total=1.90mg/L -Changed low lift free reagents - OK -Collected weekly BacT sample YD #W11705592, weekly algae sample YD #W11705322, monthly THM sample YD #W11705294 & GLIP sample -Calibrated low lift pH probe due to high pH | Keswick Water Treatment Plant | 2026-03-31
CENTRAL | March | 11:11 remote Filter performance check. Both filters are at 100% performance. No issues found. | Keswick Water Treatment Plant | 2026-03-04
CENTRAL | March | Received call from ROC regarding low CL2 influent. Plant not running. Checked trends, looks like CL2 influent has been slowly dropping over the past run cycle, now currently reading 1.09mg/l and triggering low alarm. Initiated Backwash on Filter #1 as it was getting close to backwash, this way, can draw down clearwell and refill with higher chlorinated water. Increased Post CL2 dosage factor from 142% to 155%. Influent increased to 1.20mg/l while filter was draining for backwash. Will inform Central crew this morning, may look at increasing PACL dosage due to increased raw turbidity and will monitor/adjust POST CL2 dosage depending on influent CL2 levels. | Keswick Water Treatment Plant | 2026-03-12
CENTRAL | March | Remotely reviewed filter performance. Both filters 100% and ok. No issues found. | Keswick Water Treatment Plant | 2026-03-05
CENTRAL | March | Onsite to receive chlorine cylinder delivery. Lo influent chlorine alarm triggered with analyzer reading 1.09 mg/l. Raw turbidity readings erratic. Found raw water analyzer flow too low and corrected. Tested post injection chlorine system as duty started and found no issues with regulator or chlorinators. 14:45 Took influent clear well grab: 1.35. Analyzer 1.31 and climbing. No issues found. | Keswick Water Treatment Plant | 2026-03-12
CENTRAL | March | Filter performance reviewed, both 100% | Keswick Water Treatment Plant | 2026-03-13
CENTRAL | March | filter performance checked, both 100% | Keswick Water Treatment Plant | 2026-03-03
CENTRAL | March | -Performed station check - logged station readings into PWQ sheet -Checked CL17 reagents - OK -Performed filter performance review - 100% | Keswick Water Treatment Plant | 2026-03-13
CENTRAL | March | Reviewed filter performance both 100% | Keswick Water Treatment Plant | 2026-03-11
CENTRAL | March | -Collected GAC sample -Changed chlorine cylinder -Put filter back to service - refilled filter 1 to 35cm - set high wash time from 420s to 180 and backwashed filter 1 to re-stratify media - during sampling, there is sample to turbidimeter which caused a high turbidimeter reading=0.465NTU and filter 1's effluent valve was always closed - after backwashing, run filter to waste until turbidity came below 0.1NTU | Keswick Water Treatment Plant | 2026-03-10
CENTRAL | March | Under direction of OIC (Ben H) Station and equipment check Completed labs, no issues Plant not running during readings Filter performance review via scada both F1 and F2 100% Ops normal | Keswick Water Treatment Plant | 2026-03-02
CENTRAL | March | Test backflow preventer Passed | Keswick Water Treatment Plant | 2026-03-02
CENTRAL | March | Onsite to look for CO2 leak, found 2 small leaks within the CO2 valve cabinet. Checked filter performance both filters 100% | Keswick Water Treatment Plant | 2026-03-02
CENTRAL | March | -Performed station check - logged station readings into PWQ sheet -Checked CL17 reagents - OK -Reviewed filter performance -Collected weekly BacT sample YD #W11656973 & GLIP samples -Responded lolo CO2 adjusted pH - reviewed trends and noticed pH drop was correlated to water temperature - increased sample flow to temp probe | Keswick Water Treatment Plant | 2026-03-11
CENTRAL | March | -Performed station check - logged station readings into PWQ sheet Grab: free=1.65mg/L total=1.97mg/L@11:40 Analyzer: free=1.66mg/L total=2.03mg/L -Checked CL17 reagents - OK -Collected weekly BacT sample YD #W11637432, monthly sample YD #W11637633, 11637162, & GLIP samples | Keswick Water Treatment Plant | 2026-03-04
CENTRAL | March | Under direction of oic (Ben H) onsite to complete monthly maximo workorders Change chlorine cylinder with JZ (Post chlorination right side) Station ops normal | Keswick Water Treatment Plant | 2026-03-05
CENTRAL | March | Informed TL Ben Hess of changes made to Chlorine and PACL setpoints. Was recommended by Ben to increase Settling tank valve open waste time from 2 minutes back to 4 minutes. Made that adjustment. Adjusted Pre chlorine dosing from 82 to 86%. | Keswick Water Treatment Plant | 2026-03-12
CENTRAL | March | 11:30 reviewed filter performance. Both filters 100%. No issues found. | Keswick Water Treatment Plant | 2026-03-06
CENTRAL | March | Under direction of oic (Ben H), onsite to complete station check PLant not running at time of check Took grabs from treated @ 10:10 am Total: 1.98 mg/l Free: 1.75 mg/l All other readings on PD sheets Topped up PACL day tank Chemicals/reagents ok Informed ROC (Angelica C) With the assistance of Ben H performed manual backwash of filter 1, leaving drained and OOS for media sampling tomorrow | Keswick Water Treatment Plant | 2026-03-09
CENTRAL | March | Attended SCADA in response to a call from RO Christian Van Beek regarding a CO2 dosing interruption, filter 1 and 2 low level and low settled water conduit level. Checked raw water pH, and low lift pumps. Monitored filter and conduit level top up. Reset all alarms. Achieving desired filter turbidity. Station and equipment okay. Back in normal operation. | Keswick Water Treatment Plant | 2026-03-05
CENTRAL | March | Received call from ROC for High Settling Water turbidity. Plant running at the time. Logged into SCADA, settled water turbidity increasing as well as raw turbidity. Could be due to increased flooding/runoff from rain. Monitored Filter effluent turbidity, head loss and runtime. No issues, filter turbidity below 0.100ntu. Able to filter out higher turbidity. Will keep plant running as duty shut off will be soon. | Keswick Water Treatment Plant | 2026-03-11
CENTRAL | March | Checked filter performance, both 100% | Keswick Water Treatment Plant | 2026-03-16
CENTRAL | March | Checked filter performance both 100% | Keswick Water Treatment Plant | 2026-03-17
CENTRAL | March | Completed filter performance check: filter 1- 100%, filter 2- 100% | Keswick Water Treatment Plant | 2026-03-25
CENTRAL | March | -Received CO2 delivery -Adjusted raw sample flow -Decreased post chlorine dosage from 155 to 150 and PACL dosage from 15mg/L to 14mg/L due to improved raw water quality | Keswick Water Treatment Plant | 2026-03-24
CENTRAL | March | Attending site to check low flow to Raw Water Turbidimeter (W11761664). Replaced flow sensor. Checked existing sensor and found rubber debris blocking flow sensor impeller. ROC was notified before and after maintenance activities. | Keswick Water Treatment Plant | 2026-03-26
CENTRAL | March | -Lowered post chlorine dosage from 150 to 145 due to high clearwell influent free -Performed station check - logged station readings into PWQ sheet -Checked CL17 reagents - OK -Collected weekly BacT sample YD #W11690242 | Keswick Water Treatment Plant | 2026-03-25
CENTRAL | March | 07:34 Remotely reviewed turbidity performance. Both filters at 100%. No issues found. | Keswick Water Treatment Plant | 2026-03-24
CENTRAL | March | -Responded PACL P1 & Low Lift P3 uncommand stop - PACL P1 & Low Lift P3 restarted in auto duty 1 as of 1530 - reviewed trends - PACL day tank level is reclining & low lift flow meter is reading @ 70L/s - Both PACL P1 & Low Lift P3 were running normally in this cycle - I was assuming a power blip caused the uncommand stop alarm since the two alarm came in at the same time | Keswick Water Treatment Plant | 2026-03-17
CENTRAL | March | ROC called for fluoride residual lolo while plant is running. Instructed ROC to switch fluoride duty and monitor. | Keswick Water Treatment Plant | 2026-03-16
CENTRAL | March | 12:05 completed filter turbidity performance review remotely. Both filters at 100%. No issues found. | Keswick Water Treatment Plant | 2026-03-18
CENTRAL | March | Completed filter performance check: filter 1- 100%, filter 2- 100% | Keswick Water Treatment Plant | 2026-03-26
CENTRAL | March | #NAME? | Keswick Water Treatment Plant | 2026-03-23
CENTRAL | March | 15:04 Remotely reviewed filter turbidity performance. Both filters running at 100%. No issues found. | Keswick Water Treatment Plant | 2026-03-23
CENTRAL | March | Check drip oiler Cleaned drip oiler wiped dry and clean re installed and filled | Keswick Water Treatment Plant | 2026-03-20
CENTRAL | March | -Tested high lift pump 2's flow control valve -Performed station check - logged station readings into PWQ sheet -Checked CL17 reagents - OK | Keswick Water Treatment Plant | 2026-03-27
CENTRAL | March | Under direction of oic JZ, station and equipment check Take weekly bacT sample and grabs @ 11:40 am (plant running) Treated Total: 1.98 mg/l Treated Free: 1.70 mg/l All other readings on PD sheets Topped up chemicals as needed Completed monthly maximo workorders Informed ROC (Christian V) of ongoings CL2 Leak alarm test complete Analyzer (fluoride) maintenance complete, verified grabs (PD sheets) Ops normal | Keswick Water Treatment Plant | 2026-03-18
CENTRAL | March | -Performed station check - logged station readings into PWQ sheet -Changed chlorine cylinder -Changed clear well free reagents -Low lift turbidimeter fault alarm outstanding - flow sensor faulted - A CMP already in - I will email instrumentation team again today | Keswick Water Treatment Plant | 2026-03-20
CENTRAL | March | Completed filter performance check: filter 1- 100%, filter 2- 100% | Keswick Water Treatment Plant | 2026-03-27
CENTRAL | March | 09:00 remotely checked Filter turbidity performance. Both filters at 100%. No issues found. | Keswick Water Treatment Plant | 2026-03-20
CENTRAL | March | 10:26 completed filter turbidity performance review remotely. Both filters at 100%. No issues fou | Keswick Water Treatment Plant | 2026-03-19
CENTRAL | March | Attending site to check flow sensor on Raw Water Turbidimeter (W11726557). Flowmeter was fouled and replaced. ROC was notified before and after maintenance activities. Associated alarms were cleared. | Keswick Water Treatment Plant | 2026-03-23
CENTRAL | March | Under direction of OIC completed station check and labs Topped up all chemicals Troubleshoot fluoride pump, (air locked) Adjusted flow to RAW turbidimeter, was reading false too high Change chlorine cylinder w/ JZ (pre) Completed maximo workorders OPs normal | Keswick Water Treatment Plant | 2026-03-16
EAST | March | On site to complete station check. Collecting weekly Bac-t Sample. Collecting VOC Samples. W11706392 Weekly Bac-t Sample. W11706364 VOC Samples. Time: 10:00 Grab (mg/l) Analyzer (mg/l) Free: 1.18 1.13 Total: 1.49 Entered data into PWQ sheet. Verified analyzer on site with grabs. Checked site and trends. No OOS equipment on site. No outstanding alarms. CL-17 reagents have been changed on site. | Sutton Elevated Tank | 2026-03-31
CENTRAL | March | -Performed station check - logged station readings into PWQ sheet -Changed filter top free reagents | Keswick Water Treatment Plant | 2026-03-06
CENTRAL | March | Reviewed filter performance both 100% | Keswick Water Treatment Plant | 2026-03-12
CENTRAL | March | Remotely reviewed fitter performance. Both filters are 100%. Filter 1 placed oos for media sampling. Adjusted flow from 80 to 40 L/s. | Keswick Water Treatment Plant | 2026-03-09
CENTRAL | March | 08:42 Remote filter turbidity performance review. Both filters at 100%. Filter 1 is oos and drained for media sampling. No issues found. | Keswick Water Treatment Plant | 2026-03-10
CENTRAL | March | Increased PACL dosage from 12 to 15mg/l due to high settling tank and raw turbidity. Reduced flow rate in filters from 40L/S to 30L/S and High Lift flow rate from 80L/S to 60L/S. Will continue to monitor plant operation. | Keswick Water Treatment Plant | 2026-03-14
CENTRAL | March | Under direction of oic Ben H onsite to complete monthly maximo workorders Informed ROC (Christian V) of ongoings New diesel generator test run on building power Start Hours: 43 hrs 48 min Stop Hours: 45 hrs 9 min With plant "off" Settled water analyzer and turbidimeter cleaned @ 10:00 am Cleaned Filter 1 and 2 Turbidimeters @ 10:30 am Cleaned Raw water analyzers and turbidimeter @ 11:30 am Cleaned Clearwell analyzer @ 1:00 pm ack/reset all alarms and placed plant back to auto Ops normal | Keswick Water Treatment Plant | 2026-03-03
EAST | March | On site to complete station check. Collecting weekly Bac-t Sample. Collecting monthly VOC Samples. W11638376 Weekly Bac-t Sample. W11638348 Monthly VOC Samples. Time: 08:35 Grab (mg/l) Analyzer (mg/l) Free: 1.29 1.24 Total: 1.60 Verified analyzer on site. No outstanding alarms on site. No OOS equipment on site. Entered data into PWQ sheet. | Sutton Elevated Tank | 2026-03-04
EAST | March | On site to complete following work orders: W11635386 JHSC Inspection W11654557 Chlorine Analyzer Maintenance W11656475 Inlet/Outlet Heat Trace Insp. W11656484 Sump Pit System Inspection. W11656497 Low Temp Alarm Test W11660678 Cleaning W11656718 Portable Gas Generator Test Verifying chlorine analyzer with grabs after completing maintenance. Time: 10:25 Grab (mg/l) Analyzer (mg/l) Free: 1.30 1.25 Calibrated chlorine pocket colorimetre it passed. No issues with analyzer maintenance. No issues with work orders on site. Any changes in trends are due to work orders being completed. | Sutton Elevated Tank | 2026-03-03
EAST | March | On site to complete station check. Collecting weekly Bac-t Sample. W11673527 Weekly Bac-t Sample. Time: 08:36 Grab (mg/l) Analyzer (mg/l) Free: 1.27 1.20 Total: 1.52 Verified analyzer with grabs. Checked site and trends. No outstanding alarms on site. No OOS equipment. | Sutton Elevated Tank | 2026-03-18
EAST | March | On site to complete station check. Collecting weekly Bac-t Sample. W11657667 Weekly Bac-t Sample. Time: Grab (mg/l) Analyzer (mg/l) Free: Total: At 08:50 shut down Sutton ET duty tower is currently at 8.32m duty shuts down at 8.50m. Verified analyzer with grabs. Entered data into PWQ sheet. Checked site and trends. No outstanding alarms on site. No OOS equipment on site. | Sutton Elevated Tank | 2026-03-11
EAST | March | On site to complete station check. Collecting weekly Bac-t Sample. W11690826 Weekly Bac-t Sample. Time: 09:10 Grab (mg/l) Analyzer (mg/l) Free: 1.23 1.16 Total: 1.52 Verified analyzer with grabs all ol. No outstanding alarms on site. No OOS equipment on site. Entered data into PWQ sheet. | Sutton Elevated Tank | 2026-03-25
EAST | March | Deactivate Sutton PRV duty to stagger duty activation together with plant duty. Plant duty is off right now and KSTKWP = 62%. | Sutton Elevated Tank | 2026-03-25
EAST | March | Deactivated Sutton PRV duty in order to test re-chlor logic at KSETDP. Re-activated duty. | Sutton Elevated Tank | 2026-03-25
EAST | March | On site for station check/analyzer verification and to verify the function of CL2 Dosing system. 09:45hrs: Adjusted Pre-Injection Cl2 Analyzer Free from 1.36mg/l to 1.53mg/l based on multiple Cl2 grab residuals. 09:55hrs: Adjusted Post-Injection Cl2 Analyzer Free from 1.40mg/l to 1.71mg/l based on multiple Cl2 grab residuals. 10:10hrs: Adjusted Outlet Cl2 Analyzer Free from 1.40mg/l to 1.71mg/l based on multiple Cl2 grab residuals. Activated GWTP @ 10:15hrs to observe Chlorine dosing system. Conducted zero point calibration on Pre-Injection and Post injection Cl2 Analyzers due to drifting when inlet flow was registering. Informed ROC of the work and to disregard chlorination alarms during this time. Conducted additional CL2 grab residuals to ensure accuracy of the CL2 Analyzers. Adjusted Chlorine dosing target setpoint from 1.80mg/l to 1.50mg/l. Monitored Chlorination system while tower was filling, did not see any issues, system seems to be dosing accurately. Will continue to monitor. | Keswick Deer Park Elevated Tank | 2026-03-30
EAST | March | On site to complete station check. Collecting weekly Bac-t sample. Collecting VOC sample. Time: 10:45 Pre-injection Grab (mg/l) Analyzer (mg/l) Free: 1.60 1.67 Time: 10:48 Post-injection Grab (mg/l) Analyzer (mg/l) Free: 1.64 1.71 Total: 1.91 1.83 Time: 10:55 Outlet Grab (mg/l) Analyzer (mg/l) Free: 1.55 1.60 Total: 1.95 2.00 Verified analyzers on site with grabs. Checked site and trends. Entered data into PWQ sheet. No OOS equipment on site. No outstanding alarms on site. | Keswick Deer Park Elevated Tank | 2026-03-31
EAST | March | Repair leak on chlorine injection line | Keswick Deer Park Elevated Tank | 2026-03-05
EAST | March | Back on site to verify the post and pre-injection analyzers with grabs. Time: 12:39 Pre-Injection Grab (mg/l) Analyzer (mg/l) Free: 0.38 0.39 Time: 12:43 Post-Injection Grab (mg/l) Analyzer (mg/l) Free: 0.35 0.33 Total: 0.65 0.59 Verified analyzers with grabs. Analyzers are reading correctly on site. All valves inside the valve gallery are reading in the correct position. At 13:02 started opening the drain valve on the inlet riser to bring up the Pre and Post-injection readings. Taking grabs to verify Pre and Post Injection readings. Time: 13:18 Post Injection Grab (mg/l) Analyzer (mg/l) Free: 1.11 1.16 Total: 1.45 1.75-1.45 Time: 13:21 Pre Injection Grab (mg/l) Analyzer (mg/l) Free: 0.50 0.53 After multiple grabs adjusted the post injection total from a 1.75mg/l to a 1.45mg/l at 13:18. Closed the inlet drain at 13:22. Wasted 9.6m3 sodium thiosulphate was at the outfall. Called Joe Mazza at 13:24 to activate duty at the GWTP to make sure the altitude valve here on site will open. Altitude valve is operating normally and opening with duty active. Analyzers are reading correctly on site. Time: 13:55 Pre Injection Grab (mg/l) Analyzer (mg/l) Free: 0.95 1.37-0.95After multiple grabs adjusted the pre injection free from a 1.37mg/l to a 0.95mg/l at 13:57. Time: 14:06 Post Injection Grab (mg/l) Analyzer (mg/l) Free: 1.02 1.13-1.02 Total: 1.30. 1.50-1.30 after multiple grabs adjusted the post injection free from 1.13mg/l to 1.02mg/l. Also adjusted the total from a 1.50mg/l to a 1.30mg/l at 14:07 Time: 14:10 Outlet Grab (mg/l) Analyzer (mg/l) Free: 1.01 0.98 Total: 1.30 1.36 Before leaving site analyzers have been checked and adjusted properly while on the fill cycle. | Keswick Deer Park Elevated Tank | 2026-03-02
EAST | March | On site for station check. Collected Cl2 grab residuals on: Inlet tap: FCL: 1.01mg/l Analyzer FCL: 1.03mg/l TCL: 1.35mg/l Analyzer TCL: 1.41mg/l Outlet tap: FCL: 0.96mg/l Analyzer FCL: 1.38mg/l TCL: 0.98mg/l Analyzer TCL: 1.42mg/l Checked station readings, verified Cl2 analyzer. All information in PWQ sheet. Equipment out of service: None. | Keswick Deer Park Elevated Tank | 2026-03-13
EAST | March | 9:44 On site to assist Chris I and Tyler S to isolate and inlet pipe in order to modify the chlorine injection line. Tower is on a draining cycle. 11:20 maintenance needs parts for the injection line. Reopened inlet pipe. Rechlor system remains isolated and OOS. | Keswick Deer Park Elevated Tank | 2026-03-12
EAST | March | On site to complete station check. Collecting Weekly Bac-t Sample. Collecting VOC Samples. Collecting Q1 Samples. W11638390 Weekly Bac-t Sample W11638362 VOC Samples. W11673942 Q1 Samples. Time: 09:50 Pre Injection Grab (mg/l) Analyzer (mg/l) Free: 1.31 1.26 Time: 09:53 Post Injection Grab (mg/l) Analyzer (mg/l) Free: 1.29 1.36 Total: 1.76 1.75 Time: 09:55 Outlet Grab (mg/l) Analyzer (mg/l) Free: 0.84 0.85 Total: 1.27 1.21 Verified analyzers on site. Checked station and trends. No outstanding alarms. No OOS equipment. | Keswick Deer Park Elevated Tank | 2026-03-04
EAST | March | On site to see if ET can go on line. Will be flushing the water to waste to see if residual will come up. Sodium thiosulphate is in place for wasting. Started flushing to waste at 09:30 at 11L/s. Taking grab sample to verify analyzer is reading correctly. Time: 09:35 Outlet Grab (mg/l) Analyzer (mg/l) Free: 0.96 1.00 Total: 1.35 1.36 After taking grabs the tower can be put online. Flushed 9.9m3 to waste. Outlet is fully open on both the riser and the main. Tightened down the packing for the drain valve to stop the leaking from happening. Taking one last grab before leaving site. Time: 10:10 Outlet Grab (mg/l) Analyzer (mg/l) Free: 1.05 1.00 Total: 1.36 1.48 After multiple grabs were taken adjusted the total analyzer on the outlet from a 1.48mg/l to a 1.36mg/l at 10:16. Due to the fact that the boost has not been tested yet. The alarms for the post-injection can be disregarded. | Keswick Deer Park Elevated Tank | 2026-03-02
EAST | March | Deactivated alarm for post-injection combined chlorine residual LOLO Alarm. | Keswick Deer Park Elevated Tank | 2026-03-02
EAST | March | On site to complete station check. On site to commission chlorine system. Time: 09:30 Pre Injection Grab (mg/l) Analyzer (mg/l) Free: 1.19 1.14 Time: 09:32 Post Injection Grab (mg/l) Analyzer (mg/l) Free: 1.29 1.21 Total: 1.68 1.74 Time: 09:35 Outlet Grab (mg/l) Analyzer (mg/l) Free: 0.94 1.02 Total: 1.41 1.48 Verified analyzers with grabs all ok. Checked site and trends. Entered data into PWQ sheet. No outstanding alarms. Chlorine system OOS work being done on it to bring it back on line. At 10:00 called ROC about work being completed on site. After testing chlorine injection point system with the booster pump. Found it to be unsafe team lead will be creating a work order for maintenance to redo the chlorine injection system. Alarms have been cleared. | Keswick Deer Park Elevated Tank | 2026-03-06
EAST | March | On site to test the booster pumps and chlorine system to see if it is ready to come online. After opening the valves and testing the booster pump found a leak on the 1 1/2? line. Informed team lead and work order is being created for maintenance to take a look. | Keswick Deer Park Elevated Tank | 2026-03-03
EAST | March | On site to complete station check. Time: 10:50 Pre Injection Grab (mg/l) Analyzer (mg/l) Free: 1.21 1.21 Time: 10:55 Post Injection Grab (mg/l) Analyzer (mg/l) Free: 1.26 1.21 Total: 1.69 1.66 Time: 11:00 Outlet Grab (mg/l) Analyzer (mg/l) Free: 1.01 1.02 Total: 1.49 1.54 Verified analyzers with grabs. No outstanding alarms on site. No OOS equipment on site. Checked station and trends. Entered data into PWQ sheet. | Keswick Deer Park Elevated Tank | 2026-03-09
EAST | March | On site to complete station check. Collecting weekly Bac-t Sample. W11673541 Weekly Bac-t Sample. Time: 09:46 Pre Injection Grab (mg/l) Analyzer (mg/l) Free: 1.17 1.04-1.17 After multiple grabs were taken adjusted the Pre Injection from a 1.04mg/l to 1.17mg/l at 09:47 Time: 09:50 Post Injection Grab (mg/l) Analyzer (mg/l) Free: 1.02 1.04 Total: 1.52 1.44 Time: 09:53 Outlet Grab (mg/l) Analyzer (mg/l) Free: 1.01 0.95 Total: 1.32 1.31 Verified analyzers with grabs. Checked station and trends. Chlorine system OOS due to PCS work needing to be done. No outstanding alarms. Entered data into PWQ sheet. | Keswick Deer Park Elevated Tank | 2026-03-18
EAST | March | On site to complete station check. Time: 10:45 Pre Injection Grab (mg/l) Analyzer (mg/l) Free: 1.18. 1.15 Time: 11:00 Post Injection Grab (mg/l) Analyzer (mg/l) Free: 1.16 1.14 Total: 1.73 2.16-1.73 after multiple grabs adjusted the treated total from a 2.16mg/l to a 1.73mg/l at 11:31. Time: 11:30 Outlet Grab (mg/l) Analyzer (mg/l) Free: 1.14 1.44 -1.14 Total: 1.60 1.65 After multiple grabs adjusted the treated free on the outlet analyzer from 1.44mg/l to 1.14mg/l at 11:35. Verified analyzers with grabs. Cleared outstanding hihi total alarm on post chlorine analyzer. No OOS equipment on site. Electrician Dan Boate on site to confirm heat trace system is working correctly. | Keswick Deer Park Elevated Tank | 2026-03-26
EAST | March | On site to complete station check. Time: 10:40 Pre Injection Grab (mg/l) Analyzer (mg/l) Free: 1.00 0.94 Time: 10:42 Post Injection Grab (mg/l) Analyzer (mg/l) Free: 0.97 1.04 Total: 1.36 1.31 Time: 10:50 Outlet Grab (mg/l) Analyzer (mg/l) Free: 0.91 0.91 Total: 1.35 1.30 Verified analyzers with grabs all ok. No outstanding alarms on site. Entered data into PWQ sheet. Checked site and trends. Chlorine system currently OOS until it is tested properly. | Keswick Deer Park Elevated Tank | 2026-03-16
EAST | March | On site to test and verify proper operation of heat trace system. | Keswick Deer Park Elevated Tank | 2026-03-26
EAST | March | Made following changes with in training with Chris Scott: Chlorinator 1 and 2 dose factor to 100%. Chlorine setpoint from 1.5 to 1.8 mg/l Loop update rate from 60s to 180s. | Keswick Deer Park Elevated Tank | 2026-03-27
EAST | March | On site to complete station check. Completing following work orders: Portable generator test, JHSC inspection. Time: 11:30 Pre Injection Grab (mg/l) Analyzer (mg/l) Free: 1.40 1.32 Time: 11:35 Post Injection Grab (mg/l) Analyzer (mg/l) Free: 1.23 1.22 Total: 1.50 1.54 Time: 11:42 Outlet Grab (mg/l) Analyzer (mg/l) Free: 1.16 1.15 Total: 1.41 1.47 Verified analyzers with grabs all ok. Checked site and trends. No outstanding alarms on site. Chlorine system currently OOS due to commissioning issues. Entered data into PWQ sheet. | Keswick Deer Park Elevated Tank | 2026-03-23
EAST | March | On site to complete chlorine system commissioning with PCS. Opening up all valves for the chlorine booster pump and putting pump into auto. Chlorine system is currently in auto and ready for test. All alarms due to chlorine are due to the testing that is taking place. Activated duty at 09:50. Joe Mazza on site to help with troubleshooting chlorine system. Was able to get system activated and tested. Chlorine system is now online set points have been adjusted accordingly. Loop Update rate: 31sec to 60sec Automatic dosing step value: 2% to 1% Any changes in trends are due to work being done on chlorine system. All alarms have been activated for chlorine system and any alarms that came in were due to chlorine system commissioning. | Keswick Deer Park Elevated Tank | 2026-03-24
EAST | March | On site to work with PCS on the rechlorination system at the tower to make sure the dosing logic is working. At 09:45 informed ROC that work was going to be completed on the chlorine system. At 09:51 activated duty to start work. Was not able to complete chlorine commissioning due to instrumentation at the treatment plant needing the plant off to complete their calibrations. Will reschedule this to another day. Chlorination system has been put to manual off till the work can be completed. | Keswick Deer Park Elevated Tank | 2026-03-20
EAST | March | On site to complete station check. Collecting weekly Bac-t Sample. W11690840 Weekly Bac-t Sample. Time: 10:13 Pre Injection Grab (mg/l) Analyzer (mg/l) Free: 1.50 1.45 Time: 10:16 Post Injection Grab (mg/l) Analyzer (mg/l) Free: 1.27 1.30 Total: 1.88 1.32 after multiple grabs were taken adjusted the post injection total from 1.32mg/l to 1.88mg/l at 10:20. Time: 10:25 Outlet Grab (mg/l) Analyzer (mg/l) Free: 1.21 1.26 Total: 1.52 1.53 Also while on site troubleshooting chlorine dosing points to make sure everything is linear with each other. Verified analyzers with grabs. No outstanding alarms on site. No OOS equipment on site. Entered data into PWQ sheet. Tested the chlorination system to see if it is all linear and after testing everything is good and dosing properly. | Keswick Deer Park Elevated Tank | 2026-03-25
EAST | March | On site to complete station check. Collecting weekly Bac-t Sample. W11657681 Weekly Bac-t Sample. Time: 09:52 Pre Injection Grab (mg/l) Analyzer (mg/l) Free: 1.05 0.98 Time: 09:55 Post Injection Grab (mg/l) Analyzer (mg/l) Free: 0.96 0.98 Total: 1.38 1.31 Time: 10:03 Outlet Grab (mg/l) Analyzer (mg/l) Free: 0.88 0.80 Total: 1.36 1.32 Checked station and found heat tracer for the inlet/outlet off and not working, checked breaker a couple times and found it still not to be working. Will make a work order for electricians to check it out. Checked trends. No outstanding alarms on site. Entered data into PWQ sheet. | Keswick Deer Park Elevated Tank | 2026-03-11
CENTRAL | March | -Performed station check - logged station readings into PWQ sheet -Checked CL17 reagents - OK | Keswick West Park Reservoir | 2026-03-13
CENTRAL | March | -Finished the following work orders *Chemical system inspection *CL17 analyzer maintenance *H&S inspection -Performed station check - logged station readings into PWQ sheet -Checked CL17 reagents - OK | Keswick West Park Reservoir | 2026-03-10
CENTRAL | March | -Performed station check - logged station readings into PWQ sheet -Checked CL17 reagents - OK | Keswick West Park Reservoir | 2026-03-06
CENTRAL | March | Station and equipment check Take weekly BacT sample W11657912 and grabs @ 8:05 am (draining) Total: 1.80 mg/l Free: 1.44 mg/l Analyzer Total: 1.79 mg/l Analyzer Free: 1.46!mg/l No adjustments required Chemicals/reagents ok Ops ok | Keswick West Park Reservoir | 2026-03-11
CENTRAL | March | -Performed station check - logged station readings into PWQ sheet Grab: free=1.39mg/L total=1.71mg/L@8:45 Analyzer: free=1.44mg/L total=1.78mg/L -Checked CL17 reagents - OK -Collected weeky BacT sample YD #W11638785 & monthly sample YD #W11638771 | Keswick West Park Reservoir | 2026-03-04
CENTRAL | March | *Test run portable generator | Keswick West Park Reservoir | 2026-03-17
CENTRAL | March | -Tested chlorine leak alarm -Performed station check - logged station readings into PWQ sheet -Checked CL17 reagents - OK | Keswick West Park Reservoir | 2026-03-23
CENTRAL | March | Station and equipment check Take weekly BacT sample W11673668 and grabs @ 8:10 am (draining) Total: 1.74 mg/l Free: 1.41 mg/l Chemicals/reagents ok Ops normal | Keswick West Park Reservoir | 2026-03-18
CENTRAL | March | -Performed station check - logged station readings into PWQ sheet -Changed treated total reagents | Keswick West Park Reservoir | 2026-03-20
CENTRAL | March | -Performed station check - logged station readings into PWQ sheet -Checked CL17 reagents - OK | Keswick West Park Reservoir | 2026-03-16
CENTRAL | March | -Performed station check - logged station readings into PWQ sheet -Changed treated free reagents | Keswick West Park Reservoir | 2026-03-27
CENTRAL | March | Station and equipment check Take weekly BacT sample W11690908 @ 8:00 am Total: 1.60 mg/l Free: 1.28 mg/l (Draining) Chemicals/reagents ok Ops normal | Keswick West Park Reservoir | 2026-03-25
CENTRAL | March | Station and equipment check Took grabs @ 2:50 pm Total: 1.78 mg/l Free: 1.50 mg/l No adjustments to analyzers needed Chemicals/reagents ok Ops normal | Keswick West Park Reservoir | 2026-03-02
EAST | March | Under Direction of OIC Dan Zhou On site for; - Station checks - Regulatory sampling, micro, (W11705392) - Operational sampling (iron, FCl, TCl, Temp, ATP) Data in PWQ workbook Regulatory sample taken @ 12:32 hrs. Grabs Taken @ 12:32 hrs. Grab FCl: 1.25 mg/L Grab TCl: 1.43 mg/L Analyzer: FCl: 1.27 mg/L Tower draining Facility: OK | Musselman's Lake Elevated Tank | 2026-03-31
EAST | March | Under Direction of OIC Dan Zhou On site for; - Station checks - Regulatory sampling, micro, (W11656809) Data in PWQ workbook Regulatory sample taken @ 11:57 Grabs Taken @ 11:57 hrs. Grab FCl: 1.36 mg/L Grab TCl: 1.56 mg/L Analyzer: FCl: 1.32 mg/L Changed AIT buffer and indicator reagents. Tower draining Facility: OK | Musselman's Lake Elevated Tank | 2026-03-11
EAST | March | Under Direction of OIC Dan Zhou On site for; - Station checks - Regulatory sampling, micro, (W11690078) Data in PWQ workbook Regulatory sample taken @ 11:55 hrs. Grabs Taken @ 11:55 hrs. Grab FCl: 1.27 mg/L Grab TCl: 1.48 mg/L Analyzer: FCl: 1.27 mg/L Tower draining Facility: OK | Musselman's Lake Elevated Tank | 2026-03-25
EAST | March | Under direction of OIC Patrick Fobert On site for PM's; - Chlorine analyzer maintenance - Heat trace system inspection - Sump pit system inspection - Comprehensive cleaning - Manual valve exercise - JHSC health and safety inspection - Portable generator test Pre chlorine analyzer grab verification: Grab @ 12:08 hrs. FCl: 1.29 mg/L Analyzer: FCl: 1.29 mg/L Chlorine analyzer maintenance: Clean start @ 12:10 hrs. Clean Stop @ 12:43 hrs. Post clean verification Grab @ 13:01 FCl: 1.30 mg/L Analyzer: FCl: 1.28 mg/L Heat trace system operational Low temp alarm manually triggered @ 12:37 hrs. Portable gas generator for 20 mins. No observed issues. | Musselman's Lake Elevated Tank | 2026-03-19
EAST | March | Under Direction of OIC Patrick Fobert On site for; - Station checks - Regulatory sampling, micro, (W11672695) Data in PWQ workbook Regulatory sample taken @ 12:00 hrs. Grabs Taken @ 12:00 hrs. Grab FCl: 1.27 mg/L Grab TCl: 1.50 mg/L Analyzer: FCl: 1.28 mg/L Tower draining Facility: OK | Musselman's Lake Elevated Tank | 2026-03-18
EAST | March | On site to check station and equipment.? Tower is filling.? 14:05 grab chlorine residual from outlet: F = 1.59 mg/l, T= 1.78 mg/l.? Analyzer free= 1.58 mg/l. 14:05 collected micro sample, YD W11637232 15:06 collected in house samples.? CL17 reagents are at 50%? 14:18 opened the drain for 2 minutes to verify the outfall pipes. It's draining. Reviewed trends. No issue.? | Musselman's Lake Elevated Tank | 2026-03-04
EAST | March | On site to complete station check. Collecting Weekly Bac-t sample. Collecting VOC sample. Time: 12:00 Header Grab (mg/l) Analyzer (mg/l) Free: 1.32 1.28 Total: 1.60 1.68 Time: 12:05 Inlet Grab (mg/l) Analyzer (mg/l) Free: 1.65 1.29-1.65 Total: 2.00 2.08 At 12:05 adjusted the inlet free from 1.29mg/l to 1.65mg/l after multiple grabs were taken. Time: 12:10 Outlet Grab (mg/l) Analyzer (mg/l) Free: 1.34 1.40 Total: 1.75 1.76 Entered data into PWQ sheet. Verified analyzers with grabs. Checked site and trends. Cleared outstanding alarms. No OOS equipment on site. | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2026-03-31
EAST | March | On site to complete station check. Time: 10:05 Header Grab (mg/l) Analyzer (mg/l) Free: 1.45 1.49 Total: 1.70 1.76 Time: 10:10 Inlet Grab (mg/l) Analyzer (mg/l) Free: 1.41 1.39 Total: 1.85 1.86 Time: 10:13 Outlet Grab (mg/l) Analyzer (mg/l) Free: 1.39 1.39 Total: 1.75 1.71 Verified analyzers with grabs. No outstanding alarms on site. No OOS equipment on site. Checked station and trends. Entered data into the PWQ sheet. | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2026-03-09
EAST | March | On site for station check. Collected Cl2 grab residuals on: Header tap: FCL: 1.34mg/l Analyzer FCL: 1.40mg/l TCL: 1.70mg/l Analyzer TCL: 1.67mg/l Inlet tap: FCL: 1.72mg/l Analyzer FCL: 1.72mg/l TCL: 1.71mg/l Analyzer TCL: 1.71mg/l Outlet tap: FCL: 1.36mg/l Analyzer FCL: 1.29mg/l TCL: 1.67mg/l Analyzer TCL: 1.62mg/l Checked station readings, verified Cl2 analyzer. All information in PWQ sheet. Equipment out of service: None. | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2026-03-13
EAST | March | On site to complete following work orders: W11636028 Inlet/Outlet Heat Trace Inspection. W11634972 Circulation Pump Test W11635323 Standby Power Generator Test W11660858 Housekeeping W11635084 Chlorine Gas Detectors Test W11635455 JHSC Inspection W11636037 Chlorine Analyzer Maintenance W11636277 Ventilation System Inspection W11636374 Actuated Valve Exercise/Inspection W11636387 Dehumidifier Cleaning and Inspection W11636782 Chlorine Scrubber Check W11638272 Chemical System Inspection Leaving site to assist maintenance at Deer Park will be back on site. Back on site to complete some more work orders. caused lo free alarms on all analyzers. verifying analyzers with grabs Time: 13:25 Header Grab (mg/l) Analyzer (mg/l) Free: 1.51 1.51 Total: 1.82 1.84 Time: 13:30 Inlet Grab (mg/l) Analyzer (mg/l) Free: 1.53 1.70-1.53 Total: 1.90 1.89 after multiple grabs were taken adjusted the inlet free from a 1.70mg/l to a 1.53mg/l at 13:32. Time: 13:40 Outlet Grab (mg/l) Analyzer (mg/l) Free: 1.43 1.60-1.43 Total: 1.78 1.79 after multiple grabs adjusted the outlet free analyzer reading from a 1.60mg/l to a 1.43mg/l, at 13:40. Pocket colorimeter passed calibration test with vials. Tried to run generator on site still causing issues. will inform team lead and team tomorrow morning including on call operator tonight. Was not able to complete the chemical system inspection, or the chlorine gas detector test. will come back to site to do that. Any changes in trends or alarms created were due to work orders being completed. | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2026-03-05
EAST | March | On site to complete station check. Time: 11:50 Header Grab (mg/l) Analyzer (mg/l) Free: 1.44. 1.40 Total: 1.78 1.85 Time: 11:57 Inlet Grab (mg/l) Analyzer (mg/l) Free: 1.42 1.66-1.42 Total: 1.73 1.76 Time: 12:00 Outlet Grab (mg/l) Analyzer (mg/l) Free: 1.48 1.52 Total: 1.77 1.80 After taking multiple grabs adjusted the inlet free analyzer from a 1.66mg/l to a 1.42mg/l at 11:57 No outstanding alarms on site. No OOS equipment on site. Checked site and trends. | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2026-03-02
EAST | March | On site to complete station check. Collecting weekly Bac-t Sample. W11657681 Weekly Bac-t Sample. Time: 11:07 Header Grab (mg/l) Analyzer (mg/l) Free: 1.42 1.42 Total: 1.71 1.70 Time: 11:11 Inlet Grab (mg/l) Analyzer (mg/l) Free: 1.40. 1.11-1.40 Total: 1.67 1.72 Time: 11:15 Outlet Grab (mg/l) Analyzer (mg/l) Free: 1.30 1.35 Total: 1.66 1.64 At 11:11 adjusted the inlet free after multiple grabs from 1.11mg/l to 1.40mg/l. Checked site and trends. No outstanding alarms on site. No OOS equipment on site. Entered data into PWQ sheet. | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2026-03-11
EAST | March | On site to complete station check. Collecting weekly Bac-t Sample. Collecting VOC Samples. W11638390 Weekly Bac-t Sample. W11638362 VOC Samples. Time: 10:48 Header Grab (mg/l) Analyzer (mg/l) Free: 1.51 1.54 Total: 1.90 1.92 Time: 10:50 Inlet Grab (mg/l) Analyzer (mg/l) Free: 1.56 1.47 Total: 1.82 1.83 Time: 10:55 Outlet Grab (mg/l) Analyzer (mg/l) Free: 1.57 1.63 Total: 1.77 1.76 Verified analyzers with grabs all ok. Checked station and trends. Entered data into PWQ sheet. No outstanding alarms on site. No OOS equipment. | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2026-03-04
EAST | March | On site to complete station check. Time: 08:15 Header Grab (mg/l) Analyzer (mg/l) Free: 1.46 1.46 Total: 1.74 1.79 Time: 08:18 Inlet Grab (mg/l) Analyzer (mg/l) Free: 1.51 1.45 Total: 1.78 1.79 Time: 08:22 Outlet Grab (mg/l) Analyzer (mg/l) Free: 1.37 1.37 Total: 1.73 1.74 Verified analyzers with grabs all ok. Checked station and trends. No outstanding alarms on site. No OOS equipment on site. | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2026-03-06
EAST | March | On site to complete station check. Time: 09:20 Header Grab (mg/l) Analyzer (mg/l) Free: 1.41 1.44 Total: 1.72 1.72 Time: 09:25 Inlet Grab (mg/l) Analyzer (mg/l) Free: 1.39 1.36 Total: 1.74 1.67 Time: 09:28 Outlet Grab (mg/l) Analyzer (mg/l) Free: 1.38 1.32 Total: 1.75 1.67 Verified analyzers with grabs all ok. Checked site and trends. Making work order for the portable generator issues here on site. Entered data into PWQ sheet. No outstanding alarms on site. No OOS equipment. | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2026-03-16
EAST | March | On site to complete station check. Collecting weekly Bac-t Sample. W11690840 Weekly Bac-t Sample. Time: 11:41 Header Grab (mg/l) Analyzer (mg/l) Free: 1.24. 1.37-1.24 Total: 1.58 1.63 After multiple grabs adjusted the header free residual from a 1.37mg/l to a 1.24mg/l at 11:42. Time: 11:45 Inlet Grab (mg/l) Analyzer (mg/l) Free: 1.31 1.11-1.31 Total: 1.66 1.75 After multiple grabs were taken adjusted the inlet free from a 1.11mg/l to a 1.31mg/l at 11:46 Time: 11:50 Outlet Grab (mg/l) Analyzer (mg/l) Free: 1.27 1.25 Total: 1.58 1.60 Verified analyzers. Checked station and trends. No outstanding alarms on site. No OOS equipment. Entered data into PWQ sheet. | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2026-03-25
EAST | March | On site to complete station check. Completing following work order. Chlorine gas emergency test. Time: 12:28 Header Grab (mg/l) Analyzer (mg/l) Free: 1.31 1.34 Total: 1.66 1.62 Time: 12:30 Inlet Grab (mg/l) Analyzer (mg/l) Free: 1.38 1.68-1.38 Total: 1.66 1.69 After multiple grabs adjusted the inlet free residual reading from a 1.68mg/l to a 1.38mg/l at 12:31. Time: 12:35 Outlet Grab (mg/l) Analyzer (mg/l) Free: 1.26 1.23 Total: 1.64 1.58 Verified analyzers with grabs. Checked station and trends. Completed work order with out issue. Cleared alarms associated with work order at 12:37. No OOS equipment on site. Entered data into PWQ sheet. | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2026-03-23
EAST | March | On its to complete station check. Time: 09:46 Header Grab (mg/l) Analyzer (mg/l) Free: 1.36 1.33 Total: 1.70 1.76 Time: 09:50 Inlet Grab (mg/l) Analyzer (mg/l) Free: 1.53 1.89-1.53 Total: 1.88 1.97 After multiple grabs adjusted the inlet free from a 1.89mg/l to a 1.53mg/l at 09:52. Time: 09:57 Outlet Grab (mg/l) Analyzer (mg/l) Free: 1.27 1.30 Total: 1.70 1.72 Verified analyzers with grabs. Checked station and trends. No OOS equipment on site. No outstanding alarms on site. Entered data into PWQ. | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2026-03-26
EAST | March | Test backflow preventer Passed | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2026-03-02
EAST | March | Chris Iliohan Tyler Smith. Picked up Honda generator for repairs. Left a working generator (non electric start) onsite until we can get this one working | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2026-03-19
EAST | March | On site to complete station check. Time: 13:30 Grab (mg/l) Analyzer (mg/l) Free: 0.07 0.02 Total: 1.40 1.32 Checked station and trends. No OOS equipment on site. No outstanding alarms on site. Verified analyzer with grabs. | Markham Pumping Station | 2026-03-30
EAST | March | On site to complete station check. Collecting weekly Bac-t Sample. W11673541 Weekly Bac-t Sample. Time: 10:32 Header Grab (mg/l) Analyzer (mg/l) Free: 1.36 1.37 Total: 1.61 1.69 Time: 10:40 Inlet Grab (mg/l) Analyzer (mg/l) Free: 1.37 1.44 Total: 1.67 1.55-1.67 After multiple grabs adjusted the treated total inlet analyzer from a 1.55mg/l to 1.67mg/l at 10:43. Time: 10:45 Outlet Grab (mg/l) Analyzer (mg/l) Free: 1.31 1.27 Total: 1.70 1.65 Verified analyzers with grabs. Checked station and trends. No outstanding alarms on site. No OOS equipment. Entered data into PWQ sheet. | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2026-03-18
EAST | March | On site with Total Power for generator annual PM. In able to load test as water pump is leaking. | Markham Pumping Station | 2026-03-10
EAST | March | On site to check station and equipment. Requested ROC to exercise each pump for 15 minutes earlier. P2 is running upon arrival by ROC. 12:50 chlorine residuals grab/analyzer in mg/l: Total: 1.31/1.31 Free: 0.03/0.02 Other station readings are in PWQ sheets. Reviewed trends, Station is under normal operation. Equipment OOS: none. | Markham Pumping Station | 2026-03-02
EAST | March | On site for facility station check and equipment verifications All pumps in manual off as per normal operation Verified analyzer readings: @10:30 Grab free: 0.05 / Analyzer: 0.01 mg/L Grab total: 1.40 / Analyzer: 1.32 mg/L Reviewed trends, equipment ok Station operation normal | Markham Pumping Station | 2026-03-06
EAST | March | On site for station check and equipment verifications Remotely started pump #2 in manual @10:44 for station check Pump #2 running - 370 L/s, 496 kpa discharge pressure Recorded data in PWQ sheets Verified analyzer readings @11:08 Grab free: 0.05 / Analyzer: 0.02 mg/L Grab total: 1.29 / Analyzer: 1.30 mg/L No adjustments needed Reviewed trends Equipment OOS: None Station operation normal | Markham Pumping Station | 2026-03-16
EAST | March | Station Check (no issues found) Input data to PWQ 12:30 Verified Depolox (mg/l) Free: Grab 0.05, A 0.02 Total: Grab 1.31, A 1.36 | Markham Pumping Station | 2026-03-20
EAST | March | On site for station check and weekly micro sampling (W11705564) Tower level - 68% and draining Recorded data in PWQ sheets Verified analyzer readings with grab chlorine residuals @13:15 Grab free: 0.03 mg/L / Analyzer: 0.00 mg/L Grab total: 1.55 mg/L / Analyzer: 1.57 mg/L Collected micro sample @13:20 Advanced monitoring using SL1000 / Nitrification control monitoring Mono: 1.40 mg/L Free NH3: 0.06 mg/L Total NH3: 0.33 mg/L NO2: 0.004 mg/L pH: 8.01 Temp: 4.1 C Reviewed trends Station operation normal | Markham Milliken Elevated Tank | 2026-03-31
EAST | March | On site for station check, equipment verifications, and to complete monthly PMs - JHSC Health and safety inspection - Flood alarm test - Dehumidifier inspection and cleaning - Ventilation system inspection - Diesel Generator test run and hours log Pre checks: Oil level: Ok Coolant Level: Ok Coolant Recirc Pump: Ok Fluid Leaks: Ok Battery Terminals / Cables: Ok Battery Cell Levels: N/A Start Hours: 591.2 (Started @10:50) Start Fuel: 97.6 / 97.8 cm (541/542 L) Ran Pump #1 during generator run Data While Generator running: AMPs: 202 / 199 / 199 amps Voltage: 600 V Frequency: 59.9 hz Engine Speed: 1798 RPMs Oil Temp: 197 F Oil Pressure: 61 psi Coolant Temp: 183 F Exhaust: 672 / 691 F Stop Hours: 592.4 (Stopped @12:06) Stop Fuel: 93.4 / 93.2 cm (518 / 517 L) No issues with test or power transfer Verified chlorine analyzer readings: @13:00 Grab FCL: 0.02 mg/L / Analyzer: 0.01 mg/L Grab TCL: 1.29 mg/L / Analyzer: 1.31 mg/L Reviewed trends, equipment ok Recorded readings in PWQ sheets Station operation normal | Markham Pumping Station | 2026-03-12
EAST | March | On site for station check and weekly micro sampling (W11637404) Tower level - 82% and filling Recorded station readings in PWQ sheets Verified analyzer readings with grab residuals @12:20 Grab/ Analyzer (mg/L) FCL: 0.04 / 0.00 TCL: 1.65 / 1.65 No adjustments needed Collected micro sample @12:24 Collected in-house operational monitoring samples for ATP and phosphorus Advanced monitoring using SL1000 / Nitrification control monitoring: Mono: 1.44 mg/L Free / Total NH3: 0.07 / 0.35 mg/L NO2: 0.004 mg/L pH: 8.00 Temp: 4.3 C Reviewed trends, equipment OOS: None Station okay | Markham Milliken Elevated Tank | 2026-03-04
EAST | March | On site for station check and weekly micro sampling (W11690214) Tower level - 54% and draining Recorded data in PWQ sheets Verified analyzer readings with grab chlorine residuals @11:59 Grab free: 0.08 mg/L / Analyzer: 0.00 mg/L Grab total: 1.65 mg/L / Analyzer: 1.63 mg/L Collected micro sample @12:03 Advanced monitoring using SL1000 / Nitrification control monitoring Mono: 1.41 mg/L Free NH3: 0.06 mg/L Total NH3: 0.35 mg/L NO2: 0.004 mg/L pH: 8.02 Temp: 3.9 C Reviewed trends Station operation normal | Markham Milliken Elevated Tank | 2026-03-25
EAST | March | On site for station check and weekly micro sampling (W11672839) Tower level - 68% and filling Recorded data in PWQ sheets Verified analyzer readings with grab chlorine residuals @10:51 Grab free: 0.02 mg/L / Analyzer: 0.00 mg/L Grab total: 1.62 mg/L / Analyzer: 1.62 mg/L Collected micro sample @10:55 Collected in-house operational sampling for ATP and phosphorus Advanced monitoring using SL1000 / Nitrification control monitoring Mono: 1.40 mg/L Free NH3: 0.03 mg/L Total NH3: 0.31 mg/L NO2: 0.003 mg/L pH: 8.04 Temp: 3.9 C Reviewed trends, equipment ok Station operation normal | Markham Milliken Elevated Tank | 2026-03-18
EAST | March | On site for station check and weekly micro sampling (W11705564) Reservoir level - 54% and draining (West cell only) East cell is OOS for capital projects Recorded data in PWQ sheets Verified analyzer readings with grab chlorine residuals: @11:00 Grab Free: 0.06 mg/L / Analyzer: 0.03 mg/L Grab total: 1.42 mg/L / Analyzer: 1.42 mg/L Collected micro sample from west cell @11:12 Collected in-house operational samples for ATP and phosphorus Advanced monitoring using SL1000 / nitrification control monitoring: Mono: 1.20 mg/L Free NH3: 0.07 mg/L Total NH3: 0.31 mg/L NO2: 0.004 mg/L pH: 8.05 Temp: 7.1 C Reviewed trends Equipment OOS: East Reservoir cell for capital projects | Markham PD5 Reservoir | 2026-03-31
EAST | March | On site for station check and weekly micro sampling (W11656945) Tower level - 79% and filling Recorded data in PWQ sheets Verified analyzer readings with grab chlorine residuals @11:20 Grab free: 0.04 mg/L / Analyzer: 0.01 mg/L Grab total: 1.70 mg/L / Analyzer: 1.69 mg/L Collected micro sample @11:25 Collected in-house operational sampling for ATP and phosphorus Advanced monitoring using SL1000 / Nitrification control monitoring Mono: 1.48 mg/L Free NH3: 0.05 mg/L Total NH3: 0.34 mg/L NO2: 0.003 mg/L pH: 8.04 Temp: 4.3 C Completed the following PMs: - Chlorine analyzer maintenance: See above for grabs verifications. No issues - Actuated valve exercise from 11:51 to 11:56. Tower was filling, called ROC to request metro to turn off PD6s pumps while exercising the valve. Called ROC back to tell Metro they can resume normal operations - Manual valves exercise - ran the tower draining through the bypass line while testing the mainline actuated valve - JHSC health and safety inspection - Dehumidifier inspection and test - Low temperature alarm test - Inlet / Outlet heat trace system inspection - Sump pit inspection - Level transmitter flush and inspection Equipment all back to auto Reviewed trends Station operation normal | Markham Milliken Elevated Tank | 2026-03-11
EAST | March | On site for station check and weekly micro sampling (W11637404) Reservoir level is 48% - East cell is OOS for capital upgrades Contractors on site interior and exterior for capital projects Verification of chlorine analyzer: @10:50 West Cell grabs / analyzers: FCL: 0.08 mg/L / 0.03 mg/L TCL: 1.37 mg/L / 1.40 mg/L Collected sample @10:55 from west cell Collected advanced operational monitoring samples @10:55 for ATP and phosphorus Advanced monitoring with SL1000 / Nitrification control monitoring Mono: 1.16 mg/L Free / Total NH3: 0.10 / 0.33 mg/L NO2: 0.004 mg/L pH: 8.02 Temp: 6.4 C Reviewed trends, equipment OOS: East cell Station operation ok | Markham PD5 Reservoir | 2026-03-04
EAST | March | On site for station check and weekly micro sampling (W11690214) Reservoir level - 54% and draining (West cell only) East cell is OOS for capital projects Recorded data in PWQ sheets Verified analyzer readings with grab chlorine residuals: @10:30 Grab Free: 0.02 mg/L / Analyzer: 0.01 mg/L Grab total: 1.37 mg/L / Analyzer: 1.31 mg/L Collected micro sample from west cell @10:35 Collected in-house operational samples for ATP and phosphorus Advanced monitoring using SL1000 / nitrification control monitoring: Mono: 1.19 mg/L Free NH3: 0.08 mg/L Total NH3: 0.32 mg/L NO2: 0.004 mg/L pH: 8.03 Temp: 6.6 C Free Chlorine fault alarm was generated during sampling, analyzer faulted due to not enough flow with sample tap running. Cleared alarm, no further issues Reviewed trends Equipment OOS: East Reservoir cell for capital projects | Markham PD5 Reservoir | 2026-03-25
EAST | March | On site for station check and weekly micro sampling (W11656945) Outstanding Free Chlorine analyzer fault alarm from 09:02. Checked analyzer, no issues observed. Contractor informed that the analyzer tubing was leaking, likely bumped by a contractor working, which caused the fault, they rectified the issue. Alarm cleared on SCADA Reservoir level - 64% and draining (West cell only) East cell is OOS for capital projects Recorded data in PWQ sheets Verified analyzer readings with grab chlorine residuals: @09:35 Grab Free: 0.07 mg/L / Analyzer: 0.02 mg/L Grab total: 1.44 mg/L / Analyzer: 1.48 mg/L Collected micro sample from west cell @09:42 Collected in-house operational samples for ATP and phosphorus Advanced monitoring using SL1000 / nitrification control monitoring: Mono: 1.23 mg/L Free NH3: 0.07 mg/L Total NH3: 0.32 mg/L NO2: 0.003 mg/L pH: 8.04 Temp: 6.5 C Completed the following PMs: - JHSC Health and safety inspection - Chlorine analyzer maintenance - see grabs above for verifications - External venting system inspection - High / Low water level alarms test Reviewed trends Equipment OOS: East Reservoir cell for capital projects Station operation normal | Markham PD5 Reservoir | 2026-03-11
EAST | March | On site to respond chlorine fault alarm. The analyzer drain line was pinched at the door and air locked as a result. Informed Jeff B (site super for contractor). Reinstate the drain line. 11:22 chlorine residual from west cell. Grab free = 0.04 analyzer free = 0.01 Grab total = 1.44 analyzer total = 1. Building low temp outstanding. Adjusted low temp sensor to 4 degree C. Reset alarms. No outstanding alarms. East cell remains offline and OOS. | Markham PD5 Reservoir | 2026-03-26
EAST | March | On site for station check and weekly micro sampling (W11672839) Reservoir level - 61% and filling (West cell only) East cell is OOS for capital projects. Contractors on site. Recorded data in PWQ sheets Verified analyzer readings with grab chlorine residuals: @09:45 Grab Free: 0.03 mg/L / Analyzer: 0.00 mg/L Grab total: 1.38 mg/L / Analyzer: 1.35 mg/L Collected micro sample from west cell @09:50 Collected in-house operational samples for ATP and phosphorus Advanced monitoring using SL1000 / nitrification control monitoring: Mono: 1.21 mg/L Free NH3: 0.04 mg/L Total NH3: 0.28 mg/L NO2: 0.004 mg/L pH: 8.03 Temp: 6.6 C Free Chlorine fault alarm was generated during sampling, analyzer faulted due to not enough flow with sample tap running. Cleared alarm, no further issues Entered East Cell (OOS) Restricted space. Contractors also on site. Inspected leakage from interconnect valve, the leakage is the same / similar amount to the previous inspection by Ops. Reviewed trends Equipment OOS: East Reservoir cell for capital projects Station ok | Markham PD5 Reservoir | 2026-03-18
EAST | March | On site for station check and Bac-T sampling W11705508 Collected raw and treated samples, verified analyzers, 11:15, in mg/L Influent FCl - G 2.50; A 2.47 Effluent FCl - G 2.40; A 2.53 Effluent TCl - G 2.80 Recorded observations in the shared PWQ sheet Station and equipment okay | Stouffville Well 3 | 2026-03-31
EAST | March | On site for sampling W11656903 and station check Collected raw and treated samples, 10:45, and verified chlorine analyzers, in mg/L Influent FCl - G 2.54; A 2.51 Effluent FCl - G 2.58; A 2.48 Adjusted to match average of grabs Effluent TCl - G 2.80 Recorded observations in the shared PWQ sheet Station and equipment okay | Stouffville Well 3 | 2026-03-11
EAST | March | Attended site for station check Replaced eyewash station water Verified chlorine analyzers. Recorded observations in the shared PWQ sheet Station and equipment okay | Stouffville Well 3 | 2026-03-30
EAST | March | Attended site for CMU5 W11769468 influent and effluent free low and low low lockout Grabs, 8:15, in mg/L Effluent FCl: 0.35; Analyzer 0.32 Effluent TCl: 0.45 Replaced influent and effluent free chlorine CL17 analyzer reagents and primed Acknowledged alarms and placed well in local off to prevent unwanted start up Initiated backflush, following dechlorination protocol, 8:19 Completed backflush, 9:04 Found stuck regulator on chlorine cylinder 1 that failed to open on chlorine bank transfer. Manually opened regulator Verified chlorine analyzers after backflush, 9:07, in mg/L Influent FCl - G 1.26; A 1.23 Effluent FCl - G 1.57; A 1.56 Effluent TCl - G 1.78 Placed well manual on, 9:09, for supervised start up | Stouffville Well 3 | 2026-03-31
EAST | March | Attended site for preventative maintenance Changed chlorine cylinder bank 2 with Travis Wyatt Completed Chlorine analyzer cleaning Turbidimeter cleaning Silicate pump and line flush Chlorine system inspection Silicate pump inspection Isolated well from distribution and depressurized to hot flush silicate lines. Primed and reset PSV on chemical board. Backflushed well with dechlorination pucks in catch to purge excess silicate from priming the lines Test ran the well while on site and rotated silicate pumps to ensure proper operation Station and equipment okay | Stouffville Well 3 | 2026-03-10
EAST | March | On site for station check Inspected chlorine and silicate systems Reviewed station trends Checked pump and process piping Recorded observations and analyzer verification in the shared PWQ sheet Station and equipment okay | Stouffville Well 3 | 2026-03-06
EAST | March | On site for station check Verified chlorine analyzers, 13:26, in mg/L Influent FCl G 2.56; A 2.48 Effluent FCl G 2.44; A 2.46 Effluent TCl G 2.72 Reviewed SCADA and station trends Checked station and equipment Inspected chlorine and silicate system Recorded observations in the shared PWQ sheet Station and equipment okay | Stouffville Well 3 | 2026-03-02
EAST | March | On site to check station and equipment. Well 3 is man/on since Zone 1 ET is filling. 13:23 chlorine grab residual / analyzer in mg/l: Influent free: 2.48 / 2.55 Effluent free: 2.54 / 2.58 Effluent total: 2.64 Reviewed trends. No issue. Chlorinator 2 is OOS and isolated from the system. | Stouffville Well 3 | 2026-03-13
EAST | March | Attended site for chlorine cylinder change with Patrick Fobert Changed chlorine cylinder bank 1, tested and inspected chlorine system | Stouffville Well 3 | 2026-03-24
EAST | March | Onsite to perform annual maintenance/Rebuild chlorinators #2. Informed ROC and Jack onsite isolated gas cylinders and purged the lines. Tested halogen system, confirmed operation as intended. We rebuilt both the chlorinators. Connected both the chlorinators back to hard PVC chlorine line. performed vacuum test. No leak found. Performed gas calibration and Performed verification and Put both chlorinators back in service. All the related alarms were cleared. No issues. Back flushed well for five minute duration under the direction of OIC Jack Palmer, following dechlorination protocol and he started the well remotely. Monitored for while. No issues. Informed ROC, armed the building and left the site. | Stouffville Well 3 | 2026-03-18
EAST | March | Attended site for station check and silicate line flush, pump maintenance and inspection Isolated and depressurized station header for work Hot water flushed silicate pumps 1 and 2 into common injection point from suction side Disassembled and rebuilt silicate pump 1 suction and discharge check valves on pump head Cleaned and flushed PSV and PRVs on chemical board, set to 450 and 625 kPa respectively Primed silicate pumps and line to injection point Re-pressurized station header and backflushed excess silicate, dechlorinating at catch basin Test ran well in manual, cycling silicate pump duty while supervised on site Station and equipment okay | Stouffville Well 3 | 2026-03-26
EAST | March | Under the direction of Patrick Fobert, Worked along side Network Analyst Kevin Wen, to replaced a Network switch to Cisco IE3300 inside PAC panel. ROC is informed and Well 3 was in manual off before commencing the work Historian hrbt alarm and Comm fail alarms were triggered Provided 24 VDC power to new switch. There is a trend gap on SCADA between 09:18 AM to 09:53 AM due to this work. After the switch replacement, checked all the ports and reset the comm alarms. New switch model is Cisco IE3300-8T2S. | Stouffville Well 3 | 2026-03-19
EAST | March | On site for station check Recorded observations in the shared PWQ sheet Shut well down and cleaned turbidimeter cuvette Placed silicate pump 1 in duty 1 Station and equipment okay | Stouffville Well 3 | 2026-03-23
EAST | March | On site for sampling W11637348 and station check Collected raw and treated sample, 10:05, and verified chlorine analyzers in mg/L Influent free Cl: G 2.58; A 2.52 Effluent free Cl: G 2.48; A 2.48 Effluent total Cl: G 2.80 Inspected station equipment Recorded observations in the shared PWQ sheet Chlorinator 2 is out of service - booster pump local off Station and equipment okay Well 3 back in auto | Stouffville Well 3 | 2026-03-04
EAST | March | On site for station check and sampling W11672797 Completed JHSC inspection Collected raw and treated water samples, 9:42, and verified chlorine analyzers (mg/L) Influent FCl - G 2.58; A 2.54 Effluent FCl - G 2.42; A 2.57 Adjusted to match average of grabs Effluent TCl - G 2.76 Placed well in manual off, closed both chlorine cylinders and purged both chlorine trains for Instrumentation to install chlorinator 2 today. Informed RO Christian Van Beek. He will leave the well manual off for Instrumentation to perform their work. Recorded observations in the shared PWQ sheet Tested emergency halogen system - gas detector succeeded in quantifying the test gas, but the halogen valves failed to close. W11743947 CMU4 created for Electrical Maintenance to attend Station and equipment okay | Stouffville Well 3 | 2026-03-18
EAST | March | Attended site for station check Recorded observations and analyzer verification in the shared PWQ sheet Station and equipment okay | Stouffville Well 3 | 2026-03-20
EAST | March | Attended site to receive sodium silicate delivery. Approximate start level 20 cm Approximate stop level 89 cm | Stouffville Well 3 | 2026-03-17
EAST | March | On site for station check and sampling W11690172 Collected raw water and treated water samples, 10:35, and verified chlorine analyzers (mg/L) Influent FCl - G 2.38; A 2.46 Adjusted to match average of grabs Effluent FCl - G 2.36; A 2.39 Effluent TCl - G 2.74 Replaced free and total chlorine analyzer reagents Recorded observations in the shared PWQ sheet Station and equipment okay | Stouffville Well 3 | 2026-03-25
EAST | March | Attended site for station check Collected grab samples and recorded results and observations in the shared PWQ sheet Station and equipment okay Received delivery of 8 full chlorine cylinders and returned 8 empty. | Stouffville Well 3 | 2026-03-09
EAST | March | On site for station check and Bac-T sampling W11705508 Collected well 2 raw and treated sample, 9:45, verified analyzers, in mg/L Influent FCl - G 3.26; A 3.38 Effluent FCl - G 2.01; A 1.94 Effluent TCl - G 2.38 Received hypo delivery Start 900/ 900 L Stop 1255/ 1281 L Collected well 1 raw sample, 10:22 Recorded observations in the shared PWQ sheet Station and equipment okay | Stouffville Well 1 & 2 | 2026-03-31
EAST | March | On site to check station and equipment. Well 1 is running in duty 1. Placed well 1 man/on since Zone 1 ET is filling. 11:36 chlorine grab residual / analyzer in mg/l: Influent free: 3.54 / 3.48 Effluent free: 2.01 / 1.90 (Standardized with 3 grabs? average of 1.97 mg/l) Effluent total: 2.54 Lowered chlorine residual setpoint from 3.50 mg/l to 3.40 mg/l. Reviewed trends. No issue. Hypo tank 1 is OOS and isolated from the system. | Stouffville Well 1 & 2 | 2026-03-13
EAST | March | On site for station check Verified analyzers and recorded observations in the shared PWQ sheet. Station manual off while waiting for hypo delivery Station and equipment okay | Stouffville Well 1 & 2 | 2026-03-09
EAST | March | ROC called regarding Well 1 Fault due to power outage this afternoon. Will leave off until Monday, Well #2 available and in duty. | Stouffville Well 1 & 2 | 2026-03-15
EAST | March | On site for hypo delivery: Tank #1 will not be filled, as it OOS for replacement Tank #2 start: 42.2 cm Tank #2 stop: 200.6 cm Manual started well #1 after hypo tank filled @14:22 | Stouffville Well 1 & 2 | 2026-03-10
EAST | March | Macnamarra fuel inspection | Stouffville Well 1 & 2 | 2026-03-09
EAST | March | On site for sampling W11637348 and station check Collected well 2 raw and treated sample, verified free chlorine analyzers, 8:30, mg/L Influent free: G 3.46; A 3.54 Effluent free: G 2.03; A 2.01 Effluent total: G 2.52 Recorded observations in the shared PWQ sheet Equalized hypo tanks by opening tie valve - left open Placed wells 1 and 2 manual off, 8:40, and rotated well 1 to duty 1, well 2 duty 2 Placed well 1 in manual on for raw water sampling, 8:51 Collected well 1 raw sample, 9:05 Zone 2 duty deactivated, zone 1 activated. Leaving well 1 manual on and monitoring elevated turbidity remotely while offsite. Station and equipment okay. Off site at 9:20 | Stouffville Well 1 & 2 | 2026-03-04
EAST | March | Attended site for station check Recorded observations and analyzer verification in the shared PWQ sheet Station and equipment okay | Stouffville Well 1 & 2 | 2026-03-06
EAST | March | On site for station check Verified free chlorine analyzers, 12:15, mg/L Influent free - G 3.84; A 3.72 Effluent free - G 2.03; A 2.02 Effluent total - G 2.74 Checked station and equipment Inspected chemical system Reviewed trends and SCADA Recorded observations in the shared PWQ sheet Station and equipment okay | Stouffville Well 1 & 2 | 2026-03-02
EAST | March | Attended site for station check. Recorded observations and analyzer verification in the shared PWQ sheet Reviewed station trends Station and equipment okay | Stouffville Well 1 & 2 | 2026-03-20
EAST | March | On site for station check Recorded observations in the shared PWQ sheet Station and equipment okay | Stouffville Well 1 & 2 | 2026-03-23
EAST | March | On site to cut the PVC analyzer to waste pipe, and direct it to the storm pipe. Made sure that dechlorination pucks have been put into the storm drain to prevent any chlorine residual from going to environment. | Stouffville Well 1 & 2 | 2026-03-27
EAST | March | On site for sampling W11656903 and station check Collected well 1 raw and treated samples, 9:27. Verified influent free and effluent free chlorine analyzers, mg/L Influent free Cl - G 3.30; A 3.42 Effluent free Cl - G 1.81; A 2.09 Adjusted to match average of grabs Effluent total Cl - 2.14 Collected raw sample from well 2, 9:50 Found well 2 discharge check valve passing. Consulted with Water Resources, Leanne Paterson and Jason Moore to confirm no chance of water flowing back into aquifer due to check valve on the submersible well pump. Will create a work order for maintenance to replace well 2 discharge valve Wells 1 and 2 manual off for step test tomorrow. ROC informed. Station and equipment okay | Stouffville Well 1 & 2 | 2026-03-11
EAST | March | Attended site to perform step test with Water Resources, Leanne Paterson and Jason Moore. Steps: 9:00 11 L/s 10:00 22 L/s 11:00 33.5 L/s 12:00 Rest 13:00 well will be returned to auto operation Pumped out hypo tank 1 into temporary day tank in prep for hypo tank 1 replacement. Disregard LIT, tank is empty. Completed silicate and hypo pump inspection. Station and equipment okay | Stouffville Well 1 & 2 | 2026-03-12
EAST | March | On site for preventative maintenance work orders Informed RO, Christian Van Beek Wells manual off for maintenance Completed: Chlorine analyzer maintenance Turbidimeter maintenance and calibration with a 20.7 NTU standard Hypo pump inspection, P1 and P2 Silicate pump inspection, P1 and P2 JHSC inspection Verified chlorine analyzers, 14:31, mg/L Influent free G 3.18; A 3.32 Effluent free G 1.86; A 1.76 Adjusted effluent free chlorine analyzer to match average of grabs Adjusted silicate pump 1 max flow 95mL/min to 90 Test ran well in manual and cycled through hypo and silicate pump duties, verified station function - all okay Station back in service. Left well 2 manual on (duty 1), well 1 off duty 2 | Stouffville Well 1 & 2 | 2026-03-03
EAST | March | STW12 On site for station check and sampling W11690172 Collected well 1 raw water and treated samples, 9:50, and verified chlorine analyzers (mg/L) Influent FCl - G 3.32; A 3.38 Effluent FCl - G 2.12; A 1.98 Adjusted to match average of grabs Effluent TCl - G 2.60 Collected well 2 raw water sample, 10:15 Reduced hypo pump 2 dosing factor from 50 to 45% to reduced the influent free chlorine from rotating wells Replaced influent and effluent free chlorine analyzer reagents Recorded observations in the shared PWQ sheet Station and equipment okay | Stouffville Well 1 & 2 | 2026-03-25
EAST | March | Attended site for hypo delivery Start levels: 95.41/ 98.78 cm Stop levels: 197.8/ 200.5 cm Approximately 1500 L | Stouffville Well 1 & 2 | 2026-03-24
EAST | March | Under the direction of Patrick Fobert, Worked along side Network Analyst Kevin Wen, to replaced a Network switch to Cisco IE3300 inside PAC panel. ROC is informed and all Well and high lift pumps in ST area were in manual off before commencing the work This included STW3, STW12, STRS48 High Lift pumps, STPSMR Pumps, STPSTL pumps Historian hrbt alarm and Comm fail alarms were triggered Provided 24 VDC power to new switch. There is a trend gap on SCADA between 01:16 PM to 1:35 PM due to this work. After the switch replacement, checked all the ports and reset the comm alarms. New switch model is Cisco IE3300-8T2S. | Stouffville Well 1 & 2 | 2026-03-19
EAST | March | Under Direction of OIC (Patrick Fobert) On site for Hypo Receiving Tank 1; Start cm: 30 cm Stop cm: 82.61 cm Start V: 197 L Stop V: 891 L Tank 2: Start cm: 105.7 cm Stop cm: 139 cm Start V: 695 L Stop V: 914 L Total V on SCADA: 913 L | Stouffville Well 1 & 2 | 2026-03-19
EAST | March | Attended site for station check, maintenance support and generator test. Completed station check - all okay Reset fault on the multilin on pump 1. Generator test run: Hours Start 663.5 Stop 664.8 Fuel Start 960 L Stop 943 L Run statistics Exhaust temperature 350 C Oil pressure 25 PSI Coolant temperature 86 C Battery voltage 25 V Oil temperature 160 F Speed 1800 RPM Frequency 60 Hz Well 2 running in manual on and Well 1 back in auto. Off site. | Stouffville Well 1 & 2 | 2026-03-16
EAST | March | On site for station check and sampling W11672797 Collected well 2 raw and treated water samples, 8:05. Verified chlorine analyzers, mg/L. Influent FCl - G 3.32; A 3.39 Effluent FCl - G 1.93; A 1.91 Effluent TCl - G 2.50 Recorded observations in the shared PWQ sheet Confirmed the new hypo tank 1 fittings are not leaking, LIT is calibrated. Waiting on hypo delivery to fill. Collected well 1 raw sample, 8:30. Station and equipment okay | Stouffville Well 1 & 2 | 2026-03-18
EAST | March | Onsite to check on Hypo TK 2 LIT Informed ROC Found Hypo TK2 LIT reading OOR , tank level at 1.45m Cycled power to LIT Reading OK now at 1.45m Informed ROC, armed building and left site | Stouffville Well 1 & 2 | 2026-03-17
EAST | March | This is my first log entry! And now it's been updated! | Ballantrae Well 1 & 2 | 2026-03-28
EAST | March | On site for station check and silicate pump and board maintenance Isolated and depressurized the station header for work Hot flushed silicate pumps 1 and 2 from the suction side Pulled injection points, cleared and reinstalled Flushed silicate chemical board, PSV and PRVs Cleaned silicate pump 1 suction and discharge check valves Primed silicate lines and tested PRVs Re-pressurized station header after silicate pump maintenance Backflushed station header to purge excess silicate from priming operations Test ran well and both silicate pumps Station and equipment okay | Stouffville Well 1 & 2 | 2026-03-26
EAST | March | Under direction of OIC Dan Zhou On site for; - Station checks - Regulatory sampling, micro (W11705392) - Hypo receiving Data in PWQ Workbook *100 L of hypo received Pre fill L: 321 L Post fill L: 421 L Regulatory samples TW and Raw well 2 taken @ 10:31 hrs. , Raw well 1 taken @ 11:15 hrs. Influent Grab @ 10:28 hrs. FCl: 1.96 mg/L Analyzer: FCl: 2.00 mg/L Effluent Grabs @ 10:31 hrs. FCl: 1.62 mg/L TCl: 1.84 mg/L Analyzer: FCl: 1.63 mg/L @ 10:35 hrs. Placed well pump 2 in manual off @ 10:46 hrs. placed well pump 1 in manual on for raw water sample @ 11:15 hrs. changed well pump 1 to duty 1 and well pump 2 to duty 2. placed well pumps 1 and 2 in auto. Duty inactive Equipment OOS: None Facility OK | Ballantrae Well 1 & 2 | 2026-03-31
EAST | March | Under direction of OIC Dan Zhou @ 10:59 hrs. well pump 1 in auto @ 11:12 hrs. well pump 2 in auto Duty inactive. | Ballantrae Well 1 & 2 | 2026-03-11
EAST | March | On site to top up silicate bulk tank. Start level: 32.9 cm Stop level: 39.9 cm The hot water heater is not working, informed onsite contractor and consultant Adil. | Ballantrae Well 1 & 2 | 2026-03-04
EAST | March | Under direction of OIC Dan Zhou On site for; - Station checks Data in PWQ Workbook Influent Grab @ 12:22 hrs. FCl: 1.96 mg/L Analyzer: FCl: 1.98 mg/L Effluent Grabs @ 12:26 hrs. FCl: 1.84 mg/L TCl: 2.50 mg/L Analyzer: FCl: 1.85 mg/L Pump 2 active in duty 1 Equipment OOS: None Facility OK | Ballantrae Well 1 & 2 | 2026-03-06
EAST | March | Under direction of OIC Dan Zhou Remotely Started well pump 1 manually for sampling. | Ballantrae Well 1 & 2 | 2026-03-04
EAST | March | Macnamarra fuel inspection | Ballantrae Well 1 & 2 | 2026-03-09
EAST | March | Under direction of OIC Dan Zhou On site for; - Station checks - Operational sampling, iron Data in PWQ Workbook Influent Grab @ 12:50 hrs. FCl: 2.10 mg/L Analyzer: FCl: 2.04 mg/L Effluent Grabs @ 12:47 hrs. FCl: 1.94 mg/L TCl: 2.44 mg/L Analyzer: FCl: 1.88 mg/L Pump 2 active in duty 1 Equipment OOS: None Facility OK | Ballantrae Well 1 & 2 | 2026-03-09
EAST | March | Under direction of OIC Dan Zhou On site for; - Station checks - Regulatory sampling, micro (W11656809) Data in PWQ Workbook @ 08:23 placed well pumps 1 and 2 in manual off to repair silicate injection point. Replaced parker fitting on injection quill, silicate pump 2 line. @ 09:05 hrs. placed well pump 2 in manual on Regulatory samples TW and Raw well 1 taken @ 09:37, Raw well 2 taken @ 10:25 hrs. Influent Grab @ 09:37 hrs FCl: 2.10 mg/L Analyzer: FCl: 2.07 mg/L Effluent Grabs @ 09:37 hrs. FCl: 1.89 mg/L TCl: 2.50 mg/L Analyzer: FCl: 1.97 mg/L @ 09:43 hrs. Placed well pump 2 in manual off @ 09:55 hrs. placed well pump 1 in manual on for raw water sample Equipment OOS: None Facility OK | Ballantrae Well 1 & 2 | 2026-03-11
EAST | March | Under direction of OIC Dan Zhou On site for PM's; - Generator test run and inspection - JHSC Health and safety inspections - CL-17 influent and effluent clean/maintenance - Turbidity analyzer clean/maintenance/calibration - Silicate system inspection and maintenance - Hypo delivery receiving - Sodium hypochlorite system inspection and maintenance @ 10:30 hrs. placed well pumps in manual off for generator test run prep Generator test run: Start Fuel: 1014 L Stop Fuel: 998 L Start Hours: 1023.2 Stop Hours: 1024.8 Start Time: 10:36 hrs. Pre run checks; Battery Cell Levels: Ok Battery Terminals and Cables: Ok Oil Level: Ok Coolant Level: Ok Fluid Leaks: NO Coolant Recirculating pump: Ok Faulty Gauges: NO @ 10:31 hrs. Switched ATS to Test for generator power @ 11:22 hrs. Placed generator under facility load Well pump 2 in Manual ON *Well pump 1 interlocked due to generator running. Informed ON Call PCS operator Kyle Carlen. Interlock disengages once power is switched to facility power. Start Fuel: 1017 L Stop Fuel: 997 L Start Hours: 658.5 Stop Hours: 650.1 Start Time: 10:31 hrs. *under load* Operating Current: 59 Amps Operating Frequency: 60 Hz Operating Voltage: 570 Volts Engine speed: 1525 RPM Water/coolant Temp: 160 f Oil Pressure: 60 kpa Oil Temperature: 175 f @ 12:00 hrs. placed well pump 2 in manual off for ATS switch @ 12:02 hrs. Toggled ATS to normal @ 12:07 power switched to station power @ 12:14 cooldown stopped Chlorine analyzer maintenance on AIT 1 and 2, well pumps 1 and 2 in manual off, no flow directed to users. Start Clean @ 10:40 hrs. Exited Clean @ 11:10 hrs. Effluent (Treated Water) AIT verification Grab @ 11:17 hrs. FCl: 1.81 mg/L Analyzer FCl: 1.83 mg/L Influent AIT verification Grab @ 11:19 hrs. FCl: 1.89 mg/L Analyzer FCl: 1.87 mg/L Turbidity analyzer maintenance: Start @ 11:01hrs. Stop @ 11:09 hrs. @ 15:17 returned well pumps 1 and 2 to auto Well pump 2 active in Duty 1 @ 15:31 hrs. influent hihi, on well start up, came down next reading | Ballantrae Well 1 & 2 | 2026-03-10
EAST | March | Under direction of OIC Dan Zhou On site for; - Station checks - Regulatory sampling, micro (W11637232) Data in PWQ Workbook Regulatory samples TW and Raw well 1 taken @ 14:16, Raw well 2 taken @ 14:36 Regulatory sample Raw well 2 taken @ Influent Grab @ 14:21 hrs FCl: 2.20 mg/L Analyzer: FCl: 2.12 mg/L Effluent Grabs @ 14:16 FCl: 1.89 mg/L TCl: 2.10 mg/L Analyzer: FCl: 1.84 @ 14:22 Placed well pump 1 in auto, duty inactive @ 14:27 placed well pump 2 in manual on for raw water sample Equipment OOS: None Facility OK | Ballantrae Well 1 & 2 | 2026-03-04
EAST | March | Under direction of OIC Dan Zhou On site for; - Station checks Data in PWQ Workbook Influent Grab @ 15:11 hrs FCl: 1.79 mg/L Analyzer: FCl: 1.77 mg/L Effluent Grabs @ 15:16 FCl: 1.73 mg/L TCl: 2.10 mg/L Analyzer: FCl: 1.74 Equipment OOS: None Facility OK | Ballantrae Well 1 & 2 | 2026-03-02
EAST | March | Under direction of OIC Dan Zhou On site for; - Station checks Data in PWQ Workbook Influent Grab @ 09:01 hrs. FCl: 1.67 mg/L Analyzer: FCl: 1.68 mg/L Effluent Grabs @ 09:05 hrs. FCl: 1.69 mg/L TCl: 2.10 mg/L Analyzer: FCl: 1.64 mg/L Duty inactive Equipment OOS: None Facility OK | Ballantrae Well 1 & 2 | 2026-03-13
EAST | March | On site responding to VFD fault alarm on both pumps due to power outage. Both pumps faulted on "Over Current" on VFD. Was able to reset the faults. Duty was active, W2 back into auto, duty 1 and active. No further issues. | Ballantrae Well 1 & 2 | 2026-03-15
EAST | March | Under direction of OIC Dan Zhou On site for; - Station checks - Regulatory sampling, micro (W11672695) Data in PWQ Workbook Silicate pump 1 not drawing silicate. Placed pump in manual off. Removed airlock from pump. Placed pump back in auto. Regulatory samples TW and Raw well 1 taken @ 14:01 hrs. , Raw well 2 taken @ 14:50 hrs. Influent Grab @ 13:55 hrs FCl: 1.98 mg/L Analyzer: FCl: 1.99 mg/L Effluent Grabs @ 14:01 hrs. FCl: 1.89 mg/L TCl: 2.71 mg/L Analyzer: FCl: 1.81 mg/L @ 14:06 hrs. Placed well pump 2 in manual off @ 14:16 hrs. placed well pump 1 in manual on for raw water sample Equipment OOS: None Facility OK | Ballantrae Well 1 & 2 | 2026-03-18
EAST | March | Under direction of OIC Dan Zhou 13:07 hrs. Started well pump 1 for sampling. | Ballantrae Well 1 & 2 | 2026-03-25
EAST | March | @ 15:20 hrs. Stopped well pump 2 and placed well pumps 1 and 2 in auto. | Ballantrae Well 1 & 2 | 2026-03-18
EAST | March | ROC called regarding high station turbidity while W2 was running. Turbidity over 1.00ntu. Manually stopped W2. Investigated Turbidity Analyzer, cleaned vial and turbidity value dropped to below 0.5ntu. Checked silicate pumps, no issues with pumps. Silicate dose in PWQ sheet, dose within range. Placed W1 into duty 1 and monitored start up. Turbidity value dropping below 0.45ntu. Will inform operations tomorrow to observe W2 operation and treated turbidity. W1 currently running and turbidity value <0.45ntu and still dropping. | Ballantrae Well 1 & 2 | 2026-03-17
EAST | March | Under direction of OIC Dan Zhou @ 07:30 hrs. Placed well pumps 1 and 2 in manual off in preparation for March 24, 2026 step test. | Ballantrae Well 1 & 2 | 2026-03-23
EAST | March | Under direction of OIC Dan Zhou On site for; - Station checks Data in PWQ Workbook Influent Grab @ 13:08 hrs. FCl: 2.01 mg/L Analyzer: FCl: 2.05 mg/L Effluent Grabs @ 13:11 hrs. FCl: 1.82 mg/L TCl: 2.09 mg/L Analyzer: FCl: 1.85 mg/L Well pump 1 in duty 1 Duty active Equipment OOS: None Facility OK | Ballantrae Well 1 & 2 | 2026-03-26
EAST | March | Under direction of OIC Patrick Fobert On site for; - Station checks Data in PWQ Workbook Influent Grab @ 09:46 hrs. FCl: 1.66 mg/L Analyzer: FCl: 1.63 mg/L Effluent Grabs @ 09:51 hrs. FCl: 1.62 mg/L TCl: 1.95 mg/L Analyzer: FCl: 1.59 mg/L Changed buffer and analyzer reagents for influent and effluent AIT Duty inactive Equipment OOS: None Facility OK | Ballantrae Well 1 & 2 | 2026-03-16
EAST | March | Under Direction of OIC (Patrick Fobert) On site for Hypo Receiving Tank 1; Start cm: 55.34 cm Stop cm: 82.61 cm Start V: not observed L Stop V: 427 L Upon logging into SCADA onsite see silicate pump 1 has failed to start alarm. Checked pump, analog setting in place but not back in analog mode, pressed stop button to set pump in analog. | Ballantrae Well 1 & 2 | 2026-03-19
EAST | March | Under direction of OIC Patrick Fobert On site to isolate service line, valved at backflow preventer for new service line tie in. | Ballantrae Well 1 & 2 | 2026-03-20
EAST | March | Under direction of OIC Dan Zhou On site for; - Station checks Data in PWQ Workbook Influent Grab @ 14:42 hrs. FCl: 1.66 mg/L Analyzer: FCl: 1.64 mg/L Effluent Grabs @ 14:44 hrs. FCl: 1.55 mg/L TCl: 1.83 mg/L Analyzer: FCl: 1.55 mg/L Well pumps 1 and 2 in manual off. Duty inactive Equipment OOS: None Facility OK | Ballantrae Well 1 & 2 | 2026-03-23
EAST | March | On site to facilitate and assist with construction project station power outage and replacement of main breaker and associated testing upon completion. | Ballantrae Well 1 & 2 | 2026-03-20
EAST | March | Under direction of OIC Dan Zhou Placed well pumps 1 and 2 in auto. | Ballantrae Well 1 & 2 | 2026-03-25
EAST | March | @ 13:01 placed well pump 1 in manual on for regulatory sampling. | Ballantrae Well 1 & 2 | 2026-03-18
EAST | March | Under direction of OIC Patrick Fobert On site for service line tie in verification and re-pressurization of service line at backflow preventer. Ball valve placed by contractor down stream of backflow preventer for additional tie ins. | Ballantrae Well 1 & 2 | 2026-03-20
EAST | March | Under direction of OIC Dan Zhou On site for; - Station checks - Regulatory sampling, micro (W11690078) - Operational sampling, (iron, FCl, TCl, NTU, Temp) Data in PWQ Workbook Regulatory samples TW and Raw well 1 taken @ 14:20 hrs. , Raw well 2 taken @ 15:05 hrs. Influent Grab @ 14:19 hrs. FCl: 1.92 mg/L Analyzer: FCl: 1.95 mg/L Effluent Grabs @ 14:20 hrs. FCl: 1.84 mg/L TCl: 2.10 mg/L Analyzer: FCl: 1.83 mg/L @ 14:31 hrs. Placed well pump 2 in manual off Changed duty 1 to well pump 2 and duty 2 to well pump 1 @ 14:39 hrs. placed well pump 1 in manual on for raw water sample Equipment OOS: None Facility OK | Ballantrae Well 1 & 2 | 2026-03-25
EAST | March | Under direction of OIC Dan Zhou On site for; - Step test (On site with Leanne Paterson from water resources) Step test Part 1 @ 08:55 hrs. changed well setpoint for well pump 1 to 10 L/s @ 09:05 hrs. started well pump 1 for part 1 of step test Step test Part 2 @ 10:05 hrs. changed well setpoint for well pump 1 to 20 L/s Step test Part 3 @ 11:05 changed well setpoint for well pump 1 to 31 L/s @ 12:05 hrs. returned well pump 1 to auto, and well setpoint to 30 L/s, and well pump 2 to auto | Ballantrae Well 1 & 2 | 2026-03-24
EAST | March | Under Direction of OIC (Dan Zhou) On site for Hypo Receiving Tank 1; Start cm: 67.9 cm Stop cm: 84.5 cm Start V: 351 L Stop V: 437 L Total Volume received = 86 L | Ballantrae Well 1 & 2 | 2026-03-24
EAST | March | Under direction of OIC Patrick Fobert On site for; - Station checks Data in PWQ Workbook Well 1 in manual ON for grabs Influent Grab @ 14:18 hrs. FCl: 1.98 mg/L Analyzer: FCl: 1.96 mg/L Effluent Grabs @ 14:20 hrs. FCl: 1.81 mg/L TCl: 2.00 mg/L Analyzer: FCl: 1.77 mg/L @ 14:26 placed well pumps 1 and 2 in auto Duty inactive Equipment OOS: None Facility OK | Ballantrae Well 1 & 2 | 2026-03-20
EAST | March | Silicate top up (36.3 to 48.1cm) | Ballantrae Well 1 & 2 | 2026-03-19
EAST | March | Time in: 08:10 On site to support contractor to repair the leak on chlorine solution line #2. Engaged E-Stop for chlorine booster pump 2. Depressurized the chlorine solution line 1&2. Contractor applied coatings on the leaky spot for line #2. I replaced the leaky ball valve on chlorine #1 line. Primed chlorine line #1. Tested chlorinator #1 vacuum, it responds well. Opened cylinders, tested chlorinators in local and remote, no issue. Man/Start well 3. Switched silicate pump to #2 to check it's operation, no issue. Verified chlorinator 1 performance, it is dosing at 50%, 25 ppd, vacuum = -90 mbar. Chlorine booster pump 1 discharge pressure = 210 psi. 09:33 verified chlorine analyzer readings: Grab influent = 2.15 mg/l, analyzer = 2.11 mg/l Grab effluent = 1.48 mg/l, analyzer = 1.51 mg/l. Will place well 3 to auto remotely. Time out: 09:55 | Ballantrae Well 3 | 2026-03-28
EAST | March | Under direction of OIC Dan Zhou @ 11:17 hrs. Placed well pump 3 in manual on for sampling. | Ballantrae Well 3 | 2026-03-31
EAST | March | Under direction of OIC Dan Zhou On site for; - Station checks - Regulatory sampling, micro (W11705392) Data in PWQ workbook Regulatory samples taken @ 11:57 hrs. Influent grabs @ 11:54 hrs. FCl: 2.10 mg/L Analyzer: FCl: 2.18 mg/L Effluent Grabs @ 11:57 hrs. FCl: 1.35 mg/L TCl: 1.67 mg/L Analyzer: FCl: 1.39 mg/L NTU: 0.027 @ 12:04 hrs. placed well pump 3 in auto Duty inactive Well pump 4 in local Equipment OOS: None Facility OK | Ballantrae Well 3 | 2026-03-31
EAST | March | Under direction of OIC Dan Zhou On site for PM's - AIT maintenance and clean, effluent and influent - Turbidity analyzer maintenance and clean - Repair AIT line to sight glass and fix leak at y-screen Chlorine analyzer maintenance: Start clean @ 12:43 hrs. Stop clean @ 13:36 hrs. Disregard lo influent and effluent alarm, due to low flow to analyzer and no water directed to users. Adjusted flow. Replaced broken parker fitting on effluent sight glass with 1/2 inch fast and tite, cleaned up flooded area Analyzer verification: Effluent grab @ 13:58 FCl: 1.39 mg/L Analyzer: FCl: 1.42 mg/L Influent grab @ 13:03 FCl: 1.45 mg/L Analyzer: FCl: 1.43 mg/L Tubidity meter maintenance: Start @ 12:55 hrs. Stop @ 13:07 hrs. @ 14:07 hrs. manually activated well 3 @ 14:40 hrs. Returned well 3 to auto, duty deactivated | Ballantrae Well 3 | 2026-03-03
EAST | March | Under direction of OIC Dan Zhou On site for; - Test chlorine train 2 system for leaks, place back in service @ 09:05 hrs. informed ROC of chlorine system work @ 09:10 hrs. place BP2 in local on to test for leaks, chlorine cylinders and regulators closed, (no dosing of raw water for leak test) -no leaks observed in chlorine train 2, vacuum produced - Re opened chlorine cylinders and regulators - Placed chlorine train 2 in duty 1 @ 09:26 placed well pump 3 in manual on @ 09:50 hrs. stopped well pump 3, check valve flag showed as closed. @ 10:26 hrs. - Verified by senior OIC team lead Dan Zhou that the flag indicator on the check valve is broken - Restarted well and verified equal pressures before and after check valve and flow rate on FIT verified chlorine system with grabs Effluent: Grab @ 11:31 hrs. FCl: 1.54 m g/L Effluent analyzer FCl: 1.59 mg/L Influent: Grab @ 11:21 hrs. FCl: 2.18 mg/L Analyzer: 2.23 mg/L @ 11:38 hrs. placed well pump 3 in auto, duty inactive System functional Equipment OOS: None Station OK | Ballantrae Well 3 | 2026-03-30
EAST | March | Under direction of OIC Dan Zhou On site for; - Station checks - Regulatory sampling, micro (W11656809) Data in PWQ workbook @ 13:07 placed well pump 3 in manual on Regulatory samples taken @ 10:47 hrs. Influent grabs @ 10:50 hrs. Influent: FCl: 2.12 mg/L Analyzer: FCl: 2.18 mg/L Effluent Grabs @ 10:47 hrs. FCl: 1.45 mg/L TCl: 1.75 mg/L Analyzer: FCl: 1.46 mg/L NTU: 0.017 @ 11:00 hrs. placed well pump 3 in auto Duty inactive Well pump 4 in local (not commissioned yet) Duty Inactive Equipment OOS: None Facility OK | Ballantrae Well 3 | 2026-03-11
EAST | March | Under direction of OIC Dan Zhou @ 10:14 hrs. placed well pump 3 in manual on for sampling. | Ballantrae Well 3 | 2026-03-11
EAST | March | Under direction of OIC Dan Zhou On site for; - Station checks - Supply fan 1 check - Exhaust fan check - Chlorine leak detector test - Chlorine emergency repair kit inspection - Chlorine scrubber check and inspection - Low temp alarm test - Pump 3 oil drip top up Data in PWQ workbook Duty active for grabs Influent grabs @ 13:15 hrs. Influent: FCl: 2.14 mg/L Analyzer: FCl: 2.19 mg/L Effluent Grabs @ 13:20 hrs. FCl: 1.43 mg/L TCl: 1.83 mg/L Analyzer: FCl: 1.48 mg/L NTU: 0.015 @ 13:47 hrs. duty deactivated, tower @ 92%, placed well pump 3 in manual, for pm's @ 13:49 hrs. raised low temp alarm setting, triggered building low temp alarm @ 13:51 hrs. @ 13:53 hrs. manually triggered chlorine leak alarm, scrubbers turned on, Cl2 gas monitor in silicate room and Cl2 gas room readings present Exhaust fans 1,2,3 triggered manually, louvers opened @ 14:43 hrs. returned well pump 3 to auto Well pump 4 in local (not commissioned yet) Duty Inactive Equipment OOS: None Facility OK | Ballantrae Well 3 | 2026-03-06
EAST | March | #11668224 Generator test: 12:14 Pre-Check complete 13:25 Start (412:25 hrs) 14:30 End (413:32 hrs) Fuel Start : 85.9cm (848L), 80.7cm (798L) Fuel End: 84.4cm (837L), 79.8cm(788L) 15:55 reading: 595volts, 75amps, 60hz, oil pres.57psi, coolant temp. 174F, 1800rpm #11718890, #11669695 silicate (hot flush completed ) Silicate top up (175L to 200L) | Ballantrae Well 3 | 2026-03-12
EAST | March | Under direction of OIC Dan Zhou On site for; - Station checks - Regulatory sampling, micro (W11637232) Data in PWQ workbook @ 13:07 placed well pump 3 in manual on Regulatory samples taken @ 13:30 Influent grabs @ 13:31 hrs. Influent: FCl: 2.10 mg/L Analyzer: FCl: 2.19 mg/L Effluent Grabs @ 13:30 hrs. FCl: 1.47 mg/L TCl: 1.78 mg/L Analyzer: FCl: 1.46 mg/L NTU: 0.017 @ 13:43 placed well pump 3 in auto Well pump 4 in local (not commissioned yet) Duty Inactive Equipment OOS: None Facility OK | Ballantrae Well 3 | 2026-03-04
EAST | March | Under direction of oic Dan Zhou @ 13:11 hrs. Returned well pump 3 to auto. Duty active. | Ballantrae Well 3 | 2026-03-09
EAST | March | Under direction of oic Jack Palmer. On site for Chlorine cylinder change. | Ballantrae Well 3 | 2026-03-10
EAST | March | McNamara fuel inspection | Ballantrae Well 3 | 2026-03-09
EAST | March | Under direction of OIC Patrick Fobert On site for; - Station checks Data in PWQ workbook Influent grabs @ 09:03 hrs. Influent: FCl: 1.42 mg/L Analyzer: FCl: 1.40 mg/L Effluent Grabs @ 09:05 hrs. FCl: 1.46 mg/L TCl: 1.65 mg/L Analyzer: FCl: 1.47 mg/L NTU: 0.03 Well pump 4 in local Duty inactive Equipment OOS: None Facility OK | Ballantrae Well 3 | 2026-03-16
EAST | March | Under direction of OIC Dan Zhou @ 12:02 placed well pump 3 in manual on for sampling. | Ballantrae Well 3 | 2026-03-25
EAST | March | Under direction of OIC Patrick Fobert On site for; - Station checks Data in PWQ workbook Influent grabs @ 09:40 hrs. Influent: FCl: 1.43 mg/L Analyzer: FCl: 1.40 mg/L Effluent Grabs @ 09:43 hrs. FCl: 1.41 mg/L TCl: 1.64 mg/L Analyzer: FCl: 1.45 mg/L NTU: 0.03 Well pump 4 in local Duty inactive Equipment OOS: None Facility OK | Ballantrae Well 3 | 2026-03-20
EAST | March | Under direction of OIC Dan Zhou On site for; - Station checks - Regulatory sampling, micro (W11690078) - Operational sampling, (iron, NTU, FCl, TCl, Temp) Data in PWQ workbook Regulatory samples taken @ 12:43 hrs. Influent grabs @ 12:40 hrs. FCl: 2.19 mg/L Analyzer: FCl: 2.22 mg/L Effluent Grabs @ 12:43 hrs. FCl: 1.49 mg/L TCl: 1.76 mg/L Analyzer: FCl: 1.51 mg/L NTU: 0.039 @ 13:08 hrs. placed well pump 3 in auto @ 13:12 informed ROC and placed well pump 3 in manual off for turbidity analyzer vial cleaning Turbidity analyzer vial cleaning: Clean start @ 13:14 hrs. Clean stop @ 13:30 hrs. @ 13:31 placed well pump 3 back in auto Duty inactive Well pump 4 in local Equipment OOS: None Facility OK | Ballantrae Well 3 | 2026-03-25
EAST | March | Under direction of OIC Dan Zhou On site for operator assistance with chemical line tie ins for well 4; - Sodium silicate flush and depressurize - Chlorine gas system purge and depressurize - Piping gallery depressurization - Station check Worked with OIC Dan Zhou, for operator assistance tasks @ 08:48 hrs. Informed ROC of well 3 shutdown and chemical line tie ins. Placed well pump 3 in local at PLC and in E-stop. Flushed silicate system with hot water. Depressurized silicate system, as drain valves remain open. Closed chlorine cylinders and placed chlorine regulators in off position. Purged chlorine gas system in local, using booster pump 1 for line 1 and then booster pump 2 for line 2, 5 minutes each. Valved close hypochlorous lines post chlorinator and pre injection to isolate for chemical line tie ins. Isolated well 3 at isolation valve Opened valve connections below tie in on chemical lines to verify depressurization of silicate line and hypochlorous acid line. Verified depressurization of piping gallery at raw water sample tap. Well isolated from distribution system. Witnessed chemical line tie ins. All valves closed for isolation are locked out and tagged out. Data in PWQ workbook Influent grabs @ 11:54 hrs. Influent: FCl: 1.60 mg/L Analyzer: FCl: 1.60 mg/L Effluent Grabs @ 11:55 hrs. FCl: 1.40 mg/L TCl: 1.65 mg/L Analyzer: FCl: 1.41 mg/L NTU: 0.039 Well pump 4 in local off, well pump 3 in local off/ E-stop, silicate pumps 1 and 2 in local/hand, chlorine booster pumps 1 and 2 in local off/E-stop. Systems interlocked and facility shutdown until March 27 Equipment OOS: Well pumps 3,4 and chlorine booster pumps 1 and 2, station offline Facility OK | Ballantrae Well 3 | 2026-03-26
EAST | March | Under direction of OIC Dan Zhou On site for; - Station checks Data in PWQ workbook Duty active for grabs Influent grabs @ 10:24 hrs. Influent: FCl: 1.44 mg/L Analyzer: FCl: 1.44 mg/L Effluent Grabs @ 10:29 hrs. FCl: 1.54 mg/L TCl: 1.67 mg/L Analyzer: FCl: 1.55 mg/L NTU: 0.030 Well pump 4 in local Duty inactive Equipment OOS: None Facility OK | Ballantrae Well 3 | 2026-03-13
EAST | March | Under direction of OIC Dan Zhou On site for; - Station checks - JHSC health and safety inspection Data in PWQ workbook Influent grabs @ 13:38 hrs. Influent: FCl: 1.76 mg/L, 1.76 mg/L, 1.75 mg/L *Adjusted influent analyzer to 1.75 mg/L Analyzer: FCl: 1.62 mg/L Effluent Grabs @ 13:47 hrs. FCl: 1.70 mg/L TCl: 2.05 mg/L Analyzer: FCl: 1.73 mg/L NTU: 0.088 NTU pre clean NTU: 0.015 NTU post clean @ 13:55 hrs. placed well pump 3 in manual off to clean turbidity analyzer, water not going to users. Disregard any turbidity alarm. @ 14:13 hrs. returned pump 3 to auto Changed influent analyzer reagents, indicator and buffer Well pump 4 in local (not commissioned yet) Duty Inactive Equipment OOS: None Facility OK | Ballantrae Well 3 | 2026-03-02
EAST | March | Under direction of OIC Dan Zhou On site for; - Station checks - Operational sampling Data in PWQ workbook Duty active for grabs Influent grabs @ 13:27 hrs. Influent: FCl: 2.44 mg/L Analyzer: FCl: 2.50 mg/L Effluent Grabs @ 13:30 hrs. FCl: 1.49 mg/L TCl: 1.77 mg/L Analyzer: FCl: 1.46 mg/L NTU: 0.016 Well pump 4 in local (not commissioned yet) Well pump 3 Active in Duty 1 Equipment OOS: None Facility OK | Ballantrae Well 3 | 2026-03-09
EAST | March | Under direction of OIC Dan Zhou Placed well pump 3 in manual off. | Ballantrae Well 3 | 2026-03-09
EAST | March | Onsite to top up silicate day tank. Start: 80l Stop: 210 L Switch silicate pump duty since #1 is not dosing correctly. | Ballantrae Well 3 | 2026-03-04
EAST | March | Under direction of OIC Dan Zhou @ 08:25 hrs. Placed well pump 3 in manual off. | Ballantrae Well 3 | 2026-03-11
EAST | March | Under direction of OIC Patrick Fobert On site for; - Station checks - Regulatory sampling, micro (W11672695) Data in PWQ workbook Regulatory samples taken @ 12:53 hrs. Influent grabs @ 12:51 hrs. FCl: 2.18 mg/L Analyzer: FCl: 2.22 mg/L Effluent Grabs @ 12:53 hrs. FCl: 1.44 mg/L TCl: 1.72 mg/L Analyzer: FCl: 1.46 mg/L NTU: 0.042 @ 13:01 hrs. placed well pump 3 in auto Duty inactive Well pump 4 in local (not commissioned yet) Equipment OOS: None Facility OK | Ballantrae Well 3 | 2026-03-18
EAST | March | On site to swap ejector #1 on chlorine train #1. Purged chlorine system for work, replaced ejector. Tested chlorine system after swap, and tested well #3 in manual. Station operations normal | Ballantrae Well 3 | 2026-03-24
EAST | March | Silicate top up (150 to 200L) | Ballantrae Well 3 | 2026-03-19
EAST | March | Under direction of OIC Patrick Fobert @ 12:10 hrs. Placed well pump 3 in manual on for regulatory sampling. | Ballantrae Well 3 | 2026-03-18
EAST | March | Under direction of OIC Dan Zhou On site for; - Station checks Data in PWQ workbook Influent grabs @ 13:51 hrs. Influent: FCl: 2.18 mg/L Analyzer: FCl: 2.22 mg/L Effluent Grabs @ 13:57 hrs. FCl: 1.52 mg/L TCl: 1.86 mg/L Analyzer: FCl: 1.55 mg/L NTU: 0.085 Changed buffer and analyzer reagents for effluent AIT. Well pump 4 in local Duty active Equipment OOS: None Facility OK | Ballantrae Well 3 | 2026-03-23
EAST | March | On site for BacT sampling W11706508 Collected well 5 raw sample, 12:56 Collected treated water sample, 13:05, and verified free chlorine analyzer, in mg/L FCl - G 1.73; A 1.76 TCl - G 1.94 Collected well 6 raw sample, 13:10 Station and equipment okay | Stouffville Reservoir and Wells 5 & 6 | 2026-03-31
EAST | March | On site responding to Influent Lolo chlorine lockout. CMU5 #W11749880 Arrived on site @16:30 and took grab residuals on Influent: Grab: 0.09 mg/L / Analyzer: 0.05 mg/L Set up backflushing hose around the back of the building to that waste man hole and started backflushing @14:43 Well had been running from 23:26 yesterday until 00:53 today. Influent chlorine had been stable from 23:30 to 00:43, when it suddenly started decking until it locked out @00:53. Chlorinator #1 had been running, trends look stable. Tested chlorine train #1 in local, and did not observe any issues. @17:28 stopped backflushing - Analyzer is reading 1.29 mg/L on Influent @17:33 started well #3 in manual to test well operation Chlorine train #1 is left OOS for the rest of the weekend. Will further investigate next week. Leaving well #3 running in manual - requested ROC to place well back to auto after 30 minutes @18:15 Station operation okay | Ballantrae Well 3 | 2026-03-21
EAST | March | On site to bring well 3 back online after chemical line work by contractors. Primed and tested both silicate lines. Primed and tested both chlorine solutions lines. Chlorine train 1?s isolation ball valve in chlorinator room is leaking slightly, tried to tighten it, not able to seal. Left chlorine #1 system in local off. Tested chlorine train 2 in local and remote, noticed the vacuum gauge is stuck in high vacuum. Will issue work order to INST. Shelved the chlorinator 2 high vacuum alarm in order to run chlorine #2 system. Backflushed well 3 for a few minutes. Man/start well 3, checked silicate #1 operation, no issues. While checking chlorine #2 performances, noticed a leak at the new elbow. Notified Jason G. (ETO). Placed well 3 Local Off. Isolated both gas cylinders. Purged chlorine line 2 with system water. Contractors are coming back to site tomorrow morning to address cl2 line 2 leak. Well 3 remains OOS for the night. Informed ROC. | Ballantrae Well 3 | 2026-03-27
EAST | March | On site for station check Recorded observations in the shared PWQ sheet Verified reservoir influent and effluent free chlorine analyzers - see PWQ sheet Station and equipment okay | Stouffville Reservoir and Wells 5 & 6 | 2026-03-30
EAST | March | Macnamarra fuel inspection | Stouffville Reservoir and Wells 5 & 6 | 2026-03-09
EAST | March | On site for sampling and station check Sampling work orders: Micro samples W11656903 HAA W11707190 Collected well 5 raw, 12:30 Collected well 6 raw, 12:20 Collected STRS48 treated water samples, 12:55 FCl G 1.82; A 1.80 TCl G 2.02 Recorded observations in the shared PWQ sheet Rotated reservoirs for sampling Station and equipment okay | Stouffville Reservoir and Wells 5 & 6 | 2026-03-11
EAST | March | Macnamarra fuel inspection | Stouffville Reservoir and Wells 5 & 6 | 2026-03-10
EAST | March | On site for station check and equipment verification Duty is not active - reservoir level is 84% Recorded data in PWQ sheets Verified CL-17 analyzer readings @09:10 to 09:19 (Grab / Analyzer mg/L) Influent FCL: 1.95 / 2.03 Effluent FCL: 1.76 / 1.78 Effluent TCL: 1.93 No adjustments needed Reviewed trends, equipment OOS: none Station operation normal | Stouffville Reservoir and Wells 5 & 6 | 2026-03-13
EAST | March | On site for station check Verified post injection FCl, 9:45, mg/L G 1.94; A 1.99 Verified effluent free FCl, 10:39, mg/L G 1.66; A 1.70 Effluent TCl grab: 1.87 Recorded observations in the station PWQ sheet Changed chlorine cylinder bank 2 with Dan Zhou, verified regulator function Switched influent sample line to reservoir Performed visual inspection of equipment, chemical system, sample pumps, all okay Station and equipment okay | Stouffville Reservoir and Wells 5 & 6 | 2026-03-02
EAST | March | On site for CMU5 W11722310 Hi lift pump 2 fail to stop Attended site with Sean Peoples (Electrical) and worked with Ian Williams (remote, PCS) Sean opened limit switch on P2 FCV and the pump stopped. Test ran the pump for three cycles and found no issues starting and stopping HLP2 back in service. | Stouffville Reservoir and Wells 5 & 6 | 2026-03-10
EAST | March | On site for station check and sampling W11637348 Collected well 5 raw, 12:45 Collected reservoir treated, 12:58, and verified free chlorine analyzer: FCl G 1.78; A 1.79 mg/L; TCl G 1.93 mg/L Collected well 6 raw, 13:10 Recorded observations and process analyzer verification in the shared PWQ sheet. Station and equipment okay | Stouffville Reservoir and Wells 5 & 6 | 2026-03-04
EAST | March | On site to install halogen system. | Stouffville Reservoir and Wells 5 & 6 | 2026-03-25
EAST | March | On site for facility station check and equipment verifications and to collect well #5 raw resample for YD lab (W11746801) High lift pump #2 running in manual - 52 L/s Wells duty is active - res level is 81% Recorded data in PWQ sheets Verified analyzer readings: @0915-0920 Influent FCL: 1.98 / 1.94 Effluent FCL: 1.80 / 1.82 Effluent TCL: 1.95 Collected well #5 raw sample @09:10 Reviewed trends, equipment ok Placed high lift pump 2 back to auto Station operation normal | Stouffville Reservoir and Wells 5 & 6 | 2026-03-20
EAST | March | On site for station check and sampling W11690172 Verified reservoir influent free chlorine analyzer and collected well 5 raw water sample, 11:45, in mg/L FCl - G 2.09; A 2.08 Collected reservoir effluent sample and verified free chlorine analyzer, 12:02, in mg/L FCl - G 1.70; A 1.77 TCl - G 1.94 Collected well 6 raw water sample, 12:12. Replaced influent and effluent free chlorine analyzer reagents Recorded observations in the shared PWQ sheet Ferguson Electric on site working on generator flashing and insulation Electrician Ernesto Hidalgo on site working on emergency halogen shut off system Station and equipment okay | Stouffville Reservoir and Wells 5 & 6 | 2026-03-25
EAST | March | On site for preventative maintenance Completed Chlorine scrubber inspection Chlorine system inspection Chlorine leak emergency kit inspection Chlorine analyzer cleaning (post injection) Housekeeping Station and equipment okay | Stouffville Reservoir and Wells 5 & 6 | 2026-03-17
EAST | March | On site to install halogen system | Stouffville Reservoir and Wells 5 & 6 | 2026-03-27
EAST | March | On site for station check and sampling W11672797 Collected treated sample, 13:28, and verified free chlorine analyzer (mg/L) FCl - G 1.76; A 1.76 TCl - G 1.94 Collected well 5 raw, 13:32 Collected well 6 raw, 13:45 Recorded observations in the shared PWQ sheet Station and equipment okay | Stouffville Reservoir and Wells 5 & 6 | 2026-03-18
EAST | March | On site to work on halogen system installation. | Stouffville Reservoir and Wells 5 & 6 | 2026-03-26
EAST | March | On site for station check Recorded observations in the shared PWQ sheet Rotated reservoir sample line and pump Station and equipment okay | Stouffville Reservoir and Wells 5 & 6 | 2026-03-23
EAST | March | On site for preventative maintenance work orders Completed Generator test run JHSC inspection Chlorine analyzer maintenance Turbidity analyzer maintenance Housekeeping Genset: Performed pre and post run inspection Fuel Start 3098 L Stop 3064 L Hours Start 14.25 Stop 16.55 Reviewed genset run statistics - okay Station and equipment okay | Stouffville Reservoir and Wells 5 & 6 | 2026-03-05
EAST | March | On site for facility station check and equipment verifications Duty is not active for reservoir or high lift - res level is 84% Recorded data in PWQ sheets Reset fault on sample pump #1 - showing overcurrent fault on display Changed chlorine cylinders with Jack P (Left) tested for leaks, none observed Verified analyzer readings with grab residuals (Grab/Analyzer mg/L Influent FCL: 1.85 / 1.89 Effluent FCL: 1.81 / 1.79 Effluent TCL: 1.92 Reviewed trends, equipment ok Station ok | Stouffville Reservoir and Wells 5 & 6 | 2026-03-16
EAST | March | On site for station check Verified free chlorine analyzer and recorded observations in the shared PWQ sheet Station and equipment okay | Stouffville Highway 48 Booster Pumping Station | 2026-03-30
EAST | March | On site for station check and equipment verifications Recorded data in PWQ sheets Ran air compressor in hand to draw down level in pressure tanks a bit Verified analyzer reading - no adjustments needed Reviewed trends, equipment ok Station ok | Stouffville Highway 48 Booster Pumping Station | 2026-03-13
EAST | March | Verified effluent FCl, 10:26, in mg/L G 1.66; A 1.63 TCl grab: 1.79 Checked pressure tanks, inspected pipes, sensors, gauges and analyzers, all okay and meeting expectations. Recorded observations in the shared PWQ sheet Station and equipment okay | Stouffville Highway 48 Booster Pumping Station | 2026-03-02
EAST | March | On site for preventative maintenance Completed Chlorine analyzer maintenance Turbidity analyzer maintenance Station and equipment okay | Stouffville Highway 48 Booster Pumping Station | 2026-03-05
EAST | March | Attended site for station check Recorded observations and analyzer verification in the shared PWQ sheet Station and equipment okay | Stouffville Highway 48 Booster Pumping Station | 2026-03-06
EAST | March | On site for facility station check Readings in PWQ sheets Verified CL-17 analyzer reading Checked site and equipment Station ok | Stouffville Highway 48 Booster Pumping Station | 2026-03-20
EAST | March | On site for station check and equipment verifications Recorded readings in PWQ sheets Verified analyzer readings with grab residuals @09:25 Grab FCL: 1.55 mg/L / Analyzer: 1.53 mg/L Grab TCL: 1.63 mg/L Station and equipment ok | Stouffville Highway 48 Booster Pumping Station | 2026-03-16
EAST | March | Attended site for station check Verified free chlorine analyzer, 14:53, mg/L Effluent FCl - G 1.68; A 1.75 Effluent TCl - G 1.92 Recorded observations in the shared PWQ sheet Station and equipment okay | Stouffville Highway 48 Booster Pumping Station | 2026-03-26
WEST | March | -on site to complete station check -site out of service -site secure -no issues found | King City Wells 3 & 4 | 2026-03-02
EAST | March | Attended site for station check Recorded observations in the shared PWQ sheet Station and equipment okay | Stouffville Highway 48 Booster Pumping Station | 2026-03-23
WEST | March | -on site to complete station check -site out of service -site secure -no issues found -completed JHSC Health and Safety Inspection | King City Wells 3 & 4 | 2026-03-09
WEST | March | On site to check station. Site offline, facility secure. | King City Wells 3 & 4 | 2026-03-23
WEST | March | On site to inspect facility, no issues on site. | King City Wells 3 & 4 | 2026-03-17
WEST | March | -on site to complete station check and collect samples -sample work order # W11637596 -site offline and isolated from distribution system 09:47 - started well #3 in local running to waste at 25.5 l/s 09:47 - started well #4 in local running to waste at 26.5 l/s -checked equipment -reviewed trends -analyzer reagents ok -verified treated water chlorine analyzers: 09:57 - Analyzer readings: Free Chlorine = 0.01 mg/L Total Chlorine = 1.91 mg/L 09:57 - Grabs: Free Chlorine = 0.03 mg/L Total Chlorine = 1.86 mg/L 10:24 - collected weekly well #3 raw water micro. sample 10:24 - collected weekly well #4 raw water micro. sample -put both wells back into local off -no issues found | Kleinburg Wells 3 and 4 | 2026-03-04
WEST | March | -on site to complete station check and collect samples -sample work order # W11705756 -site offline and isolated from distribution system 09:30 - started well #3 in local running to waste at 25.6 l/s 09:30 - started well #4 in local running to waste at 26.7 l/s -checked equipment -reviewed trends -analyzer reagents ok -verified treated water chlorine analyzers: 09:34 - Analyzer readings: Free Chlorine = 0.02 mg/L Total Chlorine = 1.92 mg/L 09:34 - Grabs: Free Chlorine = 0.03 mg/L Total Chlorine = 1.92 mg/L 10:02- collected weekly well #3 raw water micro. sample 10:02 - collected weekly well #4 raw water micro. sample -put both wells back into local off -no issues found | Kleinburg Wells 3 and 4 | 2026-03-31
WEST | March | -on site to complete work orders -informed ROC of work -completed Diesel Generator Test Run -pre inspection ok 09:01 - transfer to generator power -ran KLPSWL pump #3 on generator power Start hours = 417.3 Stop hours = 418.6 Run time = 1.3 hours Start fuel = 1928 L Stop fuel = 1876 L Fuel used = 52 L -completed Deep Well Exhaust Valve, Maintenance -completed Pressure Relief Valve, Inspection -completed Turbidimeter Maintenance -cleaned and verified turbidimeter -completed Chlorine Analyzer, Maintenance -checked grit sand and electrolyte -flushed sample lines -zero calibrated influent and effluent FCL analyzers -verified analyzers after maintenance 09:52 - influent analyzer = 0.01 mg/L grab = 0.03 mg/L 09:54 - effluent analyzer = 0.00 mg/L grab = 0.02 mg/L 09:56 - Treated Analyzer readings: Free Chlorine = 0.01 mg/L Total Chlorine = 1.94 mg/L 09:56 - Treated Grabs: Free Chlorine = 0.02 mg/L Total Chlorine = 1.96 mg/L -completed Ventilation System - Exhaust Fans 10:09 - transfer back to utility power -no issues with generator test run -completed JHSC Health and Safety Inspection, Kleinburg Well 3/4 and Whisper Lane -completed Chlorine Cylinder Emergency Repair Kit Inspection -completed Manual Valve, Exercise -completed Chlorine Scrubber, Check -completed Chlorine Leak Detector, Test -completed Chemical System Inspection - Silicate -completed Ammonia System, Inspection -completed Chemical System Inspection - Chlorine -no issues, site back to normal operation | Kleinburg Wells 3 and 4 | 2026-03-10
WEST | March | -on site to complete station check and collect samples -site offline and isolated from distribution system 08:37 - started well #3 in local running to waste at 25.5 l/s 08:37 - started well #4 in local running to waste at 26.7 l/s -checked equipment -reviewed trends -analyzer reagents ok -verified treated water chlorine analyzers: 08:42 - Analyzer readings: Free Chlorine = 0.01 mg/L Total Chlorine = 1.91 mg/L 08:42 - Grabs: Free Chlorine = 0.01 mg/L Total Chlorine = 1.91 mg/L 09:12 - collected weekly well #3 raw water micro. sample - W/O# W11657170 09:12 - collected weekly well #4 raw water micro. sample - W/O# W11657170 -put both wells back into local off -no issues found | Kleinburg Wells 3 and 4 | 2026-03-11
WEST | March | -on site to complete station check and collect samples -site offline and isolated from distribution system -sample work order # W11690439 09:38 - started well #3 in local running to waste at 25.6 l/s 09:38 - started well #4 in local running to waste at 26.6 l/s -checked equipment -reviewed trends -analyzer reagents ok -verified treated water chlorine analyzers: 09:45 - Analyzer readings: Free Chlorine = 0.02 mg/L Total Chlorine = 1.90 mg/L 09:45 - Grabs: Free Chlorine = 0.06 mg/L Total Chlorine = 1.92 mg/L 10:16 - collected weekly well #3 raw water micro. sample 10:16 - collected weekly well #4 raw water micro. sample -put both wells back into local off -no issues found | Kleinburg Wells 3 and 4 | 2026-03-25
WEST | March | #NAME? | Schomberg Elevated Tank | 2026-03-31
WEST | March | -on site to complete station check -checked equipment -reviewed trends -analyzer reagents ok -verified treated water chlorine analyzers: 09:41 - Analyzer readings: Free Chlorine = 0.02 mg/L Total Chlorine = 2.10 mg/L 09:41 - Grabs: Free Chlorine = 0.03 mg/L Total Chlorine = 2.14 mg/L -no issues found | Kleinburg Wells 3 and 4 | 2026-03-27
WEST | March | -on site to complete station check and collect samples -sample work order # W11672975 -site offline and isolated from distribution system 09:10 - started well #3 in local running to waste at 25.4 l/s 09:10 - started well #4 in local running to waste at 26.6 l/s -checked equipment -reviewed trends -analyzer reagents ok -verified treated water chlorine analyzers: 09:19 - Analyzer readings: Free Chlorine = 0.02 mg/L Total Chlorine = 1.87 mg/L 09:19 - Grabs: Free Chlorine = 0.02 mg/L Total Chlorine = 1.83 mg/L 09:41 - collected weekly well #3 raw water micro. sample 09:41 - collected weekly well #4 raw water micro. sample -put both wells back into local off -no issues found | Kleinburg Wells 3 and 4 | 2026-03-18
WEST | March | On site to collect weekly bact sample (W11637544). Verified online common inlet/outlet chlorine analyzer via hach field kit. Collected sample for in house lab analyses. Entered readings into PWQ sheet. Common chlorine grab residual @ 10:10 Free: 0.03 mg/L Total: 3.45 mg/L Mono: 2.91 mg/L Analyzer: 3.49 mg/L Checked analyzer reagents-ok. Station operation normal, no issues on site. | Schomberg Elevated Tank | 2026-03-04
WEST | March | Onsite for station check Reviewed SCADA and trends Visual inspection of instrumentation and equipment Recorded station readings into pwq data sheet Common inlet/outlet -time 1436hrs Free grab 0.03 mg/l Total grab 3.48 mg/l analyzer 3.51 mg/l Post injection- time: 1441 hrs Free grab =0.05 mg/l Total grab =3.60 mg/l analyzer =3.56 mg/l | Schomberg Elevated Tank | 2026-03-02
WEST | March | Onsite to collect weekly bact sample (W11657095). Verified online common inlet/outlet chlorine analyzer via hach field kit. @12:18 Free grab: 0.05 mg/L Total: 3.62 mg/L Analyzer: 3.56 mg/L | Schomberg Elevated Tank | 2026-03-11
WEST | March | -on site to complete following work order -generator run - topped up generator - switched to emergency power -JHSC inspection: all ok | Schomberg Elevated Tank | 2026-03-10
WEST | March | On-site for station check Reviewed scada and trends, duty active, ET @ 32% and filling @ 2 l/s Verified chlorine analyzers readings Visual inspection on instrumentation and equipment AOK Chlorine grabs: @ 1206 hrs Outlet Grabs: Analyzer reading TCL = 3.60 mg/l TCL = 3.61mg/l FCL = 0.05 mg/l FCL = mg/l Chemical pumps: Chlorine: Hypo pump #1 in duty1 and running at 3% speed Dose scada: 3:4mL/min Hypo system pressure 600 kpa Activated duty for post chlorine injection grabs Chlorine Grab @ 1258 hrs Post Grabs: Analyzer reading TCL = 3.48 mg/l TCL = 3.48mg/l FCL = 0.04 mg/l FCL = mg/l Placed Hypo pump2 in manual off for the weekend due to fail to start issues Further troubleshoot required | Schomberg Elevated Tank | 2026-03-06
WEST | March | All trends checked and ok, all equipment checked and ok All measurements are in mg/l Common inlet outlet - 11:30 Total grab 3.45 vs analyzer 3.50 Free 0.04 Mono 2.99 Post injection - 11:40 Total grab 4.35 vs analyzer 4.36 Free 0.02 | Schomberg Elevated Tank | 2026-03-09
WEST | March | On site to collect weekly bact sample (W11690364) from outlet sample tap. Common inlet/outlet Free: 0.02 mg/L grab Total: 3.22 mg/L grab vs analyzer 3.17 mg/l Post injection Total: 3.61 mg/l grab vs 3.67 mg/l analyzer | Schomberg Elevated Tank | 2026-03-24
WEST | March | On site to collect weekly bact sample (W11672923) from outlet sample tap. Tested chlorine residuals via hach field kit. Free: 0.04 mg/L Total: 3.64 mg/L Changed common inlet/outlet analyzer reagents. Entered readings into PWQ sheet. | Schomberg Elevated Tank | 2026-03-18
WEST | March | SHETCS- Hypo Pump 1 failed to start, hypo pump 2 uncmd start. Called Jacob M. He is onsite working on them | Schomberg Elevated Tank | 2026-03-19
WEST | March | At site for Station check All equipment looks good and trends checked. All measurements are in mg/l Common inlet 11:10 Total: 3.59 grab vs 3.50 analyzer Free: 0.07 grab Mono: 2.98 Post injection Total: 4.40 vs 4.28 analyzer Free: 0.09 | Schomberg Elevated Tank | 2026-03-27
WEST | March | Onsite to complete work orders Completed hypo pump inspection Ran pumps to sight glass P1 135 ml/min P2 150 ml/min Placed hypo pump 2 in duty | Schomberg Elevated Tank | 2026-03-19
WEST | March | -on site for station check -checked trends: all ok -entered readings in PWQ: all ok -verified analyzer -pre injection 08:50: 3.33mg/l grab: 3.34mg/l -free cl grab: 0.04mg/l -post injection 09:00: 3.66mg/l grab: 3.64mg/l -reagents all ok -equipment all ok | Schomberg Elevated Tank | 2026-03-16
WEST | March | -on site to complete following work orders -manual valve exercise: all ok -drain valve exercise: all ok -heat trace inspection: all ok -chlorine analyzer maintenance- cleaned -took pre injection grab 11:00 -analyzer: 3.53mg/l grab: 3.50mg/l -took post injection 11:15 -analyzer: 3.50mg/l grab: 3.50mg/l -reagents all ok -low temp alarm test: -altitude valve inspection: all ok | Schomberg Elevated Tank | 2026-03-10
WEST | March | On site to inspect facility. Collected sample for in house lab analyses. Verified common inlet/outlet analyzer via hach field kit. Changed post injection analyzer reagents. Common inlet/outlet analyzer: 3.52 mg/L Grab total: 3.58 mg/L Grab free: 0.03 mg/L | Schomberg Elevated Tank | 2026-03-23
LINEAR | March | VNMCYS: Onsite to verify FIT installation Informed ROC Created CSE permit Verified mag flow meter installed correctly. Checked wiring. Potted. Installed clamp-on ultrasonic FIT and confirmed flow direction. At the time it was reverse flow and matched mag meter Closed CSE permit Informed ROC Left site | Linear Water System | 2026-03-10
LINEAR | March | T0530-07 Worked with North Rock to change AV in chamber T0530-07. It was completed and WM is back to normal. Total Cl2: 1.55mg/L Free Cl2: 0.02mg/L | Linear Water System | 2026-03-02
LINEAR | March | Worked with North Rock to install a new 100 mm air valve in chamber 69-10. Grab chlorine residual test as follows Free- 0.05mg/l Total- 1.26mg/l All isolated valves are open and the system is back to normal operation. | Linear Water System | 2026-03-04
LINEAR | March | Worked with North Rock replaced two air valves in chamber T9632-01 reopened isolation valves and cl2 residual is total cl2 ; 1.75 mg/L and free cl2; 0.03 mg/L. | Linear Water System | 2026-03-06
LINEAR | March | Worked with North Rock to install a new AV in T0528-10. Grab chlorine residual test as follows Free- 0.02mg/l Total- 1.57mg/l All isolated valves are open and the system is back to normal operation. | Linear Water System | 2026-03-17
LINEAR | March | Worked with North Rock to install a new air valve in chamber T0530-03. Grab chlorine residual test as follows Free- 0.03mg/l Total- 1.68mg/l All isolated valves are open and the system is back to normal operation. | Linear Water System | 2026-03-11
LINEAR | March | Worked with North Rock to replace air valves in chamber T0528-06 for the air valve mods project. Grab chlorine test results as follows Free- 0.0.2mg/l Total- 1.24 mg/l All isolated valves are open and the system is back to normal operation. | Linear Water System | 2026-03-03
LINEAR | March | Worked with North Rock to install AV?s in 3 chambers for contract #2. Grab chlorine residual test as follows Chamber 2 Free- 0.04mg/l Total- 1.53mg/l ChamberLS12 Free- 0.05mg/l Total- 1.55mg/l Chamber LS10 Free- 0.05mg/l Total- 1.58mg/l All isolated valves are open and the system is back to normal operation. | Linear Water System | 2026-03-20
WW-CEAST | March | -On site to perform a station check. -Entered station readings into SharePoint. -Checked drywell. -Checked screen room, raked rag bin, bar screen oil topped up, cleaned rags off conveyors and floor. -Pump 4 OOS. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-03-30
WW-CEAST | March | on site in response to high incoming flow and 5 pumps running. Throttled down Newmarket SPS, turned off Greenlane | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-03-31
WW-CEAST | March | -Remotely monitoring site during period of high flows. Periodically partially diverting to EQ tanks. Throttling flows down at Newmarket SPS to help slow incoming flows and get NMMC Manhole 2 Level below HiHi Alarms set point. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-03-31
WW-CEAST | March | -station check of site -reviewed SCADA -inspected site -entered data into SharePoint -pump floor inspection/cleaning -cleaned screen room/rotated bins as necessary -dump pad heat trace inspection -station okay | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-03-06
WW-CEAST | March | LOTO Drain pump 1 piping Lift pump and put new gasket between piping and pump. Reinstall pump and flood Pump has leakage alarm. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-03-03
WW-CEAST | March | Check Harry Walker for wires for pump 4. None on site. Complete pump PM?s on pumps 1,2,3,5,&6. Added 50 grams of grease to lower bearings while pump running. Checked seal leakage chamber. Topped up coolant in cooling jackets as required, detailed in work orders. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-03-05
WW-CEAST | March | On site to install pump one motorized valve programming did not match pump six faults indicated when testing will return tomorrow to troubleshoot | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-03-02
WW-CEAST | March | -station check of site -reviewed SCADA -inspected site -entered data into sharepoint -pump 1 and 4 are OOS, 4 pumps available -station okay | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-03-02
WW-CEAST | March | -station check of site -reviewed SCADA -inspected site -entered data into SharePoint -cleaned screen room and rotated bins -station okay | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-03-09
WW-CEAST | March | #NAME? | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-03-10
WW-CEAST | March | -station check of site -reviewed SCADA -entered data into SharePoint -inspected site -rotated bin in screen room -pumps 1 and 4 manual off, duty 7, maintenance working on them -on site for monthly work orders -Air Compressor Inspection -Air Dryer Inspection -JHSC Inspection -bins out for pickup, cleaned screen room -pump 1 back to auto duty 1, running with no issues -5 pumps available in auto, pump 4 OOS -backflushed line 2 at dump pad, cleared alarm, back to available -station okay | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-03-04
WW-CEAST | March | Adjusted pump duty 3,4, and 5 start/stop setpoint for early duty activation in response to high flow. Original set point: D3(4.90/5.70) D4(5.80/6.40) D5(6.60/7.10) Changed setpoint: D3(4.80/5.60) D4(5.70/6.30) D5(6.40/7.00) | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-03-11
WW-CEAST | March | On site to troubleshoot line 3 overtorque alarm. Back flushed the line to clear blockage and cleared the alarm Put line 3 back in service. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-03-12
WW-CEAST | March | -station check of site -reviewed SCADA -inspected site -entered data into SharePoint -high flows at AUSS, 5 pumps active, wet well slowly coming down -put ISS East FM valve back to remote in case ISS pumps need to run -cleaned screen room, rotated bin as necessary -air compressor inspection -dump pad inspection/cleaning -EQ OCF inspection -station okay -giving a tour to IAM department around 14:00 today | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-03-11
WW-CEAST | March | -left site to assist Kevin Shaji at Newmarket PS to unclog Pump 4 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-03-09
WW-CEAST | March | -station check of site -reviewed SCADA -entered data into SharePoint -inspected site -cleaned screen room and rotated bin -station okay | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-03-13
WW-CEAST | March | -on site for monthly work orders -Aurora SPS Consolidated Wetwell and Outfall Inspection -Monthly Surge Tank Inspection -Aurora EQ Tipping Bucket Test -outfall is okay, creek is well below duckbill -pump 1 was tested from the request of maintenance, leakage alarm came in, pump 1 is manual off, duty 7 -pump 4 is OOS -4 pumps available -Housekeeping of site, cleaned up garbage on all levels -station okay | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-03-03
WW-CEAST | March | -at 09:00 met CPD and the contractors who are doing the gravity sewer clean out south of Bloomington, the contractors put their locks on the already locked out valves before they started their work -on site for station check -reviewed SCADA -inspected site -entered data into SharePoint -inspected air compressors -cleaned screen room, rotated bins as necessary -station okay -met contractor at 5:15 to get their locks off the LOTO valves | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-03-25
WW-CEAST | March | Cut and replaced gasket on fuel primer pump for generator 3. Work on basement cleanup | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-03-19
WW-CEAST | March | -on site to pump out ISS actuated valve chamber, which has the two actuated valves for the two ISS pumps, the chamber has a leak in the roof from a crack which let's ground water in, a sump pump should be installed in this chamber to prevent future floods -AUSSSR line 2 overtorque, flushed line, reset alarms, line 2 back in service -put East Forcemain back online, removed LOTO of East FM discharge valve, ISS East discharge valve, East surge tank valves, all pump east forcemain valves back to remote/auto, East FM back to online in setpoints -station okay, contractors are on site still | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-03-26
WW-CEAST | March | On sit with Total Lift for inspections | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-03-18
WW-CEAST | March | On site to test run generator 3 after CMS fixed the defective fuel filter primer. Ran tested in manual without load, it was observed that the fuel filter primer that was installed is leaking a bit like one drop per second. Put generator 3 back in out of service and informed CMS (Terry C. and Bill VB.) | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-03-19
WW-CEAST | March | -station check of site -reviewed SCADA -inspected site -entered data into SharePoint -inspected overflow sampling kit -cleaned screen room, raked out bin -station okay | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-03-16
WW-CEAST | March | -station check of site -reviewed SCADA -inspected site -entered data into sharepoint -cleaned screen room, rotated bin as necessary -inspected generator 3, back to auto/available -station okay | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-03-20
WW-CEAST | March | Pick up and replace broken fuel primer pump for generator 3 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-03-18
WW-CEAST | March | -station check of site -reviewed SCADA -inspected site -entered data into sharepoint -station okay | Newmarket Green Lane Pumping Station | 2026-03-30
WW-CEAST | March | On site to investigate alarms- Generator 1 Warning//Engine Battery Low Volts. Upon arrival noticed acid odours and fumes coming out of battery cells for generator 1. Requested ROC to connect to an electrician. As per the electrician request, battery charger is turned off and generator 1 is turned off. Electrician on the way to fix the issue with battery. Daniel Boate replaced the 2 old batteries with new ones. Run the generator to test the new batteries and no issues were found on startup. All generator 1 related alarms cleared on scada. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-03-14
WW-CEAST | March | -On site to complete work orders. -Alectra on site for hydro meter replacement. Discovered meter due for replacement was for solar power, so no disruption to station power is needed. -0855 - Transferred station to generator power. -Upon transfer to generator power, Generator 3 fuel filter primer cap blew out of the filter causing diesel fuel to spill onto ground. Immediately stopped Generator 3 and used absorbent pads to contain and clean up fuel spill. -0956 - Transferred site back to utility power. -Monthly diesel generator test run completed, readings entered into SharePoint. -Generator 1: Start: 629.3hrs, Stop: 630.4hrs, Run time: 1.1hrs. -Generator 2: Start: 621.5hrs, Stop: 622.6hrs, Run time: 1.1hrs. -Generator 3: Start: 825.3hrs, Stop 825.3hrs. -Generator 3 OOS until repairs can be made. -Station check completed, readings entered into SharePoint. -Checked drywell. -Air compressors, inspection and cleaning completed. -Checked screen room, changed out rag bin, bar screen oil topped up. -Bar screen rag bin removal completed, bins out for pick up. -Pump 4 OOS, Generator 3 OOS. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-03-18
WW-CEAST | March | -station check of site -reviewed SCADA -entered data into sharepoint -inspected site -received email/call at 09:44 from Daniel Kim regarding an odour complaint that came in north of AUSS -began investigating odour complaint thoroughly for 2-3 hours, completed Part A of Odour Complaint Form -all odour complaint findings can be found under Complaint ID#: 222 -facility is operating normally, chemical dosing systems to reduce H2S are operating normally, all rag bins are stored inside with doors sealed, no disruptions to pumping system | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-03-27
WW-CEAST | March | -station check of site -reviewed SCADA -inspected site -entered data into SharePoint -rotated bin in screen room, cleaned screen room -reset pump 1 for discharge valve fault -pump 4 remains OOS, 5 pumps available -locked out and tagged out East Forcemain for gravity sewer cleaning south of Bloomington: all 6 pumps east discharge valves are in local stop, east surge tanks valve are closed and depowered, East forcemain common discharge valve is local closed, and depowered, ISS east discharge valve is local closed, in local stop -setpoints on SCADA show East is not in service, west forcemain is manually selected as in service -notified ROC and CEWW of East Forcemain OOS -station okay | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-03-23
WW-CEAST | March | Station readings taken and updated on sharepoint. Reviewed trends, ok. both pumps available in all stop auto duty rotation station ok, no issues. JHSC Health and Safety Inspection completed. | Newmarket Green Lane Pumping Station | 2026-03-02
WW-CEAST | March | @ 8:30am - turned all pumps off in manual to throttle down flow going to Aurora SPS | Newmarket Green Lane Pumping Station | 2026-03-31
WW-CEAST | March | Station readings taken and updated on sharepoint. Reviewed trends, ok. both pumps available in all stop auto duty rotation station ok, no issues. | Newmarket Green Lane Pumping Station | 2026-03-13
WW-CEAST | March | Station check complete and the readings have been entered into the sharepoint | Newmarket Green Lane Pumping Station | 2026-03-06
WW-CEAST | March | Put both pumps in local to prevent backup mode to start the pumps | Newmarket Green Lane Pumping Station | 2026-03-11
WW-CEAST | March | Completed workorders. Wet well High level alarm test. Received and confirmed by ROC RS pump inspection. Pump #1- 40% = 175.8 L/s. Pump #2- 40% = 272.5 L/s. | Newmarket Green Lane Pumping Station | 2026-03-18
WW-CEAST | March | Station readings taken and updated on sharepoint. Reviewed trends, ok. both pumps available in all stop auto duty rotation station ok, no issues. overflow kit inspection completed | Newmarket Green Lane Pumping Station | 2026-03-16
WW-CEAST | March | Remotely put pumps OOS/Manual in response to high flow event. | Newmarket Green Lane Pumping Station | 2026-03-11
WW-CEAST | March | Station readings taken and updated on sharepoint. Reviewed trends, ok. both pumps available in all stop auto duty rotation station ok, no issues. | Newmarket Green Lane Pumping Station | 2026-03-09
WW-CEAST | March | -On site for lab analysis and sludge handling. -Decanted STT to headworks, then emptied tank into SHT. -Added two bags of soda ash to each aeration tank. -Completed lab analysis, entered results into SharePoint. -Batch wasted 8m3, ran RAS pumps at 100% speed when returning to service. -Verified alum dosing and sand filter operation. -Clarifier 1 OOS, WAS Pump 2 OOS, RAS Pump 3 OOS, UV Bank 1A OOS, OCU OOS. | Mount Albert Water Resource Recovery Facility | 2026-03-29
WW-CEAST | March | Weather today is Partly Cloudy and 10 Celsius -On site to complete work order W11699719, W11698764, W116761554, W11699274, W11699499, W11699512. -Completed station check. -Entered station readings into SharePoint. -Completed Sludge Processing. -Bar Screen Bin, Removal and Replacement. -Post Aeration Alum mixing chamber and RAS/WAS inlet channel inspection/cleanout. -Added two bags of soda ash to each aeration tank. -Clarifier 1 still OOS and, presently filling with effluent water in preparation to put it back in service. -Alum delivery/Receiving started at 1.16 m filled to 3.79 m. | Mount Albert Water Resource Recovery Facility | 2026-03-30
WW-CEAST | March | Completed in-house lab Analysis (See details on SharePoint) Decanting STT into the Headworks. Transferred the sludge and processing. Batch wasted 5m3. Added 2 bags of soda ash into each aeration tank. | Mount Albert Water Resource Recovery Facility | 2026-03-30
WW-CEAST | March | On site to complete work order. Lab Analysis (See results on SharePoint) and Sludge Processing. STT decanted, afterwards, remaining sludge dumped into the SHT. Based on the SCADA trends there is no flow coming into the WRRF from the Mt Albert PS between 3:30am up to 9:35am, due to the power failure happened at the Mt Albert PS. Lagoon level at around 11:00am is at 102 inches. Added two bags of Soda Ash into each Aeration Tanks. Batch wasted 10m3 from clarifier 2. Clarifier 1 still out of service. | Mount Albert Water Resource Recovery Facility | 2026-03-31
WW-CEAST | March | -on site for lab analysis and sludge handling -reviewed SCADA -inspected site -entered data into sharepoint -started decanting sludge thickening tank -wasted sludge in thickening tank to sludge holding tank -added 4 bags of soda ash to aeration tanks -lab completed -sludge handling completed -wasted 10 m3 of sludge from clarifiers to thickening tank -station okay | Mount Albert Water Resource Recovery Facility | 2026-03-05
WW-CEAST | March | Phil and I here to fix the hose on the de-cant pump. Brought the pump up and disconnected the hose and cut about a foot off the end and re-attached it back onto the de-cant pump. Lowered pump down and set the level up so its pumping clear liquid. Flow coming out of the pump is much better. Lots of hose left if we need to cut more off. | Mount Albert Water Resource Recovery Facility | 2026-03-02
WW-CEAST | March | On site completed Lab Analysis (See results on SharePoint) and Sludge Processing. STT decanted, afterwards remaining sludge dumped into the SHT. Added two bags of Soda Ash into each Aeration Tanks. Clarifier 1 still draining into the lagoon. Checked Alum dosing injection points at prefilter and post aeration. Removed rags from the inlet/outlet sluice gates at aeration tanks. Also, collected weekly sewage samples under YD #W11656931. | Mount Albert Water Resource Recovery Facility | 2026-03-11
WW-CEAST | March | Here to continue the draining of Clarifier 1 - put RAZ pump 3 in manual on at 50% and also completed the Lab sheet for Sunday (small lab). I had to slow down the flow on RAZ pump 3 due to UV train 1 coming on/off quit frequently due to the higher flows. Entered the results from the Lab into Sharepoint and put the station back to normal ops at the end of the day. Ammonia was a little Hi but the rest of the Lab was OK. | Mount Albert Water Resource Recovery Facility | 2026-03-07
WW-CEAST | March | On site completed work orders. Station Check (See details on SharePoint). STT decanted, afterwards remaining sludge dumped into the SHT. STT hosed down after decanting. Added two bags of Soda Ash into each Aeration Tanks. Checked Alum dosing injection points at prefilter and post aeration. Removed rags from the inlet/outlet sluice gates at aeration tanks. Consolidated Headworks Building Inspection Grit Vortex Travelling Screen Dewatering Press Screening Press | Mount Albert Water Resource Recovery Facility | 2026-03-12
WW-CEAST | March | Weather today Partly cloudy and -1 Celsius. -On site to complete work order W11661150, W11660965, W11660939. -Completed Lab Analysis and Sludge Processing. -Entered lab analysis readings into SharePoint. - Post Filtration/UV channel hose down. -RAS/WAS inlet channel inspection/cleanout. -Wasted 4m3 from clarifier #1. | Mount Albert Water Resource Recovery Facility | 2026-03-12
WW-CEAST | March | -On site to perform a station check. -Entered station readings into SharePoint. -Verified alum dosing and sand filter operation. -Cleaned out grease and solids from Clarifier 1 inner ring. -Traveling screen and OCU remain OOS. | Mount Albert Water Resource Recovery Facility | 2026-03-05
WW-CEAST | March | Weather today Partly Cloudy and 9 Celsius -On site to complete work order W11651437, W11651087, W11651073, W11651059, W11650205. -Completed station check. -Entered station readings into SharePoint. - RAS Pumps 1,2, and 3 Inspection. - WAS Pumps 1and 2 Inspection. - Scum Pumps 1and 2 Inspection. - Sump Pumps Maintenance. | Mount Albert Water Resource Recovery Facility | 2026-03-10
WW-CEAST | March | Removed south clarifier, gearbox and motor | Mount Albert Water Resource Recovery Facility | 2026-03-10
WW-CEAST | March | On site completed work orders. Lab Analysis (See results on SharePoint) and Sludge Processing STT decanted after decant pump hose fixed by Philip R. and Terry R. Dumped remaining sludge into SHT. Station Check (See details on SharePoint). Added two bags of Soda Ash into each Aeration Tanks. Checked Headworks, raked rags from the manual bar screen. Checked DO Probes, removed rags dangling from the probes. Checked Alum dosing injection points at prefilter and post aeration. Batch wasted 10m3. Ran RAS Pumps 1 and 3 to 100% to get desired flows of around 13 L/s. Post Aeration Alum Mixing Chamber Cleaned Out Removed rags from the inlet/outlet sluice gates of Aeration Tanks. | Mount Albert Water Resource Recovery Facility | 2026-03-02
WW-CEAST | March | -On site for sludge handling and lab analysis. -Added two bags of soda ash to each aeration tank. -Unable to decant STT. Hose has multiple holes right above connection to decant pump and is producing no flow. Emptied approximately 2m out of STT to make room for auto wasting tonight. -Raked manual bar screen. -Completed lab analysis and entered results into SharePoint. -Ran RAS pumps at 100% speed for several minutes. -Verified sand filter operation and alum dosing. -Cleaned solids off top of post aeration alum chamber. -Verified clarifier heater are both still running. -OCU and traveling screen remain OOS. | Mount Albert Water Resource Recovery Facility | 2026-03-01
WW-CEAST | March | Completed in-house lab Analysis (See details on SharePoint) Decanting STT into the Headworks. Transferred the sludge and processing. Added two bags each of Soda Ash into each Aeration Tanks Removed rags from the sluice gates of Aeration Tanks Post Filtration/UV channel hose down. Clarifier #1 taken OOS due to gearbox issue. Emptying clarifier #1 now. Bar screen put back to service. | Mount Albert Water Resource Recovery Facility | 2026-03-06
WW-CEAST | March | On site completed work orders. Lab Analysis (See results on SharePoint) and Sludge Processing Decanting STT started. Station Check (See details on SharePoint) Checked DO Probes, ok. Checked Alum dosing injection points at prefilter and post aeration, ok. Also, collected weekly and monthly sewage samples under YD #s W11637306, W11637092, W11637362 and W11637028. Out around 11:00am, to collect sewage samples at Mt Albert PS. Back at 12:30pm, to continue completing work orders. Decanting STT done, afterwards remaining sludge dumped into the SHT. Batch wasted 10 m3. Ran RAS Pumps 1 and 3 at 100% speed to get desired flows of around 13 L/s at 0% auto speed setpoint. They are running at 12% auto speed before that with around 13 L/s flows. Added two bags of Soda Ash into each Aeration Tanks, one in the morning and one in the afternoon. Removed rags from the inlet/outlet sluice gates of Aeration Tanks. Raked rags from the manual bar screen. As per Bill VB (CMS TL), mechanical bar screen gear box is defective, need new one. | Mount Albert Water Resource Recovery Facility | 2026-03-04
WW-CEAST | March | Completed in-house lab Analysis (See details on SharePoint) Station Check (See details on SharePoint). Decanting STT into the Headworks. Transferred the sludge and processing. Added two bags each of Soda Ash into each Aeration Tanks | Mount Albert Water Resource Recovery Facility | 2026-03-15
WW-CEAST | March | -On site to complete work orders. -Added two bags of soda ash to each aeration tank. -Raked manual bar screen. -Cleaned out RAS inlet chamber and post aeration alum chamber. Cleaned rags off aeration tank inlet gates and DO probes. -Station check completed, readings entered into SharePoint. -Verified alum dosing and sand filter operation. -Monthly diesel generator test run completed, readings entered into SharePoint. -1013 - Transferred station to generator power. -1122 - Station transferred back to utility power. -Generator start hours: 492.3, stop hours: 493.5, run time: 1.2hrs. -Switched grit bins following pick up. -Clarifier scum system cleaning completed. Cleaned out clarifier scum troughs, hosed down walls of scum tank and ran Scum Pump 1 in local to pump out tank following cleaning. -Traveling screen and OCU remain OOS. | Mount Albert Water Resource Recovery Facility | 2026-03-03
WW-CEAST | March | Installed barscreen drive motor Electricians wired motor Tested okay. | Mount Albert Water Resource Recovery Facility | 2026-03-06
WW-CEAST | March | Put two bags of soda ash into the aeration tanks and set two up for later,, started the de-cant pump as well as RAZ pump 3 to continue emptying clarifier 1. Completed the Lab work and entered results into Sharepoint. Ammonia still Hi but the rest of the Lab looks fine. added the other two bags of soda ash and put the station back to normal operation. Clarifier 1 is about 3/4 empty now. | Mount Albert Water Resource Recovery Facility | 2026-03-08
WW-CEAST | March | Weather today Heavy rian and 3 Celsius -On site to complete work order W11655956, W11651680, W11627876. -Completed station check. -Entered station readings into SharePoint. -JHSC Health and safety inspection. -Alum chemical system flush. | Mount Albert Water Resource Recovery Facility | 2026-03-11
WW-CEAST | March | Check south clarifier and found drive motor gear assembly needs replacement. Requested quote for new assembly. | Mount Albert Water Resource Recovery Facility | 2026-03-06
WW-CEAST | March | -On site to respond to Clarifier 2 Fault Alarm, reported by ROC. -Found Clarifier 2 with a Torque Alarm on MCC. -Manually backed up clarifier 2 arm, cleared faults, and ran in auto. Repeated this several times, each time Clarifier 2 would run a little bit longer before the Torque Alarm came back in. Inspected clarifier gearbox and found that heater was running, but gearbox was full of chunks of a frozen water/oil mixture. Drained as much water as possible from gearbox and added in new oil. Turned up temperature on heater slightly and used propane torch to help thaw out gearbox. Torque reading on Clarifier 2 has dropped from approximately 45 to 25 and is continuing to slowly decrease. Left heater running, but repositioned against opposite wall. -Clarifier 2 is back in auto and running. | Mount Albert Water Resource Recovery Facility | 2026-03-01
WW-CEAST | March | On site completed Station Check (See details on SharePoint). STT decanted, afterwards dumped remaining sludge into the SHT. Added two bags of Soda Ash into each Aeration Tanks. Checked Headworks, ok. Checked DO Probes, removed rags dangling from the probes. Checked Alum dosing injection points at prefilter and post aeration. Removed rags from the inlet/outlet sluice gates of Aeration Tanks. Also, at around 10:30am, 4Refuel delivered diesel fuel, 800.4 L. Tanks previous level: 58.6cm/471L and 56.9cm/455L Tanks level after delivery: 102.0cm/859L and 100.9cm/849L. | Mount Albert Water Resource Recovery Facility | 2026-03-09
WW-CEAST | March | Completed in-house lab Analysis (See details on SharePoint) Decanting STT into the Headworks. Transferred the sludge and processing. Batch wasted 5m3 from clarifier #2. filter reject drain line flush completed. Added 2 bags of soda ash into each aeration tank. Created WO# W11722223 to fix water scour line leak for grit vortex 1. | Mount Albert Water Resource Recovery Facility | 2026-03-10
WW-CEAST | March | put two bags of soda ash into the aeration tanks and set two up for later. Started grabbing samples for the Lab and Daniel had switched WO to Kevin,, went through the station and sand filters working great and started de-cant pump. Clarifier 1 arm stopped turning, got a hold of Bill (maintenance) and he's on his way. Cleaned out the post aeration tank as well as the inlet gates while waiting. There was no Hazardous waste to dispose of and went through the weekly alarm management for EOC and YDOC and there were no changes to either site. Started emptying clarifier #1 due to gear box in motor is broken - Daniel showed up and walked us through switching everything over. Continued draining for two hours and i'll be in on the weekend to complete. Bill and Terry - maintenance got the bar screen working again so we closed off the by-pass and now flow is going through the bar screen. Clarifier 1 is down but the rest of the station is running fine. | Mount Albert Water Resource Recovery Facility | 2026-03-06
WW-CEAST | March | On site completed work orders. Lab Analysis (See results on SharePoint) and Sludge Processing STT decanted, afterwards remaining sludge dumped into the SHT. Ran RAS Pumps 1 and 3 at 100% speed to get desired flows of around 13 L/s at 0% auto speed setpoint. They are running at 17% auto speed before that with around 14 L/s flows. Sand Filter Filter-Reject Drain Line Flushed Dissolved Oxygen Meter Verification Checked DO Probes, ok. Checked Alum dosing injection points at prefilter and post aeration, ok. | Mount Albert Water Resource Recovery Facility | 2026-03-03
WW-CEAST | March | On site completed work orders. Station Check (See details on SharePoint). STT decanted, afterwards remaining sludge dumped into the SHT. Added two bags of Soda Ash into each Aeration Tanks. Checked Alum dosing injection points at prefilter and post aeration. Removed rags from the inlet/outlet sluice gates at aeration tanks. Weekly alarm management - only clarifier 1 no RAS pump running is the alarm due to clarifier 1 out of service. Clarifier 1 sludge cleanout - ACCUWORX on site to clean clarifier 1 in preparation for the gear box repair/replacement. | Mount Albert Water Resource Recovery Facility | 2026-03-13
WW-CEAST | March | Weather today Overcast and -2 Celsius. -On site to complete work order W11663911, W11660952, W11651121. W11730157. -Completed Lab Analysis and Sludge Processing. -Entered lab analysis readings into SharePoint. - Air Compressors 1-2, Cleaning & Inspection. - Post Aeration Alum mixing chamber cleanout. -Wasted 3m3 from clarifier #1. - Clarifier 1 sludge cleanout - ACCUWORX on site to clean clarifier 1 in preparation for the gear box repair/replacement. | Mount Albert Water Resource Recovery Facility | 2026-03-13
WW-CEAST | March | On site for leak at vortex solenoid outlet piping. Operators drained vortex. Backed off piping, cleaned threads, and applied new thread tape. Reinstalled piping and tightened union. Had operations run water scour to open solenoid. No leaks detected. Removed isolation gates to allow flow back to vortex. Rechecked for leaks okay. Complete. | Mount Albert Water Resource Recovery Facility | 2026-03-24
WW-CEAST | March | On site for Station Check, Lab Analysis and Sludge Processing. Completed lab analysis (See results on SharePoint) Decanted STT. Dumped remaining sludge into the SHT. Added 2 bags of Soda Ash into each Aeration Tanks. Checked DO Probes. Removed rags dangling on the probes. Removed rags from the inlet/outlet sluice gates of Aeration Tanks. Checked Alum dosing injection points at prefilter and post aeration, ok. | Mount Albert Water Resource Recovery Facility | 2026-03-21
WW-CEAST | March | Weather today Mostly cloudy and -10 Celsius. -On site to complete work order W11669544, W11669735, W11740565, W11664220. -Completed Lab Analysis and Sludge Processing. -Entered lab analysis readings into SharePoint. - Sand Filter Filter-Reject Drain Line Flush. -Clarifier 1 sludge cleanout - ACCUWORX on site to clean clarifier 1 in preparation for the gear box repair/replacement. - Training, IMS Emergency Procedure Quiz | Mount Albert Water Resource Recovery Facility | 2026-03-17
WW-CEAST | March | On site with Total Lift for annual inspections | Mount Albert Water Resource Recovery Facility | 2026-03-19
WW-CEAST | March | Went through alarm management for the WRRF this morning,, all alarms that are shelved are still currently OOS | Mount Albert Water Resource Recovery Facility | 2026-03-23
WW-CEAST | February | Put two bags of soda ash into the aeration tank and set two up for later,, started the de-cant pump as well. Cleaned the washroom in the sand filter room (this time the appliances-not the floor) and then took the traveling bar screen apart so maintenance could have a look. Cleaned out the back and a big wad on the top before the brush, washed the inside down with the hose to get it as cleaned out as possible. Pulled the de-cant pump up after emptying the thickening tank and cleaned out the bottom of the pump. Went through the station - sand filters and clarifiers all working well. Went through the alarm management the only problem we have here is the Odour Control and it is shelved and still OOS. | Mount Albert Water Resource Recovery Facility | 2026-02-27
WW-CEAST | March | -On site to respond to Alum Pump Containment Flood Alarm, reported by ROC. -Upon arrival to site, found alum pump containment area filled with water, likely from previous effluent line break. Inspected alum pumps and chemical lines, as well as nearby water line and found no sign of a leak. Alum trends also appear normal. Pumped out water from containment area, but am unable to reset Alum Pump Containment Flood Alarm on SCADA. Containment area is currently dry with no signs of a leak. Will have to investigate flood alarm float issue further tomorrow. | Mount Albert Water Resource Recovery Facility | 2026-03-26
WW-CEAST | March | On site completed work orders. STT decanted. Dumped remaining sludge into the SHT afterwards. Orlando B. (Sludge hauler) called, he cannot make it today due to weather related issue, he is behind with other facilities. Completed Lab Analysis (See results on SharePoint) Station Check (See details on SharePoint) Added two bags of Soda Ash into each Aeration Tanks. Checked DO Probes, ok. Checked Alum dosing injection points at prefilter and post aeration, ok. Removed rags from the inlet/outlet sluice gates of aeration tanks. Batch wasted 10m3 from Clarifier 2. At 2:00pm, Alum dosage increased from 15 mg/L to 20 mg/L at the prefilter. Found effluent pumps in off position at the panel. Put back in auto. | Mount Albert Water Resource Recovery Facility | 2026-03-20
WW-CEAST | March | Put in 2 bags of soda ash and set 2 up for later,, Kevin started de-cant pump and then I worked with Kevin on his Lab work to speed it up and get a lot more organized. Went through the station, UV bank 1 is OOS - sand filters working great. Checked the hoist in the aeration room and the sand filter room - all good. Cleaned out the post aeration tank and the inlet channel gates, Washed down the UV channel and shut down the effluent pumps for the night to make sure we have no breaks again. Hopefully this helped Kevin out with his Lab work, UV 1 is OOS along with clarifier 1 the rest of the station is running fine. | Mount Albert Water Resource Recovery Facility | 2026-03-19
WW-CEAST | March | On site for the Weekend Sludge Handling/Processing. STT decanted. Dumped remaining sludge into the SHT afterwards. Checked DO Probes, ok. Checked Alum dosing injection points at prefilter and post aeration. Added two bags of Soda Ash into each Aeration Tanks. Checked Headworks. Cleaned/hosed down screen room. At 9:57am, Dewatering Screw, Grit System 1 and 2 Faulted. Cleared/reset alarms at the panel. All back in auto and in service. Removed rags from the inlet/outlet sluice gates of Aeration Tanks. Batch wasted 10 m3 on Clarifier 2. Clarifier 1 still out of service due to gear box issue. Also, completed Lab Analysis (See results on SharePoint). | Mount Albert Water Resource Recovery Facility | 2026-03-22
WW-CEAST | March | Weather today Overcast and 0 Celsius. -On site to complete work order W11682416, W11682185, W11681950, W11681937, W11681610, W11681098. -Completed station check and lab analysis. -Entered station readings and lab analysis into SharePoint. -Completed Sludge Processing. -Bar Screen Bin, Removal and Replacement. -Post Aeration Alum mixing chamber and RAS/WAS inlet channel inspection/cleanout. -Added two bags of soda ash to each aeration tank. | Mount Albert Water Resource Recovery Facility | 2026-03-23
WW-CEAST | March | Put 2 bags of soda ash in and set 2 up for later,, started de-cant pump. Went through the blowers , had to top up 3. Checked the Lagoon from on top of the clarifier cat walk - all looks good, no breaks | Mount Albert Water Resource Recovery Facility | 2026-03-17
WW-CEAST | March | Replace battery in tow motor and verified unit is charging. | Mount Albert Water Resource Recovery Facility | 2026-03-17
WW-CEAST | March | Weather today Mostly cloudy and 11 Celsius. -On site to complete work order W11667140, W11667069, W11666578. -Completed Lab Analysis and Sludge Processing. -Entered lab analysis readings into SharePoint. -Bar Screen Bin, Removal and Replacement. | Mount Albert Water Resource Recovery Facility | 2026-03-16
WW-CEAST | March | Put 4 bags of soda ash in and started de-cant pump,, Daniel and I isolated the inlet at the headworks and are diverting flow to the lagoon (@ approx. 08:25 ) Put 3 knife gates in place to re-direct flow to the lagoon. Accuworxs here and are pumping down post aeration tank, Retrieved the grating at approx. 14:00 hrs and then put the station back to normal ops by removing gates from the headworks. Station back to normal ops - clarifier 1 and UV bank 1A are still OOS. | Mount Albert Water Resource Recovery Facility | 2026-03-23
WW-CEAST | March | Completed in-house lab Analysis (See details on SharePoint) Station Check (See details on SharePoint). Decanting STT into the Headworks. Transferred the sludge and processing.. Added two bags each of Soda Ash into each Aeration Tanks Post Filtration/UV channel hose down. | Mount Albert Water Resource Recovery Facility | 2026-03-19
WW-CEAST | March | On site with GFL for adhoc post aeration tank clean out to retrieve the grating that fell in last week. Started diverting to lagoon @ 8:25 am, pumping station flow totalizer @ 382m3. Dropped in 2 slide gates to isolate inlet chamber. Slide gate not perfectly water tight, about 10% going pass the gate. @14:00, Accuworx was able to drawdown the chamber to near bottom. Ops performed CSE to get the grating out. @14:15, all gates inserted in the headworks has been removed, valve to clarifier 2 has been re-opened. Both RAS put back in service | Mount Albert Water Resource Recovery Facility | 2026-03-23
WW-CEAST | March | On site to complete work orders. Station Check (See details on SharePoint) At around 09:50am, Barry and I found the effluent water pipe leaking at the union connection in the process building (Filter Room) near the entrance door. Put effluent pumps in manual/off. Sump pump in the basement was able to keep up with the leak. Work request created for CMS. Also, UV bank 1B has a major fault status. tried to run in manual but there is no lights on the nodules. Alarm can be cleared/reset but it keeps on coming back. Work request created for CMS. Added two bags of Soda Ash into each Aeration Tanks. Post aeration alum mixing chamber clean out. Removed rags from the inlet/outlet sluice gates of Aeration Tanks. Checked DO Probes, ok. Checked Alum dosing injection points at prefilter and post aeration. Decanted STT. Dumped remaining sludge into the SHT afterwards. | Mount Albert Water Resource Recovery Facility | 2026-03-16
WW-CEAST | March | On site to complete work orders. Vortex Grit System 1 isolated and water pumped out in preparation for the repair of leaking water scour line. Vortex Grit System 1 back in service after repair (See Terry C.) eLogbook entry above. Flushed Sand Filter-Filter Reject Drain Line Partially did housekeeping. | Mount Albert Water Resource Recovery Facility | 2026-03-24
WW-CEAST | March | Weather today Partly cloudy and 8 Celsius. -On site to complete work order W11682416, W11692183, W11692096, W11756498. -Completed lab analysis. -Entered lab analysis readings into SharePoint. -Completed Sludge Processing. -Post Filtration/UV channel hose down. - Admin area cleaning. -Added two bags of soda ash to each aeration tank. -Clarifier 1 and UV bank 1A are still OOS. -Clarifier 1 sludge cleanout - ACCUWORX on site to clean clarifier 1 in preparation for the gear box repair/replacement. | Mount Albert Water Resource Recovery Facility | 2026-03-26
WW-CEAST | March | Check on generator rpm and voltage fluctuations Ran generator without load for approximately 30 minutes RPM stayed at 1805-1806 Voltage stayed at 599-601 V Recommend inspecting during next full transfer. No issues at this time. | Mount Albert Water Resource Recovery Facility | 2026-03-24
WW-CEAST | March | arrived on site to respond to UV bank 1A major fault alarm. Upon arrival found the UV system running normally but there was an unhealthy lamp status on the lead UV bank 1A. Acknowledged and cleared the alarms on the UV screen. Cleared all alarms on SCADA. | Mount Albert Water Resource Recovery Facility | 2026-03-18
WW-CEAST | March | Weather today Clear and -3 Celsius. -On site to complete work order W11682416, W11684111, W11682556, W11685349, W11753100. -Completed station check and lab analysis. -Entered station readings and lab analysis into SharePoint. -Completed Sludge Processing. - H&S Vehicle Inspection, Vehicle 2057. - Pick-up Fall Arrest Equipment. -Added two bags of soda ash to each aeration tank. | Mount Albert Water Resource Recovery Facility | 2026-03-24
WW-CEAST | March | Installed clarifier drive motor and gearbox Electricians wired up on site after installation of new terminal block in motor. Advised operator to put a blue lock on the local shut off and test operation to verify correct rotation once clarifier is finished being cleaned. | Mount Albert Water Resource Recovery Facility | 2026-03-26
WW-CEAST | March | Responded to UV fail alarm found UV bank A and bank B were full of water. There was water infiltration in the UV control panel as well. Cleaned and dried out. All panels was able to get enough components between UVA and UVB to get UVB working. New parts are on order exhaust fan 206 has failed as well. Reported to the team lead to have a work order created. Device locked out. | Mount Albert Water Resource Recovery Facility | 2026-03-18
WW-CEAST | March | Weather today Partly cloudy and -3 Celsius. -On site to complete work order W11682416, W11690597, W11690200, W11689416. -Completed station check and lab analysis. -Entered station readings and lab analysis into SharePoint. -Completed Sludge Processing. - Sewage Sampling. -Added two bags of soda ash to each aeration tank. | Mount Albert Water Resource Recovery Facility | 2026-03-25
WW-CEAST | March | #NAME? | Mount Albert Pumping Station | 2026-03-31
WW-CEAST | February | Took station readings and entered into Sharepoint,, reviewed trends - all good. Station running under normal ops - no issues were found. | Mount Albert Pumping Station | 2026-02-27
WW-CEAST | March | On site for Station Check (See details on SharePoint). Both pumps available in all-stop auto duty rotation. Standby power generator available in auto. Checked dry well, ok. Station operations normal. | Mount Albert Pumping Station | 2026-03-13
WW-CEAST | March | Weather today Overcast and 2 Celsius -On site to complete work order W11656931. -Collected monthly and weekly sewage samples and then, delivered to 145 HWP. -Rinsed samples container. -Reset composite sampler for next week sewage samples collection. | Mount Albert Pumping Station | 2026-03-11
WW-CEAST | March | On site completed work orders. Station Check (See details on SharePoint). Both pumps available in all-stop auto duty rotation. Standby power generator available in auto. Checked dry well, ok. JHSC Health and Safety Inspection Hazardous Waste Collection and Removal | Mount Albert Pumping Station | 2026-03-02
WW-CEAST | March | -On site for semi annual diesel generator maintenance, including monthly test run. -Total Power on site for semi annual maintenance. -0859 - Transferred station to generator power. -1005 - Transferred station back to utility power. -Generator Start hours: 619.5, Stop hours: 620.7, run time: 1.2hrs. -Generator test run completed, readings entered into SharePoint. | Mount Albert Pumping Station | 2026-03-05
WW-CEAST | March | On site completed Station Check (See details on SharePoint) Both pumps available in all-stop auto duty rotation. Standby power generator available in auto. Checked dry well, ok. Station operations normal. | Mount Albert Pumping Station | 2026-03-20
WW-CEAST | March | On site completed work orders. Upon arrival found SCADA with generator not in auto alarm happened last Friday, March 13th, 2026, at 11:33am. Cleared/reset said alarm and check generator, ok. Station Check (See details on SharePoint) Both pumps available in all-stop auto duty rotation. Standby power generator available in auto. Checked dry well, ok. Station operations normal. Overflow Kit Inspection | Mount Albert Pumping Station | 2026-03-16
WW-CEAST | March | Weather today Partly cloudy and 11 Celsius. -On site to complete work order W11648657, W11648577, W11707125, W11648041, W11648341, W11648328, W11714174. -Completed Lab Analysis and Sludge Processing. -Entered lab analysis readings into SharePoint. -Bar Screen Bin, Removal and Replacement. -Post Aeration Alum mixing chamber and RAS/WAS inlet channel inspection/cleanout. -Wasted 25m3 from clarifier #1. -Alum Delivery/Receiving stated at 0.89m and filled to 3.52m. | Mount Albert Water Resource Recovery Facility | 2026-03-10
WW-CEAST | March | -On site to complete work orders. -GFL/Accuworx on site for Clarifier 1 cleaning. -Two bags of soda ash added to each aeration tank. -Cleaned out RAS inlet chamber and post aeration alum mixing chamber. -Mechanics and electricians have completed repair work on Clarifier 1. Clarifier 1 locked out at local disconnect with station lock until clarifier cleaning is completed. -Worked on UV room cleaning. Removed old/broken items. Cleaned floors. -UV Bank 1A OOS, Clarifier 1 OOS, RAS Pump 3 OOS, WAS Pump 2 OOS, OCU OOS. | Mount Albert Water Resource Recovery Facility | 2026-03-26
WW-CEAST | March | On site to complete work orders. STT decanted and sludge dumped into the SHT afterwards. As per notification of work order completion received today, effluent pipe leak has been fixed by CMS. Effluent pumps put back in auto and back in service. Lab Analysis (See results on SharePoint) and Sludge Processing. At around 9:45am, turned off both UV banks and flows diverted to the lagoon due to damaged wirings on the UV banks systems and the Trojan panel. Electricians on site troubleshooting it. Station Check (See details on SharePoint). Added two bags of Soda Ash into each Aeration Tanks. Removed rags from the inlet/outlet sluice gates of Aeration Tanks. Checked DO Probes, ok. Checked Alum dosing injection points at prefilter and post aeration. Also, collected weekly sewage samples under YD# W11672811. Terry R. delivered to 145 HWP. At around 11:26am, Post Aeration Alum dosage increased from 195 mg/L to 200 mg/L. Prefilter remains the same at 15 mg/L. At around 12:15pm, UV Bank 1B has been fixed by electricians and put back in service. Cleared/reset alarms. At 13:00pm, flows diverted back to the plant. Approximate volume of flows diverted is 220 m3. | Mount Albert Water Resource Recovery Facility | 2026-03-18
WW-CEAST | March | Weather today a few clouds and -8 Celsius. -On site to complete work order W11682416, W11696996, W11696424, W11697180. -Completed station check and lab analysis. -Entered station readings and lab analysis into SharePoint. -Completed Sludge Processing. -Weekly Alarm Management. -Added two bags of soda ash to each aeration tank. -Clarifier 1 and UV bank 1A are still OOS. | Mount Albert Water Resource Recovery Facility | 2026-03-27
WW-CEAST | March | Weather today is Partly Cloudy and 10 Celsius -On site to complete work order W11698440. -Completed station check. -Entered station readings into SharePoint. -Both pumps are available in all-stop auto duty rotation. -Standby power generator available in auto. -Checked dry well. -Station operations normal. | Mount Albert Pumping Station | 2026-03-30
WW-CEAST | March | -On site to respond to communications failure alarm reported by ROC. PCS on-call has also been notified and is on route to site. -0405 - Upon arrival to site, swipe card reader not working, local SCADA OIT panel is blank and not working, Pumps both displaying No Communication faults on panels. Wet well level is at 4.08m. Tried resetting pump faults on local panel, but pumps will not run in remote or local. Wet well backup mode is in Auto, but pumps not running. -Called on-call electrician, tried cycling power to pumps, but still not working. Tried disconnecting power for 5-10min, but pumps still not working when turned back on. On-call electrician on route to site. -0431 - Contacted ROC to initiate emergency vac truck procedure and have trucks dispatched to site. -Tried transferring site to generator power, suspecting possible phase loss on site. Unable to get generator to turn on, e-key not working on any locks on site. -Briefly left site to bump e-key at MTA WRRF. When back on site, e-key still not working. Cut lock to generator building. Generator screen is blank and unresponsive. Generator will not run in remote or manual. -0512 - Wessuc confirmed they have vac truck and tanker on route to site. -Electricians and PCS arrived at site and found multiple damaged pieces of equipment due to a suspected lightning strike on the building. They immediately began work to restore functionality of damaged equipment. -0631 - Wessuc informed of delays and that they were still approximately 1.5hrs away. -0645 - Informed SAC of ongoing spill. Spoke with environmental officer Edhilvia Campos and was assigned event# 1QG1QRG. -0655 - Informed York Region local health unit of ongoing spill. Spoke with health officer David Huang. -0700 - Notified LSCRA of ongoing spill. -0815 - Wessuc arrived on site and began setting up hoses to pump down wet well. Began pumping down wet well at approximately 0830. -0830 - Collected spill samples with Chris Rodie, CoC# W11769441. -0925 - Electricians able to get one pump running on site and began pumping down wet well to forcemain along with Wessuc pumping wet well to vac truck. -0957 - Wet well at 3.99m, below the overflow level. Spill has ended. -Kevin Shaji arrived at site to complete weekly sample collection. -When Wessuc had completed their emergency wet well pumping activities, accompanied vac truck to site of spill, which was a local East Gwillimbury manhole between the southeast corner of the Foodland parking lot and the railroad tracks. Wessuc cleaned solids and liquid from surrounding area, as well as removed excess solids from local sewer. While on site, visited by local Public Heath Inspector Darja Montsenko, who also observed spill location during cleanup and afterwards. -Instrumentation team on site to replace damaged flowmeter and level sensor. -Electricians and PCS team able to get both station pumps repaired and operational in auto. -Temporary generator set up on site and tested in manual and in auto, with a full station transfer test. -Composite sampler reset for 0700 April 7, 2026. Sample jug cleaned. -Security system and swipe card reader on site not working. Informed supervisor of issue and work request created. -Station is back running normally. Temporary generator set up on site. Both pumps available and in local. | Mount Albert Pumping Station | 2026-03-31
WW-CEAST | March | Attending site to replace wetwell level transmitter and flowmeter (W11769917). Devices were damaged due to electrical storm. Replaced, configured and tested wetwell level transmitter with Art. Parth and Rick replaced and configured discharge flowmeter. | Mount Albert Pumping Station | 2026-03-31
WW-CEAST | March | On site collected monthly and weekly sewage samples and then, delivered to 145 HWP. Rinsed samples container. Reset composite sampler for next week sewage samples collection. | Mount Albert Pumping Station | 2026-03-04
WW-CEAST | March | On site completed work orders. Station Check (See details on SharePoint). Both pumps available in auto. Standby power generator available in auto. Checked dry well, ok. Also, at around 11:00am, 4Refuel delivered diesel fuel, 400.2L. Previous level 12.2cm/914L Current level 17.6cm/1319L. Bypass sampling kit inspection Eye wash cleaning and solution inspection. Consolidated Dry Well and Hoist System Inspection Auto Dialer Alarm Test - alarm received and confirmed by ROC. Dry Well Flood Alarm Test - alarm received and confirmed by ROC. Sump Pit Inspection Hoist System Inspection No High/Low Temp Alarm Test in this facility. RS Pump Grease/Inspection Check Valve Inspection RS Pump Motor/Inspection Pump 1 - @ 50% speed, 43L: @ 100% speed, 63L Pump 2 - @ 50% speed, 37L: @ 100% speed, 58L | Mount Albert Pumping Station | 2026-03-09
WW-CEAST | March | Took station readings and entered into Sharepoint - reviewed trends - all looks good. Station running under normal ops - no issues were found. | Mount Albert Pumping Station | 2026-03-06
WW-CEAST | March | Weather today is Partly Cloudy and -9 Celsius -On site to complete work order W11696163. -Completed station check. -Entered station readings into SharePoint. -Raw Sewage sampler check. -Both pumps are available in all-stop auto duty rotation. -Standby power generator available in auto. -Checked dry well, ok. -Station operations normal. | Mount Albert Pumping Station | 2026-03-27
WW-CEAST | March | Weather today Overcast and 0 Celsius -On site to complete work order W11668817, W11680778. -Completed station check. -Entered station readings into SharePoint. -Raw Sewage sampler check. -Both pumps are available in all-stop auto duty rotation. -Standby power generator available in auto. -Checked dry well, ok. -Station operations normal. | Mount Albert Pumping Station | 2026-03-23
WW-CEAST | March | Weather today a few clouds and 2 degrees Celsius -On site to complete work order W11690200. -Collected monthly and weekly sewage samples and then, delivered to 145 HWP. -Rinsed samples container. -Reset composite sampler for next week?s sewage samples collection. | Mount Albert Pumping Station | 2026-03-26
WW-CEAST | March | -Remotely throttling flows going to Aurora SPS in response to NMMC Manhole 2 Level HiHi Alarms. -Ran two to three pumps together at reduced speeds. -Partially diverting flows to EQ tanks while keeping Screen Upstream levels below HiHi levels. | Newmarket Sewage Pumping Station & Equalization Tank | 2026-03-31
WW-CEAST | March | On site to monitor station in response to high flow. Max 2 pumps running onsite with flow output of approx 880 l/s, maintaining ww level around 5m. Changed both barscreen run/rest setpoint from 6m/2m to 8m/1m to manage screen 2 upstream level | Newmarket Sewage Pumping Station & Equalization Tank | 2026-03-11
WW-CEAST | March | On site to fix broken water line in screen room beside bay door. Also notice barscreen number 1 loud growl from top sprocket bearing. Investigated greased and ran quiet and smooth. | Newmarket Sewage Pumping Station & Equalization Tank | 2026-03-03
WW-CEAST | March | Station Check completed (See details on SharePoint). Standby power generator available in auto. Checked dry well, ok. checked screen room. Changed screen bins and flushed the drain screen and drain hose. Placed the bar screen bin outside for removal. Bar Screen 1 making a growling noise. Greased Bar screen 1 bearings and now the noise is gone. Air compressors inspection and cleaning completed. In response to high flow, Max 2 pumps running onsite with flow output of approx 680 l/s, overflowing into the EQ tanks at 3.15pm. At around 3:30pm, on site monitored SCADA for the whole Central-East WW due to the weather. Too much incoming flows. Monitored SCADA for flows due to weather till 7.20pm. | Newmarket Sewage Pumping Station & Equalization Tank | 2026-03-11
WW-CEAST | March | Station check complete and the readings have been entered into the sharepoint. Pushed empty bin back into the screen room. | Newmarket Sewage Pumping Station & Equalization Tank | 2026-03-06
WW-CEAST | March | Station Check completed (See details on SharePoint). All pumps available in auto duty rotation. Standby power generator available in auto. Checked dry well, ok. checked screen room. Raked rag bins. | Newmarket Sewage Pumping Station & Equalization Tank | 2026-03-02
WW-CEAST | March | On site to complete consolidated monthly dry well pump floor inspection. Auto Dialer Alarm Test - alarm received and confirmed by ROC. Dry Well Flood Alarm Test - received and confirmed by ROC. Sump Pit Inspection Air Compressor Inspection Check Valve Inspection RS Pump and Motor Inspection Pump 1 - @ 0% speed 234 L/s, 129 kPa, 136 A, 617 V, 39 Hz; @ 25% speed 303 L/s, 170 kPa, 170 A, 617 V, 44 Hz; @ 35% speed 376 L/s, 162 kPa, 191 A, 617 V, 46 Hz Pump 2 - @ 0% speed 217 L/s, 132 kPa, 123 A, 384 V, 797 RPM, 40 Hz; @ 25% speed 308 L/s, 135 kPa, 152 A, 431 V, 896 RPM, 45 Hz; @ 100% speed 540 L/s, 172 kPa, 246 A, 574 V, 1193 RPM, 60 Hz Pump 3 - @ 0% speed 226 L/s, 132 kPa, 134 A, 372 V, 769 RPM, 39 Hz; @ 25% speed 294 L/s, 160 kPa, 173 A, 425 V, 878 RPM, 44 Hz; @ 35% speed 335 L/s, 158 kPa, 194 A, 446 V, 921 RPM, 46 Hz. Pump 4 - @ 0% speed 128 L/s, 142 kPa, 109 A, 615 V, 39 Hz; @ 25% speed 178 L/s, 163 kPa, 143 A, 618 V, 44 Hz; @ 35% speed 223 L/s, 149 kPa, 159 A, 616 V, 46 Hz. | Newmarket Sewage Pumping Station & Equalization Tank | 2026-03-05
WW-CEAST | March | On site with Total Lift for inspections | Newmarket Sewage Pumping Station & Equalization Tank | 2026-03-18
WW-CEAST | March | Station Check completed (See details on SharePoint). All pumps available in auto duty rotation. Standby power generator available in auto. Checked dry well, ok. checked screen room. Flushed the drain screen and drain hose. Tipping bucket operational check completed. | Newmarket Sewage Pumping Station & Equalization Tank | 2026-03-27
WW-CEAST | March | On site completed consolidated Wet Well Inspection: Wet Well High Level Alarm Test - received and confirmed by ROC. Sluice Gate Valve/Actuator Exercise Wet Well Valve Exercise Wet Well Inspection and Cleaning Bar Screen Cleaning/Lubrication Screw Conveyor Cleaning/Lubrication Consolidated monthly Surge Tank Inspection Surge Tank and System Inspection Surge Tank Drain Valve Inspection Transmission Lines Flushing Surge Tank Valve and Actuator Exercise and Inspection | Newmarket Sewage Pumping Station & Equalization Tank | 2026-03-26
WW-CEAST | March | Station Check completed (See details on SharePoint). All pumps available in auto duty rotation. Standby power generator available in auto. Checked dry well, ok. checked screen room. flushed the drain screen and drain hose. Overflow kit inspection. | Newmarket Sewage Pumping Station & Equalization Tank | 2026-03-16
WW-CEAST | March | On site to perform pm on air compressors. Changed oil and checked air filters. Inspected bar screens found barscreen #2 out of alignment when travelling over top sprockets. Found top drive sprocket key and key way worn. Removed and ordered parts. Waiting for parts to install. | Newmarket Sewage Pumping Station & Equalization Tank | 2026-03-19
WW-CEAST | March | Station Check completed (See details on SharePoint). All pumps available in auto duty rotation. Standby power generator available in auto. Checked dry well, ok. checked screen room. Flushed the drain screen and drain hose. | Newmarket Sewage Pumping Station & Equalization Tank | 2026-03-20
WW-CEAST | March | Station Check completed (See details on SharePoint). All pumps available in auto duty rotation. Standby power generator available in auto. Checked dry well, ok. Changed screen bins and flushed the drain screen and drain hose. Placed the bar screen bin outside for removal. Air compressors inspection and cleaning completed. | Newmarket Sewage Pumping Station & Equalization Tank | 2026-03-25
WW-CEAST | March | Station Check completed (See details on SharePoint). All pumps available in auto duty rotation. Standby power generator available in auto. Checked dry well, ok. checked screen room. Changed screen bins and flushed the drain screen and drain hose. Placed the bar screen bin outside for removal. Air compressors inspection and cleaning completed. | Newmarket Sewage Pumping Station & Equalization Tank | 2026-03-18
WW-CEAST | March | Station Check completed (See details on SharePoint). All pumps available in auto duty rotation. Standby power generator available in auto. Checked dry well, ok. checked screen room. flushed the drain screen and drain hose. | Newmarket Sewage Pumping Station & Equalization Tank | 2026-03-23
WW-CEAST | March | @8:30am - Made some changes in response to high flow event. put pump 2 in duty 3 and increased duty 1 vfd min speed from 15% to 50% to minimize duty 2 start cleared ultrasonic interlock on pump 3 pump 1 vfd fault outstanding from last night, will be investigated on upcoming station checks. @12:32 - Put duty 1 vfd min speed back to 15%. | Newmarket Bogart Creek Sewage Pumping Station | 2026-03-31
WW-CEAST | March | -station check of site -reviewed SCADA -inspected site -entered data into SharePoint -station okay | Newmarket Bogart Creek Sewage Pumping Station | 2026-03-30
WW-CEAST | March | -Remotely made changes to respond to alarms coming in during period of high flows. -Placed pump 2 in duty 3. Pump 4 in duty 1, Pump 3 in duty 2. -Changed controlling LIT from LIT1 to LIT4. -Lowered duty 1 start set point from 2.25m to 2.20m -Increased duty 1 minimum speed set point from 15% to 25% to help avoid multiple duty 2 starts. | Newmarket Bogart Creek Sewage Pumping Station | 2026-03-31
WW-CEAST | March | Station readings taken. Data entered on sharepoint. Reviewed SCADA, trends. Station running normal. Consolidated Dry Well & Hoist System Inspection. Hoist System Inspection. Check valve inspection. Dry well flood alarm test. received and confirmed by ROC. Sump pit inspection. Air relief valve inspection. High low temp alarm test. received and confirmed by ROC. Autodialer test. alarm received and confirmed by ROC. RS pump motor / inspection. Pumps 1-4 RS pump motor / inspection. Pump 1 -16% - 82.9 L/s Pump 2 constant speed ? 193.9 L/s Pump 3 - 16% - 76.9 L/s Pump 4 - 16% - 82.7 L/s | Newmarket Bogart Creek Sewage Pumping Station | 2026-03-13
WW-CEAST | March | Station readings taken. Data entered on sharepoint. Reviewed SCADA, trends. Checked basement. ok Station running normal. JHSC Health and Safety Inspection completed. Hazardous Waste Collection and Removal Odour control system, inspection and cleaning. Standby Power Generator Test Run - pre-test checked, ok. Generator started and stopped running without problem. Gen Start time: 273.22, Stop time: 274.37, Run time: 1:15hrs. Cleared/reset all alarms. Generator back in auto and available. | Newmarket Bogart Creek Sewage Pumping Station | 2026-03-02
WW-CEAST | March | Station readings taken. Data entered on sharepoint. Reviewed SCADA, trends. Checked basement. ok Station running normal | Newmarket Bogart Creek Sewage Pumping Station | 2026-03-09
WW-CEAST | March | On site to complete work orders. Manual valve exercise completed. RS pump discharge valve and Actuator, inspection and exercise. comprehensive housekeeping completed | Newmarket Bogart Creek Sewage Pumping Station | 2026-03-12
WW-CEAST | March | On site to grease pump motors and drive shafts | Newmarket Bogart Creek Sewage Pumping Station | 2026-03-10
WW-CEAST | March | Station readings taken. Data entered on sharepoint. Reviewed SCADA, trends. Checked basement. ok Station running normal Seal water system maintenance completed. Overflow kit, inspection completed. | Newmarket Bogart Creek Sewage Pumping Station | 2026-03-16
WW-CEAST | March | Station readings taken. Data entered on sharepoint. Reviewed SCADA, trends. Checked basement. ok Station running normal. | Newmarket Bogart Creek Sewage Pumping Station | 2026-03-27
WW-CEAST | March | On site for vibration readings. All pumps left in auto | Newmarket Bogart Creek Sewage Pumping Station | 2026-03-25
WW-CEAST | March | -station check of site -reviewed SCADA -inspected site -entered data into SharePoint -OCU exhaust piping for wet well has blown apart, created a WO for CMS and notified CEWW Team - W117533481 -station okay | Newmarket Bogart Creek Sewage Pumping Station | 2026-03-23
WW-CEAST | March | On site to complete work orders. Station Check (See details on SharePoint) Peristaltic Pump Inspection | SEC Boxgove Corrosion Control Facility | 2026-03-30
WW-CEAST | March | -station check of site -reviewed SCADA -entered data into sharepoint -inspected site -cleaned screen room, rotated bin in screen room as necessary -station okay | Newmarket Sewage Pumping Station & Equalization Tank | 2026-03-30
WW-CEAST | March | @8:25 - Placed pumps 1 and 3 OOS in manual off to leave 2 other pumps running in auto and in manual speed of 30% to slow down flow to Aurora SPS. | Newmarket Sewage Pumping Station & Equalization Tank | 2026-03-31
WW-CEAST | March | Station Check completed (See details on SharePoint). All pumps available in auto duty rotation. Standby power generator available in auto. Checked dry well, ok. checked screen room. flushed the drain screen and drain hose. | Newmarket Sewage Pumping Station & Equalization Tank | 2026-03-13
WW-CEAST | March | Station Check completed (See details on SharePoint). All pumps available in auto duty rotation. Standby power generator available in auto. Checked dry well, ok. Changed screen bins and flushed the drain screen and drain hose. Placed the bar screen bin outside for removal. Monthly diesel generator test run completed, readings entered into SharePoint. 9.50am - Transferred site to generator power. 10.55am - Transferred site back to utility power. Generator Start time: 288.7, Stop time: 290.0, Run time: 1:3hrs. JHSC Health and Safety Inspection completed. Hazardous Waste Collection and Removal Air compressors inspection and cleaning completed. Completed station housekeeping. | Newmarket Sewage Pumping Station & Equalization Tank | 2026-03-04
WW-CEAST | March | Station Check completed (See details on SharePoint). All pumps available in auto duty rotation. Standby power generator available in auto. Checked dry well, ok. Unclogged RS Pump #4 with Chris R. | Newmarket Sewage Pumping Station & Equalization Tank | 2026-03-09
WW-CEAST | March | -on site to complete work orders -Tank 1 has water in it, tank 2 has 0.5 meters of 50% H2O2 -using Tank 1 to keep chemical pumps running for warranty period -topping up Tank 1 with water -Chemical Tank Maintenance -Sump Pump Test -Ventilation System Inspection -Housekeeping -station okay | SEC Boxgove Corrosion Control Facility | 2026-03-31
WW-CEAST | March | Took station readings and entered into Sharepoint ,, completed H & S inspection as well. Checked paristaltic pumps,, 1 of the pumps is down but 2 are working fine. Station running under normal ops - dosing water. | SEC Boxgove Corrosion Control Facility | 2026-03-02
WW-CEAST | March | On site to meet with SPD for back pressure/pressure relief adjustment for chemical pumps. Back pressure has been changed from 40 psi to 10 psi. Pressure relief have been changed from 60 psi to 30 psi | SEC Boxgove Corrosion Control Facility | 2026-03-05
WW-CEAST | March | Took station readings and entered into Sharepoint,, went through the station - no leaks in tanks, all looks good. Checked sump pits - OK. Station running under normal ops - no issues were found. | SEC Boxgove Corrosion Control Facility | 2026-03-09
WW-CEAST | March | Station check complete and the readings have been entered into the sharepoint. Revised 2026 sharepoint page via POA as it did not reflect recent chemical feed system upgrade. | SEC Boxgove Corrosion Control Facility | 2026-03-16
WW-CEAST | March | Took station readings and entered into Sharepoint - added water to tank 1 and went through the shelved alarms and nothing has changed. Cleaned the washroom and also swept out the HVAC room. Station running under normal ops - no new issues were found. | SEC Boxgove Corrosion Control Facility | 2026-03-27
WW-CEAST | March | Took station readings and entered into Sharepoint ,, greased the fan bearings and topped up the nutrient tanks. Tested the 3 actuators for the water supply in local - all good and they are back in remote, activated the sump pump and also tested the alarm - both work fine and sump pit is clear of debris. The HVAC is currently off - I believe due to winter temps. Could not check media spray as it takes two people to complete the task. Checked the Y strainers while topping up nutrient tanks - they all look good only the 2nd bio scrubber has a recirc pump running. Fan 3 is OOS but the rest of the staztion is running fine. Cleared all the alarms that I could. | SEC Markham Odour Control Facility | 2026-03-09
WW-CEAST | March | On site completed work orders. Station Check (See details on SharePoint) Currently, fan 1 and fan 2 running in auto as duty 1 and 2, respectively. Standby power generator available in auto. Water supply pumps are full of oil. Put fan 3 in e-stop/local out of service, CMS currently on-site checking knife gate that has faulted. Nutrient Tank Batch Mixing Nutrient tanks are full of water. Odour Control Fans Impeller Bearing Lubrication | SEC Markham Odour Control Facility | 2026-03-30
WW-CEAST | March | Here to meet up with contractor ( got a phone call) and we are going to run the Diesel and do the maintainance check. Checked the fluids out on the Diesel - all good, Batteries need to be replaced as well as the Fan belts ( Company will submit a evaluation ) Shut the Fans down and transferred power over to Diesel - no issues. While Diesel was running completed H & S inspection - no issues were found. Took Diesel readings and entered into Sharepoint - Company found that the Diesel was operating fine. Shut the fans back down and switched back to main power - no issues during transfer ,, cleared the alarms and informed ROC I was all finished here. Fan 3 is still OOS but 1 & 2 are fine. | SEC Markham Odour Control Facility | 2026-03-03
WW-CEAST | March | Took station readings and entered into Sharepoint,, checked all 3 nutrient tanks as well as the oil level on the water pumps - all good. Greased the bearings on Fans 1 & 2 - 3 is OOS and also cleaned up the washroom/ office area and swept out the MCC room. Station running under normal ops - Fan 3 is OOS. Also went through the shelved alarms and nothing has changed. | SEC Markham Odour Control Facility | 2026-03-27
WW-CEAST | March | Station check complete and the readings have been entered into the sharepoint. Created CMU3 for INST to repair O2 sensors @ shaft 9/ocf damper station/fan room Cleared fan room O2 alarm and turned off high ventilation. Heaters in the fan/mech room still not working as intended and producing room temp air, notified SUP to follow up with PS Fan 3 OOS due to the suction knife gate fault, CMU has been previously submitted to CMS | SEC Markham Odour Control Facility | 2026-03-16
WW-CEAST | March | -On site for immersion heater inspections. -Inspected immersion heaters, pumped down humid chambers to test low level alarms and ensure heaters turned off with low levels. -Equipment Room 3 immersion heater has been locked out by the electrical team and is OOS. | SEC Markham Odour Control Facility | 2026-03-24
WW-CEAST | March | Onsite to troubleshoot carbon unit O2 sensor and fan room outlet O2 sensor Informed ROC Replaced sensor and calibrated Cleared associated alarms ODOR _GO25 is still in alarm on local gas panel. Cannot locate this device on scada or at facility Informed ROC and left site | SEC Markham Odour Control Facility | 2026-03-24
WW-CEAST | March | Went through alarm management for the SEOC and YDOC - all alarms shelved are still OOS. | SEC Markham Odour Control Facility | 2026-03-23
WW-CEAST | March | Took station readings and entered into Sharepoint,, reviewed trends - all good. Completed H & S inspection as well as Diesel Test run and entered readings into Sharepoint. Verified Heat trace is on and operational. Exercised all the actuators with the Fans as well as a partial exercise of the knife gate valves. All alarms cleared except O2 sensor(WO has been created) and station is running under normal ops. | SEC Fairport Air Handling Facility (Shaft 4) | 2026-03-11
WW-CEAST | March | Here to clean the mist eliminators , opened the panel door and hosed down the mist eliminators - a bit messy. cleaned up the floor and washed everything down the drain. Station running under normal ops - Fan 3 is OOS. | SEC Markham Odour Control Facility | 2026-03-05
WW-CEAST | March | Entered station readings into Sharepoint ,, greased blowers 1 & 2 - blower 3 is OOS,, topped up nutrient tanks and also checked the oil level on the water pumps. Walked through the station and everything looks good also went into the Diesel room - no leaks around the Diesel and everything is in auto. Also checked the blower Fans 1 & 2 - belts look fine and are running straight. Station is running under normal ops - blower 3 is OOS. | SEC Markham Odour Control Facility | 2026-03-02
WW-CEAST | March | Took station readings and entered into Sharepoint,, reviewed trends - all good. Cleared alarms from last night and station is running under normal ops - no issues were found. ( gas monitor sensor is out but WO has been created) | SEC Fairport Air Handling Facility (Shaft 4) | 2026-03-04
WW-CEAST | March | Took station readings and entered into Sharepoint, reviewed trends - all good. Swept out main office and cleaned up washroom. Station running under normal ops - no issues found. | SEC Fairport Air Handling Facility (Shaft 4) | 2026-03-18
WW-CEAST | March | Onsite to troubleshoot fan room O2 sensor. Informed ROC Found O2 gas detector reading 10% Replaced sensor and calibrated Cleared associated alarms Informed ROC, armed building and left site | SEC Fairport Air Handling Facility (Shaft 4) | 2026-03-24
WW-CEAST | March | Took station readings and entered into Sharepoint,, reviewed trends and checked the Diesel room - all good. Station running under normal ops - no issues were found. | SEC Fairport Air Handling Facility (Shaft 4) | 2026-03-25
WW-CEAST | March | On site for vibration readings. Had the ROC rotate duty?s | SEC Fairport Air Handling Facility (Shaft 4) | 2026-03-25
WW-CEAST | March | Took station readings and entered into Sharepoint and reviewed trends - all good. Checked Heat Trace system - all working fine. Station running under normal ops - no issues were found. | SEC Altona Air Handling Facility (Shaft 6/7) | 2026-03-11
WW-CEAST | March | Checked fluids on Diesel and then transferred power over for the Diesel test run,, entered station readings into Sharepoint and reviewed trends - all looks good. Exercised actuators by switching fan Duty once power was transferred (shut fans down before transferring power). Partially exercised knife gates before and after switching fan Duty. Completed H & S check - all good. | SEC Altona Air Handling Facility (Shaft 6/7) | 2026-03-04
WW-CEAST | March | Met up with the water delivery and we could not fill the tank as there was a valve closed but the E-Key does not work on that door so water delivery will have to be re-scheduled. Took station readings and entered into Sharepoint, reviewed trends - all good. Also swept out the main room, MCC room. Station running under normal ops - no issues were found. | SEC Altona Air Handling Facility (Shaft 6/7) | 2026-03-25
WW-CEAST | March | Station check complete. confirmed condensation draining as intended. No unusual odor detected onsite during visit Heater element - 71.8 Hydro - 288964 kwh VFD Chiller - no display on-site | Bayview & Steeles Air Management Facility | 2026-03-30
WW-CEAST | March | Took station readings and entered into Sharepoint - reviewed trends, all good. Verified hoist operation and also checked the filters on the HVAC but its off due to winter temps. Station running under normal ops - no issues were found. | SEC Altona Air Handling Facility (Shaft 6/7) | 2026-03-18
WW-CEAST | March | -On site to complete work orders. -Station check completed. -Heater element: 95.4F. -Hydro meter: 283523kWh. -Fan is running, no odours detected while on site. -Monthly JHSC H&S inspection completed. -Odour control scrubber inspection completed. | Bayview & Steeles Air Management Facility | 2026-03-02
WW-CEAST | March | -On site to complete work orders. -Station check completed, readings entered into SharePoint. -Heater element: 82.2F. -Hydro meter: 284777kWh. -Mist eliminator filters, clean and replace completed. All mist eliminator filters changed out with clean spares. -0937 - Turned off fan for mist eliminator maintenance. -0953 - Fan turned back on after changing out mist eliminator filters. -Inspected fan belts and greased fan shaft while on site. | Bayview & Steeles Air Management Facility | 2026-03-09
WW-CEAST | March | On site for station check. Heater Element - 89.1 F Hydro Meter Reading - 287516 Kwh VFD Chiller - No temp reading. Fan and motor running. No bad odour at time of visit. Station operation normal. | Bayview & Steeles Air Management Facility | 2026-03-23
WW-CEAST | March | -On site to perform a station check. -Heater element: 86.0F. -Hydro meter: 286147kWh. -Fan running, no odours detected on site. | Bayview & Steeles Air Management Facility | 2026-03-16
WW-CEAST | March | On site for electric meter replacement to be done by Toronto Hydro. Address on their work order is 8A Pickering Townline, which is YDOC 2001 Scarborough Pickering Townline. They arrived on site at around 8:00am, however, I'm not yet on site so they went to another appointment. When I called them, they said they will be back around 12:00pm. At 12:00 Noon, Toronto Hydro arrived on site. They replaced the electric meter of the Boundary Meter Facility, not YDOC. | SEC Pickering Odour Control Facility (York/Durham) | 2026-03-30
WW-CEAST | March | Took station readings and entered into Sharepoint ,, reviewed trends and went through the station. Nutrient tanks are good. Fan 1 is still OOS but rest of the station is running under normal ops. | SEC Pickering Odour Control Facility (York/Durham) | 2026-03-04
WW-CEAST | March | Here to clean the mist eliminators,, Fan 2 is the only one running so I left that one but I took 1 out - no to bad, hosed it down as best I could and replaced it. Station running under normal ops - fan 1 is OOS but the rest is running fine. | SEC Pickering Odour Control Facility (York/Durham) | 2026-03-05
WW-CEAST | March | Here to complete WO's,, checked fluid levels on the Diesel, green light on the batteries and started my Diesel test run. while Diesel was running I completed the H & S check - no issues were found. Entered readings from the Diesel run into Sharepoint. Had to bring the contractor back after SEOC - I had no idea this was going on today, He took down the readings from the Diesel run and also checked out the Diesel. Station back to normal ops - Fan 1 is still OOS. | SEC Pickering Odour Control Facility (York/Durham) | 2026-03-03
WW-CEAST | March | Took station readings and entered into Sharepoint,, reviewed trends and Fan 1 is OOS. Checked nutrient tanks - all good. Station running with 1 fan(2) . | SEC Pickering Odour Control Facility (York/Durham) | 2026-03-11
WW-CEAST | March | Took station readings and entered into Sharepoint,, reviewed trends - all good. Fan 1 is OOS and nutrient tanks have been topped up. cleared all alarms (new). Station running with Fan 2 only. | SEC Pickering Odour Control Facility (York/Durham) | 2026-03-18
WW-CEAST | March | Took station readings and entered into Sharepoint,, reviewed trends and also checked the nutrient tanks. Checked the strainers on the recirc pumps and cleaned them both out. Did a blower inspection on Fan 2 and greased it, Fan 1 is OOS, walked around the cat walk and checked media sprayers on line 2 - there are a few not working. Also swept up the main floor and around the Generator. Fan 1 is OOS but Fan 2 is working fine. | SEC Pickering Odour Control Facility (York/Durham) | 2026-03-25
WW-CEAST | March | Check battery type 4D Belt is due for replacement. | SEC Pickering Odour Control Facility (York/Durham) | 2026-03-26
WW-CEAST | March | On site for vibration readings | SEC Pickering Odour Control Facility (York/Durham) | 2026-03-25
WW-CEAST | March | -Passive scrubber inspections/maintenance completed for the following locations: -Major Mackenzie and Leslie -Warden and Enterprise -Milne Park -Tuclor Lane -Woodbine and 16th | Central-East Wastewater Linear System | 2026-03-11
WW-CEAST | March | -On site to perform Aurora East Forcemain Chamber inspections. -Completed inspections, multiple chambers full of water, will have to revisit chambers at a later date to pump out groundwater. | Central-East Wastewater Linear System | 2026-03-12
WW-CEAST | March | -inspected Jefferson Forest and Yonge passive scrubber -media was replaced, site okay | Central-East Wastewater Linear System | 2026-03-25
WW-CEAST | March | On site for Leslie PS forcemain inspection of the following chambers. 71-01 (chamber pumped out) LSMFT-01 (chamber pumped out) LSMFT-02 (Chamber full of water but cannot be pumped out due to no access for the truck/equipment) 71-03 71-04W 71-04E (chamber pumped out) 43-02 LSMFT-03 | Central-East Wastewater Linear System | 2026-03-25
WW-CEAST | March | On site to continue working on the Leslie PS chamber inspections. 71-02 (Chamber cannot find - near chamber no. LSFMT-02) 94-01 (Chamber cannot find) 43-01 (chamber pumped out) 43-03 (Chamber cannot find) LSFMT-04 (Chamber cannot find) 43-04 (Outfall - did not inspect) | Central-East Wastewater Linear System | 2026-03-26
WW-CEAST | March | On site for chamber inspection of Aurora West Forcemain and Henderson Twin Forcemains. 28-CH01 - Yonge/Henderson 28-CH02 - Yonge/Industrial Pkwy S 28-CH03 - Industrial Pkwy S/Yonge | Central-East Wastewater Linear System | 2026-03-19
WW-CEAST | March | -completed chamber checks for Aurora East FM inspections -pumped out half of the chambers which were flooded, still require a days work to pump out the rest | Central-East Wastewater Linear System | 2026-03-25
WW-WEST | March | onsite for station check - no new issues. reviewed trends and added data into sharepoint. pump run test: pump 1 - 553.1L/s at 300kPa pump 2 - 450.4L/s at 268lPa at 100% pump 3 - 133.0L/s at 214lPa at 100% pump 4 - 467.1L/s at 261kPa at 100% pump 5 - OOS (known issue) All pumps placed back into auto and back into duty rotation. pushed barscreen bin outside for pick up. completed comprehensive housekeeping - cleaned bathroom and entrance. | Vaughan Black Creek Pumping Station | 2026-03-31
WW-WEST | March | Onsite for station check - no new issues reviewed trends and added data to SharePoint. Oil dispenser for bar screen not pumping. Tried to fix with no success. Will need to order new one. | Vaughan Black Creek Pumping Station | 2026-03-10
WW-WEST | March | Onsite for PMs with Marcus. Completed dry well consolidated inspection. Wetwell and barscreen consolidated inspection and air relief valve flushing. Created work order for pump 4 check valve not closing. | Vaughan Black Creek Pumping Station | 2026-03-09
WW-WEST | March | Station checks, SharePoint readings and review of continuous monitoring data Level screen room bin and clean floor. Pump test runs on pump 1 & 4. - ok- Pump 3 running on entry and 2/5 OOS. | Vaughan Black Creek Pumping Station | 2026-03-13
WW-WEST | March | In to Complete Scheduled WOs. Notified ROC. Placed Pumps #1, 3 and 4 in Manual Off. Transferred Station to Generator Power with No Issues. Acknowledged and Cleared Associated Alarms. Returned Pumps #1, 3 and 4 to Auto. Duties #1 and 2 Activated Automatically. Completed Heat Exchanger Radiator Inspection. Visible Internal and External Piping OK. Unable to Assess Rooftop Radiator Unit due to Ladder Access H&S Concerns. Placed Pumps #1, 3 and 4 in Manual Off. Activated Pump #1 in Manual for Wet Well Drawdown. Drawdown Complete, Returned Pump #1 to Manual Off. Transferred Station Back to Utility Power with No Issues. Cleared Associated Alarms. Returned Pumps #1, 3 and 4 to Auto. Completed JHSC and Hazardous Waste Inspections with No Issues. Cleared Associated Alarm. | Vaughan Black Creek Pumping Station | 2026-03-11
WW-WEST | March | On site to look at pump 4 check valve stuck open. Removed end caps on shaft cleaned out debris greased and re installed. Check valve now moving free. | Vaughan Black Creek Pumping Station | 2026-03-12
WW-WEST | March | LOTO Complete PM?s on all pumps Greased driveshafts and pumps. Complete | Vaughan Black Creek Pumping Station | 2026-03-06
WW-WEST | March | Onsite for station check. Pump run test and seal water test pm. Station check ok - no new issues. Reviewed trends and added data into SharePoint. Pushed empty bin back in and topped up oil on bar screen. Pump run test : Pump1 - 601.7L/s at 281kPa Pump 2 - 469.9L/s at 100% at 257kPa Pump 3 - 133.3L/s at 100% at 214kPa Pump4 - 470.1L/s at 100% at 267kPA Pump 5 -OOS Completed seal water test PM no new issues. Checked seal water screens - all clear. | Vaughan Black Creek Pumping Station | 2026-03-06
WW-WEST | March | In to Complete Scheduled WOs. Notified ROC. Manually Rotated Scrubber Blower Duties. Blower #2 in Duty #1, Pump #1 in Duty #2. Completed Bar-screen and Wet Well Inspections. Tested Wet Well Overflow Alarms. Confirmed Reception by the ROC. No Issues Found. Returned to Service. Cleared Associated Alarms. Completed Consolidated Dry Well Inspections. Tested Hi/Lo Temperature and Dry Well Flood Alarms. Confirmed Reception by the ROC. Returned to Service. Cleared Associated Alarms. Pump #2 Failed to Start on Several Attempts, Using Multiple Methods, Such as Manual Start and Auto Duty Start. Suspected Discharge Valve Communication Error. Created Follow Up WO for PCS ?> W11719088. Pump #2 Manual Off and OOS Until Issue Rectified. Completed FM Air Valve Flushing and Inspections with No Issues. Returned to Service. | Vaughan Black Creek Pumping Station | 2026-03-09
WW-WEST | March | On site to troubleshoot pump 2 failing to start. With assistance from ROC, was able to observe pump 2 starting and running for two auto cycles. There were no issues to be seen. | Vaughan Black Creek Pumping Station | 2026-03-26
WW-WEST | March | Onsite for station check and weekly pump run test. No new issues. Reviewed trends and added data into SharePoint. Pump run test: Pump1 - 571.5L/s at 303kPa Pump 2 - OOS Pump 3 - 131.3L/s at 215kPa Pump4 - 473.8L/s at 269kPa Pump 5 -OOS After running pump 4 and placing it in manual off - discharge valve closed alarm came in. Reset and cleared alarm. Checked discharge and check valve all normal. Will continue to monitor. Returned all in service pumps back to auto. Pumps 2 and 5 left in manual off. Known issues with work orders created. Bar screen running and operating normally. | Vaughan Black Creek Pumping Station | 2026-03-20
WW-WEST | March | Onsite for station check - no new issues. Reviewed trends and added data into SharePoint. Bar screen room okay- replaced broken oil pump and topped up bar screen oil. Inspected spill kit - all sample bottles ok | Vaughan Black Creek Pumping Station | 2026-03-24
WW-WEST | March | Completed wetwell manual valve exercise. All valves exercised and sprayed down floors. Everything operating as normal | Vaughan Black Creek Pumping Station | 2026-03-23
WW-WEST | March | Onsite for station check - no new issues. Reviewed trends and entered data into SharePoint Pumps #2 and #5 still OOS - known issues with WO made Ran pump 4 to try to replicate the disch. Valve closed alarm from yesterday - alarm did not come in and pump ran normally. Checked contact on the valve and it appeared normal. Bin pushed out for pick up. Barscreen room ok. | Vaughan Black Creek Pumping Station | 2026-03-17
WW-WEST | March | On site to investigate bar screen fault alarm. No visual indicators of problem. Pressed reset button. Screen started and ran fine. Ran in hand for a few cycles and monitored. Found no problems. Returned to auto and reset alarms. | Vaughan Black Creek Pumping Station | 2026-03-19
WW-WEST | March | In to Complete Scheduled WO. | Vaughan Black Creek Pumping Station | 2026-03-23
WW-WEST | March | Onsite for station check and PMs Station check completed - reviewed trends and added data into SharePoint. Pump 4 check valve not closing. Cycled pump on to try to clear unsuccessful in getting check valve to close. Will continue to monitor and create work order if needed. Bar screen bin placed outside for pick up. Inspected odour control scrubber unit. Put unit into LOTO - Greased and checked belts. All okay. Mist eliminator at 2inches of water. Removed filter to clean and replaced with spare clean filter. Returned unit to on. Unit now at 1.6inches of water. | Vaughan Black Creek Pumping Station | 2026-03-03
WW-WEST | March | Remotely Rotated Scrubber Blower Duties. Blower #1 in Duty #1, Pump #2 in Duty #2. | Vaughan Black Creek Pumping Station | 2026-03-16
WW-WEST | March | On site to check dialer. Low battery alarm. Got replacement battery and installed. Ok now. | Vaughan Black Creek Pumping Station | 2026-03-19
WW-WEST | March | Onsite for station check - no new issues. Pump 2 fixed and back into duty rotation. Reviewed trends and added data into SharePoint. Barscreen okay - no issues | Vaughan Black Creek Pumping Station | 2026-03-27
WW-WEST | March | Onsite for station check - no new issues. Reviewed trends and added data into SharePoint. Bins pushed outside for pick up | Vaughan Humber Pumping Station | 2026-03-31
WW-WEST | March | Onsite to level barscreen bins | Vaughan Humber Pumping Station | 2026-03-29
WW-WEST | March | Onsite for station check and to meet Total Lift for sky jack and pallet truck inspection. Station check ok, no new issues. Reviewed trends and added data into SharePoint. Bar screen okay - rag bins leveled Empty rag bins pushed back in. Total Lift onsite at 10am Offsite at 10:20am - total power going to get new batteries for pallet truck. Back onsite at 11:11am to wait for Total Lift to return. Total Lift back onsite at 11:45am. Pallet truck batteries replaced and on charge. Skyjack batteries water refilled and inspections completed by Total Lift at 12:30pm Signed and reviewed all papers. | Vaughan Humber Pumping Station | 2026-03-13
WW-WEST | March | In to Complete Scheduled WO. Reviewed SCADA and Trends. No Issues Found. Levelled and Adjusted Bins. Inspected and Tidied HWs. Bar-screen Oil Hoppers OK. | Vaughan Humber Pumping Station | 2026-03-15
WW-WEST | March | On site to check and level screen room bins. | Vaughan Humber Pumping Station | 2026-03-07
WW-WEST | March | In to Receive Odour Control Unit Components for New Construction WVSS. | Vaughan Humber Pumping Station | 2026-03-03
WW-WEST | March | Onsite to assist with new odour control parts delivery. Completed station check - no new issues reviewed trends and added data into SharePoint. Bins pushed out for pick up. | Vaughan Humber Pumping Station | 2026-03-03
WW-WEST | March | Onsite for PMs. Called ROC to inform of generator run test and work being done. Pumped down wet well and placed all pumps in manual before transferring power to generator at 9:03am. Transferred smoothly pumps placed back in auto. Recorded generator run data into SharePoint. Inspected heat exchanger - operating normally Generator run test completed at 10:10am and power transferred back to hydro smoothly. Completed JHSC inspection and checked site for hazardous waste. Inspected hoist system - operates normally. Inspected force main valve chamber and triggered the valve chamber flood alarm. | Vaughan Humber Pumping Station | 2026-03-02
WW-WEST | March | Onsite for station check - no new issues. Reviewed trends and added data into SharePoint. Leveled bins and pushed empty bins back inside. | Vaughan Humber Pumping Station | 2026-03-06
WW-WEST | March | Onsite for dry well and wet well consolidated work orders with Marcus Completed housekeeping work order - cleaned bathroom and swept main room | Vaughan Humber Pumping Station | 2026-03-18
WW-WEST | March | Onsite for station check. No new issues. Reviewed trends and added data into SharePoint. Inspected spill kit - no issues. Bins out for pick up | Vaughan Humber Pumping Station | 2026-03-24
WW-WEST | March | In to Complete Scheduled WOs. Notified ROC. Completed Consolidated Dry Well Inspections and Maintenance. Greased Pumps and Driveshafts. Tested Associated Alarms and Confirmed Reception by the ROC. Cleared Associated Alarms. Completed Consolidated Wet Well Inspections and Maintenance. Greased Bar-screen Sprockets. Tested Associated Alarms and Confirmed Reception by the ROC. Cleared Associated Alarms. | Vaughan Humber Pumping Station | 2026-03-18
WW-WEST | March | On site for annual inspection of scissor lift and pallet lift. | Vaughan Humber Pumping Station | 2026-03-17
WW-WEST | March | Onsite for station check - no new issues. Reviewed trends and added data into SharePoint. Bar screen room okay - leveled rag bins | Vaughan Humber Pumping Station | 2026-03-20
WW-WEST | March | In to Complete Scheduled WOs and Assist Maint. with Bar-screen #2 Repair Work. Bar-screen #2 Rake Re-Aligned and Tested with No Issues. Returned Bar-screen Inlet Gate to Manual Open. Cleared Associated Alarm. Adjusted Bar-screen #1 Run Time Interval: 6 ?> 12.5 mins. Removed and Replaced HWs Bins for Pick Up. Tidied and Inspected HWs. Topped Up Bar-screen Oil Hoppers. No New Issues Found. Reviewed SCADA and Trends. No Issues Found. | Vaughan Humber Pumping Station | 2026-03-17
WW-WEST | March | On site to meet with Total Lift to have the 10 year engineering certify on scissor lift. | Vaughan Humber Pumping Station | 2026-03-24
WW-WEST | March | Checked and levelled screen room rag bins. | Vaughan Humber Pumping Station | 2026-03-22
WW-WEST | March | In to Investigate Bar-screen #2 Fault Communicated by the ROC. Found Bar-screen Torque Overload Fault due to Rake Misalignment. Placed Bar-screen in Local Off/OOS and Isolated Inlet Valve. Bar-screen #2 Not in Auto Alarm to Remain Outstanding. Adjusted Bar-screen #1 Run Time Interval: 12.5 ?> 6 mins. Created Follow-Up WO for Maint. ?> W11737270. Will Communicate with Appropriate Staff for Remedy at Next Earliest Convenience. | Vaughan Humber Pumping Station | 2026-03-16
WW-WEST | March | Onsite for station check - no new issues. reviewed trends and added data into SharePoint Bins pushed out for pick up. | Vaughan Humber Pumping Station | 2026-03-10
WW-WEST | March | Onsite for station check - no new issues reviewed trends and added data into SharePoint. Pushed fixed rag bin back inside. Topped up oil on bar screen | Vaughan Humber Pumping Station | 2026-03-27
WW-WEST | March | Repaired barscreen 2 Completed PM?s on both barscreens Barscreen 1 needs a chain oiler brush. | Vaughan Humber Pumping Station | 2026-03-17
WW-WEST | March | Check backflow setup for new building | Vaughan Humber Pumping Station | 2026-03-24
WW-WEST | March | On site with Lance Johnson. Sealed holes around screen room roll up door where rats have been getting access. Used spray foam, dirt, stones and bricks. | Vaughan Humber Pumping Station | 2026-03-24
WW-WEST | March | remotely enabled batch wasting mode at 6am Onsite at 8:30am manually wasted 30m3 total from 8:30am to 9am. RAS resumed after wasting completed. added 14 bags of soda ash to hopper | Kleinburg Water Resource Recovery Facility | 2026-03-29
WW-WEST | March | Harie Rajamithiran(OIT) working under the direction of Daniel Hirstwood(OIC). -Supernated STT 1 & transferred to SHT -Started batch wasting process at 09:30 to waste from 10:00 - 12:25 for 36.97m^3, Train 1(14.97m^3) & Train 2(22.00m^3). Wasted more from tank 2 to help balance out solids. -Completed lab analysis & station check, no abnormalities found -Turned RAS pumps 1&3 into manual off -Turned RAS pumps 2&4 into auto -Turned WAS pumps 1 &2 into manual off -Added 11 bags of soda ash into hopper -Completed scum tank cleaning, used skimmers in local. Set skimmers back into remote. -Completed aeration tank/channel outlet weir cleaning -Completed aeration condensation line bleed out, no liquid or solids were present -Raked bar screen & dewatering press -Cleaned rags off of distribution chamber inlet valve stem & aeration inlet valve stems -Switched outlet weir effluent hose to tank 1 due to outlet weir foam build up -Hosed down and cleaned sand filters | Kleinburg Water Resource Recovery Facility | 2026-03-30
WW-WEST | March | Harie Rajamithiran(OIT) working under the direction of Daniel Hirstwood(OIC). -Collected weekly compliance samples -Started batch wasting process at 09:45 to waste from 11:00-13:15 for 36.13m^3 into STT 1. Train 1(15.03m^3) & Train 2(21.10m^3), wasted more from train 2 to balance out solids. -Completed lab analysis station check , no issues found -Generator 2 being worked on by contractors -Added 9 bags of soda ash into hopper -Raked bar screen & dewatering press -Cleared rags from distribution inlet valve stem -Checked aeration inlet valve stems, no rags present -Switched effluent hose to aeration tank 2 outlet weir -Diesel generator 2 ran by contractors for 3.9 hrs -Diesel generator 1 being ran until approximately 16:30 -Completed biorem odour control unit inspection, no issues found -Turned WAS pumps 1&2 into manual off | Kleinburg Water Resource Recovery Facility | 2026-03-31
WW-WEST | March | Onsite for influent flow meter chamber inspection. Called ROC to inform of work being done. inspection completed - no issues found. No need to pump out. Activated plant 2 influent chamber float alarm - reset alarm. Reset thick'd sludge pmp 2 pres. switch hi alm with Harie - alarm now cleared. Set raw sampler to be ready for sample collection tommorow. | Kleinburg Water Resource Recovery Facility | 2026-03-30
WW-WEST | March | Switch aeration alum pumps to manual speed @ 46%. Filter inlet alum pump speed to 30% manual. | Kleinburg Water Resource Recovery Facility | 2026-03-11
WW-WEST | March | Harie Rajamithiran(OIT) working under the direction of Gavin Walker(OIC). -Supernated thickening tank 1 and transferred to holding tank -Completed lab analysis and station check , no issues found -Wasting process from 09:00-13:00, wasted 13.50m^3 from train 1 & 13.58m^3 from train 2 for a total of 27.08m^3 -Completed scum tank cleaning -Completed Biorem Odour Control Unit inspection , no issues found -Trend gap in SCADA data is present due to PAC issues from 11:27 -12:20 | Kleinburg Water Resource Recovery Facility | 2026-03-03
WW-WEST | March | Harie Rajamithiran(OIT) working under the direction of Daniel Hirstwood(OIC). -Completed lab analysis & station check , no issues found -Started batch wasting process at 09:00 , wasting from 10:00-12:00 for 25.01m^3 -Added 10 bags of soda ash into hopper -Turned WAS pumps 1&2 to manuel off -All 3 scum pumps are in manuel due to high flows -Checked Raw Sewage & Final Composite Effluent Samplers , no issues found -Checked headworks heat traces , no issues found -Inspected Bioremediation Odour Control Unit , no issues found -WAS_MV2 valve is hand cranked fully closed | Kleinburg Water Resource Recovery Facility | 2026-03-10
WW-WEST | March | Remotely Enabled Batch Waste Set-point. RAS Pumps Auto Off in Preparation for Wasting @ 08:50. | Kleinburg Water Resource Recovery Facility | 2026-03-15
WW-WEST | March | Remotely changed alum pumps 1, 3, 4 speed to auto | Kleinburg Water Resource Recovery Facility | 2026-03-12
WW-WEST | March | Harie Rajamithiran(OIT) working under the direction of Lance Johnson(OIC). -Collected weekly compliance samples -Started batch wasting process 10:00, wasting from 11:00-13:00 for 30.02m^3 -WAS_MV2 is now operational -Completed online DO probe maintenance -Completed sand filter hose down and performance check -Hosed down clarifier weirs | Kleinburg Water Resource Recovery Facility | 2026-03-11
WW-WEST | March | Completed labs and entered data in ace sheets. Added 9 bags soda ash to hopper. Enabled wasting timer at 9:57. Set auto wasting to waste 15 m3 from each train in 6 cycles between 11:00 and 13:00. Reset high temp alarm on sludge blower motor. Set scum pumps to auto. Cleared high level alarm on scum tank. Completed station check. No issues found. Corrected sand filter 2, cell one so its pulling sand again. | Kleinburg Water Resource Recovery Facility | 2026-03-12
WW-WEST | March | Harie Rajamithiran(OIT) working under the direction of Young Jung(OIC). -Completed lab analysis & station check , no issues found -Started batch wasting process at 10:00 , wasting from 11:00-13:00 for 26.01m^3 -Added 8 bags of soda ash into hopper -Received 400 bags of soda ash from 10:40-11:10 -Completed circular plant clarifier maintenance , did not run clarifier as bottom of the tank is frozen -Completed rectangular plant clarifier maintenance , no issues found except for having to adjust the shear pin slightly on clarifier 1 to avoid false over torque alarm -Completed scum tank 3 valve/actuator exercise -Thickening tank 2 LIT level trend does not correspond with the increases in level expected from the wasting process. The affected timeline is 11:00-14:39 , PCS will be notified and a CMU 4 will be created | Kleinburg Water Resource Recovery Facility | 2026-03-05
WW-WEST | March | Remotely enabled batch wasting mode at 21:20 On site added 8 x 25kg bags of soda ash to auto dispenser hopper. Begin wasting and will continue WAS process remotely. | Kleinburg Water Resource Recovery Facility | 2026-03-07
WW-WEST | March | Completed the diesel generator runs Completed the jhsc inspection WAS_MV2 faulted and could not be reset W11702216 was created to address this | Kleinburg Water Resource Recovery Facility | 2026-03-03
WW-WEST | March | Manually exercised aeration butterfly valves. Manually exercised distribution chamber butterfly valves. Inspected soda ash gear reducer. Changed oil and inspected vortex blowers. Changed oil and inspected diversion tank blowers. Inspected circular plant blowers. Completed 2 month maintenance on air compressors. | Kleinburg Water Resource Recovery Facility | 2026-03-04
WW-WEST | March | - Received a call from ROC at 2:55 about a PAC3 communication failure alarm that occurred at 2:06. PCS on call was already notified and could not resolve issue remotely. Requested PCS on call, Yash Savaliya be dispatched to site - Looked through intelex procedure and followed protocol - Arrived on site at 3:33 and PCS on call arrived at roughly 3:38. Dialer alarm shows RTU failure in the headworks scada panel room. - No communication (PAC3) for sludge/scum loading, and sludge, and WAS pumps interlocked due to the failure. Aeration temperature value, aeration DO readings and aeration solids value are all affected since 1:51 until 2:47. Plant 2 influent readings is affected from 1:51 until 3:46 (gap in trend from 2:46 until 3:46) - PCS on call made repairs. Changed blown out fuse and reset breakers affecting FIT. Reset historian heartbeat alarm. Gap in trend from 4:19:37 until 4:19:47 - Reset alarms, pac4 to pac3 communication failure, pac3 communication alarm, KBSPSH pac communication failure, historian heartbeat alarm all cleared - Quickly addressed the issue and no local controls was needed to operate the plant - Once confirming proper operation. Left site at 4:23 | Kleinburg Water Resource Recovery Facility | 2026-03-01
WW-WEST | March | Harie Rajamithiran(OIT) working under the direction of Daniel Hirstwood(OIC). -Completed lab analysis & station check , no issues found -Started batch wasting process at 10:00 , wasting from 11:00-13:00 for 26.02m^3 -Added 12 bags of soda ash into hopper -Rotated RAS pumps, P1 for train 1 & P3 for train 2 -Completed scum tank cleaning -Supernated STT 1 and transferred to SHT -Turned WAS pumps 1&2 to manuel off -WAS_MV2 is hand cranked fully open | Kleinburg Water Resource Recovery Facility | 2026-03-09
WW-WEST | March | Remotely Responded to Scum Tank Level HiHi Alarm. Paced Scum Pumps #1 and 2 in Manual Off for the Duration of On-going High Flows Entering the Plant. Notified ROC and On-call Staff Member. | Kleinburg Water Resource Recovery Facility | 2026-03-10
WW-WEST | March | Harie Rajamithiran(OIT) working under the direction of Lance Johnson(OIC). -Completed lab analysis & station check , no issues found -Started batch wasting process at 09:00 , wasting from 10:00-12:00 for 26.02m^3 -Added 11 bags of soda ash into hopped -WAS_MV2 is hand cranked closed -Turned WAS pumps 1&2 into manuel off -Supernated thickening tank 2 and transferred to holding tank -Completed plant 2 WAS pumps 1-2 and check valve inspections , no issues found -Cleared bar screen and dewatering press of debris -Programmed final effluent composite sampler to start on March.8/2026 | Kleinburg Water Resource Recovery Facility | 2026-03-06
WW-WEST | March | Received load of alum. Reviewed and confirmed certificate of analysis. Filled tank from 0.76m to 3.45m. Inspected sludge, rectangular plant aeration, diversion and vortex blowers. No issues with any of the above. | Kleinburg Water Resource Recovery Facility | 2026-03-13
WW-WEST | March | In to Complete Scheduled WOs. WAS Pump #1 and 2 Manual On and Off Intermittently and Sequentially for Wasting. Topped Up Soda Ash Hopper ?> 16 Bags. Wasting Complete, Reset Batch Wasting Set-point. RAS Pumps #1 and 3 Running in Auto. Wasted 15 m3 from Each Clarifier. Rotated Active Sludge Thickening Tank. WAS Valve #2 Manual Closed, WAS Valve #1 Manual Open. | Kleinburg Water Resource Recovery Facility | 2026-03-15
WW-WEST | March | Exercised ras and was valves for rectangular and circular plant. Inspected rectangular plant ras pumps. Inspected circular plant blowers. Inspected circular plant ras and was pumps. | Kleinburg Water Resource Recovery Facility | 2026-03-11
WW-WEST | March | Harie Rajamithiran(OIT) working under the direction of Marcus Remonde(OIC). -Supernated thickening tank 2 and transferred to holding tank -Completed lab analysis and station check , no issues found. MLVSS was omitted , as oven temperature was too hot and melted samples -Added 12 bags of soda ash into the hopper -Started batch wasting process at 09:00 , wasting 30.02m^3 from 10:00 - 12:00 -Put WAS pumps 1&2 into manuel off -Completed RSHW BLO1 & BLO2 inspections , no issues found -Bled aeration condensation line.No condensate or liquid came out , only air was present -Completed aeration outlet weir rag cleaning -Cleaned bar screen/dewatering area | Kleinburg Water Resource Recovery Facility | 2026-03-02
WW-WEST | March | Hosed aeration tank outlets and weirs. | Kleinburg Water Resource Recovery Facility | 2026-03-16
WW-WEST | March | Harie Rajamithiran(OIT) working under the direction of Daniel Hirstwood(OIC). -Started batch wasting process at 10:00 , wasting from 11:00-13:00 for 30.03m^3. Train 1(15.07m^3) & Train 2(14.95m^3). -Wasted an additional 5.08m^3 from train 2 as solids are higher in aeration tank 2 -Put WAS pumps 1&2 into manuel off -Supernated STT 1 & transferred to SHT -Completed lab analysis and found that clarifier 1&2 has a slight spike of ammonia, 0.197mg/L & 0.177mg/L respectively. Final Effluent parameters are good. -Transferred sludge from STT 2 to SHT without supernating to make sure weekend wasting has space. Initial STT 2 level - 2.20m & Final STT 2 level-1.88m after transferring to SHT without supernating -Completed station check , no issues found -Removed rags from aeration inlet & distribution chamber inlet valve stems -Raked bar screen & dewatering press -Added 10 bags of soda ash into hopper -Turned off Effluent hose that was running in headworks building by the soda ash hopper | Kleinburg Water Resource Recovery Facility | 2026-03-27
WW-WEST | March | Onsite for daily PMs Decanted sludge thickening tank 2 and transferred remaining sludge to holding. Placed WAS pumps into Auto - Enabled batch wasting mode at 8:45am and set auto waste to waste 30m3 (15m3 each tank) from 10am to 12pm. WAS pumps placed back into manual upon wasting completion and RAS pumps placed back into operation. Rotated RAS pumps in operation from RAS pumps 1 and 3 to RAS pumps 2 and 4. Added 7 bags of soda ash to hopper. Ran helical skimmers in manual and Manually pumped down scum tank to clean scum tank. Scum pump placed back into auto and skimmers also placed back into auto upon completion. Barscreen cleared of rags and confirmed operation. Distribution valve cleared of rags. Completed daily lab and Completed station check - no new issues added data into SharePoint | Kleinburg Water Resource Recovery Facility | 2026-03-16
WW-WEST | March | On site to assist contractor Total Power with diesel generator 1 maintenance and load test. Informed ROC of generator work. Completed work on generator 1. | Kleinburg Water Resource Recovery Facility | 2026-03-16
WW-WEST | March | Completed labs and entered data in ace sheet. Completed station check. No issues found. Enabled was timer at 09:53. Set autowasting for 15 m3 per train in 3 cycles each between 10:00 and 12:00. Autowasting wasted 13 m3 from train 1 and 17 m3 from train 2. Added 10 bags to soda ash hopper. Inspected odour control machine. Adjusted pressure regulating valve to get 30 psi on the irrigation line pressure. Completed housekeeping in blower building. Cleaned aeration channel and bled condensation. | Kleinburg Water Resource Recovery Facility | 2026-03-17
WW-WEST | March | Collected weekly compliance samples. Lowered supernate tube on sludge tank 1. | Kleinburg Water Resource Recovery Facility | 2026-03-18
WW-WEST | March | On site with total lift for annual inspecttions | Kleinburg Water Resource Recovery Facility | 2026-03-19
WW-WEST | March | Harie Rajamithiran(OIT) working under the direction of Daniel Hirstwood(OIC). -Turned RAS pumps 2&4 into manuel off -Turned RAS pumps 1&3 into auto -Started batch wasting process at 09:00 , wasting from 10:00-12:00 for 30.02m^3 -Completed lab analysis & station check , no issues found -Turned WAS pumps 1&2 into manuel off -Supernated STT 1 and transferred to SHT -Added 9 bags of soda ash into hopper -Raked bar screen and dewatering press -Completed scum tank cleaning -Completed aeration outlet weir cleaning -Bled out aeration condensation line , no condensate was found | Kleinburg Water Resource Recovery Facility | 2026-03-23
WW-WEST | March | On site to assist contractor Total Power with Diesel Generator #2 PM. | Kleinburg Water Resource Recovery Facility | 2026-03-17
WW-WEST | March | Shut off Bertha/Generator 2 for contractors. Completed labs and entered data in ACE sheets. Completed station check. No issues found. Added 9 bags to soda ash hopper. Enabled was timer at 8:51. Set auto-wasting for 30 m3 total between 11:00 and 13:00 in 6 cycles. Wasted a bonus 5 m3 from train 2. Shut effluent water to headworks off for maintenance work order. Wasted an extra 5 m3 from tank 2 at 13:05. Verified correct dip switch positions for uv channel 1 bank 2, rack 2. They are in the correct positions. Turned water back on in headworks after pipe repaired. Turned generator 2 back to auto. | Kleinburg Water Resource Recovery Facility | 2026-03-26
WW-WEST | March | Completed labs and entered data in ace sheet. Completed station check. No issues found. Enabled was timer at 09:11. Set autowasting for 10 m3 per train in 2 cycles each between 10:00 and 11:00. Added 10 bags to soda ash hopper. Cleaned out UV channel. | Kleinburg Water Resource Recovery Facility | 2026-03-20
WW-WEST | March | Did housekeeping. | Kleinburg Water Resource Recovery Facility | 2026-03-16
WW-WEST | March | Added 17 bags to soda ash hopper. Raked inside bar screen. Picked rags from valve stems. Confirmed auto-wasting under way. | Kleinburg Water Resource Recovery Facility | 2026-03-22
WW-WEST | March | Cleaned and verified DO probes. | Kleinburg Water Resource Recovery Facility | 2026-03-25
WW-WEST | March | Enabled 200 min was timer. Set autowasting for 30 m3 total between 10:00 and 12:00. Set was pumps to auto. | Kleinburg Water Resource Recovery Facility | 2026-03-22
WW-WEST | March | Completed labs and entered data in ace sheet. Completed station check. No issues found. Enabled was timer at 08:55. Set autowasting for 15 m3 per train in 3 cycles each between 10:00 and 12:00. Added 9 bags to soda ash hopper. | Kleinburg Water Resource Recovery Facility | 2026-03-19
WW-WEST | March | Harie Rajamithiran(OIT) working under the direction of Lance Johnson(OIC). -Turned WAS pumps 1&2 into manuel off -Completed aeration building housekeeping -Completed odour control building & sludge blower room housekeeping | Kleinburg Water Resource Recovery Facility | 2026-03-19
WW-WEST | March | Harie Rajamithiran(OIT) working under the direction of Daniel Hirstwood(OIC). -Collected weekly compliance samples -Started batch wasting process at 10:00 , wasting from 11:00-13:00 for 30.01 m^3. Train 1 (15.04m^3) & Train 2 (14.97m^3) -Added 9 bags of soda ash into hopper -Completed lab analysis & station check , no issues found -Turned WAS pumps 1&2 into manuel off -Raked bar screen & dewatering press -Swept sludge handling building | Kleinburg Water Resource Recovery Facility | 2026-03-25
WW-WEST | March | Harie Rajamithiran(OIT) working under the direction of Daniel Hirstwood(OIC). -Started batch wasting process at 08:40 , wasting from 10:00-12:00 for 26.05 m^3. Train 1 (12.98m^3) & Train 2 (13.07m^3) -Added 8 bags of soda ash into hopper -Completed lab analysis & station check , no issues found -Turned WAS pumps 1&2 into manuel off -Raked bar screen & dewatering press -Cleaned rags off of aeration inlet valve stems & distribution tank valve stem -Swept & mopped circular plant MCC room & washroom -Completed biorem odour control unit inspection , no issues found -Completed filter bypass float alarm test , no issues found and verified with ROC that alarm came through | Kleinburg Water Resource Recovery Facility | 2026-03-24
WW-WEST | March | On site to assist contractor Total Power with diesel generator #2 load test. Completed | Kleinburg Water Resource Recovery Facility | 2026-03-18
WW-WEST | March | Supernated STT and released to SHT. Completed labs and entered data in ace sheet. Completed station check. No issues found. Enabled was timer at 09:49. Set autowasting for 15 m3 per train in 3 cycles each between 10:00 and 12:00. Autowasting volumes are correct with waste pumps in auto speed. Added 8 bags to soda ash hopper. Completed housekeeping work order for headworks building. Completed DO probe maintenance. Created work order (W11744156) for service water pipe in need of re-securing to wall in headworks. | Kleinburg Water Resource Recovery Facility | 2026-03-18
WW-WEST | March | Checked in with David Dougherty and diesel mechanics. Cleaned and hosed aeration outlets. | Kleinburg Water Resource Recovery Facility | 2026-03-16
WW-WEST | March | Onsite for station check - no new issues, reviewed trends and added data into sharepoint. flushed barscreen and auger, bar screen room okay. | King City Pumping Station | 2026-03-31
WW-WEST | March | Harie Rajamithiran(OIT) working under the direction of Lance Johnson(OIC). -Collected weekly compliance samples -Completed lab analysis and station check , ammonium was spiked for two composite final effluent samples for 0.181 mg/L & 0.192 mg/L . Final grab was tested for ammonium verification for 0.174 mg/L. -Aeration tank 2 inlet was clogged up with rags, upon removal of rags tank 2 DO has dropped back to regular levels. -Wasting was not done to regulate solids due to ammonium spike , clogged up aeration tank 2 inlet and DO spike. -Completed tertiary and headworks sump inspections , verified pumps, tipped floats and verified with ROC of alarms. -No hazardous waste present for collection and removal -Added 8 bags of soda ash into hopper -Completed online DO probe maintenance | Kleinburg Water Resource Recovery Facility | 2026-03-04
WW-WEST | March | In to Investigate UV Channel #1 Low Intensity Alarm and Potential Burnt Out Bulb. Placed Channel Inlet Valve in Local Off and UV Bank A in Local On for Testing Purposes. No Issues Found. UVI Sensor for Channel #2, Bank A Not Functioning Properly. Rotated Bank Lead/Lag Priority. Bank B in Lead Position. Outstanding Intensity Alarms Cleared. Will Conduct Investigation of UVI Sensor at Next Earliest Convenience. | Kleinburg Water Resource Recovery Facility | 2026-03-02
WW-WEST | March | On site with Technician from Rotork to try and repair WAS FV2 actuator. Actuator is repaired. Back in remote operation. | Kleinburg Water Resource Recovery Facility | 2026-03-11
WW-WEST | March | Wasted 12.5m3 per side for a total of 25m3. Reset batch wasting mode. RAS pumps back into auto and running. Scum tank in hi level - notify ROC to disregard as sludge holding tank is too high to pump scum. | Kleinburg Water Resource Recovery Facility | 2026-03-07
WW-WEST | March | In to Provide Assistance with FE and Raw Composite Sampler Inspections and Programming. Returned All to Service. | Kleinburg Water Resource Recovery Facility | 2026-03-09
WW-WEST | March | Harie Rajamithiran(OIT) working under the direction of Lance Johnson(OIC). -Supernated STT 1 and transferred to SHT -Completed consolidated headworks inspection -Added 10 bags of soda ash into hopper -Started batch wasting process at 10:00 , wasting from 11:00 - 13:00 for 26.01 m^3 into STT 2 -Turned WAS pumps 1&2 into manuel off | Kleinburg Water Resource Recovery Facility | 2026-03-13
WW-WEST | March | Returned ?Bertha? to auto. | Kleinburg Water Resource Recovery Facility | 2026-03-19
WW-WEST | March | Station checks, SharePoint readings and review of continuous monitoring data. Cycled and cleaned screen room equipment. Site walkthrough. | King City Pumping Station | 2026-03-13
WW-WEST | March | Check leaking backflow preventer leaking | King City Pumping Station | 2026-03-11
WW-WEST | March | Onsite for station check- no new issues. Reviewed trends and added data into SharePoint. Barscreen okay - flushed and checked oil levels. Checked overflow sample kit. - no issues. | King City Pumping Station | 2026-03-10
WW-WEST | March | On site to let King Township in to replace water meter. Successfully replaced the water meter with no issues | King City Pumping Station | 2026-03-02
WW-WEST | March | Onsite to assist with wet well cleaning and assisted with work orders. | King City Pumping Station | 2026-03-05
WW-WEST | March | Onsite for station check - reviewed trends and added data into SharePoint. Found service water backflow preventer leaking. Created work order. | King City Pumping Station | 2026-03-03
WW-WEST | March | Onsite to push Barscreen rag bin out. Bin out and ready for pick up | King City Pumping Station | 2026-03-19
WW-WEST | March | Onsite for for station check - no new issues. Reviewed trends and added data into SharePoint. Barscreen okay - flushed and pushed empty bin back in | King City Pumping Station | 2026-03-20
WW-WEST | March | On site for pump vibration test. Rotated 2 and 3. Pump1 is OOS | King City Pumping Station | 2026-03-20
WW-WEST | March | Remotely Responded to Pump #3 Fault Communicated by the ROC. Rotated RS Pump Duties. RS Pump #3 Manual Off, Duty #4/OOS. RS Pump #1 in Auto, Duty #2. | King City Pumping Station | 2026-03-16
WW-WEST | March | Onsite for station check - no new issues. Reviewed trends and added data to SharePoint. Flushed and checked Barscreen - no issues oil levels good | King City Pumping Station | 2026-03-27
WW-WEST | March | Reset pump 3 fault. Tested. Works well. | King City Pumping Station | 2026-03-16
WW-WEST | March | On site for annual generator PM and load test | King City Pumping Station | 2026-03-23
WW-WEST | March | Onsite for station check - no new issues. Reviewed trends and added data into SharePoint. Barscreen flushed and oil levels ok. | King City Pumping Station | 2026-03-17
WW-WEST | March | On site to check the raw composite sampling schedule. all okay and good for sampling tomorrow | Nobleton Janet St. Sewage Pumping Station | 2026-03-30
WW-WEST | March | Onsite for station check - no new issues reviewed trends and entered data into SharePoint. | King City Pumping Station | 2026-03-03
WW-WEST | March | In to Complete Scheduled WOs. Notified ROC. Placed Pumps #1 and 3 in Manual On for Wet Well Level Drawdown. Drawdown Complete, Placed Pumps in Manual Off. Transferred Station to Generator Power with No Issues. Acknowledged and Cleared Associated Alarms. Returned Pump #1 to Auto, Duty #2. Placed Pumps #3 in Manual On for Wet Well Level Drawdown. Drawdown Complete, Placed Pump in Manual Off. Completed JHSC Inspection with No Issues. Transferred Station Back to Utility Power with No Issues. Cleared Associated Alarms. | King City Pumping Station | 2026-03-11
WW-WEST | March | In to Complete Scheduled WOs. Notified ROC. Contractor On-site for Wet Well Cleaning. Completed Drawdown and Isolation Procedures as Necessary. Completed Hi/Lo Temp., Dry Well Flood and Diesel Containment Flood Alarm Tests. Confirmed Reception by the ROC. Returned to Service and Cleared Associated Alarms. Completed Dry Well Manual Valve Exercises, Overhead Hoist and Sump System Inspections with No Issues. Returned to Service. Wet Well Cleaning Complete. Returned Station to Service. Cleared Associated Alarms. Completed Consolidated Screen Room Inspections and Maintenance with No Issues. Returned to Service. | King City Pumping Station | 2026-03-05
WW-WEST | March | Onsite for station check - no new issues, reviewed trends and added data into SharePoint. Rotated duty pumps. Barscreen room good - flushed bar screen screw | King City Pumping Station | 2026-03-06
WW-WEST | March | Reset pump 3, which tripped breaker when power transferred to generator. Loss of power due to planned power outage. Reviewed generator parameters. All okay at this time. Set pump 3 to auto/duty 4/oos and pump 2 auto/duty 2. Pump 1 running in duty 1. Reset SCADA alarms. | King City Pumping Station | 2026-03-25
WW-WEST | March | In to Complete Scheduled WOs. Rotated Pump Duties. Pump #2 Manual Off, Duty #4/OOS. RS Pump #1 in Auto, Duty #2. Reviewed SCADA and Trends. No Issues Found. Levelled Bin. Inspected and Tidied HWs. Topped Up Bar-screen Oil Hopper. No Issues Found. | King City Pumping Station | 2026-03-24
WW-WEST | March | Onsite for pump 1 and pump 2 ultrasonic backup mode alarms. Wetwell hi hi level alarm and wetwell overflow alarm due to hi level. Wetwell in backup mode and high levels due to rain event. Upon arrival onsite both pumps 2 and 3 running in backup mode with wetwell at 4.20m. Wet well level slowly coming back down as rain event finishes. Wetwell did not exceed 4.30m. No overflow occurred. Checked wetwell manually to confirm. Placed pump 1 and pump 3 in manual to try to rotate pumps to place pump 1 in duty and pump 3 in off. Due to an energy limit in the coding and being in backup mode pump 1 failed to start and pump 3 failed to stop. Will continue to monitor as wetwell level comes back down | Nobleton Janet St. Sewage Pumping Station | 2026-03-31
WW-WEST | March | - Checked station and recorded readings on SharePoint. No new issues - Collected weekly regulatory samples | Nobleton Janet St. Sewage Pumping Station | 2026-03-31
WW-WEST | March | Harie Rajamithiran(OIT) working under the direction of Daniel Hirstwood(OIC). -Dropped off Kleinburg WRRF weekly compliance samples -Created contingency entry due to EZmax mobile error. | Nobleton Janet St. Sewage Pumping Station | 2026-03-31
WW-WEST | March | Harie Rajamithiran(OIT) working under the direction of Lance Johnson(OIC). -Dropped off Kleinburg weekly compliance samples | Nobleton Janet St. Sewage Pumping Station | 2026-03-04
WW-WEST | March | Relieve Young Jung from site. Wessuc completed sewer cleaning and camera inspection. Change pump duty 1 and 2 start and stop set points to their original and normal operating ranges. Duty 1: start @ 1.4m, Stop @0.90m Duty 2: start @ 1.7m, Stop @ 1.10m Enabled low level lockout and review local scada. All pumps returned to auto speed. | Nobleton Janet St. Sewage Pumping Station | 2026-03-09
WW-WEST | March | Collected regulatory samples | Nobleton Janet St. Sewage Pumping Station | 2026-03-11
WW-WEST | March | In to Complete Scheduled WOs. Reviewed SCADA and Trends. No Issues Found. Completed Overflow Kit Inspection and Refill. No Issues Found. | Nobleton Janet St. Sewage Pumping Station | 2026-03-13
WW-WEST | March | Once Wessuc was done with sewer line cleaning and wet well cleaning. Placed pumps 1 and 2 to auto speed. Placed pump 3 back into pump rotation as duty 3. Changed pump duty rotation from all stop to timed. Changed wet well duty 1 start from 1 m to 1.4 m. Duty 1 stop from 0.75 m to 0.9 m. Changed wet well duty 2 start from 1.3 m to 1.7 m. Kept duty 2 stop the same at 1.1 m Reenabled low level lockout Checked dry well once again and confirmed normal plant operation | Nobleton Janet St. Sewage Pumping Station | 2026-03-06
WW-WEST | March | Checked station and recorded readings on SharePoint. No new issues Inspected raw sampler. No issues | Nobleton Janet St. Sewage Pumping Station | 2026-03-10
WW-WEST | March | Harie Rajamithiran(OIT) working under the direction of Lance Johnson(OIC). -Dropped off Kleinburg WRRF weekly compliance samples | Nobleton Janet St. Sewage Pumping Station | 2026-03-11
WW-WEST | March | On site to meet Wessuc to finish up sewer line cleaning. Notified ROC of the work being performed Disabled low level lock out to bring the wet well down to operate at a lower pump start and stop cycle. Currently hydrostatic is controlling. Placed pump 2 to duty 1, pump 1 to duty 2, and pump 3 to duty 4. Changed wet well duty 1 start from 1.4 m to 0.9 m. Duty 1 stop from 0.9 m to 0.63 m Changed wet well duty 2 start from 1.7 m to 1.3 m. Kept stop at the same level at 1.10 m. Pumped down wet well using pump 1 at manual 100% speed. Once wet well level went down to 0.63 m and pumps shut off. Changed pump duty rotation to all stop and to rotate between pump 1 and 2. Placed pump 3 into duty 4. Placed pump 1 and pump 2 to manual speed 85%. Will monitor and adjust pump speed as needed depending on incoming flows | Nobleton Janet St. Sewage Pumping Station | 2026-03-09
WW-WEST | March | On site to meet Wessuc for sewer line cleaning. Notified ROC of the work being performed Disabled low level lock out to bring the wet well down to operate at a lower pump start and stop cycle. Currently hydrostatic is controlling. Placed pump 2 to duty 1, pump 1 to duty 2, and pump 3 to duty 4. Changed wet well duty 1 start from 1.4 m to 1.00 m. Duty 1 stop from 0.9 m to 0.74 m Changed wet well duty 2 start from 1.7 m to 1.3 m. Kept stop at the same level at 1.10 m. Pumped down wet well using pump 1 at manual 100% speed and pump 2 in auto speed. Once wet well level went down to 0.8 and pumps shut off. Changed pump duty rotation to all stop and to rotate between pump 1 and 2. Placed pump 3 into duty 4. Will monitor and adjust pump speed as needed depending on incoming flows | Nobleton Janet St. Sewage Pumping Station | 2026-03-06
WW-WEST | March | - Checked station and recorded readings on SharePoint. No new issues - Notified ROC of the work being performed - Inspected the generator and fuel level, all okay. Started the generator at 10:56. Recorded readings on SharePoint after 30 minutes, no issues. Ran for approximately one hour. Runtime for generator 1 from 456:57:00 hrs to 458:00:00 hrs. Fuel level from 76 cm (1496 L) to 76 cm (1494 L). Past trend shows LIT for fuel level bouncing around. Will monitor and create a work order if it occurs again - Performed JHSC inspection. Tested eyewash. No issues found | Nobleton Janet St. Sewage Pumping Station | 2026-03-03
WW-WEST | March | Checked station and recorded readings on SharePoint. No new issues | Nobleton Janet St. Sewage Pumping Station | 2026-03-27
WW-WEST | March | Worked on valve exercise and comprehensive housekeeping work orders. | Nobleton Janet St. Sewage Pumping Station | 2026-03-23
WW-WEST | March | On site for vibration. Rotated all 3 pumps | Nobleton Janet St. Sewage Pumping Station | 2026-03-20
WW-WEST | March | Harie Rajamithiran(OIT) working under the direction of Daniel Hirstwood(OIC). -Dropped off Kleinburg WRRF weekly compliance samples | Nobleton Janet St. Sewage Pumping Station | 2026-03-25
WW-WEST | March | In to Investigate Pump #1 VFD Fault Communicated by the ROC. Pump #1 Overcurrent Fault Outstanding. No Other Issues Observed. Reset Fault Locally and Via SCADA. Returned Pump to Duty. | Nobleton Janet St. Sewage Pumping Station | 2026-03-16
WW-WEST | March | Completed comprehensive housekeeping and valve exercise work orders. | Nobleton Janet St. Sewage Pumping Station | 2026-03-23
WW-WEST | March | Checked station and recorded readings on SharePoint. No new issues | Nobleton Janet St. Sewage Pumping Station | 2026-03-24
WW-WEST | March | Checked station and trends, and recorded readings on SharePoint | Nobleton Janet St. Sewage Pumping Station | 2026-03-20
WW-WEST | March | Checked station and trends. No new issues | Nobleton Janet St. Sewage Pumping Station | 2026-03-17
WW-WEST | March | On site to collect weekly regulatory samples. No issues | Nobleton Janet St. Sewage Pumping Station | 2026-03-25
WW-WEST | March | Collected weekly regulatory samples | Nobleton Janet St. Sewage Pumping Station | 2026-03-18
WW-WEST | March | Onsite for station check - no new issues. Reviewed trends and added data into SharePoint | Vaughan Pine Valley Pumping Station | 2026-03-31
WW-WEST | March | Collected regulatory samples | Nobleton Janet St. Sewage Pumping Station | 2026-03-04
WW-WEST | March | - Inspected the hoist system. No issues - Inspected pump 1-3, motor and check valve. No issues found - Flushed air relief valve. All okay - Tested dry well flood alarm. Alarm received on dialer and SCADA as sewage station flood alarm - Tested building how and low temperature alarm. Alarm received - Tested sump pump. Both sump pumps run on hand control and by float. No issues - Checked station and recorded readings on SharePoint. No new issues | Nobleton Janet St. Sewage Pumping Station | 2026-03-06
WW-WEST | March | Onsite for station check - no new issues. Reviewed trends and added data into SharePoint. | Vaughan Pine Valley Pumping Station | 2026-03-13
WW-WEST | March | Onsite for station check - no new issues reviewed trends and added data into SharePoint. | Vaughan Pine Valley Pumping Station | 2026-03-03
WW-WEST | March | On site for odour control PM. Completed | Vaughan Pine Valley Pumping Station | 2026-03-23
WW-WEST | March | Onsite for station check - no new issues. Reviewed trends and added data into SharePoint. Checked overflow spill kit and checked expiration date. No issues found. | Vaughan Pine Valley Pumping Station | 2026-03-17
WW-WEST | March | In to Complete Scheduled WOs. Notified ROC. Reviewed SCADA and Trends. Identified Discrepancy Between Hydrostatic and Ultrasonic LITs. Notified TL for Future Corrective Action. Duty Pumps Cycling Without Issue Despite. Transferred Station to Generator Power with No Issues. Acknowledged Associated Alarms. Transferred Station Back to Utility Power with No Issues. Cleared Associated Alarms. Completed Generator Exhaust Stack Condensate Draining with No Issues. Completed Consolidated Dry Well Inspections. Confirmed Reception of Associated Alarms with ROC. Returned to Service and Cleared Associated Alarms. Completed JHSC and Hazardous Waste Inspections. Identified Degrading of Station External Roof Material and Notified TL and West WW-Staff. No Other Issues Found. Completed Odour Control Scrubber System Inspection. Belt and Media OK. Exercised Manual Isolation Valve and Greased Bearings. Identified Burnt Out Intrinsically Safe Bulb within Odour Control Room. Notified TL for Replacement. | Vaughan Pine Valley Pumping Station | 2026-03-20
WW-WEST | March | Onsite for station check - no new issues. Reviewed trends and added data into SharePoint. Odour control unit room okay. | Vaughan Pine Valley Pumping Station | 2026-03-27
WW-WEST | March | Onsite for station check and manual valve exercise PM Station check ok. No new issues. Reviewed trends and added data into SharePoint. Completed manual valve exercise WO. When doing the manual valve exercise WO. pumps 2 and 3 were placed into manual off with pump 1 in auto. Pump 1 kicked on in ultrasonic mode at 100% and interlocked causing alarm. When pumps 2 and 3 placed back into auto pump 1 interlock caused pump 2 to come on causing discharge flow hihi alarm. Placed pump 1 into local off to stop pump. Pump 1 back up mode most likely triggered due to wrong duty rotation. Placed pump 1 back into remote on cleared alarms and placed back into duty 1 with pumps 2 and 3 in auto. Pump 1 was called for as normal operation, and ran normally for multiple cycles. Will continue to monitor in case of sensor issue or PAC issue. | Vaughan Pine Valley Pumping Station | 2026-03-06
WW-WEST | March | Onsite for station check - no new issues reviewed trends and added data into SharePoint. | Vaughan Pine Valley Pumping Station | 2026-03-10
WW-WEST | March | In to Drop Off Oil Storage Skid for Station. | Vaughan Pine Valley Pumping Station | 2026-03-24
WW-WEST | March | In to Complete Scheduled WO. Notified ROC. Placed LITs #2 and 4 in Calibration Mode Independently and Sequentially. Completed Wet Well Inspection and Flushing. Greased Channel Grinder. Inspected and Flushed Hydrostatic LIT Sensor Lines and Heads. Returned to Service. Cleared Associated Interlocks and Alarms. | Vaughan Pine Valley Pumping Station | 2026-03-23
WW-WEST | March | Onsite for station check and housekeeping PM Station check ok - no new issues. Reviewed trends and added data into SharePoint. Swept main room and bathroom. | Vaughan Pine Valley Pumping Station | 2026-03-24
WW-WEST | March | Completed the station check and daily lab work Decanted then emptied the sludge thickening tank Auto batch wasted from clarifier 2 over the weekend: Friday: 48m3 Saturday: 47m3 Sunday 49m3 Everything operating as intended | Schomberg Water Resource Recovery Facility | 2026-03-30
WW-WEST | March | Received alum delivery. Reviewed and signed bill of lading and certificate of analysis. Filled tanks from 0.882m/0.872m to 2.586m/2.592m. Collected weekly compliance samples. Started in-house labs. | Schomberg Water Resource Recovery Facility | 2026-03-31
WW-WEST | March | Completed labs and entered data in ace sheets. Completed station check. No issues found. Set ras P1 to manual on at 50% speed to help ras P2, which is duty 1, meet flow requirements. | Schomberg Water Resource Recovery Facility | 2026-03-31
WW-WEST | March | In to Complete Scheduled WOs. WAS Pump #1 Auto-Wasted 46 m3 Overnight. Lowered and Activated Decant Pump. Completed Sludge Blower Building Room Supply Fan Filter Replacement with No Issues. Completed Filter Inlet TSS Sensor Inspection. Placed Unit in Calibration Mode Locally, Cleaned Probe. No Issues Found. Returned to Service. Decant Complete, Raised and Deactivated Decant Pump. Sludge Transfer Valve Manual Open, Transferred Thickened Sludge. Transfer Valve Returned to Manual Closed. Inspected Alum Dosage Points, Pump Function and Trends. Inspected Sand Filter Function. All OK. Adjusted Clarifier Eff. Alum Dosage Set-point Based On In-House and External Laboratory Results: 20 ?> 23 mg/L. Completed Compressors #1 and 2 Inspections. Tested Low Oil Level Alarms. Confirmed Reception by the ROC. Identified Slow Inlet Leak on Compressor #2 and Condensation Leak on Compressor #1 Air Dryer. Notified Appropriate Staff of Potential Deficiencies. No Other Issues Found. Cleared Associated Alarms. | Schomberg Water Resource Recovery Facility | 2026-03-06
WW-WEST | March | Completed labs and entered data in ace sheet. Completed station check. No issues found. Adjusted aeration alum dosage from 115 mg/l to 110 mg/l to account for high volumes of melt-water. Set RAS P3 in manual on at 60% speed. RAS P2 is running auto speed in duty 1. This will help meet higher RAS flow requirements. Exercised SHT overflow valve. Tested SHT high level float. Inspected PB sump system. Inspected BB sump system. ROC received high level alarms from all three floats. | Schomberg Water Resource Recovery Facility | 2026-03-10
WW-WEST | March | Completed the station check and daily lab work Entered data into SharePoint Decanted the sludge thickening tank Batch wasted 43m3 from clarifier 2 overnight | Schomberg Water Resource Recovery Facility | 2026-03-13
WW-WEST | March | Completed the station check and daily lab work Entered data into SharePoint Was pump 1 wasted 46m3 from clarifier 2 RAS pump 2 kept getting a speed deviation alarm and was running loud Tried some troubleshooting but could not get it running properly, placed it in manual for the night until I can open it up Greased and inspected RAS, WAS and scum pumps Placed RAS pumps 1 and 3 in duty 1 to hit the desired flow rate | Schomberg Water Resource Recovery Facility | 2026-03-12
WW-WEST | March | In to Complete Scheduled WOs. WAS Pump #1 Auto-Wasted 49 m3 Overnight. Lowered and Activated Decant Pump. Pulled and Cleaned Raw Composite Sampler Suction Line. Returned to Service with No Interruption to Sampling Schedule for Regulatory Sampling. Decant Complete, Raised and Deactivated Decant Pump. | Schomberg Water Resource Recovery Facility | 2026-03-03
WW-WEST | March | Supernated STT and released some to SHT. left 1.76 m in thickening tank as holding tank reached high level. Auto wasting wasted 40 m3 yesterday. Completed labs and entered data in ace sheet. Completed station check. No issues found. Cleared rags from RAS pump 2. Set to duty 1 and it seems to work well with no speed deviation alarms. Completed consolidated head works work order. ROC received e-stop alarms. | Schomberg Water Resource Recovery Facility | 2026-03-09
WW-WEST | March | Completed regulatory weekly sampling. Decanted sludge thickening tank and transferred remaining sludge to holding. Completed daily lab and station check no new issues - added data into SharePoint WAS pump wasted 47m3 overnight. Cleaned and verified aeration tank DO probes. | Schomberg Water Resource Recovery Facility | 2026-03-04
WW-WEST | March | Collected weekly compliance samples | Schomberg Water Resource Recovery Facility | 2026-03-11
WW-WEST | March | Completed the station check and daily lab work Entered data into SharePoint Decanted the sludge thickening tank Inspected the aeration blowers | Schomberg Water Resource Recovery Facility | 2026-03-05
WW-WEST | March | On site to check UV bank B, rack 7. Found blown fuse. Could not find cause of blown fuse. Replaced fuse. Was able to reset major fault alarm. Tested bank B. Ok now. | Schomberg Water Resource Recovery Facility | 2026-03-10
WW-WEST | March | Completed the station check and daily lab work Entered data into SharePoint Batch wasted 56m3 from clarifier 2 overnight Everything operating as intended | Schomberg Water Resource Recovery Facility | 2026-03-17
WW-WEST | March | On site for blower 1 oil leak. We will return with seals | Schomberg Water Resource Recovery Facility | 2026-03-23
WW-WEST | March | Began diverting flow from the head works to the lagoon at 9:00am and ended at 11:15am. Diverted 169m3 total We diverted flow to drain the filter inlet channel to replace the filter inlet valves Work wasn?t completed and will be addressed at a later date Completed the station check and daily lab work Entered data into SharePoint Batch wasted 56m3 overnight | Schomberg Water Resource Recovery Facility | 2026-03-19
WW-WEST | March | Investigate hydraulics for valve replacement Will reschedule with operations. | Schomberg Water Resource Recovery Facility | 2026-03-19
WW-WEST | March | Completed the station check and daily lab work Batch wasted 49m3 Tuesday night Hung warning signs around the lagoon and front entrance Cleaned the online DO probes Everything operating as intended | Schomberg Water Resource Recovery Facility | 2026-03-25
WW-WEST | March | Collected weekly compliance samples | Schomberg Water Resource Recovery Facility | 2026-03-25
WW-WEST | March | Pulled apart and cleaned out RAS pump 2, this pump was activating the speed deviation alarm and is making a loud noise when running Cleaned up in the aeration basement and process building | Schomberg Water Resource Recovery Facility | 2026-03-26
WW-WEST | March | Completed the station check and daily lab work Entered data into SharePoint Everything operating as intended Batch wasted 56m3 from clarifier 2 overnight | Schomberg Water Resource Recovery Facility | 2026-03-20
WW-WEST | March | Completed the station check and daily lab work Entered data into SharePoint Overnight the plant batch wasted 40m3 from clarifier 2 Changed the batch wasting window from 16:00-22:00 to 16:00-23:00 Inspected the filter reject pumps Cleaned the tss probe in the aeration tank | Schomberg Water Resource Recovery Facility | 2026-03-16
WW-WEST | March | Completed the station check and daily lab work Entered data into SharePoint Batch wasted 51m3 Friday night, 47m3 Saturday night and 47m3 Sunday night Cleaned the washrooms on site Inspected the lagoon berm | Schomberg Water Resource Recovery Facility | 2026-03-23
WW-WEST | March | Installed new shaft seals(Viton) Sealed flange with silicone Installed back shroud Installed sheaves and aligned with straight edge. Installed belts with Gavin Installed front shroud Filled blower with oil. Complete | Schomberg Water Resource Recovery Facility | 2026-03-24
WW-WEST | March | Returned RAS operation to one pump as average daily flows are back to normal. P3 in duty 2. P2 in duty 2. P1 is duty 3/OOS. | Schomberg Water Resource Recovery Facility | 2026-03-19
WW-WEST | March | Collected weekly compliance samples | Schomberg Water Resource Recovery Facility | 2026-03-18
WW-WEST | March | Completed the station check and daily lab work Decanted the sludge thickening tank Reset aeration blower 1, test ran it and it ran well Cleaned the tss and do probes | Schomberg Water Resource Recovery Facility | 2026-03-11
WW-WEST | March | In to Complete Scheduled WOs. Notified ROC. King Township Staff and Contractor On-site for Water Meter Replacement. WAS Pump #2 Cumulatively Auto-Wasted 104 m3 Over the Span of the Weekend. Placed Supernatant Drain Valve in Manual Open. Rotated WAS Pump Duties. Pump #2 Manual Off, Pump #1 in Auto. Lowered and Activated Decant Pump. Rotated RAS Pump Duties. Pump #3 in Duty #1, Pump #1 in Duty #3, OOS. Returned Supernatant Drain Valve to Manual Closed. Decant Complete, Raised and Deactivated Decant Pump. Sludge Transfer Valve Manual Open, Transferred Thickened Sludge. Transfer Valve Returned to Manual Closed. Identified Locally Outstanding Low Pressure Alarm on Compressor #2. Inspection Rendered No Issues. Notified Appropriate Staff of Potential Deficiency. Transferred Station to Generator Power with No Issues. Acknowledged and Cleared Associated Alarms. Completed JHSC Inspection. Topped Up Generator Room Spill Kit with Sorbent Socks. No Other Issues Found. Transferred Station Back to Utility Power with No Issues. Cleared Associated Alarms. | Schomberg Water Resource Recovery Facility | 2026-03-02
WW-WEST | March | In to Complete Scheduled WO. Notified ROC. Completed Consolidated Aer., Sludge and Vortex Blower Inspections. Topped Up Oil Reservoirs and Replaced Air Filters Where Necessary. All Belts OK. Returned to Service and Cleared Associated Alarms. Created Follow-Up WO Regarding Aer. Blower #1 Oil Leak for Maint. ?> W11740816. | Schomberg Water Resource Recovery Facility | 2026-03-17
WW-WEST | March | Completed daily lab and station check - no new issues. Recorded data into SharePoint. Batch wasted 49m3. Assisted Gavin with work on RAS pump 2. | Schomberg Water Resource Recovery Facility | 2026-03-26
WW-WEST | March | Completed the station check and daily lab work Batch wasted 51m3 overnight Cleaned the DO probes Aeration blower 1 cooling fan faulted and cannot be reset Blower 1 is currently left out of service | Schomberg Water Resource Recovery Facility | 2026-03-18
WW-WEST | March | In to Complete Scheduled WO. Notified ROC. Completed UV System Inspection and Channel Clean Out. Replaced Damaged Sleeve and Tested Unit with No Issues. Returned to Service. | Schomberg Water Resource Recovery Facility | 2026-03-24
WW-WEST | March | Completed the station check and daily lab work Entered data into SharePoint Cleaned the tss probe in the aeration tank There was a very brief power blip which put clarifier 2 and the grit blowers oos, I reset the clarifier but the grit blowers continued to trip Brent S. Came out to site and there was an issue with the PCS, Artour L. Was able to reprogram it and get the issue fixed | Schomberg Water Resource Recovery Facility | 2026-03-27
WW-WEST | March | Completed the station check and daily lab work Entered data into SharePoint Inspected the heat trace on the debris auger Batch wasted 54m3 on Monday night Cleaned the floor in the filter room | Schomberg Water Resource Recovery Facility | 2026-03-24
WW-WEST | March | onsite due to power blip causing VFD failure on pump 1 - reset VFD and pump now back in duty | Schomberg Dr. Kay Pumping Station | 2026-03-31
WW-WEST | March | In to Complete Station Check. Reviewed SCADA and trends. No Issues Found. | Schomberg Dr. Kay Pumping Station | 2026-03-06
WW-WEST | March | Completed station check. No issues found. | Schomberg Dr. Kay Pumping Station | 2026-03-31
WW-WEST | March | In to Complete Scheduled WOs. Notified ROC. Transferred Station to Generator Power with No Issues. Acknowledged Associated Alarms. Reviewed SCADA and Trends. No Issues Found Completed Hi/Lo Temperature Alarm Test. Confirmed Reception by the ROC. Returned to Service. Cleared Associated Alarms. Completed JHSC and Hazardous Materials Inspections with No Issues. Manually Activated Duty #1 Pump Start Set-point. Transferred Station Back to Utility Power with No Issues. Cleared Associated Alarms. | Schomberg Dr. Kay Pumping Station | 2026-03-03
WW-WEST | March | Completed station check. No issues found. | Schomberg Dr. Kay Pumping Station | 2026-03-10
WW-WEST | March | Completed the station check Entered data into SharePoint Everything operating as intended | Schomberg Dr. Kay Pumping Station | 2026-03-13
WW-WEST | March | Allowed access to Hydro One contractors to change hydro meter. Shut off diesel. Shut off main breaker. Meter changed. Restored power to facility. Returned diesel to auto. Cleared alarms. Activated duty 1. | Schomberg Dr. Kay Pumping Station | 2026-03-09
WW-WEST | March | In to Complete Station Check. Reviewed SCADA and Trends. No Issues Found. | Schomberg Dr. Kay Pumping Station | 2026-03-24
WW-WEST | March | Completed the station check Wessuc on site to do a wet well cleaning Disabled the low level lock out Manually pumped down the wet well during the cleaning Enabled the low level lock out when they finished the cleaning Returned the station to normal operation Everything operating as intended | Schomberg Dr. Kay Pumping Station | 2026-03-17
WW-WEST | March | Couldn?t make it to site due to issues at SBSP Did a remote station check and entered data into sharepoint | Schomberg Dr. Kay Pumping Station | 2026-03-27
EAST | March | SYSTEM TESTING - PLEASE IGNORE | Georgina Water Treatment Plant | 2026-03-28
EAST | March | SYSTEM TESTING - PLEASE IGNORE | Georgina Water Treatment Plant | 2026-03-28
EAST | March | Reviewed MIT and daily filter performance on all membrane trains - all passed and within range - recorded data in PWQ sheets. | Georgina Water Treatment Plant | 2026-03-30
EAST | March | On site to conduct manual backwash on GAC 1. Plant off during this time. Lee Ferguson on site for Backflow preventor work on UV cooling systems. 13:50hrs: Received a UV dosage High alarm due to running only one train through the UV system to top influent channel due to GAC 1 Filter to waste line open which draws down the channel. Informed ROC of disregard. Topped up Sodium Hydroxide from 60L to 100L. Completed GAC 1 and filter to waste at 14:30hrs. GAC 1 in service. Equipment out of service: Sludge P3 (leaking volute). Maple Reindeers on site conducting station upgrades on exterior of facility for driveway/gate and GWTP intake works. Alarms to disregard (ROC notified through SCADA review PWQ sheet): Sludge P3 Emergency Stop Alarm, GAC 3, 4 Flow Control Valve Deviation Alarm. | Georgina Water Treatment Plant | 2026-03-30
EAST | March | Informed ROC. Plant Running. Unable to perform calibrations. Informed ROC and left the site | Georgina Water Treatment Plant | 2026-03-30
EAST | March | Placed UV 1 & 2 manual off, and changed membrane trains 5-8 to OFF mode for instrumentation work. | Georgina Water Treatment Plant | 2026-03-30
EAST | March | On site for station check and to collect weekly micro samples (W11705578), Algae samples (W11705308), VOC (W11705280) and in house ATP samples, GLIP samples. Reviewed MIT and daily filter performance on all membrane trains - all passed and within range - recorded data in PWQ sheets. 08:52hrs: Adjusted Clearwell 1 from 1.65mg/l to 1.75mg/l based on multiple CL2 grab residuals. 08:57hrs: Adjusted Clearwell 2 from 1.55mg/l to 1.70mg/l based on multiple CL2 grab residuals. 09:02hrs: Adjusted Post Clearwell from 1.47mg/l to 1.63mg/l based on multiple CL2 grab residuals. 09:30hrs: Adjusted Sutton Total from 1.76mg/l to 1.89mg/l based on multiple CL2 grab residuals. 09:35hrs: Adjusted Keswick Free from 1.46mg/l to 1.56mg/l based on multiple CL2 grab residuals. 09:38hrs: Adjusted Keswick Total from 1.77mg/l to 1.88mg/l based on multiple CL2 grab residuals. 11:25hrs: Collected all raw water samples. Collected Treated samples (Keswick Line) @ 11:35hrs. Cl2 grab residuals: FCL: 1.78mg/l TCL: 2.08mg/l Received Sodium Hydroxide delivery 31 jugs. Received Hypo delivery 1500L. Changed High Lift Duties due to low Chlorine in Contact #2. HL P3 now in duty 1. Turned off fluoride pumps during this change as to not cause a fluoride spike. Informed ROC. Collected Flouride grabs @ 14:25hrs: Keswick grab: 0.69mg/l, Analyzer: 0.70mg/l, Sutton Fluoride grab: 0.68mg/l Analyzer: 0.63mg/l. Equipment out of service: Sludge P3 (leaking volute). Alarms to disregard (ROC notified through SCADA review PWQ sheet): Sludge P3 Emergency Stop Alarm, GAC 3 and 4 Flow Control Valve Deviation Alarm, Chlorine Tank 2 weight alarm | Georgina Water Treatment Plant | 2026-03-31
EAST | March | AT 15:55 activated duty early to run through the night. | Georgina Water Treatment Plant | 2026-03-30
EAST | March | THIS IS A SYSTEM TEST PLEASE IGNORE Testing with iPhone on WIFI Testing revision | Georgina Water Treatment Plant | 2026-03-31
EAST | March | Reviewed MIT and daily filter performance on all membrane trains - all passed and within range - recorded data in PWQ sheets. Rotated air compressor duty to Kaiser. Triggered raw water sample pump duty rotation. Rotated chlorinator 5 into duty for clearwell dosing. | Georgina Water Treatment Plant | 2026-03-31
EAST | March | Test backflow preventers All five passed | Georgina Water Treatment Plant | 2026-03-30
EAST | March | Informed ROC, GWTP Low Lift- onsite to perform annual calibration. Devices were done as below : NIT, AITs, pH, chlorine gas detector, TIT. Used calibration mode. Total chlorine analyzers were calibrated using service water and by taking multiple grab samples. Adjusted analyzers accordingly. G-1.75 mg/l, A- 1.75 mg/l Total chlorine analyzers as left at 0.00 mg/l using process water. Put everything back in service. All the related alarms were cleared. No issues. Informed ROC, armed the building and left the site. | Georgina Water Treatment Plant | 2026-03-02
EAST | March | SYSTEM TESTING PLEASE IGNORE Testing logentry without wifi Revision 1 | Georgina Water Treatment Plant | 2026-03-31
EAST | March | Test backflow preventers B1 both passed | Georgina Water Treatment Plant | 2026-03-31
EAST | March | On site for station check and to collect weekly micro samples (W11637418), Algae samples (W11637619), VOC (W11637148) and in house ATP samples, GLIP samples. Reviewed MIT and daily filter performance on all membrane trains - all passed and within range - recorded data in PWQ sheets. Placed Train #8 into ACID R-Clean. Data entered in PWQ sheets. Placed Low Lift P3 back into service. Instrumentation on site for calibrations. 10:15hrs: Collected all raw water samples. Collected Treated samples (Keswick Line) @ 10:35hrs. Cl2 grab residuals: FCL: 1.75mg/l FCL Analyzer: 1.71mg/l TCL: 1.97mg/l TCL Analyzer: 1.95mg/l Conducted Treated Header Cl2 Maintenance, verifications in station check PWQ sheet. Conducted Chlorine System Inspection - no issues. Equipment out of service: Sludge P3 (leaking volute). Alarms to disregard (ROC notified through SCADA review PWQ sheet): Sludge P3 Emergency Stop Alarm, GAC 3 and 4 Flow Control Valve Deviation Alarm, Chlorine Tank 2 weight alarm | Georgina Water Treatment Plant | 2026-03-04
EAST | March | Reviewed MIT and daily filter performance on all membrane trains - all passed and within range - recorded data in PWQ sheets. GAC 4 Offline for sample media collection today. Activated plant @ 12:55hrs 13:14hrs: Began filling Backwash Clearwell. Placed HLP2 off for contractors to have a look. Placed back online after inspection complete. Informed ROC of all work completed. Placed Trains 5 to 8 M-Clean schedule back on after SCADA upgrades today. Filled Backwash Clearwell Tank to refill GAC 4 this week. Equipment out of service: Sludge P3 (leaking volute). Alarms to disregard (ROC notified through SCADA review PWQ sheet): Sludge P3 Emergency Stop Alarm, GAC 3 and 4 Flow Control Valve Deviation Alarm, Chlorine Tank 2 weight alarm | Georgina Water Treatment Plant | 2026-03-10
EAST | March | On site for weekly sampling, station check, and lab sampling. Entered data into PWQ Sheets. Refilling GAC4 using backwash system. Notified ROC, expecting turbidity alarms. 10:25 open backwash clearwell fill valve. 10:29 close backwash clearwell fill valve. 10:30 open back wash drain valve and backwash inlet valve. 10:33 open backwash pump 2 recirculating valve. 10:35 manual start backwash pump 2. 10:36 manual open backwash pump 2 FCV to 20%. 10:49 Increase backwash pump 2 FCV open setpoint to 25% 11:08 Close GAC4 backwash drain valve. 11:18 Close backwash FCV, manual stop backwash pump 2, close recirculating valve and backwash inlet valve. 11:33 Manual open GAC4 inlet valve, and GAC4 filter to waste valve. 11:55 Manual close GAC4 filter to waste valve, place effluent valve back in auto. GAC4 back in service. 13:30-14:30 Completed chlorine analyzer maintenance on Wash water and to the lake analyzers. | Georgina Water Treatment Plant | 2026-03-11
EAST | March | On site to replace network switch with network analyst Kevin wen, Aaron Magsakay and John Dimarco. Hub 1 and GWTP local server lost comms due to this. At GWTP, no trends between 9:25 AM and 10:20 AM Powered off the old switch and plugged in the ports to new switch. Checked the connections to all PAC and Servers once the replacement is completed Checked local OIT at GWTP - All ok | Georgina Water Treatment Plant | 2026-03-10
EAST | March | On site for MIT review, station check, lab analysis. Collected weekly micro samples (W11656959), GLIP samples. Data recorded in PWQ sheet. Reviewed MIT and daily filter performance on all trains - all passed. Reviewed SCADA trends and UV trends. 10:05hrs: Collected all raw water samples. Collected Treated samples (Keswick Line) @ 09:30hrs. Cl2 grab residuals: FCL: 1.55mg/l FCL Analyzer: 1.55mg/l TCL: 1.86mg/l TCL Analyzer: 1.79mg/l 10:10hrs: Train #1 shutdown on Uncommanded stop. Checked Train, did not see any issues with the pump or outstanding VFD alarms. Placed Train back into service to monitor. Refilling of GAC4 to place back into service. GAC 4 back online. Turned plant off @11:05hrs for instrumentation to conduct Calibrations on High Lift Keswick and Sutton Header including Fluoride probes. 14:25hrs: Verified Keswick Fluoride Analyzer after calibration: Grab: 0.73mg/l , Analyzer 0.70mg/l. Equipment out of service: Sludge P3 (leaking volute). Maple Reindeers on site conducting station upgrades on exterior of facility. Alarms to disregard (ROC notified through SCADA review PWQ sheet): Sludge P3 Emergency Stop Alarm, GAC 3, 4 Flow Control Valve Deviation Alarm. | Georgina Water Treatment Plant | 2026-03-11
EAST | March | Restarted the local sever for GWTPL PAC removal, trending is posted at the Hub server. Plant is off | Georgina Water Treatment Plant | 2026-03-12
EAST | March | On site for station check and lab analysis. Reviewed MIT and daily filter performance on all membrane trains - all passed and within range - recorded data in PWQ sheets. Reviewed SCADA, completed station check and lab analysis. Station OK. | Georgina Water Treatment Plant | 2026-03-13
EAST | March | Reviewed MIT and daily filter performance on all membrane trains - all passed and within range - recorded data in PWQ sheets. UV's in manual off for UV maintenance, cleaning and calibration. Informed ROC of work. Powered down UV's during work. Instrumentation on site for Annual calibrations. 13:30hrs: Swapped out dehumidifier in UVT Analyzer. UV alarms cleared after swap. 14:00hrs: Started up Duty #1 to monitor. 14:45hrs: Low Lift building flood alarm came in on SCADA. Went to investigate. Sump was high and high switch alarm was going off, was able to troubleshoot issue with floats over the phone with Dan B and managed to get P1 working. P2 is out of service in local off. Equipment out of service: Sludge P3 (leaking volute). Alarms to disregard (ROC notified through SCADA review PWQ sheet): Sludge P3 Emergency Stop Alarm, GAC 3 and 4 Flow Control Valve Deviation Alarm | Georgina Water Treatment Plant | 2026-03-12
EAST | March | Onsite for annual calibrations Informed ROC and operations Plant offline Worked on train 6-7 FITs and NITs as well as train 7,6,5 and 1 MIT PITs Operations started plant Informed ROC Left site No issues | Georgina Water Treatment Plant | 2026-03-05
EAST | March | Reviewed MIT and daily filter performance on all membrane trains - all passed and within range - recorded data in PWQ sheets. PCS on site in low lift for PAC removal. Placed plant off for PAC panel replacement. Instrumentation on site conducting calibrations on Trains 6,7. Placed Trains off during this time. Placed Train 8 back online from ACID R-CLEAN yesterday. MIT conducted. Passed. Topped up Sodium Hydroxide Tanks from 50L to 102L. Low Lift Cl2 Analyzer maintenance, Treated Header Turbidity Maintenance and greasing of low lift sample pumps. Received 3 Full Chlorine Tonner's, sent back 3 empty to Brenntag. 14:05hrs: Started up plant for PCS to ensure plant functioning correctly after server work. 14:13hrs: Received a UV lockout on UV#1 critical fault, Lo Water flow alarm. Was able to switch to UV2 and cleared alarms on UV1. 14:26hrs: UV2 shutdown on critical fault, Lo water flow alarm. Deactivated the duty to investigate the issue. 14:45hrs: Restarted the plant to investigate the issue. Received a UV2 Critical fault alarm, low water flow alarm. Noticed that when the UV system is ready, the Trains are not starting up and providing any flow through the UV's causing the UV's to fault. Informed PCS Chris Scott of the issue as there is an interlock on the trains stating PAC-3 communication failed. 15:05hrs: Reset both UV's by powering them down and back up again. Chris Scott onsite to troubleshoot why trains are not starting when UV is ready. PCS looking into it. 16:14hrs: Activated Duty to run plant as per PCS request. Plant is now running with no issues. | Georgina Water Treatment Plant | 2026-03-05
EAST | March | Informed ROC and operations. Onsite to perform annual calibration. Used calibration mode. Devices were done as below: Train 8 (NIT, PITs, FIT). Highlift LITs, Sutton and Keswick line FITs. Troubleshoot High lift AIT, found ingress of water at electric connections. Cleaned it and put it back in Service. Put everything back in service All the related alarms were cleared. No issues. Informed ROC and operations and left the site. | Georgina Water Treatment Plant | 2026-03-04
EAST | March | 14:43 Initiated train 8 MIT. It passed with 1.95kpa/1.90kpa hi/low pressure decay. It is in standby. | Georgina Water Treatment Plant | 2026-03-09
EAST | March | Onsite to respond to chlorinators 5 and 6 vacuum hi hi alarm Before arriving to site asked ROC to deactivate duty. CC lo alarm active ~ CC1 analyzer reading 0.8 mg/l. Placed chlorine ejector solenoid valves in manual and tested both ejectors, no issues Tested chlorinators 5 and 6 in manual vacuum increased to over -500 mg Found chlorine line isolation valve closed. Opened valve and slowly pressurized chlorine gas line to chlorinators CC tanks residual further dropped down to 0.09 mg/l during troubleshooting with system water./ Collected grab on CC1 ~ 0.55 mg/l. Tank 2 analyzer was 1.25 mg/l, grabs was 1.22 mg/l Opened solenoid valve in manual and opened chlorinator 5 to push some chlorine solation into tanks. Ran recirculation pump in manual to good mixing in the CC. Activated duty monitored plant until residual from CC tanks recovered, notified ROC before leaving site | Georgina Water Treatment Plant | 2026-03-04
EAST | March | Onsite for station check and lab analysis, entered data into PWQ sheets. Reviewed MIT and daily filter performance on all membrane trains - all passed and within range - recorded data in PWQ sheets. *Also reviewed monthly filter performance on all membrane trains. No issues. 11:00hrs: Zero'd and calibrated High Lift Free Chlorine CL17 Analyzer. Adjusted Reading from 0.86mg/l to 1.64mg/l based on CL2 grab residuals. WO made for this analyzer as it continues to drift. Conducted JHSC inspection in the low lift. 13:50hrs: Adjusted Keswick Fluoride Analyzer from 0.85mg/l to 0.76mg/l using the offset based on in house lab analysis. 14:05hrs: Adjusted Sutton Fluoride Analyzer from 0.90mg/l to 0.77mg/l using the offset based on in house lab analysis. | Georgina Water Treatment Plant | 2026-03-02
EAST | March | Rebuilt 200ppd regulator. Instrumentation on site for calibrations. Responded to low lift flood alarm. Float was stuck against wall, was able to move float and allow P1 to run. P2 OOS, WO initiated to maintenance for replacement of pump. Equipment out of service: Sludge P3 (leaking volute). Alarms to disregard (ROC notified through SCADA review PWQ sheet): Sludge P3 Emergency Stop Alarm, GAC 3 and 4 Flow Control Valve Deviation Alarm, Chlorine Tank 2 weight alarm | Georgina Water Treatment Plant | 2026-03-13
EAST | March | Onsite for annual calibrations Informed ROC and operations Plant offline Worked on train 2-5 FITs and NITs as well as GAC 1 effluent Flow Operations started plant Informed ROC Left site No issues | Georgina Water Treatment Plant | 2026-03-06
EAST | March | Verified low lift sump pump 2 is seized. Gathered info required for replacement. | Georgina Water Treatment Plant | 2026-03-02
EAST | March | On site for work orders. Changed SBS pump duty change to All Stop, and triggered duty rotation. UV system cleaning, UV reactors sensors calibration, UV inventory assessment. | Georgina Water Treatment Plant | 2026-03-12
EAST | March | Inspected sump pump #2 after reports of it not working, removed unit and confirmed it does spin and pumps water, I believe there may be an underlying issue with the floats intermittently working. Will require Electrician on-site. | Georgina Water Treatment Plant | 2026-03-12
EAST | March | Onsite to continue with annual calibrations Informed ROC and operations Plant off line Calibrated plant chlorine gas detectors and sulphonator detectors Cleared associated alarms Informed ROC and operations Left site | Georgina Water Treatment Plant | 2026-03-12
EAST | March | Received a call from the ROC at 16:31 for a Train 5 shutdown alarm. Attended SCADA to investigate. Found Train 5 turbidity erratic. Working with OIC Joe Mazza, Chris Scott (PCS) was troubleshooting UV programming, which caused unplanned UV duty rotation. The fluctuation of the low lift pumps starting on and shutting off would cause air entrainment in the membranes and result in false turbidity spikes. Train 5 left OFF for the night until an on site operator can investigate. Received a UV start/stop sequence fault at 17:08, resulting from troubleshooting. Reset UV2 alarms and monitored. Station back in service. | Georgina Water Treatment Plant | 2026-03-05
EAST | March | While on site completed multiple grab samples on the hi lift analyzer. This was done after instrumentation was here to validate that the analyzer was reading correctly. Time: 14:15 Hi Lift Grab (mg/l) Analyzer (mg/l) Free: 1.56 1.61 No issues with analyzer after verification. | Georgina Water Treatment Plant | 2026-03-04
EAST | March | Fluoride pumps manual off. | Georgina Water Treatment Plant | 2026-03-06
EAST | March | Reviewed monthly turbidity performance data - all within spec. | Georgina Water Treatment Plant | 2026-03-02
EAST | March | Move water pumps inside | Georgina Water Treatment Plant | 2026-03-05
EAST | March | Onsite to continue with annual calibrations Informed ROC and operations Plant is off line Calibrated: Chemical room LITs, GAC LITs, CIP FITs, waste water LITs, sedimentation LITs, Backpulse FIT, channel LITs Informed Operations and ROC No issues Left site | Georgina Water Treatment Plant | 2026-03-13
EAST | March | Attended site to address Train 3 turbidity fault - informed by RO Adam Button. CMU5 W11714562. Removed cuvette and flushed entrained bubbles that were adhered to the side of the cuvette. Placed Train 3 back in service. | Georgina Water Treatment Plant | 2026-03-06
EAST | March | Onsite for annual calibrations Informed ROC Coordinated calibration with operations. Plant offline Instruments calibrated: Train 1 NIT and FIT GAC 2-4 FITs Low Lift FIT High lift NITs Informed operations. Plant available to go online Informed ROC No issues Left site | Georgina Water Treatment Plant | 2026-03-09
EAST | March | Logged in for Contact Tank 1 lolo alarm which caused GAC's to stop flowing. Deactivated duty to allow UV's to shut down, received UV Critical Fault alarm on shutdown. Was able to clear alarm and restart duty and plant. Switched to High Lift P1 to bring up residual in Clearwell. | Georgina Water Treatment Plant | 2026-03-14
EAST | March | ROC called @16:15 for UV intensity low alarm. Came in on plant startup when UV first saw flow. Immediately recovered to normal levels | Georgina Water Treatment Plant | 2026-03-23
EAST | March | Reviewed MIT and daily filter performance on all trains - all passed. Also on site for monthly meeting and OJT training. At 10:16 turned trains 1, 4 and 8 off for instrumentation to complete annual calibrations. | Georgina Water Treatment Plant | 2026-03-27
EAST | March | @14:00 ROC called for High lift tanks 1 and 2 low alarms - levels are 4.59 / 4.56 m. Alarms were a result from the GAC 2 Lolo alarms that came in overnight - The GAC 2 LIT is not working properly, causing GAC 2 to be interlocked. Will need instrumentation to investigate tomorrow. 148 L/s is going to the Clearwell, while 180 L/s is being pumped by high lifts. With GAC 2 still in service, but interlocked, the other GACs could not increase flow to compensate. Placed GAC 2 OOS on the GAC setpoints filtration page, allowing the other GACs to increase flow. There is now 206 L/s GAC flow going to the Clearwell. GAC2 OOS. Clearwell levels will now recover slowly. Informed ROC to monitor | Georgina Water Treatment Plant | 2026-03-22
EAST | March | eviewed MIT and daily filter performance on all trains - all passed. 09:05hrs: Conducted manual backwash on GAC 3, informed ROC of work. Instrumentation on site for rebuild and calibration of Mussel Control Chlorine system. Plant off during this time. Chlorinator 7 and 8. Aeration blower maintenance. Sludge Pump inspection completed. Flood alarm testing in plant completed, no issues. High Lift Pump inspection completed. OJT on R and M-clean with Jackie S. Conducted M-Clean check on Train #7. Hypo residual was 100ppm, neutralization was 0ppm. No issues with M-Clean process. 13:25hrs: Activated plant for instrumentation to calibrate Chlorinator's 7 and 8. Left duty active. Equipment out of service: Sludge P3 (leaking volute). Maple Reindeers on site conducting station upgrades on exterior of facility. Alarms to disregard (ROC notified through SCADA review PWQ sheet): Sludge P3 Emergency Stop Alarm, GAC 3, 4 Flow Control Valve Deviation Alarm. | Georgina Water Treatment Plant | 2026-03-17
EAST | March | Onsite to continue annual calibrations Informed ROC and operations Completed high lift pumps 1, 2 and 4 PITs Informed ROC and operations Completed Left site No issues | Georgina Water Treatment Plant | 2026-03-19
EAST | March | Onsite to continue with annual calibrations Informed ROC and operations Plant offline Completed GAC NITs, Backwash LIT and Filter NIT Cleared associated alarms Informed ROC and operations Left site | Georgina Water Treatment Plant | 2026-03-25
EAST | March | Reviewed MIT and daily filter performance on all membrane trains - all passed and within range - recorded data in PWQ sheets. Conducted station check and lab analysis. Readings in PWQ sheet. Placed Train 7 back on line. Initiated MIT. Train 7 had MIT failure over the weekend. Re-trying MIT test. MIT test showed increased pressure decay (6.5kpa) on low pressure side. Investigated train and found significant leak on Cassette G. WO issued to further repair. Will keep Train 7 offline. Placed GAC 2 back into service, LIT issues over the weekend. Trend show LIT back online. Instrumentation on site and investigated the LIT. No further issues at this point. Will monitor. Changed Duty on Air compressors. BOGE now Duty 1. Changed Duty on Low Lift sample pumps: P2 from D1 to D3 and P1 to D1. Reviewed MIT and daily filter performance on all trains - all passed. Equipment out of service: Sludge P3 (leaking volute). Maple Reindeers on site conducting station upgrades on exterior of facility. Alarms to disregard (ROC notified through SCADA review PWQ sheet): Sludge P3 Emergency Stop Alarm, GAC 3, 4 Flow Control Valve Deviation Alarm. | Georgina Water Treatment Plant | 2026-03-23
EAST | March | On site for station check, lab analysis. Data recorded in PWQ sheet. Placed plant to offline by placing UV's to manual and placed Sutton PRV valves into local and closed valves in basement for Trial Isolation of valve work to be completed to fix broken gear box in Valve chamber that feeds Keswick to Sutton. Completed Maple Reindeers GWTP site online orientation. Reviewed MIT and daily filter performance on all trains - all passed. 10:30hrs: Purged Clearwell Chlorinators 5 and 6 for instrumentation to rebuild chlorinators. 13:00hrs: Instrumentation conducted Chlorinator calibrations, require operational assistance to open and close Post chlorination solenoids during calibrations. 14:00hrs: Activated duty to run plant and ensure Sutton PRVs working as intended and GWTP Chlorinators working. 14:00hrs: There is an outstanding High Alarm on Contact Tank 1 due to the Chlorinator calibrations. Residual will decrease as plant is running. Reviewed SCADA trends and UV trends. Equipment out of service: Sludge P3 (leaking volute). Maple Reindeers on site conducting station upgrades on exterior of facility. Alarms to disregard (ROC notified through SCADA review PWQ sheet): Sludge P3 Emergency Stop Alarm, GAC 3, 4 Flow Control Valve Deviation Alarm. | Georgina Water Treatment Plant | 2026-03-16
EAST | March | Troubleshoot MIT high pressure side on train #6 - it has been high (8.12 kpa last nights MIT) Manually added pressure to train #6 using MIT SV2 69kpa. Pressurized high pressure side of train only. Once pressurized, isolated all the cassettes, to test if we are still losing pressure with only the header / valves. Pressure is still dropping, indicating that the backpulse or permeate valve are passing. Reopened cassettes and purged air from train @11:15. Left train in OFF position for now Deactivated duty @13:30 to have the plant quiet during train #6 testing Pressurized train #6 again @13:31 and inspected train on the valve side. Observed a drip leak coming from the permeate valve. Upon closer inspection it is leaking and hissing air while pressurized. Purged train @13:53. Placed valves back to auto. Created W11756506 for maintenance to address the valve. The train can still be ran Placed train to ON @14:31 - it?s back in standby Activated system duty again @14:34 | Georgina Water Treatment Plant | 2026-03-24
EAST | March | On site to complete comprehensive housekeeping. Deactivating plant at 13:30. Troubleshooting train 6 on hi MIT results. Train 6 had an issue with a permeate valve passing which is contributing to the hi MIT results. Work order has been created. | Georgina Water Treatment Plant | 2026-03-24
EAST | March | Activated both the Sutton and Keswick duties at 15:47. Will monitor off site. | Georgina Water Treatment Plant | 2026-03-25
EAST | March | Test backflow preventers All 4 passed | Georgina Water Treatment Plant | 2026-03-25
EAST | March | Reviewed MIT and daily filter performance on all trains - all passed. At 11:10 put train 4 back on line to complete an MIT that is currently outstanding. Train 4 MIT passed. At 11:50 activated duty for both Sutton and Keswick due to instrumentation finishing their work early. Time: 12:45 Hi Lift Grab (mg/l) Analyzer (mg/l) Free: 1.39 1.42 Time: 12:52 Keswick Grab (mg/l) Analyzer (mg/l) Free: 1.45 1.47 Total: 1.69 1.69 Time: 12:55 Sutton Grab (mg/l) Analyzer (mg/l) Free: 1.41 1.41 Total: 1.71 1.68 Verified analyzers on site and completed station check. Switched duty 1 hi lift pumps from pump 2 to pump 3 to bring up the contact tank 2 residual. Checked station and trends. Entered data into the PWQ sheet. | Georgina Water Treatment Plant | 2026-03-20
EAST | March | Instrumentation on site for Train 1, 4, 8 LIT calibration. Placed trains offline for calibrations. Conducted on site OJT for Tonner Change with Travis W, Jackie S, Patrick F, Dan Z. Equipment out of service: Sludge P3 (leaking volute). Maple Reindeers on site conducting station upgrades on exterior of facility for driveway/gate and GWTP intake works. Alarms to disregard (ROC notified through SCADA review PWQ sheet): Sludge P3 Emergency Stop Alarm, GAC 3, 4 Flow Control Valve Deviation Alarm. | Georgina Water Treatment Plant | 2026-03-27
EAST | March | On site for station check and lab analysis. Verified Keswick header, Sutton header, and CT&CW chlorine analyzers. Entered data into PWQ Sheets. Adjusted free chlorine analyzer for post clear well after three grab samples. Sample at 10:46 - Free grab: 1.71 mg/L Analyzer: 1.59 mg/L Adjusted free chlorine analyzer for contact tank 2 after three grab samples. Sample at 11:05 - Free grab: 2.74 mg/L Analyzer: 2.55 mg/L | Georgina Water Treatment Plant | 2026-03-09
EAST | March | On site for work orders. Completed the following work orders: Clear well drain pump maintenance and inspection, placed pump manual off to inspect. Clear well drain valves exercise. GAC4 media sampling. 12:55 Chlorine gas leak detector test, Notified ROC of alarm test. Chlorine gas scrubber check. Permeate/BP pumps inspections. Wastewater transfer pump inspection and duty change. 13:45 Manual closed GAC4 filter to waste valve, and manual closed backwash drain valve. 13:47 Manual open GAC backwash tank fill valve. | Georgina Water Treatment Plant | 2026-03-10
EAST | March | Onsite for annual calibrations Coordinated calibration with operations. Plant offline Instruments calibrated: High Lift AIT, Keswick and Sutton line free AIT Keswick Fluoride AIT UVT AIT Informed operations. Plant available to go online No issues Left site | Georgina Water Treatment Plant | 2026-03-11
EAST | March | On site to investigate scada position feedback error for GAC4 effluent valve. Found analog output from actuator zero out of adjustment. Found fully closed output at 4.7mA. Adjusted output to 4mA when valve fully closed. Reading 0% on scada now. | Georgina Water Treatment Plant | 2026-03-02
EAST | March | Train #1 was offline for the weekend - Had a low performance alarm come in (99.18%) at midnight on March 8, 2026. The low alarm is set to 99.20%. Monthly performance at 99.92%, well within the objectives. Train 1 placed online. Placed Train 1 back into service and conducted MIT. Reviewed MIT and daily filter performance on all membrane trains - all passed and within range - recorded data in PWQ sheets. Instrumentation conducting calibrations on Train #1, placed Train to off. Changed duty on Air compressors: BOGE in D1, Kaiser to Standby. Low Lift drainage pump #1 had an overload alarm from the weekend. Checked the VFD MCC and was able to reset the fault (Fault code 25). Will continue to monitor, if it comes in again, will send WO to electrical. Placed Pump 1 to D1 and activated duty. No issues/faults came back in. GAC 4 Offline for sample media collection tomorrow. Drained GAC 4 through the effluent valve and then to filter to waste to empty for tomorrow's sample collection. ROC informed. Opened backwash drain valve. GAC 4 empty at 13:50hrs. Turbidimeter in faulted state due to no flow. Changed duty setpoint on Raw water sample pumps: P2 was running in D1, placed it to D3, P3 to D1, P1 to D2. Disabled M-Cleans for Trains 5 to 8 for tomorrow. 14:50hrs: Placed Train # 1 back online Equipment out of service: Sludge P3 (leaking volute). GAC 4 offline for the night. Alarms to disregard (ROC notified through SCADA review PWQ sheet): Sludge P3 Emergency Stop Alarm, GAC 3 and 4 Flow Control Valve Deviation Alarm, Chlorine Tank 2 weight alarm | Georgina Water Treatment Plant | 2026-03-09
EAST | March | Reviewed MIT and daily filter performance on all membrane trains - all passed and within range - recorded data in PWQ sheets. Placed Train #5 back online due to turbidity spike yesterday. MIT initiated and recorded in PWQ sheet. Will monitor on next start up. Instrumentation working on Trains 4 and 5 calibrations. Placed to off. Conducted manual backwash on GAC4. Hoist inspection in low lift. Equipment out of service: Sludge P3 (leaking volute). Alarms to disregard (ROC notified through SCADA review PWQ sheet): Sludge P3 Emergency Stop Alarm, GAC 3 and 4 Flow Control Valve Deviation Alarm, Chlorine Tank 2 weight alarm | Georgina Water Treatment Plant | 2026-03-06
EAST | March | Reviewed MIT and daily filter performance on all membrane trains - all passed and within range - recorded data in PWQ sheets. Conducted Turbidimeter TU5400 SC Analyzer maintenance and calibration on Trains 1 to 8 Permeate. Conducted Diesel generator test run. Disabled M-Cleans on Train 7 and 8. Informed ROC of the work. Diesel Generator Run Monthly Test: Start Runtime: 10:35hrs (Run hrs: 515.92hrs) Fuel Start: 1.01m Stop Runtime: 11:45hrs (Run hrs: 517.18hrs ) Fuel Stop: 0.97m Generator Performance Data recorded below: Battery Cell Levels: OK Battery Terminals/Cables: Ok Oil and Coolant: Ok Amps: 300amps Volts: 600 Hertz: 60 RPM: 2000 Oil Pressure: 100psi Water temp: 170F Oil temp: 190 Ran plant during test run under load. No issues during test run. Re-enabled M-Cleans after generator run. JHSC Inspection completed. Visual inspection of chemical system. No leaks observed. Train 8 to Chemical Injection via Recirculation for R-Clean Hypo tomorrow. Chemical pump system inspections completed. | Georgina Water Treatment Plant | 2026-03-03
EAST | March | On site to assist with station check and lab analysis. No issues on site. | Georgina Water Treatment Plant | 2026-03-23
EAST | March | Onsite to perform annual maintenance/Rebuild chlorinators #7 and #8. Informed ROC. Joe isolated gas cylinders and purged the lines. We rebuilt both the chlorinators. performed vacuum test. No leak found. Performed gas calibration and Performed verification and Put both chlorinators back in service. No issues. Operations put the plant in service during calibration. All the related alarms were cleared. No issues. Informed ROC and operations and left the site. | Georgina Water Treatment Plant | 2026-03-17
EAST | March | Onsite to perform annual maintenance/Rebuild chlorinators #5 and #6. Informed ROC and Joe isolated gas cylinders and purged the lines. We rebuilt both the chlorinators. performed vacuum test. No leak found. Performed gas calibration and Performed verification and Put both chlorinators back in service. No issues. Operations put the plant in service. All the related alarms were cleared. No issues. Informed ROC and operations and left the site. | Georgina Water Treatment Plant | 2026-03-16
EAST | March | Reviewed MIT and daily filter performance on membrane trains - passed and within range - recorded data in PWQ sheets. Train #7 offline due to High MIT on Low Pressure side. Will be conducted repairs on low pressure cassette G today. Conducted repairs, replaced O rings on end cap of Cassette G. Conducted MIT test. MIT test passed. Placed Train 7 back online. Conducted Train 6 troubleshooting due to higher than normal MIT High Pressure decay. Found an air leak at the Permeate valve. WO issued. Train 6 back to online. Tested two way radio's on site. No issues. Equipment out of service: Sludge P3 (leaking volute). Alarms to disregard (ROC notified through SCADA review PWQ sheet): Sludge P3 Emergency Stop Alarm, GAC 3 and 4 Flow Control Valve Deviation Alarm | Georgina Water Treatment Plant | 2026-03-24
EAST | March | On site for station check, lab analysis, and weekly sampling (W11672853) Reviewed MIT and daily filter performance on all membrane trains - all passed and within range - recorded data in PWQ sheets. Manual start clearwell recirculation pump. Reviewed SCADA trends. 10:24 Activate Keswick system duty 11:41 Took TW and raw water samples. 14:39 Call from ROC regarding GWTP Comm alarms caused UV start/stop sequence fault alarms. Deactivated Keswick system duty. 14:52 Unable to clear alarms. Notified ROC and Called Chris Scott, on-call PCS, for assistance. 15:05 Alarms cleared. | Georgina Water Treatment Plant | 2026-03-18
EAST | March | On site to repair crane control cable. | Georgina Water Treatment Plant | 2026-03-06
EAST | March | On site to complete following work orders: W11646352 Air Dryer Check. W11648000 Compressed Air System Inspection. W11646363 Air Compressor Maintenance. W11702020 GAC Sampling W11652127 MIT Daily Filter Performance Review Reviewed MIT and daily filter performance on all trains - all passed. At 09:02 duty for the system was shut down in anticipation for network having work done on it. At 12:53 activated duty. GAC 4 has been sampled with no issues. No issues with work orders being completed.. | Georgina Water Treatment Plant | 2026-03-10
EAST | March | On site to complete station check. Completing work order of low lift pump inspection. No issues with work order. Reviewed MIT and daily filter performance on all trains - all passed. Comm alarm caused UVs to interlock received call from ROC at 14:41. Deactivated duty at 14:42. On going comm fail at the UVs causing them to be interlocked. Will be calling on call PCS Chris Scott to see if the issue can be resolved. | Georgina Water Treatment Plant | 2026-03-18
EAST | March | Onsite to perform annual calibration. Informed ROC and operations. Plant offline. Devices were done as below : Backwash PITs, High lift Disch2 PIT, Utility PIT, Gen LIT, back pulse LITs. Put everything back in service. All the related alarms were cleared. No issues. Informed ROC, left the site. | Georgina Water Treatment Plant | 2026-03-23
EAST | March | On site for station check and lab analysis. Reviewed MIT and daily filter performance on all membrane trains - all passed and within range - recorded data in PWQ sheets. Changed duty from BOGE air compressor to Kaiser air compressor. Triggered duty rotation for raw sample pumps. | Georgina Water Treatment Plant | 2026-03-16
EAST | March | On site for MIT review, station check, lab analysis. Collected weekly micro samples (W11690826), GLIP samples. Data recorded in PWQ sheet. Reviewed MIT and daily filter performance on all trains - all passed. 09:35hrs: Adjusted Contact Tank 2 Cl2 Analyzer from 1.68mg/l to 1.53mg/l based on multiple CL2 grab residuals. 09:38hrs: Adjusted Contact Tank 1 Cl2 Analyzer from 1.68mg/l to 1.55mg/l based on multiple CL2 grab residuals. 10:55hrs: Collected all raw water samples. Collected Treated samples (Keswick Line) @ 11:10hrs. Cl2 grab residuals: FCL: 1.61mg/l TCL: 1.95mg/l 11:25hrs: Adjusted Keswick Fluoride reading from 0.77mg/l to 0.72mg/l based on in house lab analysis. 12:30hrs: Instrumentation on site for annual calibrations on GAC Turbidimeters, refer to instrumentation e-log entry. Sedimentation and Outfall to lake Cl2 Analyzer maintenance completed. Equipment out of service: Sludge P3 (leaking volute). Maple Reindeers on site conducting station upgrades on exterior of facility. Alarms to disregard (ROC notified through SCADA review PWQ sheet): Sludge P3 Emergency Stop Alarm, GAC 3, 4 Flow Control Valve Deviation Alarm. | Georgina Water Treatment Plant | 2026-03-25
EAST | March | ROC called regarding UV comm alarms and UV start/stop sequence fault alarms. Alarms occurred at 05:57. UV had been running for about 1 hour when the alarms came in Duty is active - Controlling ET is at 48% Cleared alarms - UV1 started. Same issue occurred yesterday afternoon. Will get PCs involved if the alarms come in again Will monitor | Georgina Water Treatment Plant | 2026-03-19
EAST | March | Reviewed MIT and daily filter performance on all trains - all passed. Also on site to complete comprehensive housekeeping work orders. At 11:38 transmembrane pressure alarm came in on train 5 was able to clear it with no issues. Put all high lift pumps in manual off for instrumentation at 13:07. Completed a vial cleaning and replacement on GAC2 due to NTU not dropping below 0.199. Did all this between 13:30 and 13:50. At 14:12 put the hi lift pumps back to auto after instrumentation finished their work. No issues with work orders on site. | Georgina Water Treatment Plant | 2026-03-19
EAST | March | Onsite for annual calibrations Informed ROC and ops Plant offline Calibrated HLP PITs Informed ROC and ops Left site | Georgina Water Treatment Plant | 2026-03-20
EAST | March | Train #7 had shutdown overnight on MIT low pressure decay failed alarm. It failed at a 7.66 kpa. Cleared alarms and initiated another MIT on train #7 @11:26. @11:27 - Activated duty 1 Low pressure passed - 5.19 kpa decay | Georgina Water Treatment Plant | 2026-03-21
EAST | March | On site to help with getting site ready for tours tomorrow. Instrumentation currently on site to complete annual calibrations. | Georgina Water Treatment Plant | 2026-03-25
EAST | March | Onsite to continue with annual calibrations Informed ROC and operations Plant offline Completed Train # 2,3,5.6,7,8 LITs Cleared associated alarms Informed ROC and operations Left site | Georgina Water Treatment Plant | 2026-03-26
EAST | March | @11:08 - Activated duty 1 | Georgina Water Treatment Plant | 2026-03-22
EAST | March | Started Duty 1 for Keswick at 07:45. Will monitor off site. | Georgina Water Treatment Plant | 2026-03-16
EAST | March | On site for station check and lab analysis. Verified basement chlorine analyzers. Adjusted Post clearwell free chlorine analyzer after three grab samples: Grab: 1.66 mg/L Analyzer: 1.93 mg/L Completed the following work orders: Chlorine analyzer maintenance - Permeate and CIP 12:55 Start back wash sequence on GAC 4: Open back wash drain valve, Open backwash recirculating valve, and backwash inlet valve. Start backwash pump 1, Open backwash pump 1 flow control valve to 25% for 2 mins. Increase flow control valve to 40% open for 7 mins, Reduce flow control valve to 25% open for 2 mins, Close backwash drain valve. 13:23 close flow control valve, shut off backwash pump 1, close recirculation valve, and close backwash inlet valve. Letting GAC filter settle. 13:40 open GAC4 inlet valve and filter to waste valve. 14:45 close GAC4 filter to waste valve, place effluent valve back in auto, and change filter setpoint back to in service. 13:30 Instrumentation team completed work on trains 4 and 5. Turned both trains back on. Will be working on train 2 and 3 next, placed both trains in off mode. 14:30 Instrumentation team completed work on trains 2 and 3, placed trains back on. 14:33 Activated system duty 14:38 Placed fluoride pumps back in auto. | Georgina Water Treatment Plant | 2026-03-06
EAST | March | Reviewed MIT and daily filter performance on all membrane trains - all passed and within range - recorded data in PWQ sheets. 9:40-13:20 GAC2 Backwash - Followed procedure for GAC backwash. Notified ROC that GAC2 placed OOS for the duration. Any Backwash and GAC2 alarms will be related to the procedure and will be assessed and reset when completed. 12:51 ROC called for UV1 and UV2 comm alarms, requested Christian V.B. to deactivate system duty. Reset Comm alarms. Called Chris S. to request assistance in determining why the comm alarms have occurred multiple times. Completed housekeeping work orders. | Georgina Water Treatment Plant | 2026-03-19
EAST | March | Onsite to continue with annual calibrations Informed ROC and operations Plant offline Completed: Train LITs 1, 4 and 8 Train header PITs 4, 3 and 2 Cleared associated alarms Informed operations and ROC No issues Left site | Georgina Water Treatment Plant | 2026-03-27
WW-NORTH | March | Rotate duty?s on pinch valves Pinch valve # 2 now in duty 1 for the day 185kpa | Newmarket Pinch Valves | 2026-03-09
WW-NORTH | March | Switch back to pinch valve 1 after 24hr rotation on 2. Pinch valve operation on 2 ok however the low pressure alarm will come in while duty is active | Newmarket Pinch Valves | 2026-03-10
WW-NORTH | March | Onsite for CSE inspection Check air valves Inspect sump pit/ test float functionality | Newmarket Pinch Valves | 2026-03-20
ROC | March | Christian Van Beek signing in. Weather 10C and clear. | ROC General | 2026-03-29
ROC | March | Ethan U signing in Weather 0. | ROC General | 2026-03-29
ROC | March | Ethan Ullalkar signing out. | ROC General | 2026-03-29
ROC | March | Christian Van Beek creating a test log entry at the request of Jennifer Chung. | ROC General | 2026-03-28
ROC | March | Connor Smith signing out | ROC General | 2026-03-29
ROC | March | Christian Van Beek signing out. | ROC General | 2026-03-28
ROC | March | Adeela Khan Signing out | ROC General | 2026-03-30
ROC | March | Christian Van Beek signing out. | ROC General | 2026-03-30
ROC | March | Ethan U signing in Weather 4. | ROC General | 2026-03-30
ROC | March | Testing eLog | ROC General | 2026-03-31
ROC | March | AUSS, Garrick from Ferguson Electric is on site | ROC General | 2026-03-31
ROC | March | AUSS - Theodore (AB) on site | ROC General | 2026-03-30
ROC | March | Gluzen Ramos Ong signing out | ROC General | 2026-03-30
ROC | March | KSSP - Drew from Ferguson finished at site | ROC General | 2026-03-30
ROC | March | MTSP - Steve from LCD mechanical for maintenance on auto drain for compressed air system | ROC General | 2026-03-30
ROC | March | Adeela Khan signing in | ROC General | 2026-03-30
ROC | March | Ethan Ullalkar signing out. | ROC General | 2026-03-30
ROC | March | SUSSHS, Chad S from Bell Canada is on site | ROC General | 2026-03-31
ROC | March | Christian Van Beek signing in. Weather: 18C and clear. | ROC General | 2026-03-30
ROC | March | Adeela Khan signing out | ROC General | 2026-03-31
ROC | March | NBSP - Ben from Property Services is on site for HVAC PM's | ROC General | 2026-03-31
ROC | March | Ethan U signing in Weather 14. | ROC General | 2026-03-31
ROC | March | Christian Van Beek signing in. | ROC General | 2026-03-04
ROC | March | Carter D Signing Out | ROC General | 2026-03-08
ROC | March | Angelica Chepiga signing in,weather -6C | ROC General | 2026-03-02
ROC | March | Ethan U signing in | ROC General | 2026-03-12
ROC | March | Ethan Ullalkar signing out. | ROC General | 2026-03-11
ROC | March | Christian Van Beek signing in. | ROC General | 2026-03-09
ROC | March | Christian Van Beek signing in. Weather: 2C and rain. | ROC General | 2026-03-05
ROC | March | KSETDP - Owen S from Asset management leaving site. | ROC General | 2026-03-02
ROC | March | MAPS - Dave from property services on site to work on an air handling system. | ROC General | 2026-03-09
ROC | March | EGSSSC - Joe O from CPD on site. | ROC General | 2026-03-12
ROC | March | YDOC - Drew from Ferguson Electric on site for a generator TSSA inspection and test. Arthur L monitoring remotely. | ROC General | 2026-03-13
ROC | March | SHSP - Steve B onsite for for clean up with electrical inspector SHSP - Steve B onsite for for clean up with elctrical inspector | ROC General | 2026-03-05
ROC | March | GWTP - Derek S (contractor) attending site for pick up on some gear. Will be working on project for muscle control system throughout the year | ROC General | 2026-03-12
ROC | March | KSSP - Garrick from Ferguson onsite running some pipe | ROC General | 2026-03-11
ROC | March | KSSP- Garrick from Ferguson Electric is on site NMETYS- Dennis from Landmark is on site | ROC General | 2026-03-06
ROC | March | MKPSSA - Drew from Ferguson Electric on site. | ROC General | 2026-03-03
ROC | March | KSSP - Garrick from Ferguson finished at site | ROC General | 2026-03-12
ROC | March | NMPSKC, Theodor from AB is leaving site | ROC General | 2026-03-13
ROC | March | KSTKWP - Dominic from Honeywell on site. | ROC General | 2026-03-13
ROC | March | KSSSQW - Joe O on site to complete a warranty walkthrough. | ROC General | 2026-03-12
ROC | March | Christian Van Beek signing in. | ROC General | 2026-03-13
ROC | March | KSTKWP - Dominic from Honeywell leaving site. | ROC General | 2026-03-13
ROC | March | NBW3, Drew from Ferguson Electric is leaving site | ROC General | 2026-03-13
ROC | March | NBW3, Drew from Ferguson Electric is on site | ROC General | 2026-03-13
ROC | March | NMTKKC - Theodore from ABPMC on site for TSSA generator inspection with no transfer to load. | ROC General | 2026-03-13
ROC | March | Adeela Khan signing out | ROC General | 2026-03-13
ROC | March | Ethan U signing in Weather -7. | ROC General | 2026-03-03
ROC | March | Ethan U signing in | ROC General | 2026-03-11
ROC | March | Adeela Khan signing in. Weather: 16C and Sunny | ROC General | 2026-03-09
ROC | March | STRS48, STW56, STETBR - Security intrusion alarm. FMC will notify Corp security. | ROC General | 2026-03-15
ROC | March | STPSTL - Security intrusion alarm. FMC will notify Corp security. | ROC General | 2026-03-15
ROC | March | YDOC 9 - Jon from property services leaving site. | ROC General | 2026-03-10
ROC | March | Angelica Chepiga signing in,weather -4C | ROC General | 2026-03-15
ROC | March | NBSP - Ken from ITS on site for High-speed internet upgrade. Will attend NBETRS site after. | ROC General | 2026-03-15
ROC | March | NMETYS - Thomas from IM onsite for minor repairs | ROC General | 2026-03-03
ROC | March | MKPSSA - Drew from Ferguson Electric leaving site. | ROC General | 2026-03-03
ROC | March | Carter Dunn Signing Out | ROC General | 2026-03-14
ROC | March | Adeela Khan signing in. Weather: 0C and Sunny | ROC General | 2026-03-04
ROC | March | JDSS, Phil from AB is leaving site | ROC General | 2026-03-13
ROC | March | Adeela Khan signing in. Weather: 0C and snowing | ROC General | 2026-03-13
ROC | March | GWTP - Evan from Hydro One (705 783 2728) is on site and is taking a look at the meter. Requests access to the gate. Called Joe M. who will let Evan in | ROC General | 2026-03-04
ROC | March | SUSP - David from property services on site to complete maintenance on an electrical heater. | ROC General | 2026-03-02
ROC | March | BLETNL - Dominic from Honeywell on site. | ROC General | 2026-03-09
ROC | March | KSSP - Garrick from Ferguson electric on site. | ROC General | 2026-03-09
ROC | March | LSSS - Emily from EME on site to collect samples. Emily requested that pump 6 be placed into duty 1. Made the necessary change. | ROC General | 2026-03-02
ROC | March | AUSS - Scott L from AIM leaving site. | ROC General | 2026-03-09
ROC | March | MTETNL - Dominic from Honeywell off site. | ROC General | 2026-03-09
ROC | March | Stouffville - Lane from town of Stouffville flushing zone 2 all day | ROC General | 2026-03-06
ROC | March | Angelica Chepiga signing out | ROC General | 2026-03-08
ROC | March | Ethan Ullalkar signing out. | ROC General | 2026-03-15
ROC | March | Christian Van Beek signing out. | ROC General | 2026-03-03
ROC | March | Carter Dunn Signing In, 16D/Rain | ROC General | 2026-03-07
ROC | March | Adam Button signing out | ROC General | 2026-03-07
ROC | March | SECC- Johnathan from Property Services onsite for fire testing. | ROC General | 2026-03-10
ROC | March | Carter Dunn Signing in, 3D/Clear | ROC General | 2026-03-15
ROC | March | Angelica Chepiga signing out | ROC General | 2026-03-15
ROC | March | Ethan U singing in | ROC General | 2026-03-06
ROC | March | Adeela Khan signing out | ROC General | 2026-03-04
ROC | March | Adeela Khan signing out | ROC General | 2026-03-09
ROC | March | BLETNL - Dominic from Honeywell leaving site. Heading to MTETNL. | ROC General | 2026-03-09
ROC | March | BLETNL - Sean from Stouffville water will be flushing in the Ballantrae Water System today. | ROC General | 2026-03-09
ROC | March | AUSS - Scott from IAM on site for the tour. | ROC General | 2026-03-09
ROC | March | Adam Button signing out | ROC General | 2026-03-06
ROC | March | GWTPLL - Joe O from CPD on site. | ROC General | 2026-03-10
ROC | March | KBSP - Drew from Ferguson Electric on site for pipe work. No alarms anticipated from this work. | ROC General | 2026-03-02
ROC | March | NMETYS - Carlos from landmark Municipal Services attended site to gain access. Carlos's security card is not working as intended and he will be contacting his York Region contact to fix it. Carlos noticed that the door to the tower opens freely. Contacted Security who will send a mobile operator to secure the site. Also informed Area operations. | ROC General | 2026-03-02
ROC | March | NBSP - Dave from property services leaving site. | ROC General | 2026-03-03
ROC | March | Adam Button signing in 8C clear | ROC General | 2026-03-07
ROC | March | Christian Van Beek signing out | ROC General | 2026-03-12
ROC | March | KSTP - Theodore from AB onsite for measurements 9:19 - Finished at site | ROC General | 2026-03-05
ROC | March | KSTP - Apurva from Honeywell leaving site. | ROC General | 2026-03-09
ROC | March | STETBR - Dominic from Honeywell on site. | ROC General | 2026-03-10
ROC | March | BLSS - Chris from property services on site to test the fire alarm. | ROC General | 2026-03-09
ROC | March | Christian Van Beek signing out. | ROC General | 2026-03-09
ROC | March | KSSP - Drew from Ferguson Electric leaving site. | ROC General | 2026-03-09
ROC | March | KSSP - Drew from Ferguson onsite ESA inspector 11:54 - Drew will run generator temporarily | ROC General | 2026-03-11
ROC | March | Ethan Ullalkar signing out. | ROC General | 2026-03-05
ROC | March | Connor Smith signing in -12 C Clear | ROC General | 2026-03-01
ROC | March | Angelica Chepiga signing out | ROC General | 2026-03-12
ROC | March | VNET - Meaguel from YR police onsite for Monthly site visit | ROC General | 2026-03-11
ROC | March | Connor Smith signing out | ROC General | 2026-03-10
ROC | March | Christian Van Beek signing out. | ROC General | 2026-03-10
ROC | March | NBSP - Dave from property services on site to complete work on the diesel room exhaust fan. | ROC General | 2026-03-03
ROC | March | KSSP, Garrick from Ferguson Electric is on site | ROC General | 2026-03-13
ROC | March | QVW12 - Drew from Ferguson Electric leaving site. | ROC General | 2026-03-10
ROC | March | Pesticon Visiting Following Sites; NBSSJA, KCSSKR, KCETFS, KCETDS | ROC General | 2026-03-11
ROC | March | Christian Van Beek signing out. | ROC General | 2026-03-04
ROC | March | JDSS - Stephen from AB project. Generator back in auto and can run KSETDP - Will from Honeywell onsite | ROC General | 2026-03-05
ROC | March | NBSP - Dave from PS leaving site | ROC General | 2026-03-11
ROC | March | Christian Van Beek signing in. | ROC General | 2026-03-03
ROC | March | GWTP- Chris from Property Services onsite to check out fire panel | ROC General | 2026-03-04
ROC | March | Connor Smith signing in 1C Cloudy | ROC General | 2026-03-03
ROC | March | Angelica Chepiga signing in, weather +7C | ROC General | 2026-03-09
ROC | March | Forced corporate computer restart | ROC General | 2026-03-07
ROC | March | STETBR- Dominic from Honeywell finished onsite. | ROC General | 2026-03-10
ROC | March | Connor Smith signing out | ROC General | 2026-03-02
ROC | March | Carter Dunn Signing In, -2D/Clear | ROC General | 2026-03-05
ROC | March | Ethan U signing in | ROC General | 2026-03-05
ROC | March | KSSP - Garrick from Ferguson onsite | ROC General | 2026-03-12
ROC | March | Carter Dunn Signing Out | ROC General | 2026-03-07
ROC | March | Adam Button signing in 0C Raining | ROC General | 2026-03-06
ROC | March | Ethan Ullalkar signing out. | ROC General | 2026-03-12
ROC | March | NMETYS - Junjie from CPD leaving site with Landmark contractors. | ROC General | 2026-03-03
ROC | March | Connor Smith signing out | ROC General | 2026-03-01
ROC | March | KSSSQW - Joe O finished and leaving site. | ROC General | 2026-03-12
ROC | March | Ethan Ullalkar signing out. | ROC General | 2026-03-03
ROC | March | Christian Van Beek signing in. Weather: 10C and clear. | ROC General | 2026-03-10
ROC | March | AUSS, Dave from Property services is leaving site | ROC General | 2026-03-05
ROC | March | Adeela Khan signing in. Weather: 10C and sunny | ROC General | 2026-03-08
ROC | March | SUSP - David from property services leaving site. | ROC General | 2026-03-02
ROC | March | STRS48 - Dominic from Honeywell leaving site. | ROC General | 2026-03-02
ROC | March | Angelica Chepiga signing in, weather +7C | ROC General | 2026-03-10
ROC | March | KSTP - Apurva from Honeywell on site. | ROC General | 2026-03-09
ROC | March | KSTP - Garrick from Ferguson Electric on site. | ROC General | 2026-03-10
ROC | March | RHPSPA - Dominic from Honeywell on site. | ROC General | 2026-03-10
ROC | March | RHPSPA - Dominic from Honeywell leaving site and heading to BLETNL. | ROC General | 2026-03-10
ROC | March | Christian Van Beek signing out. | ROC General | 2026-03-06
ROC | March | Adeela Khan signing out | ROC General | 2026-03-01
ROC | March | SEOC6/7 - Drew from Ferguson Leaving site and headed to YDOC for sticker placement. | ROC General | 2026-03-03
ROC | March | KSETDP, Dominic from honey well is leaving site | ROC General | 2026-03-05
ROC | March | Carter Dunn Signing In, -2D/Clear | ROC General | 2026-03-04
ROC | March | KBSP - Drew from Ferguson Electric on site for photos. Drew will be on site for a short period. | ROC General | 2026-03-09
ROC | March | STPSMR - Antonio from Torbear construction on site to complete some hot work. | ROC General | 2026-03-09
ROC | March | Town of Stouffville - Corey from Stouffville informed they are flushing nineth line North of Hoover | ROC General | 2026-03-03
ROC | March | KCETFS, Kingsley from Freedom Mobile is on site | ROC General | 2026-03-05
ROC | March | Carter Dunn Signing In, 1D/Rain | ROC General | 2026-03-06
ROC | March | Angelica Chepiga signing in, weather +3C | ROC General | 2026-03-08
ROC | March | Connor Smith signing out | ROC General | 2026-03-05
ROC | March | Ethan U signing in Weather 0. | ROC General | 2026-03-14
ROC | March | MAPS - Intrusion alarm, FMC will notify Corp security. | ROC General | 2026-03-15
ROC | March | Carter Dunn Signing In, -7D/Clear | ROC General | 2026-03-13
ROC | March | STRS48/STPS48 - Intrusion alarm, FMC will notify Corp security. | ROC General | 2026-03-15
ROC | March | QVW12- Gerrick from Ferguson onsite | ROC General | 2026-03-10
ROC | March | SEOC - Drew from Ferguson Electric on site to complete a generator TSSA inspection and test. Arthur L monitoring remotely. | ROC General | 2026-03-13
ROC | March | Christian Van Beek signing in. | ROC General | 2026-03-13
ROC | March | SEOC 6/7 Drew from Ferguson Electric on site to complete work on the local fuel transmitter. | ROC General | 2026-03-03
ROC | March | Carter Dunn Signing Out | ROC General | 2026-03-05
ROC | March | PVSS - Scott from IAM on site with Mike L for a tour of the facility. | ROC General | 2026-03-12
ROC | March | Carter Dunn Signing In. -3D/Snowing | ROC General | 2026-03-14
ROC | March | Christian Van Beek signing out | ROC General | 2026-03-02
ROC | March | Connor Smith signing out | ROC General | 2026-03-11
ROC | March | Connor Smith signing in -1C windy | ROC General | 2026-03-12
ROC | March | BLW12 - Shahin with Torbear onsite for soldering work 416-4254-9527 | ROC General | 2026-03-05
ROC | March | NBW3 - Drew from Ferguson Electric will be testing the generator wit no transfer to load. | ROC General | 2026-03-13
ROC | March | Connor Smith signing out | ROC General | 2026-03-04
ROC | March | Connor Smith signing out | ROC General | 2026-03-13
ROC | March | KSTP - Drew from Ferguson electric leaving site. | ROC General | 2026-03-09
ROC | March | Angelica Chepiga signing in,weather +5C | ROC General | 2026-03-11
ROC | March | Ethan Ullalkar signing out. | ROC General | 2026-03-14
ROC | March | PVSS - Scott finished at site | ROC General | 2026-03-12
ROC | March | Angelica Chepiga signing in, weather +4C | ROC General | 2026-03-19
ROC | March | Adeela Khan signing in. Weather: -7C and Cloudy | ROC General | 2026-03-17
ROC | March | Adeela Khan signing out | ROC General | 2026-03-19
ROC | March | AUSS- Phil from AB onsite. 14:13- Offsite | ROC General | 2026-03-26
ROC | March | KSSP - Cody from Ferguson onsite for epoxy work | ROC General | 2026-03-20
ROC | March | SHETCS - Rob from Chubb on site. | ROC General | 2026-03-18
ROC | March | NMTKKC- Jamie from ETO Engineering onsite. | ROC General | 2026-03-19
ROC | March | Christine S visiting the following sites; JDSS, KSETP, KSSP, GRSSWA | ROC General | 2026-03-25
ROC | March | RHAMF1, Eric from NAC on site, Fixed the Recirculation Pump 1/2 issue, reset alarms | ROC General | 2026-03-23
ROC | March | STPSMR - Drew from Ferguson Electric is on site | ROC General | 2026-03-23
ROC | March | MTSS - Andrew from Westlake construction called to inform that the gate was repaired and locked. | ROC General | 2026-03-16
ROC | March | KSTP - Garrick from Ferguson electric leaving site, heading to KSSP. KSSP - Drew from Ferguson electric on site. | ROC General | 2026-03-26
ROC | March | Gluzen Ramos Ong signing in KSSP - Drew (Ferguson) onsite working on PAC panels, informed Artour L (PCS) will also be on site. Will follow up with Artour L. if alarms received | ROC General | 2026-03-27
ROC | March | KBSP- Phil from AB is on site | ROC General | 2026-03-16
ROC | March | Carter Dunn Signing In, 3D/Clear | ROC General | 2026-03-16
ROC | March | Angelica Chepiga signing in,weather -11C | ROC General | 2026-03-18
ROC | March | QVW12- Will M onsite for analyzer maintenance. Disregard alarms while onsite. *Wrong Book | ROC General | 2026-03-17
ROC | March | JDSS - Drew from Ferguson electric on site. 16:00 Drew off site. AURSBS - Mark from Process optimization on site 15:30 Mark leaving site. | ROC General | 2026-03-18
ROC | March | Angelica Chepiga signing out | ROC General | 2026-03-26
ROC | March | Adeela Khan signing in. Weather: 8C and raining | ROC General | 2026-03-26
ROC | March | Connor Smith signing out | ROC General | 2026-03-20
ROC | March | 16:09 - KBSP - Theodore (AB Constr.) leaving site 17:20 - KSSP - Garrick (Ferguson) leaving Generator Bldg. Confirmed Armed | ROC General | 2026-03-19
ROC | March | HLETPR- Megsen from YRP onsite. | ROC General | 2026-03-24
ROC | March | Connor Smith signing in 0C Snowy | ROC General | 2026-03-20
ROC | March | KBSP - Theodore from AB onsite working on fuel system | ROC General | 2026-03-20
ROC | March | GWTP- Derek from Maple Reinders onsite. | ROC General | 2026-03-25
ROC | March | KSSSQW- Joe O CPD offsite. | ROC General | 2026-03-25
ROC | March | Pestacon visiting the following sites; NMETIB, NMETHW, NMETDD, NMSSBP, NMSSHS, NMW12, NMW15, NMETYS, NMPSKC, NMW136, NMTKBS, ANW23 | ROC General | 2026-03-25
ROC | March | Ethan U signing in | ROC General | 2026-03-21
ROC | March | AUSS - Dan T from ABPMC on site for piping work related to the generator fuel system. | ROC General | 2026-03-27
ROC | March | NMETYS- Kevin from Yorknet onsite. 13:43- Offsite | ROC General | 2026-03-25
ROC | March | KSSP - Christian from Ferguson Electric leaving site. | ROC General | 2026-03-25
ROC | March | SEOC67 - Dominic from Honeywell off site. | ROC General | 2026-03-26
ROC | March | Christian Van Beek signing in. Weather: 2C and clear. | ROC General | 2026-03-20
ROC | March | HLSSBS - Kevin K. (CPD) on site for site meeting Heading to QVSSSC, EGSSSC | ROC General | 2026-03-27
ROC | March | KBSP- Steven from AB onsite. | ROC General | 2026-03-26
ROC | March | KSSSQW - Joe O from CPD with contractor Tormont working on generator. | ROC General | 2026-03-16
ROC | March | KSSP - Phil from ABPMC on site to complete work in the generator room. | ROC General | 2026-03-18
ROC | March | JDSS- Drew from Ferguson onsite. | ROC General | 2026-03-20
ROC | March | KSSP - Phil from AB on site. | ROC General | 2026-03-17
ROC | March | MARS- Chris from Property Services onsite for fire alarm testing | ROC General | 2026-03-16
ROC | March | NMETHW - Kalid from AIM on site with contractors. | ROC General | 2026-03-17
ROC | March | MTSP- Dominic from Honeywell onsite. 08:35- Offsite | ROC General | 2026-03-19
ROC | March | Angelica Chepiga signing out | ROC General | 2026-03-18
ROC | March | KBSP - Garrick from Ferguson electric leaving site. | ROC General | 2026-03-26
ROC | March | Christian Van Beek signing out. | ROC General | 2026-03-21
ROC | March | STRS48 - Drew from Ferguson electric on site and requested a fuel tank level reading. | ROC General | 2026-03-25
ROC | March | Connor Smith signing in | ROC General | 2026-03-19
ROC | March | Adeela Khan signing in. Weather: -2C and Cloudy | ROC General | 2026-03-18
ROC | March | STPSMR - Drew from Ferguson Electric on site for tagging. | ROC General | 2026-03-19
ROC | March | KSSSQW - Joe O from CPD on site with Toromont to complete work on the generator starter. | ROC General | 2026-03-25
ROC | March | Carter Dunn Signing In, 0D/Clear | ROC General | 2026-03-23
ROC | March | KSSP - Drew from Ferguson electric leaving site. | ROC General | 2026-03-24
ROC | March | Christian Van Beek signing in. | ROC General | 2026-03-25
ROC | March | Connor Smith signing in -3C Cloudy | ROC General | 2026-03-25
ROC | March | SEOC4, SEOC OCF, SEOC6/7, SEOC8 -Jonathan from Property services attending sites for Fire alarm testing. | ROC General | 2026-03-16
ROC | March | Connor Smith signing out | ROC General | 2026-03-25
ROC | March | KSSP- Gerrick from Ferguson onsite. | ROC General | 2026-03-19
ROC | March | Adeela Khan signing out | ROC General | 2026-03-27
ROC | March | Adeela Khan Signing Out | ROC General | 2026-03-18
ROC | March | Christian Van Beek signing in. | ROC General | 2026-03-18
ROC | March | SUSP - Steven T from CPD leaving site. | ROC General | 2026-03-19
ROC | March | Adeela Khan signing out | ROC General | 2026-03-22
ROC | March | KSSP - Garrick from Ferguson Electric is on site and will be entering the generator building. Garrick informed he will not be running the generator at this time | ROC General | 2026-03-23
ROC | March | KSSSQW- Joe O CPD Leaving site. | ROC General | 2026-03-16
ROC | March | KSTP - Hamid from ETO engineering leaving site. | ROC General | 2026-03-18
ROC | March | EGSSSC- Cameron from IT onsite troubleshooting modem | ROC General | 2026-03-16
ROC | March | Connor Smith signing out | ROC General | 2026-03-19
ROC | March | QVW12 - Mark from Process optimization team on site. | ROC General | 2026-03-18
ROC | March | Christian Van Beek signing out. | ROC General | 2026-03-18
ROC | March | SEOC OCF - Ben (PSB) finished on site | ROC General | 2026-03-19
ROC | March | KBSP - Drew from Fergugon entering site | ROC General | 2026-03-20
ROC | March | YDSS + YNSS Normal | ROC General | 2026-03-20
ROC | March | SEOC67 - Dominic from Honeywell on site. | ROC General | 2026-03-26
ROC | March | Angelica Chepiga signing in | ROC General | 2026-03-16
ROC | March | Adeela Khan signing in | ROC General | 2026-03-23
ROC | March | Kingsley M restarting SCADA screens and Patriot | ROC General | 2026-03-26
ROC | March | NRETBR - Stephen from Newcort tech on site. | ROC General | 2026-03-26
ROC | March | Ethan Ullalkar signing out. | ROC General | 2026-03-24
ROC | March | STPSMR/TSRS48/STW12/STW3/STETTL/STETBR/BLETNL/STW56/BLW3, PCO Pest Control on site | ROC General | 2026-03-23
ROC | March | KBSP - Theodore from ABPMC on site to complete a generator pressure test. The generator will be offline and unavailable during this test | ROC General | 2026-03-19
ROC | March | AUSS - Rory from PS testing fire alarm 8:43 - Leaving site | ROC General | 2026-03-20
ROC | March | STRS48 - Drew from Ferguson onsite removing scrap metal onsite | ROC General | 2026-03-20
ROC | March | MKETFA, David from the RCMP is on site, moving some of his equipment/antenna | ROC General | 2026-03-23
ROC | March | KBSP- Theodore from AB Offsite. | ROC General | 2026-03-20
ROC | March | NMETYS - Freedom Mobile contractor on site. 12:20 Off site. | ROC General | 2026-03-26
ROC | March | KSSP - Gerrick from Ferguson Electric leaving site. | ROC General | 2026-03-27
ROC | March | QVW12- Drew from Ferguson onsite. 15:06- Offsite | ROC General | 2026-03-19
ROC | March | NMSSHS- Joe O CPD onsite. 10:30 Offsite | ROC General | 2026-03-19
ROC | March | EGSSSC - Kevin K from CPD on site. | ROC General | 2026-03-27
ROC | March | Connor Smith signing in -12C Windy | ROC General | 2026-03-17
ROC | March | Carter D Signing Out | ROC General | 2026-03-25
ROC | March | KSSP - Garrick from Ferguson Electric on site. | ROC General | 2026-03-25
ROC | March | Connor Smith signing out | ROC General | 2026-03-24
ROC | March | Christian Van Beek signing out. | ROC General | 2026-03-25
ROC | March | Connor Smith signing in 9C Cloudy | ROC General | 2026-03-16
ROC | March | HLPSYS- Dominic from Honeywell off site. | ROC General | 2026-03-26
ROC | March | EGSSSC - Kevin from CPD off site. | ROC General | 2026-03-27
ROC | March | Connor Smith signing out | ROC General | 2026-03-17
ROC | March | KBSP - Teodore from AB leaving site. | ROC General | 2026-03-26
ROC | March | JDSS- Drew from Ferguson offsite | ROC General | 2026-03-20
ROC | March | Angelica Chepiga signing out | ROC General | 2026-03-16
ROC | March | SEOC OCF - Ben Han from property services on site to work on an air handling unit. | ROC General | 2026-03-19
ROC | March | Angelica Chepiga signing out | ROC General | 2026-03-24
ROC | March | NBSSJA - Dave W from property services leaving site. | ROC General | 2026-03-25
ROC | March | Ethan Ullalkar signing out. | ROC General | 2026-03-21
ROC | March | KSSP- Gerrick from Ferguson offsite. | ROC General | 2026-03-17
ROC | March | Connor Smith signing in | ROC General | 2026-03-24
ROC | March | BLSS - Mohsen from CPD on site. | ROC General | 2026-03-16
ROC | March | Carter D Signing In, 4D/Clear | ROC General | 2026-03-25
ROC | March | Angelica Chepiga signing in,weather -7C | ROC General | 2026-03-24
ROC | March | Angelica Chepiga signing in | ROC General | 2026-03-26
ROC | March | KSTP- Gerrick from Ferguson onsite. 08:10- Gerrick informed that door of generator building was wide open when he arrived. Informed Security and they will send someone to check it out. | ROC General | 2026-03-26
ROC | March | MKPSSA- Drew from Ferguson onsite. 14:28- Offsite | ROC General | 2026-03-26
ROC | March | Christian Van Beek signing out. | ROC General | 2026-03-22
ROC | March | QVW34- Drew from Ferguson onsite. 15:45- Offsite | ROC General | 2026-03-19
ROC | March | Christian Van Beek signing in. Weather: 3C and clear. | ROC General | 2026-03-21
ROC | March | QVW12- Rory from Property Services onsite. | ROC General | 2026-03-24
ROC | March | STPSTL- Drew from Ferguson onsite. | ROC General | 2026-03-19
ROC | March | STRS48- Drew from Ferguson offsite. | ROC General | 2026-03-20
ROC | March | KBSP- Drew from Ferguson leaving site. | ROC General | 2026-03-20
ROC | March | QVW12 - Mark S from process optimization leaving site. | ROC General | 2026-03-18
ROC | March | Carter Dunn Signing Out | ROC General | 2026-03-17
ROC | March | Angelica Chepiga signing out | ROC General | 2026-03-20
ROC | March | NMSSBP- Pat from Property Services onsite for fire testing. 087:18- Finished onsite. | ROC General | 2026-03-20
ROC | March | STRS48- Drew from Ferguson onsite working on generator. May have to shut it down and trigger some alarms. | ROC General | 2026-03-25
ROC | March | SEOC Shaft 6/7 - Jeff from Keyshack on site to work on a fan room door. | ROC General | 2026-03-25
ROC | March | QVW12 - Rory from Property Services is on site to take a look at a broken door | ROC General | 2026-03-23
ROC | March | Ethan U signing in | ROC General | 2026-03-20
ROC | March | Angelica Chepiga signing in | ROC General | 2026-03-27
ROC | March | Connor Smith signing out | ROC General | 2026-03-26
ROC | March | KSSP - Cody from Ferguson electric on site. | ROC General | 2026-03-16
ROC | March | RHRSTR - Jonathan from Property Services is on site for a sprinkler flow test | ROC General | 2026-03-23
ROC | March | Connor Smith signing in 3C Clear | ROC General | 2026-03-26
ROC | March | KCETDS- Kalid from IM offsite. | ROC General | 2026-03-24
ROC | March | YDOC- Ben from Property Services onsite. 13:49- Offsite. | ROC General | 2026-03-17
ROC | March | Christian Van Beek signing in. Weather: -2C and clear. | ROC General | 2026-03-19
ROC | March | Ethan U signing in Weather 5. | ROC General | 2026-03-22
ROC | March | SEOC67- Kevin from Yorknet offsite. | ROC General | 2026-03-25
ROC | March | Carter Dunn Signing Out | ROC General | 2026-03-16
ROC | March | HLW2 - Treated free chlorine hihi HLW1 - Combined chlorine lo. Alarms came in during start up. Readings came back within range and cleared alarm | All Water System ROC General | 2026-03-29
ROC | March | HLW1 - Treated free chlorine hihi alarm. Checked site, well is manual/off no water being directed to users. Trending shows a variable reading of the treated free chlorine and treated combined chlorine. Possible analyzer issue. Continuing to monitor. | All Water System ROC General | 2026-03-29
ROC | March | KSTP - Raw water turbidity fault. Disregard as per shift report | All Water System ROC General | 2026-03-29
ROC | March | HLETYS - Noted the inlet tower flow has dropped below the threshold to activate the chemical rechlorination system. Increasing flow setpoint at HLW2 FCV, SCADA will not accept command. Contacted Cole W who assisted with the the adjustment of the flow setpoint. Increased flow from 20L/s to 30L/s in 5L/s increments. #consult | All Water System ROC General | 2026-03-29
ROC | March | MKRSEM - Called Toronto Water (Pouvia) and requested two pumps be activated to fill the reservoir. | All Water System ROC General | 2026-03-29
ROC | March | NMW12 - Treated combined and treated total chlorine lolo alarms. Checked site, wells are not running no water being directed to users. Trending shows an abnormal dip of the treated total and combined chlorine readings which recovered within two reading intervals. SHTP - Filter 3 post rinse NIT high alarm. Checked site, plant is active. Shift report states this alarm can be reset once by remote operators. Reset alarm. | All Water System ROC General | 2026-03-30
ROC | March | VNRSKS - Activated duty 1 to drawdown MARS. | All Water System ROC General | 2026-03-30
ROC | March | STW12/STW3 - Place well 2 & 3 man/on for Zone 1 tower KSTP - Filter 2 backwash OOS. Informed Phil D, will investigate Consult ARPS - Jerry (Peel) informed they are switching from pump 7 to pump 5. May experience pressure fluctuation temporarily | All Water System ROC General | 2026-03-29
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-30
ROC | March | NMW15 - Chlorinator 1 fail to close, interlocked well. Place well in man/off as duty nearing stop as to not let well run at this point. Able to clear alarm. Will place back in auto after duty stop | All Water System ROC General | 2026-03-29
ROC | March | JFPS- Deactivated duty in preparation for Maple to Jefferson feed. | All Water System ROC General | 2026-03-29
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-29
ROC | March | KCETDS - Metering chamber flood alarm. No note on disregard list. Previous log entries for this alarm from this month state that this alarm is a disregard overnight and can be handled by operators in the morning. Sent email to OCO. | All Water System ROC General | 2026-03-30
ROC | March | GWTP LL - low lift pump 4 hydraulic valve fail to close alarm. Shift report states this alarm can be reset and the valve returned to service. Able to reset alarm. | All Water System ROC General | 2026-03-30
ROC | March | STETBR - Tower level hi alarm. Placed STW12 and STW3 in auto mode as per the interim procedure. | All Water System ROC General | 2026-03-30
ROC | March | QVW34 - Chlorine gas leak, CL2 emergency valve closure active. Informed Joe D of update. Placed well 3 man/off for remainder of weekend Consult | All Water System ROC General | 2026-03-29
ROC | March | MKRSEM- Called Toronto and requested pumps off. | All Water System ROC General | 2026-03-29
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-29
ROC | March | Christian Van Beek signing in. Weather 10C and clear. | All Water System ROC General | 2026-03-29
ROC | March | Christian Van Beek signing out. | All Water System ROC General | 2026-03-28
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-29
ROC | March | HLW1 - Treated free chlorine climbed following the ammonia pump rotation. Rotated back to ammonia pump 1. Noted that the free chlorine hihi alarm is currently deactivated. Contacted Cole W to ask if the treated free chlorine hihi alarm is disabled for a reason, Cole W was unaware of this and directed to enable the alarm. Treated free chlorine reading is dropping with ammonia pump 2 active. May see a drop of combined chlorine reading on the HLETYS analyzer. #consult | All Water System ROC General | 2026-03-29
ROC | March | RHRSTR - Activate duty 1 AURSBS - Deactivate duty 1 to lessen demand for MARS | All Water System ROC General | 2026-03-29
ROC | March | QVW34 - Joe D found no leaks, placed well back in auto as possible faulty reading on gas detector. Will investigate further tomorrow. Leaving site | All Water System ROC General | 2026-03-29
ROC | March | VNRSKS - Swapped supply pumps from two VNPS pumps to one VNPS pump and one MAPS pump. | All Water System ROC General | 2026-03-29
ROC | March | HLW2 - Silicate pump 1 leak and uncommanded stop alarm. Checked site, duty 1 rotated to silicate pump 2 which activated. Will monitor system for containment and abnormal operation alarms. | All Water System ROC General | 2026-03-29
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-28
ROC | March | NMVCBA- Placed valve in manual 20L/s to assist in keeping NMETIB and NMETHW offset. 00:53- Placed valve back into auto. | All Water System ROC General | 2026-03-28
ROC | March | HLW1 - Treated free chlorine reading is still above the hihi alarm setpoint. Deactivated HLW1 in manual mode. HLW2 and HLW2FCV still running. Will monitor system to ensure tower still fills without HLW1. | All Water System ROC General | 2026-03-29
ROC | March | VNRSKS - Swapped supply pumps to two MAPS pumps. | All Water System ROC General | 2026-03-29
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-28
ROC | March | HLW1 - Treated free chlorine hi alarm. Checked site, well is active. Trending shows that the treated free chlorine is reading higher than normal the last two run cycles. Swapped ammonia tank duties and monitored. 18:45 - HLW1 - Treated free chlorine reading still hi. Rotated ammonia pump duty. | All Water System ROC General | 2026-03-29
ROC | March | Connor Smith signing in 1C Clear | All Water System ROC General | 2026-03-28
ROC | March | QVW34 - Chlorine gas leak hihi, CL2 emergency valve closure activity. Informed Joe D of outstanding alarm and ppm reading going up. Joe will take a look on SCADA 10:49 - Joe D placed wells 3 & 4 man/off for now, will head out later to address issue w Phil D, gas level went down now chlorinators are isolated. CMU = 11765263 | All Water System ROC General | 2026-03-29
ROC | March | MARS- Cell1(North) Lvl Lo Alarm VNRSKS- Deactivated duty | All Water System ROC General | 2026-03-28
ROC | March | AURSBS - Activated duty 1 to fill the reservoir. | All Water System ROC General | 2026-03-29
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-29
ROC | March | Connor Smith signing out | All Water System ROC General | 2026-03-29
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-29
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-29
ROC | March | MKRSEM - Called Toronto Water (Pouria) and requested they stop flow to MKRSEM | All Water System ROC General | 2026-03-30
ROC | March | Ethan U signing in Weather 4. | All Water System ROC General | 2026-03-30
ROC | March | AURSBS - Activated duty 1 to drawdown MARS. | All Water System ROC General | 2026-03-30
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-30
ROC | March | Christian Van Beek signing out. | All Water System ROC General | 2026-03-30
ROC | March | NBW2 - Place well back in auto as noted in shift report. | All Water System ROC General | 2026-03-30
ROC | March | Gluzen Ramos Ong signing in BVPS - Dan B. and Kyle R. doing generator load test. Informed will not be transferring or losing power to station, pumps unaffected. MKETFA - Andrew (Toronto Water) testing PRV to ET. Duty currently active, about halfway through cycle. Monitoring | All Water System ROC General | 2026-03-30
ROC | March | 08:44 - HLW2 - Tim H., Benson S., Adeela K., Ethan U., on site for cylinder change 08:56 - NBW2 - Jacob M. with GFL on site for silicate removal. Duty just deactivated and well in local off | All Water System ROC General | 2026-03-30
ROC | March | RHRSTR - Deactivated duty 1 to prevent overfilling in low morning demand. | All Water System ROC General | 2026-03-30
ROC | March | SHTP - Filter 3 Post Rinse NIT High alarm came in. Ack/reset as per shift repot 07:24 - Alarm came back in. Spoke to Cole W. who directed to ack/reset alarm again but to let him know if alarm comes back in 07:45: Alarm came back in. Spoke to Cole W. who directed to initiate a backwash and someone will attend site today for a turbidimeter clean. Backwash has been initiated | All Water System ROC General | 2026-03-30
ROC | March | MARS - Tegbeer from OCWA called to inform that he will be completing the daily pump change. Will be going from pump 6 to 7 | All Water System ROC General | 2026-03-31
ROC | March | GWTP - Ricardo L, Parth P. and Eric S. are on site for annual calibration | All Water System ROC General | 2026-03-30
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-30
ROC | March | GWTP - UV reactor 2 intensity lo. Checking site reading came back within range GWTP - GAC 4 flow control valve deviation alarm. Disregard as per shift report VNP8 - Duty shows OOS, place pump back man/off | All Water System ROC General | 2026-03-30
ROC | March | BLW3 - working on chemical train 2 | All Water System ROC General | 2026-03-30
ROC | March | Adeela Khan signing in | All Water System ROC General | 2026-03-30
ROC | March | HLW1 - Combined Chlorine LoLo. Ongoing WM break. Well is man/off and water is not being directed to users. | All Water System ROC General | 2026-03-31
ROC | March | HLW1 - Tim H onsite working on silicate and pump GWTP - Joe M onsite for GAC 1 backwash | All Water System ROC General | 2026-03-30
ROC | March | BVPS - Dan B. and Kyle R. are on site for generator maintenance and will be placing the generator on/off throughout the day. Operations will not be affected. | All Water System ROC General | 2026-03-31
ROC | March | NMTKBS, Outlet Flow OOR/Fault and hi flow alarm, contacted Jason G but no response, left a voice message, will call him back within 5 minutes again | All Water System ROC General | 2026-03-31
ROC | March | RHRSTR - Deactivated duty 1 to avoid overfilling during low demand morning period. | All Water System ROC General | 2026-03-31
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-30
ROC | March | EGMCRW - PAC Control panel power failure alarm. Checked site, operations appear normal. Trending shows no interruptions to data collection. Unable to clear alarm. Will email area operations. | All Water System ROC General | 2026-03-31
ROC | March | NMVCBA/NMVCIB - Reverted setpoints back to 40L/s and 80 L/s respectively NMETIB - Deactivated duty to help offset with NMETHW | All Water System ROC General | 2026-03-30
ROC | March | VNRSKS - Swapped supply pumps from one VNPS and one MAPS to two MAPS pumps to increase the demand on MARS. | All Water System ROC General | 2026-03-31
ROC | March | MKVCMM - Site power failure alarm and PAC control panel power failure alarm. Checked site, operations appear normal. Able to clear alarms. | All Water System ROC General | 2026-03-30
ROC | March | AUW57 - Influent free chlorine hihi. Checked site, Well recently started, trending shows a spike of the influent free chlorine reading which returned to normal range within two reading intervals. Reset alarms, | All Water System ROC General | 2026-03-31
ROC | March | Gluzen Ramos Ong signing out | All Water System ROC General | 2026-03-30
ROC | March | Keswick - Derek from Aquazition will be flushing | All Water System ROC General | 2026-03-30
ROC | March | STETBR - Tower low level alarm. Delaying the start of STW12 and STW3 until the duty at STETBR begins. STETTL has been overfilled through the morning by flow from STETBR to STETL through the flow control valve. Day shift operators will activate STW12 and STW3 when STETTL begins to drain. | All Water System ROC General | 2026-03-30
ROC | March | HLETYS - Outlet flow hihi alarm. Checked site, tower is draining and system duty is not active. Trending shows three abnormal spikes of the outlet flow reading. It is possible that local municipality operators are completing spring hydrant flushing. Will monitor. | All Water System ROC General | 2026-03-30
ROC | March | HLETYS - PAC control panel pwoer failure alarm. Checked site, tower is currently filling. Chemical system shut down during the initial power failure resulting in a post injection combined chlorine low alarm. Not able to reset power related alarms. Informed Cole W during initial call for SHTP. ANW23 Generator running status alarm and discharge pressure low and lolo alarms. Checked site, no duty 1 assigned to pumps. Re-applied duties. Trending shows that the distribution system pressure has recovered. Generator running alarm outstanding. Will monitor. HLPSYS - Generator running alarm. Checked site, pumps are active, normal operations. | All Water System ROC General | 2026-03-31
ROC | March | MKRSEM - PAC Control panel power fail alarm. Checked site, operations appear normal. Reservoir is filling from Toronto COTFA pumps. Trending not impacted. | All Water System ROC General | 2026-03-31
ROC | March | HLW1 and HLW2 - HLW1 and HLW2 to HLETYS communication failure alarms. Checked site, wells have interlocked. Wells were active when the alarms triggered. Placed the wells manual/off to prevent activation as the tower is very close to duty stop. Cole W called to state he is on the way to the HLETYS tower to check the system during the power fail. Created CMU5#W11768997 #CMU5 | All Water System ROC General | 2026-03-31
ROC | March | EGSSSC - recirculation loop flow low and lowlow alarms. Flow control valve fault alarms and recirculation mode failure alarm. Station still operating, wet well cycling. Able to reset valve faults and recirculation flow alarms. Will monitor. *wrong book* | All Water System ROC General | 2026-03-31
ROC | March | HLW2 - Ammonia pump 1 fault alarm and treated free chlorine hihi alarm. Checked site, well is currently active. Ammonia pump duty 1 rotated to ammonia pump 2 which is active. Treated free chlorine spiked following the ammonia pump fault. Able to clear the fault alarm. Will monitor the free chlorine reading. | All Water System ROC General | 2026-03-30
ROC | March | STW12/STW3 - Man/start both well 2 & 3 for zone 1 fill | All Water System ROC General | 2026-03-30
ROC | March | GWTP - Low lift pump 3 uncommanded stop alarm. Checked site, plant is active. Low lift pump 2 currently running in duty 1. Reset alarm. | All Water System ROC General | 2026-03-30
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-30
ROC | March | MKRSEM - Low level alarm. Called Toronto Water (Zoran) and requested they activate two pumps to push flow to MKRSEM. | All Water System ROC General | 2026-03-30
ROC | March | STW3 - Effluent Free Chlorine LoLo Switch alarm came in. Well is not running and water is not being directed to users | All Water System ROC General | 2026-03-31
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-30
ROC | March | HLETYS - CMU5 for historian heartbeat alarm from earlier W11769421 #CMU5 | All Water System ROC General | 2026-03-31
ROC | March | AUPSOH - Kinglsey M. called to inform that he will be working on the OIT and will receive a historian heartbeat alarm. Operations will not be affected | All Water System ROC General | 2026-03-30
ROC | March | AUETOH - Parth P. Ricardo L. and Eric S. are on site for a flowmeter installation | All Water System ROC General | 2026-03-30
ROC | March | AUPSRR - Kinglsey M. called back to inform that he will be restarting the OIT and will trigger a historian heartbeat. Operations will not be affected | All Water System ROC General | 2026-03-30
ROC | March | MARS - Cell 1 Level Lo alarm came in. Deactivated duty 1 at AURSBS | All Water System ROC General | 2026-03-30
ROC | March | Christian Van Beek signing in. Weather: 18C and clear. | All Water System ROC General | 2026-03-30
ROC | March | MTW3 - Emergency Eyewash Flow Switch Alarm came in. Called Travis W. who informed he was cleaning the station and triggered the alarm. Travis will try to clear on site but if it does not clear, Travis would like a call back | All Water System ROC General | 2026-03-30
ROC | March | STETBR - Tower level hi alarm. Placed STW12 and STW3 in auto mode. | All Water System ROC General | 2026-03-30
ROC | March | YWS + NYWS Normal HLW2 - Downstream pressure hihi alarm. Checked site, system duty is active and tower is filling. Flow setpoints for the HLW2 FCV were changed yesterday to accommodate the loss of HLW1. HLW1 is back in service today but the flow setpoint was not reverted. Waited for the HLW2 FCV to close and then reverted the flow setpoint from 30L/s back to 20L/s and cleared alarm. Monitored valve opening. | All Water System ROC General | 2026-03-31
ROC | March | GWTP, Contact Chamber 2 Cl2 lo alarm, notified Joe M, he is looking into it 12:55, Joe M called directed to disregard fluoride lo alarm, he has placed both fluoride pumps in man/off at the moment | All Water System ROC General | 2026-03-31
ROC | March | MTETNL - Travis W. called to inform that he is on site | All Water System ROC General | 2026-03-31
ROC | March | VNPSCD - Chlorine System Failure and Scrubber Gas Leak alarms came in. Checked site. Chlorine system is interlocked. Called Benson S. who will take a look 12:31 - Due to this Chlorine System Failure, switched back to MAPS PD7 for VNRSKS fill cycle 12:40 - MARS - Due to VNRSKS about to start up, Called Toronto Water (Brett) and requested increased flow to reservoir | All Water System ROC General | 2026-03-31
ROC | March | BVPS - Activated duty 1 | All Water System ROC General | 2026-03-31
ROC | March | Adeela Khan Signing out | All Water System ROC General | 2026-03-30
ROC | March | Toronto Water - Gary T. called to inform of a sodium adverse. Notified Dean L. Zahra K. and Central and East Water. Jeremy H. forwarded AWQI forms to areas and the City of Vaughan. AWQI 171877 Sodium Adverse Occurred at the Dufferin Reservoir Date/Time ? Mar/16 2026 12:00 Sodium levels = 20.5 mg/L AWQI 171876 Sodium Adverse Occurred at the Keele Reservoir Date/Time ? Mar/16 2026 13:30 Sodium 27.5 mg/L | All Water System ROC General | 2026-03-31
ROC | March | HLW1 - Treated free chlorine hihi alarm. Checked site, well recently activated to fill the system. Trending shows the treated free chlorine reading is higher the last few run cycles. Will monitor site to determine if the reading will drop. | All Water System ROC General | 2026-03-30
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-31
ROC | March | Ethan Ullalkar signing out. | All Water System ROC General | 2026-03-30
ROC | March | HLW2 - Downstream pressure hihi alarm. HLW2 FCV closing due to alarm. Tower almost finished fill cycle, system pressure is naturally high. Will address this when system hydro failures have been addressed. | All Water System ROC General | 2026-03-31
ROC | March | VNPSCD - Called Benson S. for an update. Benson informed that he cleared alarms and monitored site. | All Water System ROC General | 2026-03-31
ROC | March | HLETYS - Noticed all chem pumps were left man/off. Nothing noted in elogbook at the site or shift report. Called Cole W to confirm any abnormalities that cause chem pumps left off as i see post-inj total is at lo level. Placed all chem pumps back in auto Consult | All Water System ROC General | 2026-03-31
ROC | March | Gluzen Ramos Ong signing in AUPSRR - Kingsley M. working on OIT. Pumps currently not active, but 1% away from starting. Placed man/off until work complete MAPS - Talha H. working on OIT panel, no expected comm disruptions or alarms | All Water System ROC General | 2026-03-31
ROC | March | NBET - Rob P. is on site to complete Pm's | All Water System ROC General | 2026-03-31
ROC | March | BVPS, Duty was activated however pump 3 was failing to open due to a suction valve failure, no alarms present just the interlock, rotated pump duty so pump 3 is in D2 and pump 4 is in D1. Change priority so pump 4 has 1 priority. Notified Patrick F, he will attend site to look into the issue | All Water System ROC General | 2026-03-31
ROC | March | NBET27, Rob P on site doing work orders, testing level alarms/temp alarms/sump alarms | All Water System ROC General | 2026-03-31
ROC | March | MAPS PD7, Placed pump 2/3 man/off VNPS PD7, Placed pump 1 in auto | All Water System ROC General | 2026-03-31
ROC | March | KSTP, Cl2 Emerg Vlv Closure Sys Fault/Active, notified Jerry Z, he will look into it | All Water System ROC General | 2026-03-31
ROC | March | BVPS - Dan B. called to request to deactivate duty so he can switch over to generator power for a test run. Dan informed he confirmed with Dan Z. and Jack P. Deactivated duty 1 at BVPS 13:43 - Placed pumps in man/off. During transfer, Discharge Total/Free Chlorine OOR and multiple suction VC fault alarms. Informed Patrick F. who is headed to site. CMU5 Created W11769868 #CMU5 | All Water System ROC General | 2026-03-31
ROC | March | YWS + NYWS Normal Adeela Khan signing out | All Water System ROC General | 2026-03-31
ROC | March | NMTKBS - Hi outlet flows. Called Ben H. who informed there is a WM break in the Town of Newmarket. Ben informed that he contacted the Town of Newmarket and operator has been dispatched. Ben also informed that an YR operator will also attend site 13:46 - Jason G. called back to inform that Town of Newmarket was able to isolate their main and NMTKBS is filling again | All Water System ROC General | 2026-03-31
ROC | March | SHTP/SHETCS, Power Outage, a blip occurred on both sites, Plant was running when the blip occurred, Plant shutdown. All alarms were able to be cleared, notified Cole W of the power outage on site consult | All Water System ROC General | 2026-03-31
ROC | March | MARS - Lo Level alarms came in. Deactivated duty 1 at AURSBS | All Water System ROC General | 2026-03-31
ROC | March | VNPSAP, Tim H on site, testing low temp and flood alarm. HLETYS, Tower is flat lining, contacted Artour L he is looking into it NMETIB, Historian Heartbeat Alarm, notified Artour L, he is looking into it | All Water System ROC General | 2026-03-31
ROC | March | MKRSEM - Request (Zoran) TO to run 2 pumps MARS - Request TO to go back to regular flow | All Water System ROC General | 2026-03-31
ROC | March | STW12/STW3 - Place well 1 & 3 back in auto as Zone 1 finished filling | All Water System ROC General | 2026-03-31
ROC | March | MAPS PD7, Placed pumps 2/3 man/off VNPS PD7, Placed pumps 1/3 in auto | All Water System ROC General | 2026-03-31
ROC | March | JSPS - Jerry Z finished at site, pumps restored. Informed of generator running at QVW34, okay to leave running for night. Will monitor. Infomred NMW15 man/off VNP7 - place remainder pumps man/off MAP8 - Place pump 3 auto | All Water System ROC General | 2026-03-31
ROC | March | QVW34 - Combined Chlorine Hi and Effluent Free Chlorine hi alarms came in. Checked site. Well is man/on. Called Ben H. who informed he is running the site in manual due to a high turbidity. Ben informed that if the well locks out, it can be left man/off for the night | All Water System ROC General | 2026-03-31
ROC | March | AUPSRR - Placed pumps back in auto | All Water System ROC General | 2026-03-31
ROC | March | HLETYS, Rick L/Parth P finished on site | All Water System ROC General | 2026-03-31
ROC | March | JFPS - WPS gen xfer switch, WPS pumps 2 & 3 fail to start. Unable to clear alarm as pump fail to start again. Pump 4 not comin on with duty. Ran in man/on as pump 1-3 fail to start. Infomred Jerry Z, will attend site CMU = 11770073 AUMCBS - Control panel power fail. Status went to normal RHRSTR - Site power fail alarm, control panel power failure. VNP8 - PROC sump pump 1 & 2 fault, able to clear alarm RHPSPA - Hydro power failure, able to clear HLW2 FCV2 - Cole W requested FCV2 back in duty 1 & monitor start up for any pressure or flow alarms. Will place well 2 back in duty 1 as well shortly after as requested Downstream pressure or no flow | All Water System ROC General | 2026-03-31
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-31
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-31
ROC | March | AURSBS, Deactivated D1 | All Water System ROC General | 2026-03-31
ROC | March | NMETIB - Historian Heartbeat Alarm came in. Called Artour L. who will take a look | All Water System ROC General | 2026-03-31
ROC | March | VNETAG, Tim H directed to call him if the hi/lo level alarms come in on site | All Water System ROC General | 2026-03-31
ROC | March | QVW34 - RIO control panel power failure, PAC control panel power failure. Generator running. Control panel power failure alarms cleared right away, generator running, will monitor site | All Water System ROC General | 2026-03-31
ROC | March | YWS + NYWS normal | All Water System ROC General | 2026-03-31
ROC | March | NMW136 - Well not avialbel, well 13 uncmd stop, able to reset. NMW15 - Well 15 VFD fault. left man/off | All Water System ROC General | 2026-03-31
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-31
ROC | March | Gluzen Ramos Ong signing out | All Water System ROC General | 2026-03-31
ROC | March | BVPS, Activated D1 | All Water System ROC General | 2026-03-31
ROC | March | Ethan U signing in Weather 14. | All Water System ROC General | 2026-03-31
ROC | March | Carter Dunn signing out | All Water System ROC General | 2026-03-31
ROC | March | GWTP- ZW1 Permeate Pump Uncommanded Stop, Shutdown. Notified Joe M. He will look into it. | All Water System ROC General | 2026-03-11
ROC | March | JFPS- Ernie H onsite. Requested to run Pump 1 in manual. Placed man/on. Placed pumps 3,4 in manual so would not start up in duty. Pump 2 already man/off. 11:51- Ernie H requested to stop pump and place back into auto. | All Water System ROC General | 2026-03-11
ROC | March | *Wrong Book Entry* | All Water System ROC General | 2026-03-04
ROC | March | NMTKKC - Ammonia Pump 1 failed to start alarm. Ammonia pump 1 faulting consistently on activation. Checked site, duty 1 rotated to ammonia pump 2 which is operating normally. Spoke with Joe W who stated that the ammonia pump 1 can be placed into manual off and he will inform the rest of area operations. Leaving alarm outstanding as there is a work order in place to have the pump inspected and fixed. | All Water System ROC General | 2026-03-04
ROC | March | MKETFA - Patrick F onsite testing low temp, working on LIT, and valve exercise. Requested TO (Peter) to stop pumping for valve work 12:02 - Request TO (Peter) to put pumps back to normal operations. | All Water System ROC General | 2026-03-11
ROC | March | YWS + NYWS NORMAL | All Water System ROC General | 2026-03-11
ROC | March | KSTP - Settl water Turbidity Hi alarm. Disregard alarm until morning as per Joe M. # Consult | All Water System ROC General | 2026-03-11
ROC | March | MKRSEM- Called Toronto and requested both pumps off. | All Water System ROC General | 2026-03-05
ROC | March | MKRSEM - Called Toronto water (Zoran) and requested stop filling Res. | All Water System ROC General | 2026-03-03
ROC | March | GWTP- Train 4 turbidity OOR/ fault alarms came in. Notified Joe M. Parth P is performing annual calibrations on trains 4/5 | All Water System ROC General | 2026-03-06
ROC | March | Ethan Ullalkar signing out. | All Water System ROC General | 2026-03-05
ROC | March | RHMCMD - Man/open 100% | All Water System ROC General | 2026-03-06
ROC | March | NMW12 - Silicate tank 1 level lolo alarm. Checked site, well is active and the silicate pumps have interlocked on the lolo level alarm. Deactivated duty 1 for NMTKKC to shut down the wells and called Joe D to inform. Joe D stated that Jason G is completing the Silicate top ups today. Will contact Jason G and request he visit NMW12 asap. | All Water System ROC General | 2026-03-10
ROC | March | VNPS PD7- Placed pump 3 in manual MAPS PD7- Placed pump 2 in auto | All Water System ROC General | 2026-03-11
ROC | March | YWS + NYWS Normal Connor Smith signing out | All Water System ROC General | 2026-03-05
ROC | March | MKPSSA - Danielle Z called and requested that the pumps at MKPSSA be exercised. MKRSMR duty 1 is almost active, called Toronto Water and requested they activate the duty early for MKRSMR. When the valves have rotated and the flow from Toronto has started, will exercise each pump at MKPSSA individually for fifteen minutes. | All Water System ROC General | 2026-03-02
ROC | March | RHRSTR/VNPS - Benson S on site for station checks and requested that the duty 1 for RHRSTR be activated to initiate flow into the reservoir. Activated duty 1 and monitored BVPS pump start. | All Water System ROC General | 2026-03-02
ROC | March | QVW34 - Treated total chlorine OOR, lolo alarm. Called Donald M confirming he is onsite. Ernie H replacing analyzer, taking out total. Wells local off isolated. | All Water System ROC General | 2026-03-12
ROC | March | STW12- Placed well 1 back into auto STW3- Placed well back into auto. STETBR Fill cycle complete | All Water System ROC General | 2026-03-05
ROC | March | STRS48 - High lift pump 1 fail to stop alarm. Checked site, system duty is not active but the pump is still pushing flow. Placed the pump in manual mode and tried to stop it. The pump remained on. Contacted Jack P who will attend site. Ian W from PCS completed OIT work at this site earlier today. Jack P requested that Ian be contacted to have him check whether the previous work may have impacted the SCADA logic for the high lift pump. Contacted Ian W who will check the system. 13:34 - STRS48 - jack P attended site and requested a CMU5. Created CMU5#W11722310 #CMU5 | All Water System ROC General | 2026-03-10
ROC | March | GWTP - High lift pump 2 emergency stop alarm. Joe M called to inform that he triggered the high lift pump 2 emergency stop. | All Water System ROC General | 2026-03-10
ROC | March | NBW2 - Jake M finished and leaving site. Jake directed to leave the well running in manual mode until 16:00. | All Water System ROC General | 2026-03-03
ROC | March | GWTP - Sutton header fluoride low alarm. Checked site, Sutton PRV is not open no flow into Sutton tower system. Trending shows the fluoride level dipped earlier in the morning and stayed low but is starting to recover. Will monitor site to determine if the value will recover before duty starts for SUETDR. | All Water System ROC General | 2026-03-04
ROC | March | GWTP - Joe M onsite working on GAC2 | All Water System ROC General | 2026-03-05
ROC | March | Connor Smith signing in 3 C Rain | All Water System ROC General | 2026-03-11
ROC | March | JFRS - Sean P outside valve house for valve actuator work | All Water System ROC General | 2026-03-11
ROC | March | YWS + NYWS NORMAL | All Water System ROC General | 2026-03-08
ROC | March | KSTP - CO2 adjusted pH LoLo alarm. Checked site, high lift pumps not active, plant not active and low lift pumps interlocked on the alarm. Trending indicates that there was a small dip of the adjusted pH value which is slowly recovering. Reset alarm when it passed the alarm setpoint. | All Water System ROC General | 2026-03-09
ROC | March | HLETYS - Tower Mixer VFD Fault alarm. Spoke with Cole W who stated that Tyler CS from maintenance will be attending site. | All Water System ROC General | 2026-03-04
ROC | March | KSTP - Jason G on site, draining Filter 1 for manual cleaning. Filter 1 off for the night. | All Water System ROC General | 2026-03-09
ROC | March | VNPSAP - Aaron CM from PCS called to inform he will be completing a reboot of the cellular modem for this location. Aaron stated the work would be best completed with pumps off. Deactivated the tower duty at VNETAG and confirmed pumps are off and the valve is closed before informing Aaron they can move forward with the reboot. | All Water System ROC General | 2026-03-04
ROC | March | VNRSKS - Swapped supply pumps to one MAPS pump and one VNPS pump. | All Water System ROC General | 2026-03-04
ROC | March | KSTP- Raw Water Turbidity Fault Alarm. Disregard as per SCADA Report | All Water System ROC General | 2026-03-05
ROC | March | VNPSAP/VNETAG, Aaron M from PCS is finished working on the signal on site, Trends for both sites are normal | All Water System ROC General | 2026-03-04
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-04
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-06
ROC | March | GWTP- Joe M requested to activate duty | All Water System ROC General | 2026-03-11
ROC | March | MAPSN1 SCADA Server Reset, Kingsley M called, will be resetting the server at 09:30 | All Water System ROC General | 2026-03-05
ROC | March | MARS - High level alarm. Activated AURSRS duty 1 to draw down the reservoir. YWS + NYWS Normal | All Water System ROC General | 2026-03-06
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-01
ROC | March | ARPS - Sam from Peel/OCWA control room called to inform that there is an operator changing the reagents for the chemical analyzer at ARPS and that he will be making the daily pump rotation at ARPS. No impact to YWS expected. | All Water System ROC General | 2026-03-03
ROC | March | *WRONG BOOK ENTRY* | All Water System ROC General | 2026-03-04
ROC | March | QVW34 - PAC Communication failure alarm came in. Checked site. Site came back within 2 mins and alarms cleared. Trending is okay | All Water System ROC General | 2026-03-09
ROC | March | GWTP- Eric S and Parth P on site for calibrations. Will speak with OPS on site before starting work RHRSTR- Benson S on site to do station checks. Req BVPS to be activated. Activated D1 | All Water System ROC General | 2026-03-06
ROC | March | NMETHW- Activated D1 at 45% to offset from NMETIB as per shift report | All Water System ROC General | 2026-03-06
ROC | March | RHPSPA - Generator Warning alarm came in. Checked site. Site is still connected to hydro power and generator is not running. Alarm is unable to clear. Not mentioned in the shift report. Will continue to monitor site. 03:35 - Called Ben H. who directed to disregard alarm #CONSULT | All Water System ROC General | 2026-03-02
ROC | March | BLW3- Travis W onsite for health and safety work orders and turbidimeter cleaning. | All Water System ROC General | 2026-03-02
ROC | March | YWS + NYWS NORMAL | All Water System ROC General | 2026-03-08
ROC | March | NMW136- Eric S onsite troubleshooting free chlorine analyzer. Placed well man/off | All Water System ROC General | 2026-03-10
ROC | March | NMW136- Treated Free Chlorine Hi Alarm. Value did not recover. Rotated Ammonia pumps so pump 1 in duty 1. Will monitor. 09:29- Joe D requested to rotate Ammonia Pump tanks and call if it does not come down in 20 minutes. 09:38- Joe D will go to site. 10:13- Joe D finished onsite. Instrumentation will attend. W11722182 CMU5 | All Water System ROC General | 2026-03-10
ROC | March | KLPSWL/ KLW34- Dave T onsite for work orders. Running generator, Cl analyzer maintenance, Health and Safety, Cl Leak detection, low temp, and flood alarm. | All Water System ROC General | 2026-03-10
ROC | March | NBW5 - Eric S finished at site NMW12 - Influent free chlorine hihi on startup | All Water System ROC General | 2026-03-11
ROC | March | AUW57- Joe D and Donald M onsite for chlorine cylinder change. | All Water System ROC General | 2026-03-02
ROC | March | QVW34 - Rick L & Parth P onsite for chlorine analyzer switching out Cl17 | All Water System ROC General | 2026-03-12
ROC | March | GWTP LL, Chris S on site removing the PAC on site, directed to disregard comm alarms until he has left | All Water System ROC General | 2026-03-05
ROC | March | QVETQS - Will M onsite cleaning analyzer for free and total | All Water System ROC General | 2026-03-05
ROC | March | GWTP/KSTP/SUETDR - John Demarco ready to initiate the network maintenance for the Keswick/Georgina/Sutton water systems. Contacted Dan Z to inform that the duty will be shut down for this work. Dan Z stated they will inform the area operators. | All Water System ROC General | 2026-03-10
ROC | March | NBW2 - Chris I onsite. Leaving well man/off to work on broken valve, isolating section | All Water System ROC General | 2026-03-06
ROC | March | YWS + NYWS Normal GWTP, ZW1 Performance Yesterday Lo Alarm, as per instructions/SOP, Sent email to on call operator and area so they are aware that this alarm did come in. | All Water System ROC General | 2026-03-08
ROC | March | MTW12 - Travis W on site to complete JHSC and station checks. | All Water System ROC General | 2026-03-02
ROC | March | AURSBS, Donald M on site, he is placing the chemical system offline, testing the Ammonia flood alarm, dehumidifier off/Cl2 leak detection, chemscan offline. Doing work orders for the site | All Water System ROC General | 2026-03-05
ROC | March | NMW136 - Alex B onsite putting well 13 in local, isolated, pulling silicate injection point MKETFA - Peter (TO) informed they are rotating pump 1 to duty 1 | All Water System ROC General | 2026-03-12
ROC | March | GWTP- Keswick Header Fluoride HiHi Alarm. High LIft Pump 1,2,3 Lockout Alarms. Called Joe M. No answer, informed that instrumentation is onsite for calibrations. | All Water System ROC General | 2026-03-11
ROC | March | NMW12 - Eric S on site to complete a button replacement on the CL17. Eric has requested that the well be deactivated. System duty is almost complete. Contacted Alex B to confirm the wells do not need to be on for other work orders. Deactivated NMTKKC duty to shut down NMW12. | All Water System ROC General | 2026-03-03
ROC | March | VNRSKS - Swapped supply pumps to two MAPS pumps to increase demand on MARS. | All Water System ROC General | 2026-03-03
ROC | March | NMVCBA - Placed valve in manual at 40 L/s 00:15 - Placed valve back to auto | All Water System ROC General | 2026-03-09
ROC | March | MKRSEM - Reservoir 1 Level Lo. Called Toronto Water (Paul) and requested 2 pumps on. 03:10 - Called Toronto Water (Paul) and requested to stop pumping to reservoir | All Water System ROC General | 2026-03-09
ROC | March | KSTP - Clearwell influent free CL2 res lo. Informed Donald M. Low lift turbidity reading high while low lifts off. Place raw water turbidity in calibration mode at request of Donald M. Donald M looking into issue and chlorine pumps | All Water System ROC General | 2026-03-12
ROC | March | ARPS- Jerry from Peel called and is switching from transfer pump 7 to pump 5 | All Water System ROC General | 2026-03-11
ROC | March | GWTP - Erick S & Parth P & Rick L onsite for annual calibrations | All Water System ROC General | 2026-03-12
ROC | March | MKPSSA - Patrick F running generator, flood alarm, analyzer maintenance GWTP - Joe M onsite with Jackie S working on UV maintenance | All Water System ROC General | 2026-03-12
ROC | March | Adeela Khan signing out | All Water System ROC General | 2026-03-04
ROC | March | SHTP- Filter 3 Post Rinse NIT High Alarm. Reset alarm as per SCADA Report | All Water System ROC General | 2026-03-04
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-05
ROC | March | NMVCBA- Placed valve in manual 20L/s to assist in keeping NMETIB and NMETHW offset. 01:15- Placed back into auto | All Water System ROC General | 2026-03-04
ROC | March | VNPS PD7- Placed pumps 1 and 2 in auto MAPS PD7- Placed Pump 2 in auto | All Water System ROC General | 2026-03-01
ROC | March | GWTP, Low Lift Drainage Pump 1 Overload Alarm, Still have 1 drainage pump available, notified Jack P, he will look into it 19:44, Jack P to disregard for the night since there is still 1 other pump available at this time. Jack P adjusted the hi level alarm from 4.0 to 4.1 and turned on the hi level alarm so that if the pump can't keep up with the drainage, there will be a notification to the ROC and the RO will contact Jack P consult | All Water System ROC General | 2026-03-06
ROC | March | AUW23/5, Placed wells man/off to take more water from AURSBS. This will help take more water from MARS | All Water System ROC General | 2026-03-07
ROC | March | YWS+NYWS normal | All Water System ROC General | 2026-03-07
ROC | March | AUPSWS - Lee F on site to complete vibration testing on the pumps and would like the duty 1 to be rotated from pump 5 to pump 4. Made the necessary duty change. | All Water System ROC General | 2026-03-12
ROC | March | MKRSMR - Artour L finished at site | All Water System ROC General | 2026-03-11
ROC | March | HLETYS - Activated duty 1 as per Tim H. | All Water System ROC General | 2026-03-02
ROC | March | YWS + NYWS NORMAL | All Water System ROC General | 2026-03-03
ROC | March | MTW3, Sean P/Ernie H working on the generator switch 10:52, Sean/Ernie are leaving site | All Water System ROC General | 2026-03-13
ROC | March | GWTP, Rick L/Eric S on site, doing annual calibrations | All Water System ROC General | 2026-03-13
ROC | March | VNRSKS - Swapped supply pumps to two MAPS pumps. | All Water System ROC General | 2026-03-09
ROC | March | VNRSKS - Swapped supply pumps to one MAPS pump and one VNPS pump to equalize the demand between RHRSTR and MARS. | All Water System ROC General | 2026-03-03
ROC | March | QVW34- Ben H called to imform wells will remain man/off. Can be used in an emergency. | All Water System ROC General | 2026-03-10
ROC | March | SUSP - UV channel 1 common critical alarm, UV channel 1 high level alarm and UV system critical failure alarm. Checked site, UV channel 2 is active. Trending shows that flow through the UV channel recently started. Shift report states these alarms trigger when flow starts and are a disregard. Cleared alarms. *Wrong book. Belongs in ROC Wastewater* | All Water System ROC General | 2026-03-10
ROC | March | VNPS PD7, Placed pumps 2/3 in man/off MAPS PD7, Placed pumps 2/3 in auto RHRSTR, Deactivated D1 | All Water System ROC General | 2026-03-13
ROC | March | YWS + NYWS Normal Carter D Signing Out | All Water System ROC General | 2026-03-13
ROC | March | KSTP, Fin Water Fluoride Res Hi, Notified Joe M and Ben H, they are looking into it | All Water System ROC General | 2026-03-13
ROC | March | YWS + NYWS normal | All Water System ROC General | 2026-03-13
ROC | March | Adeela Khan signing out | All Water System ROC General | 2026-03-13
ROC | March | SHTP - Treated water turbidity fault. Highlifts not running, plant is running. trend shows no value change for NTU last hour but on SCADA can see third decimal value change showing movement. Informed Jordan B of outstanding alarm, will wait till highlifts come on and see if able to clear fault. Will monitor 19:12 - Treated water turbidity hi, start up of highlifts shows increase in turbidity. Informed Jordan B, will head to site CMU = 11733253 20:33 - Jordan B finished at site. | All Water System ROC General | 2026-03-13
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-13
ROC | March | YWS + NYWS Normal Connor Smith signing out | All Water System ROC General | 2026-03-13
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-10
ROC | March | STETBR - Tower level hi alarm. Placed STW12 and STW3 in auto | All Water System ROC General | 2026-03-06
ROC | March | STW12 - Communication loss to STW12 alarm. STETL to STW12 Comm alarm. Notified Yash S. He will check SCADA. # CMU5 W11700739 11:36 Yash S called, communication restored. | All Water System ROC General | 2026-03-02
ROC | March | MKRSEM- Free Chlorine Residual Fault Alarm. Alarm cleared. | All Water System ROC General | 2026-03-11
ROC | March | NMTKKC - Outlet total CL2 lolo, reading within range able to clear alarm. No dips appear in trends. | All Water System ROC General | 2026-03-11
ROC | March | NMTKKC - Ammonia pump 1 uncommanded stop alarm. Checked site, ammonia pump 2 started on duty 1. Was able to clear alarm. Will monitor. | All Water System ROC General | 2026-03-03
ROC | March | AUW2/3/5, Placed wells man/off to help take water from AURSBS | All Water System ROC General | 2026-03-08
ROC | March | YWS + NYWS NORMAL | All Water System ROC General | 2026-03-10
ROC | March | MKRSEM - Called Toronto water (Paul) and requested to start filling Res. | All Water System ROC General | 2026-03-11
ROC | March | GWTP, Filter 2 Shutdown alarm/Filter 2 BW Exceeded duration alarm, notified Jack P, he will look into it, directed to place the filter 2 off for the time being consult | All Water System ROC General | 2026-03-07
ROC | March | MAPS PD7, Placed pump 2 man/off VNPS PD7, Placed pump 3 in auto | All Water System ROC General | 2026-03-14
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-14
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-14
ROC | March | GWTP - ZW1 Permeate Pump Uncommanded Start and ZW1 Shutdown alarms came in. Checked site. Called Jack P. who directed to ack/reset permeate pump alarm and then directed to place the train mode off and then back on. Both alarms have cleared #CONSULT | All Water System ROC General | 2026-03-10
ROC | March | AURSOH - Joe D finished at site | All Water System ROC General | 2026-03-12
ROC | March | Christian Van Beek signing in. | All Water System ROC General | 2026-03-13
ROC | March | YWS + NYWS NORMAL | All Water System ROC General | 2026-03-15
ROC | March | YWS + NYWS NORMAL Angelica Chepiga signing out | All Water System ROC General | 2026-03-09
ROC | March | GWTP - ZW3 membrane tank level hi alarm. Checked site, train 3 is going through a chemical clean process. Trending shows the filter level is slightly above the hi alarm setpoint. Filter level will drop as the cleaning sequence progresses | All Water System ROC General | 2026-03-09
ROC | March | YWS + NYWS Normal Connor Smith signing out | All Water System ROC General | 2026-03-11
ROC | March | VNPS7 - Place pumps 1 & 2man/off MAP7 - Place pump 3 in auto. Done to slow demand pulling from MARS | All Water System ROC General | 2026-03-12
ROC | March | Angelica Chepiga signing out | All Water System ROC General | 2026-03-08
ROC | March | Connor Smith signing in -1C windy | All Water System ROC General | 2026-03-12
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-12
ROC | March | AUW14- Joe D called and requested all wells man/on for sampling | All Water System ROC General | 2026-03-11
ROC | March | NMVCBA, Placed valve in manual and set it to 40L/sec | All Water System ROC General | 2026-03-15
ROC | March | NMVCBA, Placed valve back to auto | All Water System ROC General | 2026-03-16
ROC | March | STW2/3, Placed wells back to auto | All Water System ROC General | 2026-03-16
ROC | March | GWTPLL, Low Lift Surge Relief Valve Open alarm, Came in on Plant shutdown, Past elogs showed the alarm can be reset, will wait 15 minutes and then reset 03:09, Alarm has cleared | All Water System ROC General | 2026-03-16
ROC | March | RHRSTR, Deactivated D1 so more water moves from MARS to RHRSTR | All Water System ROC General | 2026-03-16
ROC | March | NMTKKC- Kingsley M performing server reboot. Requested to have tank topped up. Confirmed with Jason G and activated duty | All Water System ROC General | 2026-03-02
ROC | March | QVW34 - Donald M informed testing of Flood containment alarm | All Water System ROC General | 2026-03-12
ROC | March | RHRSWA - Ian W. informed that he is working on the OIT and requested to disregard the Historian Heartbeat alarm 14:25 - Ian informed that he is finished working on the OIT | All Water System ROC General | 2026-03-13
ROC | March | YWS + NYWS Normal HLW2, Ammonia pump 1 fault, placed pump man/off for the time being, emailed on call operator/area to let them know | All Water System ROC General | 2026-03-14
ROC | March | NMETHW, Activated D1 to have the towers offset | All Water System ROC General | 2026-03-14
ROC | March | KLPS27/KLET27 - Yash S on site to complete the scheduled PCS network maintenance. Deactivated tower duty to shutdown the pumps for the duration of the maintenance. | All Water System ROC General | 2026-03-04
ROC | March | Carter Dunn Signing In, 16D/Rain | All Water System ROC General | 2026-03-07
ROC | March | KLET27, KLMCHR, KLMCIA, KLPS27, KLPSWL, KLW34, NBETRS, NBET27, NBW2, NBW3, NBW5 - Kingsley M completing a Hub 5 server restart. No impact to operations. | All Water System ROC General | 2026-03-03
ROC | March | HLW1 - Treated free chlorine hi. Ammonia pump 1 running. Informed Jordan B as known issue with this ammonia pump. Place ammonia pump 2 duty 1. Place ammonia pump 1 man/off | All Water System ROC General | 2026-03-11
ROC | March | MARS, Contacted Toronto operator Paul to increase the flow to MARS | All Water System ROC General | 2026-03-14
ROC | March | KSTP, Fin Water Fluoride Res Hi Alarm, Notified Joe M, directed to disregard as plant just started up | All Water System ROC General | 2026-03-14
ROC | March | VNMVYS- Ric L onsite troubleshooting flow meter. | All Water System ROC General | 2026-03-10
ROC | March | Christian Van Beek signing out. | All Water System ROC General | 2026-03-06
ROC | March | GWTP - Rick L on site to complete annual calibrations at the low lift building. | All Water System ROC General | 2026-03-02
ROC | March | Ethan U signing in Weather 0. | All Water System ROC General | 2026-03-14
ROC | March | YWS + NYWS Normal Carter Dunn Signing Out | All Water System ROC General | 2026-03-14
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-14
ROC | March | SHTP - Well pump 2 uncommanded start alarm. Checked site, plant is not active. Well pump 2 is not active. Trending shows the plant recently shut down. Able to clear alarm. SHTP - Site power failure and generator running status alarms. SCADA shows the ATS in local connected to the generator indicating this is an operator activated test. Jen S is on site. Alarms cleared locally. Plant not active. MTW12/MTW3 - Placed well pumps in auto following the completion of the historian trend maintenance. STRS48 - High lift pump 1 failed to stop alarm. Alarm triggered when the system was deactivated in preparation for the Historian trend maintenance. Able to reset alarm. | All Water System ROC General | 2026-03-03
ROC | March | SHTP - High lift pump 4 fault. Checked site, high lift pump 4 is local off. STW3 - Jack P on site to complete chemical system inspections including turbidity analyzer, Chlorine analyzer and silicate system. | All Water System ROC General | 2026-03-10
ROC | March | Carter D Signing Out | All Water System ROC General | 2026-03-04
ROC | March | Christian Van Beek signing out. | All Water System ROC General | 2026-03-03
ROC | March | GWTP - Sutton header fluoride low alarm. Checked site, when the alarm triggered there was no flow to the Sutton system. Trending shows a dip of the fluoride reading which recovered. Cleared alarm. | All Water System ROC General | 2026-03-10
ROC | March | NMW12 - Christian B. called to inform that he is on site with Alex B. and they will be completing PM's. These include testing the Chlorine Detection, Chlorine Analyzer maintenance, ammonia inspection and Turbidimeter maintenance | All Water System ROC General | 2026-03-04
ROC | March | GWTP, Rick L/Eric S is finished on site | All Water System ROC General | 2026-03-05
ROC | March | VNPS PD7, Placed pump 2 man/off MAPS PD7, Placed pumps 2/3 in auto MARS is on the higher end, trying to help draw it back down for night shift RO | All Water System ROC General | 2026-03-05
ROC | March | QVETQS, Comb Inlet Cl2 lo alarm, tower is filling, notified Donald M as this could affect the outlet since the residual has dropped quite a bit and is on a constant decline, Reason for drop in Residual is due to the work that was happening at QVW12, Donald M will look into the situation 20:02, Donald M called back, Operator placed the tie valve man/open. directed to place the valve back to auto either at 10PM or if the residual goes back to normal level. Also notified the RO that he would like QVW3 to also go back to auto at 10PM. 21:02, Placed tie valve back to auto as per Donald M instructions, the residuals have come back to normal range 21:09, Inlet Free Cl2 hihi Switch Alarm, HMA alarm/High Priority, contacted Donald M as this may be caused by his earlier work, he will look into it 21:18, Directed to disregard at this time, if the hihi alarm comes in, he will attend site consult | All Water System ROC General | 2026-03-06
ROC | March | Christian Van Beek signing out | All Water System ROC General | 2026-03-12
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-03
ROC | March | Christian Van Beek signing in. | All Water System ROC General | 2026-03-04
ROC | March | MAPS - Tim H onsite running diesel, testing diesel spill, and eyewash alarms | All Water System ROC General | 2026-03-05
ROC | March | AUW14 - Joe D running generator. Wells placed man/off | All Water System ROC General | 2026-03-05
ROC | March | KCETDS - Metering chamber flood. Informed Jordan B, disregard for the night will drain it out in the morning Consult | All Water System ROC General | 2026-03-12
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-12
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-12
ROC | March | SHTP- FILT 1 Turbidity Hi, Filter 3 Turbidity Hi Alarms. Backwash just completed. Disregard as per SCADA report | All Water System ROC General | 2026-03-13
ROC | March | H1GWTPP1 - Chris S restarting serve. QVW12 - Lee F onsite looking to check waste valve issue. Activated duty as near duty start Hub2 - Kingsley M restarting server | All Water System ROC General | 2026-03-05
ROC | March | MKRSEM - Called Toronto Water (Mehdi) and requested they deactivate the pumps pushing flow to MKRSEM. | All Water System ROC General | 2026-03-06
ROC | March | VNMCYS - Kevin W called to inform he is re-booting the APN for this site. No impact to operations expected. | All Water System ROC General | 2026-03-09
ROC | March | RHRSTR - Deactivated duty 1. | All Water System ROC General | 2026-03-09
ROC | March | NBW2 - Historian heartbeat alarm, able to clear | All Water System ROC General | 2026-03-06
ROC | March | AUW5- Joe D onsite for work orders including Cl analyzer and turbidimeter maintenance, and Cl Leak. | All Water System ROC General | 2026-03-10
ROC | March | HLETYS - Tower Mixer uncommanded stop alarm came in. Checked site. Tower is still filling. Ack/reset alarm and alarm cleared. Will monitor | All Water System ROC General | 2026-03-01
ROC | March | YWS + NYWS NORMAL | All Water System ROC General | 2026-03-10
ROC | March | MARS - Tim H onsite for cleaning analyzer, & hi/lo level | All Water System ROC General | 2026-03-11
ROC | March | AUW57 - Joe D. called and requested to place the well back to auto. Well is now running in auto | All Water System ROC General | 2026-03-13
ROC | March | NMW136, Placed well 13 back to auto | All Water System ROC General | 2026-03-13
ROC | March | Ethan U signing in Weather -0. Snowing | All Water System ROC General | 2026-03-13
ROC | March | NMETHW - Activated Duty 1 @ 43% to offset NMETIB. | All Water System ROC General | 2026-03-08
ROC | March | YWS + NYWS NORMAL | All Water System ROC General | 2026-03-08
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-15
ROC | March | STW12 - Well 1 pump fault alarm. Generator running alarm. Placed Well 1 pump man/off. STPSTL - Generator running alarm. Power outage, pumps stopped and restarted. ATS switch in local mode. BLW12 - Pump 1 VFD fault alarm after power blip. Placed Pump 1 man/off. Duty not active. STW3 - Well 3 pump was running in manual, power blip, pump stopped. No outstanding alarms. Placed P3 to auto, restarted ok. 12:44 BLW12 - Generator running alarm. 12:45 Checked Hydro one website. Power outage in the area. BLW12 - ETR 15:30, STW12 - ETR 15:30. ATS switch at STPSTL back in auto. # Notified Joe M. | All Water System ROC General | 2026-03-15
ROC | March | STRS48 - Sample pump 1 fault alarm. Sample pump 2 is running, will monitor. | All Water System ROC General | 2026-03-15
ROC | March | NMETIB - Activated Duty 1 to offset NMETHW. | All Water System ROC General | 2026-03-15
ROC | March | MARS - Tim H onsite for cleaning analyzer, & hi/lo level KSTP - Fin water flouride res hi near startup, reading came down within range | All Water System ROC General | 2026-03-11
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-13
ROC | March | Angelica Chepiga signing in,weather -4C | All Water System ROC General | 2026-03-15
ROC | March | STW12 - Power restored. Generator stopped. Assigned Well 2 pump to Duty 1/ placed man/on for STETBR fill cycle. | All Water System ROC General | 2026-03-15
ROC | March | STPSTL - Power restored/generator stopped. | All Water System ROC General | 2026-03-15
ROC | March | YWS + NYWS NORMAL | All Water System ROC General | 2026-03-15
ROC | March | YWS + NYWS NORMAL | All Water System ROC General | 2026-03-15
ROC | March | VNPS PD7- Placed P3 man/off MARS PD7 - Placed P3 to auto. To help maintain MARS and RHRSTR levels. | All Water System ROC General | 2026-03-15
ROC | March | GWTP - Joe M on site to complete maintenance on the turbidity sensors of all the membrane trains and to complete a chlorine system inspection. Joe M directed to disregard the associated alarms. HLW2 - Influent free chlorine hihi alarm. Checked site, well is active. Tim H signed in on site and recently completed a chlorine cylinder change. | All Water System ROC General | 2026-03-03
ROC | March | ANW23 - Sean P completed with his ATS testing. Activated reservoir duty 1 and monitored well activation. | All Water System ROC General | 2026-03-03
ROC | March | QVETQS, Residual at the tower is dropping slowly, QVW12 is filling and putting out good residuals. Earlier Donald M had to go to site to work on the chlorinators which did have low residuals. As a game plane on what RO did last night, opened up the tie valve at QVETQS to not fill the tower with bad water. Will continue to monitor site. Notified Donald M for a game plan just incase the inlet does drop. Donald M requests a call if the inlet does drop to the low low level alarm 20:25, Placed tie valve back to auto, residuals are back to normal levels consult | All Water System ROC General | 2026-03-07
ROC | March | STW3 - Running in auto. Zone 1 filling, placed well man/on | All Water System ROC General | 2026-03-11
ROC | March | KSTP - Raw water turbidity fault. Disregard as per shift report | All Water System ROC General | 2026-03-14
ROC | March | NMETIB, Activated D1 to keep the towers offset | All Water System ROC General | 2026-03-14
ROC | March | MAPS PD7- Placed pump 2 to man/off VNPS PD7- Placed pump 2 to auto. | All Water System ROC General | 2026-03-15
ROC | March | STW12, STW3- Placed well 1 and well 3 pumps man/on for STETBR fill cycle. | All Water System ROC General | 2026-03-15
ROC | March | YWS + NYWS NORMAL | All Water System ROC General | 2026-03-15
ROC | March | ARPS -David from OCWA called. Completing daily pump duty rotation, from Pump 7 to Pump 6. | All Water System ROC General | 2026-03-15
ROC | March | MARS - High level alarm. Placed VNPSPD7P2 man/off, MARS PD7 pump 2 back to auto and activated Duty 1. | All Water System ROC General | 2026-03-15
ROC | March | BLW12 - Site back to normal OP, Joe M leaving site. | All Water System ROC General | 2026-03-15
ROC | March | YWS + NYWS NORMAL | All Water System ROC General | 2026-03-15
ROC | March | Angelica Chepiga signing out | All Water System ROC General | 2026-03-15
ROC | March | SHTP - Well pump 2 uncommanded start alarm. Checked site, plant is not active. Well pump 2 flow recently stopped. Cleared alarm. | All Water System ROC General | 2026-03-03
ROC | March | MTW3- Travis W on site for turbidity analyzer maintenance | All Water System ROC General | 2026-03-06
ROC | March | KSETDP - Phil D onsite with Chris S. Chlorine E-stop, chlorine analyzer, & halogen alarms and cylinders | All Water System ROC General | 2026-03-06
ROC | March | NBW2 - Chris I finished at site. Well back in auto | All Water System ROC General | 2026-03-06
ROC | March | YWS + NYWS normal Adeela Khan Signing Out | All Water System ROC General | 2026-03-09
ROC | March | Christian Van Beek signing in. | All Water System ROC General | 2026-03-09
ROC | March | wrong book | All Water System ROC General | 2026-03-02
ROC | March | STRS48/STPS48, Jack P on site running the generator, doing analyzer maintenance and working on the turbidity analyzers | All Water System ROC General | 2026-03-05
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-01
ROC | March | YWS + NYWS NORMAL | All Water System ROC General | 2026-03-02
ROC | March | NMW12 - Christian B onsite with Alex B pulling injector lines for silicate | All Water System ROC General | 2026-03-05
ROC | March | KSETDP - Post injection free and combined chlorine lolo alarms are still active. Contacted Phil D who stated that these alarms will be disregarded and outstanding until maintenance can attend site. Requested that Phil D has these alarms added to the shift report. | All Water System ROC General | 2026-03-02
ROC | March | STPSMR - Historian Heartbeat Alarm. Checked site, pump was active when alarm came in. Alarm cleared on an acknowledge and reset. Pumps activated but trends are now showing "No Data" shutdown the pumps in manual mode. Called Yash S who will check the system. Created CMU5#W11702333 #consult #CMU5 | All Water System ROC General | 2026-03-03
ROC | March | NBW5, Yash S resetting OIT on site, well is currently man/off | All Water System ROC General | 2026-03-05
ROC | March | AUW57, Joe D is leaving site | All Water System ROC General | 2026-03-05
ROC | March | MAP8 - Pump 2 discharge valve failed to open and Pump 2 failed to start alarms came in. Checked site. Duty recently activated. This fault inhibited the pumps. After 10 mins, the pumps rotated duty so pump 2 is no longer in duty 1. Alarms and inhibit cleared and pump 1 and 3 started up. | All Water System ROC General | 2026-03-04
ROC | March | SHETCS - Tim H heading to site later this morning to complete chlorine analyzer maintenance and test the high/low temperature alarms. | All Water System ROC General | 2026-03-10
ROC | March | Carter Dunn Signing Out | All Water System ROC General | 2026-03-05
ROC | March | Ethan U signing in | All Water System ROC General | 2026-03-05
ROC | March | YWS+NYWS normal Adam Button signing out | All Water System ROC General | 2026-03-06
ROC | March | NMVCBA - Placed valve in man at 40 L/s 00:05 - Placed valve back to auto | All Water System ROC General | 2026-03-08
ROC | March | MMW1-Kyle C called ROC for update on site. Notified Kyle C that Sean P is attempting to restore power to site via generator and that the ROC will contact Kyle C if outstanding historian heartbeat alarm is not able to clear or if any other alarms are outstanding. NBW3- Influent free Cl2 lolo alarm came in on scheduled start up. Reset alarms after 6 mins and monitored well start up | All Water System ROC General | 2026-03-07
ROC | March | MMW1- Rob P. Notified ROC wells are back on and station is running on generator. Called Kyle C about outstanding historian heartbeat alarm. Created CMU5 W11714725 #CMU5 | All Water System ROC General | 2026-03-07
ROC | March | NBW5 - Silicate pump 2 uncommanded start and Turbidity Hi alrms, Jacob M working on site. | All Water System ROC General | 2026-03-09
ROC | March | QVW12 - Noticed NMETHW duty is active but no duty 1 well was available. Called Will M. to confirm sampling was finished as the wells were left in manual. Will informed that he is finished on site and requested to place wells back to auto | All Water System ROC General | 2026-03-04
ROC | March | NMETIB - activated D1 to offset NMETHW | All Water System ROC General | 2026-03-08
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-09
ROC | March | JFPS- Benson S onsite for generator run, flood test, hi/low temp, health and safety and valve exercise. | All Water System ROC General | 2026-03-10
ROC | March | MAPS PD7- Placed pump 3 man/off VNPS PD7- Placed pump 3 in auto | All Water System ROC General | 2026-03-01
ROC | March | MKRSEM- Called Toronto (Mehdi) and requested pumps on. | All Water System ROC General | 2026-03-01
ROC | March | KLMCHR - Vaughan Pressure HiHi alarm came in. Checked site. Checked MARS. TMC317 has been pushing 42 ML/d since around 2:05 AM. Called Paul at Toronto Water who informed a pump had started in auto. Paul informed that he will shut that pump down and go back to normal flows 03:53 - KLMCHR - Pressure went back to normal range and alarm cleared | All Water System ROC General | 2026-03-02
ROC | March | KLPS27, KLET27 - Jen S. doing cl analyzer maintenance, testing flood and temp alarms. GWTP - Yash S. informed finished with network, he will notify ops. Left HLP man/off | All Water System ROC General | 2026-03-10
ROC | March | STETBR - Hi level alarm, placed STW12 pump 2 and STW3 back to auto. | All Water System ROC General | 2026-03-03
ROC | March | NMW15 - Treated free chlorine hi. Alarm triggered earlier this morning on well activation. Alarm was addressed by area operations and ROC operator Ethan U. Alex B and Donald M attending site to inspect the ammonia pumping system. Created CMU5#W11701894 at the request of Alex B. #CMU5 | All Water System ROC General | 2026-03-03
ROC | March | Christian Van Beek signing out | All Water System ROC General | 2026-03-02
ROC | March | YWS + NYWS NORMAL | All Water System ROC General | 2026-03-03
ROC | March | NMW15 - treated free hihi, combined chlorine lo. Rotated ammonia pump 1 to duty 1. Readings came back down. Noticed central ops rotated ammonia pump back. Reading back to normal. Issue came back with free chlorine. Well was placed man/off | All Water System ROC General | 2026-03-03
ROC | March | BLW34 - Travis W on site to complete a generator test with a contractor, no ATS activation. Travis will also be completing chlorine and turbidity analyzer maintenance. | All Water System ROC General | 2026-03-03
ROC | March | AUW57 - Treated free chlorine residual Hi alarm at duty startup. Alarm cleared. | All Water System ROC General | 2026-03-02
ROC | March | GWTP - sodium, hypo tank level hihi. Chemical delivery scheduled for today. | All Water System ROC General | 2026-03-03
ROC | March | AUPSRR - Donald M on site to complete a chlorine leak detection test. | All Water System ROC General | 2026-03-10
ROC | March | MARS- Called Toronto (Mehdi) and requested to revert back to normal flow VNPS PD7- Placed Pump 3 in manual MAPS PD7- Placed Pump 3 in auto | All Water System ROC General | 2026-03-10
ROC | March | GWTP- Jack P heading to site Created CMU5 W11714562 #CMU5 | All Water System ROC General | 2026-03-06
ROC | March | MAP7 - place pump 3 man/off VNP7 - Place pump 2 auto. Change made to help assist with demand from MARS | All Water System ROC General | 2026-03-05
ROC | March | AUPSWS- PAC control panel power fail alarm came in. Cleared upon acknowledgement pump 4 running okay . | All Water System ROC General | 2026-03-07
ROC | March | STW12/3- Placed well 1/3 man/on as per interim | All Water System ROC General | 2026-03-07
ROC | March | Adeela Khan signing in. Weather: -11C and Sunny | All Water System ROC General | 2026-03-01
ROC | March | MARS- Called Metro spoke with Zorhan to increase flow VNPS PD7- Placed P2 in man/off MAPS PD7- Placed P2 in auto | All Water System ROC General | 2026-03-07
ROC | March | MAPS- Air handling unit compressor fault outstanding. Notified Dave T directed to call if VFD room temp hi comes in JFPS- Res temp alarm came in. Notified Donald M directed to disregard #consult | All Water System ROC General | 2026-03-07
ROC | March | MMW1- Kyle C was able to restore trends on site. | All Water System ROC General | 2026-03-07
ROC | March | NBW5 - Pump uncommanded stop alarm. Called Jake M who stated he is on site and will be decreasing the flow setpoint before re-activating the pump and monitoring system. | All Water System ROC General | 2026-03-04
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-02
ROC | March | NBW5 - Turbidity high alarm. Well recently activated. Will monitor site. | All Water System ROC General | 2026-03-08
ROC | March | SHTP - KMNO Pump 2 Uncommanded stop alarm. Duty rotated, Pump 1 running on duty 1. Was able to clear alarm. | All Water System ROC General | 2026-03-03
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-07
ROC | March | Angelica Chepiga signing in,weather +5C | All Water System ROC General | 2026-03-11
ROC | March | VNMCYS- PAC comm fail on site alarm cleared upon acknowledgement | All Water System ROC General | 2026-03-07
ROC | March | GWTP, UV Reactor 1 Start/Stop Fault//uncommanded stop and a UV Comm alarm came in, notified Jack P, he is looking into it consult | All Water System ROC General | 2026-03-07
ROC | March | AUW2/3/5, Placed wells back to auto RHRSTR, Deactivated D1 | All Water System ROC General | 2026-03-08
ROC | March | Carter D Signing Out | All Water System ROC General | 2026-03-08
ROC | March | HLETYS - Benson S. called back and requested to place the start setpoint at the tower from 25% back to 35% | All Water System ROC General | 2026-03-01
ROC | March | YWS + NYWS NORMAL | All Water System ROC General | 2026-03-11
ROC | March | ARPS -Benish from OCWA called, Completing daily pump duty rotation. Will run pump 4 for 2 hours and switch to pump 5 after. | All Water System ROC General | 2026-03-09
ROC | March | VNPSCD - Benson S on site to complete station checks and requested that the RHRSTR duty be activated so that BVPS pumps start and push flow into RHRSTR to activate the chemical system. Activated RHRSTR duty 1. | All Water System ROC General | 2026-03-09
ROC | March | NMVCBA-Placed valve manual 30L/s to assist in NMETHW and NMETIB offset 00:29- Placed valve back to auto | All Water System ROC General | 2026-03-12
ROC | March | KSTP- Raw Water Turbidity Fault. Disregard as per SCADA Report. | All Water System ROC General | 2026-03-12
ROC | March | KLMCIA - Security Intrusion and Meter Chamber Flood alarms came in. Shift report indicates that the site is OOS. Called Rob P. who directed to disregard alarms and someone will attend site tomorrow to pump down the chamber. Rob informed that the security intrusion and meter chamber flood alarms are tied together and come in at the same time #CONSULT | All Water System ROC General | 2026-03-08
ROC | March | GWTP - PLC-3 (LLP) Permissive to Run Lost alarm. Called Joe M, no response. Sent message, will call again. GWTPLL - Permissive to Run Lost alarm, Joe M draining GAC4. | All Water System ROC General | 2026-03-09
ROC | March | AUW57 - Combine chlorine residual low alarm after duty stop, no water directed to users, residual recovered in 8 minutes. Alarm cleared. | All Water System ROC General | 2026-03-02
ROC | March | YWS + NYWS NORMAL | All Water System ROC General | 2026-03-11
ROC | March | NMMCBR - Created CMU5#W11719262 for Rob P at the request of Dwayne L. #CMU5 | All Water System ROC General | 2026-03-09
ROC | March | STW3- Placed well back into auto for STETBR fill cycle completion | All Water System ROC General | 2026-03-13
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-13
ROC | March | STETBR - Low level alarm. Man/started Well 3 pump. | All Water System ROC General | 2026-03-08
ROC | March | QVW34 - Chris I finished on site. Generator back to normal OP. | All Water System ROC General | 2026-03-09
ROC | March | STRS48 - Ian W on site to complete work on the OIT and has directed to disregard the associated historian heartbeat alarm. | All Water System ROC General | 2026-03-09
ROC | March | STW12 - Effluent turbidity Hi alarm. Pumps placed man/off earlier today, no water directed to users. | All Water System ROC General | 2026-03-09
ROC | March | GWTP - Sutton header fluoride low alarm. Value has recovered with no actions taken. Cleared alarm. | All Water System ROC General | 2026-03-04
ROC | March | MTW12/MTW3 - Place wells man/off STW3 - Place back auto STETTL - Deactivate duty 1 STETBR - Deactivate duty 1. Done as preemptive response to network trend maintenance impacting those sites. | All Water System ROC General | 2026-03-03
ROC | March | NMTKKC- Chloramine Analyzer Offline Alarm. Joe W onsite performing analyzer hot flush. | All Water System ROC General | 2026-03-02
ROC | March | GWTP- RIc L finished onsite. | All Water System ROC General | 2026-03-02
ROC | March | KSTP - Joe M called, he started filter 1 backwash, requested High lift Pump back to auto. Joe M will notify OP. | All Water System ROC General | 2026-03-12
ROC | March | YWS + NYWS NORMAL | All Water System ROC General | 2026-03-12
ROC | March | NMTKKC - Chloramine analyzer offline alarm. Checked site, Joe W signed into facility in the logbook. SCADA shows the chemical system is all manual/off. The Chloramine analyzer offline alarm changed to Normal status and cleared on acknowledgement. Called Joe W, no answer. Will monitor site and wait for reply. | All Water System ROC General | 2026-03-09
ROC | March | YWS + NYWS normal | All Water System ROC General | 2026-03-10
ROC | March | Christian Van Beek signing in. Weather: 10C and clear. | All Water System ROC General | 2026-03-10
ROC | March | Christian Van Beek signing in. Weather: -3C and clear. | All Water System ROC General | 2026-03-12
ROC | March | Ethan U signing in | All Water System ROC General | 2026-03-12
ROC | March | MKRSEM - Request TO (Peter) to drop both pumps | All Water System ROC General | 2026-03-12
ROC | March | VNP7 - Place pump 2 auto MAP7 - Place pumps man/off | All Water System ROC General | 2026-03-12
ROC | March | VNRSKS - Swapped supply pumps from two MAPS pumps to one MAPS and one VNPS pump to equalize demand on MARS and RHRSTR. | All Water System ROC General | 2026-03-13
ROC | March | KSTP- Raw Water Turbidity Fault Alarm. Disregard as per SCADA Report | All Water System ROC General | 2026-03-11
ROC | March | QVW12 - Sean P on site to complete a generator load bank test. | All Water System ROC General | 2026-03-12
ROC | March | MARS- Cell1 (North) Lvl Lo Alarm AURSBS- Deactivated duty | All Water System ROC General | 2026-03-01
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-01
ROC | March | QVW12 - Will M on site to complete a chlorine leak detection test. | All Water System ROC General | 2026-03-10
ROC | March | MAPS PD7 - Placed the active pump (Pump 3) in manual mode and deactivated to reduce the demand on MARS while ARPS is down. VNPS PD7 - Placed pump 3 in auto mode and monitored start up. MARS - Called Toronto Water and requested additional flow to MARS through TMC317 while ARPS is down. NMW136 - Eric S completed his work on site and leaving | All Water System ROC General | 2026-03-10
ROC | March | KSTP - Filter 1 and Filter 2 Backwash is out of services alarms. Jerry Z is signed into the facility logbook. MWW1 - Tyler ZJ on site and will be turning off the temporary generator to complete some wiring changes. Estimated work duration is thirty minutes. | All Water System ROC General | 2026-03-10
ROC | March | STPSMR - Dan B onsite working on fan exhaust | All Water System ROC General | 2026-03-11
ROC | March | GWTP- Jackie S called and is filling GAC4 and placing turbidimeter back into service. | All Water System ROC General | 2026-03-11
ROC | March | GWTP - Chris S called to inform he will be completing a server restart for GWTP. Chris will contact operations to ensure there is no impact to operations. Plant is currently offline for UV system work. | All Water System ROC General | 2026-03-12
ROC | March | KCPSDS - Benson S. informed that if the hypo pump 2 fails to start alarm comes back in, place the pump in manual and send an email. | All Water System ROC General | 2026-03-01
ROC | March | GWTP - Outstanding High Lift Free Chlorine Lo alarm. Plant recently started up. Free chlorine Levels are still low. Called Stephen B. who informed that this alarm can be disregarded. Stephen informed he would like a call back for any clearwell related alarms and if the keswick and sutton free chlorine line starts to drop. #CONSULT | All Water System ROC General | 2026-03-01
ROC | March | VNRSKS - Deactivated duty and switched pumps from VNPS PD7 to MAPS PD7 | All Water System ROC General | 2026-03-01
ROC | March | KSETDP - Post injection free chlorine lolo and combined chlorine lolo alarms. Checked site, outlet analyzer reading stable and normal values while the post injection analyzer showing abnormal values. Facility logbook shows Phil D on site for flushing to waste and to bring the tower online. Phil D still logged in indicating he is on site. Phil D collected grab samples which show normal range for free and total chlorine. | All Water System ROC General | 2026-03-02
ROC | March | KSTP- CO2 Adjusted pH LoLo Alarm. Notified Jerry Z. he will look into it. 14:40- Jerry Z cleared alarm | All Water System ROC General | 2026-03-10
ROC | March | VNRSKS - Swapped supply pumps from one VNPS and one MAPS pump to two MAPS pumps to increase demand on MARS. | All Water System ROC General | 2026-03-10
ROC | March | YWS + NYWS Normal Connor Smith signing out | All Water System ROC General | 2026-03-10
ROC | March | NMVCBA - Placed valve in man/open at 30 L/s | All Water System ROC General | 2026-03-02
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-04
ROC | March | QVW34 - Treated Toral chlorine low alarm. Wells off, no water directed to users. Value recovered in two readings. Alarm cleared. | All Water System ROC General | 2026-03-08
ROC | March | YWS + NYWS NORMAL | All Water System ROC General | 2026-03-08
ROC | March | NBW37- Influent free Cl2 lolo alarm on Schedule mode start up. Influent free chlorine residual recovered, cleared alarm and restarted well pump 7 on schedule mode. | All Water System ROC General | 2026-03-08
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-09
ROC | March | VNRSKS - swapped supply pumps to one VNPS pump and one MAPS pump to equalize the draw on MARS and RHRSTR. | All Water System ROC General | 2026-03-09
ROC | March | EGMCDD - Arthur L on site to complete commissioning of new instruments on site. Arhtur requested that alarms be disregarded from this site. | All Water System ROC General | 2026-03-03
ROC | March | AUW57 - Free chlorine hi, rotate ammonia pump 2 duty 1, reading came down AUW14 - Joe D onsite placing wells man/off. Working on chlorine analyzer, turbidimeter, chlorine leak. | All Water System ROC General | 2026-03-03
ROC | March | MKRSEM- Artour L. onsite working on PAC. No impact to operations | All Water System ROC General | 2026-03-11
ROC | March | YWS + NYWS Normal Christian Van Beek signing out. | All Water System ROC General | 2026-03-04
ROC | March | GWTP - GAC4 control valve deviation, backwash tank 1 level high, disregard as per shift report | All Water System ROC General | 2026-03-12
ROC | March | NMVCBA- Placed valve in manual 20L/s to keep NMETIB and NMETHW offset 17:31- Adjusted to 30L/s | All Water System ROC General | 2026-03-10
ROC | March | NMVCBA- Placed valve in manual 30L/s to assist offset of NMETIB and NMETHW | All Water System ROC General | 2026-03-11
ROC | March | Ethan Ullalkar signing out. | All Water System ROC General | 2026-03-11
ROC | March | RHRSTR, Deactivated D1 to allow more water to move from MARS to RHRSTR | All Water System ROC General | 2026-03-07
ROC | March | BLW3 - Travis W onsite. Scrubber check, exhaust, fan, chlorine leak, temp alarm | All Water System ROC General | 2026-03-06
ROC | March | Carter Dunn Signing In, -2D/Clear | All Water System ROC General | 2026-03-05
ROC | March | HLETYS- Kingsley M requested to deactivate duty for HUB3VR reset. Confirmed with Tim H NMTKKC- Kingsley M requested to deactivated duty for HUB3SVR reset. Notified Alex B as NMW13 running in manual. Alex informed Ben H. Kingsley confirmed still able to perform reset. Will lose comms for 5-10 minutes. | All Water System ROC General | 2026-03-02
ROC | March | Angelica Chepiga signing in, weather +7C | All Water System ROC General | 2026-03-09
ROC | March | NBW5 - Influent free chlorine residual Hi alarm at duty start up. Alarm cleared in 5 minutes. | All Water System ROC General | 2026-03-10
ROC | March | RHMCMD - Control panel power failure, site power failure and valve 1 and 2 fault alarms. Suite of power failure alarms triggered for site within Richmond Hill. Checked site, trending shows the valves closed and then opened. Able to reset alarms. RHPSWA /RHRSWA - Control panel power failure and site power failure alarm. Checked site, reservoir was draining when alarms triggered. RHPSWA was not active when the alarms triggered. SCADA showing normal operations. Reset alarms. AUMCBS - Control panel power failure and site hydro power failure alarms. Checked site, trending indicates normal operations. Cleared alarms. JFPS - Power failure affected pump operations. Tim H investigating and cleared alarms before the site could be checked. BVPS - Pump 1 multilin alarm. Station was affected by a power failure which interlocked the pumps during duty start. Tim H completed a site check on SCADA and cleared alarms. VNMCBA - Control panel power failure and site hydro failure. Checked site, trending shows normal operations. Cleared alarms. RHPSPA - Hydro power failure alarm. Richmond Hill was affected by a brief power failure. Checked site, trending show operations are normal. Pumps were not active during the power failure. Cleared alarms. | All Water System ROC General | 2026-03-03
ROC | March | John D called back informing of roll back on East historian trends | All Water System ROC General | 2026-03-03
ROC | March | VNPS- Chlorine System Failure Alarm VNPS- CL2 Emergency System 1,2 Fault Alarm. Chemical system is interlocked. Notified Ben H. He will attend site. Placed BVPS man/off 22:04- Ben H finished onsite. All alarms cleared. Chemical system back in operation. Placed BVPS back into auto W11702361 CMU5 JFPS- RES UPS ATS Source S2 (Line), WPS UPS ATS Source S2 (line) Not Ok Alarm- Alarm Cleared VNPS- Pump 2 Not Ready Alarm, Soft Starter Fault- Pump OOS VNPS- Chlorine Water Pressure LoLo Alarm- Alarm Cleared RHPSPA- Such. Pressure HiHi, Hydro Power Failure - Alarm Cleared VNPS PD8- Pumps shut down. Rotated duties so pump 4 and 1 in duty 1,2 and restarted duty | All Water System ROC General | 2026-03-03
ROC | March | NMETIB - Activated D1 to offset with NMETHW. | All Water System ROC General | 2026-03-03
ROC | March | MKRSEM- Called Toronto (Mehdi) and requested pumps off | All Water System ROC General | 2026-03-11
ROC | March | KSTP- CO2 Adjusted pH LoLo, Fin Water Fluoride Res Hi Alarm, Settl Water Cond Level LoLo Alarm. Called Jerry Z No answer. Jerry Z called back. He will look into it. | All Water System ROC General | 2026-03-11
ROC | March | NMTKKC - Outlet Total CL2 Lo and LoLo Alarms, checked site, Outlet total chlorine residual reading 2,22 mg/l. Trending indicates that the value did not drop to the lo and lolo level alarm setpoints. Cleared alarms. Will monitor and notify area in the morning. | All Water System ROC General | 2026-03-10
ROC | March | BLW34 - Silicate mixer 1 fault. Silicate tank reads empty. Mixer in local off. | All Water System ROC General | 2026-03-11
ROC | March | H4AUSSP1- Kingsley M performing server reset. Will lose comms for 5-10 minutes. AURSOH duty has shut down. Confirmed with Kingsley M. Will not impact AURSBS. 14:02- Work completed | All Water System ROC General | 2026-03-02
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-10
ROC | March | BVPS - Pump1 multilin and umcmd stop. Able to clear alarm. Pump 1 & 4 duty 1 running. power blip and uncmd caused some undesired duty rotations. Rotated pump 1 & 4 duty 1. | All Water System ROC General | 2026-03-03
ROC | March | ANW23 - RSVR inlet free chlorine hihi, David T still Onsight looking into issue | All Water System ROC General | 2026-03-03
ROC | March | ARPS- OCWA called (Martin) and informed will be switching pumps over from pump 5 to pump 6 | All Water System ROC General | 2026-03-01
ROC | March | KSTP- Raw Water Turbidity Fault Alarm. Disregard as per SCADA Report. | All Water System ROC General | 2026-03-01
ROC | March | STPSMR- Historian Heartbeat Alarm came back in. Notified Yash S. He will look into it. 18:47- John D called. Heartbeat alarm caused by reboot performed. Requested to clear alarm. 19:15- John D called and informed trending should be back and will slowly repopulate over the night for Stouffville, Mount Albert and Ballantrae, but live trending is available. Informed John D no trending at MAPS, RHRSTR, VNPS, VNRSKS, ARPS. He will look into it. 20:03- John D called back and issue has been fixed. Trending is back. | All Water System ROC General | 2026-03-03
ROC | March | AUW14 - Placed back to auto. VNRSKS - Switched feed from MAPS PD7 (P2,3) to VNPS PD7(P2,3). | All Water System ROC General | 2026-03-09
ROC | March | HLW2 - Well 2 pump failed to stop alarm. Duty just deactivated. Pump stopped. Cleared alarm. | All Water System ROC General | 2026-03-09
ROC | March | AURSBS - Activated Duty 1 to maintain MARS level. | All Water System ROC General | 2026-03-03
ROC | March | RHRSTR- Deactivated Duty 1 to maintain MARS level. | All Water System ROC General | 2026-03-03
ROC | March | NMW136- Combined and treated total chlorine residual lo alarms. Wells not running, no water directed to users. Chlorine residuals recovered in 6 minutes, alarms cleared. | All Water System ROC General | 2026-03-03
ROC | March | Angelica Chepiga signing out | All Water System ROC General | 2026-03-12
ROC | March | AUW14- Joe D running wells 2, 3 in manual for sampling. He will revert to auto once completed AUW57- Joe D running well in manual for sampling. He will revert to auto once completed | All Water System ROC General | 2026-03-02
ROC | March | ARPS- Martin from Peel called to notify ROC they will be switching from P5 to P6. | All Water System ROC General | 2026-03-06
ROC | March | QVW34- Eric S finished onsite. Requested to run well. Confirmed with Will M and placed well 3 man/on. 15:49- Placed wells back into auto | All Water System ROC General | 2026-03-02
ROC | March | GWTP - UV reactor 2 intensity lo. Appears within normal range now. Joe M called us to inform he has left site, aware of alarm KSTP - Place highlifts back in auto as per Joe M | All Water System ROC General | 2026-03-05
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-02
ROC | March | YWS + NYWS Normal Connor Smith signing out | All Water System ROC General | 2026-03-02
ROC | March | GWTP - High lift free chlorine low alarm. Checked site, chlorine analyzer is showing erratic trends. Analyzer is in calibration mode and instrumentation team is on site completing annual calibrations. Analyzer readings returned to normal range shortly after, alarm was cleared locally. | All Water System ROC General | 2026-03-04
ROC | March | QVW12 - Rick L & Parth P onsite for chlorinator rebuild. Placed well 1 & 2 man/off | All Water System ROC General | 2026-03-03
ROC | March | QVW12 - Parth P finished and leaving site. Parth is headed to AUW14 to assist Joe D. Parth informed that operations will be attending QVW12 to complete some work and that the well is not supposed to run until they complete this work. Deactivated NMETIB duty 1 to reduce the demand on the NMETHW system until the work at QVW12 can be completed. | All Water System ROC General | 2026-03-03
ROC | March | Stouffville, Mount Albert, Ballantrae- During shift transfer noticed no trending at all sites. Christian VB called John D who was performing work. John D called back and confirmed this is related to work being performed and data being collected locally. No ETA on when trends will be back. | All Water System ROC General | 2026-03-03
ROC | March | MARS- Cell1 (North) Lvl Lo Alarm AURSBS- Deactivated duty. | All Water System ROC General | 2026-03-03
ROC | March | QVW12- PAC Control Panel Power Failure, Generator Running Alarm, Gas Scrubber Overload Alarm (cleared). Well shutdown and then started back up. Site currently running on generator 00:01- Contacted Hydro One. Power outage in the area and estimated time of restoration is 02:30. QVETQS- System Pressure LoLo Alarm- Cleared 02:05- QVW12- PAC Control Panel Power Failure, Well 1 Pump VFD Fault Alarm. Well 1 shut down. Deactivated duty. Unable to clear VFD Fault. Switched well 2 into duty 1. Generator has shut off and station back on utility power. Will email Ben H | All Water System ROC General | 2026-03-03
ROC | March | HLW2 - Jordan B on site to complete work orders including chlorine analyzer, chlorine leak test, turbidity analyzer maintenance hi/low temperature alarm test and PRV exercise. NBW7 - Jake M on site to complete a generator test run, chlorine analyzer maintenance and chemical system inspections. | All Water System ROC General | 2026-03-12
ROC | March | GWTP - Joe M requesting electrical on-call. Issue with sump pump not working with building flood. | All Water System ROC General | 2026-03-12
ROC | March | Ethan Ullalkar signing out. | All Water System ROC General | 2026-03-06
ROC | March | VNRSKS - Due to lower levels at MARS, switched from MAPS PD7 to VNPS PD7 VNPS - PD7 Pump 3 Failed to Open alarm came in. Checked site. Ack/reset alarm and valve opened and pump is now running 22:31 - VNRSKS - Switched back to MAPS PD7 | All Water System ROC General | 2026-03-09
ROC | March | Angelica Chepiga signing in,weather -6C | All Water System ROC General | 2026-03-02
ROC | March | ANW23 - Cole W running highlifts in local on. Disregard highlift pumps OOS alarm ad turbidity alarm | All Water System ROC General | 2026-03-12
ROC | March | RHPSWA - Man/stop pump 2 VNP8 - Place pumps back in auto one at a time as Tim H finished with surge tank work MKRSMR - Patrick F onsite running Pump 4 jokey pump | All Water System ROC General | 2026-03-12
ROC | March | RHPSPA - Lee F finished at site | All Water System ROC General | 2026-03-12
ROC | March | SUSP- Influent hihi alarm came in as both SUSSHS and SUSSWB were pumping to headworks. Trends recovered and alarm cleared **WRONG BOOK** | All Water System ROC General | 2026-03-07
ROC | March | NBW5- Jacob M leaving site. He will leave well running in manual for the next hour then place back into auto. | All Water System ROC General | 2026-03-10
ROC | March | MAP8 - Place pump 1 & 3 man/off VNP7 - Place pump 3 auto. Done to preserve water for MARS and pull more from Teston | All Water System ROC General | 2026-03-06
ROC | March | SHETCS- Hypo pump 2 failed to stop alarm came in 3 times notified Stephen B. Stephen B on site working on pump. Directed to place in man/off will trouble shoot next week | All Water System ROC General | 2026-03-06
ROC | March | HLETYS, Darrick/Jordan B on site, testing flow control valves | All Water System ROC General | 2026-03-05
ROC | March | NMTKKC, Ammonia Tank 1 lolo alarm, Joe W is on site filling the tank | All Water System ROC General | 2026-03-05
ROC | March | ARPS - David from Peel informed they are rotating pumps. Currently pump 5 running, duty 1 pump will be swapped to pump 1 | All Water System ROC General | 2026-03-12
ROC | March | Ethan U signing in Weather -7. | All Water System ROC General | 2026-03-03
ROC | March | GWTP - Joe M and Jackie S on site to complete a generator test. | All Water System ROC General | 2026-03-03
ROC | March | YWS + NYWS Norma | All Water System ROC General | 2026-03-07
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-07
ROC | March | Carter Dunn Signing Out | All Water System ROC General | 2026-03-07
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-05
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-06
ROC | March | KSTP - CO2 Adjusted pH LoLo alarm. Checked site, the plant is active but the system duty is off so the high lift pumps are not pushing flow to the system. Trending shwos the pH reading dropped slightly before starting to recover. Alarm cleared and the low lift pumps activated to continue flow to the filters. Plant should shut down soon once the clearwell level reaches its setpoint. | All Water System ROC General | 2026-03-06
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-06
ROC | March | RHPSPA - Lee F on site to complete vibration testing. Lee requested that pump 2 and 3 be deactivated and pump 1 and 4 be activated. Made the necessary duty changes. | All Water System ROC General | 2026-03-12
ROC | March | Ethan Ullalkar signing out. | All Water System ROC General | 2026-03-12
ROC | March | ARPS - Martin from Peel/OCWA control called to inform theyre completing the daily pump rotation | All Water System ROC General | 2026-03-04
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-01
ROC | March | NMETIB, Activated D1 to keep towers offset | All Water System ROC General | 2026-03-07
ROC | March | NBW5 - Turbidity Hi alarm outstanding, switched silicate pumps. Assigned silicate pump 1 to duty 1. Will monitor. | All Water System ROC General | 2026-03-08
ROC | March | SHTP - UV Reactor 3 Minor fault alarm/low priority alarm. Duty just deactivated, no flow from filters. Emailed David T. | All Water System ROC General | 2026-03-08
ROC | March | MKRSEM- Called Toronto and requested two pumps on to reservoir. | All Water System ROC General | 2026-03-12
ROC | March | VNPS- Placed PD7 pumps in manual MAPS- Placed PD7 pump 3 in auto | All Water System ROC General | 2026-03-12
ROC | March | HLW2 - Treated Total chlorine Lo/ Combined chlorine LoLo alarms. Well 2 not running, no water directed to users. Values recovered in 5 minutes. Was able to clear alarms. | All Water System ROC General | 2026-03-08
ROC | March | YDSS + YNSS Normal *Wrong Book | All Water System ROC General | 2026-03-13
ROC | March | VNPSCD - Sani Sump Pump 1 and 2 Fault and Sump Pump 1 and 2 fault at VNPSP8. Checked site. Shift report indicates to send an email. Will call OIC if high level comes in. | All Water System ROC General | 2026-03-10
ROC | March | Connor Smith signing in 1C Cloudy | All Water System ROC General | 2026-03-03
ROC | March | KCETDS- Outlet Total CL2 Res LoLo Alarm. Sudden drop in residual and returned to normal next reading. Cleared alarm. | All Water System ROC General | 2026-03-03
ROC | March | VNPS PD7- Paced pump 2 in manual MAPS PD7- Placed pump 2 into auto | All Water System ROC General | 2026-03-10
ROC | March | STRS48 - Ian W completing work on the OIT and directed to disregard any historian heartbeat alarm util the work is completed. | All Water System ROC General | 2026-03-10
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-02
ROC | March | AUEQSJ - Will from Landmark onsite | All Water System ROC General | 2026-03-05
ROC | March | MKRSMR, Patrick F is on site, testing the flood analyzer, level alarms, temp alarm and preforming analyzer maint. Notified Toronto operator Paul to place his pumps to man/off for level testing | All Water System ROC General | 2026-03-05
ROC | March | AUW57- influent free Cl2 lo alarm came in recovered after 3 mins alarm cleared. Treated free Cl2 hi alarm came in spike on well start up and recovered after 3 mins alarm cleared | All Water System ROC General | 2026-03-06
ROC | March | AUPSRR - Post-inj Free chlorine Hi and HiHi alarms. Quick spike for one reading. Duty recently activated. Alarms cleared. | All Water System ROC General | 2026-03-03
ROC | March | MAP8 - Tyler C onsite to work on pump 4. As duty 1 about to start place pumps 1 & 2 man/off to prevent duty 1 pumps running. Left pump 3 auto, and man/start pump 4 as requested 9:42 - Tyler C finished at site. Pump 4 in good standing. Placed all pumps back in auto | All Water System ROC General | 2026-03-03
ROC | March | MAPS PD7- Noticed Pump 1 was OOS on Pres Switch Low Alarm (Info). Reset alarm. Placed in manual and placed pump 2 into auto. | All Water System ROC General | 2026-03-04
ROC | March | MMW1- Rob P leaving site as power cannot be restored at this time. Sean P is on site and will be attempting to hook up generator. Once power is restored Sean P will call Rob P to attend site or start pumps remotely. | All Water System ROC General | 2026-03-07
ROC | March | YWS+NYWS normal | All Water System ROC General | 2026-03-07
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-07
ROC | March | GWTP - ZW8 Neutralization Exceeded Duration Alarm came in. Checked site. Train 8 is still in neutralization mode. Called Jack P. who informed that this train went through and R-Clean today. Directed to disregard alarm #CONSULT | All Water System ROC General | 2026-03-04
ROC | March | VNMCYS - Intrusion alarm. Checked site, unable to clear alarm. Called Rob P who stated that Dwayne L is on site. BLW12 - Travis W is on site to complete operational samples. Travis will be deactivating BLW3 so the system does not overfill. | All Water System ROC General | 2026-03-09
ROC | March | GWTP- ZW4 Memb Tank Level Hi alarm, Train 4 in neutralization. Will monitor. | All Water System ROC General | 2026-03-09
ROC | March | ANW23- Post-Inj Free Chlorine Fault/LoLo, Pre Inj Free Chlorine Fault/LoLo, Discharge Pressure LoLo. Interlocked High Lift Pumps. Notified Dave T. He will attend site. Notified King Township On Call Operator (Patrick) of likely pressure complaints. 23:12- Dave T. able to run high lift locally and clear interlock. Pumps interlocked on max number of starts. Requested to call Kyle C on call PCS to remove this inhibit. Notified Kyle C. 23:23- Patrick (437-429-3801) from Township of King called back and requested to have Dave T give him a call so that he could relay some more information to a resident that had called in. 00:32- Dave T. finished onsite. Site back to normal operations W11707888 for Dave T W11707895 for Kyle C CMU5 | All Water System ROC General | 2026-03-04
ROC | March | GWTP, ZW1 Shutdown/Permeate Pump Uncommanded Stop alarm, notified Jack P, he is looking int it consult | All Water System ROC General | 2026-03-07
ROC | March | GWTP - Chris S still onsite, requested to deactivate duty to look into UV intensity on startup issue | All Water System ROC General | 2026-03-05
ROC | March | Ethan U signing in | All Water System ROC General | 2026-03-06
ROC | March | MMW1, Control Panel Power Failure Alarm, Wells currently man/off and aren't able to be placed in the on position. Notified Rob P, Directed to disregard well hi/hihi alarms as there is nothing he will be able to do on his end. Once power is back, RO will place wells in the man/on position. Checked Alectra Power outage map, Power won't be restored till roughly 00:00 - 02:00 23:52, Contacted Alectra has their map says all outages are recovered however MMW1 is still down. Talked with Alectra operator Troy who informed the RO that there is no power outages at 320 Major Mackenzie Drive (MMW1), it may be a site issue. Contacted Rob P to inform him of the updated situation, he is heading to site. Saturday March 7/2026, 00:05, Historian Heartbeat alarm, Contacted Kyle C, he is looking into the heartbeat alarm. Notified Rob P that power has been restored on site however cant place the wells back in man/on position 00:43, Rob P is on site, Notified RO that there is power around the station but specifically in MMW1, no power seems to be available, Rob P requests on call electrician to give him a call. 00:54: Rob P has confirmed that Sean P is heading to site. Rob P has also requested a call from Dan K (Water Manager On call) as he has a few questions about the site. W11714621 CMU5: W11714612 (Rob P) CMU5: W11714621 (Kyle C) CMU5: W11714629 (Sean P) Alectra Operator: Troy | All Water System ROC General | 2026-03-06
ROC | March | GWTP- Raw water sample P3 comm alarm came in. Able to reset trends okay sample P1 running in D1 | All Water System ROC General | 2026-03-07
ROC | March | ARPS - Peel ammonia analyzer A Airport rd discharge alarm. Ammonia pumps recently switched. Alarm cleared when on the phone with Martin from OCWA. | All Water System ROC General | 2026-03-08
ROC | March | STW12 - Jack P on site to complete work orders including chlorine analyzer maintenance, turbidity analyzer maintenance, chemical pump inspections and a generator test run. SUETDR - Phil D on site to complete chlorine analyzer maintenance and low temperature alarm test. | All Water System ROC General | 2026-03-03
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-03
ROC | March | MAP8 - Pump 2 VFD fault, informed Jacob M. Will follow up with team | All Water System ROC General | 2026-03-05
ROC | March | GWTP - ZW4 membrane tank level hi and hihi switch alarm. Checked site, tank is going through a cleaning sequence. Alarm status changed to normal, alarms cleared on acknowledgement. | All Water System ROC General | 2026-03-02
ROC | March | NMW15 - Treated free chlorine HiHi alarm, switched ammonia pumps. Pump 1 to Duty 1. | All Water System ROC General | 2026-03-02
ROC | March | VNPSP8 - PD8 Pump 4 VFD Fault and Pump 4 Not ready alarm came in. Checked site. Ack/reset but alarm is unable to reset. Rotated duties so that pump 4 is no longer duty 1. Placed pump 4 man/off. Will send an email. | All Water System ROC General | 2026-03-04
ROC | March | Adeela Khan signing out | All Water System ROC General | 2026-03-10
ROC | March | YWS + NYWS NORMAL | All Water System ROC General | 2026-03-11
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-03
ROC | March | STRS48 - Jack P. called and requested to place pump back to auto | All Water System ROC General | 2026-03-04
ROC | March | YWS + NYWS normal | All Water System ROC General | 2026-03-01
ROC | March | MKRSEM - Low level alarm. Called Toronto Water (Peter) and requested they activate two pumps to push flow to MKRSEM. | All Water System ROC General | 2026-03-04
ROC | March | STETBR - Tower Level Hi alarm came in. Placed STW2 and STW3 back to auto, as per interim | All Water System ROC General | 2026-03-02
ROC | March | ANW23 - Sean P on site to complete a generator ATS switch test. The test will be five minutes. The system duty just deactivated. Deactivated the reservoir duty 1 so Sean P can complete the test. | All Water System ROC General | 2026-03-03
ROC | March | Angelica Chepiga signing in, weather +7C | All Water System ROC General | 2026-03-10
ROC | March | MARS - Called Toronto water (Paul) and requested reduce flow. | All Water System ROC General | 2026-03-10
ROC | March | NBW5 - Turbidity Hi alarm, rotated silicate pumps. Assigned silicate pump 1 to duty 1. Will monitor. | All Water System ROC General | 2026-03-10
ROC | March | ARPS - Flow lolo alarm. Checked site, all ARPS pumps either manual/off or local/off. Called Peel/OCWA (Jerry) who stated their SCADA team was working on the PLC and needed to shut down the pumps. Jerry has re-activated the pumps. | All Water System ROC General | 2026-03-10
ROC | March | AUW5 - Erick S attending site for chlorinator. Placed well in man/off | All Water System ROC General | 2026-03-03
ROC | March | MMW1- Control Panel Power Failure, Well HiH Alarms Notified Gary P. Requested to place wells 8 and 13 man/on CONSULT | All Water System ROC General | 2026-03-03
ROC | March | NMTKKC- Ammonia Pump 1 Failed to Start. Pump 2 took over in duty 1. Cleared alarm. | All Water System ROC General | 2026-03-03
ROC | March | STETBR - Hi level alarm, placed STW12 and STW3 back to auto. | All Water System ROC General | 2026-03-11
ROC | March | YWS + NYWS NORMAL | All Water System ROC General | 2026-03-11
ROC | March | NMVCBA - Placed back to auto. | All Water System ROC General | 2026-03-11
ROC | March | KSTP - Noticed Finished Water Turbidity Spiked on Duty startup for one minute and back to optimal range. High lift pump 3 running normally. Raw water Turbidity fault alarm - disregard as per SCADA review. | All Water System ROC General | 2026-03-02
ROC | March | QVW12- Donald M on site booster pump airlocked. Will backflush well and troubleshoot booster pump AUW57- Treated free Cl2 hi alarm came in. Checked trends spike on start up and recovered after 6 mins MKRSEM- Reservoir lo alarm came in. Called Metro spoke with Zoran to start 2 pumps to fill reservoir | All Water System ROC General | 2026-03-06
ROC | March | QVW12. Placed well 1 back to auto | All Water System ROC General | 2026-03-06
ROC | March | STW1/3, Placed wells back to auto | All Water System ROC General | 2026-03-07
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-07
ROC | March | YWS+NYWS normal Adam Button signing out | All Water System ROC General | 2026-03-07
ROC | March | MARS - Hi level alarm, activated VNRSKS duty 1. | All Water System ROC General | 2026-03-11
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-01
ROC | March | NMETIB- Activated duty | All Water System ROC General | 2026-03-01
ROC | March | STW12- Placed well 2 man/on STW3- Placed well 3 man/on For STETBR Fill Cycle | All Water System ROC General | 2026-03-01
ROC | March | AUW5 - Aurora Duty deactivated, placed well pump from man/on back to auto. | All Water System ROC General | 2026-03-09
ROC | March | Christian Van Beek signing out. | All Water System ROC General | 2026-03-09
ROC | March | SHTP - UV Reactor 1 Minor fault alarm. David T called and requested disregard Minor alarms. | All Water System ROC General | 2026-03-08
ROC | March | STRS48 - High Lift Pump 1 Failed to Stop Alarm came in. Checked site. Duty had recently deactivated and pump was in the process of shutting down. Ack/reset alarm and pump shut down and alarm cleared | All Water System ROC General | 2026-03-08
ROC | March | HLW1 - Jordan B and Darrick S on site to complete a chlorine leak detection test and complete maintenance on the chlorine analyzer. | All Water System ROC General | 2026-03-10
ROC | March | BLW12- Travis W onsite for work orders including generator run, CL17 maintenance, turbidimeter maintenance, hypo system cleaning and health and safety. | All Water System ROC General | 2026-03-10
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-04
ROC | March | MARS- Cell1 (North) Lvl Hi Alarm AURSBS- Activated duty | All Water System ROC General | 2026-03-04
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-01
ROC | March | AUW57 - Erick S onsite working on chlorinator 2. Was impacting chlorinator 1 giving hi influent on dose. Replacing tube | All Water System ROC General | 2026-03-06
ROC | March | QVW34 - Man/stop well 3 as treated chlorine approaching hihi level. Cleared contact tank. QVW12 - Influent free chlorine lolo, Locked out wells. Informed Will M regarding wells GWTP - Parth P finished at site QVW12 - Donald M called back that he will head to site regarding well 1 issues. CMU = 11714540 | All Water System ROC General | 2026-03-06
ROC | March | QVETQS - Inlet Free chlorine residual HiHi switch and Hi alarms at duty start. Will monitor. Alarms cleared in 5 minutes. | All Water System ROC General | 2026-03-08
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-08
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-09
ROC | March | NBW2 - Historian Heartbeat alarm. Checked site, the well was active when the alarm triggered which shut down the well. The alarm status changed to Normal and the well activated again in auto mode. Alarm cleared on acknowledgement. | All Water System ROC General | 2026-03-09
ROC | March | KSTP - Finished Water Turbidity HiHi alarm came in. Checked site. Hi lifts are interlocked. NTU is back to optimal range. Called Stephen B. for direction to clear alarm. No answer, will try again 22:15 - Stephen B. called back and directed to reset alarm as turbidity was only hihi for 1 minute. Reset alarm and hi lift pumps are now running | All Water System ROC General | 2026-03-01
ROC | March | YWS + NYWS Normal STETBR - Tower Level Hi alarm came in. Placed STW3 back to auto, as per interim | All Water System ROC General | 2026-03-09
ROC | March | STETTL- Sodium Adverse Date: March 10/26. 10:52AM Lab Contact: Mei Wang, 905-686-0041 Ex. 4318 Submission #- 2200023333 Sample Date: March 4/2026 Sample Type: Sodium Sampler Name: Jack Palmer Sample Site Location: STETTL Remote Operator: Connor S Notified Dan Z and East Ops and emailed adverse form. | All Water System ROC General | 2026-03-10
ROC | March | MAPSN1- Kingsley M working on server update. 11:34- Work completed | All Water System ROC General | 2026-03-10
ROC | March | Initiating MAPS to JFRS feed run - Placed KCPSDS pumps man/off - Placed VNPS PD8 and MAPS PD8 pumps man/off - Placed VC MV3 into man - Placed AURSBS Res MV4 to man and close - Man/start pump 3 at MAPS 05:03 - all changes have been reverted | All Water System ROC General | 2026-03-01
ROC | March | NBW3 - Influent Free Chlorine LoLo switch alarm came in. Well recently activated. LoLo influent locked out the well. Influent levels came back up within 2 mins. 20:47 - Restarted the well and all alarms cleared | All Water System ROC General | 2026-03-01
ROC | March | NMVCBA- Placed back to auto. | All Water System ROC General | 2026-03-03
ROC | March | ANW23 - Sean P onsite for diesel Pm | All Water System ROC General | 2026-03-03
ROC | March | H1GWTPP1 - Kingsley M restarting hub server | All Water System ROC General | 2026-03-03
ROC | March | GWTP- Stephen B leaving site. Site back to normal. Requested to activated duty. | All Water System ROC General | 2026-03-04
ROC | March | GWTP- GAC 4 Flow Control Valve Deviation Alarm. Disregard as per SCADA Report | All Water System ROC General | 2026-03-05
ROC | March | QVW12- Influent free lo alarm came in on well start up followed by lolo lock out alarm. Well did not pass contact tank. Notified Donald M. Will attend site created CMU5 W11714768 placed both wells in man/off QVW34- Placed well 4 in man/on. QVETQS- System pressure lo alarm came in recovered after 3 mins alarm cleared NMVCBA- Placed valve in man/open at 40 L/s VNPS PD7- Placed P3 in man/off MAPS PD7- Placed P3 in auto #CMU5 | All Water System ROC General | 2026-03-07
ROC | March | QVW34- Adjusted chlorinator 1 on well 4 from 85% to 87% as influent is below target 15:10-QVW34- Adjusted chlorinator 1 on well 4 from 87% to 89% as influent is still below target | All Water System ROC General | 2026-03-07
ROC | March | YWS + NYWS NORMAL | All Water System ROC General | 2026-03-08
ROC | March | VNPS PD7- Placed P2 in auto MAPS PD7 - Placed P2 man/off STW12/3- Placed P1/3 in man/on as per interim | All Water System ROC General | 2026-03-06
ROC | March | Angelica Chepiga signing in, weather +3C | All Water System ROC General | 2026-03-08
ROC | March | Adeela Khan signing in. Weather: 10C and sunny | All Water System ROC General | 2026-03-08
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-04
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-05
ROC | March | ARPS - Martin from OCWA called, Completing daily pump duty rotation. Turning off pump 7 and turning on pump 5. | All Water System ROC General | 2026-03-08
ROC | March | KSTP - CO2 adjusted pH lolo alarm. Checked site, plant is active. Trending shows a dip of the CO2 adjusted pH that is recovering. High lift pumps have interlocked. Shift report states that the raw water pH alarms are a disregard. Will reset alarm as it recovers above the lolo alarm setpoint. KSTP - 21:31 - Noted the conduit water level has dropped significantly due to both filters being active. Also noted the raw water turbidity alarm disregard does not apply to this reading. Contacted Jack P who will check SCADA. KSTP - 21:33 - Settl water conduit level lolo alarm. Low lift pumps interlocked due to the CO2 adjusted pH lolo alarm. On call operator has been contacted. KSTP - 2201: Jack P called back to inform that the CO2 reading recovered, the low lift pumps have activated and the conduit level has recovered. Jack stated that if the alarm triggers again the system duty can be deactivated which will result in the plant deactivating. #consult | All Water System ROC General | 2026-03-05
ROC | March | RHMCMD - Closed valve in manual mode YWS + NYWS Normal | All Water System ROC General | 2026-03-06
ROC | March | GWTP- Joe M backwashing GAC 4 | All Water System ROC General | 2026-03-06
ROC | March | MKRSMR/MKPSSA - Toronto Water has activated one COTFA pump in manual mode to fill MKRSMR as requested. Valves have rotated and reservoir is now in receiving mode. Activating one pump at MKPSSA in manual mode for fifteen minutes as directed by Dan Z. | All Water System ROC General | 2026-03-02
ROC | March | RHPSWA - Benson S onsite testing flood alarm, health & safety, temp, PRV | All Water System ROC General | 2026-03-03
ROC | March | NMVCBA- Placed valve in man/open at 40L/s | All Water System ROC General | 2026-03-06
ROC | March | QVW12- Well pump 1 VFD not ready and speed OOR both wells in local well 2 running. Called Lee F. working on well 1 wasting valve and will m running well 2 in local | All Water System ROC General | 2026-03-06
ROC | March | GWTP, UV Reactor 2 Critical Fault, notified Joe M, he is looking into it | All Water System ROC General | 2026-03-05
ROC | March | Connor Smith signing in 7C Sunny | All Water System ROC General | 2026-03-04
ROC | March | SHTP- Filter 3 Post Rinse NIT High Alarm came back in. Had gone through a backwash after the first time it came in. Notified Dave T. He will take a look. 21:53- Dave T put it through another rinse. Requested a call if it comes back in. 22:07- Alarm came in again. Dave T will attend site. 02:14- Dave T leaving site. Filter 3 back in production. Reservoir 1, 2 Level Lo Alarms. Duty almost complete. Will recover once it deactivates. W11707880 CMU5 | All Water System ROC General | 2026-03-04
ROC | March | QVW34- Eric S onsite troubleshooting Total Cl analyzer. Requested pumps man/off for work. | All Water System ROC General | 2026-03-02
ROC | March | GWTP - ZW3 train shutdown, turbidity fault ZW3. Informed Jack P, will look into issue | All Water System ROC General | 2026-03-06
ROC | March | SHTP- Power fail on site. Filter panel phase monitor alarm/ UV reactor1,2,3 minor faults came in. Plant not active at time of power loss. Notified David T. Directed to ack reset all alarms as power is restored. UV alarms would not clear and David T will take a look on SCADA #consult | All Water System ROC General | 2026-03-07
ROC | March | KCETDS, Activated D1 to help prepare for Maple to Jefferson for later tonight | All Water System ROC General | 2026-03-07
ROC | March | MKRSEM- Called Toronto water (Zoran) and requested start 2 pumps to fill the res. | All Water System ROC General | 2026-03-08
ROC | March | STPSMR - Patrick F running generator and will change chlorine cylinders with Jack P. | All Water System ROC General | 2026-03-09
ROC | March | GWTP - Jackie S onsite testing eyewash alarms. Microfiltration room low temp, disregard as old alarm from gen run | All Water System ROC General | 2026-03-03
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-09
ROC | March | KCETDS - Activated duty 1 YWS + NYWS Normal | All Water System ROC General | 2026-03-10
ROC | March | Starting Maple to Jefferson 00:30, Maple to Jefferson Feed failed, No alarms active, VC_MV3 failed to open. Placed valve originally to 10% while waiting for RES_MV4 to close. At this time VC_MV3 did not get to the 10% mark. Once RES_MV4 was fully closed, Placed VC_MV3 to 100% to see if the valve will unstick. After waiting roughly 15 minutes, Valve failed to open with no alarms present. Reverted the maple to Jefferson feed. Will send email to operators to inform them of this issue. | All Water System ROC General | 2026-03-08
ROC | March | GWTP - Rick L working on ZW1, Joe M called, directed disregard alarms. | All Water System ROC General | 2026-03-09
ROC | March | EGMCDD - Arthur L leaving site. This meter chamber is now live, alarms should be responded to as normal. | All Water System ROC General | 2026-03-03
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-03
ROC | March | GWTP - Joe M draining GAC 4, directed disregard low level alarms. GAC 4 man/off for the night. | All Water System ROC General | 2026-03-09
ROC | March | NMETIB - Activated duty 1 to help offset with NMETHW | All Water System ROC General | 2026-03-10
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-01
ROC | March | NBW2 - Jake M on site to complete work orders including a chlorine leak detection test, chlorine analyzer maintenance, PRV inspection and silicate injection point inspection. | All Water System ROC General | 2026-03-03
ROC | March | GWTP - Sutton header pH hi, sudden spike on trend when no flow going through line as duty not active. Informed Stephen B, appears to be a gradual slow decline on the pH. Speaking with Stephen we will monitor for now, duty 1 active now shows no change in reading as continuous its slow decline. | All Water System ROC General | 2026-03-03
ROC | March | BVPS - Deactivated duty 1 | All Water System ROC General | 2026-03-01
ROC | March | Ethan Ullalkar signing out. | All Water System ROC General | 2026-03-03
ROC | March | Adeela Khan signing in. Weather: 16C and Sunny | All Water System ROC General | 2026-03-09
ROC | March | MKRSEM - Called Toronto Water(Zoran) and requested start filling Res with 2 pumps. | All Water System ROC General | 2026-03-02
ROC | March | YWS + NYWS NORMAL | All Water System ROC General | 2026-03-03
ROC | March | KSTP - CO2 Adjusted pH LoLo alarm. Value is in normal range, was able to clear alarm. | All Water System ROC General | 2026-03-03
ROC | March | QVW34 -Treated total chlorine residual low alarm. Well not active, no water directed to users. Value recovered in 6 minutes, cleared alarm. | All Water System ROC General | 2026-03-03
ROC | March | STW12 - Place well 2 man/on STW3 - Place well 3 man/on. This was done as Zone 1 tower activated | All Water System ROC General | 2026-03-03
ROC | March | MARS- Cell1 (North) Lvl Hi Alarm RHRSTR- Deactivated duty | All Water System ROC General | 2026-03-05
ROC | March | STW3 - Place well man/on for Zone 1 tower fill | All Water System ROC General | 2026-03-03
ROC | March | NMETHW - Deactivated duty 1 to maintain level offset from NMETIB. | All Water System ROC General | 2026-03-05
ROC | March | STRS48 - High lfit pump 1 failed to stop alarm. Checked site, system duty recently deactivated. High lift pump 1 has stopped and there is no flow being registered leaving the pumps. Cleared alarm. | All Water System ROC General | 2026-03-05
ROC | March | Adam Button signing in 0C Raining | All Water System ROC General | 2026-03-06
ROC | March | AUW14- Placed wells 2/3 in auto AUW57- Placed Well 5 in auto MAPS PD7- Placed P1-3 in man/off VNPS PD7- Placed P2/3 in auto | All Water System ROC General | 2026-03-07
ROC | March | ARPS- Martin from Peel called ton inform ROC they will be switch from P6 to P7 | All Water System ROC General | 2026-03-07
ROC | March | NMETIB- Activated D1 at 65% to offset from NMETHW as per shift report | All Water System ROC General | 2026-03-07
ROC | March | MMW1- Rob P req Terry Cs number to have them attend site to get generator running on site | All Water System ROC General | 2026-03-07
ROC | March | AUW14, Joe D on site running the generator, he has placed the wells man/off for the time being | All Water System ROC General | 2026-03-05
ROC | March | YWS+NYWS normal | All Water System ROC General | 2026-03-07
ROC | March | YWS+NYWS Normal QVW12- Donald M on site to backflush and trouble shoot booster pump. Donald M notified ROC that site has some flooding issues and a transformer on site is close to being affected by the flooding. Checked All Pipes to ensure no water main is in the vicinity of flooded area. Watermain locate to the west of the flooded are but storm ditch and connecting culvert are draining into flooded area. Notified Roads Dispatch spoke with Jen who will dispatch a roads operator. Called Hydro One spoke with Scott to inquire about safety concerns if flooding of transformer on site. Scott confirmed with Hydro one lineman that there are no safety concerns. updated Donald M of situation 16:24-QVW12- Donald M placed booster P2 OOS and will backflush and start up well | All Water System ROC General | 2026-03-07
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-11
ROC | March | BLW12 - Power restored, generator stopped. Well 2 was running. Well 2 Pump VFD fault and Well 1&2 Pumps OOS alarms. ET is filling very slowly. Notified Joe M. He will attend site to reset pumps. # CMU 5 W11733508 | All Water System ROC General | 2026-03-15
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-15
ROC | March | VNPS - Benson S and Tim H on site to complete work orders for the surge tanks. Benson and Tim Have requested that all VNPS pumps be deactivated. Tim H directed that PD8 can be filled using RHPSWA pumps. Swapped the PD7 supply pumps to MAPS. Estimated work duration is one hour. Activated RHPSWA pump 2 and also activated RHRSTR duty 1 to push additional flow to MARS system. | All Water System ROC General | 2026-03-12
ROC | March | Carter Dunn Signing In, -7D/Clear | All Water System ROC General | 2026-03-13
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-15
ROC | March | NMETIB - Activated Duty 1 to offset NMETHW. | All Water System ROC General | 2026-03-15
ROC | March | VKRSKS - Switched feed from MAPS PD7 (P2,3) to VNPS PD7( P2,3). Duty not active. | All Water System ROC General | 2026-03-15
ROC | March | SHTP - Jordan B leaving site. | All Water System ROC General | 2026-03-15
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-13
ROC | March | VNP7 - Place pump 1 back in auto | All Water System ROC General | 2026-03-14
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-09
ROC | March | AUW57 - Silicate pump 2 fault alarm (placed man), Silicate pump 1 fault alarm outstanding, Silicate pumps not available alarm. Placed Well 5 pump man/off. Will notify OP. | All Water System ROC General | 2026-03-15
ROC | March | STRS48- High lift P1 failed to stop alarm came in. Pump shutdown on D1 deactivation cleared alarm QVW12- Donald M done on site informed ROC well is running okay but residuals may be lower . Placed well 1 back in auto. Combined Cl2 lo alarm came in. Will continue to monitor QVW34- Placed well 4 in auto | All Water System ROC General | 2026-03-07
ROC | March | GWTP - Rick L on site for annual calibrations. | All Water System ROC General | 2026-03-09
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-16
ROC | March | STPSMR- Placed pump 1 and 2 back into auto | All Water System ROC General | 2026-03-03
ROC | March | NMVCBA- Placed valve manual 20L/s to keep NMETIB and NMETHW offset. 23:56- Placed valve back into auto | All Water System ROC General | 2026-03-03
ROC | March | NMETIB- Activated duty | All Water System ROC General | 2026-03-04
ROC | March | KSTP - Fin Water Fluoride Res Hi alarm at duty start. Slowly dropping. Notified Joe M, he activated Duty remotely. # Consult | All Water System ROC General | 2026-03-15
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-12
ROC | March | BLETNL- Wes from town of Stouffville is flushing in area. Activated D1 | All Water System ROC General | 2026-03-06
ROC | March | SHTP - Filter 1 and Filter 3 High turbidity alarm after Filter 2 backwash. Disregard as per SCADA review. Cleared alarms. | All Water System ROC General | 2026-03-12
ROC | March | QVW34- Treated total Cl2 lo alarm came in. Wells not active and no water directed to users. trends recovered after 3 mins alarm cleared | All Water System ROC General | 2026-03-07
ROC | March | MKRSEM, Notified Toronto operator Medhi to start 2 pumps to fill the res | All Water System ROC General | 2026-03-15
ROC | March | Connor Smith signing in | All Water System ROC General | 2026-03-10
ROC | March | JFPS- Evgeny S rebooting OIT. Placed pumps man/off. Disregard Heartbeat Alarm. | All Water System ROC General | 2026-03-10
ROC | March | Carter Dunn Signing In, 1D/Rain | All Water System ROC General | 2026-03-06
ROC | March | Christian Van Beek signing in. | All Water System ROC General | 2026-03-13
ROC | March | AUW57, Joe D on site, working on Cl2 booster 2. Directed to place chlorinator 2 back to auto | All Water System ROC General | 2026-03-05
ROC | March | BLW3 - Joe W on site to complete a generator test on load with the well pump. | All Water System ROC General | 2026-03-12
ROC | March | MARS, Notified Toronto operator Paul to increase the flow to MARS as the level is on the lower end | All Water System ROC General | 2026-03-05
ROC | March | QVW12- Treated Free Chlorine HiHi Alarm. Value recovered after a couple of minutes. | All Water System ROC General | 2026-03-02
ROC | March | KSTP, Fin Water Fluoride lolo, notified Joe M, directed to rotate Fluoride pumps, Placed Fluoride pump 2 in D1 and pump 1 in D2. If residual doesn't come back up within the hour, Joe M directed to place the highlift pumps man/off for the night 01:54, Placed high lift pumps 2/3/4 in man/off as the fluoride residual has not recovered, as per Joe M consult | All Water System ROC General | 2026-03-16
ROC | March | KCETDS, Metering Chamber Flood Alarm, shift report doesn't say anything about this alarm, contacted Jordan B, directed to disregard, consult | All Water System ROC General | 2026-03-16
ROC | March | QVW34 - Rick L finished at site | All Water System ROC General | 2026-03-12
ROC | March | GWTP - Jackie S doing chlorine analyzer maintenance for wash water and lake | All Water System ROC General | 2026-03-11
ROC | March | AUW5 - Influent free chlorine hihi on startup, came back within range next reading | All Water System ROC General | 2026-03-13
ROC | March | GWTP - Jackie S. testing chlorine leak, she is aware duty just activated | All Water System ROC General | 2026-03-10
ROC | March | GWTP - Rick L and Parth P finished for today and leaving site. | All Water System ROC General | 2026-03-09
ROC | March | AUPSWS- Donald M onsite for work orders, running generator, flood alarm and low temp. | All Water System ROC General | 2026-03-10
ROC | March | SHTP, UV Transmittance lo alarm/Filter 1/3 turbidity hi alarm notified Jordan B of the UV alarm, he will look into it 16:21, Jordan B called back and directed to disregard, Filter 3 was back washing which cause the LO UV Transmittance alarm consult | All Water System ROC General | 2026-03-13
ROC | March | QVW34 - Chris I working on site, taking generator offline for the duration of the work. | All Water System ROC General | 2026-03-09
ROC | March | STW12 - Place well 1 back in auto STW3 - Place well back in auto as Zone 1 duty 1 stopped | All Water System ROC General | 2026-03-14
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-14
ROC | March | Carter Dunn Signing In. -3D/Snowing | All Water System ROC General | 2026-03-14
ROC | March | VNPS - Benson S on site to complete station checks and directed to activate the duty at RHRSTR so that BVPS activates to push flow and activate the chemical system. | All Water System ROC General | 2026-03-13
ROC | March | Adam Button signing in 8C clear | All Water System ROC General | 2026-03-07
ROC | March | MMW1- Kyle C informed ROC that Trends are working locally on the OIT, but they having issues with them on the DMZ and has reached out to Kevin W from network. May end up being outstanding until Monday if networking isn't able to establish connection. | All Water System ROC General | 2026-03-07
ROC | March | GWTP - GAC 4 flow control valve deviation alarm outstanding. Disregard alarm as per shift report. | All Water System ROC General | 2026-03-08
ROC | March | VNP7 - Place pumps man/off MAP7 - Place pumps 3 & 1 back in auto | All Water System ROC General | 2026-03-11
ROC | March | NBW5 - Jake M on site to complete work orders including a generator test run. chlorine leak detection test, chlorine analyzer maintenance and chlorine/silicate system inspection and maintenance. | All Water System ROC General | 2026-03-10
ROC | March | RHPSWA- Intrusion alarm, FMC will notify Corp security. | All Water System ROC General | 2026-03-15
ROC | March | 11:40 ARPS - Airport Rd discharge flow low low alarm. Called OCWA ( Benish). He is on the phone with SCADA crew, will investigate and call back. 12:01 ARPS Alarms cleared, Pump 6 started in auto. 12:12 ARPS - Benish from OCWA called with update, Electrical crew was performing UPS alarm testing, causing tank level quick drop and YR pumps interlock. Back to normal operations, pump 6 is running on auto/ Duty 1. | All Water System ROC General | 2026-03-09
ROC | March | NBW5 - Tim H at site for testing of well, issue with turbidity. Running well in man/on | All Water System ROC General | 2026-03-12
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-15
ROC | March | MKRSEM, Medhi from Toronto called, he is dropping 1 pump as they are having issues on their end | All Water System ROC General | 2026-03-15
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-16
ROC | March | Connor Smith signing in 1C Clear | ROC General | 2026-03-28
ROC | March | Maximo and EzMaxMobile Update completed. Returning to elog book. Christian Van Beek signing in, weather: -1C and sun. Please see attached photos of the paper logbooks. | All Water System ROC General | 2026-03-28
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-28
ROC | March | MKRSEM- Called Toronto and requested two pumps on | All Water System ROC General | 2026-03-28
ROC | March | Christian Van Beek signing in. Weather: -1C and sun | ROC General | 2026-03-28
ROC | March | STW12- Placed well 2 into auto STW3- Placed well into auto for completion of STETBR Fill Cycle | All Water System ROC General | 2026-03-29
ROC | March | VNRSKS - Activate duty 1 to help bring down MARS | All Water System ROC General | 2026-03-29
ROC | March | SHTP - Filter 2 & 3 turbidity hi, reading came back within range | All Water System ROC General | 2026-03-29
ROC | March | Connor Smith signing in 7C Sunny | ROC General | 2026-03-04
ROC | March | GWTP - Parth P, Rick L and Art P finished and leaving site. | All Water System ROC General | 2026-03-04
ROC | March | SHTP- Filter 3 Turbidity Hi Alarm. Backwash just completed. Disregard as per SCADA Report. | All Water System ROC General | 2026-03-04
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-04
ROC | March | NMW136 - Lee F. is on site to change the oil for well 13. Lee will be placing the well in local. Duty is not active and well is not running. Confirmed with Alex B. | All Water System ROC General | 2026-03-04
ROC | March | KSETDP- Mark from Process Optimization leaving site. | ROC General | 2026-03-10
ROC | March | MAPS - Dave from property services leaving site. | ROC General | 2026-03-09
ROC | March | HLW1 - Combined Chlorine Lo alarm came in. Well is not running and water is not being directed to users | All Water System ROC General | 2026-03-09
ROC | March | JFPS - Benson S on site completing a generator run test and has directed to activate one pump to place the generator on load. Activated pump 3 in manual mode. | All Water System ROC General | 2026-03-10
ROC | March | STW3- Placed well man/on for STETBR Fill Cycle | All Water System ROC General | 2026-03-10
ROC | March | KSTKWP- Jerry Z. Working on Cl analyzers. | All Water System ROC General | 2026-03-10
ROC | March | Ethan U signing in Weather -0. Snowing | ROC General | 2026-03-13
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-14
ROC | March | Pest control visiting sites: VNRSKS, RHRSTR, VNPS, RHRSWA. | ROC General | 2026-03-09
ROC | March | Carter D Signing Out | ROC General | 2026-03-04
ROC | March | Adeela Khan signing in. Weather: 0C and Sunny | All Water System ROC General | 2026-03-04
ROC | March | STPSMR, Dominic from Honeywell is on site | ROC General | 2026-03-05
ROC | March | Connor Smith signing in | ROC General | 2026-03-10
ROC | March | Connor Smith signing in 3 C Rain | ROC General | 2026-03-11
ROC | March | Adeela Khan signing out | ROC General | 2026-03-10
ROC | March | JDSS, Stephen from AB Project management, They are draining the fuel lines to the generator, disregard alarms on site till they refuel the lines | ROC General | 2026-03-13
ROC | March | Adeela Khan signing in. Weather: -11C and Sunny | ROC General | 2026-03-01
ROC | March | Christian Van Beek signing in. Weather: -3C and clear. | ROC General | 2026-03-12
ROC | March | KSTP - Drew from Ferguson onsite | ROC General | 2026-03-12
ROC | March | STETBR - Tower low level alarm. Activated STW3 as per the interim procedure. | All Water System ROC General | 2026-03-12
ROC | March | STPSMR - Drew from Ferguson Electric on site for a team meeting. | ROC General | 2026-03-04
ROC | March | GWTP- Gas Chlorinator 5,6 Hi Vacuum Alarms. Notified Stephen B. Requested a call if residuals start to drop. GAC 4 Flow Control Valve Deviation Alarm. Disregard as per SCADA Report KSTP- Post Chlorinator 2 Lo Vacuum Alarm. Alarm cleared. 02:00-GWTP- Contact Chamber 2 Chlorine Lo Alarm. Notified Stephen B. Requested to place KSTP High Lift pump 4 in manual to continue running and deactivate duty. Stephen B will attend site. Placed GWTP High Lifts in manual. Deactivated SUETDR as KSTKWP close to duty start. 03:55- Stephen B called and will need assistance working on the chlorinator. Requested to call Ben H. Notified Ben H. He will attend site. W11702382 For Stephen B W11702390 For Ben H CMU5 | All Water System ROC General | 2026-03-04
ROC | March | AUSSYS - Orlando from Property services on site for a short visit and is now leaving. | ROC General | 2026-03-02
ROC | March | KSTP - CO2 Adjusted pH LoLo alarm came in. Checked site. pH level is within optimal range and alarm cleared on its own | All Water System ROC General | 2026-03-01
ROC | March | Angelica Chepiga signing out | ROC General | 2026-03-09
ROC | March | JDSS, Theodor from AB is on site, turning on generator to work on fuel lines | ROC General | 2026-03-05
ROC | March | NMETYS - Denis from Landmark on site to complete work for new door landings. | ROC General | 2026-03-04
ROC | March | KBSP - Theodore doing some grinding work, call if fire alarm goes off (289-390-0704) | ROC General | 2026-03-20
ROC | March | Angelica Chepiga signing out | ROC General | 2026-03-27
ROC | March | Carter Dunn Signing Out | ROC General | 2026-03-26
ROC | March | Christian Van Beek signing out. | ROC General | 2026-03-19
ROC | March | Gluzen Ramos Ong signing out | ROC General | 2026-03-27
ROC | March | STPSMR - Drew from Ferguson Electric was on site earlier today and is now leaving. Site is secure. | ROC General | 2026-03-18
ROC | March | KSSP - Garrick from Ferguson electric on site. | ROC General | 2026-03-24
ROC | March | HLPSYS- Dominic from Honeywell onsite. | ROC General | 2026-03-26
ROC | March | Adeela Khan signing in. Weather: 0C and cloudy | ROC General | 2026-03-22
ROC | March | Angelica Chepiga signing in | ROC General | 2026-03-17
ROC | March | Christian Van Beek signing in. Weather: -6C and clear. | ROC General | 2026-03-27
ROC | March | KSSP - Garrick and Drew from Ferguson electric leaving site. | ROC General | 2026-03-18
ROC | March | NMETHW - Kalid from AIM leaving site. | ROC General | 2026-03-16
ROC | March | Connor Smith signing out | ROC General | 2026-03-16
ROC | March | AUPSWS - Kyle R from Maintenance replacing floats. Corrections/ wrong book | ROC General | 2026-03-16
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-29
ROC | March | QVW34 - Joe D onsite, will be running well in man/on to help locate leak. | All Water System ROC General | 2026-03-29
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-29
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-30
ROC | March | MAPS/JFRS- Initiated Maple to Jefferson Feed 03:45- Reverted changes | All Water System ROC General | 2026-03-29
ROC | March | Ethan U signing in Weather 0. | All Water System ROC General | 2026-03-29
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-29
ROC | March | VNP7 - Place pump 1 & 3 auto MAP7 - Place pump 1-3 man/off. Done to pull more from Teston res and less from MARS | All Water System ROC General | 2026-03-29
ROC | March | KCETDS - Outlet total Cl2 res lo, reading came back within range next reading. Cleared alarm | All Water System ROC General | 2026-03-29
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-29
ROC | March | Ethan Ullalkar signing out. | All Water System ROC General | 2026-03-29
ROC | March | SHTP- UV Transmittance OOR CMU5 for Cole W from Friday Night Shift. W11765112 CMU5 Chamber 2311- Chamber Entry Assistance CMU5 for Cole W from Saturday Day Shift requested by Cristina S. W11765120 CMU5 | All Water System ROC General | 2026-03-28
ROC | March | Christian Van Beek creating a test log entry at the request of Jennifer Chung. | All Water System ROC General | 2026-03-28
ROC | March | VNPS- Placed PD7 duty 1 pumps in manual MAPS- Placed PD7 duty 1 pumps in auto | All Water System ROC General | 2026-03-28
ROC | March | HLW1 - Combined chlorine low alarm. Checked site, well was recently placed manual/off. No water being directed to users. Trending shows a dip of the combined chlorine reading following well shutdown is normal. Will continue to monitor site to ensure reading recovers. | All Water System ROC General | 2026-03-29
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-29
ROC | March | AURSBS- Activate duty in preparation for Maple to Jefferson Feed | All Water System ROC General | 2026-03-29
ROC | March | SHTP - Well 2 Uncommanded start alarm. Checked site, the plant is currently active. Able to reset alarm, well activated again. | All Water System ROC General | 2026-03-29
ROC | March | KSETDP - Gas chlorinator 2 fail to close alarm. Checked site, system duty recently deactivated. Chlorinator 2 showing 16% open following duty stop. Able to clear alarm but chlorinator still showing open. The chlorine gas injector solenoid valve is closed and the chlorine booster pump is not active meaning chlorine is not being drawn through the system. Placed chlorinator in manual mode and tried to close, chlorinator did not close. Returned chlorinator to auto mode and sent email to area operations. system duty will not activate until late morning. | All Water System ROC General | 2026-03-30
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-30
ROC | March | MARS - Tegbeer from OCWA called to inform that he will be completing the daily pump switch. Will switch from pump 5 to pump 6 | All Water System ROC General | 2026-03-30
ROC | March | SHTP - Site hydro power failure alarm and associated equipment fault alarms. Checked site, plant was active when the alarms triggered. The generator is not running and the ATS is pointing to utility hydro indicating a short power failure. High lift pumps are currently active and pushing flow to the system, reservoir level is high. No concern for system deactivation at this time. Attempted to reset alarms. Both air compressors on site have failed and are showing in local mode on SCADA, unable to clear alarms. High lift pump 1 has faulted on a VFD fault and cannot be reset. High lift flow is much lower than normal. Contacted Cole W who will attend site to reset the systems that have faulted. Created CMU5#W11768966 #consult #CMU5 | All Water System ROC General | 2026-03-31
ROC | March | STW3 - Jack P. headed to site to assess the LoLo switch alarm and sampling CMU5 Created W11769468 #CMU5 | All Water System ROC General | 2026-03-31
ROC | March | Maximo server down from 10-16:00. Attached are logbook entries | All Water System ROC General | 2026-03-30
ROC | March | NBW3 - Influent Free Chlorine LoLo alarm came in. Checked site. Well was found man/off. Called Jacob M. who is aware and placed the well in manual | All Water System ROC General | 2026-03-31
ROC | March | EZ Max Mobile Access Restored Mar/31/2026 04:00 - 06:45 | All Water System ROC General | 2026-03-31
ROC | March | AUPSRR, Kingsley M resetting OIT on site, Disregard historian heartbeat alarm | All Water System ROC General | 2026-03-31
ROC | March | MAPS PD7, Placed pump 2 man/off VNPS PD7, Placed pump 3 in auto | All Water System ROC General | 2026-03-31
ROC | March | HLETYS, Rick L/Parth P on site working on the Cl2 analyzers | All Water System ROC General | 2026-03-31
ROC | March | ARPS, OCWA operator Martin called, he is rotating pumps on site. Turning off pump 7 and turning on pump 5 | All Water System ROC General | 2026-03-05
ROC | March | GWTP, Rick L on site doing annual calibrations | All Water System ROC General | 2026-03-05
ROC | March | SHTP - David T onsite testing turbidimeter, temp, backwash tank high level, eyewash | All Water System ROC General | 2026-03-05
ROC | March | QVW12 - Lee F finished at site | All Water System ROC General | 2026-03-05
ROC | March | STETBR - Tower Level Hi alarm came in. Placed STW3 back to auto as per interim | All Water System ROC General | 2026-03-10
ROC | March | MKETFA - Peter from Toronto Water called to inform he needs to shut down the active-duty pump to exercise a valve. Informed Peter that out tower level is on the low side, but the short duration exercise should be okay. | All Water System ROC General | 2026-03-12
ROC | March | MTW3 - Travis W onsite for chlorine & silicate inspections, leak detector test, running generator, health & safety, Turb and chlorine maintenance | All Water System ROC General | 2026-03-12
ROC | March | KCETDS - Dave T on site to complete work orders including chlorine analyzer maintenance, hi/low level alarm test and the low temperature alarm. Dave T will be completing an isolation test today, KCETDS will be isolated from the distribution system and the system will be supplied by KCETFS and the wells. | All Water System ROC General | 2026-03-12
ROC | March | AUPSRR - Ammonia pump 2 uncommanded stop alarm. Duty recently activated. Cleared alarm. System restarting. | All Water System ROC General | 2026-03-09
ROC | March | QVW12 - Sean P onsite to run site with generator. Deactivated duty to NMETHW. | All Water System ROC General | 2026-03-12
ROC | March | ARPS, Binnish from OCWA is stopping pump 6 and starting pump 5 STW3, Placed well 3 man/on as STETBR is filling | All Water System ROC General | 2026-03-13
ROC | March | ARPS - David from Peel informed of another switch to pumps, placing pump 6 in duty 1 NBW5 - Discharge press lolo, well shutoff. Followed up with Jacob M onsite. chlorine injector blew off, working on well now. | All Water System ROC General | 2026-03-12
ROC | March | NBW5 - Jake M finished and leaving site. Jake is leaving the well manual/off. OCO Jordan B will decide if the well goes back into service. | All Water System ROC General | 2026-03-12
ROC | March | Wrong logbook | All Water System ROC General | 2026-03-05
ROC | March | NMW12- Treated total chlorine and combine chlorine residual low alarms. Well not active no water directed to users. Will continue to monitor. | All Water System ROC General | 2026-03-03
ROC | March | NMW136- Influent Free Chlorine HiHi Alarm. Recovered next reading. Cleared alarm. | All Water System ROC General | 2026-03-12
ROC | March | QVW34 - Will M onsite testing chlorine leak | All Water System ROC General | 2026-03-12
ROC | March | AUPSOH - Joe D onsite running generator and chlorine analyzer, placing pumps man/off. | All Water System ROC General | 2026-03-12
ROC | March | NMW136 - Christian B onsite w Ben H to work on chlorine, silicate, and ammonia system | All Water System ROC General | 2026-03-12
ROC | March | GWTP - ZW2 membrane tank level hi alarm. Checked site, filter 2 is going through a cleaning process. Trending shows the tank level is slightly above the tank high level alarm. Will monitor site, tank level should drop and cleaning sequence progresses. | All Water System ROC General | 2026-03-09
ROC | March | MMW1, Dan B called, informed ROC that the power has been restored on site, Dan B switching generator off to go back to utility power | All Water System ROC General | 2026-03-13
ROC | March | YWS + NYWS NORMAL Angelica Chepiga signing out | All Water System ROC General | 2026-03-11
ROC | March | Ethan U signing in | All Water System ROC General | 2026-03-11
ROC | March | NBW3 - Influent free chlorine lolo alarm. Checked site, well recently activated in schedule mode. Trending shows a sharp dip of the influent free chlorine reading which interlocked the well pump. The influent free chlorine reading recovered quickly after the interlock. Placed the well manual/off, rotated the chlorinator duty back to chlorinator 2. Placed the pump back in auto mode and cleared alarms. Monitored well start. | All Water System ROC General | 2026-03-09
ROC | March | YWS + NYWS NORMAL Angelica Chepiga signing out | All Water System ROC General | 2026-03-03
ROC | March | STW12 - Place well 1 back in auto STW3 - Place well back in auto | All Water System ROC General | 2026-03-15
ROC | March | Ethan Ullalkar signing out. | All Water System ROC General | 2026-03-15
ROC | March | GRTPLL - Low Lift Surge Relief Valve Open alarm at duty shutdown, was able to clear alarm. | All Water System ROC General | 2026-03-15
ROC | March | QVW12, Donald M is leaving site, requested that the well run for a few hours after it clears the contact tank. When it reaches 21:00, will place the well back to auto QVW34, While Donald M was leaving site, notified Donald M that QVW3 is currently man/off, directed to leave it off at this time, directed to rotate duty so well 3 is in D5 and well 2 is in D2. | All Water System ROC General | 2026-03-06
ROC | March | BVOPLAM Server- Kingsley M rebooting server | All Water System ROC General | 2026-03-06
ROC | March | KSTP - Carbon Dioxide HiHi alarm came in. Checked site. Duty recently deactivated. Value was still within hihi levels. Called Stephen B. Levels went back to optimal range and alarm cleared on its own. Stephen B. directed to give a call back if this alarm comes back in. GWTP - High Lift Free Chlorine Lo alarm came in. Stephen B. directed to disregard alarm as there may be an issue with the analyzer. Would like a call back if the clearwell is affected #CONSULT | All Water System ROC General | 2026-03-01
ROC | March | MMW1- Terry C and Sean P done on site generator should have enough fuel until tomorrow afternoon. Terry C has truck with fuel and will refuel tomorrow. If generator fails due to lo fuel Terry C will attend site | All Water System ROC General | 2026-03-07
ROC | March | YWS+NYWS normal | All Water System ROC General | 2026-03-07
ROC | March | STRS48 - Hi lift pump 1 failed to stop alarm came in. Checked site. Both pumps are off. Ack/reset alarm and alarm cleared | All Water System ROC General | 2026-03-01
ROC | March | MTW12- Travis W on site for turbidity analyzer maintenance | All Water System ROC General | 2026-03-06
ROC | March | NBW5 - Turbidity hi alarm came in. Checked site and well is running. Noticed turbidity levels trended upwards and then rapidly came back down. Still within hi limits. Called Jacob M. who informed he is on site flushing and triggered this alarms | All Water System ROC General | 2026-03-04
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-05
ROC | March | VNPS- Placed PD7 Pump 2 in manual MAPS- Placed PD7 Pump 3 in auto | All Water System ROC General | 2026-03-04
ROC | March | KSTP, Raw Water Turbidity Fault, as per Jack P shift report, directed to disregard | All Water System ROC General | 2026-03-06
ROC | March | VNRSKS - Switched feed from MAPS PD7(pumps 2,3 man/off) to VNPS PD7 (pumps 2,3 to auto). | All Water System ROC General | 2026-03-08
ROC | March | NMW15- Influent free chlorine residual low alarm, quick dip at duty start . Alarm cleared. NMW136 - Influent free chlorine Hi alarm, quick spike at duty start. Alarm cleared. | All Water System ROC General | 2026-03-08
ROC | March | JFRS - Deactivated duty 1 and 2 in preparation for MAPS to JFRS Feed run | All Water System ROC General | 2026-03-01
ROC | March | KSETDP- Post Injection Free Chlorine Lo Alarm. Tower is offline and isolated. | All Water System ROC General | 2026-03-01
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-01
ROC | March | GWTP - Parth P, Rick L and Art P on site to start annual calibrations. | All Water System ROC General | 2026-03-04
ROC | March | ARPS- Jerry from Peel called. Communication alarm shut down their pump. Working on getting it back up and running. He will call back with an update. | All Water System ROC General | 2026-03-10
ROC | March | HLW2 - Treated total chlorine lolo, combined chlorine lolo. Well is man/off | All Water System ROC General | 2026-03-12
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-05
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-08
ROC | March | AUW14 and AUW57 - Placed all well man/off to let AURSBS drain due to higher levels at MARS | All Water System ROC General | 2026-03-09
ROC | March | MKETFA - Toronto Water (Brett) called and informed that they are turning pump off and testing PRV in their system. | All Water System ROC General | 2026-03-09
ROC | March | Christian Van Beek signing out. | All Water System ROC General | 2026-03-10
ROC | March | RHRSTR - Deactivated duty 1. | All Water System ROC General | 2026-03-11
ROC | March | NMW12 - Influent free chlorine residual HiHi alarm at duty start up. Value back to normal, cleared alarm. | All Water System ROC General | 2026-03-11
ROC | March | NBW2 - Influent chlorine residual low alarm, Well 2 pump stopped and restarted right away. Influent chlorine residual low on start up, Value recovered, alarm cleared. | All Water System ROC General | 2026-03-09
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-09
ROC | March | NMMCBR - Upstream Pressure LoLo alarm came in. Checked site. Trends show a steep drop in pressure. No flow through the flowmeter. Not indicative of flushing. Called Rob P. but no answer. Will try again. 23:20 - Called Rob P. again who informed there is a WM break for East Gwillimbury and needed to close a valve which triggered this alarm. 00:18 - Rob P. called back to inform that the WM repair is complete and Rob has reopened the valve. Rob informed that all alarms can be cleared #CONSULT | All Water System ROC General | 2026-03-09
ROC | March | STW12 - Place well 1 man/on for Zone 1 fill cycle STW3 - Place well 3 man/on Stouffville - Lane W from town of Stouffville flushing at hydrant zone (2416-366-6675) | All Water System ROC General | 2026-03-05
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-01
ROC | March | STETBR - Tower Level Hi alarm came in. Placed STW2 and STW3 back to auto as per interim | All Water System ROC General | 2026-03-01
ROC | March | Connor Smith signing in -12 C Clear | All Water System ROC General | 2026-03-01
ROC | March | Adeela Khan signing out | All Water System ROC General | 2026-03-01
ROC | March | NMVCBA - Placed valve in man/open at 30 L/s | All Water System ROC General | 2026-03-01
ROC | March | SHTP - Tim H and Murray from Honeywell on site to complete a hydro meter change. Tim H directed to place the well 2 pump in manual and then off and to placed well pump 3 in auto and duty 1. | All Water System ROC General | 2026-03-10
ROC | March | GWTP - John D. noted him and Yash S. still working on network. Plant is currently not active but HLP in auto. Placed HLP man/off. John and Yash on site, they will notify ops | All Water System ROC General | 2026-03-10
ROC | March | QVETQS - Inlet free chlorine hihi alarm. Checked site, tower is currently draining. Trending shows a steady increase of the inlet free chlorine over the past couple of days. The inlet free chlorine reading has dropped below alarm setpoint. Cleared alarm and sent an email to area ops. 07:38 - QVETQS - inlet free chlorine hihi alarm. Alarm would not clear as it is a switch alarm. Area ops are aware. | All Water System ROC General | 2026-03-09
ROC | March | VNPS PD7 - Pump 2 man/off MAPS PD7- Pump 4 to auto, to help with RHRSTR level. | All Water System ROC General | 2026-03-02
ROC | March | YWS + NYWS Normal MKRSEM, Notified Toronto operator Paul to start 2 pumps to fill the res | All Water System ROC General | 2026-03-05
ROC | March | GWTP, ZW5 Shutdown/turbidity hihi alarm, contacted Jack P, directed to place filter in the off position, he will go on to SCADA to investigate further consult | All Water System ROC General | 2026-03-05
ROC | March | GWTP - Jack P called nack, leaving train 5 off for the night | All Water System ROC General | 2026-03-05
ROC | March | MKETFA, Paul from Toronto called, they will be circulating water from one of their pipes/valves. They will be turning off one of their pumps to do this work. The work should only take 15 minutes, once completed, pumps will go back to normal operation | All Water System ROC General | 2026-03-05
ROC | March | Christian Van Beek signing in. | All Water System ROC General | 2026-03-03
ROC | March | Christian Van Beek signing in. Weather: 2C and rain. | All Water System ROC General | 2026-03-05
ROC | March | GWTP - GAC 4 flow control valve deviation alarm. Checked site, GAC 4 flow control valve is open and operations appear normal. Shift report states that the GAC 4 effluent valve deviation alarm is a disregard. After carefully reviewing the valve name on SCADA it was clear that the effluent valve and the flow control valve are the same valve and this is the alarm that is a disregard on the shift report. | All Water System ROC General | 2026-03-05
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-05
ROC | March | ARPS- Jerry from Peel changing pumps from 6 to 1. Then at noon will be changing from pump 1 to 12. | All Water System ROC General | 2026-03-10
ROC | March | NMETHW - Arthur L completing work on the OIT and has directed to disregard the historian heartbeat alarm. | All Water System ROC General | 2026-03-04
ROC | March | SHTP - John D. informed that he will be conducting minor upgrades to the site and requested the pumps be placed in manual. Called Jen S. who directed to deactivate the plant. Called John D. and relayed this information and he informed that he will start his upgrades when the plant shut downs. John will give the ROC a call back when he is finished 12:45 - John called back to inform that he is finished working on SHTP | All Water System ROC General | 2026-03-04
ROC | March | KSTP - CO2 Adjusted pH LoLo alarm came in. Shift report directs to disregard Raw Water pH alarms. After checking site, noticed that the plant is active but the CO2 Adjusted pH has taken a dip and the pH is recovering. This alarm triggered the high lift pumps to interlock. Will continue to monitor 04:16 - Settled Water Conduit Level LoLo alarm came in along with Filter 1 and 2 Level Called Jack P. who directed to ack/reset alarms. CO2 Adjusted pH alarm cleared which lifted the interlock on the low lifts. Jack P. informed it will take some time for the water to reach the filter and then to the conduit. Jack P. would like a call back if any other alarms come in for KSTP 04:40 - Alarms have cleared #CONSULT | All Water System ROC General | 2026-03-09
ROC | March | STW12- Communication Failure. Alarm cleared after a few minutes. | All Water System ROC General | 2026-03-05
ROC | March | KSTP - CO2 adjusted pH LoLo alarm. Checked site, plant is currently active. Low lift pumps interlocked on the low low pH alarm. Trending shows the CO2 adjusted pH reading is increasing. Reset alarm when the reading recovered above the lolo alarm setpoint. Monitored low lift pump start up. | All Water System ROC General | 2026-03-05
ROC | March | YWS + NYWS NORMAL | All Water System ROC General | 2026-03-02
ROC | March | KSTP - Post chlorinator 2 low vacuum alarm. Checked site, post chlorinator 1 rotated into duty 1 and is operating. Able to clear alarm. | All Water System ROC General | 2026-03-02
ROC | March | ANW23 - Dave T on site to complete work orders including a generator test, chlorine analyzer maintenance and turbidity analyzer maintenance. Dave directed to disregard associated alarms. | All Water System ROC General | 2026-03-03
ROC | March | AUPSRR - Post-injection free chlorine hihi alarm. Checked site, trending shows a sudden spike of the post injection free chlorine reading which returned to normal within one reading interval. Reset alarm. | All Water System ROC General | 2026-03-04
ROC | March | HLETYS- Noticed that Pre Injection Total and Combined Chlorine has significantly dropped lower than normal during drain cycle causing an abnormal trend. Currently reading Combined 0.43mg/L. Post Injection readings appear normal. No alarm triggered. Notified Benson S. He will log onto SCADA and take a look. 15:01- Benson S called back. Duty now active and Post Injection Combined Chlorine HiHi alarm came in. He will call ORO and call back if attending site. 15:22- Benson S requested a call if Post Injection stays above 4.0Mg/L for several minutes or if Pre Injection combined stays below 0.45 for several minutes. 15:30- Pre-Inj Combined value still dropping, Post Injection Combined HiHi Alarm coming in and out. Notified Benson S. he will attend site. Requested to deactivate duty and change duty start from 35 to 25% W11697567 CMU5 | All Water System ROC General | 2026-03-01
ROC | March | MKRSEM- Called Toronto water(Zoran) and requested to stop filling Res. | All Water System ROC General | 2026-03-08
ROC | March | VNRSKS - Deactivated duty due to low levels at RHRSTR. Placed all pumps at VNPS PD7 man/off and placed pumps 1-3 at MAPS PD7 in auto | All Water System ROC General | 2026-03-08
ROC | March | KSTP - Jason G on site to complete a generator test, turbidity analyzer maintenance, treated water analyzer maintenance and will complete the raw water analyzer maintenance if time allows. | All Water System ROC General | 2026-03-03
ROC | March | STW3 - Placed in manual/currently running for STETBR fill cycle. STW12 - Jack P directed to place wells 1 and 2 pumps man/off and use well 1 only in emergency until farther notice. Hypo tank 1 has a leak. | All Water System ROC General | 2026-03-09
ROC | March | STW12, STW3- Placed wells back into auto for completion of STETBR Fill cycle | All Water System ROC General | 2026-03-04
ROC | March | AUETAD, Jerry Z on site testing lo temp alarm | All Water System ROC General | 2026-03-05
ROC | March | MAPS Server, Kingsley M restarting the server | All Water System ROC General | 2026-03-05
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-15
ROC | March | MKMCTA - Building security intrusion alarm. Checked site, alarm system is armed and security intrusion status is active. Acknowledged and reset alarm, alarm cleared. | All Water System ROC General | 2026-03-02
ROC | March | YWS + NYWS NORMAL | All Water System ROC General | 2026-03-08
ROC | March | SHTP - Reservoir chlorine low alarm. Checked site, plant and high lift pumps are active. Trending shows a dip of the reservoir chlorine residual reading which recovered to normal range within ten minutes. Cleared alarm. | All Water System ROC General | 2026-03-03
ROC | March | SHTP - Reservoir total chlorine fault alarm. Jen S on site replacing tubing that may trigger alarms. | All Water System ROC General | 2026-03-03
ROC | March | MKRSEM, Notified Toronto operator Peter to stop pumping to the res | All Water System ROC General | 2026-03-07
ROC | March | SCADA - Incident report came through via email. Medium priority. Informed Ian w, forwarded email. Ian following up with Network on-call Evgeny S 17:39 - Ian W called back and results were a false positive. | All Water System ROC General | 2026-03-12
ROC | March | MKPSSA - Sean P on site to complete a generator load bank test. | All Water System ROC General | 2026-03-10
ROC | March | AUW57 - Influent free chlorine hi, influent free chlorine hihi, treated free chlorine hi. Issue rose during start up of well. monitored. Rotated ammonia pump 2 duty 1. Dropped chlorinator 1 dosing from 109 to 103. chlorinator 2 OOS. Monitored influent reading coming back down slowly. Dosing factor kept adjusting as influent remained hi slowly dropping and dosing came down all the way to 90. effluent free and combined chlorine were picking up on the other end of contact tank. Placed well 5 man/off to prevent hihi alarm on effluent. Informed Joe D | All Water System ROC General | 2026-03-03
ROC | March | STRS48 - Dominic from Honeywell on site to complete maintenance on the security system. | ROC General | 2026-03-02
ROC | March | Adeela Khan signing out | ROC General | 2026-03-02
ROC | March | Connor Smith signing in -16C Clear | ROC General | 2026-03-02
ROC | March | Christian Van Beek signing in. | ROC General | 2026-03-02
ROC | March | VNRSKS - Swapped supply pumps to one MAPS and one VNPS pump to equalize demand on MARS and RHRSTR. | All Water System ROC General | 2026-03-02
ROC | March | NMETHW - Deactivated duty 1 to maintain level offset from NMETIB. | All Water System ROC General | 2026-03-02
ROC | March | YWS + NYWS Normal Adeela Khan signing out | All Water System ROC General | 2026-03-02
ROC | March | STETBR - Low level alarm. Duty activating soon. Placed STw2 and STW3 manual/on as per the interim procedure. | All Water System ROC General | 2026-03-02
ROC | March | Connor Smith signing in -16C Clear | All Water System ROC General | 2026-03-02
ROC | March | ARPS- Jerry from OCWA called to inform will be rotating from pump 6 to pump 5. | All Water System ROC General | 2026-03-02
ROC | March | AUW14 - Security intrusion alarm, FMC will notify Corp security. | ROC General | 2026-03-12
ROC | March | STETBR - Security intrusion alarm, FMC will call Corp security. | ROC General | 2026-03-12
ROC | March | NMVCBA - Placed back to auto. | All Water System ROC General | 2026-03-12
ROC | March | SHTP - Well pump 2 uncommanded start alarm. Plant is not active. Well pump 2 recently stopped. Cleared alarm. | All Water System ROC General | 2026-03-12
ROC | March | MKRSEM - Called Toronto water (Puria ) and requested to start filling Res. | All Water System ROC General | 2026-03-12
ROC | March | STETBR- Tower level Hi alarm. Placed STW3 back to auto. | All Water System ROC General | 2026-03-12
ROC | March | MARS - High level alarm, deactivated RHRSTR duty 1. | All Water System ROC General | 2026-03-12
ROC | March | YWS + NYWS NORMAL | All Water System ROC General | 2026-03-12
ROC | March | YWS + NYWS NORMAL | All Water System ROC General | 2026-03-12
ROC | March | VNPSCD - Sani Sump pumps 1&2, Sump Pumps 1&2 Fault alarms. No High level alarms. Emailed area, disregard as per SCADA report. | All Water System ROC General | 2026-03-12
ROC | March | AUPSRR - Post-injection Free chlorine Hi and HiHi alarms. Quick spike for one reading. Duty recently activated. Alarms cleared. | All Water System ROC General | 2026-03-12
ROC | March | YWS + NYWS NORMAL | All Water System ROC General | 2026-03-12
ROC | March | Ethan U signing in Weather 1. | ROC General | 2026-03-23
ROC | March | Adeela Khan signing out | ROC General | 2026-03-23
ROC | March | MARS- Cell1 (North) Lvl Hi Alarm. AURSBS- Activated duty | All Water System ROC General | 2026-03-13
ROC | March | KSTP - Clearwell Influent Free chlorine residual Low alarm. Plant is not running. Will monitor. Placed High lift P3/duty 1 man/off. Will notify OP first thing in the morning. 05:30 Clearwell influent Free chlorine residual slowly dropping. Notified Joe M. He will check SCADA. # Consult | All Water System ROC General | 2026-03-12
ROC | March | SHTP- Filter 2 Turbidity Hi, Filter 3 Turbidity Hi. Backwash just completed. Disregard as per SCADA Report. | All Water System ROC General | 2026-03-13
ROC | March | ANW23, Discharge Pressure lolo alarm, Notified Tim H of these observations, directed to place pump 2 into D2, Will contact Jordan B of these changes. | All Water System ROC General | 2026-03-05
ROC | March | AUW14, Placed wells 2/3 in manual/off so that more water can be moved from AURSBS | All Water System ROC General | 2026-03-16
ROC | March | yws + nyws normal | All Water System ROC General | 2026-03-16
ROC | March | KSTKWP- Total Chlorine Low Low Sw Alarm. Tower Filling. Value recovered. Cleared alarm. | All Water System ROC General | 2026-03-13
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-13
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-04
ROC | March | Carter Dunn Signing In, -2D/Clear | All Water System ROC General | 2026-03-04
ROC | March | Adeela Khan signing in. Weather: 0C and snowing | All Water System ROC General | 2026-03-13
ROC | March | GWTP - Eric S. called to inform that he and Rick L. are finished on site | All Water System ROC General | 2026-03-13
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-04
ROC | March | MAPS PD7, Placed pumps 2/3 to auto VNPS PD7, Placed all pumps back to man/off | All Water System ROC General | 2026-03-06
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-06
ROC | March | NMETIB - Activated D1 to offset NMETHW. | All Water System ROC General | 2026-03-09
ROC | March | SHTP - Res total chlorine lo. Informed Jen S, is aware due to changeover of cell. | All Water System ROC General | 2026-03-11
ROC | March | NBW5 - Noticed turbidity increasing, reduce pump 1 & 2 max flow from155 to 145. | All Water System ROC General | 2026-03-11
ROC | March | MARS - Reservoir lo level AURSBS - Deactivate duty 1 JFRS - Activate duty 2 as duty 1 active but duty 2 was not triggered on down cycle | All Water System ROC General | 2026-03-13
ROC | March | Ethan Ullalkar signing out. | All Water System ROC General | 2026-03-14
ROC | March | AURSBS, Activated D1 to help draw water from MARS | All Water System ROC General | 2026-03-14
ROC | March | ARPS, David from OCWA called, he is rotating his pumps so pump 7 is now the lead pump. (From pump 5) | All Water System ROC General | 2026-03-14
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-01
ROC | March | YWS + NYWS Normal Connor Smith signing out | All Water System ROC General | 2026-03-01
ROC | March | NMVCBA - Placed valve back to auto MKRSEM - Called Toronto Water (Paul) and requested to stop pumping to reservoir | All Water System ROC General | 2026-03-02
ROC | March | GWTP - Low Lift Flood alarm came in. Called Joe M. who will take a look. | All Water System ROC General | 2026-03-13
ROC | March | HLETYS - Tower mixer VFD fault, mixer uncmd stop. Able to clear but returns shortly after. Informed David T who will attend site later | All Water System ROC General | 2026-03-03
ROC | March | MKRSEM, Contacted Toronto operator Paul to start 2 pumps at the res | All Water System ROC General | 2026-03-14
ROC | March | MTW12 - Silicate pump 2 fault. Unable to clear fault, silicate pump 1 running duty 1 okay. Placed silicate pump 2 man/off | All Water System ROC General | 2026-03-14
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-02
ROC | March | VNPS- Benson S onsite. Requested to activate BVPS. | All Water System ROC General | 2026-03-11
ROC | March | JFPS - RES temperature alarm. Checked site, no temperature reading available. Alarm triggered this past weekend and was a disregard by the on call operator. Disregard again and sending email to area ops. | All Water System ROC General | 2026-03-09
ROC | March | HLW1- Treated Free Chlorine Hi Alarm. Notified Jordan B. Requested to rotate Ammonia pumps so pump 2 running and place pump 1 in manual | All Water System ROC General | 2026-03-11
ROC | March | STW1/3, Placed wells man/on, STETBR currently filling | All Water System ROC General | 2026-03-14
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-13
ROC | March | STPSMR, Patrick F on site, testing Cl2 leak/scrubber alarms and doing health and safety alarms | All Water System ROC General | 2026-03-05
ROC | March | QVW12 - Treated Free chlorine residual Hi alarm. Alarm cleared. | All Water System ROC General | 2026-03-11
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-14
ROC | March | MAPS PD7, Placed pump 2 back to man/off VNPS PD7, Placed pump 2 to auto | All Water System ROC General | 2026-03-14
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-14
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-14
ROC | March | NMETHW - Activated Duty 1 @ 42% to offset NMETIB. | All Water System ROC General | 2026-03-15
ROC | March | Carter Dunn Signing in, 3D/Clear | All Water System ROC General | 2026-03-15
ROC | March | KSTP - Settle water turbidity hi. Conduit level dropped to lolo level. CO2 adjusted pH lolo, locking out low lifts feeding to settle tank. Deactivated duty to stop highlifts as near duty stop. Found raw water turbidity value sporadic on trend reading (email con-call operator). Filter 1 & 2 hit lo but went to normal after low lifts came back on with CO2 adjusted pH going back within range. Deactivated duty 1 as duty near stop | All Water System ROC General | 2026-03-14
ROC | March | VNP7 - Man/stop pump 3 & 2 MAP7 - Place pump 2 & 3 auto | All Water System ROC General | 2026-03-14
ROC | March | GWTP - Contact tank 1 free chlorine lolo, Joe M called and is aware of alarm informed he will deactivate duty and put highlift pump 1 or 2 duty 1 | All Water System ROC General | 2026-03-14
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-14
ROC | March | YDSS + YNSS Normal | All Water System ROC General | 2026-03-15
ROC | March | Carter Dunn Signing Out | All Water System ROC General | 2026-03-26
ROC | March | ARPS - Peter from OCWA called, OP on site for chemical system maintenance/ system in maintenance mode for 30 - 40 minutes. | All Water System ROC General | 2026-03-18
ROC | March | STW3 - Jack P called to inform he would like to be contacted if the halogen valve system activates. VNRSKS - Swapped supply pumps from ONE VNPS and one MAPS pump to two MAPS pumps. | All Water System ROC General | 2026-03-18
ROC | March | YWS + NYWS Normal Christian Van Beek signing out. | All Water System ROC General | 2026-03-18
ROC | March | Connor Smith signing out | All Water System ROC General | 2026-03-25
ROC | March | Angelica Chepiga signing in | All Water System ROC General | 2026-03-17
ROC | March | GWTP - Joe M backwashing GAC3, requested disregard alarms. | All Water System ROC General | 2026-03-17
ROC | March | YWS + NYWS Normal Connor Smith signing out | All Water System ROC General | 2026-03-17
ROC | March | AUVCBS - PAC communication failure alarm. Notified Artour L. He will troubleshoot # CMU5 W11762057 | All Water System ROC General | 2026-03-26
ROC | March | YWS + NYWS normal | All Water System ROC General | 2026-03-27
ROC | March | STPSMR - Lee F will attend site, requested to assign P1 to Duty 1, P2 to Duty 2. | All Water System ROC General | 2026-03-16
ROC | March | GWTP - GAC 4 Flow Control Valve Deviation Alarm came in. Disregarded as per shift report | All Water System ROC General | 2026-03-19
ROC | March | NMETIB- Activated duty | All Water System ROC General | 2026-03-16
ROC | March | MKETFA- Toronto (Puolia) called and is shutting down pump for 5 minutes, then will start back up. | All Water System ROC General | 2026-03-17
ROC | March | NMETIB- Deactivated duty | All Water System ROC General | 2026-03-20
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-18
ROC | March | Christian Van Beek signing in. | All Water System ROC General | 2026-03-18
ROC | March | Carter Dunn Signing Out | All Water System ROC General | 2026-03-23
ROC | March | Connor Smith signing in | All Water System ROC General | 2026-03-24
ROC | March | KCETDS- Tim H onsite placing tower back online. | All Water System ROC General | 2026-03-26
ROC | March | AUVCBS- PAC Communication Alarm. Alarm cleared. | All Water System ROC General | 2026-03-26
ROC | March | KSTP - Chlorine gas leak alarm and chlorine emergency valve closure alarms. Jason G called to inform he completed the chlorine leak test and everything is okay. | All Water System ROC General | 2026-03-18
ROC | March | NMW12 - Silicate pumps 1&2 OOS. Duty deactivated recently. Christian B and Ben H on site troubleshooting silicate pumps. | All Water System ROC General | 2026-03-27
ROC | March | HLETYS - Kevin W rebooted cellular APN modem using backup communication. | All Water System ROC General | 2026-03-16
ROC | March | KSTKWP - Jerry Z. is on site and will be testing the chlorine leak alarm | All Water System ROC General | 2026-03-23
ROC | March | HLW2 - Influent chlorine residual HiHi alarm. Adjusted chlorinator dosing factor from 179 to 169%. Influent chlorine residual still HiHi. Rotated chlorinators, 1 on duty 1. Notified Jordan B, he will check SCADA. Influent chlorine residual value back to normal. Was able to clear alarm. | All Water System ROC General | 2026-03-26
ROC | March | NMVCBA-Placed valve manual 30L/s to assist in NMETHW and NMETIB offset | All Water System ROC General | 2026-03-19
ROC | March | Connor Smith signing in -3C Cloudy | All Water System ROC General | 2026-03-25
ROC | March | KSETWB - Phil D. is on site and will be testing the Chlorine Leak alarm | All Water System ROC General | 2026-03-23
ROC | March | NMTKKC - Ammonia Pump 1 speed signal/leakage alarms. Eric S working on it. | All Water System ROC General | 2026-03-24
ROC | March | NMTKKC- Valve Chamber Eyewash 1,2 Flow Switch Alarms. Called Joe W. He is onsite testing. | All Water System ROC General | 2026-03-16
ROC | March | STPSMR - Patrick F. is on site and will be completing chlorine analyzer maintenance 11:40 - Patrick called back to inform he is now at BVPS and will be running the diesel generator under the load of two pumps | All Water System ROC General | 2026-03-23
ROC | March | QVW34 - Well 3 pump uncommanded stop alarm. Notified Ben H. He is on his way to site. | All Water System ROC General | 2026-03-17
ROC | March | JFPS- Lee F requested to place pump 2 man/off. Place pump 3 back in auto. After running pump 1 for one hour place in duty 2 and place pump 4 as second duty 1 pump. 11:08- Placed pump 1 man/of and switched to auto duty 5. Placed pump 4 in auto duty 1. | All Water System ROC General | 2026-03-17
ROC | March | JFPS- Tyler ZJ onsite working on pump 1. | All Water System ROC General | 2026-03-25
ROC | March | AUETFC - Joe D on site to deactivate duty for sampling. | All Water System ROC General | 2026-03-25
ROC | March | STW3 - Jack P heading to site, will work on silicate system. | All Water System ROC General | 2026-03-26
ROC | March | RHPSPA- Dan B called. He and Ernie H are exercising surge valves which triggered alarms PD7 Surge Valve 1,2 Open Alarms on SCADA. Work is completed. Cleared alarms. | All Water System ROC General | 2026-03-19
ROC | March | NRETCR - Activated duty 1 to drawdown JFRS in preparation for the Maple to Jefferson Feed. | All Water System ROC General | 2026-03-22
ROC | March | AURSBS - Activated duty 1 to fill the reservoir in preparation for the Maple to Jefferson Feed. | All Water System ROC General | 2026-03-22
ROC | March | Reverting Maple to Jefferson Feed. | All Water System ROC General | 2026-03-22
ROC | March | MKRSEM - Request TO (Zoran) to drop both pumps | All Water System ROC General | 2026-03-23
ROC | March | Angelica Chepiga signing in | All Water System ROC General | 2026-03-27
ROC | March | ARPS - Peel Ammonia Analyzer B (AIT 1B, AIT 4B, AIT 5B) Airport Rd discharge alarms. Notified Peter from OCWA, he confirmed with OP/instrumentation that alarms from Backup unit, no effect to system. They are performing maintenance on the unit. Requested disregard alarms. | All Water System ROC General | 2026-03-18
ROC | March | NRETCR - Lee F called to inform he finished his work on the altitude valve. Lee F requested that the valve be placed in auto mode and the system duty activated to test the valve opening sequence. Made the necessary adjustments, the valve opened. Lee F leaving site. Swapped controlling tower back to NRETCR | All Water System ROC General | 2026-03-27
ROC | March | HLW2- Ammonia Pump 1 Fault Alarm. Pump 2 took over in duty 1. Cleared alarm Treated Free Chlorine HiHi Alarm. Cleared alarm. | All Water System ROC General | 2026-03-19
ROC | March | NMW136 - Alex B on site to complete an ammonia system inspection. | All Water System ROC General | 2026-03-27
ROC | March | VNPS- Placed PD7 pump 1 man/off MAPS- Placed PD7 pump 2 in auto | All Water System ROC General | 2026-03-20
ROC | March | JFPS- Chris I called and notified will be placing pump 2 OOS and locking out for repairs. | All Water System ROC General | 2026-03-20
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-20
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-21
ROC | March | HLW2- Well 2 Pump Failed to Stop. Came in on duty stop. Alarm cleared. Well 2 Pump Waste Valve Open Alarm. Interlocked well. Alarm cleared after a few minutes and interlock was cleared. | All Water System ROC General | 2026-03-24
ROC | March | Adeela Khan signing in. Weather: 0C and cloudy | All Water System ROC General | 2026-03-22
ROC | March | Carter Dunn Signing Out | All Water System ROC General | 2026-03-16
ROC | March | Connor Smith signing in | All Water System ROC General | 2026-03-19
ROC | March | STETTL - Activated duty 1 to top up the tower for the interim procedure. | All Water System ROC General | 2026-03-19
ROC | March | MKRSEM - Toronto Water (Peter) called to state that Toronto Operations would like two pumps to push flow to MKRSEM for thirty minutes to complete sampling. Informed Peter that this is acceptable and that the reservoir has room to accommodate this flow. | All Water System ROC General | 2026-03-19
ROC | March | GWTP - Clearwell 2 chlorine low alarm. Patrick F on site, made chlorine adjustments. Alarm should clear. Microfiltration room low temperature alarm. Patrick F checked site/normal. Requested disregard alarm. | All Water System ROC General | 2026-03-24
ROC | March | STW3- Yash S called and requested well man/off for network shutdown work. | All Water System ROC General | 2026-03-19
ROC | March | MKRSEM - Called Toronto water(Paul) and requested to stop filling Res. | All Water System ROC General | 2026-03-20
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-22
ROC | March | GWTP- Parth P finished onsite. | All Water System ROC General | 2026-03-25
ROC | March | NMTKKC- Valve Chamber Eyewash 1 Flow Switch Alarm. Called Jason G. No answer. Will follow up. 13:51- Jason G will take a look | All Water System ROC General | 2026-03-26
ROC | March | YWS + NYWS NORMAL | All Water System ROC General | 2026-03-26
ROC | March | Angelica Chepiga signing out | All Water System ROC General | 2026-03-26
ROC | March | STW12- Placed well 1 man/on STW3- Placed well 3 man/on for STETBR fill cycle Interim Procedure | All Water System ROC General | 2026-03-24
ROC | March | KSTKWP - Site Hydro Power Failure and CL2 Emergency Closure system fault alarm came in. Checked site. Tank is draining. Likely a power blip. CL2 Emergency Valve Closure system fault alarm is outstanding. Called Patrick F. who informed that this alarm should clear on its own. 17:58 - Alarm did not clear and chlorine system has been running. Called Patrick F. who informed it can be disregarded until tomorrow. #CONSULT | All Water System ROC General | 2026-03-22
ROC | March | KCETDS, Khalid from IAM is on site | All Water System ROC General | 2026-03-23
ROC | March | Angelica Chepiga signing out | All Water System ROC General | 2026-03-16
ROC | March | SHTP - Filter 2 turbidity. Checked site, filter 1 is completing a backwash sequence. Trending shows a turbidity spike in filter 2 which quickly dropped to normal range. Alarm has been cleared. | All Water System ROC General | 2026-03-18
ROC | March | ARPS- Tegber from OCWA called and will switch from pump 5 to pump 6. | All Water System ROC General | 2026-03-25
ROC | March | MKRSEM- Called Zoran from Toronto and requested two pumps on | All Water System ROC General | 2026-03-25
ROC | March | VNPS PD7 - Benson S requested Pump man/off. Deactivated Duty 1, Placed Pump 2man/off. | All Water System ROC General | 2026-03-17
ROC | March | BLW3- Patrick F and Jack P onsite changing Cl injectors. Disregard related alarms. | All Water System ROC General | 2026-03-24
ROC | March | BLW3 - Travis W working on chlorine, silicate systems. Backflushing. He placed Well 3 pump local/off. | All Water System ROC General | 2026-03-26
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-17
ROC | March | GWTP- Jackie S testing multiple flood and sump alarms including chemical room. | All Water System ROC General | 2026-03-17
ROC | March | VNPS- Called Benson S to inquire if able to start running PD8 Pumps. Finished with power transfer. Placed PD8 pumps 1 and 3 back into auto. Pump 2 is OOS with "Pump 2 Not Ready Alarm". Currently Man/off. Benson will look into it. | All Water System ROC General | 2026-03-17
ROC | March | STPSMR- Ian W working on OIT. Has repointed the tags and bypassed the HRBT alarm so pumps will keep running during work | All Water System ROC General | 2026-03-17
ROC | March | STETTL-Outlet Free chlorine Low alarm. TWR is filling. Jack P cleaning chlorine analyzer. | All Water System ROC General | 2026-03-24
ROC | March | VNRSKS, Kingsley M resetting OIT on site VNPSAP, Chris S is leaving site | All Water System ROC General | 2026-03-23
ROC | March | AURSBS - Ben H. called to inform that he is on site with Chris S. and Donald M. and will be working on the chlorine system. In this time, Ben will need AUVCBS in man/closed. Placed the valve man/closed | All Water System ROC General | 2026-03-23
ROC | March | STW2/3, placed wells back to auto | All Water System ROC General | 2026-03-17
ROC | March | Angelica Chepiga signing in,weather -11C | All Water System ROC General | 2026-03-18
ROC | March | NMTKKC- Chris S onsite for chemscan work. Notified Ben H. Requested to place NMW13 in manual, adjust duty stop from 75-85% activate duty and place chemical pumps man/off. Ammonia Pump 1 was already man/off in duty 3. | All Water System ROC General | 2026-03-19
ROC | March | GWTP - ZW1 membrane tank level hi alarm. Checked site, filter 1 is going through a cleaning process. Filter 1 level should return to normal range as the filter continues through the cleaning sequence. Will monitor. | All Water System ROC General | 2026-03-19
ROC | March | MKRSEM- Called Toronto (Puria) and requested pumps off. | All Water System ROC General | 2026-03-16
ROC | March | SHTP- UV Reactor 2 Critical Fault Alarm, Inlet Vlv 2 Fault Alarm, UV Reactor 2 Major Fault Alarm. UV is not running, UV 1 and 3 in service. Notified Tim H. He will take a look. | All Water System ROC General | 2026-03-16
ROC | March | QVW34, Ian W working on the OIT, disregard historian alarm GWTP, Parth P is finished on aite | All Water System ROC General | 2026-03-23
ROC | March | VNPS- Benson S requested PD7 and PD8 Pumps man/off to switch power back over to utility. | All Water System ROC General | 2026-03-17
ROC | March | MARS - North cell level low alarm. Activated RHRSTR duty 1 to push flow from BVPS. Swapped the supply pumps for VNRSKS from one VNPS and one MAPS pump to two VNPS pumps to allow MARS level to recover. Informed Jack P that BVPS will be starting. | All Water System ROC General | 2026-03-19
ROC | March | NMW15 - Alex B on site for ammonia and chlorine systems inspection, cleaning chlorine analyzers. | All Water System ROC General | 2026-03-26
ROC | March | GWTP - Gas chlorinator 5/6 Hi vacuum alarms. Plant is off (Memo). Jackie S and Joe M on site. | All Water System ROC General | 2026-03-16
ROC | March | ARPS- Peter from OCWA called. They are performing maintenance on HACH total, and free ammonia. Will not impact operations. Can disregard ammonia alarms that come in as these alarms are for the backup system. | All Water System ROC General | 2026-03-19
ROC | March | NMETHW - Deactivated Duty 1 @73% to offset NMETIB | All Water System ROC General | 2026-03-26
ROC | March | AUPSRR - Metro valve man/closed no flow indication from yesterday 12:45, notified Ben H. Donnald M on site working on it. | All Water System ROC General | 2026-03-17
ROC | March | KSTP- Eric S onsite working on low lift turbidimeter 09:47- Finished onsite. | All Water System ROC General | 2026-03-26
ROC | March | STETBR/STETTL- Yash S work completed. Requested to place all pumps back into auto. STETBR duty already active. Activated STETTL. STW12- Placed well 1 into manual STW3- Placed well 3 into manual STPSTL- Pump 1, 2 Low Flow. Both pumps failed. Reset alarms. Pump 2 started up in duty 1. | All Water System ROC General | 2026-03-19
ROC | March | Gluzen Ramos Ong signing out | All Water System ROC General | 2026-03-19
ROC | March | NMETIB - activated duty 1, offset NMETHW | All Water System ROC General | 2026-03-27
ROC | March | AUVCAD - Valve chamber flood alarm, notified Gary R, will attend site. | All Water System ROC General | 2026-03-16
ROC | March | QVW12 - William M returned well 1 pump back to auto, | All Water System ROC General | 2026-03-17
ROC | March | VNPS PD8- Benson S requested to start up 2 pumps for generator run. He will call back to place off when switching back to utility power. | All Water System ROC General | 2026-03-17
ROC | March | KSTP - Place highlifts back in auto GWTP - Rick L & Parth P finished at site | All Water System ROC General | 2026-03-20
ROC | March | VNPS PD7 - Man/started P2 for Benson S, generator running . | All Water System ROC General | 2026-03-17
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-21
ROC | March | SHTP - Well pump 2 uncommanded start alarm. Checked site, recently shut down. Able to reset alarm. GWTP - GAC 2 Level fault alarm and low/lolo alarms. Checked site, plant is not active. GAC 2 level reading is within normal range. Trending shows an abnormal dip of the GAC2 level reading which returned to normal range. Cleared alarms. | All Water System ROC General | 2026-03-22
ROC | March | Initiating Maple to Jefferson Feed changes. | All Water System ROC General | 2026-03-22
ROC | March | NMW12. - Influent free chlorine hihi alarm. Checked site, well recently activated. Trending shows a spike of the influent free chlorine reading which returned to normal range within two reading intervals. Reset alarms. | All Water System ROC General | 2026-03-27
ROC | March | GWTP - Rick L and Parth P on site for annual calibration, Joe M and Jackie S on site. | All Water System ROC General | 2026-03-26
ROC | March | MAPS- PD7 P2 Uncmd Stop, P2 Disch. Valve 1 Uncmd Close. Pump 1 took over in duty 1. Placed pump 2 in manual and cleared alarms. | All Water System ROC General | 2026-03-26
ROC | March | NMETIB- Activated duty. | All Water System ROC General | 2026-03-20
ROC | March | MTETNL - Travis W leaving site. | All Water System ROC General | 2026-03-19
ROC | March | BLW3 - Dan Z and Travis W on site. | All Water System ROC General | 2026-03-27
ROC | March | BVPS - Activated duty 1 | All Water System ROC General | 2026-03-22
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-22
ROC | March | SHTP - Deactivate highlifts to let res fill | All Water System ROC General | 2026-03-23
ROC | March | MKRSEM - Request TO (Zoran) to run 2 pumps | All Water System ROC General | 2026-03-23
ROC | March | YWS + NYWS normal | All Water System ROC General | 2026-03-23
ROC | March | RHPSPA - Surge Valve 1 and 2 Open, came in 3 times since 9:30. Coincides with MKVCMM Reverse flow HiHi. Inquired with Cristina S. of any work, she will follow up. | All Water System ROC General | 2026-03-19
ROC | March | NRETBR - Joe D testing Hi/Low ET level alarms. | All Water System ROC General | 2026-03-24
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-24
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-23
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-23
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-24
ROC | March | SHTP - Gas analyzer 3 methane fault alarm. Checked site, plant is active. Able to clear alarm. | All Water System ROC General | 2026-03-21
ROC | March | MKRSEM, Reservoir 1 Level lo alarm, notified Medhi from Toronto Water to start filling the res | All Water System ROC General | 2026-03-24
ROC | March | MAPS PD7, Placed pump 3 to auto VNPD PD7, Placed pump 2 man/off | All Water System ROC General | 2026-03-25
ROC | March | KCETDS - Yash S. is on site to replace a UPS Battery Replacement | All Water System ROC General | 2026-03-23
ROC | March | Ethan U signing in Weather 1. | All Water System ROC General | 2026-03-23
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-24
ROC | March | VNRSKS - Swapped supply pumps to one VNPS pump and one MAPS pump to equalize the demand on MARS and RHRSTR. | All Water System ROC General | 2026-03-25
ROC | March | SHTP, Deactivated D1 | All Water System ROC General | 2026-03-26
ROC | March | MKRSEM- Free Chlorine Residual Fault Alarm. This alarm was disregarded yesterday. Informed Patrick F that it has come back in. | All Water System ROC General | 2026-03-26
ROC | March | MTW12 - Well 1 silicate, hypo and well 1 and 2 pumps OOS alarms. Checked site, well pump 1 is running in local. These are consistent alarms that trigger on Wednesdays when operators sample. Well is run to waste during sampling with the chemical systems offline. | All Water System ROC General | 2026-03-25
ROC | March | YWS + NYWS Normal VNRSKS - Placed all pumps at MAPS PD7 man/off and placed all available pumps at VNPS PD7 into auto | All Water System ROC General | 2026-03-22
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-22
ROC | March | VNPS7 - Man/stop pump 1 man/off. MAP7 - Place pump 3 auto. | All Water System ROC General | 2026-03-22
ROC | March | SHTP- Reservoir 2 Level Lo Alarm. Deactivated high lift duty. | All Water System ROC General | 2026-03-25
ROC | March | AURSBS- Ammonia Pump 1,2 Failed to Start, Chlorine Pump 2 Uncomm Stop Alarm. Alarms cleared. Chlorine Pump 2 Uncomm Stop alarm came back in. Notified Donald M. He will take a look. W11760331 CMU5 | All Water System ROC General | 2026-03-25
ROC | March | HLW1 - Treated free cl hi, came in 09:00. Rotated ammonia pumps from P1 to P2 at 09:15. Noticed Treated Free HiHi alarm is disabled. Notified Jordan B., he is headed to site | All Water System ROC General | 2026-03-27
ROC | March | AURSBS - Donald M. and Tyler Z. working on chlorine booster pumps, chemical system. Placed AUVCBS man/closed. Donald M. will place in auto when work complete. AU central duty currently not active. | All Water System ROC General | 2026-03-27
ROC | March | NMW12, Influent Free Cl2 hihi, abnormal spike occurred. After 2 readings, residuals went back to normal | All Water System ROC General | 2026-03-25
ROC | March | STW12, Comm Loss alarms, notified Artour L as the issue continues to happen, he will look into it CMU5: W11760480 | All Water System ROC General | 2026-03-25
ROC | March | ARPS- Tegbeer from OCWA called and will switch from pump 6 to pump 5. | All Water System ROC General | 2026-03-26
ROC | March | STPSMR - Jack P performing w/o including - temp alarms test and chlorine analyzers maintenance. | All Water System ROC General | 2026-03-24
ROC | March | YWS + NYWS Normal Connor Smith signing out | All Water System ROC General | 2026-03-24
ROC | March | AURSBS - Chlorine pump 2 uncomm stop alarm. Donald M and Chris S working on chlorine pump 2, disregard alarms for the duration of the work. | All Water System ROC General | 2026-03-26
ROC | March | SHTP - Chlorine system alarms. OP on site for chlorine system maintenance. Disregard alarms for the duration of the work/ Interim memo. | All Water System ROC General | 2026-03-26
ROC | March | YWS + NYWS NORMAL | All Water System ROC General | 2026-03-20
ROC | March | GWTP - Parth P and Rick L on site for annual calibrations. | All Water System ROC General | 2026-03-25
ROC | March | Linear Water System - Received a call from York Region corporate contact center (Bonnie S) regarding a client call in for a meter/valve chamber cover that needs to be adjusted. Dispatched Dwayne L to site. Created CMU5#W11760219 #CMU5 | All Water System ROC General | 2026-03-25
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-17
ROC | March | NMW16 - Christian B. under direction of Ben H. addressed low temp alarm, reset for him as he doesn't have SCADA permissions. | All Water System ROC General | 2026-03-27
ROC | March | SHTP- Chlorine Room Gas Leak Alarm. Called Benson S. Operators are onsite for chlorine system maintenance. Can disregard. | All Water System ROC General | 2026-03-26
ROC | March | AUW57 - Ian W working on OIT, disregard Historian Heartbeat alarm. | All Water System ROC General | 2026-03-26
ROC | March | SHTP- Tim H called and requested to place well 2 back into auto. He is heading to site and will look into UV Minor Fault alarms. | All Water System ROC General | 2026-03-16
ROC | March | MAPS PD7, Placed pump 2 in man/off VNPS PD7, Placed pump 3 in auto | All Water System ROC General | 2026-03-26
ROC | March | NBW7- Jacob M onsite for Cl and Turbidity analyzer maintenance NBW5- Diesel Tank Sump Hi Level Switch. Notified Jacob M. He will look into it. | All Water System ROC General | 2026-03-17
ROC | March | KCETDS - Cole W. called to inform that he will start filling the tower but it will not be online as sampling still needs to be done | All Water System ROC General | 2026-03-23
ROC | March | AUPSRR- Donald M onsite for generator run, Cl analyzer maintenance and adjusting metro valve. | All Water System ROC General | 2026-03-17
ROC | March | STW12 - Jack P with instrumentation team on site replacing Hypo tanks. Wells 1/2 pumps man/off for the duration of the work. | All Water System ROC General | 2026-03-16
ROC | March | QVW12- Will M onsite for analyzer maintenance. Disregard alarms while onsite. | All Water System ROC General | 2026-03-17
ROC | March | RHRSTR - Deactivated Duty 1 to maintain MARS level. | All Water System ROC General | 2026-03-20
ROC | March | NMTKKC- Eric S finished onsite. Ammonia pump 1 back in auto | All Water System ROC General | 2026-03-24
ROC | March | Angelica Chepiga signing out | All Water System ROC General | 2026-03-18
ROC | March | MTETNL- Travis W onsite for work orders including Cl analyzer maintenance, health and safety and low temp. | All Water System ROC General | 2026-03-19
ROC | March | MKRSMR- Artour L onsite changing out UPS batteries. | All Water System ROC General | 2026-03-17
ROC | March | MAPS PD7 - PD7 pump 3 discharge valve uncommanded close alarm and uncommanded stop alarm. Checked site, pumps recently activated to fill system. Pump 3 is interlocked due to the alarms. Able to clear alarms. Duty 1 rotated to pump 1 when the alarm triggered. Placed pump 3 back in duty 1 and monitored start up. | All Water System ROC General | 2026-03-21
ROC | March | ARPS - Peel/OCWA (Peter) called to inform he is completing the daily pump rotation at ARPS. | All Water System ROC General | 2026-03-19
ROC | March | MKRSMR - Toronto Water (Peter) called to inform he would like to run each of the COTFA PD6 pumps for thirty minutes for maintenance. Placed the valves at MKRSMR in manual for receiving mode and informed operations of the pump exercising. No concerns from Patrick F. KSTP - CO2 Adjusted pH LoLo alarm. Checked site, low lift pumps have interlocked. The conduit level also triggered the lolo alarm. Called Jason G who directed to clear the CO2 adjusted pH lolo alarm and call if any other issues arise from the temporary reduction in flow. | All Water System ROC General | 2026-03-19
ROC | March | QVW12 - High Treated Free chlorine residual alarm. OP man/started well 1 pump. Alarm cleared in 5 minutes. | All Water System ROC General | 2026-03-18
ROC | March | SHTP- Raw Water Tank Level 1,2 HiHi Levels. Tim H onsite. He will look into it. | All Water System ROC General | 2026-03-16
ROC | March | GWTP- Ric L onsite for chlorinator rebuild. He will coordinate with operators onsite. | All Water System ROC General | 2026-03-16
ROC | March | MKETFA - Toronto Water (Peter) called to inform he would like to test the PRV for the Miliken system. Peter stated he would like to stop the active duty pump, test the PRV and then return the pump to active duty. Informed Peter he can completed the test as needed. | All Water System ROC General | 2026-03-19
ROC | March | NMW136 - Ian W working on OIT, disregard HRBT alarm | All Water System ROC General | 2026-03-20
ROC | March | Adeela Khan signing in. Weather: -2C and Cloudy | All Water System ROC General | 2026-03-18
ROC | March | STETBR - Deactivated duty 1 and placed STW1 and STW3 back to auto, in preparation for interim 22:46 - Activated duty 1 and placed STW1 and STW3 in man, in preparation for interim | All Water System ROC General | 2026-03-18
ROC | March | Gluzen Ramos Ong signing in JFPS - man/open VC_MV3 to test after valve failed to open during Maple to Jefferson Feed run attempt on March 8th. Confirmed valve opened to 100% and registered flow. Placed back in Auto. Will notify West Water and ROC. | All Water System ROC General | 2026-03-19
ROC | March | AUW57 - In fluent free chlorine hihi alarm. Checked site, well recently activated. Trending shows a spike of the influent free chlorine reading which dropped to normal range within two reading intervals. Reset alarm. SHTP - Well 2 pump uncommanded start alarm. Checked site, plant is currently off. Trending shows that well pump 2 recently shut down. Cleared alarm. | All Water System ROC General | 2026-03-21
ROC | March | BLW34- Ian W working on OIT. disregard heartbeat alarm. | All Water System ROC General | 2026-03-17
ROC | March | STRS48- Scrubber Running Status. Called Jack P. He was testing alarm. | All Water System ROC General | 2026-03-17
ROC | March | AURSBS - Chlorine pump 2 fail to start. Able to clear and get pump to start | All Water System ROC General | 2026-03-23
ROC | March | JFPS - Rotate pump 3 & 4 to duty 1. Pump 1 was previously duty 1, rotated out due to interim to run pump 1 in man/on for 1 hr daily. As they wanted to ease pump 1 into service to monitor. | All Water System ROC General | 2026-03-21
ROC | March | MAP7 - Place pump 3 man/off VNP7 - Place pump 3 auto GWTP - ZW7 35.5 kPa MIT-press decay test failed. Train 7 shutdown 8:00 - Informed Patrick F, will look into issue, disregard for now | All Water System ROC General | 2026-03-21
ROC | March | STW3 - Jack P on site to take the chlorination system out of service so that the instrumentation team can complete a replacement of chlorinator 2. Jack has directed that STW3 is to remain offline until the work is completed and he has primed the chlorine lines. QVW12 - Well pumps not available alarm. Checked site, treated chlorine analyzers showing in calibration mode. Will M logged into facility log book and his log entry for today includes analyzer maintenance. Will monitor site. | All Water System ROC General | 2026-03-18
ROC | March | MAPS - MAEP emergency eyewash activated alarm. Notified Benson S. | All Water System ROC General | 2026-03-18
ROC | March | SHETCS - Activate duty | All Water System ROC General | 2026-03-24
ROC | March | MKRSEM - Request TO to drop both pumps | All Water System ROC General | 2026-03-24
ROC | March | GWTP - Microfiltration room low temp alarm, notified Patrick F. He will check. | All Water System ROC General | 2026-03-24
ROC | March | HLW2- Combined Chlorine Hi Alarm. Notified Jordan B. He is onsite and will take a look. | All Water System ROC General | 2026-03-25
ROC | March | KCPSDS - Talha H. requested to reboot the OIT. Confirmed with Cole W. that this is okay as he is on site 12:25 - Talha H. is finished rebooting OIT | All Water System ROC General | 2026-03-23
ROC | March | KCPSDS - Place pumps 1 & 2 man/off as tower is to be drained today. Informed West Ops. Will call for pressure related alarms, disregard lo/lolo. David T will be on site later turning off analyzers. | All Water System ROC General | 2026-03-20
ROC | March | VNP7 - Place pump 2 & 3 man/off MAP7 - Place pump 1-3 back in auto | All Water System ROC General | 2026-03-23
ROC | March | ARPS - Peel (Jerry) infomred of daily pump switch over. Rotating pump 5 to pump 6 | All Water System ROC General | 2026-03-21
ROC | March | SHTP- Reservoir 1, 2 Level Lo Alarms. Notified Benson S. Requested to change duty setpoints to 15/45% and deactivated duty | All Water System ROC General | 2026-03-26
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-25
ROC | March | Aurora, Emergency Locate, Sent email out to Tom H (Locate on call) and gave a call but no response, left a voice message. Waited for roughly 10 minutes then called again, but still no response. If no response on the third call, will escalate 22:44, Notified Tom H of the emergency locate, he will look into it | All Water System ROC General | 2026-03-25
ROC | March | NMW15 - Treated Total chlorine Hi alarm. Adjusted chlorinator 1 dosing factor from 48 to 47%. | All Water System ROC General | 2026-03-26
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-21
ROC | March | STETBR - Tower Level Lo alarm came in. Placed STW1 and STW3 man/on as per interim | All Water System ROC General | 2026-03-22
ROC | March | KSTP- CO2 Adjusted pH LoLo. Interlocked Low Lift Pumps. Ben H directed to clear alarm. | All Water System ROC General | 2026-03-20
ROC | March | VNPS- Placed PD7 Pump 3 Man/off MAPS Placed PD7 Pump 3 in auto | All Water System ROC General | 2026-03-20
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-20
ROC | March | NMETHW - Deactivated duty 1 while NMETIB fills to maintain level offset between the two towers. | All Water System ROC General | 2026-03-20
ROC | March | MKRSEM - Low level alarm. Called Toronto Water (Zoran) and requested two pumps on to fill the reservoir. | All Water System ROC General | 2026-03-20
ROC | March | BLW34 - Influent free chlorine low and lolo alarms. Checked site, well was active when alarms triggered. Trending shows a steady decline of the influent free chlorine reading. Placed well manual/off for the night. | All Water System ROC General | 2026-03-21
ROC | March | MKRSEM, Notified Toronto operator Brent to stop filling the res | All Water System ROC General | 2026-03-26
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-26
ROC | March | MTW3 - Ernie H working on generator ventilation system. Disregard alarms for the duration of the work. | All Water System ROC General | 2026-03-24
ROC | March | COTFA- PD5 Discharge Pressure LoLo Alarm. Quick dip. Cleared alarm. | All Water System ROC General | 2026-03-25
ROC | March | STETBR - High level alarm. Placed STW12 and STW3 in auto mode. | All Water System ROC General | 2026-03-21
ROC | March | Ethan U signing in Weather 2c. | All Water System ROC General | 2026-03-21
ROC | March | VNRSKS - Placed all pumps at MAPS PD7 man/off and placed all available pumps at VNPS PD7 into auto | All Water System ROC General | 2026-03-23
ROC | March | STETBR - Tower Level Lo alarm came in. Placed STW1 and STW3 man/on as per interim | All Water System ROC General | 2026-03-23
ROC | March | NMTKKC - total chlorine lo, trends show no dip, able to clear right away as reading within range | All Water System ROC General | 2026-03-23
ROC | March | Christian Van Beek signing in. | All Water System ROC General | 2026-03-25
ROC | March | NMVCBA/NMVCIB - Reverted valve setpoint changes made earlier in the day by Ben H. | All Water System ROC General | 2026-03-25
ROC | March | Adeela Khan signing in | All Water System ROC General | 2026-03-23
ROC | March | Carter D Signing Out | All Water System ROC General | 2026-03-25
ROC | March | STPSMR, Free Cl2 Res lolo, Duty is active, tower is draining, trends show a staircase drop, contacted Patrick F, he is heading to site STETBR, Deactivated D1 CMU5: W11756650 | All Water System ROC General | 2026-03-24
ROC | March | SHTP - Deactivate highlifts for interim to assist in filling res | All Water System ROC General | 2026-03-24
ROC | March | KCETDS - Tim H finished on site. Tower is isolated, waiting for the sample results. KCETFS controlling tower. | All Water System ROC General | 2026-03-24
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-22
ROC | March | AUW57 - Historian Heartbeat alarm. Notified Ian W, he will check. | All Water System ROC General | 2026-03-16
ROC | March | BVPS - Lee F completed work on site. Placed P4man/off. Placed P3 back to auto. Pump 4 back to auto/ duty 2. | All Water System ROC General | 2026-03-16
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-17
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-17
ROC | March | NMVCBA - Placed valve man/open at 40 L/s 23:18 - Placed valve back to auto | All Water System ROC General | 2026-03-18
ROC | March | ARPS - Peel Ammonia Analyzer B Airport Rd Discharge B (AIT4B, AIT5B, AIT11B). Called OCWA (Binesh) who informed these alarms are from the backup system and can be disregarded. 02:18 - Peel Ammonia Analyzer A (AIT5A) Airport Rd Discharge alarm came in. As this is not part of the previous alarms that came in, called OCWA (Tegbeer) who informed there were no alarms on his end and made sure that the pump is working and the flow is okay. Tegbeer also informed that the ammonia system is running normally. Tegbeer also informed that he will give the ROC a call back in case any issue does arise | All Water System ROC General | 2026-03-18
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-19
ROC | March | JFPS - Deactivated pump 2. Placed pump 3 in auto mode. | All Water System ROC General | 2026-03-25
ROC | March | GWTP - Rick L working on zebra mussels chlorinator rebuild. Jackie S and Joe M on site to assist. | All Water System ROC General | 2026-03-17
ROC | March | KSTP - Raw water turbidity Fault alarm, disregard as per Shift report. | All Water System ROC General | 2026-03-18
ROC | March | STETTL - Activated duty in preparation for interim NMTKKC - Activated duty in preparation for interim YWS + NYWS Normal | All Water System ROC General | 2026-03-19
ROC | March | MARS - Hi level alarm came in. Activated duty 1 at VNRSKS | All Water System ROC General | 2026-03-19
ROC | March | RHRSTR - Deactivated duty 1 so the reservoir does not overfill during low morning demand. | All Water System ROC General | 2026-03-22
ROC | March | NBW3 - Influent Free Chlorine LoLo switch alarm came in. This occurred on well startup. After 2 mins, influent free levels came back to optimal range. Will wait 10 mins before resetting alarm 08:18 - Alarms have cleared and well is running | All Water System ROC General | 2026-03-22
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-22
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-17
ROC | March | VNPS- Placed PD7 Pump 3 man/off MAPS- Placed PD7 Pump 1 in auto | All Water System ROC General | 2026-03-26
ROC | March | KSTP - Raw water turbidity fault alarm. Disregard as per shift report. | All Water System ROC General | 2026-03-26
ROC | March | MARS - High Level alarm came in. Activated duty 1 at VNRSKS | All Water System ROC General | 2026-03-27
ROC | March | QVW12 - Chlorine leak detection alarm, and cl2 emergency valve closure fault alarms came in. Checked site, wells were not running when the alarm triggered. Trending shows a short spike of the chlorine gas detection reading which returned to normal range. Called Will M who will head to site to reset the valve interlock. | All Water System ROC General | 2026-03-27
ROC | March | EGMCDD - PAC Control Panel Power Failure alarm, checked Hydro one website, power outage in the area, ETR 19:45. | All Water System ROC General | 2026-03-16
ROC | March | MKRSEM, notified Toronto operator peter to start filling the res | All Water System ROC General | 2026-03-16
ROC | March | GWTP- UV Reactor 2 Dosage Hi Alarm. Notified Jackie S and Joe M, GWTP- Gas Chlorinator 5,6 Hi Vacuum. Jackie S informed instrumentation working on it. | All Water System ROC General | 2026-03-17
ROC | March | NBET27 - Outlet Total CL2 Hi alarm came in. Checked site. NBET is the controlling tower. Trends indicate the total chlorine level is trending upwards. NBET, NBW2, NBW3 and NBW5 chlorine analyzers are reading within normal range. Will continue to monitor 22:17 - Total chlorine levels are continuing to rise. Called Jordan B. who informed to refer to NBET for tower total chlorine readings. Jordan informed that once that tower stops filling, levels should come down. Jordan B. would like a call back if it reaches hihi levels #CONSULT | All Water System ROC General | 2026-03-17
ROC | March | GWTP - High Lift Tank 1 and 2 Level Lo alarms came in. Checked site. Hi lift is running. Called Patrick F. who will take a look on SCADA. 17:15 - Called Patrick F. for an update. Patrick informed that he placed GAC2 OOS so that it would not be called for. The other GAC's increased flows to compensate for the loss of GAC2. All Hi lift tank alarms have been cleared #CONSULT | All Water System ROC General | 2026-03-22
ROC | March | KLMCIA - Meter Chamber Flood and Security Intrusion alarms came in. Shift report indicates that site is OOS. Called Dwayne L. but no answer. 15:13 - Dwayne L. called back and informed that this can be disregarded until tomorrow | All Water System ROC General | 2026-03-22
ROC | March | MKVCSA - Building security Intrusion alarm. Notified Rob P. He will attend. # CMU5 W11743940 10:45 Rob P attended site, alarm cleared, leaving site. | All Water System ROC General | 2026-03-18
ROC | March | QVW34 - Will M on site to complete some well testing. Will has requested that alarms be disregarded from site. | All Water System ROC General | 2026-03-19
ROC | March | SHTP - Gas analyzer 3 methane fault alarm. Checked site, all methane alarms sensors reading normal. This alarm has triggered several times and has cleared each reset. No known impact to operations. Will leave alarm outstanding to be inspected by area operations on Monday. | All Water System ROC General | 2026-03-21
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-19
ROC | March | GWTP - Multiple communication alarms came in along with UV Reactor 1 and 2 Start/sequence fault alarms. Checked site. Duty recently activated. Called Patrick F. who will take a look on SCADA #CONSULT | All Water System ROC General | 2026-03-19
ROC | March | BLETNL- Travis W onsite for Cl analyzer maintenance, low temp and valve exercising. | All Water System ROC General | 2026-03-19
ROC | March | Angelica Chepiga signing out | All Water System ROC General | 2026-03-20
ROC | March | STW3 - Parth P and Rick L finished and leaving site. | All Water System ROC General | 2026-03-18
ROC | March | QVETQS- TIe Valve Failed to Open. Alarm cleared. QVW34- Will M placed wells man/off for injector work. Disregard low pressure alarms. | All Water System ROC General | 2026-03-26
ROC | March | HLPSYS - Dan B finished on site. | All Water System ROC General | 2026-03-17
ROC | March | VNPS- Placed PD7 duty 1 pumps in auto MAPS- Placed PD7 duty 1 pumps in manual | All Water System ROC General | 2026-03-26
ROC | March | NMW15- Alex B onsite for Cl system inspection. Will be backflushing. Disregard vacuum alarm if it comes in. 14:21- Eric S onsite troubleshooting Treated Total Cl analyzer | All Water System ROC General | 2026-03-26
ROC | March | GWTP - Jackie S and Joe M on site to complete maintenance of the outfall chlorine analyzer and the sedimentation tank chlorine analyzer. Jackie directed that associated alarms be disregarded. | All Water System ROC General | 2026-03-25
ROC | March | BVPS- Historian Heartbeat Alarm. Notified Chris S. He will look into it. | All Water System ROC General | 2026-03-19
ROC | March | GWTP - Rick L on site for annual calibrations. | All Water System ROC General | 2026-03-19
ROC | March | NMTKKC - Parth P finished and leaving site. Ammonia pump 1 will remain OOS. | All Water System ROC General | 2026-03-19
ROC | March | GWTP, Parth P on site doing annual calibrations | All Water System ROC General | 2026-03-23
ROC | March | MKRSEM - Free chlorine residual fault alarm. Patrick F called to inform he is on site completing sampling. AUW57 - Joe D called and requested that AUW57 be activated in manual mode for sampling. Made the necessary change. | All Water System ROC General | 2026-03-25
ROC | March | STW3 - Rick L called to inform he is on site to troubleshoot the chlorine leak detection system and replace chlorinator 2. | All Water System ROC General | 2026-03-18
ROC | March | ARPS - Peter from OCWA called, chemical system maintenance completed, back to normal. | All Water System ROC General | 2026-03-18
ROC | March | SHETCS - Hypo P1 uncomm start/ hypo pumps 1&2OOS alarms. Called Tim H, Jenn S will attend site. | All Water System ROC General | 2026-03-18
ROC | March | KLMCIA, KLPSWL - Aaron CM working on APN network configuration. 15:05 Aaron CM completed work. | All Water System ROC General | 2026-03-17
ROC | March | EGMCDD - Pressure low alarm, quick spike. Alarm cleared. | All Water System ROC General | 2026-03-18
ROC | March | GWTP - Derek from Aquazition is flushing in Keswick from 8:30 -1Pm. Emailed East OP team. | All Water System ROC General | 2026-03-17
ROC | March | GWTP, UV Reactor 2 Intensity lo (HMA). plant currently running, trends show a small gap with low intensity, notified Patrick F, directed to disregard as the intensity is back to normal consult | All Water System ROC General | 2026-03-23
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-23
ROC | March | NMW15 - Donnald M and Alex B , cleaning silicate tank. Disregard silicate tank level alarms for the duration of the work. | All Water System ROC General | 2026-03-24
ROC | March | NMPSKC - Jason G running generator. | All Water System ROC General | 2026-03-26
ROC | March | STETBR - Tower level Hi alarm. Placed STW3 pump back to auto. | All Water System ROC General | 2026-03-26
ROC | March | GWTP- Patrick F onsite working on MIT for Train 6. Disregard all train 6 alarms. | All Water System ROC General | 2026-03-24
ROC | March | MKRSEM - Reservoir Level Lo alarm came in. Called Toronto Water (Mehdi) and requested two pumps on 02:22 - Called Toronto Water (Paul) and requested to stop pumping to reservoir | All Water System ROC General | 2026-03-18
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-18
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-25
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-25
ROC | March | MTW12- Historian Heartbeat Alarm. Notified Artour L. He will look into it. 11:17- Artour L unable to reset remotely. He will attend site. | All Water System ROC General | 2026-03-26
ROC | March | MKRSEM - Called Toronto Water (Pooriyah) and requested to stop pumping to reservoir | All Water System ROC General | 2026-03-26
ROC | March | QVW34- Influent Free Chlorine HiHi. Quick spike, then recovered, cleared alarm. | All Water System ROC General | 2026-03-19
ROC | March | QVW34 - Well 3 pump running in manual/recently started. Influent chlorine residual LoLo alarm. Well 3 pump interlocked. Notified William M will attend site. | All Water System ROC General | 2026-03-18
ROC | March | YWS + NYWS Normal Adeela Khan signing out | All Water System ROC General | 2026-03-27
ROC | March | ARPS- OCWA called to inform they are switching pumps from pump 7 to pump 2 | All Water System ROC General | 2026-03-17
ROC | March | AUPSRR - Historian Heartbeat alarm, cleared when acknowledged. | All Water System ROC General | 2026-03-17
ROC | March | Carter Dunn Signing In, 0D/Clear | All Water System ROC General | 2026-03-23
ROC | March | RHRSTR, Deactivated D1 to have more water move from MARS to RHRSTR | All Water System ROC General | 2026-03-23
ROC | March | KCETFS, Isolation Valve Fault/Control Panel Power Fail, Tower @ 68%, Draining. KCETDS, Control Panel Power Fail, Tower currently isolated KCPSDS, PAC Control Panel Power Fail/Site Power Fail/Discharge FCV Fault. Pumps currently interlocked Notified Jen S, she is heading to site 01:26, Contacted Hydro 1 and spoke with Operator Abby, Informed her of the outages, Abby informed the ROC that this was a planned outage and work is currently being done to their system. Power outage should last from 1AM-4AM. Passed on this new information to Jen S 02:20, Notified Jen S that we have lost communication to the king city sites CMU5: W11756686 | All Water System ROC General | 2026-03-25
ROC | March | YWS + NYWS NORMAL | All Water System ROC General | 2026-03-20
ROC | March | KSETDP- Phil D onsite with PCS working on chlorine system. Disregard all related alarms. | All Water System ROC General | 2026-03-20
ROC | March | JFPS - Man/start P2 as per Interim Memo. 07:24 Man/stop P2, back to auto. As per Interim Memo. | All Water System ROC General | 2026-03-27
ROC | March | VNRSKS - Placed all pumps at VNPS PD7 man/off and placed all available pumps at MAPS PD7 into auto | All Water System ROC General | 2026-03-22
ROC | March | YWS + NYWS normal | All Water System ROC General | 2026-03-22
ROC | March | AURSBS - Activate duty 1 as MARS reaching high level | All Water System ROC General | 2026-03-23
ROC | March | Ethan Ullalkar signing out. | All Water System ROC General | 2026-03-23
ROC | March | AUPSRR - Ian W working on OIT, disregard historian heartbeat alarm. 15:27 Ian W completed work. | All Water System ROC General | 2026-03-24
ROC | March | NRETCR- Donald M onsite for work orders including chlorine analyzer maintenance, building low temp and valve exercising. | All Water System ROC General | 2026-03-19
ROC | March | SHTP, Adjusted Tower Duty 1 from 15/45% to 50/80% as per interim | All Water System ROC General | 2026-03-23
ROC | March | NMW15- Well 15 Emergency Stop Alarm. Lee F onsite. | All Water System ROC General | 2026-03-20
ROC | March | Christian Van Beek signing in. Weather: 3C and clear. | All Water System ROC General | 2026-03-21
ROC | March | HUB3SVR- Communication to H4AUSSP1 Server Alarm. Notified Artour L. He will take a look. 09:52- Artour L called back. There was an accidental restart. All old H4AUSSP1 Alarms came back in. | All Water System ROC General | 2026-03-26
ROC | March | RHRSTR- Activated duty as MARS approaching low level alarm setpoint | All Water System ROC General | 2026-03-26
ROC | March | STW2/3, Placed wells 2/3 in manual/on to help fill STETBR | All Water System ROC General | 2026-03-25
ROC | March | SHETCS, Activated D1 to top up the tower | All Water System ROC General | 2026-03-26
ROC | March | AUW2/3/5, Placed wells 2/3/5 man/off to take more water from AURSBS | All Water System ROC General | 2026-03-26
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-26
ROC | March | NMW15 - Eric S finished on site. Placed well 15 pump back to auto as per Joe D. | All Water System ROC General | 2026-03-26
ROC | March | AUVCBS - Artour L called with update. Communication restored, slow. Network team troubleshooting. VC opening slow. | All Water System ROC General | 2026-03-26
ROC | March | STETBR - Tower Level Lo alarm came in. Placed STW2 and STW3 man/on, as per interim | All Water System ROC General | 2026-03-26
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-21
ROC | March | MAPS PD7 - Pump 3 to auto. VNPS PD7 - Pump 1 man/off | All Water System ROC General | 2026-03-26
ROC | March | Christian Van Beek signing in. Weather: -6C and clear. | All Water System ROC General | 2026-03-27
ROC | March | Angelica Chepiga signing in | All Water System ROC General | 2026-03-16
ROC | March | KSTP - Fin water tot CL2 res fault, Fin flouide water res lolo. Disregard as per shift report | All Water System ROC General | 2026-03-22
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-23
ROC | March | MTETNL, Travis W on site, disregard intrusion alarm | All Water System ROC General | 2026-03-23
ROC | March | Connor Smith signing in 9C Cloudy | All Water System ROC General | 2026-03-16
ROC | March | EGMCDD, Motorized Valve 1/2 Fault, Power has come back to site, tried resetting fault but no success, notified Gary P, he is looking into the issue 19:57, Gary P directed to disregard for the night, if any low pressures come in, Gary would like a call consult | All Water System ROC General | 2026-03-16
ROC | March | VNPS PD8 - Benson S running generator, he placed pumps man/off to switch to gen. | All Water System ROC General | 2026-03-17
ROC | March | NMW15 - Treated total chlorine hi, able to clear but looking a little hi. Seeing influent higher than target range, dropped chlorinator 2 dosing from 52 to 50 | All Water System ROC General | 2026-03-22
ROC | March | MTW12 - Historian Heartbeat alarm cleared, Artour L leaving site. | All Water System ROC General | 2026-03-26
ROC | March | MKRSEM- Called Toronto (Zoran) and requested two pumps on | All Water System ROC General | 2026-03-26
ROC | March | KCETFS- Valve Room Eyewash Flow Alarm, Valve Room High/Low Temp Alarm. Called Jen S who is signed in onsite. No answer, will try again. 09:35- Called Jen S. She is onsite testing these alarms. | All Water System ROC General | 2026-03-17
ROC | March | VNPS PD8 - Placed pump 3(currently running ) man speed setpoint 30%. | All Water System ROC General | 2026-03-17
ROC | March | ARPS - Peter from OCWA called, completed P2 test, switching back to P7. | All Water System ROC General | 2026-03-17
ROC | March | AUPSRR- Donald M running generator and doing chlorine cylinder change. | All Water System ROC General | 2026-03-17
ROC | March | Ethan Ullalkar signing out. | All Water System ROC General | 2026-03-24
ROC | March | JFPS - Man/start Pump 1 as per Interim memo. 07:20 Man/stop Pump1, back to auto/duty 2 as per Interim memo. | All Water System ROC General | 2026-03-24
ROC | March | GWTP- Darek from Aquazition on his way to Keswick for flushing. Notified Patrick F, he will contact Darek. (Memo from Aaron W. to have system full for Linear/area/town work). | All Water System ROC General | 2026-03-16
ROC | March | QVW12 - Kyle R replacing lights/controls on well 2 pump. Placed Well 2 pump man/off for the duration of the work. HLPSYS - Dan B on site for generator maintenance. Disregard generator alarms. | All Water System ROC General | 2026-03-17
ROC | March | MTW3, NMMCWA- Aaron CM working on network. May briefly lose comms. No impact to operations. | All Water System ROC General | 2026-03-17
ROC | March | KSTP - Backwash pump 1 uncmd stop. Alarm cleared, filters backwashing | All Water System ROC General | 2026-03-20
ROC | March | MTETNL - Intrusion alarm. Travis W on site. | All Water System ROC General | 2026-03-18
ROC | March | STW3 - Ian W working on OIT. 14:00 Ian W completed work. | All Water System ROC General | 2026-03-17
ROC | March | NMVCIB - Adjusted flow from 80 to 40l/s to help with NMETHW level. NMVCBA - Adjusted flow from 40 to 80l/s | All Water System ROC General | 2026-03-17
ROC | March | NMTKKC - Eric S working on Ammonia pump 1. | All Water System ROC General | 2026-03-24
ROC | March | NRETCR - Lee F working on altitude valve. Requested altitude valve man/close. Deactivated Duty 1 and man/closed altitude valve and switched controlling tower to NRETBR | All Water System ROC General | 2026-03-27
ROC | March | MKRSEM - Called Toronto Water and requested they activate two pumps to push flow to MKRSEM | All Water System ROC General | 2026-03-19
ROC | March | AURSBS - Donnald M and Chris S finished on site. Chlorine pump 1 on duty 1 , chlorine pump 2 man/off. STW12 - Jack P finished on site. | All Water System ROC General | 2026-03-26
ROC | March | KSTP - Eric S. called to inform that he is on site to replace the flow sensor on the raw water turbidimeter 11:34 - Eric S. is finished on site and is now headed to GWTP | All Water System ROC General | 2026-03-23
ROC | March | Gluzen Ramos Ong signing in | All Water System ROC General | 2026-03-27
ROC | March | HLW1- Treated Free Chlorine Hi Alarm. Tim H requested to rotate Ammonia Pumps, and disable duty rotate. | All Water System ROC General | 2026-03-19
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-18
ROC | March | VNRSKS - Swapped supply pumps from two MAPS pumps to one VNPS and one MAPs pump. | All Water System ROC General | 2026-03-18
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-18
ROC | March | VNPS - Benson S on site for station checks. Benson directed to activate the duty for RHRSTR so that BVPS activates. Made necessary changes. | All Water System ROC General | 2026-03-18
ROC | March | 12:30 MKRSMR - Res low level alarm. Duty active, pump 10 is running, no flow. Notified Mehdi from Metro, he will investigate. 12:37 Confirmed flow , res filling. As per Mehdi Pump 10 is running for gen test. | All Water System ROC General | 2026-03-18
ROC | March | NBW2- Ric L finished onsite. Cole W still onsite. | All Water System ROC General | 2026-03-19
ROC | March | NBW3- Influent Free Chlorine LoLo Alarm. Interlocked well on schedule mode start up. Influent recovered. Cleared alarm and well started back up. | All Water System ROC General | 2026-03-26
ROC | March | KCETFS - Historian Heartbeat. Evgeny S. working on OIT | All Water System ROC General | 2026-03-27
ROC | March | STPSMR- Free Residual (sim) LoLo Alarm. Recovered next reading. Cleared alarm. | All Water System ROC General | 2026-03-16
ROC | March | NMW12 - Influent Free chlorine residual quick spike on duty start. Alarm cleared. | All Water System ROC General | 2026-03-24
ROC | March | EGMCDD - Artour L. on site testing valves 09:37 - work completed, confirmed all alarms cleared. Leaving site | All Water System ROC General | 2026-03-27
ROC | March | NMETIB- Deactivated duty NMVCBA- Adjusted from 80 back to 40L/s NMVCIB- Adjusted from 40 back to 80L/s | All Water System ROC General | 2026-03-17
ROC | March | VNPSAP - Dave T on site to complete work orders including flood alarm test, low temperature alarm test and chlorine analyzer maintenance. | All Water System ROC General | 2026-03-19
ROC | March | KSTP - Finished Water Fluoride Residual LoLo, Fin Water Fluoride and Total CL2 alarms came in. Disregarded as per shift report | All Water System ROC General | 2026-03-26
ROC | March | VNPS - Benson S on site for a station check and has requested that BVPS be activated. Activated duty 1 at RHRSTR to activate the BVPS pumps. | All Water System ROC General | 2026-03-27
ROC | March | NMETDD - Site hydro power failure, UPS supply power failure, PAC control panel power failure. No outage showing on Newmarket outage map. Informed Chris S to confirm we are now running on UPS for communication as although site is offline and empty we still monitor pressure which may be powered by UPS battery temporarily. CMU = 11749865 13:10 - Confirmed we are on UPS power. Called Donald M to update of situation, will head to site CMU = 11749873 | All Water System ROC General | 2026-03-21
ROC | March | MARS - Low level alarm came in. Deactivated VNRSKS | All Water System ROC General | 2026-03-22
ROC | March | RHPSPA - Parth P working on Pump 3 pressure switch replacement. Placed P3 man/off and assigned P1 to duty 1. | All Water System ROC General | 2026-03-24
ROC | March | KLET27 - Aaron CM from PCS will be switching the network cellular connection. The tower is almost full, deactivated the duty so that the pumps shut down and tower drains during this work. No impact to operations expected. | All Water System ROC General | 2026-03-18
ROC | March | BVPS- Jack P and Patrick F onsite for work orders. Testing sump floats, hihi alarm and running generator. | All Water System ROC General | 2026-03-19
ROC | March | STW3 - Influent chlorine residual low, man/started well 3 pump. Increased chlorinator 1 dosing factor from 250 to 253%. 12:42 Influent chlorine residual value recovered. Cleared alarm. | All Water System ROC General | 2026-03-20
ROC | March | MTW12- Gen tank 1 level Hi alarm, disregard as per Shift report. | All Water System ROC General | 2026-03-27
ROC | March | SHTP, Kathryn D from Public health called, notified ROC that she got a call from a Liam A (King Bylaw Officer) that the doors to the building are wide open. Notified YR security, they will send one of their guards over to lock the site up. Notified Jen S of this call as well. Kathryn Damas ? 2893382495 (Public Health Inspector) Liam Audette ? 9058334053 (Bylaw) | All Water System ROC General | 2026-03-25
ROC | March | KSTP - Raw water turbidity fault alarm. Checked site, plant is currently not active. Shift report states this alarm is a disregard. | All Water System ROC General | 2026-03-27
ROC | March | Connor Smith signing in -12C Windy | All Water System ROC General | 2026-03-17
ROC | March | QVW34 - PAC minor fault, monitor site as not active. Email on-call PCS Chris S | All Water System ROC General | 2026-03-24
ROC | March | KCETFS - Activate duty 1 for interim | All Water System ROC General | 2026-03-24
ROC | March | KSETDP - Phil D and Chris S working on chlorine system. | All Water System ROC General | 2026-03-24
ROC | March | VNPSAP- TIm H requested to place pumps in manual. Will be performing some valving as a test to float VNETAG tower today. | All Water System ROC General | 2026-03-25
ROC | March | MTETNL - Travis W on site for sampling. | All Water System ROC General | 2026-03-25
ROC | March | VNRSKS - Swapped supply pumps from two MAPS pumps to two VNPS pumps to reduce demand on MARS. | All Water System ROC General | 2026-03-25
ROC | March | Christian Van Beek signing in. Weather: 2C and clear. | All Water System ROC General | 2026-03-20
ROC | March | Angelica Chepiga signing in | All Water System ROC General | 2026-03-26
ROC | March | NMVCBA - Placed back to auto. | All Water System ROC General | 2026-03-20
ROC | March | YWS + NYWS Normal NMVCBA, Placed valve back to auto | All Water System ROC General | 2026-03-25
ROC | March | NMETIB - Activated Duty 1 to offset NMETHW. | All Water System ROC General | 2026-03-16
ROC | March | YWS + NYWS NORMAL | All Water System ROC General | 2026-03-27
ROC | March | QVW12 - Chlorine gas leak alarm. Eric S called to inform that there is a chlorine odour in the room which is causing the chlorine gas leak alarm. Eric contacted Joe D to return to site to investigate the chlorine leak source. Created CMU5#W11764741 for Joe D. #CMU5 | All Water System ROC General | 2026-03-27
ROC | March | VNPS- Benson S onsite for work orders. Requested to activate BVPS. | All Water System ROC General | 2026-03-16
ROC | March | VNPSCD - Chemscan OFFLINE status alarm, Benson S working on it. | All Water System ROC General | 2026-03-16
ROC | March | RHRSTR - Deactivated duty 1 to prevent overfilling in early morning low demand period. | All Water System ROC General | 2026-03-20
ROC | March | GWTP - Backpulse tank 2 level hi alarm. Checked site, backpulse tank 2 reading is high. Trending shows that the level has been slowly climbing but the fill valves are showing as closed and interlocked. If the HiHi alarm triggers will call OCO as the valves may be passing. | All Water System ROC General | 2026-03-21
ROC | March | STW12 - Jack P flushing silicate system. He placed Wells 1,2 pumps man/off. | All Water System ROC General | 2026-03-26
ROC | March | STRS48- Jack P onsite for Cl analyzer cleaning. | All Water System ROC General | 2026-03-17
ROC | March | HLW1 - Tim H on site, ammonia pump 1 was airlocked, back to auto. | All Water System ROC General | 2026-03-18
ROC | March | NBW3 - Influent free chlorine lolo on startup, analyzer came back within range and cleared alarm | All Water System ROC General | 2026-03-21
ROC | March | STETBR - Tower level lo STW12/STW3 - Place well 1 & 3 man/on for zone 1 tower NMETIB - Communication alarm, able to clear | All Water System ROC General | 2026-03-21
ROC | March | STW12- Placed well 2 man/on STW3- Placed well man/on for STETBR Fill Cycle | All Water System ROC General | 2026-03-17
ROC | March | JFPS - Placed pump 1 Man/on as per Cole W's interim procedure 07:42 - Placed pump 1 back to auto | All Water System ROC General | 2026-03-23
ROC | March | Carter Dunn Signing In, 2D/Clear | All Water System ROC General | 2026-03-24
ROC | March | MAPS PD7, Placed pump 3 in auto VNPS PD7, Placed pump 1 man/off 22:08, Reverted the changes so MAPS PD7 pump 3 is back to man/off and VNPS PD7 pump 1 back to auto | All Water System ROC General | 2026-03-24
ROC | March | STETTL- Wes from Town of Stouffville called to inform of flushing in Zone 2 for a couple of hours. | All Water System ROC General | 2026-03-16
ROC | March | GWTP - Parth P and Rick L finished on site. | All Water System ROC General | 2026-03-17
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-18
ROC | March | VNRSKS - Placed all pumps at VNPS PD7 man/off and placed all available pumps at MAPS PD7 into auto | All Water System ROC General | 2026-03-18
ROC | March | AUPSRR - Free chlorine hihi, trend show spike in reading but drops within range next reading. Able to clear alarm | All Water System ROC General | 2026-03-21
ROC | March | MKRSEM - Request TO (Zoran) for 2 pumps | All Water System ROC General | 2026-03-22
ROC | March | STW3, STETBR- Jack P onsite running generator. | All Water System ROC General | 2026-03-17
ROC | March | BLW12- Station Turbidity Hi Alarm. Rotated silicate pumps so silicate pump 2 in duty 1. Notified Joe M. He will take a look 17:51- Joe M placed well man/off and will attend site. W11740913 CMU5 | All Water System ROC General | 2026-03-17
ROC | March | Adeela Khan signing in. Weather: -7C and Cloudy MAP8 - PD8 P1 Pump 1 failed to stop alarm came in. Checked site and noticed that AURSBS recently deactivated. Ack/reset and alarm cleared. Will monitor | All Water System ROC General | 2026-03-17
ROC | March | MKRSEM - Reservoir Level Lo alarm came in. Called Toronto Water (Peter) and requested two pumps on | All Water System ROC General | 2026-03-17
ROC | March | ARPS- Peter from OCWA called to inform they are rotating from pump 6 to pump 7 | All Water System ROC General | 2026-03-16
ROC | March | MKRSEM- Peter from High Level finished running pumps. | All Water System ROC General | 2026-03-19
ROC | March | NMW15 - Alex B called requesting CMU for Eric S/ Treated Total chlorine analyzer motor issue. # CMU5 W11761894 | All Water System ROC General | 2026-03-26
ROC | March | STPSMR - Lee F finished on site. Assigned P1 to Duty 1, P2 to Duty 2. | All Water System ROC General | 2026-03-16
ROC | March | RHPSPA- Disch. Header Flow 1 LoLo. Duty just deactivated. Cleared alarm. | All Water System ROC General | 2026-03-17
ROC | March | MKETFA - Peter from Toronto Water caleld to inform that he would like to exercise a valve but would require the pump be turned off for 10 mins. Peter will call back once the valve exercise is complete 10:33 - Peter called to inform that he is finished exercising the valve and pump 3 is now running again | All Water System ROC General | 2026-03-23
ROC | March | NMTKKC - Donald M. called to inform that he is on site topping up the ammonia system | All Water System ROC General | 2026-03-23
ROC | March | ARPS - Martin (OCWA) informed switching from P5 to P6. | All Water System ROC General | 2026-03-27
ROC | March | MARS - Noticed Toronto Water Pushing higher than usual flow for 1 hour. Called Toronto Water (Pooriyah) who will place the flow back to optimal range YWS + NYWS | All Water System ROC General | 2026-03-27
ROC | March | GWTP- Ric L finished onsite. | All Water System ROC General | 2026-03-19
ROC | March | STPSMR- Jack P called. He will attend site and coordinate with Patrick F regarding high lifts interlocked | All Water System ROC General | 2026-03-20
ROC | March | VNRSKS - Swapped supply pumps to one VNPS pump and one MAPS pump. | All Water System ROC General | 2026-03-27
ROC | March | JFPS - Lee F finished on site. Pump 2 man/off, assigned P3 to duty 1. | All Water System ROC General | 2026-03-27
ROC | March | STW3- Ric L onsite to trouble shoot hypo tank LIT 10:02- Finished onsite. | All Water System ROC General | 2026-03-17
ROC | March | VNPS- Dave T onsite for work orders including chemscan maintenance, ammonia system maintenance, Cl leak detection test, and Cl analyzer maintenance. | All Water System ROC General | 2026-03-17
ROC | March | YWS + NYWS NORMAL Angelica Chepiga signing out | All Water System ROC General | 2026-03-17
ROC | March | AUPSRR - post injection free chlorine hi and hihi alarms. Checked site, trending shows an abnormal spike of the post injection free chlorine reading which returned to normal range within one reading interval. Reset alarms. | All Water System ROC General | 2026-03-21
ROC | March | QVW34 - Power failure alarms came in along with generator running status. Checked site. Likely a power blip and site is still running on hydro power. All alarms cleared | All Water System ROC General | 2026-03-22
ROC | March | SHTP - Res total chlorine lolo, trend shows reading have sudden drop within lolo range. Monitored for next reading, no sign of analyzer reading changing, possible fault. Informed Jen S, will head to site CMU = 11750153 | All Water System ROC General | 2026-03-23
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-24
ROC | March | BLW12 - Joe M. called back to inform that he is finished on site and the well 1 is running. Joe informed that if the hi turbidity levels come back in, the wells can be placed man/off | All Water System ROC General | 2026-03-17
ROC | March | VNPS PD8 - Pump 2 not ready alarm came in. Checked site. Pump was left man/off with same alarm earlier in the day. Pump 2 is a duty 3 pump. Placed pump back to auto and alarm cleared. Will continue to monitor 23:32 - Alarm came back in and stayed outstanding. Placed pump man/off and will send an email to the central/west team | All Water System ROC General | 2026-03-17
ROC | March | STW3 - Jack P on site and will be completing the chlorine leak detection alarm test. | All Water System ROC General | 2026-03-18
ROC | March | RHRSTR- Deactivated duty as MARS approaching high level. | All Water System ROC General | 2026-03-24
ROC | March | NMTKKC - Deactivated duty in preparation for interim procedure | All Water System ROC General | 2026-03-19
ROC | March | VNRSKS - Swapped supply pumps from two MAPS pumps to one VNPS and one MAPS pump. | All Water System ROC General | 2026-03-19
ROC | March | GWTP - Sutton header fluoride low alarm. Checked site, Sutton system duty is not active. Trending shows a slow dip of the fluoride reading for the Sutton header line. Will monitor this value when the Sutton header opens for duty 1. | All Water System ROC General | 2026-03-19
ROC | March | STW12/STW3/STRS48/STPSMR - placed all wells and pumps in manual/off for the duration of the PCS/Network scheduled upgrades. | All Water System ROC General | 2026-03-19
ROC | March | VNPSAP - Chris S. is on site and will be replacing the UPS | All Water System ROC General | 2026-03-23
ROC | March | Adeela Khan signing out | All Water System ROC General | 2026-03-23
ROC | March | Angelica Chepiga signing in, weather +4C | All Water System ROC General | 2026-03-19
ROC | March | STW3 - Influent chlorine residual low alarm. Duty just deactivated. Will monitor. | All Water System ROC General | 2026-03-20
ROC | March | MKRSEM - Pouria from Metro running generator, will run 2 pumps , one in a time, 30 minutes each. | All Water System ROC General | 2026-03-18
ROC | March | HLETPR- Tim H onsite running generator, chamber flood and low temp alarms. | All Water System ROC General | 2026-03-19
ROC | March | STPSTL- Yash S requested pumps man/off | All Water System ROC General | 2026-03-19
ROC | March | YWS + NYWS NORMAL | All Water System ROC General | 2026-03-19
ROC | March | NMETDD - Tyler Z will be attending site, & contacted Newmarket Hydro regarding hydro power failure. Donald M leaving site CMU = 11749890 | All Water System ROC General | 2026-03-21
ROC | March | NMETIB, Activated D1 | All Water System ROC General | 2026-03-25
ROC | March | GWTP- Jackie S performing backwash on GAC2. Disregard related alarms. | All Water System ROC General | 2026-03-19
ROC | March | STETTL- Yash S finished with work. Requested to clear all communication alarms. Will be performing work on STETBR in one hour. | All Water System ROC General | 2026-03-19
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-25
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-26
ROC | March | RHRSTR, Deactivated D1 so water is moved from MARS to RHRSTR | All Water System ROC General | 2026-03-26
ROC | March | Angelica Chepiga signing in,weather -7C | All Water System ROC General | 2026-03-24
ROC | March | SHTP - Jen S called, Jen S and Dan B on site, constructor working on UVs. Plant will be off for the day. Disregard alarms for the duration of the work. | All Water System ROC General | 2026-03-24
ROC | March | RHPSPA - Parth P finished on site. Placed Pump 3 back to auto. | All Water System ROC General | 2026-03-24
ROC | March | Newmarket Water System- Received a call and email from Traci from roads regarding a broken valve lid in the road at 16775 Leslie just North of Mulock. Appears to be York Region 750mm Water Main according to All Pipes. Notified Dwayne L. He will have someone replace it at some point today. | All Water System ROC General | 2026-03-20
ROC | March | MKRSEM - Low level alarm. Called Toronto Water (Zoran) and requested two pumps on to push flow to MKRSEM. | All Water System ROC General | 2026-03-21
ROC | March | GWTP - GAC 2 level fault, low and lowlow level alarms. Checked site, the GAC 2 level sensor has faulted and is reading an abnormal value resulting in the low and lowlow level alarms. The plant is currently off as the system is full. Will monitor these alarms and contact the OCO closer to duty start later in the morning. | All Water System ROC General | 2026-03-22
ROC | March | NMW136 - Alex B testing chlorine leak alarm and troubleshooting influent chlorine analyzer. | All Water System ROC General | 2026-03-18
ROC | March | Adeela Khan signing in. Weather: 8C and raining | All Water System ROC General | 2026-03-26
ROC | March | MTW12- Travis W onsite for turbidimeter maintenance. | All Water System ROC General | 2026-03-20
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-22
ROC | March | QVETQS - Site power failure and site heat trace fault alarms came in. Tower is draining. Likely apart of the power blip. All alarms have been cleared and site is operating normally | All Water System ROC General | 2026-03-22
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-20
ROC | March | NMETDD - Site back online, Tyler Z leaving site, informed Chris S of outstanding heartbeat alarm and UPS/battery with UPS offline. 16:40 site back in normal operation | All Water System ROC General | 2026-03-21
ROC | March | NMTKKC, Jason G on site, doing a hot water flush to the chemical systems, he is placing the analyzers in calibration mode and turning off the chemical system, directed to disregard at this time | All Water System ROC General | 2026-03-23
ROC | March | MTW3 - Travis W. is on site with Phil D. and will be completing a chlorine system inspection | All Water System ROC General | 2026-03-23
ROC | March | BVPS- Jack P requested to place pumps back into auto RHPSPA- Jack P heading to site to assist with surge valve work. | All Water System ROC General | 2026-03-19
ROC | March | QVW12- Will M onsite. Isolated station for injector work. Disregard low pressure alarms. | All Water System ROC General | 2026-03-26
ROC | March | MKMCAP - PRV chamber flood alarm. Gary P testing alarm. | All Water System ROC General | 2026-03-26
ROC | March | NMW15, Station Turbidity Hi alarm, Rotated Silicate pumps so pump 2 is in D1. Will continue to monitor the site | All Water System ROC General | 2026-03-24
ROC | March | VNETAG - Dave T on site to complete work orders including a generator test run, a flood alarm test and a low temperature alarm test. NBW2 - Rick L on site to complete work on a silicate LIT sensor and a chlorinator. Placed the well pump manual/off for Rick. | All Water System ROC General | 2026-03-19
ROC | March | SHTP - Filter 2 turbidity hi alarm. Checked site, filter 1 completed a backwash. Shift report states that post backwash NTU spikes can be disregarded if they reset. Able to reset alarm. | All Water System ROC General | 2026-03-19
ROC | March | MKRSMR - Toronto Water called to inform they have completed their pump testing for COTFA PD6 and the valves at MKRSMR can be returned to normal operations. Made the necessary changes. | All Water System ROC General | 2026-03-19
ROC | March | Angelica Chepiga signing out | All Water System ROC General | 2026-03-27
ROC | March | Ethan U signing in | All Water System ROC General | 2026-03-20
ROC | March | NMETHW, Activated D1 to have towers offset | All Water System ROC General | 2026-03-16
ROC | March | RHRSTR, Deactivated D1 | All Water System ROC General | 2026-03-16
ROC | March | STW2, STW3 - Placed man/start for STETBR fill cycle. | All Water System ROC General | 2026-03-16
ROC | March | NBW5 - Discharge Press LoLo alarm. Well 5 Local off. Cole W signed in station logbook. | All Water System ROC General | 2026-03-16
ROC | March | STW5- Received a call from YD Lab Tasmeem Karimgee (905-686-0041 ext. 4300) requesting a resample. Forwarded email to East Ops and informed Patrick F, acting team lead. Resample will be taken tomorrow. | All Water System ROC General | 2026-03-19
ROC | March | Connor Smith signing in 0C Snowy | All Water System ROC General | 2026-03-20
ROC | March | MTW3- Travis W onsite for turbidimeter maintenance | All Water System ROC General | 2026-03-20
ROC | March | MTW3, NMMCWA APN- Aaron CM Completed work. | All Water System ROC General | 2026-03-17
ROC | March | STETBR - Tower Level Hi alarm came in. Placed STW2 and STW3 back to auto, as per interim | All Water System ROC General | 2026-03-18
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-18
ROC | March | MKRSEM, Notified Toronto operator Medhi to stop filling the res | All Water System ROC General | 2026-03-25
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-16
ROC | March | ARPS - Peter (OCWA) confirmed ops finished work on HACH ammonia analyzers. No alarms, will check trending | All Water System ROC General | 2026-03-19
ROC | March | SHTP- KMNO pump 2 uncommanded stop alarm. Plant just deactivated. Alarm cleared. | All Water System ROC General | 2026-03-20
ROC | March | Angelica Chepiga signing out | All Water System ROC General | 2026-03-24
ROC | March | RHRSTR, Deactivated D1 to allow water to move from MARS to RHRSTR | All Water System ROC General | 2026-03-25
ROC | March | YWS + NYWS NORMAL | All Water System ROC General | 2026-03-24
ROC | March | KCETDS, Historian Heartbeat Alarm, power has been restored on site, notified Chris S, he will look into it. CMU5: W11756711 | All Water System ROC General | 2026-03-25
ROC | March | JFPS - Deactivated pump 1 and placed back into auto. | All Water System ROC General | 2026-03-25
ROC | March | STETBR - Tower high level alarm. Called Jack P to ensure he is completed sampling at STW12 and STW3 and that those well pumps can be placed into auto mode. Jack stated he is finished with the sampling at those wells and is currently at STETBR for sampling. Jack requested that the duty for STETBR be deactivated so the tower can drain for his sampling. Made the necessary changes. STRS48 - Jack P has requested that the high lift pump 2 be placed in auto mode. made the necessary change. | All Water System ROC General | 2026-03-25
ROC | March | VNPS- Benson S onsite for PMs including generator run, health and safety, air valve flush, and chemical system inspection. | All Water System ROC General | 2026-03-17
ROC | March | NMTKKC- Joe W onsite testing flood alarm. | All Water System ROC General | 2026-03-17
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-21
ROC | March | GWTP - GAC 4 flow control valve deviation, disregard as per shift report | All Water System ROC General | 2026-03-21
ROC | March | Ethan Ullalkar signing out. | All Water System ROC General | 2026-03-21
ROC | March | BLW34 - Placed well pump 3 in auto as directed by Patrick F. | All Water System ROC General | 2026-03-21
ROC | March | VNRSKS - Placed pump 1 at MAPS PD7 into man/off and placed pump 3 at VNPS PD7 into auto | All Water System ROC General | 2026-03-22
ROC | March | JFPS- Placed pump 2 in man/on for 1 hour 07:32- Placed pump 2 man/off Interim Procedure. | All Water System ROC General | 2026-03-26
ROC | March | VNRSKS - Swapped supply pumps from two MAPS pumps to one MAPS pump and one VNPS pump. | All Water System ROC General | 2026-03-27
ROC | March | KCETDS - Outlet pressure lolo, tower finished draining to 0% around 10am this morning as its now offline. Notified Jen S of pressure alarms, okay to disregard for weekend and okay with pressure dropping to 0 Consult | All Water System ROC General | 2026-03-21
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-21
ROC | March | YWS + NYWS Normal Adeela Khan signing out | All Water System ROC General | 2026-03-22
ROC | March | JFPS - Man/stop pump 1 and put pump 3 back in auto | All Water System ROC General | 2026-03-21
ROC | March | Connor Smith signing out | All Water System ROC General | 2026-03-19
ROC | March | STPSMR - Free chlorine res lolo, came in during startup. Infomred Patrick F, will head to site. STETBR - Deactivate duty 1 to assist with Tenth Line tower STW12/STW3 - place wells 1 & 3 back in auto | All Water System ROC General | 2026-03-20
ROC | March | NMW15 - Ben H onsite working on silicate, will run well later AUPSOH - Rick L finished at site | All Water System ROC General | 2026-03-20
ROC | March | Adeela Khan Signing Out | All Water System ROC General | 2026-03-18
ROC | March | ARPS - Peter from Peel/OCWA transmission control called to inform he is completing the daily pump rotation. | All Water System ROC General | 2026-03-18
ROC | March | AUPSRR - Donald M. turning chem system off for analyzer maintenance | All Water System ROC General | 2026-03-19
ROC | March | NMTKKC - Hypo tank 1 HiHi alarm. Jason G on site. | All Water System ROC General | 2026-03-24
ROC | March | NMETIB- Activated duty | All Water System ROC General | 2026-03-17
ROC | March | MKRSEM - Free chlorine residual fault alarm. Patrick F on site sampling and triggered this alarm. Cleared alarm. MTW12 - Hypo pump 1 and Silicate pump 1 failed to start alarms. Well pump 1 is running in local mode, operators likely on site for sampling. Well has interlocked due to hypo pump 2 and silicate pump 2 were placed in manual mode. Travis W is on site and well is being pumped to waste during sampling. No flow being directed to users. | All Water System ROC General | 2026-03-18
ROC | March | STW3 - Noticed that the well was turned off. Called Jack P. who informed he noticed high turbidity that did not trigger an alarm and shut the well off. Jack informed he will try to determine the cause of high turbidity | All Water System ROC General | 2026-03-23
ROC | March | QVW34 - William M on site performing chlorine analyzers and turbidity meter maintenance. | All Water System ROC General | 2026-03-18
ROC | March | QVW12- Kyle R finished onsite. Placed well back into auto. | All Water System ROC General | 2026-03-19
ROC | March | AUPSRR- Donald M onsite doing Cl analyzer maintenance. | All Water System ROC General | 2026-03-26
ROC | March | AUVCBS - Site back to normal. | All Water System ROC General | 2026-03-26
ROC | March | GWTP - Parth P. and Ric L. doing annual calibrations on membrane LIT and PITs. They will notify ops on site. | All Water System ROC General | 2026-03-27
ROC | March | YWS + NYWS Normal Christian Van Beek signing out. | All Water System ROC General | 2026-03-21
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-21
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-25
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-21
ROC | March | AUW14- Joe D and Donald M working on Ammonia System and placed wells man/off 14:59- Finished onsite. | All Water System ROC General | 2026-03-26
ROC | March | VNP7 - P1 and 3 man/stop MAP7 - P2 and 3 back in auto | All Water System ROC General | 2026-03-19
ROC | March | JFPS - Activated pump1 in manual mode for one hour as per the interim procedure | All Water System ROC General | 2026-03-25
ROC | March | JFPS - Placed pump 1 Man/on as per Cole W's interim procedure 10:20 - Placed valve back to auto | All Water System ROC General | 2026-03-22
ROC | March | NMVCBA - Placed valve man/open at 40 L/s | All Water System ROC General | 2026-03-22
ROC | March | HLW1 - Treated Free Chlorine Hi alarm came in. Checked site. Duty recently activated. Free chlorine value did not recover. Rotated ammonia pumps so that pump 2 is now running in duty 1. Will continue to monitor | All Water System ROC General | 2026-03-22
ROC | March | GWTP- Ric L finished onsite. | All Water System ROC General | 2026-03-26
ROC | March | QVW12, QVW34- Noticed that all wells were in manual/off. Nothing noted on SCADA Report or e logs. Placed all wells back into auto. | All Water System ROC General | 2026-03-25
ROC | March | Christian Van Beek signing out. | All Water System ROC General | 2026-03-25
ROC | March | GWTP - UV 1 and UV 2 comm alarms and UV 1 uncommanded stop alarms. Contacted Jackie S who directed to deactivate the duty so she can investigate. | All Water System ROC General | 2026-03-19
ROC | March | NMW15 - Silicate pump 1 working in good condition now dropping turbidity, rotates to silicate pump 2 as requested by Ben H to test silicate pump 2. | All Water System ROC General | 2026-03-20
ROC | March | Connor Smith signing out | All Water System ROC General | 2026-03-20
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-21
ROC | March | GWTP - Backpulse tank 2 level hihi alarm. Called Patrick F to inform. Patrick directed to initiate a backwash sequence for membrane tank 1 to drawdown the backpulse tank. #consult | All Water System ROC General | 2026-03-21
ROC | March | BLW3 - Influent free CL2 lolo, Patrick F attending site CMU = 11749880 | All Water System ROC General | 2026-03-21
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-22
ROC | March | NMETIB - Activated duty 1 to maintain level offset from NMETHW. | All Water System ROC General | 2026-03-18
ROC | March | JFPS - Benson S requested to run pump 1. Rotated pump 1 to duty 1. place pump 3 duty 5. Pump 1 & 4 active | All Water System ROC General | 2026-03-20
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-26
ROC | March | VNP7 - Place pump 1 & 2 auto. MAP7 - Place remaining pumps man/off | All Water System ROC General | 2026-03-23
ROC | March | YWS + NYWS NORMAL | All Water System ROC General | 2026-03-16
ROC | March | Carter Dunn Signing In, 3D/Clear | All Water System ROC General | 2026-03-16
ROC | March | NMETIB - Deactivate duty 1 to help offfset NMETHW | All Water System ROC General | 2026-03-21
ROC | March | YWS + NYWS normal | All Water System ROC General | 2026-03-26
ROC | March | KCETDS - Metering Chamber Flood Alarm came in. Shift report does not indicate to disregard alarm. Called Cole W. who directed to disregard alarm until tomorrow #CONSULT | All Water System ROC General | 2026-03-26
ROC | March | RHPSPA- PD6 Surge Valve 1,2 Open Alarms. Alarms cleared MKVCMM- Reverse Flow 2 HiHi Alarms. Alarms cleared | All Water System ROC General | 2026-03-19
ROC | March | AUPSWS - Kyle R /maintenance replacing floats. Testing flood alarm. | All Water System ROC General | 2026-03-16
ROC | March | HLW2 - Well 2 pump failed to stop alarm at duty stop. Alarm cleared in a few minutes. | All Water System ROC General | 2026-03-18
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-19
ROC | March | STW12 - Jack P and instrumentation team completed Hypo tanks replacement. Site back to normal. Jack P is running generator. | All Water System ROC General | 2026-03-16
ROC | March | STETBR - Level Hi alarm, placed STW12 pump 1 and STW3 pump back to auto. | All Water System ROC General | 2026-03-19
ROC | March | YWS + NYWS NORMAL | All Water System ROC General | 2026-03-19
ROC | March | MTW12 - Travis W performing PM's including: Turbidity meter, chlorine analyzers cleaning, chlorine and silicate systems maintenance, working on silicate pump 2, generator test, VLVs exercising, Hi/Low temp alarms testing. | All Water System ROC General | 2026-03-17
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-17
ROC | March | NMVCBA - Placed valve man/open at 40 L/s 00:09 - Placed valve back to auto | All Water System ROC General | 2026-03-17
ROC | March | MARS - Level Hi alarm came in. Activated AURSBS | All Water System ROC General | 2026-03-18
ROC | March | BLW34 - Dan Z called to inform that BLW34 will be offline for tonight. Dan Z and a contractor will be on site tomorrow to address a leak in the chlorine system. | All Water System ROC General | 2026-03-27
ROC | March | BLW3 - Travis W on site to complete turbidity analyzer maintenance. | All Water System ROC General | 2026-03-25
ROC | March | YWS + NYWS normal | All Water System ROC General | 2026-03-27
ROC | March | QVW34- Will M onsite working on chlorine analyzers and running generator. | All Water System ROC General | 2026-03-16
ROC | March | NMVCBA, Placed flow set point to 80L/sec from 40L/sec NMVCIB, Placed flow set point to 40L/sec from 80L/sec. Both NMETIB and NMETHW are active | All Water System ROC General | 2026-03-23
ROC | March | AURSBS, Activated D1 AUW2/3/5, Placed well 2/3/5 in man/on. 02:27, Placed wells 2/3/4 back to auto | All Water System ROC General | 2026-03-25
ROC | March | Newmarket, Leslie Street & Stellar Drive, Karen from Dispatch called, informed ROC of a main break, after checking all pipes, notified Karen to get in contact with the Town of Newmarket. Reviewed Newmarket trends, no abnormalities on YRs end | All Water System ROC General | 2026-03-25
ROC | March | ARPS- OCWA called (Peter) and informed will be shutting down pump 7 and starting pump 5 | All Water System ROC General | 2026-03-20
ROC | March | ARPS, Tegbeer from OCWA is rotating pump on site so pump 5 is man/off and pump 6 is in auto | All Water System ROC General | 2026-03-23
ROC | March | KCPSDS - Dan B. is on site for a work order for the hot water at the eyewash station. | All Water System ROC General | 2026-03-23
ROC | March | AUW14 - Joe D. is on site | All Water System ROC General | 2026-03-23
ROC | March | AUW2/3/5, Placed wells back to auto | All Water System ROC General | 2026-03-25
ROC | March | AUW14, Placed wells 2/3 back to auto | All Water System ROC General | 2026-03-16
ROC | March | YWS + NYWS Normal Ethan Ullalkar signing out. | All Water System ROC General | 2026-03-20
ROC | March | AUETFC - Joe D on site to complete work orders including deplox analyzer maintenance, temperature alarm tests and eyewash alarm test. | All Water System ROC General | 2026-03-19
ROC | March | GWTP- Ric L finished onsite. | All Water System ROC General | 2026-03-16
ROC | March | QVW34 - Ben H directed Man/start well 3 pump. | All Water System ROC General | 2026-03-17
ROC | March | MAPS- Placed PD7 Pump 2 in manual VNPS- Placed PD7 Pump 2 in auto | All Water System ROC General | 2026-03-16
ROC | March | MARS - Jerry from OCWA called to inform that he will be completing the daily pump transfer. Will be switching from pump 6 to pump 5 | All Water System ROC General | 2026-03-22
ROC | March | YWS + NYWS NORMAL | All Water System ROC General | 2026-03-19
ROC | March | MKVCAP. Rob P on site, working on the valve chamber disregard alarms from site | All Water System ROC General | 2026-03-23
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-20
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-21
ROC | March | JFRS - Man/stop pump 3, place pump 1 man/on for interim | All Water System ROC General | 2026-03-21
ROC | March | AURSBS - Chlorine pump 2 fail to start alarm. Checked site, Aurora central system duty recently activated which opened AUVCBS and triggered the chemical system at AURSBS. Chlorine pump 2 failed on start, cleared alarm twice. Chlorine pump 1 and chlorinator 1 are currently Manual/off and able to run in an emergency. Called Donald M who will check SCADA. 22:02 - AURSBS - Chlorine pump 2 fail to start. Donald M called back to inform he was able to get chlorine pump 2 running. If the chlorine pump fails on later fill cycles Donald directed to use chlorinator 1 and reduce the flow setpoint of AUVCBS to 400L/s. If chlorinator 1 is maxed out at this flow setpoint Donald directed to reduce the combined chlorine target setpoint. # consult | All Water System ROC General | 2026-03-21
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-24
ROC | March | GWTP - GAC 4 Flow control valve deviation alarm, disregard as per shift report. Cleared alarm. | All Water System ROC General | 2026-03-19
ROC | March | NRETBR - Christian B and Joe D on site performing PMs including Temp alarms test and chlorine analyzers maintenance. | All Water System ROC General | 2026-03-24
ROC | March | JFPS - Lee F performing vibration pump testing, switched P1 to Duty 1 and P4 to duty 5. Man/stopped P3 and Man/started Pump 2 . Lee F confirmed with Cole W , ok to run P2. | All Water System ROC General | 2026-03-17
ROC | March | NMTKKC - Parth P on site to verify the analyzers following the scheduled chemical analyzer work. | All Water System ROC General | 2026-03-19
ROC | March | NMTKKC - Joe W working on site, placing all chemical pumps man/off for 30 minutes. | All Water System ROC General | 2026-03-16
ROC | March | BVPS- Lee F onsite. Requested Pump 3 off and Pump 2 on. Pump 1 already running in duty. Confirmed okay with Benson S. | All Water System ROC General | 2026-03-16
ROC | March | MKRSEM - Called Toronto Water (Brett) and requested they deactivate the pumps pushing flow to MKRSEM. | All Water System ROC General | 2026-03-22
ROC | March | MARS - Hi level alarm came in. Short cycled VNRSKS to help lower levels at MARS | All Water System ROC General | 2026-03-22
ROC | March | GWTP - Called Patrick F. to address the outstanding GAC 2 Level LoLo and fault alarms. Patrick informed he will take a look #CONSULT | All Water System ROC General | 2026-03-22
ROC | March | KSTP- Raw Water Turbidity Fault Alarm. Disregard as per SCADA report | All Water System ROC General | 2026-03-19
ROC | March | RHPSPA- Patrick F onsite for work orders including generator run, flood alarm and surge valve. | All Water System ROC General | 2026-03-17
ROC | March | KSTP - Place highlifts in manual. with highlift pump 3 man/on GWTP - Deactivate duty 1 as per Aaron W for instrumentation | All Water System ROC General | 2026-03-20
ROC | March | QVW12 - Kyle R finished on site, Placed Well 2 pump to auto. | All Water System ROC General | 2026-03-17
ROC | March | VNPS7 - Place pumps 1 & 3 auto MAP7 - Place pump 1, 2 & 3 man/off, done to conserve MARS water and drawdown from Teston | All Water System ROC General | 2026-03-20
ROC | March | GWTP - Rick L onsite for annual calibrations | All Water System ROC General | 2026-03-20
ROC | March | NMW15- Alex B onsite working on turbidimeter. NMW13- Placed well back into auto for completion of NMTKKC work. Confirmed ok with Alex B. | All Water System ROC General | 2026-03-19
ROC | March | AUPSOR - Joe D onsite, requesting CMU for Parth P who is attending site for crack in probe for deplox. CMU5 = 11749594 | All Water System ROC General | 2026-03-20
ROC | March | NMETIB- Activated duty to keep offset with NMETHW | All Water System ROC General | 2026-03-24
ROC | March | VNETFD- Dave T onsite for work orders including flood alarm, low temp, hi/low level and eyewash. | All Water System ROC General | 2026-03-24
ROC | March | NMW136 - Alex B finished on site. NMW15 - Alex B heading to site, will test chlorine leak alarm. | All Water System ROC General | 2026-03-18
ROC | March | NMW136- Alex B working on silicate system | All Water System ROC General | 2026-03-19
ROC | March | NMW15 - Ben H finished at site | All Water System ROC General | 2026-03-20
ROC | March | QVW34 - Eric S finished on site. | All Water System ROC General | 2026-03-24
ROC | March | NMW15- Alex B onsite working on silicate system | All Water System ROC General | 2026-03-25
ROC | March | Adeela Khan signing out | All Water System ROC General | 2026-03-19
ROC | March | RHPSPA- PD6 Surge Valve 1,2 Open Alarms. Alarms cleared MKVCMM- Reverse flow hihi alarm. Alarm cleared 09:42- PD6 Surge Valve 1,2 Open Alarms came in again and cleared | All Water System ROC General | 2026-03-19
ROC | March | NMTKKC - Chris S finished and off site. | All Water System ROC General | 2026-03-19
ROC | March | Christian Van Beek signing in. Weather: -2C and clear. | All Water System ROC General | 2026-03-19
ROC | March | NMETIB - Activated duty 1 to maintain level offset from NMETHW. | All Water System ROC General | 2026-03-19
ROC | March | RHRSTR- Activated duty as MARS approaching low level alarm. | All Water System ROC General | 2026-03-25
ROC | March | YWS + NYWS NORMAL | All Water System ROC General | 2026-03-20
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-21
ROC | March | RHRSTR - Adjusted D1 start from 70 to 65% | All Water System ROC General | 2026-03-19
ROC | March | BLW12- Dan B called. He is onsite assisting with construction project. Power will be shut off onsite. Placed wells man/off 13:06- Dan B finished with work. He will coordinate with Patrick F about running a Well. | All Water System ROC General | 2026-03-20
ROC | March | HLW1 - Treated free chlorine residual HiHi, rotated ammonia pumps, placed P1 man/off, P2 is running on duty 1. | All Water System ROC General | 2026-03-18
ROC | March | NMETHW - Deactivated duty 1 while NMETIB fills. | All Water System ROC General | 2026-03-21
ROC | March | STPSMR- Patrick F requested a CMU5 for Jack P and himself for Free Chlorine Res LoLo W11749627 CMU5 | All Water System ROC General | 2026-03-20
ROC | March | GWTP- Jackie S finished with Outfall and Sedimentation Tank Chlorine analyzer maintenance. | All Water System ROC General | 2026-03-25
ROC | March | GWTP - Comm alarm and UV reactor 1 fault alarms. Called Jackie S who stated the communication alarm interrupted the normal operation of the UV reactor at GWTP. Jackie deactivated system duty and will let the plant shut down. When the system drains the plant will start again. | All Water System ROC General | 2026-03-18
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-18
ROC | March | BLW12 - Silicate Pump 1 Failed to start alarm came in. Checked site and found that silicate pump 2 has rotated to duty 1. Reset alarm. Will monitor | All Water System ROC General | 2026-03-19
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-25
ROC | March | MKVCMM- Reverse Flow 2 HiHi Alarm. Alarm cleared after a few minutes MKVCEM- Forward Flow HIHI Alarm. Alarm cleared after a few minutes | All Water System ROC General | 2026-03-25
ROC | March | KSETDP- Post injection Total Chlorine HiHi Alarm. Tower is filling, value recovered. Cleared alarm | All Water System ROC General | 2026-03-25
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-29
ROC | March | RHAMF1 - Unit 1 recirculation pump 1 and pump 2 overload alarms. Checked system, Unit 2 recirculation pumps still active and both AMF fans active. Shift report states that all alarms can be disregarded as long as atleast one fan is running and there is no power outage. Disregard alarms. | All Wastewater System ROC General | 2026-03-29
ROC | March | SUSP - UV Ch .1 common critical, high level, system critical failure. Status went to normal, known issue upon startup | All Wastewater System ROC General | 2026-03-29
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-29
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-29
ROC | March | SUSP - UV channel 1 and 2 high level alarm, UV channel 1 and 2 common critical alarm and UV system critical alarm. Checked site, trending shows flow to the UV system recently started. All alarms changed to normal status immediately after triggering. Shift report states that these alarms are disregard if flow to the UV system recently started, such as in this instance. Cleared alarms. | All Wastewater System ROC General | 2026-03-29
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-30
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-30
ROC | March | Connor Smith signing out | All Wastewater System ROC General | 2026-03-29
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-29
ROC | March | KBSP - Aeration basin 2 suspended solids fault alarm. Checked site, trending shows an abnormal spike of the suspended solids reading which returned to normal range quickly. Able to clear the alarm. | All Wastewater System ROC General | 2026-03-29
ROC | March | NBSP - Vortex 2 air scour uncommanded close alarm. Shift report states this alarm is a disregard if it can be cleared. Able to clear alarm. | All Wastewater System ROC General | 2026-03-30
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-29
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-29
ROC | March | NBSP - Mechanical barscreen OOS and general alarm. Lauren S called back and will attend site. Created CMU5#W11765387. #CMU5 | All Wastewater System ROC General | 2026-03-30
ROC | March | MTSP - Clarifier 1 no RAS pump running. Clarifier 1 OOS noted on shift report. | All Wastewater System ROC General | 2026-03-29
ROC | March | SUSSWB- Ventilation H2S OOR Alarm. Disregard as per SCADA Report. | All Wastewater System ROC General | 2026-03-29
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-29
ROC | March | Christian Van Beek signing in. Weather 10C and clear. | All Wastewater System ROC General | 2026-03-29
ROC | March | NBSP - Secondary system general alarm on autodialer. No issues on SCADA site, Will monitor | All Wastewater System ROC General | 2026-03-29
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-29
ROC | March | KBSP - Thick'd sldg pmp 2 pres switch hi, called to inform Lauren S, will take a look on SCADA Consult | All Wastewater System ROC General | 2026-03-29
ROC | March | NMSSHS - PAC communication failure, status went to normal, no issue w trends or site. CLeared alarm | All Wastewater System ROC General | 2026-03-29
ROC | March | Ethan U signing in Weather 0. | All Wastewater System ROC General | 2026-03-29
ROC | March | KSSSQW - Pump 2 uncommanded stop alarm. Checked site, pump 3 is currently duty 1 and running. Trending shows that pump 2 was running and recently shut down. Able to clear alarm. | All Wastewater System ROC General | 2026-03-30
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-28
ROC | March | Ethan Ullalkar signing out. | All Wastewater System ROC General | 2026-03-29
ROC | March | Connor Smith signing in 1C Clear | All Wastewater System ROC General | 2026-03-28
ROC | March | Maximo and EzMaxMobile Update completed. Returning to elog book. Christian Van Beek signing in, Weather: -1C and sun. Please see attached photos of the paper logbooks. | All Wastewater System ROC General | 2026-03-28
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-29
ROC | March | NBSP - Mechanical barscreen general and out of service alarms. Checked site, barscreen showing local/off. Unable to clear alarm. Will monitor the screen differential level, and call out if it climbs. 01:46 - NBSP - Mechanical barscreen OOS and general alarms. Channel inlet level and barscreen differential continued to climb. Called Lauren S who directed to place the barscreen in the continuous override mode. Made the change, barscreen still in local and unable to clear alarms. Lauren will check SCADA and call back if she goes to site. #consult | All Wastewater System ROC General | 2026-03-30
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-29
ROC | March | Christian Van Beek signing out. | All Wastewater System ROC General | 2026-03-28
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-29
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-28
ROC | March | Christian Van Beek creating a test log entry at the request of Jennifer Chung. | All Wastewater System ROC General | 2026-03-28
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-29
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-30
ROC | March | Ethan U signing in Weather 4. | All Wastewater System ROC General | 2026-03-30
ROC | March | YDSS + YNSS Normal KSSP - ZW1 TMP high alarm. Alarm status changed to normal immediately after alarm triggered. Alarm reset on acknowledgement. | All Wastewater System ROC General | 2026-03-30
ROC | March | NBSP - Mechanical Bar Screen General and OOS alarm came in. Checked site. Mech screen is showing local. Called Lauren S. who will reset alarm on site | All Wastewater System ROC General | 2026-03-30
ROC | March | Adeela Khan signing in | All Wastewater System ROC General | 2026-03-30
ROC | March | Maximo down between 10:00 and 16:00. Attached is pictured of logbook entries | All Wastewater System ROC General | 2026-03-30
ROC | March | Christian Van Beek signing in. Weather: 18C and clear. | All Wastewater System ROC General | 2026-03-30
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-30
ROC | March | RHAMF - Eric from NAC onsite to reset pump 1 & 2 | All Wastewater System ROC General | 2026-03-30
ROC | March | QVSSSC - Channel Grinder Emergency Stop Alarm came in. Checked site. Channel Grinder was showing in Local/off. Called Chris C. who informed that the maintenance team will need to attend site. Chris informed that all channel grinder and hi/hihi inlet and level alarms can be disregarded for the time being until Maintenance can attend site. | All Wastewater System ROC General | 2026-03-31
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-30
ROC | March | QVSSSC - Chris C. called back to inform that he is finished on site. Chris informed that if any channel grinder related alarms come in, they can be disregarded. Chris would like a call back if there are any issues with the pumps. | All Wastewater System ROC General | 2026-03-30
ROC | March | YDOC - Terry C. generator maintenance KBSP - Lauren S. testing plant 2 influent chamber flood alarm | All Wastewater System ROC General | 2026-03-30
ROC | March | Gluzen Ramos Ong signing out | All Wastewater System ROC General | 2026-03-30
ROC | March | HLSSBR - Sewage pump 2 E-stop & speed OOR alarm. Followed up with Darren B, expected maintenance to be there. | All Wastewater System ROC General | 2026-03-30
ROC | March | NMSSHS - Intermittent PAC communication fails come in. Called Artour L. who will take a look 11:42 - Artour L. called back to inform that he has spoken to the network team who has restarted the cell modem. A ticket is open with Bell due to ongoing issues | All Wastewater System ROC General | 2026-03-30
ROC | March | Gluzen Ramos Ong signing in | All Wastewater System ROC General | 2026-03-30
ROC | March | Ethan Ullalkar signing out. | All Wastewater System ROC General | 2026-03-30
ROC | March | QVSSSC - Chris C called to inform that any alarms related to the inlet channel grinder and inlet channel level hi/hihi are a disregard for the nigh.t Chris also stated that sewage pump 2 has bene having issues and he would like to be contacted if this pump faults and cannot be returned to service. | All Wastewater System ROC General | 2026-03-30
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-31
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-30
ROC | March | SUSP - UV channel 1 high level, common critical and UV system critical failure alarms. Trending shows that flow to the UV system recently started. Shift report states these alarms are a disregard in this scenario. Alarms cleared on acknowledgement. | All Wastewater System ROC General | 2026-03-30
ROC | March | SUSP - SBR storm alarm. Checked site, SBR cycle operation mode showing as storm. EQ tank level is normal but filter feed pump speed and filter has increased. Will monitor. While watching site the SBR cycle operation mode returned to normal status. | All Wastewater System ROC General | 2026-03-31
ROC | March | Christian Van Beek signing out. | All Wastewater System ROC General | 2026-03-30
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-30
ROC | March | SEBR - S2 humid chamber lolo level switch alarm. Disregard as per the shift report. | All Wastewater System ROC General | 2026-03-30
ROC | March | MTSS - communications loss to MTSS. Heavy thunderstorm impacting operations across the Region. No visual of site on SCADA. Checked the influent flow meter at the MTSP, trending shows no flow from the MTSS pumping station since communications lost. Contacted Arthur L to determine if communications can be revived and contacted Phil R to head to site to determine if operations have been impacted. Created CMU5#W11768975 for Arthur and CMU5#W11768982 for Phil R. MTSP - Grit system 1 and 2 uncommanded stop alarm, barscreen uncommanded stop alarm and dewatering press uncommanded stop alarm. Able to reset all alarms. #consult #CMU5 | All Wastewater System ROC General | 2026-03-31
ROC | March | AUSS - Wet well hi level alarms. Placed Pump 5 with a manual setpoint of 60% | All Wastewater System ROC General | 2026-03-31
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-31
ROC | March | Adeela Khan signing out | All Wastewater System ROC General | 2026-03-31
ROC | March | KBSP - Christian from Ferguson Electric is finished on site. Christian informed that "Stella" generator failed and remained local/off. Both generators power different parts of the plant. Called Lauren S. to get more information as this is not noted in the shift report. Lauren will look into this. 16:57 - Drew from Ferguson Electric called back and requested to know if the generators were in auto as Dan H. contacted him. Informed that the "Stella" is Local/off and "Bertha" has a Remote-control status. Drew from Ferguson informed that Christian will head back to site 17:24 - After checking site, noticed that the "Stella" generator is now in auto. Lauren S. called back and informed that Christian from Ferguson is finished on site. Lauren also informed that one generator can power the whole plant but it is best to have both available. #CONSULT | All Wastewater System ROC General | 2026-03-31
ROC | March | HLSSBS - Gen still running, outage map has team responding to site. Informed Chris C of situation that gen may be running prolong for the night. Consult SUSP - UV critical, high level, alarm on startup, cleared right after NMSSBP - Wet well 1 & 2 hihi switch/level/overflow. See pump 2 & 4 man/off, Phil R on SCADA looking at site | All Wastewater System ROC General | 2026-03-31
ROC | March | AUSS/NMSSBP - Terry R. called back to inform that the pumps are back to normal operations as the high flows have subsided for the time being. Terry also informed that NMVCBP will be off for the night | All Wastewater System ROC General | 2026-03-31
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-31
ROC | March | Contingency Log, March 31, 0400 to 0645, eLogs were down. Attached are the paper logs for that time stamp | All Wastewater System ROC General | 2026-03-31
ROC | March | Adeela Khan Signing out | All Wastewater System ROC General | 2026-03-30
ROC | March | KSSP - ZW2 Permeate Pump Speed Signal Error Alarm came in. Neil O. informed that Satnam M. is on site working on train 2 and all train 2 related alarms can be disregarded for the next 2 hours | All Wastewater System ROC General | 2026-03-31
ROC | March | SHSP - Site hydro failure alarm. Checked site, generator is not running and ATS is pointing to utility hydro indicating a short power failure. Able to reset all alarms. Trending shows that the UV system did not deactivate or lose power. All duties appear normal on site. SHSSDK - Control panel power failure. Checked site, operations appear normal. No fault on pumps. Cleared alarms. | All Wastewater System ROC General | 2026-03-31
ROC | March | SECC - Chris R. called to inform he is on site and will be running sump pumps. Directed to disregard all hi/lo level alarms until work is complete | All Wastewater System ROC General | 2026-03-31
ROC | March | MTSS - Communications loss alarm. Arthur L called to inform that he and the Network on call operator are unable to connect to the station. Arthur will attend site. KSSSQW - Wet well 1 hydrostatic level hihi alarm. Checked site, duty 1 and 2 active. Duty 3 not yet active. Heavy rainfall causing increased levels of flow. Will monitor site. | All Wastewater System ROC General | 2026-03-31
ROC | March | AUSSSR - Noticed Line 3 Overtorque Alarm is outstanding. Only 1 line is available. Called Phil R. who directed to disregard alarm and he will attend site in the morning. Phil requested a call if line 3 goes down. MTSS - Phil R. informed that site is back to normal operations and all operators have left site. Phil would like a call back if any issues arise #CONSULT | All Wastewater System ROC General | 2026-03-31
ROC | March | NMSSHS - Pump 1 VFD fault from this morning outstanding, placed pump 1 man/off. Pump 3 shows interlock and running in ultrasonic mode, appears partially on at 0% speed. Informed Phil R of site alarm NMMC - Manhole 2 level hihi, informed Phil R AUSS - Reached hihi level, informed Phil R as well Consult | All Wastewater System ROC General | 2026-03-31
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-31
ROC | March | MTSS - CMU5 created for communication loss at 02:26 for Christian S. W11769413 #CMU5 | All Wastewater System ROC General | 2026-03-31
ROC | March | NMSSHS - Pump 1 VFD Fault alarm came in. Checked site. Unable to clear. Called Chris R. who will attend site later today. Chris would like a call back if another pump goes down | All Wastewater System ROC General | 2026-03-31
ROC | March | KBSP - Christian from Ferguson Electric is on site and will be completing a load bank test for the generator. | All Wastewater System ROC General | 2026-03-31
ROC | March | HLSSBS - Gen shut off. Chris C called to inform to disregard current reading on we well overflow as small flow going though analyzer due to heavy rainfall and rising level from connecting lake in area | All Wastewater System ROC General | 2026-03-31
ROC | March | NMSSHS, PAC Comm Fail Alarm, Terry R contacted Matt S for him to look into it | All Wastewater System ROC General | 2026-03-31
ROC | March | NMSSBP, Dan K notified ROC that they are overflowing into the EQ tank. MTSS, 2 Operators are still on site working on the issue | All Wastewater System ROC General | 2026-03-31
ROC | March | KBSP - UV Ch2 dosage lo, plant 2 influent flow hihi | All Wastewater System ROC General | 2026-03-31
ROC | March | AUSS - Found pump 1 in manual speed setpoint, placed back in auto. EGSSSC - Inlet channel level hihi, disregard as per area shift report KSSSQW - Wet well ultrasonic level hihi. Heavy rainfall in area. Will monitor site | All Wastewater System ROC General | 2026-03-31
ROC | March | NBSSJA - Lauren S finished at site | All Wastewater System ROC General | 2026-03-31
ROC | March | MTSS - Historian Heartbeat alarm came in. Called Artour L. who is looking into it | All Wastewater System ROC General | 2026-03-31
ROC | March | NBSSJA - Wet well 1 hydrostatic backup mode,, ultrasonic back up mode, wet well hihi level for both modes, LIT2 controlling on hydrostatic,. Informed Lauren S. During call wet well hihi level and overflow was triggered. Overflow is set to 7.64m while hydrostatic trend shows still below 3m and climbing at this time. Lauren S will head to site CMU = 11770082 AUSS - Activate duty 5 as seeing flows increase and will be triggered shortly KCSSKR - Discharge pressure hi, screen fail to stop. Able to clear screen alarm | All Wastewater System ROC General | 2026-03-31
ROC | March | YDSS + YNSS Normal Carter D signing out | All Wastewater System ROC General | 2026-03-31
ROC | March | BLSS - Screen diff lvl hi, monitored site and able to reset bar screen alarm. level came back within range | All Wastewater System ROC General | 2026-03-31
ROC | March | Ethan U signing in Weather 14. | All Wastewater System ROC General | 2026-03-31
ROC | March | HLSSBS - Generator running, fuel pump control panel power fail, PAC control panel power failure. PAC control alarm cleared. Monitoring site EGSSSC - Site hydro power failure, fuel pump control panel power fail, forcemain reverse flow hihi. Able to clear alarms. Pump 3 active | All Wastewater System ROC General | 2026-03-31
ROC | March | RHAMF - AMF fan 1 fail to start, odor control system emergency mode, system offline for odor control, unit 2 recirculation pump 1 overload, station power failure, control panel utility power failure. Able to reset alarms but fan 1 fail to start. Fan 2 running, disregard as per area shift report | All Wastewater System ROC General | 2026-03-31
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-31
ROC | March | SUSP- Basin 1 High Level. Decant phase just beginning and level will start lowering. Notified Tyson C. Can disregard. Requested a call if HiHi comes in. UV System Critical Failure, UV Ch.1,2 High Level. Alarms cleared upon acknowledgement. Known issue on SCADA Report. CONSULT | All Wastewater System ROC General | 2026-03-12
ROC | March | QVSSSC - Darren B on site to complete work orders including a generator test run, JHSC checks and a dry well flood alarm test. Darren has requested that the associated alarms be disregarded. | All Wastewater System ROC General | 2026-03-04
ROC | March | NBSP - UV System Minor fault alarm. Checked site, UV 1A and 1B running. UV duty switching over from Bank 1A to 1B. Disregard alarm as per shift report. | All Wastewater System ROC General | 2026-03-08
ROC | March | AUSS - Generator 1, 2. 3 Not in Auto alarms came in. Checked site. Alarms cleared upon acknowledgement. Generators are not running and site is still connected to utility power | All Wastewater System ROC General | 2026-03-08
ROC | March | SEOC4 - Terry R finished at site | All Wastewater System ROC General | 2026-03-11
ROC | March | SEOC 9 - Shaft 9 O2 monitor OOR, HiHi alarms. Disregard as per SCADA review. NMSSBP - Kevin S still on site. Will call when leaving. 2 pumps remain in man/off for now. Stopped diverting to EQ. | All Wastewater System ROC General | 2026-03-11
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-07
ROC | March | NBSP, Aer Basin 2 Back DO lo/lolo, contacted Dan H as the original interim couldn't be found, suspected that it is expired, notified Dan H that the trends have been up and down but are now holding on the lower end, directed to place a second blower on to help with the DOs 19:14, Placed Blower 2 back to auto 20:22, Dan H is heading to site CMU5: W11714790 | All Wastewater System ROC General | 2026-03-07
ROC | March | GRSSWA- Mechanical Screen Overload Alarm. Mechanical Screen Power Not Avail Alarm. Notified Mike B. Directed disregard alarm until morning. # Consult. | All Wastewater System ROC General | 2026-03-11
ROC | March | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-03-11
ROC | March | NBSP - Influent Flow HiHi and Influent High float alarms came in. After checking site, influent flow levels are slightly above hihi due to higher temperatures and melting snow. Will continue to monitor 19:02 - Mechanical Bar Screen Fail to Stop and OOS alarms came in. Checked site. Called Dan H. who directed to ack/reset. Unable to clear alarms. Dan H. will head to site. CMU5 Created W11714953 20:25 - Dan H. called back to inform that he was able to clear alarm and will not be heading to site. Dan informed that if the alarm comes in again to try and reset, but if unable to reset, Dan would like a call back #CONSULT #CMU5 | All Wastewater System ROC General | 2026-03-08
ROC | March | YDSS + YNSS Normal Connor Smith signing out | All Wastewater System ROC General | 2026-03-05
ROC | March | AUSSYS - Chris R on site and will be completing work orders including the dry well flood alarm test and hi/low temp alarm test. | All Wastewater System ROC General | 2026-03-02
ROC | March | NBSP - Inlet channel level high float, influent flow hihi. Plant is currently experiencing high inlet flows from NBSSJA and heavy rain. Monitoring situation and levels SHSP - Aeriation blower fan 1 overload. Still running 6:37 - Informed Dan H. Expected levels to continue to climb due to weather. Will monitor Consult | All Wastewater System ROC General | 2026-03-11
ROC | March | Ethan U signing in | All Wastewater System ROC General | 2026-03-12
ROC | March | SHSSDK - Marcus R on site to complete a generator test and JHSC checks. | All Wastewater System ROC General | 2026-03-03
ROC | March | SUSP- UV Ch.2 Common Critical Alarm, UV Ch. 1,2, High Level. Alarms cleared upon acknowledging. Known issue on SCADA Report. | All Wastewater System ROC General | 2026-03-11
ROC | March | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-03-12
ROC | March | AUSS - Pump 2 Disch header MV3 failed to close alarm. Cleared alarm/disregard as per shift report. | All Wastewater System ROC General | 2026-03-08
ROC | March | KBSP- Marcus R and Harie R onsite changing UV bulbs. Disregard related alarms. | All Wastewater System ROC General | 2026-03-02
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-05
ROC | March | SUSP- UV system critical failure/ CH 1 high level/ common critical alarms. UV CH 2A is running. Flow to the UV system recently started. All alarms cleared when acknowledged. Disregard on shift report. | All Wastewater System ROC General | 2026-03-09
ROC | March | LSSS - Spoke with Terry R and placed pump 1 and pump 5 in manual/off for the night. Four pumps available. | All Wastewater System ROC General | 2026-03-04
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-04
ROC | March | KCSSKR - Marcos R onsite as well testing dry well flood, sump pit high level, diesel float, leak, and hi/low temp. Checking bar screen and headworks | All Wastewater System ROC General | 2026-03-05
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-06
ROC | March | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-03-08
ROC | March | AUSS- P5 MV# failed to open alarm came in. Reset alarm | All Wastewater System ROC General | 2026-03-06
ROC | March | KBSP - Sludge Tank Level HiHi alarm came in. Checked site. Scum Pumps are interlocked. Called Dan H. who directed to disregard alarm until tomorrow. SHSP - Spoke to Dan about the Sludge tank level hihi alarm. Dan directed to disregard alarm until tomorrow #CONSULT | All Wastewater System ROC General | 2026-03-09
ROC | March | KSSP - ZW4 Permeate Turbidity and Shutdown alarms. Disregard alarms until morning as directed by Tyson C in previous conversation. He will investigate in the morning. Emailed area. | All Wastewater System ROC General | 2026-03-12
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-01
ROC | March | SUSP- UV System Critical Failure, UV CH. 1 Common Critical, UV Ch. 1 High Level. Alarms cleared upon acknowledging. Known issue on SCADA Report. | All Wastewater System ROC General | 2026-03-01
ROC | March | KSSP - Neil O tasting Admin Bld Sump HiHi level alarm. | All Wastewater System ROC General | 2026-03-09
ROC | March | Connor Smith signing in 7C Sunny | All Wastewater System ROC General | 2026-03-04
ROC | March | SUSP- Influent Flow HiHi Alarm. Quick Spike. Cleared alarm. | All Wastewater System ROC General | 2026-03-04
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-04
ROC | March | MTSP - Phil R on site to complete a generator test run. | All Wastewater System ROC General | 2026-03-03
ROC | March | AUSSSR - Line 3 fail to close, overtorque alarm. Informed Kevin S, will head to site CMU = 11730458 | All Wastewater System ROC General | 2026-03-12
ROC | March | LSSS- Communication Failure Alarm. Alarm cleared. | All Wastewater System ROC General | 2026-03-05
ROC | March | NMSSBP - Placed all pumps speed back to auto. | All Wastewater System ROC General | 2026-03-12
ROC | March | KCSSKR - Marcus R running generator onsite, health & safety | All Wastewater System ROC General | 2026-03-11
ROC | March | SUSP- UV System Critical Failure, High Level. Alarms cleared. Known issue on SCADA Report. | All Wastewater System ROC General | 2026-03-10
ROC | March | KSSP - Aeration tank 1 inlet/outlet DO Hi alarms. Will monitor. | All Wastewater System ROC General | 2026-03-12
ROC | March | YDSS+YNSS NORMAL Angelica Chepiga signing out | All Wastewater System ROC General | 2026-03-12
ROC | March | SUSP - Tyson has completed work on the UV system ad is leaving site. | All Wastewater System ROC General | 2026-03-12
ROC | March | KBSP, Scum Tank level hihi/Sludge tank hihi, Dan H called in, directed to disregard for the weekend | All Wastewater System ROC General | 2026-03-07
ROC | March | SUSSHS - Mike B on site to complete a generator test run. | All Wastewater System ROC General | 2026-03-12
ROC | March | KCSSKR, Marcus R called requesting a CMU5. King received a odour complaint and got in contact with Marcus CMU5: W11711498 | All Wastewater System ROC General | 2026-03-05
ROC | March | BLSS - Terry C onsite. Greasing off drive shaft | All Wastewater System ROC General | 2026-03-06
ROC | March | KSSP - UV channel 1 Bank 1A low UV intensity fault. Checked site, UV channel 1 is active. Trending shows the dosage is within normal range and the intensity does not show any abnormal dips. Alarm status changed to Normal during site inspection, alarm cleared on acknowledgement. | All Wastewater System ROC General | 2026-03-03
ROC | March | Adeela Khan signing in. Weather: 16C and Sunny | All Wastewater System ROC General | 2026-03-09
ROC | March | NBSP - Young J on site to complete a generator test run. | All Wastewater System ROC General | 2026-03-02
ROC | March | MTSS - Generator running status alarm. Checked site, operations appear normal. The generator is active but the ATS is pointing to town hydro indicating a short power failure. Will monitor site. MTSP - Compressor 1 motor overload alarm. Checked site, duty rotated to compressor 2. Will contact area operators on site. | All Wastewater System ROC General | 2026-03-13
ROC | March | AUSSYS - Terry R on site to complete pump tests. Terry will be allowing the wet well to fill above the normal range so he can complete all of the pump tests in sequence. Terry stated that the wet well hi/hihi alarms may be triggered but he is on site and watching. | All Wastewater System ROC General | 2026-03-12
ROC | March | NMSSHS - PAC communication failure alarm. informed Ian W of outstanding alarm, will take a look | All Wastewater System ROC General | 2026-03-12
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-03
ROC | March | GRSSWA- Wet Well H2S Sample No Flow Alarm. Disregard as per SCADA Report | All Wastewater System ROC General | 2026-03-11
ROC | March | SUSP - UV system critical failure, UV channel 1 common critical alarm and UV channel hi level alarm. Checked site, trending shows that flow through the UV system recently started. These alarms are disregards on the shift report when flow starts. Alarm status immediately changed to Normal and alarms cleared on acknowledgement. | All Wastewater System ROC General | 2026-03-04
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-01
ROC | March | Connor Smith signing in -12 C Clear | All Wastewater System ROC General | 2026-03-01
ROC | March | KSSSQW, Pump 2 lo flow, rotated pump dudty | All Wastewater System ROC General | 2026-03-07
ROC | March | Carter Dunn Signing In, 16D/Rain | All Wastewater System ROC General | 2026-03-07
ROC | March | KSSSQW - Kevin K on site to complete some pump testing and has requested all alarms be disregarded on site. | All Wastewater System ROC General | 2026-03-12
ROC | March | KSSSQW, Pump 2 flow lolo//Pump 2 wire to water lolo/Efficiency lolo, contacted both Mike B/Chris C, both didn't answer, left a voice message, will call again in 10 minutes | All Wastewater System ROC General | 2026-03-13
ROC | March | YDSS + YNSS Normal Connor Smith signing out | All Wastewater System ROC General | 2026-03-13
ROC | March | SUSP - UV Critical alarms came in. Plant just started and alarms cleared upon acknowledgment. Disregard as per shift report | All Wastewater System ROC General | 2026-03-13
ROC | March | MTSP - Compressor 1 and 2 E.stop alarms came in. Checked site. Both are interlocked. Checked Barry M's MTSP Logbook post which states compressor 1 and 2 cleaning and inspection | All Wastewater System ROC General | 2026-03-13
ROC | March | KSSSQW - Neil O. called to inform he will be completing a backflush of pump 1 to increase the flow | All Wastewater System ROC General | 2026-03-13
ROC | March | YDSS + YNSS Normal Carter D Signing Out | All Wastewater System ROC General | 2026-03-13
ROC | March | KSSP - ZW2 shutdown alarm. Checked site, all other trains are either in production or going through an M-clean process leaving no filters on standby. Called Niel O to inform. | All Wastewater System ROC General | 2026-03-13
ROC | March | Adeela Khan signing out | All Wastewater System ROC General | 2026-03-13
ROC | March | Christian Van Beek signing out. | All Wastewater System ROC General | 2026-03-13
ROC | March | SUSP- UV system critical failure/ CH 1 high level/ common critical alarms. UV CH2 is running. Alarms cleared when acknowledged, disregard on shift report. | All Wastewater System ROC General | 2026-03-10
ROC | March | NMSSBP - Wet Well 1 and 2 Hi alarms. Alarms cleared. | All Wastewater System ROC General | 2026-03-10
ROC | March | AUSSYS - Terry R finished at site | All Wastewater System ROC General | 2026-03-12
ROC | March | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-03-11
ROC | March | AUSSMP - Wet Well 1/2 High alarms. Placed Pump 2 man/currently running 60%-man speed , Pumps 5 and 6 manual speed - 60% to pump down wet well. | All Wastewater System ROC General | 2026-03-11
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-04
ROC | March | Angelica Chepiga signing in, weather +7C | All Wastewater System ROC General | 2026-03-09
ROC | March | SUSP - Woodriver Bend flow fault /OOS alarms. Two pumps running at SUSSWB. | All Wastewater System ROC General | 2026-03-11
ROC | March | YDSS+YNSS NORMAL Angelica Chepiga signing out | All Wastewater System ROC General | 2026-03-11
ROC | March | Angelica Chepiga signing in, weather +7C | All Wastewater System ROC General | 2026-03-10
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-14
ROC | March | Harvest Hills Blvd and Old Field Cres, Kevin J from Paramedic Services called, informed the RO that a car took out a green box on the location provided, when checking all pipes, location shows a wastewater pumping station on site however no info about said pumping station. Took down Kevin J information to pass on to an operator. Contacted Kevin S and informed him of the situation, Kevin directed to contact ORO Marcus R as he isn't aware of any wastewater sites in that area. Marcus R is looking into it. Marcus R suggested calling Central Water Operator as it may be one of their sites, Will contact Central Operator Ben H just incase this is a water site 10:10, Talked with Ben H, its not a central water site. After digging further into all pipes and adjusting a few settings, the pumping station belongs to East Gwillimbury. Contacted EG After hours support operator Martin and passed on the information Kevin J: 2897163243 (YR Paramedic Services) Martin (East Gwillimbury After Hours Support) | All Wastewater System ROC General | 2026-03-14
ROC | March | MTSP, Aeration Tank 2 DO lo alarm, Placed blower 2 man/on as per shift report 13:09, Placed blower 2 back to auto | All Wastewater System ROC General | 2026-03-14
ROC | March | NMSSBP - Wet well 1 & 2 overflow, hihi level. Pumps 1 & 2 were left man/off. Followed up with Dan K. Leaving those pumps off to divert to EQ and lessen load to AUSS as high flows coming in | All Wastewater System ROC General | 2026-03-11
ROC | March | HMSS - Security intrusion alarm on the dialer. No alarms on SCADA, trends normal. Marcus R on site. # Consult | All Wastewater System ROC General | 2026-03-15
ROC | March | MTSP, DO between the 2 aerations tanks is quite drastic. Tank 2 is alot higher than tank 1. contacted Kevin S about this observation as D2 wont be stopping for a bit, got no response, left a voice message, will call again in 15 minutes 19:38, Called 2 more times but no response, will call one more time at 20:00, will continue to monitor the DOs on site 19:55, directed to disregard at this time, If DOs remain the same in an hour, Kevin S will call back and will make some changes to the system 21:50, Kevin S called back, notified him that the DO range is still in the same spot, directed to place both blowers 2/3 man/off for the time being. If the DO lo comes in, directed to place the blowers back to auto and leave it for the night, will send email to operator 22:09, Placed blowers 2/3 back to auto as the DO dropped off consult | All Wastewater System ROC General | 2026-03-15
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-15
ROC | March | EGSSSC - Inlet channel level HiHi, quick spike, alarm cleared. | All Wastewater System ROC General | 2026-03-08
ROC | March | RHAMF1 - Unit 2 Recirculation Pumps 1 and 2 overload alarms came in. Low priority alarms. Shift report directs to make sure a fan is running. Both fans are still running Unit 1 Recirc Pump 1 is still running | All Wastewater System ROC General | 2026-03-01
ROC | March | NBSS - Young J testing eyewash alarm. | All Wastewater System ROC General | 2026-03-09
ROC | March | GRSSWA - Wet well 1 and 2 ultrasonic and hydrostatic levels Hi alarms. All 3 pumps running on Hydrostatic mode. Wet well level slowly increasing. Notified Mike B. # Consult 05:59 Wet well 1/2 HiHi switch alarms. Notified Mike B. He will check SCADA. # Consult | All Wastewater System ROC General | 2026-03-11
ROC | March | Christian Van Beek signing in. | All Wastewater System ROC General | 2026-03-13
ROC | March | QVSSSC - Generator running status alarm. Checked site, generator is running but ATS is pointing to town hydro indicating a power blip scenario. No impact to operations, will monitor site. | All Wastewater System ROC General | 2026-03-13
ROC | March | SUSP - UV channel 2 high level and common critical alarm, UV channel 1 high level and common critical alarm and UV system critical failure alarm. Checked site, UV channel 1 is active. Trending shows that flow to the UV system recently started. Shift report states these alarms are triggered when flow starts and can be disregarded in these circumstances. Cleared alarms. | All Wastewater System ROC General | 2026-03-13
ROC | March | KSSP - UV channel 2 Bank 2 A lamp fail and adjacent lamp fail alarms. UV channel 2 is active. Alarm disregard as per shift report. | All Wastewater System ROC General | 2026-03-15
ROC | March | BLSS - Marcus R testing temperature and Drywell flood alarms. | All Wastewater System ROC General | 2026-03-09
ROC | March | LSSS - Pump 1 Motor/Bearing Hi Temp and Hi Temp Trip alarms. Phil R on site. | All Wastewater System ROC General | 2026-03-09
ROC | March | SHSSDK - Generator fault alarm. Lance J on site, contractor changing the Hydro meter. Lance J will clear alarm. | All Wastewater System ROC General | 2026-03-09
ROC | March | SEOC4 - Shaft 4 O2 Monitor 2 OOR and HiHi alarms came in. Disregarded as per shift report | All Wastewater System ROC General | 2026-03-08
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-12
ROC | March | EGSSSSC- Inlet Channel Level HiHi Alarm. Alarm cleared | All Wastewater System ROC General | 2026-03-11
ROC | March | EGSSSC- Satnam M onsite for soft start work on pump 2 and placed in Local. Pump 3 is available in duty 1. 11:35- Satnam M finished onsite. Pump 2 is back in auto. | All Wastewater System ROC General | 2026-03-02
ROC | March | SUSP - Filter hi level alarm. Checked site, trending shows that the filter flow rate is higher than normal due to to the EQ tank pump speed being higher than normal. Called Tyson C who will relay the message to his team. | All Wastewater System ROC General | 2026-03-13
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-14
ROC | March | AUSS, Generator 1 Warning Alarm/engine battery low voltage alarm/Gen1Engine (Warning) alarm Shift report doesn't mention generator alarms, notified Kevin S, he is looking into the issue. Alarm was able to be cleared however it did come back in a second time. Kevin S is heading to site 16:04, Kevin S called back, has asked for Electrical on call to give him a call as he believes one of the batteries may be burning. Contacted Dan B, he will give Kevin S a call 16:10, Dan B is heading to site CMU5: W11733335 (Kevin S) CMU5: W11733345 (Dan B) | All Wastewater System ROC General | 2026-03-14
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-16
ROC | March | SUSP - UV channel 1 common critical alarm, UV channel 1 high level alarm and UV system critical failure alarm. Checked site, UV channel 2 is active. Trending shows that flow through the UV channel recently started. Shift report states these alarms trigger when flow starts and are a disregard. Cleared alarms. | All Wastewater System ROC General | 2026-03-10
ROC | March | LSSS - Phil R on site to complete pump valve exercising. Phil stated all associated alarms can be disregarded until the work is done. | All Wastewater System ROC General | 2026-03-13
ROC | March | NMSSHS, Kevin S on site, doing wet well testing, testing dry well flood/Auto dialer alarms and testing temp alarms | All Wastewater System ROC General | 2026-03-13
ROC | March | NBSP - UV System Minor Fault alarm came in. Checked site. Bank 1B is running. Disregarded as per shift report | All Wastewater System ROC General | 2026-03-04
ROC | March | Carter Dunn Signing Out | All Wastewater System ROC General | 2026-03-07
ROC | March | AUSS - Wet wells Hi and HiHi alarms in and out. 3 pumps constantly running, 4th pump on and off. 1 extra pump available. High flows. Monitoring. | All Wastewater System ROC General | 2026-03-08
ROC | March | NBSSJA - Young J informed contractors onsite and they are doing sewer cleaning, running wells on low level while cleaning in progress | All Wastewater System ROC General | 2026-03-06
ROC | March | LSSS - Emily B from EME on site to take samples. Emily requested that pump 6 be activated to draw a sample. Made the necessary pump duty change. | All Wastewater System ROC General | 2026-03-04
ROC | March | NMSSHS - Kevin S on site to complete a generator test run. Associated generator alarms will be triggered. | All Wastewater System ROC General | 2026-03-02
ROC | March | SUSP - UV channel 1 common critical and high level alarm and UV system critical alarm. Checked site, UV flow recently started. Disregard as per the shift report. Alarms cleared on acknowledgement. | All Wastewater System ROC General | 2026-03-03
ROC | March | Ethan U signing in Weather 0. | All Wastewater System ROC General | 2026-03-14
ROC | March | AUSS - Dan B & Kevin S finished at site, replaced 2 batteries for gen 1 | All Wastewater System ROC General | 2026-03-14
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-14
ROC | March | SUSP- UV system critical failure/ CH 1+2 high level/ common critical alarms. Flow to the UV system recently started. All alarms cleared when acknowledged. Disregard on shift report. | All Wastewater System ROC General | 2026-03-08
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-11
ROC | March | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-03-12
ROC | March | NBSSJA - Young J onsite testing generator | All Wastewater System ROC General | 2026-03-03
ROC | March | NBSP- Inlet Channel High Float. Alarm cleared. | All Wastewater System ROC General | 2026-03-10
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-14
ROC | March | Christian Van Beek signing in. | All Wastewater System ROC General | 2026-03-04
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-03
ROC | March | Christian Van Beek signing out. | All Wastewater System ROC General | 2026-03-03
ROC | March | SEOC Shaft 6/7 - Terry R. is on site and will be running the diesel generator 11:26 - Terry R. is finished on site | All Wastewater System ROC General | 2026-03-04
ROC | March | YDSS + YNSS Normal Connor Smith signing out | All Wastewater System ROC General | 2026-03-01
ROC | March | KSSP - Membrane Operating Area MUA-10 Temp Switch Lo alarm came in. Disregarded as per shift report KSSP- Makeup Air Unit 5 Temp Switch Lo alarm came in. Disregarded as per shift report KSSP - Alum Chem Room MUA - 11 Differential Pressure Switch Hi alarm came in. Will email Cam B. | All Wastewater System ROC General | 2026-03-02
ROC | March | SUSP - Influent flow hihi alarm. Checked site, multiple sewage pump[ing stations pushing flow to the headworks resulting in high flows. Flows dropped while monitoring. Cleared alarms. | All Wastewater System ROC General | 2026-03-05
ROC | March | Christian Van Beek signing in. Weather: 2C and rain. | All Wastewater System ROC General | 2026-03-05
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-05
ROC | March | Adam Button signing in 0C Raining | All Wastewater System ROC General | 2026-03-06
ROC | March | NMSSHS - Aaron M. from the Network team is on site to check the cell modem due to the intermittent PAC communications that have been coming in. Aaron informed that communication will be lost for 5 mins but will repopulate shortly. Aaron informed that this should not affect operations. Confirmed with Kevin S. 14:31 - Aaron called back to inform he is finished on site | All Wastewater System ROC General | 2026-03-04
ROC | March | AUSS, Rotated pump duty for Terry C, Terry C on site working on the pumps | All Wastewater System ROC General | 2026-03-05
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-06
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-13
ROC | March | BLSS - Marcus R testing wet well levels and sump pit alarms. | All Wastewater System ROC General | 2026-03-09
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-06
ROC | March | MTSP- Terry R heading to site to drain clarifier 1. Directed to place RAS P3 in man/on | All Wastewater System ROC General | 2026-03-07
ROC | March | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-03-11
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-05
ROC | March | SUSP - UV system critical failure alarm, UV channel 1 high level alar and UV Channel 1 common critical alarm. Checked site, UV system is active. Trending shows that flow to the UV system recently started. Shift report states these alarms will trigger when flow activates and can be disregarded under these circumstances. Alarm status changed to Normal, alarms cleared on acknowledgement. | All Wastewater System ROC General | 2026-03-05
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-13
ROC | March | Ethan U signing in Weather -0. Snowing | All Wastewater System ROC General | 2026-03-13
ROC | March | QVSSSC- Sewage pump 2 VFD fault alarm, notified Mike B. He will check SCADA. # Consult 15:30 Mike B will attend site. # CMU5 W11714918 | All Wastewater System ROC General | 2026-03-08
ROC | March | KSSP - ZW2 MDF Flow TMP Delta Low and High Alarms, cleared when acknowledged. ZW2 in backwash. | All Wastewater System ROC General | 2026-03-08
ROC | March | NBSP - Inlet channel High Float alarm and Mech Bar screen OOS , failed to stop alarms. Was able to clear all alarms. Influent flow HiHi alarm outstanding. High flows. Monitoring. | All Wastewater System ROC General | 2026-03-08
ROC | March | AUSS - 4 pumps running constantly, twin forcemain is active, wet well level increasing. Notified Terry R. Requested Run Pump 2(duty 5) in manual. Placed pump 2 in man/on. Pump not starting. Left man/off. Placed Pump 5 manual (currently running) increased speed to 60%. Terry R will check SCADA. # Consult Placed Pump 6 manual 40% speed and decreased Pump 5 speed from 60 to 40%. Placed Pump 1 man/on 40% speed. | All Wastewater System ROC General | 2026-03-08
ROC | March | AUSS - Increased Pump 6 speed from 40 to 60%. Requested NMSSBP Pumps 2,3,4 man/stop and send flow to EQ. Terry R not able to login to SCADA. He will contact Kyle C and call back. | All Wastewater System ROC General | 2026-03-08
ROC | March | SUSP - UV channel 1 common critical/channel 1 high level alarms and UV system critical failure alarm. UV channel 1 is active, flow through the UV channel recently started. Disregard alarms as per shift report. Alarms cleared when acknowledged. | All Wastewater System ROC General | 2026-03-15
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-13
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-13
ROC | March | SUSP - UV Ch. 1 common critical, high level, critical failure. Alarm cleared upon acknowledgment as UV alarm came in during startup. | All Wastewater System ROC General | 2026-03-13
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-13
ROC | March | LSSS - Wet well screen 1 differential level hihi, monitored level and saw it come down | All Wastewater System ROC General | 2026-03-14
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-15
ROC | March | Angelica Chepiga signing in,weather -4C | All Wastewater System ROC General | 2026-03-15
ROC | March | Ethan Ullalkar signing out. | All Wastewater System ROC General | 2026-03-15
ROC | March | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-03-15
ROC | March | Carter Dunn Signing In, 1D/Rain | All Wastewater System ROC General | 2026-03-06
ROC | March | KSSP - UV Ch.1 Bank 1A low UV intensity. Checked site, UV1 running showing intensity | All Wastewater System ROC General | 2026-03-14
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-14
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-14
ROC | March | Carter Dunn Signing In. -3D/Snowing | All Wastewater System ROC General | 2026-03-14
ROC | March | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-03-15
ROC | March | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-03-15
ROC | March | LSSS - Terry R onsite to reset fault on pump 1. Running pump 1 duty 1 to help break down build up. Disregard pump 1 fault when it comes it as triggered due to bearing temperrature. | All Wastewater System ROC General | 2026-03-05
ROC | March | NBSSJA- Young J testing hi/lo temp/drywell flood and sump hi alarms | All Wastewater System ROC General | 2026-03-06
ROC | March | YDSS + YNSS Normal Adeela Khan signing out | All Wastewater System ROC General | 2026-03-09
ROC | March | LSSS - Generator 3 warning and DGC not in auto alarms. Notified Phil R, he will investigate. | All Wastewater System ROC General | 2026-03-09
ROC | March | KBSP - Historian Heartbeat and PAC Communication Failure alarm came in. Checked site. Flatlining. Called Yash S. who will take a look. CMU5 created W11697421 02:55 - Yash S. called back to inform that he is unable to access and redirect the site to be able to trend again. Yash explained that there is a power issue with the sludge building and requested to give Young J. a call. 02:58 - Called Young J. who will look at SCADA 03:01 - Yash S. called back and informed he will speak to Network On Call 03:05 - Young J. called back informed that he will attend site (CMU5 Created W11697431) and requested for Yash S. to meet him there. 03:08 - Called Yash S. who is headed to site. 04:28 - Yash S. called to inform that he and Young J. are both finished on site. Yash informed that the issue was a blown fuse. All alarms have been cleared, and site is now back to normal operations #CONSULT #CMU5 | All Wastewater System ROC General | 2026-03-01
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-01
ROC | March | EGSSSC - River Bridge Heat Trace Alarm came in. Low Priority alarm. Checked site. Trending is okay. Will send an email to On call North WW operator. | All Wastewater System ROC General | 2026-03-01
ROC | March | KSSP - UV Ch1 bank 1A Low UV intensity fault alarm, UV 1 running, alarm cleared upon acknowledgement. | All Wastewater System ROC General | 2026-03-02
ROC | March | SEOC OCF - FAN1 and FAN2 uncommanded stop alarms. ACK/reset alarms. FAN1 and FAN2 restarted. Will monitor. | All Wastewater System ROC General | 2026-03-02
ROC | March | KSSP - Garrick remove batteries for generator temporarily for work | All Wastewater System ROC General | 2026-03-05
ROC | March | Ethan Ullalkar signing out. | All Wastewater System ROC General | 2026-03-03
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-01
ROC | March | LSSS - Pump 1 fault alarm. Checked site, pump duty rotated to pump 5. Phil R logged into the facility logbook to complete work orders. Will monitor site. | All Wastewater System ROC General | 2026-03-02
ROC | March | KSSP - UV CH.1 Bank 1A Low UV Intensity Fault alarm. UV CH1 is running. Notified Cam B. He directed disregard alarm until tomorrow. He will inform Kevin K to create w/o with instrumentation. # Consult. | All Wastewater System ROC General | 2026-03-02
ROC | March | SUSP - Eric S. informed that he is finished working on the lagoon flowmeter and no alarms remain | All Wastewater System ROC General | 2026-03-04
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-05
ROC | March | PVSS- P1 in a ultrasonic mode/ discharge flow hi alarms came in. Lauren S on site performing valve exercises and had P2/3 in man/off. Lauren S not sure why P1 went into ultrasonic mode but will investigate on site | All Wastewater System ROC General | 2026-03-06
ROC | March | KBSP - Harie R. called to inform that he will be conducting an inspection to the sump pits in both the tertiary and headworks building. Harie informed that he will be tipping floats making sure that pumps are working | All Wastewater System ROC General | 2026-03-04
ROC | March | YDSS+YNSS normal Adam Button signing out | All Wastewater System ROC General | 2026-03-06
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-07
ROC | March | YDSS+ YNSS Normal | All Wastewater System ROC General | 2026-03-07
ROC | March | YDSS + YNSS Normal NBSP, Placed BLower 2 back to auto | All Wastewater System ROC General | 2026-03-08
ROC | March | SUSP- SBR storm alarm came in notified Mike B. Will take a look on SCADA 12:00-SUSP- Mike B notified ROC to disregard SBR storm alarm but call for super storm alarm #consult | All Wastewater System ROC General | 2026-03-07
ROC | March | YDSS+YNSS normal AUSS- wet well 1/2 Lit 1/2 hi alarms. D4 active will continue to monitor | All Wastewater System ROC General | 2026-03-07
ROC | March | GRSSWA- P1/3 in ultrasonic mode. Wet well slowly pumping down. Will continue to monitor | All Wastewater System ROC General | 2026-03-07
ROC | March | LSSS - Surge tank 1 level High alarm. Duty just reassigned and pumps started. Quick spike. Alarm cleared. | All Wastewater System ROC General | 2026-03-08
ROC | March | SUSP- UV system critical failure/ CH 1+2 high level/ common critical alarms. Flow to the UV system recently started. All alarms cleared when acknowledged. Disregard on shift report. | All Wastewater System ROC General | 2026-03-08
ROC | March | YDSS + YNSS normal | All Wastewater System ROC General | 2026-03-09
ROC | March | NMSSBP- Kevin S called , Locking out Pump 4. Local/off until farther notice. | All Wastewater System ROC General | 2026-03-09
ROC | March | GRSSWA - Mechanical Screen Power Not Available and Overload alarms came in. Mechanical Screen 1 is stopped and in local. Called Mike B. who will take a look on SCADA 20:57 - Mike B. called back to inform that he is headed to site. CMU5 Created W11719346 #CONSULT #CMU5 | All Wastewater System ROC General | 2026-03-09
ROC | March | NBSP - UV Minor Fault alarm. Checked site, UV bank 1B is active. Trending shows the duty recently rotated. Shift report states this alarm is a disregard as long as one UV bank is active. | All Wastewater System ROC General | 2026-03-10
ROC | March | MTSP - Clarifier 1 no RAS Pump running alarm. Checked site, clarifier 1 showing as manual/off. Shift report states that clarifier 1 is OOS so RAS pump 3 is also manual/off. | All Wastewater System ROC General | 2026-03-10
ROC | March | KBSP - PAC communication failure, historian heartbeat. Informed Yash S of outstanding alarms PAC4 to PAC3 comm fail. PAC3 comm fail | All Wastewater System ROC General | 2026-03-03
ROC | March | GRSSWA - Chris C finished at site | All Wastewater System ROC General | 2026-03-03
ROC | March | Christian Van Beek signing out | All Wastewater System ROC General | 2026-03-02
ROC | March | YDOC - Terry R onsite running generator rotating fan 9:15 - Finished at site SEOC - Terry R continuing work with generator and fan rotation | All Wastewater System ROC General | 2026-03-03
ROC | March | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-03-02
ROC | March | KSSP- MUA2 Low Temp alarm. Disregard as per SCADA report. | All Wastewater System ROC General | 2026-03-02
ROC | March | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-03-03
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-03
ROC | March | GRSSWA- Mechanical Screen Overload Alarm. Mechanical Screen Power Not Avail Alarm. Notified Chris C. He will look into it. | All Wastewater System ROC General | 2026-03-10
ROC | March | KSSP - Neil O onsit. Testing chem flood alarm, & membrane sump pit | All Wastewater System ROC General | 2026-03-06
ROC | March | AUSS - Wet well 1 level High alarm. Man/start Pump 6 to pump down wet well / help with high flows. | All Wastewater System ROC General | 2026-03-10
ROC | March | YDSS+YNSS normal | All Wastewater System ROC General | 2026-03-07
ROC | March | YDSS+YNSS normal | All Wastewater System ROC General | 2026-03-07
ROC | March | EGSSSC- Inlet channel hihi alarm came in. High flows and D1 active pumping both wet well and inlet channel down. Cleared alarm when level dropped below setpoint | All Wastewater System ROC General | 2026-03-07
ROC | March | YDSS+YNSS normal | All Wastewater System ROC General | 2026-03-07
ROC | March | MTSS, Philip R on site, doing a generator test | All Wastewater System ROC General | 2026-03-05
ROC | March | YDSS+YNSS Normal | All Wastewater System ROC General | 2026-03-07
ROC | March | MTSP - Clarifier 2 Failed to Start and Fault alarms came in. Checked site. Called Phil R. who is headed to site. CMU5 Created W11697603 23:27 - Phil called back to inform that he is finished on site as he was able to get clarifier 2 up and running again. Phil requested a call back if that fault comes back in #CONSULT #CMU5 | All Wastewater System ROC General | 2026-03-01
ROC | March | Christian Van Beek signing out. | All Wastewater System ROC General | 2026-03-12
ROC | March | SUSSWB - Ventilation H2D high/fault, hihi. Disregard wetwell gas alarms afterhours as per shift report. Able to clear alarms | All Wastewater System ROC General | 2026-03-12
ROC | March | EGSSSC - Inlet channel Level HiHi alarms at duty start up, alarms cleared shortly after. | All Wastewater System ROC General | 2026-03-11
ROC | March | NMSSBP, AUSSMP, NMSSHS - Kevin S called. All pumps back to auto, auto speed. NMEQBP - Marcos T man/started Dewatering pump 1 to pump down EQ tank. | All Wastewater System ROC General | 2026-03-11
ROC | March | KSSP - ZW4 Permeate Turbidity HiHi / Shutdown alarms. Notified Tyson C. He will check SCADA. # Consult QVSSSC - Sewage pump 2 VFD Fault alarm. Pump 1 running ok. Disregard until tomorrow as per Tyson C. 23:03 QVSSSC - Tyson C checked SCADA, He will attend site to reset pump. # CMU5 W11726656 | All Wastewater System ROC General | 2026-03-11
ROC | March | QVSSSC - Pump 2 back to auto. Tyson C leaving site. | All Wastewater System ROC General | 2026-03-11
ROC | March | AUSS - Placed P2 back to auto/ auto speed. | All Wastewater System ROC General | 2026-03-11
ROC | March | NMSSBP - Wet well level HiHi alarm. EGSSSC and NMVCBP duty deactivated. NMSSBP HiHi level alarms cleared. | All Wastewater System ROC General | 2026-03-08
ROC | March | NMSSBP - Placed Pump 3 back to auto. | All Wastewater System ROC General | 2026-03-08
ROC | March | AUSS - Terry R. called back to inform that he spoke with Kyle C. and determined that there was an issue with the programming which was able to be resolved. Terry informed that pump 2 is up and running now. Terry also informed that all pumps can go back to auto at both AUSS and NMSSBP. Terry would like a call back if any other issues arise AUSS and NMSSBP - All pumps have been placed back to auto | All Wastewater System ROC General | 2026-03-08
ROC | March | KSSP - ZW1 MDF Flow Incycle TMP Low alarm came in. Alarm cleared upon acknowledgement | All Wastewater System ROC General | 2026-03-08
ROC | March | Christian Van Beek signing in. | All Wastewater System ROC General | 2026-03-09
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-01
ROC | March | AUSS - Wet Well 1/2 High level alarms. Placed Pump 2(currently running) to 60% manual speed. | All Wastewater System ROC General | 2026-03-11
ROC | March | SEOC4 - Shaft 4 O2 Mon HiHi alarm, disregard as per SCADA review. | All Wastewater System ROC General | 2026-03-11
ROC | March | NMSSBP - Wet well Level Hi alarms. Duty 3 about to start. AUSSMP - All pumps running. Called Kevin S to stop dewatering pump at EQ tank. Will empty EQ tank later, when flows slow down. # Consult | All Wastewater System ROC General | 2026-03-11
ROC | March | Angelica Chepiga signing in, weather +3C | All Wastewater System ROC General | 2026-03-08
ROC | March | Carter Dunn Signing In, -2D/Clear | All Wastewater System ROC General | 2026-03-04
ROC | March | BLSS- Screen 1 Emergency Stop. Christian S onsite for PMs. | All Wastewater System ROC General | 2026-03-11
ROC | March | LSSS- Ubah (Student) onsite and requested pump 6 in duty 1 for sampling. | All Wastewater System ROC General | 2026-03-11
ROC | March | SHSP - Lance J on site to complete work orders and will be testing e-stop alarms in the headworks building. | All Wastewater System ROC General | 2026-03-09
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-12
ROC | March | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-03-08
ROC | March | KSSSQW - Chris C leaving site. All pumps now available. | All Wastewater System ROC General | 2026-03-09
ROC | March | HLSSBS - Darren B onsite testing drywell flood autodialer, and running generator | All Wastewater System ROC General | 2026-03-05
ROC | March | SHSP - Sludge holding tank level hihi alarm. Checked site, sludge holding tank level has been steady since early this morning. Alarm triggered due a small increase in level registered by SCADA which could be due to the sludge blowers "lifting" the surface level. Will monitor site, if the level shows signs of increasing will call OCO. | All Wastewater System ROC General | 2026-03-09
ROC | March | YDSS + YNSS Normal Connor Smith signing out | All Wastewater System ROC General | 2026-03-04
ROC | March | SUSSWB - Pump fail alarm on the dialer. Checked SCADA, quick dip in flow trend/recovered right away. Pump 2 is running. | All Wastewater System ROC General | 2026-03-11
ROC | March | QVSSSC - Test alarm on the dialer. Checked site, duty just deactivated. All trends normal. | All Wastewater System ROC General | 2026-03-12
ROC | March | NBSP - UV System Minor fault alarm. Checked site, UV 1A running. Disregard alarm as per shift report. | All Wastewater System ROC General | 2026-03-09
ROC | March | Carter Dunn Signing Out | All Wastewater System ROC General | 2026-03-05
ROC | March | Ethan Ullalkar signing out. | All Wastewater System ROC General | 2026-03-05
ROC | March | SUSP- Influent free Cl2 hihi alarm came in. Flow returned to normal reset alarm | All Wastewater System ROC General | 2026-03-06
ROC | March | Adeela Khan signing out | All Wastewater System ROC General | 2026-03-01
ROC | March | SUSSWB - Mike B onsite running diesel | All Wastewater System ROC General | 2026-03-05
ROC | March | KSSP - ZW5 TMP control low alarm. Disregard alarm as per the shift report. | All Wastewater System ROC General | 2026-03-12
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-01
ROC | March | SEOC4- Terry R onsite to run diesel generator. | All Wastewater System ROC General | 2026-03-11
ROC | March | MTSP - Final Effluent Flow LoLo alarm came in. Disregarded as per shift report | All Wastewater System ROC General | 2026-03-01
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-01
ROC | March | KSSP - Niel O on site to complete maintenance on the Alum system and directed that all associated alarms can be disregarded. | All Wastewater System ROC General | 2026-03-10
ROC | March | SHSP - RAS pump 2 speed deviation alarm. Checked site, RAS pump is still pushing floe. Reset the alarm once and it trigged again. Called Gavin W who will check the pump. | All Wastewater System ROC General | 2026-03-12
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-01
ROC | March | Adeela Khan signing in. Weather: -11C and Sunny | All Wastewater System ROC General | 2026-03-01
ROC | March | NBSP- Inlet Channel High Float. Alarm cleared. Mechanical Bar Screen Fail to Stop. Alarm Cleared | All Wastewater System ROC General | 2026-03-10
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-04
ROC | March | YDSS + YNSS Normal Connor Smith signing out | All Wastewater System ROC General | 2026-03-10
ROC | March | NBSP- Inlet Channel High Float. Alarm cleared. Mechanical Bar Screen Fail to Stop. Alarm Cleared | All Wastewater System ROC General | 2026-03-10
ROC | March | MTSS - Communication Loss to MTSS alarm. Notified Kyle C. He will investigate. # CMU5 W11722573 05:05 Kyle C called. Communication recovered. Trends OK. | All Wastewater System ROC General | 2026-03-11
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-09
ROC | March | NBSP - Harrie R onsite working on scum pumps | All Wastewater System ROC General | 2026-03-12
ROC | March | KSSSQW - Wet well Ultrasonic and Hydrostatic levels Hi Hi alarms. Duty 3 Just activated. Will monitor. | All Wastewater System ROC General | 2026-03-11
ROC | March | NBSP- Inlet Channel High Float. Alarm cleared. Mechanical Bar Screen Fail to Stop. Alarm Cleared. | All Wastewater System ROC General | 2026-03-11
ROC | March | NBSSJA - Young J called, contractors cleaning Wet well on site. He disabled LoLo level lockout alarm. | All Wastewater System ROC General | 2026-03-09
ROC | March | YDSS+YNSS NORMAL Angelica Chepiga signing out | All Wastewater System ROC General | 2026-03-09
ROC | March | EGSSSC- Inlet Channel Level HiHi Alarm. Alarm cleared. | All Wastewater System ROC General | 2026-03-11
ROC | March | BLSS- Marcus R onsite testing eye wash alarm. | All Wastewater System ROC General | 2026-03-11
ROC | March | SUSP - UV Ch. 1 high level, common critical, UV system major fault, multiple lamp fault Ch. 2, 2A major fault. Informed Tyson C onsite, will look into issue | All Wastewater System ROC General | 2026-03-12
ROC | March | EGSSSC - Sewage pump 2 bypass alarm. Checked site, no obvious issues on site. Alarm was cleared remotely. AUSS - Pump 1 discharge MV2 Fault alarm. Checked site, duty 1 has rotated to pump 5 which is operating normally. Able to clear alarm. | All Wastewater System ROC General | 2026-03-02
ROC | March | SHSP - Marcus R on site to complete a generator test run and JHSC checks. KBSP - Harie R on site to complete an inspection for the RSHW blowers. | All Wastewater System ROC General | 2026-03-02
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-10
ROC | March | SUSP- UV System Critical Failure. UV Ch. 1,2 high level. Alarms cleared after acknowledging. Known issue on SCADA Report. | All Wastewater System ROC General | 2026-03-11
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-07
ROC | March | QVSSSC- Chris C and Darren B on site to test wetwell floats | All Wastewater System ROC General | 2026-03-06
ROC | March | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-03-08
ROC | March | Carter Dunn Signing In, -2D/Clear | All Wastewater System ROC General | 2026-03-05
ROC | March | Ethan U signing in Weather -7. | All Wastewater System ROC General | 2026-03-03
ROC | March | KSSSQW- Chris C on site to test hi wet well alarms | All Wastewater System ROC General | 2026-03-06
ROC | March | NBSP, As per Dan H direction, if the back DO drops below 1.25PPM, place on a second blower. Placed Blower 2 Man/on | All Wastewater System ROC General | 2026-03-07
ROC | March | NMSSBP - Placed Pump 3 man/on to pump down wet well before EGSSSC duty will activate. | All Wastewater System ROC General | 2026-03-08
ROC | March | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-03-08
ROC | March | SUSP - UV System Critical Failure , Ch 1 High Level, Ch.2 Common critical alarms came in. Checked site. Plant recently activated. Disregard as per shift report. Cleared upon acknowledgement. | All Wastewater System ROC General | 2026-03-08
ROC | March | SUSP - UV channel 1 and 2 high level alarm, UV channel 1 and 2 common critical alarm and UV system critical alarm. Checked site, UV channel 2 is active. Trending shows that flow through the UV channel recently started. Shift report states that these alarms are disregards following flow start. Alarm status changed to Normal and alarms cleared on acknowledgement. | All Wastewater System ROC General | 2026-03-09
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-01
ROC | March | AUSS - Terry C onsite requesting to have pump 2 run in duty. Rotated pump 2 to duty 1 KBSP - Harie R onsite inspecting clarifier, may alternate duty on clarifiers | All Wastewater System ROC General | 2026-03-05
ROC | March | KSSP - Cam B onsite for monthly disel run | All Wastewater System ROC General | 2026-03-03
ROC | March | KSSP - Train ZW2,3,4,5 MDF flow inclycle tmp low, transmembrane pressure lo, temp delta high . Informed Mike B. Will let the morning team now, issue due to weather and hi flow Consult | All Wastewater System ROC General | 2026-03-11
ROC | March | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-03-11
ROC | March | NMSSBP - Kevin S leaving site, 2 pumps running and 2 pumps man/off. Kevin S and Marcos T (back-up) will check system later tonight to return pumps to auto, NMEQBP -Kevin S requested to leave / not to run dewatering pumps until tomorrow morning. | All Wastewater System ROC General | 2026-03-11
ROC | March | SUSP - UV channel 1 common critical and high level alarm and UV system critical alarm. Checked site, UV flow recently started. Disregard as per the shift report. Alarms cleared on acknowledgement. | All Wastewater System ROC General | 2026-03-02
ROC | March | BLSS - Marcus R testing generator | All Wastewater System ROC General | 2026-03-11
ROC | March | KSSP - RAS combined no flow alarm. Checked site, all RAS pumps are manual/off and the WAS pumps are running, indicating that operators are wasting. | All Wastewater System ROC General | 2026-03-02
ROC | March | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-03-02
ROC | March | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-03-03
ROC | March | AUSS - Chris R on site to complete a generator test run and the JHSC checks. Chris R stated that maintenance is on site to complete work related to pump 1 and 4 and that these alarms can be disregarded as both pumps are OOS. 09:34 - AUSS - Chris R will not be running the generator. | All Wastewater System ROC General | 2026-03-04
ROC | March | Ethan U signing in | All Wastewater System ROC General | 2026-03-11
ROC | March | Adeela Khan signing in. Weather: 0C and Sunny | All Wastewater System ROC General | 2026-03-04
ROC | March | SUSP - UV System Critical Failure Alarm, UV Ch.1 High Level and Common Critical alarms came in. Alarms value went normal right away. Checked site. Plant recently started up. Disregard as per shift report | All Wastewater System ROC General | 2026-03-04
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-05
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-02
ROC | March | Angelica Chepiga signing in,weather +5C | All Wastewater System ROC General | 2026-03-11
ROC | March | Christian Van Beek signing in. Weather: -3C and clear. | All Wastewater System ROC General | 2026-03-12
ROC | March | YDSS + YNSS Normal Connor Smith signing out | All Wastewater System ROC General | 2026-03-11
ROC | March | SUSSWB - Ventilation H2S OOR alarm. As per shift report disregard alarm after hours. Will notify OP in the morning. 07:20 Value back to normal. Alarm cleared. | All Wastewater System ROC General | 2026-03-09
ROC | March | NBSP - Influent flow hihi and inlet channel high float alarm. Checked site, the Nobleton pumping station currently has two pumps active which is resulting in high influent flows at NBSP. Will monitor situation. | All Wastewater System ROC General | 2026-03-09
ROC | March | Bayview Steels OCF - Phil R on site to complete maintenance on the mist eliminator filters. Phil will be stopping the fans to complete the work. Will see associated alarm. | All Wastewater System ROC General | 2026-03-09
ROC | March | KSSSQW - Chris C on site to complete work orders including a dry well flood alarm test, hi/low temperature alarm test and a dialer alarm test. | All Wastewater System ROC General | 2026-03-09
ROC | March | KSSSQW - Chris C heading offsite and will return later. Kevin K is remotely monitoring and has placed three pumps in manual mode to increase the wet well level to increase head pressure to try clear the clogged pumps. | All Wastewater System ROC General | 2026-03-09
ROC | March | JDSS - Chris C. finished on site | All Wastewater System ROC General | 2026-03-04
ROC | March | Ethan U signing in | All Wastewater System ROC General | 2026-03-06
ROC | March | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-03-03
ROC | March | Christian Van Beek signing in. | All Wastewater System ROC General | 2026-03-03
ROC | March | SHSP - Gavin W on site to complete work on the RAS/WAS pumps. May see associated alarms. | All Wastewater System ROC General | 2026-03-12
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-12
ROC | March | Ethan Ullalkar signing out. | All Wastewater System ROC General | 2026-03-06
ROC | March | SUSP - UV Ch. 2 Bank 2A Lamp fail alarm came in. Disregarded as per shift report YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-09
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-09
ROC | March | KSSP - Generator local mode alarm and Generator fault alarm. Called Niel O who stated that contractors and Brent St C are on site working on the generator. While monitoring SCADA the generator returned to auto mode. 13:39 - KSSP - Brent St C called to inform he was working on the generator, swapping batteries with the contractor. | All Wastewater System ROC General | 2026-03-10
ROC | March | HLSSBS- Forcemain pressure hi alarm came in able to reset alarm as trends recovered | All Wastewater System ROC General | 2026-03-07
ROC | March | NMSSBP - Wet Well 1 and 2 Overflow alarms came in. Placed pumps back to auto and levels went down and alarm cleared. 18:44 - Due to higher levels at AUSS, placed pumps 2-4 at NMSSBP back to man/off. Will continue to monitor | All Wastewater System ROC General | 2026-03-08
ROC | March | SHSP - Lance J on site to test three high level float alarms. NBSP - Marcus R on site to complete maintenance of the head works machines including bar screens, and vortex systems. | All Wastewater System ROC General | 2026-03-10
ROC | March | Ethan U signing in | All Wastewater System ROC General | 2026-03-05
ROC | March | KSSP - Chase J testing headworks alarm | All Wastewater System ROC General | 2026-03-12
ROC | March | SUSP - UV Ch.1 Bank 1A intensity fault. Intensity reading 47.91 and bank 1B UV running as well with strong intensity reading | All Wastewater System ROC General | 2026-03-12
ROC | March | SEOC4- Shaft 4 O2 Mon 2 LoLo Alarm. Disregard as per SCADA Report | All Wastewater System ROC General | 2026-03-01
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-04
ROC | March | NBSP - Vortex #1 Water Scour uncommanded close alarm came in. Ack/reset as per shift report | All Wastewater System ROC General | 2026-03-04
ROC | March | SHSP- Power loss on site. Diesel generator running and aeration blower 2 fan overload still running. Notified Dan H. directed to rotate Fan 2 out of D1. Rotated duty but fan would not switch to D5 (OOS). Placed Blower 2 in man/off. All other fans are available if called upon #consult | All Wastewater System ROC General | 2026-03-07
ROC | March | Connor Smith signing in -1C windy | All Wastewater System ROC General | 2026-03-12
ROC | March | Ethan Ullalkar signing out. | All Wastewater System ROC General | 2026-03-12
ROC | March | BLSS - Marcus R and Lauren S on site to complete work on the barscreen system and test the high wet well level alarm. | All Wastewater System ROC General | 2026-03-09
ROC | March | KSSSQW - Wet well Hi alarms, Pump 3 efficiency low, wire to water alarms. Pump running on duty 2 with O flow, Rotated Duty, assigned Pump 2 to Duty 2 and placed P3 man/off. Notified | All Wastewater System ROC General | 2026-03-09
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-13
ROC | March | JDSS - Kevin K finished work and leaving site. | All Wastewater System ROC General | 2026-03-12
ROC | March | Christian Van Beek signing out. | All Wastewater System ROC General | 2026-03-10
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-02
ROC | March | Adeela Khan signing out | All Wastewater System ROC General | 2026-03-10
ROC | March | Christian Van Beek signing out. | All Wastewater System ROC General | 2026-03-09
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-06
ROC | March | SUSP- Bar Screen Hi Level Alarm. Alarm cleared | All Wastewater System ROC General | 2026-03-05
ROC | March | GRSSWA- Wetwell 1 Ultrasonic lolo. Not the controlling LIT. Check trends looks like it has dropped out in the past. Will monitor and reset if recovers or email North west wastewater team about outstanding issue | All Wastewater System ROC General | 2026-03-07
ROC | March | SUSP- Influent hihi alarm came in as both SUSSHS and SUSSWB were pumping to headworks. Trends recovered and alarm cleared | All Wastewater System ROC General | 2026-03-07
ROC | March | KSSP- Sodium bisulphate containment spill alarm came in. Notified Mike B. Will check SCADA MTSP- Both UV banks running 1a turning on and off. No alarm associated with issue. Notified Terry R to inquire if this was expected. Terry R. it was caused by both high flows and clarifier 1 draining. Will look on SCADA 12:18- KSSP- Mike B. Directed to disregard sodium bisulphate spill alarm #consult | All Wastewater System ROC General | 2026-03-07
ROC | March | QVSSSC, Diesel Containment Flood Alarm, notified Darren B, directed to disregard at this time, he will be heading to site sometime today | All Wastewater System ROC General | 2026-03-05
ROC | March | SEOC - OCF Fan Room 1 O2 Low alarm. Disregard as per shift report. | All Wastewater System ROC General | 2026-03-08
ROC | March | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-03-08
ROC | March | Adeela Khan signing in. Weather: 10C and sunny | All Wastewater System ROC General | 2026-03-08
ROC | March | HMSS - Lauren S on site to complete work orders including a generator test and a high level forcemain chamber alarm test. SUSP - UV system critical failure, UV channel 1 level high and UV channel 1 common critical alarm. Checked site, trending shows that UV channel flow recently started. Shift report states that these alarms will trigger when the plant activates and flow begins. All alarm statuses changed to "Normal". Alarms cleared on acknowledgement. RHAMF - Eric S from NAC on site to reset system alarms from last night. Cleared alarms, Eric assured that the system is now operating correctly. | All Wastewater System ROC General | 2026-03-02
ROC | March | YDSS + YNSS Normal MTSP - Final Effluent LoLo alarm came in. Disregarded as per shift report | All Wastewater System ROC General | 2026-03-02
ROC | March | MAPSN1 SCADA Server Reset, Kingsley M called, will be resetting the server at 09:30 | All Wastewater System ROC General | 2026-03-05
ROC | March | YDSS + YNSS Normal Connor Smith signing out | All Wastewater System ROC General | 2026-03-02
ROC | March | EGSSSC - Darren B onsite running generator and health and safety alarms | All Wastewater System ROC General | 2026-03-03
ROC | March | MTSP - Clarifier 1 no RAS pump running. Will be off for the weekend and drained Monday | All Wastewater System ROC General | 2026-03-06
ROC | March | KSSP - Niel O called to inform that they will be completing work on the UV system. Niel directed to disregard all UV associated alarms until the work is complete. | All Wastewater System ROC General | 2026-03-03
ROC | March | AUSSYS - Chris R on site to complete a generator test. Will see associated alarms. | All Wastewater System ROC General | 2026-03-02
ROC | March | QVSSC - Darren B leaving site. | All Wastewater System ROC General | 2026-03-04
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-01
ROC | March | Connor Smith signing in -16C Clear | All Wastewater System ROC General | 2026-03-02
ROC | March | KSSP- Sludge Holding Blwr 1 Hi Dif Press Alarm. Both blowers are OOS. Notified Cam B. He will look into it. | All Wastewater System ROC General | 2026-03-02
ROC | March | SEOC- OCF Fan1, Fan2 Uncommand Stop. Notified Phil R. He will look into it. | All Wastewater System ROC General | 2026-03-02
ROC | March | SEOC4- Shaft 4 Gas High Facility Shutdown Alarm. Disregard as per SCADA Report. | All Wastewater System ROC General | 2026-03-01
ROC | March | KSSSQW - Pump 2 Efficiency lolo, Wire-to-water Lowlow, flow lolo alarms. Notified Chris C, Assigned Pump 1 to duty 2 and placed Pump 3 back to auto. Pump 1 and 4 running normal. Chris C on his way to site. | All Wastewater System ROC General | 2026-03-09
ROC | March | KSSP - UV channel 2 Bank 2 A lamp fail and adjacent lamp fail alarms. Checked site, UV channel 2 is active. These alarms are disregards on the shift report. | All Wastewater System ROC General | 2026-03-09
ROC | March | HLSSBS - Hydrogen Sulphide Sample 1 fault alarm- disregard after hours as per shift report. | All Wastewater System ROC General | 2026-03-10
ROC | March | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-03-10
ROC | March | KSSP - UV CH1 Bank 1A Low UV intensity Fault alarm. Notified Mike B, he will check SCADA. # Consult 21:34 Mike B called, requested disregard alarm for the night. | All Wastewater System ROC General | 2026-03-10
ROC | March | RHAMF - Unit 1 recirculation water flow, odour control system offline . Unit 2 recirculation pump pressure loss. Power blip in area, able to reset alarms and get fans and recirculation pumps back running. Generator remains active, will monitor 10:35 - generator off. No outstanding issue | All Wastewater System ROC General | 2026-03-03
ROC | March | PVSS - Aaron CM from PCS called to inform he will be completing a reboot of the cellular modem for this location. Aaron stated the work would be best completed with pumps off. Waited until the wet well was pumped down and then informed Aaron he can begin the reboot. | All Wastewater System ROC General | 2026-03-04
ROC | March | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-03-11
ROC | March | Christian Van Beek signing in. Weather: 10C and clear. | All Wastewater System ROC General | 2026-03-10
ROC | March | Connor Smith signing in | All Wastewater System ROC General | 2026-03-10
ROC | March | SUSP - UV channel 1 common critical alarm, UV channel 1 high level alarm and UV system critical failure alarm. Checked site, UV channel 2 is active. Trending shows that flow through the UV channel recently started. Shift report states these alarms trigger when flow starts through the UV channel and can be disregarded. Alarm status changed to normal, alarms cleared on acknowledgement. | All Wastewater System ROC General | 2026-03-10
ROC | March | AUSS- Placed Pump 6 to auto. | All Wastewater System ROC General | 2026-03-10
ROC | March | NMSSBP - Kevin S working on alarms for wet well, temp, & auto dialer test | All Wastewater System ROC General | 2026-03-05
ROC | March | YDSS+YNSS normal Adam Button signing out | All Wastewater System ROC General | 2026-03-07
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-06
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-10
ROC | March | SUSP - Eric S on site to complete replacement of the lagoon flow meter. | All Wastewater System ROC General | 2026-03-04
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-07
ROC | March | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-03-08
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-08
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-09
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-10
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-01
ROC | March | Christian Van Beek signing in. | All Wastewater System ROC General | 2026-03-02
ROC | March | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-03-10
ROC | March | GRSSWA - Chris C on site to complete work orders including a generator test, JHSC checks and a dry well flood alarm test. KBSP, NBSP, NBSSJA - Kingsley M completing a Hub 5 server restart. No impact to operations affected. | All Wastewater System ROC General | 2026-03-03
ROC | March | SUSP, Ian W resetting OIT on site, disregard historian heartbeat alarm from site | All Wastewater System ROC General | 2026-03-05
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-05
ROC | March | KSSSQW- Wet well 1 hydrostatic level hi alarm came in. Hi flows. D2 active Pumps keeping up will clear when level pumps down | All Wastewater System ROC General | 2026-03-07
ROC | March | KSSSQW- Channel grinder 2 failed to start alarm and overload alarm came in. was not able to reset alarms and restart grinder. Notified Mike B. will head to site. Created CMU5 W11714748 NMSSBP- Wet well 1/2 ultrasonic and hydrostatic hi, Discharge flow hi, P3 pillow block hi and P4 vibration hi alarms came in D3 active. Able to reset all alarms but discharge flow hi and P4 vibration hi alarm. Will continue to monito P4 vibration hi is a disregard on shift report LSSS- LSSS2 to LSSS4 comm fail able to reset trends okay on site #CMU5 | All Wastewater System ROC General | 2026-03-07
ROC | March | Adeela Khan signing out | All Wastewater System ROC General | 2026-03-04
ROC | March | SEOC shaft 9 - O2 Monitor lolo alarm. Disregard alarm as per the shift report. | All Wastewater System ROC General | 2026-03-06
ROC | March | SUSP- Dewatering Screw Fault Alarm. Notified Cam B. He will take a look. 01:10- Cam B called back. Can disregard for the night. | All Wastewater System ROC General | 2026-03-05
ROC | March | NBSP - Influent Flow HiHi alarm. Alarm cleared. | All Wastewater System ROC General | 2026-03-08
ROC | March | Angelica Chepiga signing out | All Wastewater System ROC General | 2026-03-08
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-05
ROC | March | KBSP - Soda Ash Conveyor E. Stop alarm came in. Called Lance J. who informed he is working on the conveyor and has hit the E. stop | All Wastewater System ROC General | 2026-03-04
ROC | March | LSSS, Philip R is on site, running the generator on site and will also be running pump 1 on site. Disregard alarms that come from pump 1 | All Wastewater System ROC General | 2026-03-04
ROC | March | NMSSBP - Kevin S. called to inform he will be completing the diesel generator test run | All Wastewater System ROC General | 2026-03-04
ROC | March | PVSS, Aaron M is finished working on the signal at site, Trends are normal | All Wastewater System ROC General | 2026-03-04
ROC | March | JDSS - Chris C on site to complete work orders including generator test run, JHSC checks, dry well flood alarm test, hi/low temperature alarm test and possibly hi/low wet well level alarms. Chris has requested that alarms be disregarded until his work is complete | All Wastewater System ROC General | 2026-03-04
ROC | March | MTSP - Clarifier 2 No RAS pump running alarm and Final Effluent Extended Hi Flow event alarm. Terry R working on site. He will clear alarms. # Consult. | All Wastewater System ROC General | 2026-03-08
ROC | March | YDSS + YNSS Normal Christian Van Beek signing out. | All Wastewater System ROC General | 2026-03-04
ROC | March | Adeela Khan signing out | All Wastewater System ROC General | 2026-03-02
ROC | March | Adam Button signing in 8C clear | All Wastewater System ROC General | 2026-03-07
ROC | March | NBSP, UV System Minor Fault Alarm, UV Bank 1A is running. When checking trends, Bank 1B occasionally turns on then off, this seems to be abnormal from Trending. When Dan H calls back at 20:30, RO will notify him of this observation | All Wastewater System ROC General | 2026-03-07
ROC | March | KSSSQW - Chris C has returned to site and will be trying to test the alarms stated previously, dry well flood, high/low temp and dialer test, | All Wastewater System ROC General | 2026-03-09
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-10
ROC | March | YDSS + YNSS normal | All Wastewater System ROC General | 2026-03-10
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-07
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-08
ROC | March | NBSP - Satnam M on site with Martin D to work on RAS valve 4. RAS pump 2 and RAS pump 3 may be OOS when the valve is worked on. Satnam informed that Young J will be on site soon. | All Wastewater System ROC General | 2026-03-09
ROC | March | AUSS - Pump1 leakage alarm. Checked site, duty rotated to pump 5 and operations are normal. Contacted Kevin S who is on site with maintenance to check the pump. | All Wastewater System ROC General | 2026-03-03
ROC | March | Angelica Chepiga signing in,weather -6C | All Wastewater System ROC General | 2026-03-02
ROC | March | BLSS - Lauren S on site to inspect the odour control unit. Lauren stated she will be triggering associated alarms. | All Wastewater System ROC General | 2026-03-03
ROC | March | NMSSHS- PAC Communication Failure Alarm. Notified Yash S. He will look into it. | All Wastewater System ROC General | 2026-03-02
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-02
ROC | March | KSSP - Channel Aeration Blower 2 High Differential Pressure alarm came in. Checked site. Aeration blower 1 is running in duty 1. Will send an email to North WW. YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-02
ROC | March | SUSP - UV System Critical Failure , Ch 1 High Level, Ch.2 Common critical alarms came in. Checked site. Plant recently activated. Disregard as per shift report. Cleared upon acknowledgement. | All Wastewater System ROC General | 2026-03-09
ROC | March | AUSS - Wet well high levels. Placed pumps 2, 5, 6 with a manual setpoint of 60% 04:00 - Placed all pump setpoints back to auto | All Wastewater System ROC General | 2026-03-09
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-05
ROC | March | Christian Van Beek signing out. | All Wastewater System ROC General | 2026-03-06
ROC | March | KSSP- Scum chamber 2 high level disregard on shift report SUSP- UV system critical failure/ CH 1+2 high level/ common critical alarms came in. Cleared upon acknowledgment alarms came in as flow was established to UV channel disregard on shift report | All Wastewater System ROC General | 2026-03-07
ROC | March | AUSSYS - Chris R on site and will be testing the emergency eye wash stations and showers. | All Wastewater System ROC General | 2026-03-02
ROC | March | SUSP - Tyson C running generator | All Wastewater System ROC General | 2026-03-05
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-15
ROC | March | GRSSWA- Wetwell 1/2 hihi switch alarm came in. Critical alarm all pumps running at 100 percent. Notified Mike B. Directed to continue to monitor and notify if overflow limit is reached. #consult | All Wastewater System ROC General | 2026-03-07
ROC | March | HLSSBS- Force main 1 pressure hi. Reset alarm as trends recovered | All Wastewater System ROC General | 2026-03-07
ROC | March | HLSSBS - Channel Grinder E stop alarm/ critical alarm. Notified Tyson C, directed disregard alarm until morning. # Consult | All Wastewater System ROC General | 2026-03-12
ROC | March | KBSP- Sludge Blower 1 motor Temp Hi alarm/ start failed alarm- duty rotated to Sludge Blower 2. Will notify area. | All Wastewater System ROC General | 2026-03-12
ROC | March | HLSSBS - Inlet channel level high switch alarm. Critical level alarm. Checked site, trending shows that the inlet channel level is continually rising, Inlet channel grinder is faulted from earlier in the night. Called Tyson C who directed to disregard the alarm. #consult | All Wastewater System ROC General | 2026-03-12
ROC | March | HLSSBS - Inlet channel switch hihi alarm. Tyson C was contacted earlier and stated to disregard this alarm as well as the inlet channel overflows into the wetwell. | All Wastewater System ROC General | 2026-03-12
ROC | March | MTSP - Clarifier 1 No RAS pump running alarm. Disregard as per SCADA reiview. | All Wastewater System ROC General | 2026-03-15
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-16
ROC | March | KSSP - Niel O on site with Chase J to work on the UV system. | All Wastewater System ROC General | 2026-03-13
ROC | March | SUSP - UV channel 2 Bank 2A major alarm, UV system major fault and UV channel 2 common major alarm. Checked site, UV channel 2 Bank 2A has been placed in local/off mode by operations. UV channel 1 active. | All Wastewater System ROC General | 2026-03-13
ROC | March | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-03-15
ROC | March | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-03-15
ROC | March | KSSSQW - Wet well Hi and HiHi alarms, Pump 2 wire-to-water /efficiency lo and low/low alarms, Pump 2 Low flow alarm - Rotated Pump 1 to duty 2, Pump 3 to duty3. All alarms cleared. Will monitor Pump 2 next cycle. | All Wastewater System ROC General | 2026-03-15
ROC | March | SEOC OCF outlet fan O2 hihi alarm - Fans are running. Trend spiked and back to normal range. Disregard as per shift report. Cleared alarm. | All Wastewater System ROC General | 2026-03-15
ROC | March | NBSP- Marcus R onsite. Should not trigger any alarms however maintenance will be onsite later for work on RAS pumps. KBSP- Marcus R informed that will be leaving scum pumps man/off due to high flows. Can disregard HiHi Level alarm. | All Wastewater System ROC General | 2026-03-10
ROC | March | Connor Smith signing in 3 C Rain | All Wastewater System ROC General | 2026-03-11
ROC | March | YDSS+YNSS NORMAL Angelica Chepiga signing out | All Wastewater System ROC General | 2026-03-03
ROC | March | Connor Smith signing in 1C Cloudy | All Wastewater System ROC General | 2026-03-03
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-04
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-12
ROC | March | KSSSQW, Placed pump 1 in D1 and pump 4 in D2 Carter D Signing Out | All Wastewater System ROC General | 2026-03-08
ROC | March | NMSSBP - Wet well Hi and discharge flow Hi alarms. 3 pumps active. Alarms cleared in 5 minutes. | All Wastewater System ROC General | 2026-03-08
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-08
ROC | March | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-03-15
ROC | March | Angelica Chepiga signing out | All Wastewater System ROC General | 2026-03-15
ROC | March | NBSP - UV system minor fault alarm. Shift report states this alarm is a disregard as long as one UV bank is active. Checked site, UV bank 1B is active. Trending shows the UV duty recently swapped banks. | All Wastewater System ROC General | 2026-03-02
ROC | March | YDSS+YNSS Normal | All Wastewater System ROC General | 2026-03-07
ROC | March | NBSP - UV Minor fault alarm. Checked site, both UV banks active. Shift report states this alarm is a disregard. Cleared alarm. | All Wastewater System ROC General | 2026-03-12
ROC | March | NBW7 - Jacob M heading to site. Place well 7 man/on | All Wastewater System ROC General | 2026-03-06
ROC | March | LSSS - Phil R on site to complete a wet well level hi alarm test. | All Wastewater System ROC General | 2026-03-10
ROC | March | RHAMF1- Historian Heartbeat Alarm. Notified Kyle C. He will look into it. | All Wastewater System ROC General | 2026-03-10
ROC | March | RHAMF - Marcos T on site to complete testing. Marcos directed to disregard alarms. | All Wastewater System ROC General | 2026-03-10
ROC | March | SHSP - RAS Pump 2 Speed Deviation Alarm. Pump running 90% speed. Notified Dan H. He will investigate. | All Wastewater System ROC General | 2026-03-09
ROC | March | KBSP - Harie R. called to inform that he will be completing a headworks inspection on the bar screen and grit vortex | All Wastewater System ROC General | 2026-03-13
ROC | March | KSSP - Diesel containment flood alarm. Called Niel O who will check the diesel tanks. | All Wastewater System ROC General | 2026-03-10
ROC | March | SHSP- Marcus R on site to work on air compressors KBSP- Harie R on site to work on WAS pumps | All Wastewater System ROC General | 2026-03-06
ROC | March | SUSP - UV channel 1 common critical and High level alarms, UV system critical alarm. Checked site, UV 2 is running, UV flow recently started. Disregard as per the shift report. Alarms cleared on acknowledgement. | All Wastewater System ROC General | 2026-03-02
ROC | March | HLSSBS - Channel Grinder E stop alarm came in. Called Darren B. who informed he is headed to site. 11:48 - Darren called back and informed the maintenance team is on site | All Wastewater System ROC General | 2026-03-04
ROC | March | SEOC4 - Shaft 4 O2 Monitor hi and hihi alarm. Checked site, current value is actually reading lolo. Trending shows a spike of the O2 reading. Shift report states that these O2 Monitor alarms are all disregards. Cleared hi and hihi alarms. | All Wastewater System ROC General | 2026-03-04
ROC | March | SEOC 4 - Shaft 4 gas high facility shutdown alarm. Checked site, fan 1 is currently running in duty 1. Operations appear normal, shift report states that this alarm is a disregard after hours. | All Wastewater System ROC General | 2026-03-04
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-07
ROC | March | NMVCBP - Wet well 1 ultrasonic mode alarm. Pumps in local/off to prevent backup mode to start the pumps during high flow event. | All Wastewater System ROC General | 2026-03-12
ROC | March | AUSSYS - Generator 1 running status alar. Checked site, Generator ios running in local mode and ATS is pointed to town hydro. Facility logbook indicates that mechanical maintenance is on site to investigate a low oil situation. Terry C is logged into the facility logbook. | All Wastewater System ROC General | 2026-03-10
ROC | March | SEOC4 - Shaft 4 high facility shutdown. Disregard as per shift report | All Wastewater System ROC General | 2026-03-11
ROC | March | Ethan Ullalkar signing out. | All Wastewater System ROC General | 2026-03-11
ROC | March | Carter Dunn Signing In, -7D/Clear | All Wastewater System ROC General | 2026-03-13
ROC | March | SUSP - Bar screen Hi level alarm. Was able to clear alarm in a few minutes. | All Wastewater System ROC General | 2026-03-15
ROC | March | SUSP - Bar screen Hi level alarms in and out, Tyson C requested disregard alarm until tomorrow. # Consult | All Wastewater System ROC General | 2026-03-15
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-15
ROC | March | KCSSKR - Lauren S onsite for wet well cleaning | All Wastewater System ROC General | 2026-03-05
ROC | March | SEOC- OCF FAN Outlet O2 HIHi Alarm. Disregard as per SCADA Report. | All Wastewater System ROC General | 2026-03-12
ROC | March | SUSP- Filters Hi Level Alarm. Notified Tyson C. He will take a look CONSULT | All Wastewater System ROC General | 2026-03-13
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-13
ROC | March | Carter D Signing Out | All Wastewater System ROC General | 2026-03-04
ROC | March | BLSS - Screen 1 emergency stop, wet well 2 and wet well 1 Overflow level alarms - Marcus R called to confirm alarms. | All Wastewater System ROC General | 2026-03-09
ROC | March | KBSP - Gavin W onsite testing both generators | All Wastewater System ROC General | 2026-03-03
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-14
ROC | March | NBSP- Inlet Channel High Float. Alarm cleared. | All Wastewater System ROC General | 2026-03-11
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-14
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-14
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-15
ROC | March | KSSP - UV bank 1A low UV intensity fault. Still reading intensity with UV1 running | All Wastewater System ROC General | 2026-03-15
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-09
ROC | March | NBSP - Auto dialer inlet general alarm, inlet channel high float. flowmeter hi from NMBSSJA | All Wastewater System ROC General | 2026-03-11
ROC | March | Ethan Ullalkar signing out. | All Wastewater System ROC General | 2026-03-14
ROC | March | SUSP- Tyson C called and requested a call if basin levels hit 4.90. FIlters Hi Level Alarm came in while on phone. He will look into it. 22:54- Tyson C cleared alarm. Requested a call if it comes back in | All Wastewater System ROC General | 2026-03-12
ROC | March | LSSS- Surge Tank 1 Level High Alarm, Quick spike. Cleared alarm. | All Wastewater System ROC General | 2026-03-13
ROC | March | SUSP - Basin 1 high level, cleared upon Acknowledging alarm. Level within range | All Wastewater System ROC General | 2026-03-12
ROC | March | SUSP - UV channel 1 common critical/channel 1 high level alarms and UV system critical failure alarm. UV channel 2 is active, flow through the UV channel recently started. Disregard alarms as per shift report. Alarms cleared when acknowledged. | All Wastewater System ROC General | 2026-03-11
ROC | March | KSSP, UV Ch. 1 Bank 1A Low UV Intensity Fault, Not in shift report to disregard, contacted to Tyson C, directed to disregard for the day Consult | All Wastewater System ROC General | 2026-03-14
ROC | March | NBSP, UV System Minor Fault, As per shift report, directed to disregard as 1 bank is currently tunning | All Wastewater System ROC General | 2026-03-14
ROC | March | Ethan U signing in Weather 0. | All Wastewater System ROC General | 2026-03-14
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-14
ROC | March | NMVCBP - Dan K informed they shut the pumps and left in manual off to slow down flow to NMSSBP, disregard hi level alarms | All Wastewater System ROC General | 2026-03-11
ROC | March | Carter Dunn Signing in, 3D/Clear | All Wastewater System ROC General | 2026-03-15
ROC | March | SEOC OCF outlet fan O2 hihi alarm. Checked site, fans are running. trending shows a spike of the oxygen sensor reading which quickly returned to normal range. These alarms are a disregard on the shift report. cleared alarm. | All Wastewater System ROC General | 2026-03-12
ROC | March | SEOC4 - Shaft 4 gas facility shutdown. Disregard as per shift report | All Wastewater System ROC General | 2026-03-14
ROC | March | YDSS + YNSS Normal Carter Dunn Signing Out | All Wastewater System ROC General | 2026-03-14
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-15
ROC | March | Carter Dunn Signing Out | All Wastewater System ROC General | 2026-03-26
ROC | March | Angelica Chepiga signing in | All Wastewater System ROC General | 2026-03-26
ROC | March | SUSP - UV channel 1 Bank 1B ballast fail alarm along with UV major alarms. Called Tyson C who is on site and will check the system. | All Wastewater System ROC General | 2026-03-18
ROC | March | NMETHW - Kalid from AIM on site with contractors. | All Wastewater System ROC General | 2026-03-16
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-16
ROC | March | RHAMF- Jim from NAC onsite to inform of shutting down recirculation pumps 1 and 2. He has confirmed with Daniel K. | All Wastewater System ROC General | 2026-03-16
ROC | March | SECC - Sump 1 level low switch alarm. Checked site, sump pump 1 interlocked on the alarm. trending shows an abnormal dip of the sump 1 pit level. Able to clear alarm, will monitor site. | All Wastewater System ROC General | 2026-03-20
ROC | March | AUSS - Phil R running generator, Alectra on site replacing Hydro meter. | All Wastewater System ROC General | 2026-03-18
ROC | March | Connor Smith signing in | All Wastewater System ROC General | 2026-03-24
ROC | March | NMVCBP- Kevin S on site to complete wet well related work orders. Kevin directed to disregard alarms. | All Wastewater System ROC General | 2026-03-18
ROC | March | SEOC- Shaft 6/7 PAC Communication Fail YDOC- PAC Communication Failure Alarm SECC- Shaft 13 to Shaft 6 Comms Failure YDBR- Communication Failure Alarm Notified Chris S. He will look into it. 09:12- Aaron CM called. All alarms have cleared. | All Wastewater System ROC General | 2026-03-20
ROC | March | KBSP- Harie R testing reject hihi alarm. | All Wastewater System ROC General | 2026-03-24
ROC | March | Angelica Chepiga signing in, weather +4C | All Wastewater System ROC General | 2026-03-19
ROC | March | SUSSWB- Ventilation H2S OOR Alarm. Disregard as per SCADA Report. | All Wastewater System ROC General | 2026-03-25
ROC | March | SUSP - UV channel 1 common critical/channel 1 high level alarms and UV system critical failure alarm. UV channel 1B is active, flow through the UV channel recently started. Disregard alarms as per shift report. Alarms cleared when acknowledged. | All Wastewater System ROC General | 2026-03-24
ROC | March | SHSP - Vortex blower 1 and 2 general alarm. Checked site, both vortex blowers are in local/off mode. Called Gavin W who is working on them | All Wastewater System ROC General | 2026-03-27
ROC | March | MTSP - Alum pump containment flood alarm. Notified Phil R, he will check SCADA. # Consult | All Wastewater System ROC General | 2026-03-26
ROC | March | NBSP- UV System Minor Fault, UV Bank 1B is running. Disregard alarm as per shift report. | All Wastewater System ROC General | 2026-03-16
ROC | March | SUSP- UV System Critical/High Level Alarms. Alarms cleared. Known issue on SCADA Report. | All Wastewater System ROC General | 2026-03-16
ROC | March | MTSP - Terry R. called to inform that they have a VAC truck on site and will be pumping down the chamber. Terry informed he will have the RAS pumps off and everything is diverting to lagoons | All Wastewater System ROC General | 2026-03-23
ROC | March | YDSS + YNSS Normal Connor Smith signing out | All Wastewater System ROC General | 2026-03-26
ROC | March | SUSP- UV System Critical Failure, High Level Alarm. Alarms cleared after acknowledging. Known issue on SCADA Report. | All Wastewater System ROC General | 2026-03-24
ROC | March | SEOC - Evgeny S restarting OIT, disregard Historian heartbeat alarm. | All Wastewater System ROC General | 2026-03-27
ROC | March | SUSP- UV System Major Fault, UV Ch. 1 Bank 1B Major Alarm. UV is Local off. Tyson C informed Mike B working on it. | All Wastewater System ROC General | 2026-03-20
ROC | March | Christian Van Beek signing in. Weather: 3C and clear. | All Wastewater System ROC General | 2026-03-21
ROC | March | HLSSBS - Site Hydro Power Failure alarm came in along with Channel Grinder E stop, Generator running status, and Sewage pump 2 VFD fault. Checked site. After 10 mins, site is still connected to generator power and Sewage pump 2 VFD fault is outstanding. No outage reported on outage map. 07:27 - Outage has been reported on the outage map and is under investigation. ETA is 09:45. Informed Darren B 09:53 - Site is back to hydro power. KSSSQW - Channel Grinder 1 and 2 overload alarms came in. Unable to clear. Duty is active. Called Darren B. who will attend site. CMU5 created W11750026 #CONSULT #CMU5 | All Wastewater System ROC General | 2026-03-22
ROC | March | MTSP - Grit System 1 and 2 fault and failed to start alarms came in along with Dewatering Screw fault. Checked site. Called Marcos T. who informed he is on site and just cleaned the Mechanical Bar Screen. Marcos will look into these alarms 10:16 - Marcos called back to inform that he has cleared the alarms #CONSULT | All Wastewater System ROC General | 2026-03-22
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-22
ROC | March | SUSSWB- Brent S onsite for generator maintenance. | All Wastewater System ROC General | 2026-03-16
ROC | March | HMSS, Bar Screen 2 Fault, notified Marcus R, he is heading to site 21:32, Marcus R is requesting a second operator as he has to enter the wet well for some valving, Contacted Tyson C, he will give Marcus R a call 21:37, Tyson C is heading to site 22:30, Operators have left site CMU5: W11737262 (Marcus) CMU5: W11737271 (Tyson) | All Wastewater System ROC General | 2026-03-16
ROC | March | NBSP- Mech. Bar Screen General Alarm, Mech Bar Screen Out of Service Alarm. Unable to clear alarms. Emailed West Ops. | All Wastewater System ROC General | 2026-03-19
ROC | March | NBSP - Mech Bar screen out of service/general alarms. Will monitor Inlet channel levels and notify OP first thing in the morning. 05:30 Lance J requested to start Bar screen continuous override. Not able to reset alarm. Lance J requested disregard for now. # Consult | All Wastewater System ROC General | 2026-03-20
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-22
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-24
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-25
ROC | March | KCSSKR, Sean P on site, doing a generator load test | All Wastewater System ROC General | 2026-03-23
ROC | March | Carter Dunn Signing Out | All Wastewater System ROC General | 2026-03-16
ROC | March | MTSP - UV system Major fault alarm. Checked site, UV bank 1 A is active and trending indicates normal operations. UV bank 1B is the bank with the alarm and is in local/off mode. | All Wastewater System ROC General | 2026-03-18
ROC | March | Carter Dunn Signing In, 0D/Clear | All Wastewater System ROC General | 2026-03-23
ROC | March | SHSSDK- Gavin W onsite for wet well cleaning with contractor. Disregard low level alarms. | All Wastewater System ROC General | 2026-03-17
ROC | March | AUSS - Martin D on site to complete pump inspections and testing. Martin has requested that pump alarms be disregarded from this site until the work is complete. | All Wastewater System ROC General | 2026-03-25
ROC | March | LSSS - Noted that LSSS pump 1 is in auto and has faulted on a bearing high temperature alarm. Shift report states this pump should be manual/off and OOS status. Called Phil R to confirm. Placed pump 1 manual/off and OOS status for the weekend. | All Wastewater System ROC General | 2026-03-27
ROC | March | Angelica Chepiga signing out | All Wastewater System ROC General | 2026-03-27
ROC | March | Ethan Ullalkar signing out. | All Wastewater System ROC General | 2026-03-24
ROC | March | Connor Smith signing in 9C Cloudy | All Wastewater System ROC General | 2026-03-16
ROC | March | YDSS + YNSS Normal Connor Smith signing out | All Wastewater System ROC General | 2026-03-16
ROC | March | Angelica Chepiga signing out | All Wastewater System ROC General | 2026-03-16
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-17
ROC | March | KBSP - David D on site with Total Power to complete a generator load bank test. No transfer of station power. | All Wastewater System ROC General | 2026-03-18
ROC | March | KBSP- Gen2 REM MODE DI-STS. Lance J. called and requested to disregard as contractors are working on generator. | All Wastewater System ROC General | 2026-03-19
ROC | March | KSSP - Sludge Holding Tank 2 OOR and Fault alarms came in. Disregarded as per shift report | All Wastewater System ROC General | 2026-03-17
ROC | March | NBSP -Young J working on RAS/WAS pumps | All Wastewater System ROC General | 2026-03-18
ROC | March | NMSSBP- Kevin S testing High wet well level alarm. | All Wastewater System ROC General | 2026-03-26
ROC | March | SUSP - UV Ch.1 Common Critical alarm, High level and UV System Critical alarms came in. All alarms cleared on acknowledgement. Shift report informs that this occurs during plant start up | All Wastewater System ROC General | 2026-03-17
ROC | March | AUSS - Marcos T and Chris R on site for generator 3 testing. Test will be off load. | All Wastewater System ROC General | 2026-03-19
ROC | March | KSSP - Arthur L finished and leaving site. | All Wastewater System ROC General | 2026-03-27
ROC | March | Christian Van Beek signing in. Weather: 2C and clear. | All Wastewater System ROC General | 2026-03-20
ROC | March | YDSS + YNSS normal | All Wastewater System ROC General | 2026-03-26
ROC | March | YDSS + YNSS Normal SUSSHS - Sewage Pump 1 No Flow and VFD Fault alarms came in. Unable to clear. Called Chris C. who is heading to site. CMU5 Created W11762134 01:42 - Chris C. called back to inform that he is finished on site and informed that he left sewage pump 1 in auto but manual setpoint at 20% #CONSULT #CMU5 | All Wastewater System ROC General | 2026-03-27
ROC | March | Carter Dunn Signing In, 3D/Clear | All Wastewater System ROC General | 2026-03-16
ROC | March | NMSSBP- Mech Screen 2 Overtorque Alarm. Notified Kevin S. He will look into it. 13:59- Terry R called. Maintenance is onsite working on bar screen. | All Wastewater System ROC General | 2026-03-19
ROC | March | RHAMF - Jun Jie from NAC is on site and completing a generator test. | All Wastewater System ROC General | 2026-03-25
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-21
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-22
ROC | March | Ethan U signing in Weather 2c | All Wastewater System ROC General | 2026-03-21
ROC | March | SUSP - UV System Critical failure alarm came in. Checked site. Alarms were triggered by plant startup. Alarms cleared upon acknowledgement. Disregarded as per shift report | All Wastewater System ROC General | 2026-03-22
ROC | March | SHSP- Marcus R onsite working on aeration, sludge and vortex blowers. | All Wastewater System ROC General | 2026-03-17
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-23
ROC | March | MTSP - UV major alarm still outstanding. Called Marcos T who stated that electricians are on site to complete work on the UV system and flow has been diverted to lagoon since before their work started. | All Wastewater System ROC General | 2026-03-18
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-23
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-24
ROC | March | RHAMF - Jun jie from NAC on site and has requested that all fans and pumps be placed into auto mode and the alarms cleared. Made the necessary changes. | All Wastewater System ROC General | 2026-03-25
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-25
ROC | March | YDSS + YNSS normal | All Wastewater System ROC General | 2026-03-22
ROC | March | SEOC4- Bill VB Requested to rotate fan duty so that fan 2 is in duty 1. | All Wastewater System ROC General | 2026-03-25
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-25
ROC | March | Adeela Khan signing in. Weather: 0C and cloudy | All Wastewater System ROC General | 2026-03-22
ROC | March | KSSP - ZW2 shutdown due to not all devices in auto. Appears train 2 VFD pump is shown local off. 4 Trains remain in service. Email sent to area. | All Wastewater System ROC General | 2026-03-23
ROC | March | Carter D Signing In, 4D/Clear | All Wastewater System ROC General | 2026-03-25
ROC | March | SEOC OCF - Parth P and Rick L heading to site to replace O2 sensor. | All Wastewater System ROC General | 2026-03-24
ROC | March | RHAMF - Jun Jie from NAC on site to complete vibration testing. Jun Jie requested that the recirculation pump duties be changed so the vibration readings can be taken. Made necessary adjustments. | All Wastewater System ROC General | 2026-03-25
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-24
ROC | March | SEOC Shaft 9 0 O2 Monitor Hi, HiHi and OOR alarm. Alarms are a disregard on the shift report. Alarms cleared on reset. | All Wastewater System ROC General | 2026-03-20
ROC | March | SHSP - Gavin W on site to complete work on RAS pumps. Gavin will be placing RAS pumps in local mode for inspection and maintenance. Gavin requested the associated alarms be disregarded. | All Wastewater System ROC General | 2026-03-25
ROC | March | NBSSJA- Pump1 VFD Fault Alarm. Pump 3 running in auto. Notified Marcus R | All Wastewater System ROC General | 2026-03-16
ROC | March | AUSS - Kyle B on site to replace a UPS battery. | All Wastewater System ROC General | 2026-03-18
ROC | March | Connor Smith signing in 3C Clear | All Wastewater System ROC General | 2026-03-26
ROC | March | KSSP- Theodore from AB onsite doing some welding. Requested a call if any smoke alarms come in. Phone-289-839-0704 | All Wastewater System ROC General | 2026-03-17
ROC | March | AUSS- Generator 1,2,3 Not in Auto Alarms. Alarms cleared on their own. | All Wastewater System ROC General | 2026-03-25
ROC | March | KSSP- Neil O onsite working on membranes. Disregard low levels. | All Wastewater System ROC General | 2026-03-17
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-16
ROC | March | SHSP - Aeration blower 1 uncommanded stop and start alarm. Called Gavin W who stated he is working on the blower. | All Wastewater System ROC General | 2026-03-18
ROC | March | LSSS - Phil R working on Surge tanks, directed disregard Hi/low level alarms. | All Wastewater System ROC General | 2026-03-16
ROC | March | Angelica Chepiga signing out | All Wastewater System ROC General | 2026-03-20
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-25
ROC | March | Carter D Signing Out | All Wastewater System ROC General | 2026-03-25
ROC | March | NMEQBP - Potable water flow HiHi and fault alarms. Called Kevin S who is on site and triggered the alarms. Able to reset once the flow returned to normal range. | All Wastewater System ROC General | 2026-03-27
ROC | March | SUSSHS - Terry C on site to complete vibration testing. Terry requested that pump 1 be placed into duty 1. | All Wastewater System ROC General | 2026-03-18
ROC | March | Angelica Chepiga signing in | All Wastewater System ROC General | 2026-03-27
ROC | March | KBSP- David D from maintenance onsite for work on generator 2. | All Wastewater System ROC General | 2026-03-17
ROC | March | KBSP- UV. Ch. 1 Common Major Alarm. Notified Lance J. He was testing onsite and cleared alarm. | All Wastewater System ROC General | 2026-03-17
ROC | March | AUSS, Chris R on site, placed the east force main in isolation | All Wastewater System ROC General | 2026-03-23
ROC | March | NMSSHS- Kevin S onsite for work orders | All Wastewater System ROC General | 2026-03-16
ROC | March | SUSP- UV Critical Alarm/High Level Alarm. Alarms cleared after acknowledging | All Wastewater System ROC General | 2026-03-16
ROC | March | KSSP - Garric from Ferguson electric turning off power to generators. Replacing batteries. | All Wastewater System ROC General | 2026-03-16
ROC | March | YDSS + YNSS Normal Connor Smith signing out | All Wastewater System ROC General | 2026-03-17
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-17
ROC | March | Gluzen Ramos Ong signing out | All Wastewater System ROC General | 2026-03-19
ROC | March | SHSP - RAS Pump 2 Speed Deviation Alarm, alarm cleared right away. | All Wastewater System ROC General | 2026-03-20
ROC | March | AUSSYS - Historian Heartbeat alarm, cleared when acknowledged . | All Wastewater System ROC General | 2026-03-17
ROC | March | HMSS - Lauren S and Marcus R performing drywell and wet well inspections, requested disregard Drywell flood and HiHi alarms. Marcus R testing Hi/Low temp alarm. Confirmed Drywell flood alarm. | All Wastewater System ROC General | 2026-03-18
ROC | March | SHSP- Aeration Blower 1 Speed Sig Error/High Temperature. Blower is Local off and Marcus R onsite. | All Wastewater System ROC General | 2026-03-24
ROC | March | PVSS - Marcus R. called to inform that he and Lauren S. are on site and will be working on the wet wells. Marcus informed that all LIT and wet well alarms can be disregarded | All Wastewater System ROC General | 2026-03-23
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-24
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-21
ROC | March | QVSSSC - Site hydro power fail, Sewage Pumps 1 and 2 failure, and generator running status alarm came in. Checked site. Site is not connected to generator power but generator is running. Likely a power blip. All alarms have cleared. | All Wastewater System ROC General | 2026-03-22
ROC | March | MTSP - Aeration tank 2 DO low alarm - Notified Barry M. He is on site/will check. | All Wastewater System ROC General | 2026-03-24
ROC | March | HLSSBS- Ric L onsite troubleshooting wetwell overflow FIT 14:47- Ric L finished onsite. | All Wastewater System ROC General | 2026-03-24
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-24
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-24
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-21
ROC | March | NBSP - Vortex 2 air scour uncomamnded close alarm. Disregard in the shift report if it can be reset. Able to reset alarm. | All Wastewater System ROC General | 2026-03-21
ROC | March | SUSP - UV channel 1 common critical alarm, UV channel 1 high level alarm and UV system critical failure alarm. Checked site, UV channel 1 is active. Trending shows flow through the UV system just started. Shift report states these alarms trigger when the UV flow starts. Disregard and clear alarms. | All Wastewater System ROC General | 2026-03-21
ROC | March | MTSP, UV System Major Fault, 2 UV systems are running, Bank 1B OOS, Notified Kevin S, directed to disregard for the night consult | All Wastewater System ROC General | 2026-03-16
ROC | March | YDSS + YNSS Normal SUSP - Bar Screen Hi alarm came in. Disregarded as per shift report | All Wastewater System ROC General | 2026-03-18
ROC | March | YDSS + YNSS Normal Christian Van Beek signing out. | All Wastewater System ROC General | 2026-03-21
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-21
ROC | March | NBSP - UV System Minor Fault alarm came in. Disregarded as per shift report as there is one bank running | All Wastewater System ROC General | 2026-03-22
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-18
ROC | March | YDOC - Pump 2 failed to start and pump 2 inlet valve failed to open alarm. Checked site, pump 2 is currently manual/off. Pump 1 is active in auto mode. Will monitor site to determine if operations is making changes. 09:23 - YDOC - Called Terry R who is on the way to site and will check operations. | All Wastewater System ROC General | 2026-03-18
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-17
ROC | March | wrong book | All Wastewater System ROC General | 2026-03-16
ROC | March | Christian Van Beek signing in. | All Wastewater System ROC General | 2026-03-18
ROC | March | KSSP - Scum Chamber 2 High Level Alarm came in. Disregarded as per shift report | All Wastewater System ROC General | 2026-03-22
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-25
ROC | March | YDSS+YNSS NORMAL Angelica Chepiga signing out | All Wastewater System ROC General | 2026-03-17
ROC | March | YDSS + YNSS Normal Connor Smith signing out | All Wastewater System ROC General | 2026-03-24
ROC | March | BLSS - David D finished on site. | All Wastewater System ROC General | 2026-03-26
ROC | March | Gluzen Ramos Ong signing out | All Wastewater System ROC General | 2026-03-27
ROC | March | MTSS, Barry M called, Site back to normal operation | All Wastewater System ROC General | 2026-03-23
ROC | March | Adeela Khan signing in. Weather: -7C and Cloudy | All Wastewater System ROC General | 2026-03-17
ROC | March | YDSS + YNSS Normal Adeela Khan signing out | All Wastewater System ROC General | 2026-03-23
ROC | March | Carter Dunn Signing Out | All Wastewater System ROC General | 2026-03-23
ROC | March | NMEQBP - Kingsley M restarting OIT. Disregard Historian Heartbeat alarm. 12:05 Kingsley M completed work. | All Wastewater System ROC General | 2026-03-26
ROC | March | NMSSBP- Mech Screen 1 Fault Alarm. Notified Kevin S. He will look into it. | All Wastewater System ROC General | 2026-03-24
ROC | March | KBSP - Aaron CM working on the KBSP APN network configuration. | All Wastewater System ROC General | 2026-03-18
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-18
ROC | March | AUSS - Marcos T called to inform that Generator 3 will remain out of service for the night. Generator 1 and 2 are available to run if a power failure occurs. Generator 1 and 2 can sustain a maximum of four pumps. SCADA will limit the number of pumps available to four in the event of a power failure. | All Wastewater System ROC General | 2026-03-19
ROC | March | BLSS - David D troubleshooting Pump 2. Requested assign Pump 2 to Duty 1 for test. Placed Pump 1 man/off , pump 2 started/running ok. Placed Pump 2 back to auto. | All Wastewater System ROC General | 2026-03-26
ROC | March | AUSSYS- Evgeni S restarting OIT. Disregard heartbeat alarm. | All Wastewater System ROC General | 2026-03-27
ROC | March | LSSS - Pump 4 emergency stop alarm, Phil R and Terry C on site. | All Wastewater System ROC General | 2026-03-27
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-16
ROC | March | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-03-26
ROC | March | YDSS + YNSS normal | All Wastewater System ROC General | 2026-03-27
ROC | March | YDSS + YNSS normal | All Wastewater System ROC General | 2026-03-27
ROC | March | Christian Van Beek signing in. | All Wastewater System ROC General | 2026-03-25
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-25
ROC | March | Angelica Chepiga signing out | All Wastewater System ROC General | 2026-03-26
ROC | March | NBSP - Mechanical Bar Screen Failed to Stop and OOS alarms came in multiple times along with Inlet Channel High Float. Checked site. Called Lance J, who directed to place the manual override setpoint to start. This triggered the Mechanical Bar Screen general alarm which placed the bar screen in local. Lance informed he is headed to site to reset these alarms. CMU5 Created W11750066 11:51 - Inlet Channel High float and level hihi alarms came in. This is due to the Mechanical Bar Screen being OOS but Lance informed once the hihi levels hit, will go through the manual bar screen 13:32 - Lance J. called to inform that he has cleared the alarms and the mechanical bar screen is running now. Lance informed that if the fail to stop alarm comes in again, place the manual override setpoint back to start. If the Mechanical Bar Screen General alarm is triggered again, Lance would like a call back. Lance directed to disregard the Sludge Thickener Hi/HiHi alarms #CONSULT #CMU5 | All Wastewater System ROC General | 2026-03-22
ROC | March | SUSP - UV channel 1 common critical/channel 1 high level alarms and UV system critical failure alarm. UV channel 1B is active, flow through the UV channel recently started. Disregard alarms as per shift report. Alarms cleared when acknowledged. | All Wastewater System ROC General | 2026-03-19
ROC | March | PVSS - David D. is on site and will be turning off the odour control system for a PM | All Wastewater System ROC General | 2026-03-23
ROC | March | MTSP - Barry M. called to inform that he is on site at MTSP but will be shutting down MTSS. Barry informed that the high wet well levels can be disregarded | All Wastewater System ROC General | 2026-03-23
ROC | March | KBSP - Inlet channel filter bypass pending alarm. Harie R testing alarm. | All Wastewater System ROC General | 2026-03-24
ROC | March | Ethan U signing in Weather 5. | All Wastewater System ROC General | 2026-03-22
ROC | March | Ethan Ullalkar signing out. | All Wastewater System ROC General | 2026-03-23
ROC | March | Angelica Chepiga signing in | All Wastewater System ROC General | 2026-03-16
ROC | March | KSSP, UV Panel Major Fault/System Major Fault/common major fault/Module Comm fail, nothing in shift report about UV items being disregarded, notified Tyson C, he will look into it 04:40, Tyson C directed to disregard, they will look into it in the morning consult | All Wastewater System ROC General | 2026-03-17
ROC | March | SUSP - UV channel 1 common critical alarm, UV channel 2 high level alarm, UV system critical failure alarm, UV channel 1 common critical and high level alarm. Checked site, UV channel 1 Bank 1B is active. Trending shows flow to the UV system recently started. Shift report states these alarms will trigger when the plant activates and flow to the UV starts. Cleared alarms. | All Wastewater System ROC General | 2026-03-20
ROC | March | NBSP- Young J onsite working on UV's | All Wastewater System ROC General | 2026-03-20
ROC | March | Connor Smith signing in -12C Windy | All Wastewater System ROC General | 2026-03-17
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-16
ROC | March | KSSP- Neil O onsite with contractors for generator work. Will be Local off for the day. | All Wastewater System ROC General | 2026-03-17
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-20
ROC | March | Carter Dunn Signing Out | All Wastewater System ROC General | 2026-03-17
ROC | March | Angelica Chepiga signing in,weather -11C | All Wastewater System ROC General | 2026-03-18
ROC | March | RHAMF-Assigned recirculation pump 1 to duty 1 for Jim from NAC. 12:12 Recirculation pump 1 for both Train 1 and 2 on duty 1, recirculation pumps 2 OOS (local off) until tomorrow. Jim from NAC leaving site. | All Wastewater System ROC General | 2026-03-16
ROC | March | RHAMF1 - Jimmy from NAC working on recirculation Pump 2. 14:40 Joe O from CPD requested switch Duty, Unit 1 recirculation Pump 2 to duty 1. Recirculation water low/low, pressure low and low/low. Recirculation pumps interlocked. Jimmy from NAC troubleshooting. 15:00 Man/stopped recirculation Pump1 for Jimmy from NAC, he is running recirculation Pump 1 in Local. 15:14 Switched Unit 2 recirculation Pump 2 to duty 1 for Jimmy from NAC 15:24 Unit 1 Recirculation Pump 1 back to auto, recirculation Pump 2 to Duty 1 as per Jimmy from NAC. 15:30 Unit 1 Recirculation Pump 1 assigned to duty 1 as per Jimmy from NAC. | All Wastewater System ROC General | 2026-03-17
ROC | March | Gluzen Ramos Ong signing in | All Wastewater System ROC General | 2026-03-27
ROC | March | NBSP - Barscreen out of service and barscreen fail to stop alarms. Checked site, barscreen is in auto but faulted. Attempted to clear alarm. Alarm cleared. | All Wastewater System ROC General | 2026-03-18
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-18
ROC | March | NMSSBP - Mech screen 2 E-stop. Eqipment OOS and Kevin S onsite | All Wastewater System ROC General | 2026-03-20
ROC | March | Adeela Khan Signing Out | All Wastewater System ROC General | 2026-03-18
ROC | March | NBSP - Bar Screen Failed to Stop and OOS alarms came in. Checked site. Bar screen is in auto. Alarm cleared. 22:26 - Alarms came back in along with Inlet Channel High float alarm. Would not clear. NBSP - Inlet Works general alarms came in multiple times today. Called Lance J. who directed to select Continuous Override Start on the bar screen setpoint. Alarms were cleared and bar screen is now running. Lance would like a call back if the alarm comes back in. #CONSULT | All Wastewater System ROC General | 2026-03-18
ROC | March | LSSS, David D on site turning off the odour control | All Wastewater System ROC General | 2026-03-23
ROC | March | KBSP - Lance J working on UV channel 1, disregard alarms for the duration of the work. | All Wastewater System ROC General | 2026-03-26
ROC | March | Christian Van Beek signing in. Weather: -2C and clear. | All Wastewater System ROC General | 2026-03-19
ROC | March | BLSS - Screen 1 fault, screen 1 uncommanded stop and mechanical screen system not on. Checked site, barscreen is interlocked. Unable to clear alarms. Contacted Marcus R who will investigate. | All Wastewater System ROC General | 2026-03-19
ROC | March | PVSS - Marcus R onsite running generator, drywell inspection, sump alarm, temp, flood, & odour control unit | All Wastewater System ROC General | 2026-03-20
ROC | March | Connor Smith signing in | All Wastewater System ROC General | 2026-03-19
ROC | March | YDSS + YNSS normal | All Wastewater System ROC General | 2026-03-23
ROC | March | NMSSYS- Daniel K onsite with contractor troubleshooting Force Main Valve 2. Pumps are in manual and Dan will monitor Wet well levels. | All Wastewater System ROC General | 2026-03-24
ROC | March | NBSP - Barscreen general alarm. Called Young J who is working on the barscreen system. | All Wastewater System ROC General | 2026-03-18
ROC | March | KBSP- David D onsite for generator work. Lauren S and Lance J also onsite. | All Wastewater System ROC General | 2026-03-16
ROC | March | Angelica Chepiga signing in | All Wastewater System ROC General | 2026-03-17
ROC | March | LSSS - Wet Well Screen 1 Differential Level LOE alarm came in. Trends are okay. Alarm cleared | All Wastewater System ROC General | 2026-03-18
ROC | March | LSSS- Ubah (Student) onsite and requested pump 6 in duty 1 for sampling. | All Wastewater System ROC General | 2026-03-18
ROC | March | SHSP - RAS pump 2 speed deviation alarm. Appears to be just rotated in. Informed Lance J, okay to rotate RAS pump 3 into duty 1. for the night | All Wastewater System ROC General | 2026-03-20
ROC | March | SUSP - UV System Critical Failure, Ch.1 High Level, and Ch.1 and 2 Common Critical alarms came in. Alarms cleared upon acknowledgement. Disregarded as per shift report | All Wastewater System ROC General | 2026-03-18
ROC | March | Connor Smith signing out | All Wastewater System ROC General | 2026-03-25
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-20
ROC | March | AUSSSR- Line 2 Valve Overtorque Alarm. Two lines are not available. Notified Chris R. He will look into it. | All Wastewater System ROC General | 2026-03-26
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-21
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-22
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-23
ROC | March | MTSP - UV Systems major Fault alarm came in. Checked site. UV bank 1B is local/off and offline as per shift report. UV Bank 1A is currently running but flashing and permissive status is interlocked. Called Kevin S. who will take a look. 22:40 - Kevin S. called back and informed that he will head to site. Kevin would like to verify that the UV Bank 1A is running even though it is reading interlocked and that there is no tertiary bypass. CMU5 Created W11740941 00:02 - Kevin S. called back to inform that UV Bank 1A was running and there was no bypass. Kevin informed that he was able to clear alarm and will investigate further in the morning. Kevin directed to disregard if the same alarm comes back in but give a call back if the UV does not have a running status 03:25 - UV System Major Fault came back in. UV Bank 1A is running. Disregarded as per Kevin S. #CONSULT #CMU5 | All Wastewater System ROC General | 2026-03-17
ROC | March | HMSS - Marcus R testing High wet well level alarms. | All Wastewater System ROC General | 2026-03-18
ROC | March | SUSP - UV channel 1 high level alarm and UV system critical failure alarm. Checked site, UV channel 1 is active. Trending shows flow recently started for the UV system. Shift report states these alarms trigger on flow start and can be disregarded. Alarms cleared on acknowledgement. | All Wastewater System ROC General | 2026-03-18
ROC | March | MTSP - Alum Pump Containment Flood Alarm outstanding. Checked MTSP logbook and noticed that Phil R. attended site. Called Phil R. who informed that he was able to pump out the chamber but it appears there is no alum leak but there was water in the chamber due to a previous effluent line break. Phil informed that he is unable to clear the alarm due to an issue with the float and directed to disregard alarm until tomorrow. Phil also requests a CMU5. CMU5 Created W11762108 #CONSULT #CMU5 | All Wastewater System ROC General | 2026-03-26
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-26
ROC | March | Ethan U signing in Weather 1. | All Wastewater System ROC General | 2026-03-23
ROC | March | MTSP - Terry C running generator not on the load. | All Wastewater System ROC General | 2026-03-24
ROC | March | KSSSQW, Chris C on site, running generator | All Wastewater System ROC General | 2026-03-23
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-20
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-19
ROC | March | SUSP - Tyson C called and directed to activate the sludge transfer sequence by hitting the 'Start Transfer" button. | All Wastewater System ROC General | 2026-03-25
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-17
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-18
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-21
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-19
ROC | March | Adeela Khan signing out | All Wastewater System ROC General | 2026-03-19
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-22
ROC | March | KSSP - CIP Cean/Recirc flow hihi/lo. Status went to normal right away. Train 3 going through cool down | All Wastewater System ROC General | 2026-03-22
ROC | March | Angelica Chepiga signing out | All Wastewater System ROC General | 2026-03-24
ROC | March | Angelica Chepiga signing in,weather -7C | All Wastewater System ROC General | 2026-03-24
ROC | March | NBSP - UV Minor Fault alarm. Checked site, UV Bank 1B is active. Trending shows that the UV system duty recently rotated. Shift report states this alarm is a disregard as long as one bank is running. | All Wastewater System ROC General | 2026-03-25
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-25
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-22
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-22
ROC | March | YDSS + YNSS Normal Christian Van Beek signing out. | All Wastewater System ROC General | 2026-03-22
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-27
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-22
ROC | March | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-03-19
ROC | March | Carter Dunn Signing In, 2D/Clear | All Wastewater System ROC General | 2026-03-24
ROC | March | NBSP - UV system minor fault, disregard as per shift report | All Wastewater System ROC General | 2026-03-21
ROC | March | KSSP - Niel O and Chase J on site to complete work on the UV system. | All Wastewater System ROC General | 2026-03-19
ROC | March | Christian Van Beek signing in. Weather: -6C and clear. | All Wastewater System ROC General | 2026-03-27
ROC | March | 13:23 SHSP - Power blip. Notified Gavin W, he is on site, will reset/clear alarms. | All Wastewater System ROC General | 2026-03-27
ROC | March | BSP- Inlet Channel High Float, Mech. Bar Screen Dif. Level HiHi Alarm. Notified Lance J. He will attend site. W11749371 CMU5 | All Wastewater System ROC General | 2026-03-20
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-17
ROC | March | yds + ynss normal | All Wastewater System ROC General | 2026-03-17
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-18
ROC | March | Connor Smith signing in -3C Cloudy | All Wastewater System ROC General | 2026-03-25
ROC | March | Angelica Chepiga signing out | All Wastewater System ROC General | 2026-03-18
ROC | March | Adeela Khan signing in. Weather: -2C and Cloudy | All Wastewater System ROC General | 2026-03-18
ROC | March | YDSS + NYWS Normal | All Wastewater System ROC General | 2026-03-19
ROC | March | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-03-20
ROC | March | Ethan Ullalkar signing out. | All Wastewater System ROC General | 2026-03-21
ROC | March | YDSS + YNSS Normal Adeela Khan signing out | All Wastewater System ROC General | 2026-03-27
ROC | March | KSSP - ZW3 High turbidity/ shutdown alarm, notified Chase J, he will investigate. | All Wastewater System ROC General | 2026-03-16
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-18
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-21
ROC | March | NMSSBP- Satnam M onsite for generator testing. 14:40- Finished onsite. | All Wastewater System ROC General | 2026-03-24
ROC | March | KCSSKR, Generator Running Alarm/Pump 3 Fault Alarm, as per interim, notified Lance J, he is heading to site 01:25, Contacted Hydro 1 and spoke with Operator Abby, Informed her of the outages, Abby informed the ROC that this was a planned outage and work is currently being done to their system. Power outage should last from 1AM-4AM. Passed on this new information to Lance J. 01:54, Lance J reset Pump 3 and placed it man/off. Lance J leaving site CMU5: W11756679 | All Wastewater System ROC General | 2026-03-25
ROC | March | SUSP- Tyson C onsite working on UV channel B | All Wastewater System ROC General | 2026-03-19
ROC | March | SUSP - UV Channel 1 Bank 1A major alarm, common major alarm and UV system major fault alarm. Checked site, UV channel 1 Bank 1 A is in local on. UV channel 1 Bank 1B is also on and in auto mode. System dose and intensitya re normal for the bank in auto. UV intensity and for Bank 1 A is higher than normal. Will monitor site and investigate who is on site. | All Wastewater System ROC General | 2026-03-18
ROC | March | NBSP- Lauren S onsite testing sump pits and working on air compressors. | All Wastewater System ROC General | 2026-03-19
ROC | March | SEOC- Phil R and Terry S onsite working on biofilters and recirc pumps. | All Wastewater System ROC General | 2026-03-24
ROC | March | BLSS - Pump 3 on duty 6/ OOS. Notified Lauren S, she assigned Pump 3 to duty 1. | All Wastewater System ROC General | 2026-03-26
ROC | March | LSSS - rotated D1 from P4 to P6 for EME sampling | All Wastewater System ROC General | 2026-03-27
ROC | March | LSSS - Ubah F. from EME is on site for weekly testing and requested pump 6 on. Duty 1 is about to activate and pump 6 is already in duty 1 | All Wastewater System ROC General | 2026-03-23
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-21
ROC | March | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-03-20
ROC | March | KSSP - Neil O and Chase J working on UV system. | All Wastewater System ROC General | 2026-03-18
ROC | March | YDSS + YNSS Normal SUSP - UV system critical failure, common critical alarm, high level Ch. 2. Cleared right away. Cleared when UV gates opened | All Wastewater System ROC General | 2026-03-22
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-23
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-21
ROC | March | LSSS - Wet well screen 1 differential hihi alarm. Checked site, trending shows an abnormal spike of the screen 1 differential level reading. Loss of echo alarms have also been triggering intermittently. Will send email to area ops. Cleared alarms. | All Wastewater System ROC General | 2026-03-21
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-21
ROC | March | RHAMF - Unit 1 Recirculation Pump 1 and 2 fan overload alarms came in. Checked site. Both fans are running and Unit 2 Recirculation Pump 1 is running. Disregarded as per shift report and will call NAC if a fan stops working or a power outage occurs | All Wastewater System ROC General | 2026-03-22
ROC | March | Adeela Khan signing in. Weather: 8C and raining | All Wastewater System ROC General | 2026-03-26
ROC | March | SUSP - UV critical failure alarm came in and cleared upon acknowledgement. Plant recently activated. Disregarded as per shift report | All Wastewater System ROC General | 2026-03-26
ROC | March | Adeela Khan signing in | All Wastewater System ROC General | 2026-03-23
ROC | March | YDOC - Terry R finished on site. | All Wastewater System ROC General | 2026-03-18
ROC | March | YDSS +YNSS Normal Adeela Khan signing out | All Wastewater System ROC General | 2026-03-22
ROC | March | NBSP - Young J, Marcus R and Lauren S are on site to complete maintenance on all blowers on site. | All Wastewater System ROC General | 2026-03-19
ROC | March | NBSP - Inlet channel level high float alarm - alarm cleared. | All Wastewater System ROC General | 2026-03-18
ROC | March | SUSP - Bar screen Hi level alarm. Disregard as per shift report. | All Wastewater System ROC General | 2026-03-20
ROC | March | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-03-20
ROC | March | PVSS - Brent St C on site with Total Power to complete generator maintenance. | All Wastewater System ROC General | 2026-03-19
ROC | March | BLSS - Screen Differential Level Hi alarm came in. Disregarded as per shift report | All Wastewater System ROC General | 2026-03-18
ROC | March | SHSP- Gavin W working on Ras pump 2, disregard alarms for the duration of the work. | All Wastewater System ROC General | 2026-03-26
ROC | March | SHSP - Aeration Blower 1 Fan Overload alarm came in. Checked site. Aeration blower 1 is still running at 51%. Called Marcus R. to receive direction to rotate duties. Rotated blower 2 to duty 1. #consult | All Wastewater System ROC General | 2026-03-18
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-23
ROC | March | AURSBS, Activated D1 AUW2/3/5, Placed well 2/3/5 in man/on. wrong book | All Wastewater System ROC General | 2026-03-25
ROC | March | NMSSBP- Satnam S onsite for generator testing. 11:31- Finished on site, all alarms cleared. | All Wastewater System ROC General | 2026-03-25
ROC | March | KCSSKR- Pump 3 Uncommanded Stop, Fault Alarms. Pump 2 running in duty 1. Notified Marcus R. | All Wastewater System ROC General | 2026-03-16
ROC | March | KSSSQW - Pump 2 lo/low- low flow, Wet wells Hi and Hihi alarms, P2 efficiency low/low-low, wire- to - water low/low alarms. Assigned P2 to duty 4/ man/off, Pump 3 to duty 3. Notified Neil O. He will attend site later today to check P2. | All Wastewater System ROC General | 2026-03-16
ROC | March | Ethan Ullalkar signing out. | All Wastewater System ROC General | 2026-03-20
ROC | March | Connor Smith signing out | All Wastewater System ROC General | 2026-03-20
ROC | March | SHSP- Gavin W onsite diverting to Lagoon for work on filter inlet channel. Disregard related alarms. | All Wastewater System ROC General | 2026-03-19
ROC | March | Ethan U signing in | All Wastewater System ROC General | 2026-03-20
ROC | March | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-03-19
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-20
ROC | March | AUSSYS - Marcos T testing High Wet well level alarm. | All Wastewater System ROC General | 2026-03-17
ROC | March | SUSP - Bar screen Hi level alarm. Disregard as per shift report. | All Wastewater System ROC General | 2026-03-24
ROC | March | SEOC9 - Shaft 9 O2 Monitor HiHi/OOR alarms, disregard as per SCADA review. | All Wastewater System ROC General | 2026-03-19
ROC | March | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-03-19
ROC | March | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-03-20
ROC | March | SUSSWB- Ventilation H2 S High Alarm. Alarm cleared. | All Wastewater System ROC General | 2026-03-24
ROC | March | MTSP - Clarifier 1 and 2 no RAS pump running alarm. Checked site, all RAS pumps currently manual/off. | All Wastewater System ROC General | 2026-03-19
ROC | March | AUSS - Kyle B finished work and leaving site. | All Wastewater System ROC General | 2026-03-18
ROC | March | AUSS - Bill V. working on Generator 3 out: 13:40. cleared outstanding gen 3 alarms | All Wastewater System ROC General | 2026-03-19
ROC | March | wrong book | All Wastewater System ROC General | 2026-03-18
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-21
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-21
ROC | March | SUSP - UV channel 1 high level alarm. UV channel 1 common critical alarm and UV system critical failure alarm. Checked site, UV channel 1 is active. Trending shows flow to the UV channel recently started. Shift report states these alarms trigger when the flow to the UV channel starts and they can be disregarded. Cleared alarms. | All Wastewater System ROC General | 2026-03-19
ROC | March | Christian Van Beek signing out. | All Wastewater System ROC General | 2026-03-19
ROC | March | Connor Smith signing out | All Wastewater System ROC General | 2026-03-19
ROC | March | Connor Smith signing in 0C Snowy | All Wastewater System ROC General | 2026-03-20
ROC | March | HMSS - Wet well 1 and 2 Metro Overflow alarms. Called Marcus R and Lauren S, no answer. Will call again. 12:58 Called Marcus R. Confirmed Metro Overflow alarms- test. | All Wastewater System ROC General | 2026-03-18
ROC | March | RHAMF - Jun Jia from NAC on site and has requested that all recirculation pumps, all building air handling fans and AMF Fans be placed manual/off to complete their testing. Called Chris R who is aware of the work and will contact Daniel K to confirm. Placed all pumps and fans manual/off. | All Wastewater System ROC General | 2026-03-25
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-19
ROC | March | KSSSQW - Ernie H on site performing Generators PM's, running generator. | All Wastewater System ROC General | 2026-03-17
ROC | March | Christian Van Beek signing out. | All Wastewater System ROC General | 2026-03-25
WW-CEAST | March | -On site to perform a station check. -Entered station readings into SharePoint. -Checked generator and valve room. -All pumps in auto and available. | Aurora Henderson Sewage Pumping Station | 2026-03-30
ROC | March | Christian Van Beek signing in. | All Water System ROC General | 2026-03-02
ROC | March | QVETQS - drawdown initiated by Ben H. NMETHW isolated. Duty 1 activated for NMETHW. NMETIB duty 1 stop setpoint increased to 85% from 75% and duty activated. | All Water System ROC General | 2026-03-03
ROC | March | MARS - lo level, deactivate AURSBS. Will monitor | All Water System ROC General | 2026-03-12
ROC | March | GWTP - Keswick header fluoride low alarm. Checked site, Keswick system is active and high lift pumps are pushing flow. Trending shows no dip of the fluoride reading below the low alarm setpoint at the time of the alarm. Alarm status changed to Normal, alarm cleared on acknowledgement. | All Water System ROC General | 2026-03-04
ROC | March | MKRSEM- Called Toronto and requested pumps off. | All Water System ROC General | 2026-03-13
ROC | March | RHRSTR- Deactivated duty | All Water System ROC General | 2026-03-13
ROC | March | SHTP - KMNO Tank 1 and 2 Level Low (info alarm). Tank 2 in duty 1. Jordan B will check SCADA and call back. # Consult 10:15 Jordan B will attend site. # CMU5 W11733473 | All Water System ROC General | 2026-03-15
ROC | March | YWS + NYWS Normal Connor Smith signing out | All Water System ROC General | 2026-03-16
ROC | March | VNPS PD7, Placed pump 2 man/off MAPS PD7, Placed pump 2 in auto | All Water System ROC General | 2026-03-16
ROC | March | HLVCMA, Valve Chamber Flood Alarm has come in 2 times but then has cleared, will continue to monitor site, if it comes in a third time, will notify Harsh P 18:32, Alarm came in a third time, notified Harsh P, he is heading to site 21:30, Harsh P is finished on site CMU5: W11760443 | All Water System ROC General | 2026-03-25
ROC | March | MAPS PD7, Placed pump 2 in auto VNPS PD7, Placed pump 2 in man/off | All Water System ROC General | 2026-03-26
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-26
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-26
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-26
ROC | March | SUETDR- Activated duty Interim Procedure | All Water System ROC General | 2026-03-16
ROC | March | 13:27 SHTP - Power blip. Plant was running. Notified Jen S , she is on site , will reset alarms. | All Water System ROC General | 2026-03-27
ROC | March | QVW12 - Chlorine gas leak alarm and valve system emergency closure faults. Called Joe D to return to site for further investigation. Placed wells in manual/off. 16:11 - QVW12 - Joe D contacted Eric S who will attend site to replace the chlorine gas detector. Joe D not attending site. CMU5 already created for Eric S previously. #consult | All Water System ROC General | 2026-03-27
ROC | March | YWS + NYWS normal Connor Smith signing out | All Water System ROC General | 2026-03-26
ROC | March | KCETDS- Tim H onsite for filling of tower | All Water System ROC General | 2026-03-24
ROC | March | Stouffville: Received call forwarded from Access York from Dave Raymer (647-395-2237, ED of Eastern Gate Village, Seniors Community). He described his issue that testing water from Stouffville Wells 1 and 2 are going onto their property (6985 Main Street, Stouffville) and their pump station that typically pumps that water has failed. He has requested that that flow is turned off until repairs to their pumps are made, currently no estimated time. Notified Jack P. 10:45 - Phil D. and Jack P. attending site. CMU5: W11764329 | All Water System ROC General | 2026-03-27
ROC | March | JFPS - Lee F working on site. Man/stop P1 / assigned to D5, Assigned P2 to duty 1 for Lee F. | All Water System ROC General | 2026-03-27
ROC | March | QVW12 - Kyle R on site to complete work on the well 2 starter devices. Kyle has placed well pump 2 local/off. | All Water System ROC General | 2026-03-19
ROC | March | BLSS - Lauren S. and Lance J. attended screen 1 fault. Screen back in service and all alarms cleared. CMU: 11746738 | All Wastewater System ROC General | 2026-03-19
ROC | March | Carter Dunn Signing Out | All Water System ROC General | 2026-03-17
ROC | March | MKETFA - Zoran from Metro called, electrical crew working on Milliken brakers. Should not affect the process. | All Water System ROC General | 2026-03-26
ROC | March | Connor Smith signing in 3C Clear | All Water System ROC General | 2026-03-26
ROC | March | YWS + NYWS NORMAL | All Water System ROC General | 2026-03-20
ROC | March | SHETCS, Activated D1 | All Water System ROC General | 2026-03-24
ROC | March | STW12 - Place well 1 back in auto STW3 - Place well back in auto | All Water System ROC General | 2026-03-24
ROC | March | Christian Van Beek signing out. | All Water System ROC General | 2026-03-19
ROC | March | RHPSPA- Disch. Header Flow 1 LoLo. Duty just deactivated. Cleared alarm. | All Water System ROC General | 2026-03-20
ROC | March | YDSS + YNSS Normal Christian Van Beek signing out. | All Wastewater System ROC General | 2026-03-18
ROC | March | Carter D Signing In, 4D/Clear | All Water System ROC General | 2026-03-25
ROC | March | NMTKKC, Inlet Total Cl2 hihi//Inlet Combined Cl2 hihi, Res currently filling, Currently the header and the outlet are both reading normal, will continue to monitor, if residual continue to rise, will take corrective actions 18:24, After 2 readings, the residual came back down to normal levels. Residuals on the outlet and header analyzers still remained in normal range | All Water System ROC General | 2026-03-25
ROC | March | STETBR - Yash S on site for planned network upgrades. | All Water System ROC General | 2026-03-19
ROC | March | NMETIB - Alex B on site to test the flood alarm and complete the JHSC checks. | All Water System ROC General | 2026-03-27
ROC | March | ARPS- OCWA called (Tegbeer) and informed will be rotating Pumps/ from P6 to P5. | All Water System ROC General | 2026-03-24
ROC | March | MAPS PD7 - Pump 3 man/off, VNPS PD7 Pump 3 to auto. | All Water System ROC General | 2026-03-24
ROC | March | EGMCDD - East Gwillimbury pressure lolo alarm. Checked site, valves are cycling between the 100mm line and the 250mm line. After valves rotated the alarms cleared. | All Water System ROC General | 2026-03-25
ROC | March | KSSP - RAS combined no flow alarm. Checked site, RAS pumps have been placed manual/off by area operations. | All Water System ROC General | 2026-03-25
ROC | March | QVW34 - Dan B and Kyle R on site to complete maintenance on well pump 4. Dan B will be cutting power to well pump 4 for the assigned work. Dan will eventually be working on well pump 3 but will coordinate with Will M as the pump is currently running manual for additional supply | All Water System ROC General | 2026-03-25
ROC | March | GWTP - ZW 5 membrane tank level lo and level switch lolo alarm. Alarm status quickly changed to normal. Checked site, tank is going through a backwash sequence. Alarms cleared on acknowledgement. Will monitor system. | All Water System ROC General | 2026-03-25
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-22
ROC | March | STW12/STW3 - Place both well 1 & 3 back in auto after zone 1 tower duty finished | All Water System ROC General | 2026-03-23
ROC | March | RHRSTR - activated Duty 1 to help with MARS level. | All Water System ROC General | 2026-03-24
ROC | March | BLW3 - Jack P requested pump 3 man/stop, back to auto. | All Water System ROC General | 2026-03-24
ROC | March | VNPS- Noticed PD8 Pump 2 running in manual and duty 1 and duty 2 about to start up. Notified Benson S who is onsite. He will contact maintenance to inquire if they are running in it. Placed pump 4 (duty 2) pump in manual to prevent 3 pumps from running. 13:32- Benson S called back. Requested to place pump 2 back into auto. Also placed pump 4 duty 2 pump back into auto. | All Water System ROC General | 2026-03-20
ROC | March | STRS48 - Chlorinator 1 failed to close alarm on, switched to normal right away, alarm cleared when acknowledged. | All Water System ROC General | 2026-03-16
ROC | March | MKETFA- Miguel from YRP onsite for monthly visit. | All Water System ROC General | 2026-03-26
ROC | March | NMW12 - Alex B on site for chlorine system inspection. AUPSRR - Donald M on site for chlorine system inspection. | All Water System ROC General | 2026-03-27
ROC | March | RHPSPA - Suction header Pressure Hi alarm, duty just deactivated. Quick spike, back to normal. | All Water System ROC General | 2026-03-26
ROC | March | STETBR - Low level alarm. Activated STW3 in manual mode as per the interim procedure. | All Water System ROC General | 2026-03-18
ROC | March | NMETIB - Inlet flow hi alarm. Checked system, NMVCBA is open more than usual and flows are high. Trending shows that flow through the valve slowed and the SCADA system opened the valve more to compensate but opened the valve too much. Monitoring site to ensure the flow returns to the setpoint. | All Water System ROC General | 2026-03-22
ROC | March | STETBR - Tower level hi alarm. Placed STW12 and STW3 in auto mode. | All Water System ROC General | 2026-03-22
ROC | March | NBW5 - Influent Free chlorine residual alarm, quick spike. Alarm cleared in 4 minutes. | All Water System ROC General | 2026-03-24
ROC | March | BLW34- Jack P called. Finished onsite. Running well in manual STW12- Heading to site for a chlorine cylinder change. | All Water System ROC General | 2026-03-24
ROC | March | VNPSCD - Benson S completed work on site. | All Water System ROC General | 2026-03-16
ROC | March | NRETBR, AUETAD- Evgeny S working on OITs. Disregard Heartbeat Alarms. | All Water System ROC General | 2026-03-26
ROC | March | NBW2- Silicate Pump 2 Uncommanded Stop. Cleared alarm. | All Water System ROC General | 2026-03-16
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-16
ROC | March | Gluzen Ramos Ong signing out | All Water System ROC General | 2026-03-27
ROC | March | QVW34 - Eric S working on influent chlorine analyzer. | All Water System ROC General | 2026-03-24
ROC | March | MAPS PD7 - Pump 2 man/off VNPS PD7 - Pump 1 to auto. | All Water System ROC General | 2026-03-24
ROC | March | SEOC4 - Parth P on site for O2 sensor replacement. 11:58 Parth P and Rick L finished on site | All Wastewater System ROC General | 2026-03-24
ROC | March | NMETYS- Alex B onsite filling eyewash. Disregard low pressure alarms that may trigger. | All Water System ROC General | 2026-03-19
ROC | March | GWTP - GAC 4 flow control valve deviation alarm outstanding. Disregard alarm as per shift report. | All Water System ROC General | 2026-03-19
ROC | March | STW3 - Placed well 3 pump back to auto. | All Water System ROC General | 2026-03-20
ROC | March | YWS + NYWS Normal | All Water System ROC General | 2026-03-23
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-23
ROC | March | JFPS - Cole W called to inform there is a new interim procedure to run JFPS pump 2 for one hour each day from March 26 - April 1. The duty is currently active for this pumping station. Placed pump 3 in manual and shut it down. Activated pump 2 in manual for one hour. | All Water System ROC General | 2026-03-25
ROC | March | YWS + NYWS Normal Christian Van Beek signing out. | All Water System ROC General | 2026-03-22
ROC | March | Ethan U signing in Weather 5. | All Water System ROC General | 2026-03-22
ROC | March | NMW15 - Combine Chlorine Low alarm. Donnald M and Alex B working on site. Well 15 pump local/off, no water directed to users. | All Water System ROC General | 2026-03-24
ROC | March | QVW12 - Joe and Eric S finished on site and leaving. Joe D has returned the system to normal operations. | All Water System ROC General | 2026-03-27
ROC | March | NMVCBA, Revert flow set point to 40L/sec from 80L/sec NMVCIB, Placed flow set point to 80L/sec from 40L/sec. | All Water System ROC General | 2026-03-23
ROC | March | NRETBR - Joe D and Christian B finished on site. | All Water System ROC General | 2026-03-24
ROC | March | SHSP - Marcus R and Gavin W working/inspecting UV system. Disregard alarm for the duration of the work. | All Wastewater System ROC General | 2026-03-24
ROC | March | AURSBS- Ian W working on OIT. Disregard Heartbeat Alarm. | All Water System ROC General | 2026-03-26
ROC | March | MAP7 - P3 back in auto VNP7 - P1 man/off | All Water System ROC General | 2026-03-27
ROC | March | JFPS - Lee F. doing pump testing on P1 | All Water System ROC General | 2026-03-27
ROC | March | QVW12 - Chlorine gas leak alarm and chlorine system emergency closure fault. Called Joe D to inform he will head to site. Joe D requested that on call instrumentation be informed. Called Eric S who will speak with Joe D and coordinate a fix. 15:34 - QVW12 - Eric S called and requested a CMU5. created CMU5#W11764578 #CMU5 | All Water System ROC General | 2026-03-27
ROC | March | KSTP - Conduit level lolo and filter 1 and filter level low alarms. The filters have interlocked on the lolo conduit level alarm. The low lift pump interlock has been cleared and the conduit level is rising. Once the conduit level passed the low alarm setpoint the filter interlock cleared and they initiated production. Called Jason G to inform of these system updates. Jason directed to clear alarms and call if anything else fails or faults. | All Water System ROC General | 2026-03-19
ROC | March | KSTP- Raw Water Turbidity Fault Alarm. Disregard as per SCADA report | All Water System ROC General | 2026-03-19
ROC | March | MAPS- Placed PD7 Pump 2 in manual VNPS- Placed PD7 pump 2 in auto | All Water System ROC General | 2026-03-17
ROC | March | KSTP - Low lift Pump 3 uncomm stop alarm, PACL Pump 1 uncomm stop alarm. Duty switched to PACL Pump 2. Duty not active, plant not running. Emailed Central OP team. | All Water System ROC General | 2026-03-17
ROC | March | NBW37- Jacob M onsite working on leak on effluent chlorine analyzer. Disregard related alarms. | All Water System ROC General | 2026-03-20
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-28
ROC | March | SHSP - Power Failure alarms came in. Checked site. Generator is running but site is still connected to hydro power. Informed Lauren S. SHSSDK - Control Panel Power Failure alarms came in along with pump 1 VFD fault. Control panel alarm cleared but VFD fault is outstanding. Called Lauren S. who is headed to site. CMU5 Created W11769394 #CMU5 #CONSULT | All Wastewater System ROC General | 2026-03-31
ROC | March | EGSSSC - recirculation loop flow low and lowlow alarms. Flow control valve fault alarms and recirculation mode failure alarm. Station still operating, wet well cycling. Able to reset valve faults and recirculation flow alarms. Will monitor. | All Wastewater System ROC General | 2026-03-31
ROC | March | Adeela Khan signing in. Weather: 0C and snowing | All Wastewater System ROC General | 2026-03-13
ROC | March | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-03-12
ROC | March | NMEQBP - Man/started Dewatering Pump 1. | All Wastewater System ROC General | 2026-03-12
ROC | March | LSSS - Pump 1 fault came in. Place pump 1 man/off | All Wastewater System ROC General | 2026-03-05
ROC | March | KSSSQW - Kevin K has completed work and is leaving site. JDSS - Kevin K is headed to site to complete pump testing. Kevin has requested all alarms be disregarded until the work is complete. | All Wastewater System ROC General | 2026-03-12
ROC | March | YDSS + YNSS Normal SUSSHS, Sewage Pump 1 no flow/VFD Fault, Notified Chris C, he is heading to site CMU5: W11760566 | All Wastewater System ROC General | 2026-03-26
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-26
ROC | March | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-03-24
ROC | March | NBSP - Mech Bar Screen oos alarm. Notified Young J. He will check NBSP - Inlet channel HiHi , High float alarms. Bar screen still OOS, Notified Yong J. He will check. | All Wastewater System ROC General | 2026-03-18
ROC | March | SHSP - Aeration blower 1 uncommanded start and stop alarm. Checked site, aeration blower 1 was not active when the alarms triggered. Aeration blower 2 was active when the alarms triggered and is still active and producing air flow. Able to reset alarms. | All Wastewater System ROC General | 2026-03-18
ROC | March | STETBR - Low level alarm. Man/started STW12 pump 1 and STW3 pump. | All Water System ROC General | 2026-03-20
WW-CEAST | March | -station check of site -reviewed SCADA -inspected site -entered data into SharePoint -Housekeeping, cleaned washroom -station okay | Aurora Henderson Sewage Pumping Station | 2026-03-13
WW-CEAST | March | On site to accommodate day 2 of wet well scum removal by WESSUC. Wet well scum cleaning complete without any issues. All pumps put back in service afterwards. | Aurora Henderson Sewage Pumping Station | 2026-03-04
WW-CEAST | March | Put all 4 pumps in manual to fill the wet well up for running the 4 pumps - informed ROC (Christian) of what I'm up to. Ran each pump - P1= 66.9L/s@ 100% with 366Kpa as pressure, P2= 66.8L/s @ 100% with 352Kpa as pressure, P3= 67.7L/s @ 100% with a pressure of 366Kpa and P4= 63.8L/s @100% with 355Kpa as pressure. Pump actuators where activated when the pump turned on and all 4 check valves are good. Flushed the air valves and also checked the odour control unit - all good. Station back to normal ops - alarms cleared and I informed ROC. | Aurora Henderson Sewage Pumping Station | 2026-03-12
WW-CEAST | March | -station check of site -reviewed SCADA -inspected site -entered data into SharePoint -maintenance on site to top up oil in generator as oil is low, notified Capital of low oil in generator -station okay | Aurora Henderson Sewage Pumping Station | 2026-03-09
WW-CEAST | March | On site for generator low oil issues. Oil level show 1/4? under the low mark. We will return with the correct oil | Aurora Henderson Sewage Pumping Station | 2026-03-09
WW-CEAST | March | Station check of site Reviewed SCADA Entered data into SharePoint Inspected site Topped up glycol for heating system Fixed gate, as it was falling off hinges and dragging on ground Oil for generator is low, created WO for Maintenance, as it's a Natural gas generator it takes a different oil then our diesel generators, will hopefully get our contractor from Total Power to do an oil change for this generator, as it's new, it may have not been changed yet. Station okay | Aurora Henderson Sewage Pumping Station | 2026-03-06
WW-CEAST | March | -station check of site -reviewed SCADA -inspected site -entered data into sharepoint -station okay | Aurora Henderson Sewage Pumping Station | 2026-03-20
WW-CEAST | March | -station check of site -reviewed SCADA -inspected site -entered data into SharePoint -valve exercising -station okay | Aurora Henderson Sewage Pumping Station | 2026-03-16
WW-CEAST | March | -station check of site -reviewed SCADA -inspected site -entered data into SharePoint -station okay | Aurora Henderson Sewage Pumping Station | 2026-03-23
WW-CEAST | March | On site with CD/Lexsan/WSP to troubleshoot FM2_MV1. Lexsan confirmed spare wire within the actuator and connected it for SCADA. Tested in both Local/Remote no issues. WSP/CD also inspected surrounding fence and noted significant damages due to snowplow. This issue will be looked at this coming spring/summer. | Aurora Henderson Sewage Pumping Station | 2026-03-24
WW-CEAST | March | Station check complete and the readings have been entered into the sharepoint | Aurora Henderson Sewage Pumping Station | 2026-03-27
WW-CEAST | March | On site to complete work orders. Wet well high level alarm test Wet well valve exercise Wet well inspection | Aurora Henderson Sewage Pumping Station | 2026-03-17
WW-CEAST | March | -station check of site -reviewed SCADA -inspected site -entered data into SharePoint -JHSC Inspection -Monthly Generator Test Run -started generator at 10:45, transfer successful, reset alarms on SCADA Generator Start Hours:81.6 Generator Stop Hours:82.8 Run Time:1.2 hrs -fuel cannot be accurately monitored as it's Natural Gas and is used for heating the building as well -generator stopped at 11:53 -test successful, on utility power -tested dry well flood alarm -assisted property services to fix broken gate, gate fixed -work completed -station okay | Aurora Henderson Sewage Pumping Station | 2026-03-02
WW-CEAST | March | Picked up recommended oil for generator Added approximately 15 L of oil to bring to the full mark. Ran generator for one hour. No smoke or other issues noted. Allowed oil to return to oil pan approximately 20 minutes. Oil level is still at full. Complete. | Aurora Henderson Sewage Pumping Station | 2026-03-10
WW-CEAST | March | -On site to perform a station check. -Entered station readings into SharePoint. -Both fans running in auto. -All recirc pumps available and in auto. -Nutrient tank batch mixing completed, tank already full. | Oak Ridges Air Management Facility | 2026-03-30
WW-CEAST | March | On site completed work orders. Station Check (See details on SharePoint) Both fans running in auto. One recirculation pump on duty from each train running in auto. Standby power generator available in auto. Nutrient Tank Batch Mixing - added 1/2 bag nutrient and topped up water from 5/8 to 7/8 level. Also on site, conducted special conditions testing together with contractors (CPD, NAC, AECOM and BIOREM) as part of the 14-day performance test. After the testing, cleared all alarms and put station back to normal operations. | Oak Ridges Air Management Facility | 2026-03-10
WW-CEAST | March | #NAME? | Oak Ridges Air Management Facility | 2026-03-20
WW-CEAST | March | On site completed work orders. Station Check (See details on SharePoint) Both fans running in auto. One recirculation pump on duty from each train running in auto. Standby power generator available in auto. Nutrient Tank Batch Mixing tank is full. | Oak Ridges Air Management Facility | 2026-03-23
WW-CEAST | March | -station check of site -reviewed SCADA -inspected site -entered data into sharepoint -station okay | Oak Ridges Air Management Facility | 2026-03-16
WW-CEAST | March | -station check of site -reviewed SCADA -inspected site -entered data into SharePoint -NAC electrician's on site, reset faults on recirculation pumps, "current inbalance", pressed reset on panel -reset alarms on SCADA, no alarms present -station okay | Oak Ridges Air Management Facility | 2026-03-02