## Operational Issues
PERSONGROUP | LOGBOOK_MONTH | LDTEXT | DESCRIPTION | EVENTDATE
WW-NORTH | October | Performed station check Completed lab analysis and entered into SharePoint Decanted and transferred STT 2 and 3 Pumped down Scum chambers Checked head works - cleared bar screen and checked bin Added 10 bags of Soda Ash Performed membrane weekly maintenance (drained hosed and refilled) Changed 4 bulbs and a sleeve on UV channel 2 | Keswick Water Resource Recovery Facility | 2025-10-30
WW-NORTH | October | Performed Sludge handling work order Decanted and transferred STT 2 and 3 Added 20 bags of soda ash | Keswick Water Resource Recovery Facility | 2025-10-19
WW-NORTH | October | Completed work orders and notified ROC of work being completed Performed standby generator test run and recorded readings in rounds sheet Start: 359.4 h Stop: 360.6 h Run time: 1.2 h Completed soda ash addition - 20 bags. | Keswick Water Resource Recovery Facility | 2025-10-16
WW-NORTH | October | disabled supernate tank Hi level alarm but left HiHi active to reduce the number of Hi level alarms we are receiving while doing sludge handling work. dissabled supernate pump flow alarms LoLo to HiHi to reduce alarms coming in during sludge handling work. will monitor to see if this helps fix the issue. | Keswick Water Resource Recovery Facility | 2025-10-16
WW-NORTH | October | Performed station check Decanted and transferred STT 1 and 3 Completed lab analysis and entered readings into SharePoint Checked head works - cleared bar screen and checked bin | Keswick Water Resource Recovery Facility | 2025-10-24
WW-NORTH | October | Performed station check Completed lab analysis and entered readings into SharePoint Decanted and transferred STT 1 and 2 Decanted STT 3 Pumped down Scum chambers Batch wasted 80m3 Checked headworks - cleared bar screen and checked bin Added 20 bags of soda ash Recorded OCU numbers | Keswick Water Resource Recovery Facility | 2025-10-23
WW-NORTH | October | On site to repair safety latch on chain fall hook. Found latch is bent. Removed latch and straightened Picked up new installation hardware. Installed safety catch and tested operation okay. Complete. | Keswick Water Resource Recovery Facility | 2025-10-16
WW-NORTH | October | Started decanting S.T.T's 1 and 3 Collected samples for in house labs Checked and leveled the grit and rag bins Cleaned off bar screen equipment Finished decanting and started transfer to S.H.T Completed turbidometer inspections/ cleaning Completed membrane T.S.S probe cleaning Recorded readings in SharePoint Switched WAS feed to S.T.T 3 | Keswick Water Resource Recovery Facility | 2025-10-29
WW-NORTH | October | Performed station check Decanted STT 2 Transferred STT 1 and 2 Batch wasted 80m3 Completed lab analysis and entered readings into SharePoint Checked head works - cleared bar screen and checked bin Added 20 bags of Soda Ash | Keswick Water Resource Recovery Facility | 2025-10-21
WW-NORTH | October | Started decanting S.T.T's 1 and 2 Collected YD samples Collected samples for in house labs Checked and leveled grit and rag bin Cleaned off bar screen equipment Received soda ash Added 10 bags of soda ash Hosed headworks Finished decanting and started transfers Recorded readings in SharePoint Switched WAS feed to S.T.T 2 | Keswick Water Resource Recovery Facility | 2025-10-28
WW-NORTH | October | On site for electrical pm. Completed. | Keswick Water Resource Recovery Facility | 2025-10-29
WW-NORTH | October | Started decanting S.T.Ts Turned off RAS pumps for batch wasting Collected samples for in house labs Finished decanting and transferred S.T.T 1 and 3 Batch wasted 40m3 from each clarifier (80m3 total) Checked and leveled grit and rag bin Cleaned off bar screen equipment Notice small leak on hypo tank, tightened hypo tank inlet port flange, hosed and pumped out small amount of hypo in containment Added 10 bags of soda ash to each areation tank (20 total) Winterized odour control unit Recorded readings in SharePoint Switched WAS feed to S.T.T 3 | Keswick Water Resource Recovery Facility | 2025-10-22
WW-NORTH | October | Performed station check Decanted STT 1, 2 and 3 Transferred STT 1 and 3 Completed lab analysis and entered readings into SharePoint Checked headworks building - levelled bin and cleared bar screen Added 20 bags of soda ash - Inspected inlet and outlet DO probes on Aeration tanks 1,2 and 3 (replaced air line on inlet line on aeration tank 1) - Tested gas monitors in Headworks building - Clarifier maintenance 1 -4 - Vortex pump inspections | Keswick Water Resource Recovery Facility | 2025-10-17
WW-NORTH | October | Open WAS feed to tank 1 Close tank 3 Review area SCADA | Keswick Water Resource Recovery Facility | 2025-10-25
WW-NORTH | October | Performed station check Completed lab analysis and entered readings into SharePoint Decanted STT 1 and 2 Transferred STT 1 Checked headworks - cleared bar screen and levelled bin Added 20 bags of soda ash Recorded odour control readings Inspected compressors | Keswick Water Resource Recovery Facility | 2025-10-06
WW-NORTH | October | Performed station check Decanted STT 2 and 3 Transferred STT 2 Completed lab analysis and entered readings into SharePoint Checked head works - levelled bin and cleared bar screen Collected weekly, monthly and alkalinity samples Added 20 bags of soda ash | Keswick Water Resource Recovery Facility | 2025-10-07
WW-NORTH | October | on site 0700hrs sludge handling. Decant and transfer STT3, WAS now feeding STT3 lab and readings Hypo delivery on site @0920hrs, hypo out at 1030hrs. 1010hrs opened outside hatch @ headworks for Honeywell. WIFI people working in membrane building. 1230hrs Jason Valtes on site with 3 people, climbing cell tower on site for town of Georgina future meter reader. 21 bags of soda ash added to inlet, and another 20 bags brought up and stacked at the inlet for Sunday. | Keswick Water Resource Recovery Facility | 2025-10-03
WW-NORTH | October | Performed station check Decanted STT 2 and 3 Transferred STT 2 Completed lab analysis and entered readings into SharePoint Checked head works - cleared bar screen and levelled bin Recorded Odour control unit numbers Added 20 bags of soda ash Completed assigned EZMax work orders: - Sodium Hydroxide panel Drawdown - Hypo panel Drawdown - Captor panel Drawdown | Keswick Water Resource Recovery Facility | 2025-10-02
WW-NORTH | October | Started decanting S.T.T's 2 and 3 Collected samples for YD labs Collected samples for in house labs Received load of alum Checked and leveled grit and rag bin Finished decanting and started transferring to S.H.T 3 Recorded readings in SharePoint Added 20 bags of soda ash to aeration tanks Switched WAS feed to S.T.T 3 | Keswick Water Resource Recovery Facility | 2025-10-01
WW-NORTH | October | Attended for sludge handling Decanted/transferred sludge thickening tanks Directed WAS to tank 2 Checked plant and raked headworks bin Completed soda ash addition - 20 bags. | Keswick Water Resource Recovery Facility | 2025-10-12
WW-NORTH | October | Completed scheduled work orders and notified ROC of work being completed Inspected and greased grit vortexes Inspected and greased bar screens Inspected rag and grit dewatering screws Inspected channel dewatering pump Tested headworks and odour control gas detector alarms Pumped down scum tanks Cleaned train 3 turbidimeter and returned to service. | Keswick Water Resource Recovery Facility | 2025-10-02
WW-NORTH | October | Started decant S.T.T's 1 and 2 Collected samples for in house labs Completed odour control checks Turned off RAS pumps for batch wasting Checked and leveled grit and rag bin Cleaned off bar screen equipment Finished decanting and started transfers Batch wasted 80m3 total RAS pumps back in auto Topped up Caustic tank with 6 carboys Added 20 bags of soda ash Changed membrane drain tank hi level alarm from 2.50m to 2.55m Switched WAS feed to S.T.T2 | Keswick Water Resource Recovery Facility | 2025-10-09
WW-NORTH | October | Onsite for sludge handling Begin decanting stt 2 and 3 Out to sutton Transfer stt 2 and 3 Review scada Add 18 bags of soda ash Switch WAS feed to stt 2 | Keswick Water Resource Recovery Facility | 2025-10-05
WW-NORTH | October | Started decanting S.T.T's 1 and 2 Collected samples for in house labs Checked and leveled grit and rag bin Added 20 bags of soda ash Received soda ash delivery Cleaned off bar screen equipment Finished decanting and started transfers Switched WAS feed to S.T.T 3 | Keswick Water Resource Recovery Facility | 2025-10-10
WW-NORTH | October | Completed scheduled work orders Inspected hydrochloric acid pumps Checked chlorine analyzer Tested chemical containment float alarms - in between 10:31-10:36 Replaced UV bulbs on channel 2A and ballast on rack 7 (bulb 1/2 ballast). | Keswick Water Resource Recovery Facility | 2025-10-08
WW-NORTH | October | Switched WAS to feed sludge thickening tank 3. | Keswick Water Resource Recovery Facility | 2025-10-13
WW-NORTH | October | Started decanting all S.T.T Turned RAS pumps off for batch waste Collected samples for in house labs Checked and leveled grit and rag bin Completed inspections on air compressors and air dryers in membrane room Finished decanting and started transferring Batch wasted 40 m3 from each clarifier (80m3 total) Inspected T.S.S probe Completed alum panel exercise Completed inspections on turbidimeters Entered readings in SharePoint Switched WAS feed to S.T.T 3 | Keswick Water Resource Recovery Facility | 2025-10-08
WW-NORTH | October | Switched WAS to feed sludge thickening tank 1. | Keswick Water Resource Recovery Facility | 2025-10-11
WW-NORTH | October | Performed station check Completed lab analysis and entered readings into SharePoint Decanted and transferred STT 1 and 2 - hosed down STT 1 and 2 Collected weekly samples W11294880 Checked headworks - leveled bin and cleared bar screen Added 20 bags of soda ash - Performed 6M membrane blower maintenance (replaced air filters and checked oil) - Checked sump systems - Collection box blower inspections | Keswick Water Resource Recovery Facility | 2025-10-14
WW-NORTH | October | Inspected channel aeration blowers - changed oil on both, greased, and checked filters. | Keswick Water Resource Recovery Facility | 2025-10-10
WW-NORTH | October | Received call from ROC regarding all aeration DO probes + tank 1 ammonia probe faulted and/or OOR (alarms in @ 11:23) Spoke to Arthur (PCS) regarding issue, he suggested it may be an instrument issue. AER_TK2_AIT3 did not fault but has been slowly increasing and is now maxed out. In the meantime, all alarms reset (11:41) Returned DO distribution setpoint from fixed air flow to DO air flow mode and monitored outlet DO levels. | Keswick Water Resource Recovery Facility | 2025-10-11
WW-NORTH | October | Plant checks completed Complete lab and enter data into SharePoint 20 bags of soda ash Hose head works Clean channel 2 classifier Clean and exercise UV channel 1 Clean turbidity meters Check permeability pumps Pumped out chambers Check scum ras and was pumps Sludge loading pumps Fixed roll up door 1 Oil change and filters on sludge blowers 1&2 Batch wasted into tank 1 Sludge handling completed Clean TSS meter Alum panel flush | Keswick Water Resource Recovery Facility | 2025-10-15
WW-NORTH | October | Attending site to check Dissolved O2 and Ammonium sensors (W11364718). Found Tank#2 ammonium reading was above full scale. Operations does not use these probes to control any part of the process. It is unclear if this high reading caused an error in the D.O./Ammonium transmitter. I adjusted the ammonium value from above 10.25, to 8.3mg/L, in case this was causing and issue with the controller. Review alarms on local D.O./Ammonium controller - the were many alarms related to the Tank#2 ammonium reading registering above full-scale. All alarms were acknowledged. Alarms did not return after 10 minutes. Notified Neil Ott and Kevin Kerek. | Keswick Water Resource Recovery Facility | 2025-10-14
WW-NORTH | October | Attended for site check Recorded cell levels in rounds sheet. | Holland Landing Lagoons | 2025-10-16
WW-NORTH | October | Enter levels into SharePoint Check outfall area - it is pretty overgrown | Holland Landing Lagoons | 2025-10-30
WW-NORTH | October | Lagoon check Enter levels into SharePoint | Holland Landing Lagoons | 2025-10-23
WW-NORTH | October | Drive around lagoon 1-287 2-217 3-206 4-180 Enter data into SharePoint | Holland Landing Lagoons | 2025-10-06
WW-NORTH | October | Attended for site check Recorded cell levels in rounds sheet Consultants here collecting sediment samples from lagoons. | Holland Landing Lagoons | 2025-10-01
WW-NORTH | October | Attended for scheduled work orders Notified ROC of work being completed Performed wet well entry and inspection Tested high level alarm - in @ 11:16 Exercised wet well valves Inspected channel grinder Swept in generator room. | Holland Landing Sewage Pumping Station | 2025-10-21
WW-NORTH | October | Station checks completed Enter data into SharePoint | Holland Landing Sewage Pumping Station | 2025-10-30
WW-NORTH | October | Attended for station check Recorded station readings in rounds sheet Checked dry well - p.3 running in duty Checked diesel containment pits Reviewed SCADA/trends. | Holland Landing Sewage Pumping Station | 2025-10-20
WW-NORTH | October | Station checks completed Look into heating (low temperature alarm) Enter data into SharePoint Dry well work orders completed Flood alarm RS pump inspection Check valves Sumps Air relief valve W/O created for unit heater | Holland Landing Sewage Pumping Station | 2025-10-27
WW-NORTH | October | Attended for station check Recorded station readings in rounds sheet Checked dry well - p.2 running in duty Reviewed SCADA/trends. | Holland Landing Sewage Pumping Station | 2025-10-16
WW-NORTH | October | Raw sewage pumps vibration data collection | Holland Landing Sewage Pumping Station | 2025-10-23
WW-NORTH | October | Semi annual diesel generator run with total power contractor Joint health and safety checks completed Check OCU Vacuum control area Start 273.8 Stop 274.9hr Check crane | Holland Landing Sewage Pumping Station | 2025-10-07
WW-NORTH | October | Onsite for annual calibrations Informed ROC Used cal mode on scada during the work Instruments calibrated: LITs, PITs, FITs, H2S sensors Cleared associated alarms Informed ROC, armed building and left site | Holland Landing Sewage Pumping Station | 2025-10-10
WW-NORTH | October | Onsite to check station Review scada/trends Enter data in sharepoint Clear h2s alarms | Holland Landing Sewage Pumping Station | 2025-10-03
WW-NORTH | October | Attended for station check Recorded station readings in rounds sheet Checked dry well Reviewed SCADA/trends. | Holland Landing Sewage Pumping Station | 2025-10-01
WW-NORTH | October | Attended for station check Recorded station readings in rounds sheet Checked dry well - p.3 running in duty Placed OCU back to hand Checked diesel containment pits Reviewed SCADA/trends. | Holland Landing Sewage Pumping Station | 2025-10-14
WW-NORTH | October | Station checks completed Enter data into SharePoint | Holland Landing Sewage Pumping Station | 2025-10-06
WW-NORTH | October | On site with Bill Vanbakel to investigate low coolant temp fault. Found coolant recirculation heater contactor to be faulty. Ran generator to confirm it would run and transfer with fault outstanding,all ok. Generator run warmed coolant enough to clear fault. Maintenance to check for parts and available time to repair. Made WO with PS to check one heater not working. | East Gwillimbury 2nd Concession Sewage Pumping Station | 2025-10-29
WW-NORTH | October | Station checks completed check hoist in basement not able to get working Enter data into SharePoint | East Gwillimbury 2nd Concession Sewage Pumping Station | 2025-10-23
WW-NORTH | October | On site for fuel tank vacuum low. Vacuum the tank to-20 and tagged it with the date. Cleared the alarm on scada | East Gwillimbury 2nd Concession Sewage Pumping Station | 2025-10-24
WW-NORTH | October | Station checks completed Enter data into SharePoint | East Gwillimbury 2nd Concession Sewage Pumping Station | 2025-10-30
WW-NORTH | October | Informed ROC. Onsite to perform annual calibrations. Put the devices in calibration mode. Devices were done as below: all well LITs, FITs,GEN LITs,PIT. Put everything back in service. All the related alarms were cleared. No issues. Informed ROC, armed the building and left the site. | East Gwillimbury 2nd Concession Sewage Pumping Station | 2025-10-16
WW-NORTH | October | Attended for station check Recorded station readings in rounds sheet Checked dry well Checked diesel containment pits Reviewed SCADA/trends. | East Gwillimbury 2nd Concession Sewage Pumping Station | 2025-10-20
WW-NORTH | October | Attended for scheduled work orders Notified ROC of work being completed Performed wet well entry and inspection Tested high level alarm - in @ 10:30 Exercised wet well valves Inspected channel grinder Swept office and washroom. | East Gwillimbury 2nd Concession Sewage Pumping Station | 2025-10-21
WW-NORTH | October | Attended for station check Recorded station readings in rounds sheet Checked dry well - p.3 running in duty Reviewed SCADA/trends. | East Gwillimbury 2nd Concession Sewage Pumping Station | 2025-10-16
WW-NORTH | October | Station checks completed Enter data into SharePoint | East Gwillimbury 2nd Concession Sewage Pumping Station | 2025-10-27
WW-NORTH | October | Semi annual diesel generator run and monthly diesel generator run completed Joint health and safety inspection Ocu inspection Drywell inspection Found the heat pump off on generator Check re-CERT loop | East Gwillimbury 2nd Concession Sewage Pumping Station | 2025-10-07
WW-NORTH | October | Onsite to check station Review scada/trends Could not enter data in sharepoint - page would not load. Will input data at a different location | East Gwillimbury 2nd Concession Sewage Pumping Station | 2025-10-03
WW-NORTH | October | Station checks completed Enter data into SharePoint Check diesel containment Contractor on site looking at fire hydrant | East Gwillimbury 2nd Concession Sewage Pumping Station | 2025-10-06
WW-NORTH | October | Attended for station check Recorded station readings in rounds sheet Checked dry well Reviewed SCADA/trends. | East Gwillimbury 2nd Concession Sewage Pumping Station | 2025-10-01
WW-NORTH | October | Station checks completed Enter data into SharePoint GHD on site- working on monitoring well | East Gwillimbury 2nd Concession Sewage Pumping Station | 2025-10-09
WW-NORTH | October | Station checks completed Enter data into SharePoint Turn on heaters Housekeeping work order completed | Queensville West Sewage Pumping Station | 2025-10-30
WW-NORTH | October | Attended for station check Recorded station readings in rounds sheet Checked dry well - p.2 running in duty Reviewed SCADA/trends. | Queensville West Sewage Pumping Station | 2025-10-16
WW-NORTH | October | Vacuum main level Station checks completed Enter data into SharePoint | Queensville West Sewage Pumping Station | 2025-10-23
WW-NORTH | October | Drop off cleaned OCU screen Station checks completed Enter data into SharePoint | Queensville West Sewage Pumping Station | 2025-10-27
WW-NORTH | October | Raw sewage pump vibration data collection | Queensville West Sewage Pumping Station | 2025-10-23
WW-NORTH | October | Attended for station check Recorded station readings in rounds sheet Checked dry well Checked diesel containment pits Reviewed SCADA/trends. | Queensville West Sewage Pumping Station | 2025-10-20
WW-NORTH | October | Onsite to check station/complete work orders Alert roc Review scada trends Enter data in sharepoint Diesel generator monthly test run Transfer station to diesel power at 08:50hrs JHSC hazardous waste removal Transfer station back to hydro power at 09:49hrs Clear all alarms and reset dialer. Alert roc operator work complete Contractor total power and electrical remain onsite | Queensville West Sewage Pumping Station | 2025-10-03
WW-NORTH | October | Attended for station check Recorded station readings in rounds sheet Checked dry well - p.2 running in duty Turned off exhaust fan in generator room (low temp alarm came in) Reset dry well supply/exhaust fans in MCC room Activated sump pump (start float was fully submerged in water) Consultants here for site walk through Reviewed SCADA/trends. | Queensville West Sewage Pumping Station | 2025-10-01
WW-NORTH | October | Station checks completed Enter data into SharePoint | Queensville West Sewage Pumping Station | 2025-10-06
WW-NORTH | October | Attended for station check Recorded station readings in rounds sheet Checked dry well - p.3 running in duty Checked diesel containment pits - vacuumed pit by tanks Reviewed SCADA/trends. | Queensville West Sewage Pumping Station | 2025-10-14
WW-NORTH | October | Onsite to investigate pump 3 check valve slamming. Topped up air over oil hydraulic dampener | Queensville West Sewage Pumping Station | 2025-10-06
WW-NORTH | October | Onsite responding to CMU5 11344709 15:43 dry well sump Flood alarm came in Float has been sticking - WO was created Check sump - level not flooded - looks like sump pumps engaged before coming to site. Shake float and test functionality - turns on pumps each time Run each sump pump in manual to verify operations Clear alarms | Queensville West Sewage Pumping Station | 2025-10-07
WW-NORTH | October | Attended for exhaust fan 1 uncommanded stop Reset overcurrent fault on VFD and cleared alarm on SCADA. | Morton Avenue Air Management Facility | 2025-10-27
WW-NORTH | October | Attended for station check Recorded station readings in rounds sheet Checked blower room - fan 2 running in duty (fan 1 OOS) Flushed blowdown on recirc line Drained water from temporary OCU Turned on breaker for immersion heater Reviewed SCADA/trends. | Morton Avenue Air Management Facility | 2025-10-30
WW-NORTH | October | Attended for station check Recorded station readings in rounds sheet Checked blower room - fan 2 running in duty Flushed blowdown on recirc line Performed H&S inspection Reviewed SCADA/trends. | Morton Avenue Air Management Facility | 2025-10-23
WW-NORTH | October | Attended for station check Recorded station readings in rounds sheet Checked blower room - fan 1 running in duty Flushed blowdown on recirc line Drained moisture from temporary unit Reviewed SCADA/trends. | Morton Avenue Air Management Facility | 2025-10-16
WW-NORTH | October | Attended for exhaust fan 1 uncommanded stop Found belt is okay but pressure is not building. Placed fan 2 into duty. | Morton Avenue Air Management Facility | 2025-10-28
WW-NORTH | October | Attended for station check Recorded station/monthly meter readings in rounds sheet Checked blower room - rotated fan 1 into duty Flushed blowdown on recirc line Drained water from temporary OCU Turned on breaker to control room heater Reviewed SCADA/trends. | Morton Avenue Air Management Facility | 2025-10-27
WW-NORTH | October | Attended for exhaust fan 1 uncommanded stop Reset overcurrent fault on VFD and cleared alarm on SCADA. | Morton Avenue Air Management Facility | 2025-10-28
WW-NORTH | October | Performed station check Drained temp unit Flushed blow downs Entered readings into SharePoint | Morton Avenue Air Management Facility | 2025-10-20
WW-NORTH | October | Performed station check Flushed blow down Checked temp unit Inspected Fan 1 and 2 Entered readings into SharePoint | Morton Avenue Air Management Facility | 2025-10-09
WW-NORTH | October | Attended for station check Recorded station readings in rounds sheet Checked blower room - fan 2 running in duty Flushed blowdown on recirc line Reviewed SCADA/trends. | Morton Avenue Air Management Facility | 2025-10-01
WW-NORTH | October | Checked station Viewed HMI and trends Switched to fan 1 Checked fan room area Flushed blow down Recorded readings in SharePoint | Morton Avenue Air Management Facility | 2025-10-06
WW-NORTH | October | Onsite to check station Review scada/trends Enter data in sharepoint Flush blowdown | Morton Avenue Air Management Facility | 2025-10-03
WW-NORTH | October | station checks sharepoint data entry flushed blowdown | Morton Avenue Air Management Facility | 2025-10-14
WW-NORTH | October | Onsite for daily operations Review scada/trends Collect in house lab samples No decant due to low stt level Unplug both submersibles feeding sbr 1. Level now at 4.20m Complete lab parameters for both sbr1 and 2 decants Data in sharepoint Check station Receive call from ROC regarding hihi lagoon wetwell Visually inspect wetwell level - ok. Alert TL - TL disabled hihi alarm on lagoon wetwell | Sutton Water Resource Recovery Facility | 2025-10-24
WW-NORTH | October | Onsite for daily operations Review scada/trends Collect in house lab samples No decanting due to low stt level Sbr 1 running in auto - wasting pump off. 2 submersibles and hydraulic pump feeding sbr 1 Out to stations | Sutton Water Resource Recovery Facility | 2025-10-23
WW-NORTH | October | Onsite for daily operations Review scada/trends Hydro one/ainsworth onsite for high voltage maintenance Alert roc - transfer station to diesel power at 0858hrs Clear alarms Collect in house lab samples Begin filling sbr1 with decanted water from EQ to test diffusers. Two submersibles and one hydraulic pump feeding sbr1 Test Was pump in sbr1 - confirmed 10.5L/s High voltage maintenance complete - transfer station back to hydro power at 14:40hrs | Sutton Water Resource Recovery Facility | 2025-10-22
WW-NORTH | October | Onsite for daily operations Review scada/trends No decant due to low stt Collect in house lab samples Check station Rake/clear rags from barscreen Clear rags on sbr inlet stems Septage haulage system back online Lab parameters back in optimal range. Place all UV?s back in auto 11:30hrs divert EQ tank from lagoon back to filters. Check Filters - ok Reset effluent sampler Remove submersible pumps from SBR catwalks | Sutton Water Resource Recovery Facility | 2025-10-27
WW-NORTH | October | On site to assist Ainsworth with high voltage PM. Also confirmed proper pump rotation and flow for WAS pump 1 with operations. Removed lockout, WAS pump 1 is back in service. | Sutton Water Resource Recovery Facility | 2025-10-22
WW-NORTH | October | Onsite for daily operations Review scada/trends No decant Collect in house lab samples Remove hydraulic pump, unplug and roll up hoses Check station Rake barscreen Check filters - ok Complete lab Enter data in sharepoint Lagoon pumps running from 0700hrs to 13:00hrs | Sutton Water Resource Recovery Facility | 2025-10-29
WW-NORTH | October | sludge handling. Load out station checks lab and reading stopped feeding lagoons after warming up UV's at 1040hrs. Plant now going through filters. Pulled and fixed air lift ( 1- f2 ) found 5 leaks on diffusers for SBR1. placed 2 submersibles in tank to pump down . hydraulic pump wouldn't start, maintenance replaced battery. screen brush put back in service. | Sutton Water Resource Recovery Facility | 2025-10-20
WW-NORTH | October | Made several changes to septage receiving tank to accommodate new septage receiving operational strategy Septage receiving setpoints Min flow from 8 to 0l/s Run time 6 to 3min Pump start 1.0 to 0.6m Pump stop 0.7 to 0.5 Hauled waste tank level HiHi level 3.0 to 4.15m Hi level 2.9 to 4.0m Lo level 0.5 to 0.4m LoLo level 0.4 to 0.2m | Sutton Water Resource Recovery Facility | 2025-10-24
WW-NORTH | October | increased lagoon pumping time back to plant from 0700 -1300 to 0700-1900 | Sutton Water Resource Recovery Facility | 2025-10-31
WW-NORTH | October | Repaired the defusers and installed a new was pump | Sutton Water Resource Recovery Facility | 2025-10-17
WW-NORTH | October | station checks sludge handling, load out lab and readings, entered into sharepoint. Assisted maintenance with Diffusers and WAS pump. GFL done cleaning SBR1 Air compressors inspection chemical pumps inspection UV inspection DO maintenance | Sutton Water Resource Recovery Facility | 2025-10-17
WW-NORTH | October | Onsite for daily operations Review scada/trends Collect in house lab samples Complete lab Enter data in sharepoint Collect weekly regulatory samples Check filters - ok Check station Clean up sbr catwalk Swap out headworks bin Place lagoon pumps in auto to run from 0700hrs to 1300hrs | Sutton Water Resource Recovery Facility | 2025-10-28
WW-NORTH | October | Turned WAS pump on SBR 2 in manual to build solids | Sutton Water Resource Recovery Facility | 2025-10-23
WW-NORTH | October | Onsite for daily operations Allow Accuworx access to continue sbr1 maintenance Review scada/trends No decant - stt at 1.61m Collect in house lab samples Complete lab Enter data in sharepoint Check station C Balmer and M Balmer onsite for sbr1 diffuser inspections and maintenance Skim debris off top of sbr 2 | Sutton Water Resource Recovery Facility | 2025-10-16
WW-NORTH | October | On site to wire new WAS pump #1. Wired pump. Unable to check rotation of pump motor until Basin is filled again. MCC disconnect for WAS pump 1 left locked out with electrical lock. | Sutton Water Resource Recovery Facility | 2025-10-21
WW-NORTH | October | Performed Sludge transfer Running 2 submersible pumps from the EQ tank to SBR1 | Sutton Water Resource Recovery Facility | 2025-10-19
WW-NORTH | October | On site to investigate bar screen wash motor found overload tripped reset and retort conductor screws Channel one we gate issue still unresolved put a call into Trojan tech-support to understand why the weird gate is beating bounced open to 4% tried adjusting some points. Nothing would change the outcome of the position. | Sutton Water Resource Recovery Facility | 2025-10-02
WW-NORTH | October | On site to install barscreen brush motor. | Sutton Water Resource Recovery Facility | 2025-10-02
WW-NORTH | October | SBR 2 has been emptied Hose diffusers that are leaking Worked with maintenance on locating the leaking areas. Found and fixed Replace all victolic couplings on SBR 2 WAS line Test WAS line and no leaks detected flow 9.9 L/S Decant and transfer sludge load GFL removed load EQ flow going to lagoon. Lower WAS flow rate on SBR 1 Start pumping down SBR 1 Slowly introduce raw flow from wood river SPS while other side is transferring Flush EQ line while no flow going through UVs back in auto Maintenance mode has been disabled on SBR 2 SBR 2 decant arm back in auto Maintenance mode | Sutton Water Resource Recovery Facility | 2025-10-03
WW-NORTH | October | On site to adjust air valve for SBR 2. The valve is holding but I believe the issue is the purge valve being plugged | Sutton Water Resource Recovery Facility | 2025-10-08
WW-NORTH | October | on site 0800hrs sludge handling, no load today. Transferred from SHT to STT. 1 GFL truck on arrival, the rest came shortly after. Maintenance on site for WAS pump work. SBR2 in maintenance mode @ 0952hrs for WAS line work in EQ tank. 1041hrs SBR2 out of maintenance mode. Reset time line on SBR2, after cycling and clearing alarm on Decanter. Assisted Maintenance with septage mixer, SBR2 purge valve function investigation, and SBR1 WAS line Victaulic coupler install. | Sutton Water Resource Recovery Facility | 2025-10-09
WW-NORTH | October | Onsite for daily operations Review scada/trends Remotely turn on eq pump 1 to pump down eq tank before decant cycle. Stop pump at 0.05m Try to decant sHT - level to low still. Place SHT blowers back in auto Collect in house lab samples Complete partial lab Accuworx onsite again for SBR 1 cleaning Enter lab data in sharepoint | Sutton Water Resource Recovery Facility | 2025-10-08
WW-NORTH | October | Onsite to insoect pumps and tank levels Unplug all 3 submersible pumps and both hydraulic pumps. Fill both hydraulic pumps with gas. Old gydraulic pump problematic - cannot start it. 6? pump still running good. Test manual aeration function for both SBR?s Will be alerting control panel every hour on the hour for 20 mins aerate tanks 1 and 2 manually until level in sbr2 increases. Turn off generator for the night Running on 3 submersibles and 1 hydraulic pump | Sutton Water Resource Recovery Facility | 2025-10-03
WW-NORTH | October | Onsite for daily operations Review scada/trends Collect sbr2 sample on first air cycle Collect weekly regulatory raw samples Collect monthly raw alkalinity sample Collect monthly sludge sample Alert ROC Diesel test run - transfer station to diesel power at 11:58hrs Enter data in sharepoint Transfer station back to hydro power at 13:02hrs Muffin monster inspection Decant arms maintenance Grit auger and dewatering auger inspection Pump down EQ tank OCU Inspection | Sutton Water Resource Recovery Facility | 2025-10-07
WW-NORTH | October | Monitor scada remotely to check SBR level with both pumping stations on and DO levels in sbr2. Sbr 2 at 4.65m and DO at 3.66ppm. No air cycle has been called for due to sufficient DO level but sequences are cycling as they should. WAS cycle completed Due to hihi being 4.95m and current SBR level, divert both pumping stations to lagoon. High street diverted at 20:08hrs Woodriver diverted at 20:04hrs | Sutton Water Resource Recovery Facility | 2025-10-04
WW-NORTH | October | Changed blower duty 2 on delay from 7 minutes to 1 minute | Sutton Water Resource Recovery Facility | 2025-10-08
WW-NORTH | October | Back onsite to inspect tank levels/ unplug pumps and refill gas for hydraulic pump Unplug all pumps. Sbr level 1 to low for current level of pumps. Sbr 2 now at 3.83m - DO probe submerged and active. Alert roc no more manual aeration required for either tank. Place sbr 1 in maintenance mode Take sbr 2 out of maintenance mode Place sbr 2 was in auto. Place sbr 2 decant arm in local off to allow level to build. Divert high st ps back to plant at 14:52hrs Change WAS setpoints for sbr 2 from 600s down to 500s Change sbr common setpoint for duty 2 on delay time from 1min back to 7mins After noticing percentage of cycle was not increasing for sbr 2 but was for sbr 1. Call oncall pcs Artour L to discuss. Found that due to decant arm being in local the sequence wont work because the arm needs to be in auto. No air needed for sbr1 - put air valve for sbr 1 in manual off, decant arm in local, and sbr1 not on maintenance mode - no sequence will commence in sbr1 due to these settings. Sbr 2 back in maintenance mode as decant arm being in local off will not allow auto program to function. Once sbr2 back in maintenance mode, percentage of sequence began counting. Sbr 2 air valve in auto, was pump in auto decant arm in local off. EQ tank still being diverted to lagoon Will monitor scada remotely and return tomorrow to continue work Change Barscreen rest time from 15mins back to 5 mins now that all pumping stations are going to plant | Sutton Water Resource Recovery Facility | 2025-10-04
WW-NORTH | October | Onsite for sludge handling Lower stt gate No transfer due to low sht level Inspect sbr levels Complete lab on sbr 2 parameters Will return Back onsite Place decant arm for sbr 2 in auto. Reset basin time and take sbr2 out of maintenance mode Phone oncall PCS Artour L and request the settle cycle be skipped (already settled and reset during decant cycle) and go straight to the decant cycle before bringing pumping stations back to the plant Monitor decant cycle Plug in 2 submersible pumps feeding EQ tank to lower sbr1 Divert WRB back to plant at 13:16hrs EQ filter feed diverted to lagoon. Set manual speed on both pumps to 50% Divert HS back to plant at 13:18hrs | Sutton Water Resource Recovery Facility | 2025-10-05
WW-NORTH | October | Onsite for daily operations Allow access for GFL - 1 Vac truck on-site.for now Review scada/trends Find stt level at 2.64m after yesterdays transfer - gate not holding - transfer after gfl load Sht blowers off to decant Sht blowers back in auto after decant Use filter feed p1 to pump down EQ tank Hose EQ to try and move some sediment towards pumps to flush Collect in house lab samples Complete lab Enter data in sharepoint Use skimmer to pull material off the top of sbr2 | Sutton Water Resource Recovery Facility | 2025-10-10
WW-NORTH | October | Onsite for daily operations Review scada/trends Electrical onsite working on UV system Pull all submersible pumps and unplug to continue seeding SBR2 Once UV?s back to normal operations, open SBR 2 inlet gate. As SBR2 level rises, test WAS pump 2 and find the WAS line leaking at coupling into EQ tank. Immediately turn off WAS, close SBR2 inlet. Divert WRB to lagoon at 11:38hrs Divert HS to lagoon at 11:44hrs Divert EQ tank to lagoon at 11:42hrs Switch all submersible pumps to pump from SBR 2 into SBR1 Found leaks in diffusers center and closer to the was pump in sbr 2. Tested was pump 2 and there is flow Raise barscreen rest time from 5 to 15 minutes and turn off brush motor as there is a knocking noise while running - alerted Maintenance | Sutton Water Resource Recovery Facility | 2025-10-02
WW-NORTH | October | On site to test septage tank mixer rotation. Mixer is ready to go back in service. Left MCC mixer disconnect in off position until septage system is back in service. Informed operator on site. | Sutton Water Resource Recovery Facility | 2025-10-10
WW-NORTH | October | Attended for sludge handling Initiated transfer from sludge holding tank as sludge thickening tank was at 1.68 m upon arrival Lowered gate part way and raised to see if it would hold any better Checked plant and cleaned rags around bar screen. | Sutton Water Resource Recovery Facility | 2025-10-12
WW-NORTH | October | Onsite for daily operations Allow access for accuworx to continue cleaning sbr1 Review scada/trends Decant stt - no transfer due to low SHT level Collect in house lab samples Complete lab Enter data in sharepoint Check station Skim rags/debris off top of sbr 2 Pump down EQ tank after each decant cycle to help flush EQ tank to lagoon Replace intake filters on SBR blowers and on Sludge holding blowers | Sutton Water Resource Recovery Facility | 2025-10-15
WW-NORTH | October | Onsite to unplug pumps inspect tank levels Turn on generator and start 6? pump. Unplug all 3 submersibles and lower the level they are sitting. Unplug hydraulic pump and lower it into inlet side of sbr. 6? pump not producing any flow - pinch points and head pressure to great. Turn off pump and turn off generator. Will return later | Sutton Water Resource Recovery Facility | 2025-10-04
WW-NORTH | October | Onsite for daily operations Review scada/trends Gfl onsite to begin tank 1 maintenance Maintenance onsite to remove 6? pump and remove the generator. Remove hydraulic pumps from sbr1 Plug in 2 submersible pumps feeding eq tank to help lower sbr level. Turn on WAS pump in SBR 1 to help lower level - feeding SHT Place all four UV banks in local off causing major/critical alarms. EQ tank being diverted to lagoon Place SHT blowers in manual off to decant holding tank tomorrow Collect SBR2 decant sample during decant cycle Collect MLSS during first air cycle | Sutton Water Resource Recovery Facility | 2025-10-06
WW-NORTH | October | Log on Scada to check/monitor DO levels in SBR1 Watched as Blower 1 and 3 ran in duty. Blower 3 came on as DO hit 2.00mg/L, second blower followed Check trends and verify D.O levels have been fluctuating | Sutton Water Resource Recovery Facility | 2025-10-02
WW-NORTH | October | Divert flow to lagoon to allow work on syphon tower and remove latter Wessuc vac syphon and continue to clean septage tank Fix cracked air diffusers is SBR 2 Replace WAS line Victolic coupling Complete lab YD samples taken to HWP After air diffusers were fixed started filling from SBR 1. Flow going to lagoon while transferring over to tank 2 Lower part of ladder removed form inlet tower Received Alum delivery | Sutton Water Resource Recovery Facility | 2025-10-01
WW-NORTH | October | Under the direction of Kevin Kerek, modified the PAC program for Raw Sewage Pump 4. When pump 4 is called to run on duty 1 in auto, pump 4 will run 100 % for 2 min to remove any clogging. After 2 minutes timer, if pump 4 flow meter has low flow alarm or pump efficiency is low then keep running pump 4 to 100% speed until it generates flow. If there is no flow or efficiency alarm after the start up then, continue running pump at calculated speed based on Level. | Keswick Sewage Pumping Station | 2025-10-16
WW-NORTH | October | Pump 1 low flow. ran pump at 100% several times now 207l/s put pump 1 back into duty rotation and running duty 1 | Keswick Sewage Pumping Station | 2025-10-26
WW-NORTH | October | Checked station Viewed HMI and trends Checked dry well area Recorded readings in SharePoint | Keswick Sewage Pumping Station | 2025-10-20
WW-NORTH | October | Attended for station check Recorded station readings in rounds sheet Checked dry well Checked generator building Reviewed SCADA/trends. | Keswick Sewage Pumping Station | 2025-10-30
WW-NORTH | October | House keeping work order completed | Keswick Sewage Pumping Station | 2025-10-28
WW-NORTH | October | Wet well entry Test high level floats Exercise gate valves Grease channel grinders | Keswick Sewage Pumping Station | 2025-10-22
WW-NORTH | October | Attended for station check Recorded station/monthly meter readings in rounds sheet Checked dry well - p.1 running in duty Checked generator building Reviewed SCADA/trends. | Keswick Sewage Pumping Station | 2025-10-27
WW-NORTH | October | Pump 3 was left in manual speed at 40%, changed to auto speed | Keswick Sewage Pumping Station | 2025-10-28
WW-NORTH | October | on site to respond to pump VFD faults all pumps pump 1 running in back up. wetwell fans and odour control VFDs also tripped. site had a power fail and generator was running before i got to site. reset VFDs and back up pump 1 duty 1 running at 0% 95.7l/s | Keswick Sewage Pumping Station | 2025-10-27
WW-NORTH | October | Attended for station check Recorded station readings in rounds sheet Checked dry well - p.1 running in duty Checked generator building Reviewed SCADA/trends. | Keswick Sewage Pumping Station | 2025-10-23
WW-NORTH | October | Attended for station check Recorded station readings in rounds sheet Checked dry well - p.4 running in duty Checked generator building Turned on boiler and heater in mechanical room Reviewed SCADA/trends - p.1 low flow (00:29), ran @ 100% and got 200 L/s. | Keswick Sewage Pumping Station | 2025-10-16
WW-NORTH | October | On site to pull blockage from pump #4 Locked out pump #4 Pull large rage from bottom port of pump Ran pump in manual @ 100% with a flow of 209L/s Pump 4 back in auto | Keswick Sewage Pumping Station | 2025-10-14
WW-NORTH | October | Attended for station check Recorded station readings in rounds sheet Checked dry well - p.2 running in duty Checked generator building Reviewed SCADA/trends. | Keswick Sewage Pumping Station | 2025-10-01
WW-NORTH | October | Attended for scheduled work orders Notified ROC of incoming alarms Performed H&S inspection Performed standby generator test run and recorded readings in rounds sheet Start: 66:48 h Stop: 68:00 h Run time: 1:12 h Inspected odour control unit and heat trace system Inspected building hoists? Performed dry well inspection including the following related tests Inspected sump pit and tested high level alarm - in @ 9:39 Tested dry well flood alarm - in @ 9:48 (10 min delay) Inspected sewage pumps and recorded flows @ 100% speed - p.1: 202 L/s, p.2: 212 L/s, p.3: 212 L/s, p.4: 210 L/s Inspected check valves Inspected air relief valves Tested high temp alarm - in @ 10:20 (10 min delay) Tested dialer - ROC advised they did not receive any alarms. | Keswick Sewage Pumping Station | 2025-10-07
WW-NORTH | October | Changed pump duty rotate from 1 hr to all stop | Keswick Sewage Pumping Station | 2025-10-10
WW-NORTH | October | Placed odour control room exhaust fan in manual off due to low temperature. | Keswick Sewage Pumping Station | 2025-10-10
WW-NORTH | October | Checked station Viewed HMI and trends Checked dry well area Recorded readings in SharePoint | Keswick Sewage Pumping Station | 2025-10-06
WW-NORTH | October | Performed station check Entered readings into SharePoint | Keswick Sewage Pumping Station | 2025-10-09
WW-NORTH | October | Checked station Viewed HMI and trends Checked dry well area Recorded readings in SharePoint | Keswick Sewage Pumping Station | 2025-10-14
WW-NORTH | October | station checks sharepoint data entry | Sutton Woodriver Bend Sewage Pumping Station | 2025-10-20
WW-NORTH | October | station checks sharepoint data entry | Sutton Woodriver Bend Sewage Pumping Station | 2025-10-16
WW-NORTH | October | On site to look at pumps general inspection of wet well pumps were recently pulled, flow rates good all looks fine | Sutton Woodriver Bend Sewage Pumping Station | 2025-10-23
WW-NORTH | October | Onsite for wetwell entry to test high wetwell level Alert roc Tip wetwell high level float Alarm came in on dialer at approximately 11:48hrs Confirm with roc Reset/arm dialer | Sutton Woodriver Bend Sewage Pumping Station | 2025-10-29
WW-NORTH | October | Onsite to check station Review scada/trends Enter data in sharepoint Dialer system was active on arrival - power button flashing Confirm with ROC alarms received were low battery. Arm dialer - check scada for any UPS/power supply alarms - all ok. At time of station check, no power/battery issues with dailer system. Roc will call if any dialer alarms come in today | Sutton Woodriver Bend Sewage Pumping Station | 2025-10-27
WW-NORTH | October | On site for Pump PM. Completed. No issues to report. | Sutton Woodriver Bend Sewage Pumping Station | 2025-10-23
WW-NORTH | October | station checks sharepoint data entry | Sutton Woodriver Bend Sewage Pumping Station | 2025-10-06
WW-NORTH | October | generator test run health and safety check | Sutton Woodriver Bend Sewage Pumping Station | 2025-10-08
WW-NORTH | October | Attended for station check Recorded station readings in rounds sheet Checked generator enclosure Reviewed SCADA/trends. | Sutton Woodriver Bend Sewage Pumping Station | 2025-10-03
WW-NORTH | October | station checks met Hazard assessment person on site. sharepoint data entry | Sutton Woodriver Bend Sewage Pumping Station | 2025-10-14
WW-NORTH | October | Onsite to check station Review scada/trends Enter data in sharepoint | Sutton Woodriver Bend Sewage Pumping Station | 2025-10-09
WW-NORTH | October | On site to meet contractor to take samples to check for asbestos | Sutton Woodriver Bend Sewage Pumping Station | 2025-10-14
WW-NORTH | October | Onsite to enter wetwell and tip hi wetwell float Alert roc Tip wetwell float General alarm came in on local OIT as general alarm - roc did not receive Will alert TL | Sutton South River Sewage Pumping Station | 2025-10-29
WW-NORTH | October | Onsite to check station Enter data in sharepoint Hatches secure | Sutton South River Sewage Pumping Station | 2025-10-23
WW-NORTH | October | station checks sharepoint data entry | Sutton South River Sewage Pumping Station | 2025-10-20
WW-NORTH | October | On site to conduct pump pms. | Sutton South River Sewage Pumping Station | 2025-10-23
WW-NORTH | October | station checks sharepoint data entry | Sutton South River Sewage Pumping Station | 2025-10-30
WW-NORTH | October | Onsite to check station Enter data in sharepoint Hatches secure | Sutton South River Sewage Pumping Station | 2025-10-27
WW-NORTH | October | station checks hi/low temp alarm test, confirmed with CPO Angelica. sharepoint data entry | Sutton South River Sewage Pumping Station | 2025-10-16
WW-NORTH | October | health and safety | Sutton South River Sewage Pumping Station | 2025-10-08
WW-NORTH | October | station checks sharepoint data entry | Sutton South River Sewage Pumping Station | 2025-10-06
WW-NORTH | October | Running south river diesel located at sutton wrrf. Diesel technician advised generator should not be ran for longer than 15 minutes when not under load. Diesel data in sharepoint | Sutton South River Sewage Pumping Station | 2025-10-07
WW-NORTH | October | Attended for station check Recorded station readings in rounds sheet Reviewed SCADA. | Sutton South River Sewage Pumping Station | 2025-10-03
WW-NORTH | October | Onsite to check station Enter data in sharepoint | Sutton South River Sewage Pumping Station | 2025-10-09
WW-NORTH | October | station checks | Sutton South River Sewage Pumping Station | 2025-10-14
WW-NORTH | October | Onsite to check station Review scada/trends Enter data in sharepoint Check pump house | Sutton High Street Sewage Pumping Station | 2025-10-27
WW-NORTH | October | station checks sharepoint data entry | Sutton High Street Sewage Pumping Station | 2025-10-16
WW-NORTH | October | station checks sharepoint data entry | Sutton High Street Sewage Pumping Station | 2025-10-30
WW-NORTH | October | Onsite for wetwell entry to test high wetwell float Alert roc Alarm came in on dialer at approximately 11:18hrs Reset/arm dialer | Sutton High Street Sewage Pumping Station | 2025-10-29
WW-NORTH | October | Onsite to gather raw sewage pump vibration data. Turned on heater in pump room | Sutton High Street Sewage Pumping Station | 2025-10-23
WW-NORTH | October | Onsite to check station Review scada/trends Enter data in sharepoint Check pump house | Sutton High Street Sewage Pumping Station | 2025-10-23
WW-NORTH | October | on site for pump testing. 1115hrs opened valve from High street to lagoon 1117hrs pump 1 @ 100% , 128.5 l/s 1119hrs pump 2 @ 100% , 110 l/s 1146hrs both pumps @ 100% , 138 l/s 1151hrs closed valve from High street to lagoon. | Sutton High Street Sewage Pumping Station | 2025-10-22
WW-NORTH | October | On site with contractor to take samples for asbestos | Sutton High Street Sewage Pumping Station | 2025-10-14
WW-NORTH | October | station checks sharepoint data entry | Sutton High Street Sewage Pumping Station | 2025-10-06
WW-NORTH | October | Onsite to check station Review scada/trends Enter data in sharepoint Check pump house | Sutton High Street Sewage Pumping Station | 2025-10-09
WW-NORTH | October | generator test run health and safety valve exercise high/low temp alarm test, on scada @ 1328hrs | Sutton High Street Sewage Pumping Station | 2025-10-06
WW-NORTH | October | Attended for station check Recorded station readings in rounds sheet Checked pump house - p.1 running in duty Reviewed SCADA/trends. | Sutton High Street Sewage Pumping Station | 2025-10-03
WW-NORTH | October | station checks sharepoint data entry pump test on 1 @100% 115.7 l/s 2 @100% 98.2 l/s both@100% 123.9l/s | Sutton High Street Sewage Pumping Station | 2025-10-14
WW-NORTH | October | Attended for station check Recorded station readings in rounds sheet Checked dry well - p.1 running in duty Checked temporary generator Contractors here working on TSSA upgrades Reviewed SCADA/trends. | Keswick Joe Dales Sewage Pumping Station | 2025-10-30
WW-NORTH | October | Attended for station check Recorded station readings in rounds sheet Checked dry well Checked temporary generator AB contractors here installing new fuel tanks Reviewed SCADA/trends. | Keswick Joe Dales Sewage Pumping Station | 2025-10-16
WW-NORTH | October | On site to conduct pump pm?s | Keswick Joe Dales Sewage Pumping Station | 2025-10-24
WW-NORTH | October | Cleaning work order completed Ferguson electric on site working on TSSA upgrades | Keswick Joe Dales Sewage Pumping Station | 2025-10-28
WW-NORTH | October | Attended for station check Recorded station readings in rounds sheet Checked dry well Checked temporary generator Inspected hoist Reviewed SCADA/trends. | Keswick Joe Dales Sewage Pumping Station | 2025-10-20
WW-NORTH | October | Attended for station check Recorded station/monthly meter readings in rounds sheet Checked temporary generator Ferguson electric on premisis Reviewed SCADA/trends Completed scheduled work orders and notified ROC of work being completed Performed dry well inspection Tested building low temp alarm - in @ 8:51 Hosed sump pit and tested high level alarm - in @ 9:01 Inspected sewage pumps and recorded flows - p.1: 50 L/s, p.2: 54 L/s, p.3: 50 L/s Inspected check valves Inspected air relief valve Exercised dry well valves Tested dialer - ROC confirmed alarm. | Keswick Joe Dales Sewage Pumping Station | 2025-10-27
WW-NORTH | October | Went well, entry test, high-level floats, exercise, gait valves, visual inspection of grinder | Keswick Joe Dales Sewage Pumping Station | 2025-10-22
WW-NORTH | October | Attended for station check Recorded station readings in rounds sheet Checked dry well - p.3 running in duty Checked temporary generator Reviewed SCADA/trends. | Keswick Joe Dales Sewage Pumping Station | 2025-10-23
WW-NORTH | October | Attended for scheduled work orders Notified ROC of incoming alarms Performed H&S inspection Performed standby generator test run and recorded readings in rounds sheet **Monthly test performed with temporary standby generator** Start: 16295:45 h Stop: 16296:58 h Run time: 1:13 h Ran sewage p.1 on generator power Checked permanent generator heat exchanger Checked for hazardous waste - none. | Keswick Joe Dales Sewage Pumping Station | 2025-10-08
WW-NORTH | October | Onsite responding to grinder fault Receive call 15:19hrs from ROC regarding faulted channel grinder Put grinder in local off/ reset alarms Place grinder back in auto - will monitor Grinder back to normal operationp | Keswick Joe Dales Sewage Pumping Station | 2025-10-02
WW-NORTH | October | Checked station Viewed HMI and trends Checked dry well area Recorded readings in SharePoint | Keswick Joe Dales Sewage Pumping Station | 2025-10-14
WW-NORTH | October | Attended for station check Recorded station readings in rounds sheet Checked dry well - p.1 running in duty Checked temporary generator Greater Toronto Fire Protection was here for inspections Reviewed SCADA/trends. | Keswick Joe Dales Sewage Pumping Station | 2025-10-01
WW-NORTH | October | Onsite to check station Review scada/trends Enter data in sharepont | Keswick Joe Dales Sewage Pumping Station | 2025-10-03
WW-NORTH | October | Checked station Viewed HMI and trends Checked dry well area Recorded readings in SharePoint | Keswick Joe Dales Sewage Pumping Station | 2025-10-06
WW-NORTH | October | On site to check odour control unit fault. Found overload tripped. Reset. Checked power, wiring, metered motor. All ok. Reset and ran unit. Monitored running current. Ok. Left unit running in auto. Cause of trip unknown. Could not recreate problem. | Keswick Joe Dales Sewage Pumping Station | 2025-10-06
WW-NORTH | October | Attended for channel grinder fault Reset and grinder ran Ferguson Electric here working on TSSA upgrades Checked OCU high differential pressure alarm - will need to return with clean mist eliminator Returned with clean filter and removed spare for cleaning Notified ROC that site is back to normal. | Keswick Joe Dales Sewage Pumping Station | 2025-10-07
WW-NORTH | October | Checked station Viewed HMI and trends Checked dry well area Checked and cleaned off bar screen equipment Recorded readings in SharePoint | Georgina No. 4 Sewage Pumping Station | 2025-10-20
WW-NORTH | October | Attended for station check Recorded station/monthly meter readings in rounds sheet Checked dry well - p.1 running in duty Ran bar screen/dewatering screw Turned on unit heater breakers Reviewed SCADA/trends. | Georgina No. 4 Sewage Pumping Station | 2025-10-27
WW-NORTH | October | Attended for station check Recorded station readings in rounds sheet Checked dry well - p.3 running in duty Hosed bar screen/dewatering screw Reviewed SCADA/trends. | Georgina No. 4 Sewage Pumping Station | 2025-10-23
WW-NORTH | October | Onsite for pump vibration data collection. | Georgina No. 4 Sewage Pumping Station | 2025-10-23
WW-NORTH | October | station checks | Georgina No. 4 Sewage Pumping Station | 2025-10-16
WW-NORTH | October | Informed ROC. Performed annual calibration and put instruments in Cal mode while doing the tasks. Devices done were FIT, PITs, LITs and gas sensors. All alarms were cleared after the job. No other issues encountered. | Georgina No. 4 Sewage Pumping Station | 2025-10-31
WW-NORTH | October | Attended for station check Recorded station readings in rounds sheet Checked dry well - p.2 running in duty Hosed bar screen/dewatering screw and topped up drip oil reservoir Reviewed SCADA/trends. | Georgina No. 4 Sewage Pumping Station | 2025-10-30
WW-NORTH | October | Attended for scheduled work orders Notified ROC of work being completed Performed wet well inspection Tested wet well high level alarm - in @ 13:27 Exercised wet well valves Greased bar screen and hosed screw press Hosed screen room floor. | Georgina No. 4 Sewage Pumping Station | 2025-10-29
WW-NORTH | October | Attended for station check Recorded station readings in rounds sheet Ran bar screen/dewatering screw Reviewed SCADA/trends Completed scheduled work orders and notified ROC of work being completed Performed H&S inspection Performed standby generator test run and recorded readings in rounds sheet Start: 499.6 h Stop: 500.7 h Run time: 1.1 h Tested diesel containment flood alarm - in @ 11:11 Inspected hoist Inspected and greased OCU Inspected air handling units Performed dry well inspection Inspected sump pit and tested building flood alarm - in @ 11:23 Tested dry well flood alarm - in @ 11:23 Inspected sewage pumps and recorded flows @ 100% speed - p.1: 100 L/s, p.2: 104 L/s, p.3: 106 L/s Inspected check valves Inspected air relief valves Tested dialer - ROC confirmed alarms Tested generator room high temp alarm - in @ 11:38 Checked for hazardous waste - none. | Georgina No. 4 Sewage Pumping Station | 2025-10-09
WW-NORTH | October | station checks sharepoint data entry put bin out | Georgina No. 4 Sewage Pumping Station | 2025-10-06
WW-NORTH | October | station checks sharepoint data entry | Georgina No. 4 Sewage Pumping Station | 2025-10-14
WW-NORTH | October | Attended for station check Recorded station readings in rounds sheet Checked dry well - p.2 running in duty Ran bar screen/dewatering screw Reviewed SCADA/trends. | Georgina No. 4 Sewage Pumping Station | 2025-10-01
WEST | October | -on site to complete station check -system duty active -checked equipment -reviewed trends -recorded readings in PWQ sheet -verified chlorine analyzers: 12:02 - Analyzer readings: Free Chlorine = 0.06 mg/L Total Chlorine = 1.77 mg/L 12:02 - Grabs: Free Chlorine = 0.03 mg/L Total Chlorine = 1.65/1.63/1.66 mg/L 12:11 - adjusted total chlorine analyzer to 1.65 mg/L based on average of 3 grabs -no other issues found | Woodbridge East Booster Pumping Station | 2025-10-31
WEST | October | Onsite for station check Duty active Checked residuals mg/L @12:16 Total analyzer 1.58 grab 1.49 Free analyzer 0.06 grab 0.03 | Woodbridge East Booster Pumping Station | 2025-10-16
WEST | October | Station check (no issues found) Input data to PWQ 11:20 Verified Depolox (mg/L) Free: Grab 0.05, A 0.06 Total: Grab 1.42, A 1.48 | Woodbridge East Booster Pumping Station | 2025-10-21
WEST | October | On site for station check. Pumps in auto Verified analyzer readings Free 0.08mg/L Total 1.63mg/L Grab Free 0.06mg/L Total 1.62mg/L Hoist and dehumidifier inspection - all okay No issues on site | Woodbridge East Booster Pumping Station | 2025-10-10
WEST | October | -on site to complete station check and complete work orders -informed ROC of work -activated system duty for station check -checked equipment -reviewed trends -recorded readings in PWQ sheet -verified chlorine analyzers: 11:43 - Analyzer readings: Free Chlorine = 0.06 mg/L Total Chlorine = 1.57 mg/L 11:43 - Grabs: Free Chlorine = 0.03 mg/L Total Chlorine = 1.52 mg/L -no issues found -completed Siemens Depolox 5 Chlorine Analyzer Maintenance -completed JHSC Health and Safety Inspection -completed Low Temperature Alarm, Test -completed Sump Pit System, Inspection -completed Flood Alarm, Test: -flood alarm not triggered, work order for CMS already created -completed Pump & Motor, Inspection -completed Check Valve Service & Inspection -no issues, site back to normal operation | Woodbridge East Booster Pumping Station | 2025-10-03
WEST | October | -On-site to complete station check and collect samples -system duty not active -checked equipment -reviewed trends 12:57 - collected grab sample: Free Chlorine = 0.04 mg/L Total Chlorine = 1.62 mg/L 13:01 - collected weekly regulatory micro. sample - W/O # W11376186 -collected quarter #4 samples - W/O # W11247754 SL1000 readings: MCL = 1.48 mg/L TNH3 = 0.40 mg/L FNH3 = 0.11 mg/L NO2 = 0.000 mg/L temp = 13.5 C -recorded readings in PWQ sheet -no issues found | Woodbridge East Elevated Tank | 2025-10-29
WEST | October | -On-site to complete station check and collect sample -system duty not active, tower = 65% -checked equipment -reviewed trends 11:07 - collected grab sample: Free Chlorine = 0.02 mg/L Total Chlorine = 1.65 mg/L 11:11 - collected weekly regulatory micro. sample - W/O # W11316454 SL1000 readings: MCL = 1.45 mg/L TNH3 = 0.41 mg/L FNH3 = 0.13 mg/L NO2 = 0.000 mg/L temp = 16.7 C -recorded readings in PWQ sheet -no issues found | Woodbridge East Elevated Tank | 2025-10-22
WEST | October | -onsite to complete work orders -completed Actuated Valve, Exercise & Inspection -completed Dehumidifier, Inspection & Cleaning -completed Sump Pit System, Inspection -completed Low Temperature Alarm, Test -completed Inlet/Outlet Heat Trace System, Inspection -completed Portable Gasoline Generator, Test -site back to normal operation | Woodbridge East Elevated Tank | 2025-10-16
WEST | October | Onsite for station check and to collect weekly micro sample W11278701 Tower draining Checked residuals mg/l @1100 Total grab 1.49 Free grab 0.01 Sl1000 Mcl 1.40 F nh3 0.14 T nh3 0.40 No2 0.000 Temp 17.9C | Woodbridge East Elevated Tank | 2025-10-08
WEST | October | -On-site to complete station check and collect sample -system duty not active, tower = 66 % -checked equipment -reviewed trends 09:54 - collected grab sample: Free Chlorine = 0.02 mg/L Total Chlorine = 1.50 mg/L 09:59 - collected weekly regulatory micro. sample - W/O # W11256486 SL1000 readings: MCL =1.42 mg/L TNH3 = 0.40 mg/L FNH3 = 0.12 mg/L NO2 = 0.002 mg/L temp =17.9 C -collected operational ATP and phosphorus samples -recorded readings in PWQ sheet -no issues found | Woodbridge East Elevated Tank | 2025-10-01
WEST | October | On site to complete station check, collect biweekly operational samples, and weekly bacti sampling W11298750. -Took grabs: Free chlorine @ 10:31 Grab: 0.02 mg/L Total chlorine @ 10:31 Grab: 1.62 mg/L -Checked trends | Woodbridge East Elevated Tank | 2025-10-14
WEST | October | -on site to complete work orders -informed ROC of work -completed Sump Pit System Inspection -completed JHSC?Health?and?Safety?Inspection -completed Air Relief Valve inspection -completed Flood Alarm, Test -completed Sensing Line Heat Trace System, Inspection -completed Low Temperature Alarm, Test -completed Portable Gasoline Generator, Test -no issues, site back to normal operation | Woodbridge West Elevated Tank | 2025-10-16
WEST | October | -On-site to complete station check and collect samples -deactivated system duty -checked equipment -reviewed trends 11:59 - collected grab sample: Free Chlorine = 0.03 mg/L Total Chlorine = 1.40 mg/L 12:06 - collected weekly regulatory micro. sample - W/O # W11376186 -collected quarter #4 samples - W/O # W11246983 SL1000 readings: MCL = 1.25mg/L TNH3 = 0.36 mg/L FNH3 = 0.11 mg/L NO2 = 0.000 mg/L temp = 12.7 C -recorded readings in PWQ sheet -no issues found | Woodbridge West Elevated Tank | 2025-10-29
WEST | October | -On-site to complete station check and collect sample -deactivated system duty -checked equipment -reviewed trends 11:55 - collected grab sample: Free Chlorine = 0.04 mg/L Total Chlorine = 1.27 mg/L 12:01 - collected weekly regulatory micro. sample - W/O # W11316454 SL1000 readings: MCL = 1.11 mg/L TNH3 = 0.33 mg/L FNH3 = 0.11 mg/L NO2 = 0.001 mg/L temp = 16.4 C -recorded readings in PWQ sheet -no issues found | Woodbridge West Elevated Tank | 2025-10-22
WEST | October | -On-site to complete station check and collect sample -deactivated system duty -checked equipment -reviewed trends 10:41 - collected grab sample: Free Chlorine = 0.03 mg/L Total Chlorine = 1.27 mg/L 10:45 - collected weekly regulatory micro. sample - W/O # W11256486 SL1000 readings: MCL = 1.13 mg/L TNH3 = 0.37 mg/L FNH3 = 0.15 mg/L NO2 = 0.001 mg/L temp = 18.1 C -collected operational ATP and phosphorus samples -recorded readings in PWQ sheet -no issues found | Woodbridge West Elevated Tank | 2025-10-01
WEST | October | On site to complete station check, biweeekly operational sampling, and weekly bacti sampling W11298750. -Took grabs: Free chlorine @ 11:20 Grab: 0.06 mg/L Total chlorine @ 11:20 Grab: 1.35 mg/L -Checked trends | Woodbridge West Elevated Tank | 2025-10-14
WEST | October | Onsite for station check and to collect weekly micro sample W11278701 Deactivated duty to get sample Checked residuals mg/l Total grab 1.25 Free grab 0.03 Sl1000 Mcl 1.08 F nh3 0.13 T nh3 0.35 Temp 17.8 *C Reactivated duty afterwards | Woodbridge West Elevated Tank | 2025-10-08
WW-CEAST | October | Here to set up wet well for cleaning,, isolated the wet well by closing the lower gate which separates the two wet wells and then the gate which separates the inlet channels. ( Phil stopped by and helped as well ) We isolated pumps 1,2 and 3 by closing the inlet channel gates for that side. Set up pumps 4,5 and 6 in duties 1,2 and 3 and the controlling LIT was already on that side. GFL doing set up and will start with wet well 1. Completed station check with Jackie and checked both compressors - all good. monitored wet well levels. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-10-20
WW-CEAST | October | Check plug valve on dump pad. Found plug valve over torque Tried back flushing valve, no change Removed limit torque and pulled guts to valve Found valve had rocks and a bolt in valve and rubber coating is coming off Cut off loose rubber Reassembled valve and reinstalled limit torque Tested operation okay No longer tripping on over torque. Returned to auto. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-10-21
WW-CEAST | October | Here for the wet well cleaning,, opened everything up for Accuworx and they got started on cell 2 again. Cleaned the washroom during the day and monitored wet well levels in cell. Wet well cleaning should be finished tomorrow morning,, all went well today. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-10-23
WW-CEAST | October | Let crane tech in first maintenance, Work on broken isolation valve stand wet well interconnect Removed hardware from interconnect pedestal. Unable to complete repair operations unavailable to assist. Will order replacement material and hardware. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-10-30
WW-CEAST | October | Weather today Light rain and 10 Celsius -on site responding to callout for bar screen #1 general alarm and not an auto W11387972. -on arrival bar screen #1 was in auto but faulted, and I was unable to reset until I jogging bar screen in reverse and then forward I was able to reset bar screen #1. -monitor bar screen #1 for a short while it appears to be running fine at this time. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-10-22
WW-CEAST | October | -Line 1 was clogged at AUSSSR, and potentially Line 3 as well -met Eric S and Ian W on site -unclogged lines and put back to operation -actuated plug valves are the culprit and need to be changed, they are not the right valves for the dumping system -helped Terry Reed revalve the wetwell for wetwell cleaning, see his entry for details | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-10-22
WW-CEAST | October | Raw sewage pump timed based pms Pumps 2,3,5,6 Added 65 grams grease to de bearing pumps 5 and 6 Pump 3 added 5L coolant Pumps 2,3 added 65 grams grease Pump 3, 3L coolant loss | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-10-22
WW-CEAST | October | -dump pad line 1 clogged again -had to back flush line 1, rags/diapers were stuck in the valve and pipe -backflushed locally a few times, cleared debris, restored valves to remote -reset alarms on SCADA -3 lines back online -actuated plug valves keep catching debris and clogging, need these valves changed -heat trace controlled 2 fault keeps coming in, could not reset, will notify team/CPD as site is under warranty | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-10-29
WW-CEAST | October | Here to check surge tanks - went up on the cat walk of both tanks - all looks good,, no issues seen while walking around them. Also set up the washroom paper towel as well as the paper towel in the Diesel area. Pump 3 still OOS but Phil and I opened the inlet channel again. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-10-16
WW-CEAST | October | Pump 3 FIT - Further investigated and found out that the new transmitter showed ?Sensor connect error?. It was concluded that the problem was on the flowtube itself and has to be replaced. Flow transmitter power supply was unplugged. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-10-20
WW-CEAST | October | -station check of site -reviewed SCADA -entered data into SharePoint -inspected site -cleaned screen room, put 3 bins out for pickup, 1 left 2/3 full in screen room -inspected air compressors -inspected suction valves, did not have time to exercise as line is clogged at dump pad requiring resolution -pump 3 remains OOS due to flowmeter fault, can be used in emergencies -station okay | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-10-29
WW-CEAST | October | -called to site to address clogged lines for dump pad -lines 1 and 2 were clogged and OOS, overtorque on plug valves -backflushed both lines, rags and diapers were stuck in the actuated plug valves, these plug valves are not the right valves for a system receiving diapers and rags, which is why these lines are frequently getting clogged and debris stuck in the plug valves -open all valves, valves back to remote -reset alarms on SCADA -all 3 lines are now available | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-10-28
WW-CEAST | October | Took station readings and entered into SharePoint,, checked the dump pad to ensure all 3 lines are available: yes they are. Checked both compressors oil/belt - OK. Checked pump floor - all looks good - no leaks and everything looks operational. Verified the sampling kit Ty-strap has not been tampered with and kit is -OK. Test ran each pump: P1- @ 23%=362.2 L/s, P2- @ 18%=305.2L/s, P3 is OOS due to flow meter and P4 - is 450L/s P5 - @42%=389.2L/s and P6 - @ 16%=310.9 L/s. Levelled out the bin in the screening room - went to top up bar screen oil but I?m gonna have to get a new bucket of oil,, I shut down the ventilation fans for the screening room as the weather is starting to change and it was pretty cool in there ( bar screens freezing up ). Went and checked the odour control for the EQ tank - greased the fan where required and it?s operating as it should. Station running as per normal, pump 3 in Duty 7 but can be ran - I will create a WO for LIT 4 EQ tank. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-10-27
WW-CEAST | October | -station check of site -reviewed SCADA -inspected site -entered data into SharePoint -cleaned screen room, rotated bins as necessary -Pump 3 primed and put back to auto, testing pump by switching to duty 1 -Pump 3 flowmeter fault came back in, Pump 3 returned to duty 7/OOS, notified instrumentation Team Lead Eric -rotated duties for pumps -station okay | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-10-17
WW-CEAST | October | Pump 3 FIT-Replaced the transmitter. Configured and tested it. Flowrate, alarm and hart signals were working good and matched SCADA. Performed heartbeat verification and it passed. All alarms were cleared and no other issues encountered. Asked operator Chris to put it on duty 1. We will observe if the issue on fault alarm will show again. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-10-17
WW-CEAST | October | Got Accuworxs all set up and running again. Went down to the dump pad and cleared line 3,, rag build up from ports,, brought the silver bin down and cleaned up the area around the dump pad. Also cleared the Heat trace alarm at the dump pad. Started cleaning up OCF room,, middle gate separating the 2 wet wells is passing - Terry and Matt helped with closing it further - gate is now holding. Finished cleaning for today,, wet well will stay isolated. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-10-21
WW-CEAST | October | -AUSSSR (Aurora Sewage Receiving) Lines 1 and 2 clogged, valves 1 and 2 overtorque alarms -was able to back flush line 1 and clear debris -line 2 valve was not able top be cleared, and over torque alarms is outstanding, will notify team and create WO -new flushing system is too small (not enough flow), pressure is okay, but not enough volume, it should be located upstream of the valve to clear valve of debris, and likely doesn?t have the volume to clear anything heavy or jammed. It is capable of clearing smaller debris in line possibly. -need new valves that don?t get clogged, and a larger flushing system -has been multiple times we have been down to one line in the last few weeks and this system is brand new -need 4? flushing lines similar to tipping buckets used in AUEQSJ -seems every few days there is a clog/overtorque if not multiple clogs every day | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-10-15
WW-CEAST | October | Here to clear overtorque alarm on line 2 at the dump pad - back flushed the line to clear the obstruction and cleared alarm on SCADA. System back on line - all 3 lines are available. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-10-10
WW-CEAST | October | On site for station check (See details on SharePoint). All pumps available in timed auto duty rotation every 3 hours, except pump 3, which has an issue with flowmeter fault alarm. All standby power generator available in auto. Checked dry well. Checked bar screens. Bar screen 1 still out of service. Levelled rags from the rag bin. Cleaned bar screen room. Switched rag bin. Hauler?s dump pad is ok. All lines available. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-10-10
WW-CEAST | October | Onsite to complete surge tank annual calibrations Informed OIC and ROC Used cal mode on scada and maintenance bypass on local panel Completed both surge tanks Removed from maintenance bypass and cal mode on scada Cleared associated alarms Informed ROC armed building and left site | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-10-03
WW-CEAST | October | On site for pump5 coolant leak. Drained 11 L and topped off with about 14 L. Placed the pump back in auto | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-10-08
WW-CEAST | October | On site to fix barscreen #1. Chain off bottom sprocket. Fixed barscreen ran tested and put back in service. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-10-14
WW-CEAST | October | Attending site to investigate for pump#3 flowmeter transmitter replacement (W11274769). Will return next week to replace transmitter. ROC notified before and after site investigation. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-10-10
WW-CEAST | October | Testing out new logbook name change, system testing, please ignore. New Name: Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-10-02
WW-CEAST | September | -this is a backdated entry for Sept 22nd, 2025 to keep a record of all the times the new dump pad upgrades/lines have clogged. -on September 22, 2025 both dump pad lines 1 and 2 were clogged and had overtorque alarms on actuators. -this was the first clogging noted of the lines, they were put online at end of day Friday Sept 19th, 2025, next full business day on Monday there were 2 lines clogged. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-09-22
WW-CEAST | October | Here to complete WO?s,,, checked all 6 check valves - all looks good, flushed out the sump pit - no issues all works. Met with fork lift company for inspection of the fork lift - parts are required to fix horn on the stearing wheel - he will get in contact with Daniel once parts have arrived. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-10-09
WW-CEAST | October | -station check of site and work orders -reviewed SCADA -entered data into SharePoint -inspected site -cleaned screen room, rotated bins as necessary -air compressor inspection/cleaning -inspect heat trace on dump pad lines | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-10-15
WW-CEAST | October | Completed Diesel pre check list and switched station over to Diesel power,, checked both compressors oil/ belts - OK and also entered readings into SharePoint. Took bins out of screening room for pick up and verified building temp alarm - verified by control. Switched station back to main power and cleared all alarms - dump pad as well. There was no hazardous waste to re move and I also helped Vetri out at the dump pad. Station is back to normal ops - pumps 3 and 5 are in duty 7. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-10-01
WW-CEAST | October | Weather today Clear and 17 Celsius -On site responding to dump pad receiving line #1 valve over torque alarm. -manually opened valve back flushed line #1 and closed valve and cleared alarm. -Dump pad receiving line #1 back in service. -On site to complete work order W11264011. -On site to perform a station check. -Entered station readings into SharePoint. -Checked drywell and air compressors. -Checked screen room, raked rag bin, cleaned rags off conveyors, bar screen oil good. -Bar Screen Bin Removal and Replacement put rag bin back inside from pick up by Miller Waste. -Pump 3 OOS with Flowmeter fault issues. -pump 5 OOS with leakage alarm issues. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-10-03
WW-CEAST | October | On site in response to Barscreen 1 not in auto alarm. Attempted to clear alarm and operate barscreen on hand, rake is stuck at the bottom not moving/causing overtorque alarm with a loud noise. Called ROC to dispatch Young J (WW) to assist in closing the barscreen 1 inlet valve to put the unit OOS. Cleared line 2 valve overtorque alarm. Flushed the line multiple times in the other direction with down stream valve closed. Young J on site, we closed barscreen 1 inlet gate valve. Went down to B2 to inspect the rake, confirmed one side chain has popped out of the sprocket. CMU3 created for CMS. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-10-05
WW-CEAST | October | Pump 6 hi hi vibration onsite to verify readings with microlog | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-10-14
WW-CEAST | October | -station check of site and work orders completed -reviewed SCADA -inspected site -entered data into sharepoint -notified from ROC Adam Pump 2 MV2 fail to open -put pump 2 manual off to investigate forcemain discharge valve and pump discharge valve fail to open alarms, exercised both forcemain discharge valves for pump 2, put pump back to auto and duty 1, started pump 2 in auto, pump 2 ran and opened valves with no issues -will monitor pump 2 remotely and notify on call operator -pump 3 remains manual off due to flowmeter fault alarm, 5 pumps available -cleaned screen room, rotated bins as necessary -bar screen 1 remains OOS, and isolated -station okay | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-10-08
WW-CEAST | October | Took station readings and entered into SharePoint,, checked both compressors oil/ belts and air- ok and also looked at air dryer and all looks good. Tested dry well flood alarm and confirmed by ROC. Completed H & S inspection - no issues and verified operation of all 3 cranes. Leveled out the bin in the screening room and cleaned out the auger and flushed out the drain as well as grease it. Pump 3 is in Duty 7 due to flow meter issue and pump 5 is in Duty 7 due to coolant leak,, inlet channel 1 is OOS due to chain off the bar screen. Rest of the station is running as per normal. Brought my chop saw in and made 4 hose stands for the dump pad. Glued saddle in today so they will be ready to go for tomorrow. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-10-06
WW-CEAST | October | On site checked station (See details on SharePoint). Both pumps available in all-stop auto duty rotation. SCADA is trending Station operations normal. | Newmarket Green Lane Pumping Station | 2025-10-20
WW-CEAST | October | -station check of site -reviewed SCADA -reviewed trends -inspected site -entered data into sharepoint -station okay | Newmarket Green Lane Pumping Station | 2025-10-17
WW-CEAST | October | -station check of site -reviewed SCADA -entered data into SharePoint -reviewed trends -station okay | Newmarket Green Lane Pumping Station | 2025-10-24
WW-CEAST | October | Completed station check. Reviewed SCADA, Reviewed trends, Entered data into sharepoint, Station operations normal. | Newmarket Green Lane Pumping Station | 2025-10-22
WW-CEAST | October | On site checked station (See details on SharePoint). Both pumps available in all-stop auto duty rotation. Currently, pump 1 is running in auto as duty 1 with a flow of 169.6 L/s. Wet well level is 3.37 m. SCADA is trending Station operations normal. | Newmarket Green Lane Pumping Station | 2025-10-06
WW-CEAST | October | On site checked station (See details on SharePoint). Both pumps available in all-stop auto duty rotation. Currently, pump 2 is running in auto as duty 1 with a flow of 153.9 L/s. Wet well level is 3.63 m. SCADA is trending Station operations normal. | Newmarket Green Lane Pumping Station | 2025-10-10
WW-CEAST | October | Completed Green Lane H & S check - no issues. | Newmarket Green Lane Pumping Station | 2025-10-02
WW-CEAST | October | -Completed station check -reviewed SCADA and trends -inspected site -station all okay | Newmarket Green Lane Pumping Station | 2025-10-08
WW-CEAST | October | Weather today Clear and 12 Celsius. -On site to complete work order W11265286. -Completed Station check and entered readings into SharePoint. -Both pumps available in all-stop auto duty rotation. -Station is trending and no outstanding alarms. -Station operation normal. | Newmarket Green Lane Pumping Station | 2025-10-03
WW-CEAST | October | -station check of site completed, roundsheet complete -Kevin Shaji completed lab, data was entered into sharepoint -decanted sludge thickening tank, wasted remaining sludge to sludge holding tank -4 bags of soda ash total were added to the aeration tanks -wasted 21 m3 from clarifier 2 to sludge thickening tank -inspected aeration alum injection chamber, and sand filter alum injection point -ran RAS pump 1 at 100% after wasting -Daniel and Kevin cleared a clog in one of the sand filters, which could be causing this rising TP issue -Daniel?s adjustment of increasing the alum dosage should help as well -grab sample of final effluent was 0.068 Total phosphorus which is slightly high, but better than the earlier 0.093 comp sample -will return tomorrow to complete another lab and get a new reading, increased alum, fixed sand filter, and wasting 21 m3 of sludge should help bring the TP down -will monitor site | Mount Albert Water Resource Recovery Facility | 2025-10-31
WW-CEAST | October | -On site to complete lab analysis and sludge handling work. -Decanted STT to headworks, then emptied tank into SHT. -Added two bags of soda ash to each aeration tank. -Completed lab analysis, entered results into SharePoint. -Found right side of cell 1 sand filter not draining and packed with sand. Cleared out under drain, removed built up sand. Pulled air lift, cleared out sand, and reset air lift. Air lift now working properly and draining. -Batch wasted 20m3, ran RAS pumps at 100% speed when returning to service. -Verified alum dosing and sand filter operation. -RAS pump 2 OOS, Aeration blower 3 OOS. | Mount Albert Water Resource Recovery Facility | 2025-10-19
WW-CEAST | October | -station check and lab analysis of site -reviewed SCADA -inspected site -completed lab analysis, data entered into SharePoint -began diverting sand filter effluent to lagoon at 08:25, to prepare for UV maintenance by contractors, stopped diverting at 11:19, approximately 136 m3 of sand filter effluent was diverted to the lagoon -notified ROC of diversion and sending email to ENV Incident Notification -UV maintenance by contractors is complete -UV 1A is duty 1 and dosing 14 mw/cm2 -started decant pump, decanting sludge thickening tank back to influent -dumped thickened sludge to sludge holding tank -wasted 20 m3 from clarifier to sludge thickening tank, 10 m3 from each clarifier -clarifier 1 is OOS, RAS pumps 2 and 3 are off -added two bags of soda ash to each aeration tank, 4 bags total -cleaned RAS chamber -cleaned alum injection chamber -UV channel hose down -station okay | Mount Albert Water Resource Recovery Facility | 2025-10-23
WW-CEAST | October | Clarifier Scum System and Weir Cleaning - approximately 73 m3 of flows have been diverted to the lagoon from 12.25pm to 2.30pm for clarifier and weir inspection | Mount Albert Water Resource Recovery Facility | 2025-10-22
WW-CEAST | October | On site completed work orders. Station Check (See details on SharePoint) Added two bags each of Soda Ash into each Aeration Tanks Checked Alum dosing injection points at pre-filter and post-aeration, ok. Removed rags from the sluice gates of Aeration Tanks Checked DO Probes, removed rags from the probes. RAS/WAS Inlet Channel Inspection and Cleaning Post Aeration Alum Mixing Chamber Cleaning Post Filtration/UV Channel Hosed Down Observed TP is slowly going up for the past few days. Will check the filter and probably flush the Alum lines. Alum dosing lines flushed. Alum dosage remains at 190 mg/l and 15 mg/l for aeration and prefilter, respectively. Reduced weir height of filter reject from 2? to 1?. Flushed filter reject drain lines. Will monitor and do further remedy. Also, checked Outfall at Hwy 48. Beaver dam back up again, more fortified than the previous ones. Partially reopened again. Water level at the Outfall is slowly lowering down. | Mount Albert Water Resource Recovery Facility | 2025-10-30
WW-CEAST | October | Weather today Light rain and 12 Celsius -On site to complete work orders W11309771, W11353484, W113373597, W11281061, W11281068, W11283051, W11316168. -Completed in-house lab analysis and station check. -Entered lab and station readings into SharePoint. -Grit Vortex 1 and 2 maintenance. -Oak ridges AMF - MUA training . -Isolated and drained down clarifier. -Daily SCADA review. -Doane Rd Effluent Discharge sewer inspection and cleaning. -Reset composite sampler for tomorrow. -Outfall inspection and cleaning. -Ran RAZ pumps #1 and #3 at 100% to clear them out for a bit - all back to auto as well as speed back to auto. -Added two bags of soda ash to each aeration tank. -Decanting STT into the Headworks. -Transferred the sludge and processing. -Aeration Blower back in service in auto duty rotation. -Clarifier 1 has been isolated, partially drained and put out of service to accommodate the works to be done by contractor. -RAS Pump 3 in manual off and out of service.? -RAS pump 2 remains OOS. | Mount Albert Water Resource Recovery Facility | 2025-10-22
WW-CEAST | October | -Reviewd scada, inspected site. -Completed in-house lab analysis and station check. -Entered lab and station readings into SharePoint. -Decanting STT into the Headworks. -Transferred the sludge and processing. -Batch wasted 7m3 from clarifier #1. Ran RAS pumps at 100% speed when returning to service. -Added two bags of soda ash to each aeration tank. -Cleaned RAS chamber. -Cleaned Alum injection chamber. | Mount Albert Water Resource Recovery Facility | 2025-10-27
WW-CEAST | October | Weather today a Few Clouds and 3 Celsius -On site to complete work order W11322495. -Completed in-house lab analysis and station check. -Entered lab and station readings into SharePoint. -Ran RAZ pumps #1 at 100% to clear it out for a bit - all back to auto as well as speed back to auto. -Batch wasted 7m3 from Clarifier #1. -Added two bags of soda ash to each aeration tank. -Decanting STT into the Headworks. -Transferred the sludge and processing. -Clarifier 1 has been isolated, partially drained and put out of service to accommodate the works to be done by contractor. -RAS Pump 3 in manual off and out of service.? -RAS pump 2 remains OOS. | Mount Albert Water Resource Recovery Facility | 2025-10-26
WW-CEAST | October | Clarifier Scum System and Weir Cleaning - approximately 60 m3 of flows have been diverted to the lagoon from 12.45pm to 2.30pm for clarifier and weir inspection and cleaning. Flows have now been back to the plant | Mount Albert Water Resource Recovery Facility | 2025-10-16
WW-CEAST | October | Blower 3 investigate noisy, Found blower to be running back Electrical onsite to address. Blower back in auto | Mount Albert Water Resource Recovery Facility | 2025-10-20
WW-CEAST | October | Weather today Partly Cloudy and 11 Celsius -On site to complete work orders W11309698, W11308482. -Completed in-house lab analysis and station check. -Entered lab and station readings into SharePoint. -Post aeration alum mixing chamber and Ras/Was inlet channel inspection and clean out. -Ran RAZ pumps #1 and #3 at 100% to clear them out for a bit - all back to auto as well as speed back to auto. -Added two bags of soda ash to each aeration tank. -Decanting STT into the Headworks. -Transferred the sludge and processing. -Aeration Blower #3 back in service in auto duty rotation. -RAS pump 2 remains OOS. | Mount Albert Water Resource Recovery Facility | 2025-10-20
WW-CEAST | October | On site completed work orders. At 9:00am, isolated clarifier 1 and partially drained and put out of service to accommodate works to be done by contractor. Put RAS Pump 3 in manual off and out of service, too. Grit Vortex 1 and 2 Maintenance Doane Rd Effluent Discharge Sewer Inspection and Cleaning Facility Outfall (at Hwy 48) Inspection and Cleaning - surrounding area of the outfall removed/cleared obstructions/tall weeds. Outfall is under water from the creek. Found beaver dam on the north side of the outfall, hence, creek has high water level. Partially opened at the point I can reached. The rest of the dam is under water. Beaver dam reported to supervisor. See Barry Middleton?s logbook entry above for further work orders details. | Mount Albert Water Resource Recovery Facility | 2025-10-22
WW-CEAST | October | On site to check station/complete lab/sludge process. Checked station equipments in response to increasing TP. Upon arrival, found one of the sandfilter not functioning. Pulled out the filter rod and cleaned the screen, placed it back in service. Added 4 bags of soda ash into the aeration. Checked all alum injection point, OK. Checked the alum pumps/trend, OK Increased alum dosage from 190/15 to 195/20 | Mount Albert Water Resource Recovery Facility | 2025-10-31
WW-CEAST | October | -Completed in-house lab analysis and station check. -Entered lab and station readings into SharePoint. -Added two bags of soda ash to each aeration tank. -Decanting STT into the Headworks. -Transferred the sludge to holding tank. | Mount Albert Water Resource Recovery Facility | 2025-10-17
WW-CEAST | October | -filled six 5 gallon pails with mixed liquor effluent from the aeration tanks -waiting for pickup from GFL to deliver them to Oak Ridges AMF to inoculate the new media -started decant pump, decanting top of sludge thickening tank back to influent of plant | Mount Albert Water Resource Recovery Facility | 2025-10-20
WW-CEAST | October | Weather today Light rain and 12 Celsius -On site to complete work orders W113312995, W11311919, W11311389, W11311206, W11313169, W11312023. -Completed in-house lab analysis and station check. -Entered lab and station readings into SharePoint. -2 tonne hoist system inspection. -Sand filter reject drain line flush. -Raw sewage sampler check. -Collected weekly raw sewage samples. -Reset composite sampler for tomorrow. -Post aeration alum mixing chamber and Ras/Was inlet channel inspection and clean out. -Ran RAZ pumps #1 and #3 at 100% to clear them out for a bit - all back to auto as well as speed back to auto. -Added two bags of soda ash to each aeration tank. -Decanting STT into the Headworks. -Transferred the sludge and processing. -Aeration Blower back in service in auto duty rotation. -RAS pump 2 remains OOS. | Mount Albert Water Resource Recovery Facility | 2025-10-21
WW-CEAST | October | -Reviewd scada, inspected site. -Completed in-house lab analysis and station check. -Entered lab and station readings into SharePoint. -Decanting STT into the Headworks. -Transferred the sludge and processing. -Batch wasted 5m3 from clarifier to sludge thickening tank. -Added two bags of soda ash to each aeration tank. -Clarifier 1 remain OOS, RAS pumps 2 and 3 are off. -WAS pump 2 switched to manually off due to clarifier 1 being OOS | Mount Albert Water Resource Recovery Facility | 2025-10-24
WW-CEAST | October | Weather today a few clouds and 10 Celsius -On site to complete work orders W11325492, W11324828, W11327324, W11327651, W11327069, W11327069, W11327749, W11327305, W11334850. -Completed in-house lab analysis and station check. -Entered lab and station readings into SharePoint. -Collected weekly raw sewage samples. -Bar screen bin removal and replacement. -Sand filter reject drain line flush. -Daily SCADA review. -TNT Reagent Inventory Confirmation and Reordering. -Reset composite sampler for tomorrow. -Ran RAZ pumps #1 at 100% to clear them out for a bit - all back to auto as well as speed back to auto. -Added two bags of soda ash to each aeration tank. -Decanting STT into the Headworks. -Transferred the sludge and processing. -Clarifier 1 remains isolated, partially drained and put out of service to accommodate the works to be done by contractor. -RAS Pump 3 in manual off and out of service.? -RAS pump 2 remains OOS. | Mount Albert Water Resource Recovery Facility | 2025-10-28
WW-CEAST | October | -Completed in-house lab analysis. Entered lab data to sharepoint -Decanting SST into headworks -Transferred the sludge and processing. -Batch wasted 16m3 from clarifier #1. | Mount Albert Water Resource Recovery Facility | 2025-10-30
WW-CEAST | October | On site completed work orders. Filter reject pumps flushed/bleed air due to abnormal trends. Sump Pumps Maintenance - RAS/WAS Sump Pumps 1 and 2, Headworks Sump Pumps 1 and 2, Filter Sump Pumps 1 and 2. All tested, ok. Grit Vortex 1 and 2 Maintenance At 10:15am, received 120 bags of 25 kgs. Soda Ash from Glen Chemicals Limited. Screw Press Maintenance Travelling Screen Maintenance Facility Outfall Inspection and Cleaning - removed some weeds surrounding the top of the outfall/needs to bring weed wacker to totally clear outfall from outgrown weeds. Outfall pipe/screen is submerged by high water level of the river/creek. | Mount Albert Water Resource Recovery Facility | 2025-10-17
WW-CEAST | October | -Completed in-house lab analysis -Entered lab readings into SharePoint. -Added two bags of soda ash to each aeration tank. | Mount Albert Water Resource Recovery Facility | 2025-10-20
WW-CEAST | October | Visited Outfall at Hwy 48, found beaver dam is back up again after I partially cleared it last week. Outfall still submerged due to the water contained by the beaver dam within the vicinity of the outfall. Partially cleared the beaver dam again and the water is slowly lowering down. Supervisor informed MTO. Will further monitor. Also on site at the WRRF to complete work orders. Lab Analysis (See details on SharePoint) and Sludge Processing Decanted STT and dumped remaining sludge into the SHT Station Check (See details on SharePoint) Added two bags each of Soda Ash into each Aeration Tanks Checked Alum dosing injection points at pre-filter and post-aeration. Removed rags from the sluice gates of Aeration Tanks Checked DO Probes, removed rags from the probes. Clarifier Scum System and Weir Cleaning - cleaned/hosed down clarifiers and weir. Diverted flows to the lagoon from 10:20am to 12:20pm. Approximately 90 m3 of flows went to the lagoon. | Mount Albert Water Resource Recovery Facility | 2025-10-29
WW-CEAST | October | On site completed work orders. Lab Analysis (See details on SharePoint) and Sludge Processing STT decanted and remaining sludge dumped into the SHT. Station Check (See details on SharePoint) Checked Headworks, ok. Removed rags from the sluice gates of Aeration Tanks. Checked Alum dosing injection points at pre-filters and post-aeration tanks, ok. Check DO Probes, removed rags from the probes. At around 10:53am, Odour Control System blower faulted. Reset tripped inside the panel. OCF blower back in service at auto. Added two bags each of Soda Ash into each Aeration Tanks. Batch wasted 20m3. Clarifier Scum System and Weir Cleaning - approximately 80 m3 of flows have been diverted to the lagoon from 12:45pm to 2:45pm for clarifier scum and weir inspection and cleaning. Flows have now been diverted back to the plant. | Mount Albert Water Resource Recovery Facility | 2025-10-08
WW-CEAST | October | On site completed work orders. Grit Tank Blowers 1 and 2 - Belts, Inlet Filters and Oil Checked Sludge Holding Tank Blowers 1 and 2 - Belts, Inlet Filters and Oil Checked Air Compressors 1 and 2 - Cleaning and Inspection Air Compressors 1 and 2 - Oil and Filter Change Inspection | Mount Albert Water Resource Recovery Facility | 2025-10-09
WW-CEAST | October | On site completed work orders. Station Check (See details on SharePoint) Checked Headworks, ok. Removed rags from the sluice gates of Aeration Tanks. Checked Alum dosing injection points at pre-filters and post-aeration tanks. Check DO Probes, ok. Sand Filter Filter-Reject Drain Line Flushed | Mount Albert Water Resource Recovery Facility | 2025-10-07
WW-CEAST | October | Weather today Mostly cloudy and 19 Celsius -On site to complete work orders W11273459, W11273557, W11273543, W11273440, W11274063. -Completed station check. -Entered station readings into SharePoint. -Collected weekly raw sewage samples. -Ran RAZ pumps #1 and #3 at 100% to clear them out for a bit - all back to auto as well as speed back to auto. -Batch wasted 20m3 from aeration tank #1 and #2. -Added two bags of soda ash to each aeration tank. -Decanting STT into the Headworks. -Transferred the sludge and processing. -Aeration Blower 3 in manual off due to Failed to Start alarm that came in. -RAS pump 2 remains OOS. | Mount Albert Water Resource Recovery Facility | 2025-10-07
WW-CEAST | October | On site to investigate Ras P2 and aeration blower 3. Replaced Ras Fan 3 with the fan from VFD 2 as it has a short circuit and requires replacement. Aeration blower three is up and running but is having mechanical issues and requires an inspection before it is placed back in service | Mount Albert Water Resource Recovery Facility | 2025-10-14
WW-CEAST | October | On site completed work orders. Station Check (See details on SharePoint) Checked Headworks, ok. Checked Alum dosing injection points at pre-filters and post-aeration tanks. | Mount Albert Water Resource Recovery Facility | 2025-10-14
WW-CEAST | October | Weather today Clear and 10 Celsius -On site to complete work orders W11270527, W11281483, W11283079, W11283066, W11280878, W11281027, W11283329. -Completed station check. -Entered station readings into SharePoint. -Post aeration alum mixing chamber and Ras/Was inlet channel inspection/cleanout. -Dissolved Oxygen meter verification. -Aeration tank blowers 1-2 inspection. -Ran RAZ pumps #1 and #3 at 100% to clear them out for a bit - all back to auto as well as speed back to auto. -Batch wasted 20m3 from aeration tank #1 and #2. -Added two bags of soda ash to each aeration tank. -Decanting STT into the Headworks. -Transferred the sludge and processing. -Aeration Blower 3 in manual off due to Failed to Start alarm that came in. -RAS pump 2 remains OOS. | Mount Albert Water Resource Recovery Facility | 2025-10-09
WW-CEAST | October | Weather today Partly Cloudy and 14 Celsius -On site to complete work orders W11270527, W11344381, 11280494, 11281956, W11290635, W11286480. -Completed station check. -Entered station readings into SharePoint. -Oak Ridges AMF SCADA training. -Clarifier 1 and 2 maintenance. -Clarifier 1 and 2 condensation draining. -Bar screen bin removal and replacement. -Ran RAZ pumps #1 and #3 at 100% to clear them out for a bit - all back to auto as well as speed back to auto. -Added two bags of soda ash to each aeration tank. -Decanting STT into the Headworks. -Transferred the sludge and processing. -Aeration Blower 3 in manual off due to Failed to Start alarm that came in. -RAS pump 2 remains OOS. | Mount Albert Water Resource Recovery Facility | 2025-10-10
WW-CEAST | October | Completed daily lab analysis. Entered data into SharePoint. | Mount Albert Water Resource Recovery Facility | 2025-10-10
WW-CEAST | October | On site completed work orders. Lab Analysis (See details on SharePoint) and Sludge Handling completed RAS/WAS inlet channel inspection and hose down. completed post aeration alum mixing chamber cleanout. Removed rags from the sluice gates of Aeration Tanks. | Mount Albert Water Resource Recovery Facility | 2025-10-06
WW-CEAST | October | Weather today Clear and 13 Celsius -On site to complete work orders W11349406, W11281161, W11281175, W11280483, W11270527. -SCADA Cybersecurity Training. -Scum Pumps 1-2 inspection. -Was pumps 1-2 inspection -Grit Dewatering Screw press maintenance. -Aeration Blower 3 in manual off due to Failed to Start alarm that came in. -RAS pump 2 remains OOS. | Mount Albert Water Resource Recovery Facility | 2025-10-08
WW-CEAST | October | On site completed work orders. Lab Analysis (See details on SharePoint) and Sludge Handling STT decanted and remaining sludge dumped into the SHT. Station Check (See details on SharePoint) Checked Headworks, ok. Removed rags from the sluice gates of Aeration Tanks. Checked Alum injection points at pre-filters and post-aeration tanks. Added two bags each of Soda Ash into each Aeration Tanks. Checked DO Probes, removed rags from the probes. Batch wasted 20 m3. Short blasted RAS Pumps 1 and 3 to get desired flows at 0% auto speed. Post-Aeration Alum Mixing Chamber Cleaned Out RAS/WAS Inlet Chamber Inspection and Cleaning Post-Filtration/UV Channel Hosed Down JHSC Health and Safety Inspection UV System 2 Inspection and Cleaning Clarifier Scum System and Weir Cleaning - approximately 85 m3 of flows have been diverted to the lagoon from 10:45am to 12:45pm for clarifier and weir inspection and cleaning. Flows have now been back to the plant. | Mount Albert Water Resource Recovery Facility | 2025-10-02
WW-CEAST | October | Back on site to continue completing work orders after delivering the sewage samples to 145 HWP. Decanting STT is done. Dumped sludge into the SHT and turned off decant pump. Batch wasted 20 m3. Removed rags from the sluice gates of Aeration Tanks. Checked Alum Dosing Injection Points at Pre-Filter and Post-Aeration, ok. Checked DO Probes. Removed rags from the probes. Post Aeration Alum mixing chamber cleaned out Added another one bag of Soda Ash into the Aeration Tanks. Sand Filter Filter Reject Drain Line Flushed | Mount Albert Water Resource Recovery Facility | 2025-10-14
WW-CEAST | October | Weather today Cloudy and 15 Celsius -On site to complete work orders W11291298, W11297726, W11299138. -Completed in-house lab analysis and station check. -Entered lab and station readings into SharePoint. -Ran RAZ pumps #1 and #3 at 100% to clear them out for a bit - all back to auto as well as speed back to auto. -Batch wasted 20m3 from aeration tank #1 and #2. -Added two bags of soda ash to each aeration tank. -Decanting STT into the Headworks. -Transferred the sludge and processing. -Aeration Blower 3 in manual off due to Failed to Start alarm that came in. -RAS pump 2 remains OOS. | Mount Albert Water Resource Recovery Facility | 2025-10-15
WW-CEAST | October | Weather today Clear and 12 Celsius -On site to complete work orders W11314022, W11255079, W11254977, W11254100, W11270523, W11257024. -Completed station check. -Entered station readings into SharePoint. -At 8:15 am Alum delivery/Receiving started at 1.36m/6412L and filled to 3.93m/18459L. -Standby Power generator test run. -Hazardous waste collection and removal. -Weekly Sewage sampling. -Ran RAZ pumps at 100% to clear them out for a bit - all back to auto as well as speed back to auto. -Batch wasted 20m3 from aeration tank #1 and #2. -Added two bags of soda ash to each aeration tank. -Decanting STT into the Headworks. -Transferred the sludge and processing. -Aeration Blower 3 in manual off due to Failed to Start alarm that came in. | Mount Albert Water Resource Recovery Facility | 2025-10-01
WW-CEAST | October | On site completed work orders. Lab Analysis (See details on SharePoint) and Sludge Handling completed aeration tank blowers belt, filter and oil check completed post filtration/UV channel hose down Removed rags from the sluice gates of Aeration Tanks. | Mount Albert Water Resource Recovery Facility | 2025-10-09
WW-CEAST | October | On site completed work orders. Lab Analysis (See details on SharePoint) and Sludge Handling Started decanting STT into the Headworks. Collected weekly sewage samples under W11294767. Added one bag of Soda Ash into each Aeration Tanks. | Mount Albert Water Resource Recovery Facility | 2025-10-14
WW-CEAST | September | Completed Lab work and entered results into SharePoint and also sludge processing was done. Wasted 20m3 and added 4 bags of soda ash. Cleaned out the post aeration tank - not much in there at all and also the Raz/Waz inlet channel. Hosed down the UV channel while Raz pumps were off and went through the rest of the station verifying operation. Station running under normal ops - no issues were detected. | Mount Albert Water Resource Recovery Facility | 2025-09-25
WW-CEAST | October | Sludge process/lab complete and the readings have been entered into the sharepoint. Unable to test FE comp sample for TP/AMM/TSS as comp sampler was not set for today, sent out reminder to WRRF Ops for this month. Found filter module 2 not functioning, clogged up with sand. Pulled out the filter rod and cleaned the screen and put back in service. Noticed a lot of algae came out soon as the filter rod was lifted. Filter module 2 back in service and operating as needed. | Mount Albert Water Resource Recovery Facility | 2025-10-05
WW-CEAST | October | On site completed work orders. Lab Analysis (See details on SharePoint) and Sludge Handling STT decanted and remaining sludge dumped into the SHT. Electrician (Brent S.) checked OCF blower fault alarm. He found it tripped inside the panel. Fixed it and ran tested in local and auto, ok. Currently, OCF System back up and running in auto. He also checked RAS Pump 2. Found blown fuses. He will come back once he has the parts. Also, he needs another electrician to check the wiring why it is bypassed, hence, even the other two RAS Pumps has no power on the multilin when they are not running or power up. Station Check (See details on SharePoint) Checked Headworks, ok. Removed rags from the sluice gates of Aeration Tanks. Checked Alum dosing injection points at pre-filters and post-aeration tanks. Added two bags each of Soda Ash into each Aeration Tanks. Check DO Probes, ok. Batch wasted 20 m3. Short blasted RAS Pumps 1 and 3 to get desired flows of around 13 L/s at 0% auto speed. | Mount Albert Water Resource Recovery Facility | 2025-10-03
WW-CEAST | October | Weather today Clear and 21 Celsius -On site to complete work orders W11270527, W11268751, W11269459, W11270421. -Completed station check. -Entered station readings into SharePoint. -Bar screen bin removal and replacement. -Ran RAZ pumps #1 and #3 at 100% to clear them out for a bit - all back to auto as well as speed back to auto. -Batch wasted 20m3 from aeration tank #1 and #2. -Added two bags of soda ash to each aeration tank. -Decanting STT into the Headworks. -Transferred the sludge and processing. -Aeration Blower 3 in manual off due to Failed to Start alarm that came in. -RAS pump 2 remains OOS. | Mount Albert Water Resource Recovery Facility | 2025-10-06
WW-CEAST | October | On site collected weekly raw sewage samples at 10:40 am under W11312666. Rinsed composite sample container. Reset composite sampler for next week raw sewage samples collection. | Mount Albert Pumping Station | 2025-10-21
WW-CEAST | October | On site for station Check (See details on SharePoint). Both pumps available in all-stop auto duty rotation. Standby power generator available in auto. Checked dry well, ok. | Mount Albert Pumping Station | 2025-10-20
WW-CEAST | October | Record raw sewage pump vibration data. | Mount Albert Pumping Station | 2025-10-23
WW-CEAST | October | On site for station Check (See details on SharePoint). Both pumps available in all-stop auto duty rotation. Standby power generator available in auto. Checked dry well, ok. | Mount Albert Pumping Station | 2025-10-17
WW-CEAST | October | Weather today Clear and 8 Celsius -On site to complete work orders W11325492, W11324005, W11212381, W11265656, W11325434, W11324978. -Completed station check. -Entered station readings into SharePoint. -Operator assistance for wet well cleaning performed by Wessuc Inc. -After completing wet well cleaning I cleared all outstanding alarms and put station back to normal operation. - Check valve inspection - Dry well flood alarm test - Sump pit inspection - RS pump motor / inspection - RS pump grease / inspection - Autodialer test? - High low temp alarm test -Comprehensive Housekeeping. -Daily SCADA review. -Pump #1 = at 47% - 45.3 L/s wet well level at 2.18 m. -Pump #2 = at 51% - 39.5 L/s wet well level at 2.24 m. | Mount Albert Pumping Station | 2025-10-27
WW-CEAST | October | Weather today Clear and 4 Celsius -On site collected weekly raw sewage samples at 10:00 am under W11327324. -Rinsed composite sample container. -Reset composite sampler for next week raw sewage samples collection. | Mount Albert Pumping Station | 2025-10-28
WW-CEAST | October | On site for station Check (See details on SharePoint). Both pumps available in all-stop auto duty rotation. Standby power generator available in auto. Checked dry well, ok. | Mount Albert Pumping Station | 2025-10-24
WW-CEAST | October | On site for generator maintenance with Total Power. Total Power technician on site, generator controller placed in local. ROC notified. Generator Fault Alarm acknowledged. Generator maintenance complete. Generator run for 10 mins upon completion of maintenance. Generator controller returned to auto. All equipment returned to normal operation. Generator Fault Alarm and Generator Running Status alarms acknowledged. ROC notified. | Mount Albert Pumping Station | 2025-10-10
WW-CEAST | October | On site collected weekly raw sewage samples at 11:00 am under W11294767. Rinsed composite sample container. Reset composite sampler for next week raw sewage samples collection. | Mount Albert Pumping Station | 2025-10-14
WW-CEAST | October | Weather today Mostly cloudy and 19 Celsius -On site collected weekly raw sewage samples at 9:35 am Work orders W11273543, W11273557. -Rinsed composite sample container. -Reset composite sampler for next week raw sewage samples collection. | Mount Albert Pumping Station | 2025-10-07
WW-CEAST | October | On site with Total Power generator technician, conducting 5 yr maintenance. Generator controller turned off. ROC notified. Generator not in auto and generator running alarms acknowledged. 2 hr load bank test performed. Generator controller returned to Auto. All equipment returned to normal operation. ROC notified. | Mount Albert Pumping Station | 2025-10-01
WW-CEAST | October | On site completed work orders. Station Check (See details on SharePoint). Both pumps available in all-stop auto duty rotation. Standby power generator available in auto. Currently, pump 1 running in auto as duty 1 with a flow of 45.4 L/s at 47% auto speed. Checked dry well, ok. Station operations normal. Hoist System Inspection Asset ID No. 00016375 Manual Hoist 2 Ton CM Model Cyclone - operated and inspected, ok. Asset ID No. 00089587 Motorized Hoist 2 Ton Vulcan-Hoist Montreal - power turned off at MCC. LOTO by CMS (With note: For maintenance staff only / Crane works). Facility Outfall Inspection and Cleaning | Mount Albert Pumping Station | 2025-10-03
WW-CEAST | October | Weather today Partly cloudy and 9 Celsius -On site to complete work order W11285246. -Completed station check. -Entered station readings into SharePoint. -Total Power on site for generator maintenance. -Checked dry well, ok. | Mount Albert Pumping Station | 2025-10-10
WW-CEAST | October | -Pump 4 was placed in manual off due to no flows earlier this morning, but left in duty rotation causing wet well high level alarms to come in. Placed Pump 4 to OOS duty and clear high level alarms. | Newmarket Sewage Pumping Station & Equalization Tank | 2025-10-29
WW-CEAST | October | On site for station check (See details on SharePoint) All pumps available in timed auto duty rotation every 3 hours, except pump 2, which is still out of service for repair. Standby power generator available in auto. Checked dry well. Checked bar screens. Added oil to reservoir tank. It is fully empty. Mech. Screen 1 has overtorque alarm due to misalignment. Screen LOTO at source of power and closed sluice gate. Created work order request (W11407597) to CMS to check the problem. Also, put pumps 1 and 4 discharge valves in open local mode, as per instruction from the Supervisor (Graham Beach). It won?t allow me to put them in manual mode, as originally instructed. Tested both pumps to run in open local mode, ok. Pumps ran as commanded in auto duty rotation. | Newmarket Sewage Pumping Station & Equalization Tank | 2025-10-31
WW-CEAST | October | -station check of site -reviewed SCADA -inspected site -entered data into SharePoint -pump 4 is OOS due to low flow alarm, likely clogged with rags, manual off -pump 4 LOTO, suction valve closed, discharge valve closed -cleaned screen room, rotated bins, bin out for pickup -inspected air compressor -shelved hi/lo temp alarm for NMSSBP_VC1 and NMSSBP_MC1, Marcos and I inspected and pumped out these chambers yesterday, no issues in these chambers, alarms will be outstanding for colder months, alarms shelved for time being, as these alarms are nuisance alarms -pump 4 back to auto, duty 1, rags cleared, LOTO removed, flow is 290 L/s at 35% -carried new oil up to platform for bar screens, platform and ladder is covered in oil and is a safety hazard -oil line has come out of oil reservoir, cannot fix oil line safely, need 2 staff members -platform and ladder should be addressed, as staff could get injured trying to keep oil levels maintained, could slip or fall on ladder/platform -station okay | Newmarket Sewage Pumping Station & Equalization Tank | 2025-10-29
WW-CEAST | October | -station check of site -inspected site -reviewed SCADA -Jackie entered data into SharePoint -Pump 1 manual off, put to duty 5, LOTO pump 1 and closing suction valve to remove rags from pump, as flow is reading lower than normal -cleaned screen room and rotated bin -pump 2 remains OOS -pump 1 back online, auto -ran pump 4 locally, then returned to auto -station okay | Newmarket Sewage Pumping Station & Equalization Tank | 2025-10-22
WW-CEAST | October | Completed station check. Reviewed SCADA, Reviews trends, Entered data into SharePoint, Pump 2 OOS, Station operations normal. Put pump 1 back in service with Chris R. After rags removed and pump returned to normal operating conditions. | Newmarket Sewage Pumping Station & Equalization Tank | 2025-10-22
WW-CEAST | October | On site to accommodate audible alarm test with PS | Newmarket Sewage Pumping Station & Equalization Tank | 2025-10-17
WW-CEAST | October | -station check of site -inspected site -reviewed SCADA -entered data into SharePoint -cleaned screen room, rotated bin as necessary -screw press lubrication -discharge valve exercise -station okay | Newmarket Sewage Pumping Station & Equalization Tank | 2025-10-17
WW-CEAST | October | On site for station check (See details on SharePoint) All pumps available in timed auto duty rotation every 3 hours, except pump 2, which is still out of service for repair. Standby power generator available in auto. Checked dry well. Checked bar screens. | Newmarket Sewage Pumping Station & Equalization Tank | 2025-10-20
WW-CEAST | October | On site for station check (See details on SharePoint) All pumps available in timed auto duty rotation every 3 hours, except pump 2, which is still out of service for repair. Standby power generator available in auto. Rag bin pushed back inside screen room after picked up by Miller Waste. | Newmarket Sewage Pumping Station & Equalization Tank | 2025-10-10
WW-CEAST | October | Testing new logbook name change, system testing, please ignore. New Name: Newmarket Sewage Pumping Station & Equalization Tank | Newmarket Sewage Pumping Station & Equalization Tank | 2025-10-02
WW-CEAST | October | -Completed station check -reviewed SCADA and trends -inspected site -entered data into SharePoint -cleaned screen room, rotated bins as necessary -station okay | Newmarket Sewage Pumping Station & Equalization Tank | 2025-10-08
WW-CEAST | October | Completed the Diesel test run and entered values into SharePoint,, tested dry well flood alarm verified by ROC on dialer and SCADA. Completed H & S for all buildings - no issues,, checked both compressors oil/belts and air filter - all good. There was no hazardous waste to dispose off,, cleaned the washroom in the pumping station - contractors still working in the EQ buildings. | Newmarket Sewage Pumping Station & Equalization Tank | 2025-10-02
WW-CEAST | October | On site completed station check (See details on SharePoint). All pumps available in timed auto duty rotation every 3 hours, except pump 2, which is still out of service for repair. Standby power generator available in auto. Bar screen bin removal and replacement - rag bin pushed outside for pick up by Miller Waste tomorrow. | Newmarket Sewage Pumping Station & Equalization Tank | 2025-10-01
WW-CEAST | October | Weather today Clear and 20 Celsius. -On site to complete work order W11263988. -On site to perform a station check. -Entered station readings into SharePoint. -Checked screen room Flushed both press drain lines, Hosed down floor, and screw press drain line water left off. -Bar Screen Bin Removal and Replacement put rag bin back inside after pick up by Miller Waste. -Pump 2 remains OOS, pump currently pulled by WW maintenance team. -Pumps 1, 3, and 4 are available in Auto 3 hour timed duty rotation. | Newmarket Sewage Pumping Station & Equalization Tank | 2025-10-03
WW-CEAST | October | On site to check pump 3 for seal water pressure alarm. Ran pump 3 in manual for about half an hour with a flow of 137.6 L/s at 25% auto speed and discharge pressure of 143 kPa, and observed, alarm did not come out. Pump 3 back in auto and available. | Newmarket Sewage Pumping Station & Equalization Tank | 2025-10-07
WW-CEAST | October | -on site to complete work orders -pump 2 remains OOS, pump is removed -shelved alarm ?Forcemain 1 Fault Alarm?, as Forcemain 1 is OOS and will remain OOS for an unknown time period -planning with Team Lead to have operators investigate hi/low temp alarms for MC1 and VC1. Investigate if there are heaters inside chambers that can be turned on, and if sensors can be adjusted. If alarms cannot be cleared they should be shelved as low temp alarms will be in all winter. -Newmarket RS Pumps 1-4 Inspection -Sump Pit Inspection -Check Valve Inspection -Discharge Valve Inspection and Exercise -Suction Valve Inspection and Exercise Pump 1 - 44% - 115 L/s Pump 2 - OOS Pump 3 - 25% - 132 L/s Pump 4 - 34% - 180 L/s -put bin back inside screen room -station okay | Newmarket Sewage Pumping Station & Equalization Tank | 2025-10-09
WW-CEAST | October | On site checked station (See details on SharePoint). All pumps available in timed auto duty rotation every 3 hours, except pump 2, which is out for repair. Checked dry well. Standby power generator available in auto. Checked bar screens. Cleaned floor of rags. Collected facility?s garbage and put in the screen room bin. | Newmarket Sewage Pumping Station & Equalization Tank | 2025-10-06
WW-CEAST | October | Station check complete and the readings have been entered into the sharepoint. Pushed out rag bin for pick up Cleaned screen room | Newmarket Sewage Pumping Station & Equalization Tank | 2025-10-15
WW-CEAST | October | -station check of site -reviewed SCADA -inspected site -entered data into SharePoint -shelved Supply Fan 2 Low Air Flow Alarm, Fan has been put offline (local off) for the winter months due to sucking in too much cold air -station okay | Newmarket Bogart Creek Sewage Pumping Station | 2025-10-24
WW-CEAST | October | -On site to perform a station check. -Station readings entered into SharePoint. -Checked drywell. -Wet well supply fan off for winter season. | Newmarket Bogart Creek Sewage Pumping Station | 2025-10-20
WW-CEAST | October | On site for station check. Reviewed SCADA and trends, Entered data in SharePoint sheet, Visual inspection in and around station. Station OK. | Newmarket Bogart Creek Sewage Pumping Station | 2025-10-31
WW-CEAST | October | -station check of site -inspected facility -reviewed SCADA -entered data into SharePoint -station okay -swept ground level and B1, hosed down B2, Housekeeping complete | Newmarket Bogart Creek Sewage Pumping Station | 2025-10-27
WW-CEAST | October | Station check complete and the readings have been entered into the sharepoint. Turned off wet well supply fan for the season. | Newmarket Bogart Creek Sewage Pumping Station | 2025-10-17
WW-CEAST | October | On site for station check (See details on SharePoint). All pumps available in timed auto duty rotation every 4 hours Standby power generator available in auto Ran pump 2 in manual mode for a few minutes with a flow of 197.2 L/s at 107 kPa discharge pressure. Checked dry well, ok. Found station under PAC mode. Put station back to auto mode. Station operations normal. | Newmarket Bogart Creek Sewage Pumping Station | 2025-10-10
WW-CEAST | October | Weather: 15 C Sunny Wind: 10 Kmh from S On site completed work orders. Station Check (See details on SharePoint) All pumps available in timed auto duty rotation every 4 hours Ran pump 2 in local mode for a few minutes with a flow of 196.7 L/s at 110 kPa discharge pressure. Checked dry well, ok. Turned on power for building ventilation system supply air fan 2. Running now in auto. Hoist System Inspection Odour Control Scrubber System Inspection and Filter Cleaning - mist eliminator filter removed, hosed down and replaced back. JHSC Health and Safety Inspection Standby Power Generator Test Run - pre-test checked, ok. Generator started and stopped running without problem. Generator is now back in auto and available. Cleared/reset all alarms. Station back to normal operations. Also, at 9:00am, Jessica Pascoe from ETO Engineering and Chris Scullion from NAPSCI on site conducted noise assessment for the OCF, building ventilation system supply air fan 2 and standby power generator while it is running. As per requests from Jessica P., auto dialer has been tested. | Newmarket Bogart Creek Sewage Pumping Station | 2025-10-06
WW-CEAST | October | On site to complete consolidated wet well inspection and cleaning. Wet well had just cleaned/removed scum by WESSUC last week - still ok. Checked facility outfall. Removed obstructions, tree branches, etc., leading to the outfall location. Gate door is obstructed by fallen big branches, removed. Exercised overflow sluice gate. Wet well high level alarm test - received and confirmed by ROC. Exercise wet well valves. Checked channel grinder, ok. | Newmarket Bogart Creek Sewage Pumping Station | 2025-10-15
WW-CEAST | October | Raw sewage pump vibration data collection | Newmarket Bogart Creek Sewage Pumping Station | 2025-10-10
WW-CEAST | October | -on site to complete work orders -Dry Well Inspection -Manual Valve Exercise -Discharge Valve Exercise, and Actuator Inspection -Pumps 1-4 Inspection Pump 1 -15% - 83.1 L/s Pump 2 constant speed - 200.1 L/s Pump 3 - 15% - 100.8 L/s Pump 4 - 15% - 85.7 L/s -pumps all operational -turned on unit heaters throughout site due to colder temperatures -station okay | Newmarket Bogart Creek Sewage Pumping Station | 2025-10-09
WW-CEAST | October | Weather today Clear and 12 Celsius. -On site to complete work orders W11257366, W11263919. -On site to perform a station check. -Entered station readings into SharePoint. -Hazardous waste collection and removal. -Checked drywell. -OCU running, supply fan off. -Ran Pump 2 in local for one duty cycle. -All pumps in auto and available. | Newmarket Bogart Creek Sewage Pumping Station | 2025-10-03
WW-CEAST | October | -On site to respond to HVAC General Alarm reported by ROC. Alarm unable to clear remotely. -Upon arrival to site, found ventilation system and MAU all operating normally. Alarm was able to be reset. Checked site, all equipment operating normally. | SEC Boxgove Corrosion Control Facility | 2025-10-21
WW-CEAST | October | -On site to perform a station check and complete work orders. -Station check completed, entered readings into SharePoint. -Chemical tanks maintenance completed. -Chemical tank 1 currently filled with water, Chemical tank 2 filled with 50% hydrogen peroxide. -Ventilation system inspection completed. Turned off chemical tank fans for winter season. Turned on unit heaters for building. -Sump pump test and maintenance completed. Functionally tested all pumps. -Chemical pump 3 running to Shaft 13B. Chemical pumps 1 and 2 in manual off. -Magnum on site for fire panel servicing. | SEC Boxgove Corrosion Control Facility | 2025-10-21
WW-CEAST | October | -On site to complete work orders. -Entered station readings into SharePoint. -Station check completed. -Peristaltic pump inspection completed, pumps 1 and 2 OOS. -Comprehensive housekeeping work orders completed. -Chemical tank 1 filled with water and currently OOS. Chemical Tank 2 in service and filled with 50% hydrogen peroxide. -Chemical pumps 1 and 2 in manual off. Chemical pump 3 running in auto. | SEC Boxgove Corrosion Control Facility | 2025-10-28
WW-CEAST | October | -on site to receive 50% hydrogen peroxide delivery for Tank 2, station check, and work orders -tank 1 has water in it, Tank 2 was emptied to be filled with chemical Tank 1: 3.17 meters - water Tank 2: 0.09 meters - 10% hydrogen peroxide, has been drained down -putting chemical pumps 2 and 3 back to auto, after testing for noise issues that should be fixed -once Tank 2 is filled it will be put to duty 1, active tank -completing work orders -JHSC Inspection -tested pumps 2 and 3 locally before putting them back in service, noise seems normal -ran sump pumps for all 3 sump pits -restored all 3 exhaust fans to service so they can run when ventilation is required -adjusted chemical dosing setpoints on SCADA, concentration from 10% to 50%, dissolved H2S from 0.5 mg/L to 1.0 mg/L, will adjust specific gravity based upon certificate of analysis -received 30,000 kg of 50% hydrogen peroxide in tank 2 Tank 2 Level: 2.72 meters, 24,576 L, 56.6% -put tank 2 to duty 1, online, outlet valve back to auto -running pump 3 in auto to fill suction line to chemical pumps with 50% hydrogen peroxide before calibration is done -putting all 3 pumps local, calibrating all 3 pumps and adjusting SCADA setpoints accordingly -specific gravity on CoA 1.198, SCADA is already set to 1.2 -calibration complete on all 3 chemical pumps, Max Flow Rate: Pump 1: 72.0 L/hr Pump 2: 79.2 L/hr Pump 3: 76.2 L/hr -45 day tested start at 13:16, Tank 2 Level: 2.72 meters, 24,563 L -pumps 1 and 2 manual off for 45 day test, just using pump 3 for test period -reviewed SCADA -entered data into SharePoint -station okay | SEC Boxgove Corrosion Control Facility | 2025-10-07
WW-CEAST | October | @8:30, Tank 2 switched over to Tank 1 due to low level. Remotely dumped Tank 2 for scheduled 50% delivery next week. Chemical pumps 2 and 3 have been fixed by KCL/SPD, awaiting to be put back in service by Ops on next station check. Pump 1 currently running in Auto with water and dosing to 13C While draining tank 2, sump 3 inlet valve failed to open alarm came in twice but was able to clear it remotely. Notified Yash S | SEC Boxgove Corrosion Control Facility | 2025-10-03
WW-CEAST | October | -On site to complete work orders. -Station check completed, readings entered into SharePoint. -Found Fan 3 in auto, but OOS. Changed fan duties and placed Fans 2 and 3 in lead duties. -Nutrient tanks all full, currently all Recirc pumps OOS in manual off. -Worked on Equipment Room 1 Recirculation Pumps. Able to prime both pumps and bleed air out from lines. Test ran both pumps in local, both flows approximately 600L/min. Left recirculating pumps both in auto, timed duty rotate enabled. -Fan lubrication work order completed. -Comprehensive housekeeping work orders completed. -Recirculation Pumps in BioFilter 2 and 3 remain OOS. | SEC Markham Odour Control Facility | 2025-10-28
WW-CEAST | October | On site completed work orders. Station Check (See details on SharePoint) Fans 1 and 2 currently running in auto as duty 1 and 2, respectively. Fan 3 standby. Standby power generator available in auto. Nutrient Tank Batch Mixing - all tanks full of water. All nutrient pumps not running. Odour Control Fans Impeller Bearing Lubrication - fans bearing greased. Recirculation Pumps and Strainer Inspection - all pumps not running. | SEC Markham Odour Control Facility | 2025-10-21
WW-CEAST | October | -On site to complete work orders. -Contractor Magnum on site for fire panel servicing. -Booster pump, solenoid valve, media spray checks completed. -Mist eliminator filters, clean and replace completed. Filters were inspected and found to be in good condition. -Activated Carbon Odour Control Unit 1 and 2 maintenance completed. Rotated carbon unit duties, observed valves and actuators open/close with no issues. Inspected filters, several filters in poor condition and need to be replaced, but correct sized filters are no on site. Will have to return at a later date to replace filters. Each side of carbon unit uses 16 24x24x4 filters. | SEC Markham Odour Control Facility | 2025-10-21
WW-CEAST | October | -On site to confirm power on site for PCS. Multiple communication failure alarms currently present in the area. -Found site had power and equipment was running normally. | SEC Markham Odour Control Facility | 2025-10-29
WW-CEAST | October | Complete vibration monitoring on blowers 2 and 3. Unable to rotate duty due to comms issue. | SEC Markham Odour Control Facility | 2025-10-29
WW-CEAST | October | Station check/generator test run completed and the readings have been entered into the sharepoint. Inspected/greased fans Put all fan discharge valves in local/fully open in response to frequent valve fault alarm. Tested Recirc pumps for EQ room 2 and 3 only, all 4 pumps NOT operational. Both recirc pumps in EQ room 3 missing a plug which can be taken from the other OOS pumps to get it going. | SEC Markham Odour Control Facility | 2025-10-07
WW-CEAST | October | Weather today Partly cloudy and 11 Celsius -On site to complete work orders W11272820, W10651756, W11235437. -Entered readings into SharePoint. -JHSC Health and Safety inspection. -H&S Vehicle 2057 inspection. -Diesel Generator annual maintenance. -Cleared out standing alarms. -Fans 1 and 2 available in auto fan 1 manual OOS. | SEC Markham Odour Control Facility | 2025-10-02
WW-CEAST | October | -station check of site and work orders -reviewed SCADA -entered data into SharePoint -inspected site -Fan Bearing Lubrication/Fan Inspection -Exercise and Inspection Water Supply Pumps/Actuators -Sump Pump Test/Maintenance -HVAC Inspection -Nutrient Tank Inspection -station okay | SEC Markham Odour Control Facility | 2025-10-14
WW-CEAST | October | On site to assist with diesel annual load test with contractor Total Power. Completed | SEC Markham Odour Control Facility | 2025-10-02
WW-CEAST | October | -On site to complete work orders. -Entered station readings into SharePoint. -Checked fan room and generator. -Station check completed. -Manually rotated fan duties. -Electric actuator exercise and inspection completed. -Cleaned filters on Fan 1 and Fan 2 MCCs. | SEC Fairport Air Handling Facility (Shaft 4) | 2025-10-16
WW-CEAST | October | -station check of site -reviewed SCADA -entered data into SharePoint -inspected site -restocked washroom with soap and cleaner -station okay | SEC Fairport Air Handling Facility (Shaft 4) | 2025-10-30
WW-CEAST | October | On site to check standby power generator not in auto alarm happened around 12:30am October 1st. Upon arrival on site, checked station. Found generator ATS is in auto. Found generator in STOP position and with control switch not in auto warning alarm. Acknowledged and reset alarm. Also, cleared/reset alarm on SCADA. Generator back in auto and available. | SEC Fairport Air Handling Facility (Shaft 4) | 2025-10-01
WW-CEAST | October | -On site to complete work orders. -Station check completed, readings entered into SharePoint. -Checked fan room and generator. -Heat trace system inspection completed. Setpoint at 5C, system currently at 10C. -Hoist system inspection completed, test overhead crane with no issues. | SEC Fairport Air Handling Facility (Shaft 4) | 2025-10-09
WW-CEAST | October | -On site to complete work orders. -Station check completed, readings entered into SharePoint. -Checked fan room and generator. -Monthly diesel generator test run completed, readings entered into SharePoint. -1236 - Transferred site to generator power. -1336 - Transferred site back to utility power. -Generator start hours: 250.1, stop hours: 251.2, run time: 1.1hrs. -Monthly JHSC H&S inspection completed, no issues noted. | SEC Fairport Air Handling Facility (Shaft 4) | 2025-10-02
WW-CEAST | October | -On site to complete work orders. -Station readings entered into SharePoint. -Checked fan room and generator. -Station check completed. -Manual rotated fan duties. -Electric actuator, exercise and inspection completed. | SEC Altona Air Handling Facility (Shaft 6/7) | 2025-10-16
WW-CEAST | October | -station check of site -reviewed SCADA -entered data into SharePoint -inspected site -restocked washroom with soap and cleaner -station okay | SEC Altona Air Handling Facility (Shaft 6/7) | 2025-10-30
WW-CEAST | October | -On site to complete work orders. -Station check completed, readings entered into SharePoint. -Checked generator and fan room. -Ventilation system inspection completed. -Heat trace system inspection completed. | SEC Altona Air Handling Facility (Shaft 6/7) | 2025-10-09
WW-CEAST | October | -On site to complete work orders. -Station check completed, readings entered into SharePoint. -Checked fan room and generator. -Monthly diesel generator test run completed, readings entered into SharePoint. -1037 - Transferred site to generator power. -1146 - Transferred site back to utility power. -Generator start hours: 214.7, stop hours: 216.0, run time: 1.3hrs. -Monthly JHSC H&S inspection completed, no issues noted. | SEC Altona Air Handling Facility (Shaft 6/7) | 2025-10-02
WW-CEAST | October | -On site to respond to Fan not Running Alarm reported by ROC. -Upon arrival to site found that fan was running in normal operation. -Reset alarm on dialer. Fan is running, no odours detected on site. | Bayview & Steeles Air Management Facility | 2025-10-19
WW-CEAST | October | -On site to investigate odour complaint that came in this morning as Case #4258970. -Found all equipment operating normally, no abnormal odours on site. Also investigated neighbourhood on Whitelaw Court where complaint originated, but also found no unusual odours. Will follow up with supervisor and complainant. | Bayview & Steeles Air Management Facility | 2025-10-28
WW-CEAST | October | -On site to investigate odour complaint received through Access York this morning, case #4255020. -Station operating normally, fan is running, no unusual odours detected. Completed site walkthrough, followed up with resident. Resident agreed odour is no longer present. Odour last noticed approximately Oct. 4-8. | Bayview & Steeles Air Management Facility | 2025-10-22
WW-CEAST | October | -On site for Pre-bid site visit with multiple bidders and engineering team. -Performed station check while on site. -Heater element: 96.9F. -Hydro meter: 258838kWh. -Fan is running. | Bayview & Steeles Air Management Facility | 2025-10-20
WW-CEAST | October | -On site to perform a station check. -Heater element: 100.6F. -Hydro meter: 257869kWh. -Fan is running, no odours detected on site. | Bayview & Steeles Air Management Facility | 2025-10-15
WW-CEAST | October | -On site to complete work orders. -Station check completed. -Heater element: 98.3F. -Hydro meter: 256094kWh. -Mist eliminator filters all remove and changed out with clean filters. -Fan turned off from 09:25?09:45 to replace filters. -Odour control scrubber inspection filter cleaning completed. -JHSC H&S inspection completed for the month, no issues noted. -Facility outfall inspection and cleaning completed. | Bayview & Steeles Air Management Facility | 2025-10-06
WW-CEAST | October | Complete vibration monitoring on both blowers and motors. | SEC Pickering Odour Control Facility (York/Durham) | 2025-10-29
WW-CEAST | October | Replaced 2 generator 4D batteries. Belts look okay. Complete | SEC Pickering Odour Control Facility (York/Durham) | 2025-10-29
WW-CEAST | October | -station check of site and work orders -reviewed SCADA -entered data into SharePoint -inspected site -nutrient tank inspection -blower inspection -recirc pump inspection -booster pump inspection -Housekeeping -station okay | SEC Pickering Odour Control Facility (York/Durham) | 2025-10-30
WW-CEAST | October | On site completed work orders. Station Check (See details on SharePoint) Nutrient tanks and pumps offline. Tanks full. Fan 1 still OOS and in manual/off. | SEC Pickering Odour Control Facility (York/Durham) | 2025-10-16
WW-CEAST | October | -On site to complete work orders. -Station check completed, readings entered into SharePoint. -JHSC H&S monthly inspection completed, changed out eyewash solution, no issues noted. -Diesel generator monthly test run completed. -1020 - transferred site to generator power. -1120 - transferred site back to utility power. -Fan 1 OOS, nutrient tanks and pumps OOS. | SEC Pickering Odour Control Facility (York/Durham) | 2025-10-09
WW-CEAST | October | Under direction of OIC Daniel Kim. Notified ROC of the testing of alarms for GEN_TK1_LIT1. Worked with contractors to calibrate and commission diesel tank LIT. | SEC Pickering Odour Control Facility (York/Durham) | 2025-10-07
WW-CEAST | October | -On site to perform a station check. -Entered station readings into SharePoint. -Nutrient tanks and pumps offline. -Fan 1 remains OOS. | SEC Pickering Odour Control Facility (York/Durham) | 2025-10-02
WW-CEAST | October | -performed inspection of 3 PHMS sites -ensured heaters are working, alarms are cleared, area around is okay, site is secure, re-armed site 1. Beare Rd. 2. Shaft 8 3. Gordon Murison | Central-East Wastewater Linear System | 2025-10-16
WW-CEAST | October | On-site to reinstate flow back into 16th ave trunk sewer after the completion of rehab work. Asset # 411901726 relief sewer valve has been closed Asset# 411901727 main knife-gate to 16th ave trunk sewer has been fully open Asset# 411901400 Markham sewer tie-in valve has been fully open Observed flow going through woodbine/16th chamber, no issues Markham has done the valving to divert 100% flow to our 16th ave trunk sewer. | Central-East Wastewater Linear System | 2025-10-28
WW-CEAST | October | NMMCHT Onsite for annual calibrations Informed Informed ROC Used cal mode on scada during the procedure Only FIT worked on Cleared associated alarms Informed ROC, armed building and left site | Central-East Wastewater Linear System | 2025-10-20
WW-CEAST | October | Investigated odor complaint received by ROC. 11685 Yonge street RH. Noticed significant positive pressure with the 2 MH lids open @ Jefferson forest/11685 yonge street. Changed carbon media for Jefferson forest. Put tough garbage bag over the MH and closed the lid for 11685 yonge street. Also spray foamed around the MH lid/pick holes. Observed no odor coming out anymore after it has been fully covered. | Central-East Wastewater Linear System | 2025-10-24
WW-CEAST | October | -passive odours scrubbers at King and Yonge, and Northlake and Yonge have been capped, and are no longer in service -replaced media in Jefferson Forest and Yonge passive scrubber -seems to be slightly less positive pressure at Jefferson Forest, however there is still pressure there | Central-East Wastewater Linear System | 2025-10-22
WW-CEAST | October | -On site at Yonge and 19th with CPD and traffic protection to open 19th ave valve and reinstate flows. Tried for hours to open lid to valve box, but were unsuccessful. Ran out of time with traffic protection and had to wrap up for the night without being able to open the 19th ave valve box. CPD suspects the entire valve box may be damaged and is planning to revisit in the near future with additional support. 19th ave valve remains closed, Yonge st valve remains open. | Central-East Wastewater Linear System | 2025-10-29
WW-CEAST | October | -On site for passive scrubber inspections. -Completed inspections for Warden/Enterprise, Hwy 7/Bullock, Milne Park, Tuclor Lane, Woodbine/16th, Leslie/Major Mackenzie. -Changed out carbon media as required. -Large holes in bottom screen of Tuclor Lane passive scrubber noted, will be repaired at a later date when extra screen material is available. | Central-East Wastewater Linear System | 2025-10-07
WW-CEAST | October | On site for Aurora West Forcemain and Henderson Twin Forcemains Chamber Inspection Run. 28-CH01 - chamber almost half full of water/pumped out. 28-CH02 28-CH03 01-CH01 - chamber has around two feet deep of water/pumped out. | Central-East Wastewater Linear System | 2025-10-15
WW-CEAST | October | -Completed passive scrubber media inspections for Yonge/North Lake and Yonge/King scrubbers. Changed out carbon media at both locations. | Central-East Wastewater Linear System | 2025-10-15
WW-CEAST | October | -Completed passive scrubber media inspections for Yonge/North Lake and Yonge/King scrubbers. Changed out carbon media at both locations. | Central-East Wastewater Linear System | 2025-10-08
WW-WEST | October | Swapped rag bins and placed the full one outside for pickup | Vaughan Black Creek Pumping Station | 2025-10-28
WW-WEST | October | Completed station check. No issues found. Entered data in spreadsheet. | Vaughan Black Creek Pumping Station | 2025-10-27
WW-WEST | October | Tested high wet-well level alarm by adjusting SCADA set points. ROC received alarm. Completed station check. Created work order for pump 4, as it is spitting from its mechanical seal and the seal water doesn?t seem to be flowing. No other issues found. Inspected raw sewage pumps. P1: 594.7 l/sec P2 @ 100%: 450 l/sec P3 @ 100%: 135 l/sec P4 @ 100%: 460 l/sec P5: 553.2 l/sec. Changed LIT1-4 high level alarm set-points to 4.25 m from 9.00 m. The backup control panel takes over at 4.5 m. Raked rag bin. | Vaughan Black Creek Pumping Station | 2025-10-24
WW-WEST | October | On site to investigate 120v receptacles on level B4. Receptacle, enclosure and wiring damaged by seepage through wall. B4 receptacle feeder isolated on B3. Receptacles on B4 de-energized until plan for replacements can be implemented. | Vaughan Black Creek Pumping Station | 2025-10-27
WW-WEST | October | Returned emptied bin to inside storage location. Completed station check. No issues found. Entered data in spreadsheet. Test ran pumps 1 - 5. Started moping floors in main room. | Vaughan Black Creek Pumping Station | 2025-10-30
WW-WEST | October | Completed station check. No issues found. Raked rag bin. Test ran pumps 1, 2, 4 and 5. | Vaughan Black Creek Pumping Station | 2025-10-17
WW-WEST | October | Completed the station check Test ran the rs pumps Greased and cleaned the bar screen Leveled the rag bin Inspected the seal water system | Vaughan Black Creek Pumping Station | 2025-10-10
WW-WEST | October | Completed station check. No issues found. Entered numbers in spreadsheet. Put empty bin back in screen room. Greased SF 2 bearings. | Vaughan Black Creek Pumping Station | 2025-10-15
WW-WEST | October | Completed station check. No issues found. Entered numbers in spreadsheet. Returned empty bin. | Vaughan Black Creek Pumping Station | 2025-10-01
WW-WEST | October | Completed station check. No issues found. Entered numbers in spreadsheet. | Vaughan Black Creek Pumping Station | 2025-10-08
WW-WEST | October | Completed station check. No issues found. Entered numbers in spreadsheet. Test ran generator 1. Start: 474.6 hrs, 104 cm/6713 L Stop: 475.9 hrs, 103 cm/6668 L Test ran generator 2. Start: 487.3 hrs, 103 cm/6668 L Stop: 488.5 hrs, 103 cm/6624 L Completed JHSC inspection with no findings. Could not inspect heat exchanger as it is on the roof. Checked for, but didn?t find any, hazardous waste. Inspected RS pump ball valves and actuators. Inspected check valves. Inspected sump pit and system. Inspected odour control scrubber system. Filter change not needed at this time. Inspected bubbler system. Inspected hoist. Tested dry well flood alarm. ROC received alarm. Tested hi/lo temperature alarms. ROC received alarm. | Vaughan Black Creek Pumping Station | 2025-10-06
WW-WEST | October | Completed station check. No issues found. Entered numbers in spreadsheet. | Vaughan Black Creek Pumping Station | 2025-10-03
WW-WEST | October | Set full rag bins out for pickup. Replaced empty bin under screen. Cleared rags off floor. Replaced pump 3 VFD air filters. Exercised valves HV1 and 2 on forcemains 1 and 2. Inspected air relief valves. Exercised suction valves with actuators. | Vaughan Black Creek Pumping Station | 2025-10-14
WW-WEST | October | Manually test ran pumps 1 and 5. | Vaughan Black Creek Pumping Station | 2025-10-03
WW-WEST | October | Rake inlet screen room rag bin. | Vaughan Humber Pumping Station | 2025-10-26
WW-WEST | October | Please note: Work performed on site, not remotely. Assisted Lauren with setup for wetwell cleaning. Completed station check. No issues found. Tested high wetwell float. ROC received alarm. Inspected availabe RS pumps: P3@100%: 630 l/sec. P4: 643 l/sec. P5: 320 l/sec. | Vaughan Humber Pumping Station | 2025-10-27
WW-WEST | October | Completed the station check Entered data into SharePoint Assisted sewer by law in setting up two auto samplers in the wet well Everything operating as intended | Vaughan Humber Pumping Station | 2025-10-30
WW-WEST | October | Completed station check. No issues found. Raked bins. Entered data in spreadsheet. | Vaughan Humber Pumping Station | 2025-10-20
WW-WEST | October | Contacted by ROC for mechanical screen 2 fault. Arrived and found screen to faulted with an interlock as well. Motor overload indicator on. Visually inspected top sprockets and looked down at flight and chains - no obvious issues . Attempted to reset the screen and it immediately tripped again as soon as the motor engaged. Attempted to run in reverse with the same result. Create follow up cmu and notify maintenance team lead. | Vaughan Humber Pumping Station | 2025-10-27
WW-WEST | October | Completed station check. No issues found. Entered data in spreadsheet. Raked bins. Returned emptied bins to screen room. | Vaughan Humber Pumping Station | 2025-10-24
WW-WEST | October | Wet well cleaning completed Reopened all valves in the wet well and returned the plant to normal operation | Vaughan Humber Pumping Station | 2025-10-27
WW-WEST | October | Isolated bar screen 2 | Vaughan Humber Pumping Station | 2025-10-28
WW-WEST | October | Placed bins with repaired wheels under screens after shoveling rags off the floor in to the bins. | Vaughan Humber Pumping Station | 2025-10-21
WW-WEST | October | Switched wetwells for cleaning. Opened valve to fill well 1. Closed valve as best we could to isolate well 2. Set well duty to well 1. 2 OOS. Set pumps 1 and 2 to duty 1 and 2. Used pump 3 to pump well2 down to the bottom. | Vaughan Humber Pumping Station | 2025-10-27
WW-WEST | October | Set full bins out for pickup. Left two broken bins out for repair. Rags being deposited on the floor. | Vaughan Humber Pumping Station | 2025-10-21
WW-WEST | October | Onsite to meet GFL for wet well cleaning. Disabled low level lockout on back up panel, Isolated wet well 1 with interconnect valve closed and inlet valve closed. Pumps 1 and 2 in manual OOS | Vaughan Humber Pumping Station | 2025-10-27
WW-WEST | October | On site for barscreen #2 OOS. Found barscreen jamming up. All chains sprockets and motor break in working order. Will need to pump down channel to see if any foreign objects are jammed into the rake at bottom of the barscreen. | Vaughan Humber Pumping Station | 2025-10-28
WW-WEST | October | Closed inlet gate to screen 2. Collected weekly running pump samples. Set full bins out for pickup and put empty bins under screens. | Vaughan Humber Pumping Station | 2025-10-28
WW-WEST | October | Raked bins. | Vaughan Humber Pumping Station | 2025-10-19
WW-WEST | October | On site to assist maintenance with barscreen 2 repair. Checked screen. Found no real issues. Closed wetwell interconnect valve. Set wetwell 2 out of service. Pumped wetwell 2 down below bar screen channel. Inspected actual screen down in the channel and found it full of wheels, concrete and asphalt. Removed 'junk' from in the screen in channel and the channel itself. Tested screen, which seemed to work successfully. Opened interconnect valve. Set wetwell 2 back in service on SCADA. Opened inlet valve for screen 2. Monitored screen. Worked well. All returned to normal. Put empty bins back inside. | Vaughan Humber Pumping Station | 2025-10-29
WW-WEST | October | On site for barscreen #2 jammed. Found barscreen jamming up with metal and asphalt. Cleared foreign materials, ran tested barscreen and put back into service. | Vaughan Humber Pumping Station | 2025-10-29
WW-WEST | October | Cleaned and lubricated the bar screen | Vaughan Humber Pumping Station | 2025-10-27
WW-WEST | October | Completed the station check Pushed the rag bins back inside the screen room Everything operating as intended | Vaughan Humber Pumping Station | 2025-10-08
WW-WEST | October | Pump 2 check valve investigation, Removed rags, cleaned rotating shaft of debris. Moves freely Back in service and tested | Vaughan Humber Pumping Station | 2025-10-07
WW-WEST | October | On site to assist Matt and Terry with pump 2 check valve investigation. Set full rag bins out for pickup. Replaced empty bins to collect rags. Inspected YP/YDSS diversion chamber. Tested high alarm. ROC received alarm. Inspected facility outfall. Actuated forcemain and interconnect valves. Inspected and greased RS pumps. After check valve repair, set pump two to duty two and tested for a few cycles. Worked well. Left in duty rotation. Set pump three to auto speed. | Vaughan Humber Pumping Station | 2025-10-07
WW-WEST | October | Completed station check. Entered numbers in spreadsheet. Put floor rags in to emptied bin. Placed emptied bin under screen. Noted second bin has broken wheel. 2 bins left outside awaiting wheel replacement. Notified team lead of broken wheel. | Vaughan Humber Pumping Station | 2025-10-15
WW-WEST | October | Collected samples from running pump 1. | Vaughan Humber Pumping Station | 2025-10-14
WW-WEST | October | On site to rake bins | Vaughan Humber Pumping Station | 2025-10-04
WW-WEST | October | Collected the weekly samples | Vaughan Humber Pumping Station | 2025-10-07
WW-WEST | October | Completed the station check Leveled the rag bins Everything operating as intended | Vaughan Humber Pumping Station | 2025-10-10
WW-WEST | October | Turned on EF14 in anticipation of forecast hot weekend weather. Completed station check. No new issues found. Entered numbers in spreadsheet. | Vaughan Humber Pumping Station | 2025-10-03
WW-WEST | October | Level screen room rag bins and shift for better weight distribution. Note there was a lot of rag build up and was falling back in the channel on both sides. | Vaughan Humber Pumping Station | 2025-10-12
WW-WEST | October | Completed the station check Everything operating as intended | Vaughan Humber Pumping Station | 2025-10-06
WW-WEST | October | Set full rag bins out for pickup. Replaced 1 empty bin under screen 1. Other empty bin outside waiting for wheel replacement. Screen 2 rags piling on floor temporarily. | Vaughan Humber Pumping Station | 2025-10-14
WW-WEST | October | - Enabled RAS batch wasting mode then wasted 20 m^3 from train 1 and 20 m^3 from train 2. Once done, reset RAS batch wasting mode - Added 8 bags of soda ash into the hopper - Checked station and recorded readings, no new issues - Performed inhouse lab and recorded readings on SharePoint | Kleinburg Water Resource Recovery Facility | 2025-10-31
WW-WEST | October | - Performed inhouse lab and recorded readings on SharePoint. All okay - Checked station and recorded readings on SharePoint. No new issues - Added 8 bags of soda ash - Placed the WAS pumps back to manual off. Wasted 40 m^3 total | Kleinburg Water Resource Recovery Facility | 2025-10-20
WW-WEST | October | On site to repair a leak on the water meter bypass line. Found a loose union and tighten it and installed it with new insulation | Kleinburg Water Resource Recovery Facility | 2025-10-22
WW-WEST | October | - Performed in-house lab and recorded readings on SharePoint - Did not waste to bring the solids up - Checked station and recorded readings. No new issues - added 8 bags of soda ash. Cleaned floors | Kleinburg Water Resource Recovery Facility | 2025-10-17
WW-WEST | October | Attending site to check Oxygen sensor in sludge control room - AIT3 (W11373829). Replaced sensor and calibrated. Also calibrated milliamp loop. ROC was notified and SCADA alarms were cleared. | Kleinburg Water Resource Recovery Facility | 2025-10-23
WW-WEST | October | Collected weekly compliance samples. | Kleinburg Water Resource Recovery Facility | 2025-10-21
WW-WEST | October | Enabled RAS timer at 8:40. Set auto wasting for 8 cycles of 5 m3 between 10 and 12 for a total of 20 m3 per train. Return pumps in auto when complete. Completed labs. Added 7 bags soda ash to hopper. Collected rags from valve stems and end of aeration tank. Inspected odour control machine. Completed station check. No issues found. Tested filter bypass float alarm. ROC received alarm. | Kleinburg Water Resource Recovery Facility | 2025-10-21
WW-WEST | October | - Added 8 bags of soda ash into the hopper - performed in-house lab and recorded readings on SharePoint - Did not waste to bring the solids up - Due to sludge blanket being consistently higher for clarifier 1. Opened two aeration tank 2 outlet sluice gate by another inch. Lowered aeration tank 1 outlet sluice gate by 1 inch. Increased RAS for train 2 to 23 l/s from 20 l/s - Checked station and recorded readings on SharePoint - Removed condensation from air lines - Moved hose to aeration tank 2 outlet for foam control - Added some water into the scum tank and manually pumped it down - Created work order to address sludge building low oxygen level alarm - Created work order for swipe pad not working for the filter building basement entrance - Inspected UV 1 and 2. All okay | Kleinburg Water Resource Recovery Facility | 2025-10-16
WW-WEST | October | - Collected weekly regulatory samples and drove them to Janet - Performed in-house lab and recorded readings on SharePoint - Huge amounts of rags blocked the aeration tank 2 inlet causing the inlet channel to rise and some flow made its way to aeration tank 1. - aeration tank 1 level was slightly above the diffusers. Notified TL - removed lots of rags from aeration inlet and outlet - Pumped down aeration tank 1 using two submersible pumps - Enabled RAS batch wasting mode and wasted 18 m^3 total then reset RAS batch wasting mode once done - Checked station and recorded reading - GFL on site to take a load of sludge - concrete condition assessment occurred for aeration tank 1 and diversion tank - Checked ordour control unit, all okay Update: Changed filter duty 2 start flow to 20 L/s from 30 L/s | Kleinburg Water Resource Recovery Facility | 2025-10-28
WW-WEST | October | Added 14 bags of soda ash to hopper. Enables RAS timer remotely at 07:08. Set autowasting to 8 cycles between 9 and 11, 0.2 hours each, total of 20 m3 per train. Picked rags from valve stems and raked inside bar screen. | Kleinburg Water Resource Recovery Facility | 2025-10-19
WW-WEST | October | Inspected tertiary building sump. ROC received high level alarm. Inspected headworks building PS. ROC received high level alarm. Inspected final effluent sampler. All okay. Inspected raw sewage sampler. All okay. Cleaned UV/FE channel. | Kleinburg Water Resource Recovery Facility | 2025-10-16
WW-WEST | October | On site for sump pump 2 alarms. I will order a new pump and return with the small crane | Kleinburg Water Resource Recovery Facility | 2025-10-27
WW-WEST | October | Set up auto wasting to begin at 8am. Batch wasting mode enabled. Total WAS set for 40m3 split between both sides of the plant. | Kleinburg Water Resource Recovery Facility | 2025-10-26
WW-WEST | October | - Worked with Gavin Walker and Daniel Hirstwood. Made entry into the aeration tank 1 to change the diffuser membranes - Removed the final submersible pump from aeration tank 1 | Kleinburg Water Resource Recovery Facility | 2025-10-29
WW-WEST | October | - Added 12 bags of soda ash into the hopper - Performed in-house lab and recorded readings on SharePoint - Property services on site to replace various outdoor bulbs - Transferred sludge from the thickening tank to the sludge holding tank - Enabled RAS batch wasting mode. Wasted 15 m^3 from train 1 and 15 m^2 from train 2 then reset RAS batch wasting mode once done - Checked station and recorded readings - Cleaned wash pump screen after notifying ROC and locking out pumps. No issue performing work. Created wash pump related alarms - Noticed huge block of rags in the aeration tank 2 outlet. Due to the aeration tank cleaning, and decanting process performed by Wessuc last week. Notified TL and called for an emergency vac truck due to the sheer volume of rags. In the outlet. Wessuc arrived at roughly 14:00 and started setting up | Kleinburg Water Resource Recovery Facility | 2025-10-27
WW-WEST | October | Shut ras pumps off at 8:50. Set auto wasting to waste 15 m3 per train between 11 and 13:00. Cleaned rags out of ras pumps 4 and 2. Opened up pumps 1 and 3 but found no rags. Ras pumps back on at 13:08. Noted some solids carrying over the weirs in clarifier 2. Likely caused by RAS pump issues. Adjusted ras flow rates to 20 l/sec for both trains. Coupling on pump 4 worn out and broken. Ras pump 4 in manual off. Made work order for coupling replacement. Added 7 bags soda ash to hopper. Completed station check. No other issues found. Completed labs. Entered data in spreadsheet. Checked clarifiers at end of day. No more solids at weirs. | Kleinburg Water Resource Recovery Facility | 2025-10-23
WW-WEST | October | - Added 8 bags of soda ash into the hopper - Checked station and recorded readings on SharePoint. No new issues - DO probe is all good - Performed in-house lab and recorded readings on SharePoint. To boost alkalinity slightly. Adjusted soda ash conveyor runtime from 5.00 sec to 5.25 sec - Removed one submersible pump from aeration tank 1 to be used elsewhere - Helped unload davit base and arm near aeration tank 1 access ladder update: Enabled RAS batch wasting mode at 9:03. Wasted 9 m^3 from train 1 and 9 m^3 from train 2 then reset RAS batch wasting mode at 10:55 | Kleinburg Water Resource Recovery Facility | 2025-10-29
WW-WEST | October | - Performed in-house lab and recorded readings on SharePoint - Enabled RAS batch wasting mode. Wasted 20 m^3 from clarifier 1 and 20 m^3 from clarifier 2 then reset RAS batch wasting mode once done - Added 8 bags of soda ash into the hopper - Checked station | Kleinburg Water Resource Recovery Facility | 2025-10-24
WW-WEST | October | Remote batch wasting completed. Put RAS pumps back in service and was pumps in manual/off. Added 7 bags of soda ash to the auto dispenser hopper. | Kleinburg Water Resource Recovery Facility | 2025-10-26
WW-WEST | October | - Performed in-house lab and recorded readings on SharePoint - Did not waste today to bring the solids up - Checked station and recorded readings. No new issues - Added 8 bags of soda ash into the hopper - Cleaned lab and washroom. Other buildings all clean | Kleinburg Water Resource Recovery Facility | 2025-10-30
WW-WEST | October | Software code the Critical Fault and Shutdown Alarms in both UV1 and UV2 with Latched Alarms in the Filtration PAC. Document modifications in Rockwell Asset Center as required. Communicate changes to the ROC and Local User Group (Area WW West) | Kleinburg Water Resource Recovery Facility | 2025-10-01
WW-WEST | October | - Cleaned the sides of aeration tank for condition assessments - Added 11 bags of soda ash - performed in-house lab and recorded readings on SharePoint. No issues - Checked station and recorded readings. No new issues - Inspected travelling bar screen. No issues. Greased fittings - Inspected grit dewatering screw. No issues - Inspected screenings compactor. No issues - Inspected vortex 1 and 2. No issues. Greased fittings - At roughly 11:50. UV2 multiple ballast fault alarm came on for bank B. Upon examination, it was a false alarm. All ballasts were running for bank B with no burnt out bulbs. Reset fault. Created work order - Enabled RAS batch wasting mode at 11:00. Wasted 55 m^3 total then reset RAS batch wasting mode once done - Removed rags from aeration outlet - Checked DO probe. All okay - Unplugged pump and - Filter 2 level sensor seems to be sticking. Will continue to monitor - Filter 3 sluice gate was stuck in travelling mode. Manually closed the gate and reset fault - Increased aeration basin DO setpoints from 2.8 ppm to 3.3 ppm - To avoid hitting filtration inlet high alarms and for filters to kick in sooner. Adjusted filter 3 start flow to 40 L/s from 50 L/s. Adjusted filter 4 start flow to 65 L/s from 75 L/s. - Pumped down diversion tank | Kleinburg Water Resource Recovery Facility | 2025-10-06
WW-WEST | October | - Finished cleaning generator room - Trojan UV contractor found hydraulic oil leak while performing inspection. Leak coming from hose on UV2 bank A 3rd cassette. Wiper will not function for the 3rd cassette due to hydraulic hose being unattached. Will order new parts - Unplugged filter 3 north side - Checked ordour control unit. No issues - Instrumentation fixed filter 3 headloss transmitter. Filter 3 headloss level out of range in shelved. Filter 3 headloss level hihi alarm unshelved. Filter 3 stage 2 head loss alarm unshelved | Kleinburg Water Resource Recovery Facility | 2025-10-01
WW-WEST | October | - Added 7 bags of soda ash into the hopper - Performed in-house lab and recorded readings on SharePoint - Checked station and recorded readings. No new issues - Checked ordour control unit. No issues - Enabled RAS batch wasting mode at roughly 9:50. Wasted 25 m^3 from train 1 and 20 m^3 from train 2 then reset RAS batch wasting mode at 13:35 - Checked facility outfall. Outfall is really clean and not obstructed - Checked DO probe and removed rags - Decanted the sludge thickening tank 1 then transferred sludge into the holding tank - Placed hose at aeration tank 1 outlet for foam control | Kleinburg Water Resource Recovery Facility | 2025-10-15
WW-WEST | October | Inspected RAS, WAS pumps Exercised RA, WAS valves Inspected WAS check valves | Kleinburg Water Resource Recovery Facility | 2025-10-07
WW-WEST | October | W11332980 On site to investigate low-level lockout on UV channel 2 found probe to be damaged and loose connections to probe. tightened connections, cleaned, and lubricated couplings reinstalled then placed back into service with no alarms placed in auto to monitor | Kleinburg Water Resource Recovery Facility | 2025-10-08
WW-WEST | October | Attending site to check TFLT_FILT3_LT3 not powering up (W11328388). Replaced transmitter and configured. ROC was notified before and after work was performed. | Kleinburg Water Resource Recovery Facility | 2025-10-01
WW-WEST | October | De-ragged pumps in aeration tank 1, lowered and restarted pumping to tank 2. Collected samples for labs. Noted really low solids in aeration tank. Adjusted RAS/WAS valving so both RAS systems are discreet and functioning normally. Changed valving at head of aeration tanks so clarifier 1 RAS is deposited in the inlet channel, rather than into the aeration tank. Set all 4 RAS pumps to run to help transfer solids for approximately 20 minutes. Completed labs and entered numbers in spreadsheet. Numbers were a little unusual based on all of the above information. Closed air valves 3 and 4 on aeration tank 2 by two notches to direct more air to the tank inlet to better manage returning solids. Placed DO and SS probes from aeration tank 2 in buckets of water to keep moist and protect from direct sunlight. Wasted 40 m3 from clarifier 1. Lowered supernate valve on sludge tank 1 to return 10 m3 back to the process. Raised valve when complete. Set RAS pumps 2 and 4 in auto, auto speed, flow control, flow set at 15 l/sec. This is normal operation. All RAS/WAS basement valves in correct/normal positions. RAS P2 discharging into the inlet, which feeds tank 2. Hosed algae and 'crud' off of level floats in filters. This caused filter 2 airlift to stop lifting. Returned filter 2 to auto. Set filter 2 to duty 5 (out of service) as it requires some weir plates to function satisfactorily. Changed duty 2 filter stop flow from 18 l/sec to 10 l/sec to better reflect influent flow rates and filter needs. Should reduce unnecessary starting and stopping of duty 2. Added 15 bags soda ash to ash hopper. De-ragged pumps in aeration tank and lowered at end of day. | Kleinburg Water Resource Recovery Facility | 2025-10-02
WW-WEST | October | - Collected weekly regulatory samples - Added 16 bags of soda ash - Enabled RAS batch wasting mode roughly at 9:20. Wasted 15 m^3 from train 1 and 8 m^3 from train 2 then reset RAS batch wasting mode once done - Aeration header and distribution valves all okay - Removed rags from aeration outlet - Cleaned scum tank and pumped it down - Performed in-house lab and recorded readings on SharePoint. No new issues. Due to high consistent alkalinity. Lowered soda ash conveyer runtime from 5.25 seconds to 5 seconds - Checked station and recorded readings. Now new issues - Reset low oxygen gas alarm | Kleinburg Water Resource Recovery Facility | 2025-10-14
WW-WEST | October | Completed station check. Found aluminum pump 2 discharge hose between PRV and flow sensor had broken off entirely. Replaced with new length of hose. Primed hose and returned to service. Completed labs. Retested clarifier TP several times due to bad vials. Ultimately received proper results. Entered numbers in spreadsheet. Inspected circular clarifier. All okay except for: Created work order to have the power light and dome replaced on clarifier control panel. Inspected rectangular clarifiers. No issues found. | Kleinburg Water Resource Recovery Facility | 2025-10-09
WW-WEST | October | - Added 16 bags of soda ash into the hopper - Due to aeration tank 1 draining. Alarms were created such as aeration basin 1 solids fault. Shelved various alarms. Shelved two or more RAS pumps not available. Shelved two or more RAS pump not available. Shelved RAS pump 1 and pump 2 E-stop alarm. Aeration basin 1 front DO out of range alarm shelved - Due to dead filter 3 headloss transmitter (WO created) shelved various alarms until it can be resolved. Filter 3 headloss level out of range shelved. Filter 3 headloss level hihi alarm shelved. Filter 3 stage 2 head loss alarm shelved - Performed in-house labs and recorded readings on SharePoint. Numbers are elevated due to draining aeration tank 1 to tank 2. Draining will take couple more days - Checked station and recorded readings on SharePoint. No new additional issues - Enabled RAS batch wasting mode at 9:20. Wasted 20 m^3 from train 2 then reset RAS batch wasting mode once done - Notified ROC of the work being performed - Performed JHSC inspection. No issues. Tested eyewash. Admin bldg eye wash flow high alarm received | Kleinburg Water Resource Recovery Facility | 2025-10-01
WW-WEST | October | - Test ran generator 1 and 2 starting from 16:26 to test UV function during generator test - Placed UV 1 and 2 into local on - Known issue but testing again to confirm. Testing revealed that after ATS power transfer for generator 1, generator 1 will shut off UV1 because generator 1 powers UV1. After ATS power transfer for generator 2, generator 2 will shut off UV2 because generator 2 powers UV2. - Due to this, during power transfers or monthly generator test, if testing generator 1, UV 2 should be running in duty to prevent UV1 from shutting off. The reverse for generator 2, for generator 2, UV1 should be running in duty to prevent UV2 from shutting off. This will ensure UV dosage is applied at all times. Notified team, supervisor and TL. - In addition, during power transfers UV channel 2 Bank A tends to fault due to power loss, causing "UV channel 2 Bank A power loss fault alarm". This tends to happen more frequently with generator 2 ATS. Will create a work order to address power loss fault for UV2 Bank A - Due to this work, multiple UV and process alarms were created. Such as, UV channel 2 bank 1a power loss fault, sec clarifier 1 and 2 overload alarm, soda ash conveyor e stop alarm, uv channel 2 bank 1a major alarm, uv channel 2 common major alarm, uv system 2 warning alarm, Site hydro power failure alarm, aut transfer switch e pow, mechanical screen lockout alarm, disel gen run alarm, mechanical screen gen alarm. Cleared all alarms and checked duties. - UV dosage was applied at all times and when testing suspected UV channel that was likely to shut off, adjusted the inlet sluice gate to close - Received call from ROC about influent channel 1 and 2 hitting hihi alarm. This is due to the higher flows coming in in addition to aeration tank 1 draining into aeration tank 2. Due to this, Placed filter 2 sluice gate to manual open and set filter 2 to run over night to prevent filters from opening and closing to catch up to higher influent channel level. - Will continue to monitor filter inlet channel and run more filters if it rises. | Kleinburg Water Resource Recovery Facility | 2025-10-01
WW-WEST | October | Wasting completed. Was pumps placed in manual off. Reset batch wasting mode and RAS pumps are running. Total WAS: side 1: 20.07m3 side 2: 19.95m3 | Kleinburg Water Resource Recovery Facility | 2025-10-12
WW-WEST | October | Trojan contractor was servicing UV Channel 2 Bank A and B for semiannual maintenance, and replaced the low level probe. The new probe was placed in but it ended up causing low level fault and level signal fault on UV2. He determined that it was the relay not functioning properly and not sending the signal back to the HMI. He tested this theory by removing the probe and trying to trigger a low level fault, which did not show alarms on HMI. He went further later on and wanted to test UV2's relay by using UV1's relay. Contractor removed the relays from UV1 bank a and b while UV1 was active, in duty 1 and running. Hence, UV1 shut off immediately due to the relay being removed and triggered a low level fault on UV1 and no UV was dosed from 15:12 ~ 15:13 with average flow of 12.5 L/s. Roughly 0.75 m^3 of final effluent was bypassed. The bypass could not be contained due to the large volume moving through and no clean up was needed. Followed bypass/spill procedure and collected composite samples at 15:15 (W11331830) Notified supervisor, Tara Magee at 16:00. Sunny day with no rain. Visually checked final effluent channel and humber river and found no abnormalities. Took photos and sent it to supervisor. Notified SAC, Elaine gold; 1-PKUITJ at 18:00. Notified MOH, Mathilda Habib; 4237216 at 18:12. Notified lake simcoe conservation authority at 18:32 via email. | Kleinburg Water Resource Recovery Facility | 2025-10-01
WW-WEST | October | - Added 6 bags of soda ash into the hopper. Cleaned floors - Collected weekly regulatory samples - Performed in-house lab and recorded readings on SharePoint. No issues - Checked station and recorded readings on SharePoint. No new issues - Cleaned up oil absorbent placed after an oil change for the raw sludge blower and placed new layer to absorb more - Checked ordour control unit. No issues - Threw out some garbage Update: enabled RAS batch wasting mode and Wasted 30 m^3 total then reset RAS batch wasting mode | Kleinburg Water Resource Recovery Facility | 2025-10-07
WW-WEST | October | Added 11 x 25kg bags of soda ash to the auto dispenser hopper. Checked grit production - lots of grit. | Kleinburg Water Resource Recovery Facility | 2025-10-12
WW-WEST | October | Supernated THCK_TK1 and released to SLDG_TK1. Set effluent sampler to start sampling at 08:00 on October 13. Enabled RAS batch wasting timer at 10:00. Set auto wasting for 30 m3 between 11:00 and 13:00. Completed labs. Entered numbers in spreadsheet. Completed station check. No issues found, except for grit. See below. Added 8 bags soda ash to hopper. Adjusted both Vistex settings as follows: Timer between cycles from 4 hrs to 1.5 hrs. Air scouring timer from 0.2 hrs to 0.1 hrs. Water scouring timer from 0.4 hrs to 0.1 hrs. Air lift pump timer left at 0.2 hrs. This should remove more grit. Also updated settings in SCADA to match settings in Vistex control panel. Manually wasted 5 m3 two more times. Total wastage train 1: 25 m3. Train 2: 15 m3. Found PLT_BL_0500 (grit blower 1) discharge fitting had come off and no air was going to the process. Corrected and the air lift actually lifts air now. Checked PLT_BL_0600 and found it to be functioning satisfactorily. Since both blowers are connected, any leak leaks for both blowers. | Kleinburg Water Resource Recovery Facility | 2025-10-10
WW-WEST | October | - wasted 30 m^3 total - added 11 bags of soda ash - cleaned headworks building Update: measured mlss for tank 2. All good | Kleinburg Water Resource Recovery Facility | 2025-10-04
WW-WEST | October | Scum tank is only pumping down to 1.6m and interlocking the pumps on no flow. Likely foam in the tank. Put pumps in manual and notified ROC to pump down if they receive a high level. | Kleinburg Water Resource Recovery Facility | 2025-10-11
WW-WEST | October | KSTP- Raw Water Turbidity Fault Alarm. Disregard as per SCADA report | Kleinburg Water Resource Recovery Facility | 2025-10-01
WW-WEST | October | - changed RAS train 2 flow rate from 15 L/s to 20 L/s due to higher clarifier sludge blanket for clarifier 2 - Added 6 bags of soda ash to the hopper - Cleaned DO probe and removed lots of rags hanging on - Enabled RAS batch wasting mode at roughly 10:50. Wasted 40 m^3 total then reset RAS batch wasting mode - Exercised scum tank 3 valve, fully opened then fully closed - Performed in-house lab and recorded readings on SharePoint. No new issues - Checked station and recorded readings. No new issues - Assisted electrical with UV2 low level fault. Once repair was complete and level sensor probe was replaced. Tested UV2 with sluice gate manually closed. No low level fault alarms. Removes low level lockout and cleared all alarms. Placed UV inlet gate back to auto - Placed hose to aeration tank 2 outlet for foam control and both banks in auto - Checks sand filters and hoses the reject compartments - Hosed scum tank and pumped it down manually | Kleinburg Water Resource Recovery Facility | 2025-10-08
WW-WEST | October | - Performed in-house lab and recorded readings on SharePoint. Solids back to normal. Ammonia for clarifier 1 and 2 are good. Ammonia for final effluent composite sample is elevated due to ongoing work. Final effluent grab ammonia number is good - Checked station and recorded readings on SharePoint - Added 6 bags of soda ash - Enabled RAS batch wasting mode at roughly 9:40. Wasted 15 m^3 from train 1 and 15 m^3 from train 2 then reset RAS batch wasting mode at 12:06 - Placed filter 2 back into duty rotation. Adjusted filter reject weir plates. Unplugged filter 2 north. - Received alum delivery at 11:40. Signed all papers and checked certificate of authenticity. Level from 0.96 m to 3.55 m. No issues receiving. Hi and Hihi alarm triggered due to this - Unclogged one submersible pump and moved it to a drawdown pit on aeration tank 1 - Reorganized soda ash room and cleaned floors - Changed eyewash solution - Played around with the submersible pump to try and draw down the aeration tank 1 as much as possible. Looked through the drawings and placed a submersible pump in the drawdown pit. After some time passed, aeration tank mlss started becoming thicker and harder to move. Tried to hose down the tank pit and try to draw more solids down - Shelved aeration tank 1 DO Lo alarm. Not needed with aeration tank 1 offline | Kleinburg Water Resource Recovery Facility | 2025-10-03
WW-WEST | October | Returned emptied bin to service. Poured rags from garbage pain in to bin. | King City Pumping Station | 2025-10-30
WW-WEST | October | Set rag bin out for pickup. Placed trash can to collect rags while bin out. | King City Pumping Station | 2025-10-16
WW-WEST | October | Completed station check. No issues found. Returned emptied bin and hosed screen room floor. | King City Pumping Station | 2025-10-17
WW-WEST | October | Completed station check. No issues found. | King City Pumping Station | 2025-10-20
WW-WEST | October | Placed the rag bin outside for pick up and topped up the Barscreen oil reservoir | King City Pumping Station | 2025-10-29
WW-WEST | October | Completed station check. No issues found. Entered data in spreadsheet. | King City Pumping Station | 2025-10-27
WW-WEST | October | Test backflow preventers Mezzanine unit passed B2 pump floor 2nd check failed and odd drip coming from relief port. Installed 2nd check and relief port rubber repair kits retested Passed | King City Pumping Station | 2025-10-23
WW-WEST | October | Completed station check. No issues found. Entered data in spreadsheet. | King City Pumping Station | 2025-10-24
WW-WEST | October | Completed station check. No issues found. Entered data in spreadsheet. Cleaned washroom and swept floors. Cleaned barscreen and screw conveyor. | King City Pumping Station | 2025-10-30
WW-WEST | October | Completed station check. No issues found. Entered numbers in spreadsheet. Returned emptied bin and dumped contents of garbage can in bin. | King City Pumping Station | 2025-10-03
WW-WEST | October | Completed the station check Test ran the generator Tested the diesel containment float switch Tested the dry well flood alarm Tested the alarm dialer Tested the building high low temp alarm Inspected the sump pit Exercised the surge protector isolation valve Inspected the RS pumps and check valves p1 - 140.9 L/s 296kpa p2 - 147.2 L/s 312kpa p3 - 129.6 L/s 332kpa Inspected the hoist system Completed the JHSC inspection Checked the site for hazardous waste | King City Pumping Station | 2025-10-08
WW-WEST | October | Completed the station check Everything operating as intended | King City Pumping Station | 2025-10-10
WW-WEST | October | Completed station check. No issues found. Entered numbers in spreadsheet. Checked and hosed bar screen. | King City Pumping Station | 2025-10-01
WW-WEST | October | Set bin out for pickup. Set garbage pail to collect rags in the absence of proper bin. Reset main breaker on pump 3. Set pump to auto. Tested pump 1 and pump 3. Both pumps ran just fine. All pumps functioning and in duty. | King City Pumping Station | 2025-10-02
WW-WEST | October | Completed station check. No issues found. Entered numbers in spreadsheet. | King City Pumping Station | 2025-10-06
WW-WEST | October | Completed station check. No issues found. Entered numbers in spreadsheet. | King City Pumping Station | 2025-10-15
WW-WEST | October | Reset pump 1 VFD fault caused by power outage. Reset alarms on SCADA. Pump in duty 3. | Nobleton Janet St. Sewage Pumping Station | 2025-10-18
WW-WEST | October | Completed the station check Everything operating as intended | Nobleton Janet St. Sewage Pumping Station | 2025-10-21
WW-WEST | October | In to Complete Station Check. Inspected, Recalibrated and Tested Raw Influent Sampler. Returned to Service. Reviewed SCADA and Trends. No Issues Found. | Nobleton Janet St. Sewage Pumping Station | 2025-10-30
WW-WEST | October | Completed the station check Everything operating as intended | Nobleton Janet St. Sewage Pumping Station | 2025-10-17
WW-WEST | October | In to Complete Station Check. On-site SCADA Access Unavailable, OIT/HMI Exhibiting Error Message. Created Follow Up WO for PCS ?> W11397821. No Other Issues Found. | Nobleton Janet St. Sewage Pumping Station | 2025-10-27
WW-WEST | October | Completed the station check Cleaned up around the station | Nobleton Janet St. Sewage Pumping Station | 2025-10-24
WW-WEST | October | Collected the weekly samples | Nobleton Janet St. Sewage Pumping Station | 2025-10-21
WW-WEST | October | In to Complete Reg. Sampling. No Issues Found. | Nobleton Janet St. Sewage Pumping Station | 2025-10-28
WW-WEST | October | Onsite to reinstall suction pipe pump 1, Opened suction and discharge valves flooded pump. Removed lock ready for testing no leaks | Nobleton Janet St. Sewage Pumping Station | 2025-10-08
WW-WEST | October | In to Complete Station Check. Reviewed SCADA and Trends. No New Issues Found. | Nobleton Janet St. Sewage Pumping Station | 2025-10-08
WW-WEST | October | In to Complete Scheduled WOs. Reviewed SCADA and Trends. No New Issues Found. Completed Raw Sewage Sampler Inspection. Replaced Peristaltic Tubing and Tested Unit with No Issues. Set Internal Clock and Sampling Schedule and Returned to Service. Completed Manual Valve Exercise with No Issues. Pump #1 Remains Isolated and OOS. | Nobleton Janet St. Sewage Pumping Station | 2025-10-03
WW-WEST | October | In to Complete Scheduled WOs. Notified ROC. Manually Deactivated Duty #1 Start Set-point. Placed Pumps #2 and 3 in Manual Off. Transferred Station to Generator Power with No Issues. Acknowledged Associated Alarms. Returned Pumps #2 and 3 to Auto, Manually Activated Duty #1 Start Set-point. Reviewed SCADA and Trends. No New Issues Found. Pump #1 Remains OOS and Isolated. Completed JHSC and Hazardous Materials Inspections. No Issues Found. Cleared Associated Alarms. Placed Pump #2 in Manual Speed for Wet Well Level Management, Returned to Auto. Manually Deactivated Duty #1 Start Set-point. Placed Pumps #2 and 3 in Manual Off. Transferred Station Back to Utility Power with No Issues. Cleared Associated Alarms. Returned Pumps #2 and 3 to Auto, Auto Speed. Completed Hoist Inspections. No Issues Found. Returned to Service. | Nobleton Janet St. Sewage Pumping Station | 2025-10-01
WW-WEST | October | Test backflow preventers | Nobleton Janet St. Sewage Pumping Station | 2025-10-15
WW-WEST | October | Pump suction leak pump 1 Loto removed suction pipe with leak Taken to 380 for repair | Nobleton Janet St. Sewage Pumping Station | 2025-10-06
WW-WEST | October | Station checks, SharePoint readings and review of continuous monitoring data. No new issues identified. | Nobleton Janet St. Sewage Pumping Station | 2025-10-10
WW-WEST | October | Removed lock from pump 1. Returned pump 1 to Auto. Set to duty 1 and tested. Pump 1 functions satisfactorily. | Nobleton Janet St. Sewage Pumping Station | 2025-10-08
WW-WEST | October | In to Complete Scheduled and Backlog WOs. Notified ROC. Reviewed SCADA and Trends. No New Issues Found. Pump #1 Remains Isolated and OOS. Completed Consolidated Dry Well Inspections. Test Hi/Lo Temp., Dry Well Flood and Sump System Hi Float Alarms. Confirmed Reception by the ROC. Returned to Service. Cleared Associated Alarms. Tested Pump #2 in Manual, Manual Speed and Pump #3 in Auto with No Issues. Returned to Service. | Nobleton Janet St. Sewage Pumping Station | 2025-10-06
WW-WEST | October | Completed the station check Everything operating as intended | Nobleton Janet St. Sewage Pumping Station | 2025-10-15
WW-WEST | October | Completed station check. No issues found. Entered data in spreadsheet. | Vaughan Pine Valley Pumping Station | 2025-10-17
WW-WEST | October | Completed station check. No issues found. Assisted Gavin with consolidated wetwell work order. | Vaughan Pine Valley Pumping Station | 2025-10-27
WW-WEST | October | Completed the comprehensive wet well cleaning Greased the channel grinder and exercised the valves | Vaughan Pine Valley Pumping Station | 2025-10-27
WW-WEST | October | Completed the station check Entered data into SharePoint Everything operating as intended | Vaughan Pine Valley Pumping Station | 2025-10-30
WW-WEST | October | Cleaned up around site | Vaughan Pine Valley Pumping Station | 2025-10-30
WW-WEST | October | Completed station check. No issues found. Entered data in spreadsheet. | Vaughan Pine Valley Pumping Station | 2025-10-24
WW-WEST | October | Completed station check. No issues found. Entered data in spreadsheet. | Vaughan Pine Valley Pumping Station | 2025-10-20
WW-WEST | October | Completed station check. No issues found. Entered numbers in spreadsheet. | Vaughan Pine Valley Pumping Station | 2025-10-03
WW-WEST | October | Completed the station check Test ran the generator Completed the JHSC inspection Inspected the site for hazardous waste Manually exercised the valves Inspected the dry well Inspected the OCU Tested the alarm dialer Tested the dry well flood alarm Tested the building high low temp alarm Cleaned the mist eliminator screen Test ran the pumps P1- 213.4 L/s 57kpa P2 - 223 L/s 52kpa P3 - 206.9 L/s 54kpa | Vaughan Pine Valley Pumping Station | 2025-10-06
WW-WEST | October | Completed station check. No issues found. Entered numbers in spreadsheet. | Vaughan Pine Valley Pumping Station | 2025-10-15
WW-WEST | October | Completed the station check Everything operating as intended | Vaughan Pine Valley Pumping Station | 2025-10-08
WW-WEST | October | Completed the station check Everything operating as intended | Vaughan Pine Valley Pumping Station | 2025-10-10
WW-WEST | October | Onsite to assist contractors with air compressors. Decanted sludge thickening tank and transferred remaining sludge to holding tank. Completed daily lab and station check no new issues added data into SharePoint. Cleaned TSS probe. Contractors finished with air compressors at 2pm - confirmed air compressor 1 and 2 back into duty auto and in duty operating normally. | Schomberg Water Resource Recovery Facility | 2025-10-24
WW-WEST | October | Decant sludge thickening tank with supernatant drain valve. Transferred thickened sludge to sludge holding tank. | Schomberg Water Resource Recovery Facility | 2025-10-27
WW-WEST | October | On site to reset clarifier rake drive after power blip. Reset duties on RAS pumps. | Schomberg Water Resource Recovery Facility | 2025-10-18
WW-WEST | October | Decanted sludge thickening tank and transferred remaining sludge to holding tank. Completed daily lab and station check- no new issues added data into SharePoint. Checked heat trace on head works building Inspected filter reject pumps 1 and 2, both functioning normally, placed back into duty. Cleaned and verified DO probes and pulled rags from aeration outlet. Cleaned UV channel with lance. | Schomberg Water Resource Recovery Facility | 2025-10-22
WW-WEST | October | Decanted sludge thickening tank and transferred remaining sludge to holding tank. Completed daily lab and station check - no new issues. Added data into SharePoint. Made work order for vortex O2 sensor reading high at 23.2% handheld gas monitor reading 20.8. Checked outfall - no issues. Cleaned and verified DO probes. Worked on comprehensive cleaning of blower building. | Schomberg Water Resource Recovery Facility | 2025-10-29
WW-WEST | October | Reset clarifier after power blip. | Schomberg Water Resource Recovery Facility | 2025-10-19
WW-WEST | October | Decanted sludge thickening tank, transferred remaining sludge to holding tank. Completed daily lab and station check - filter 3 still operating well. Added data into SharePoint. Called ROC to inform of generator run test. Started generator run test at 10:48am, transferred smoothly. Transferred power back to hydro at 11:57am. During both power transfers UVs cut out during the transfer time - contacted Anna Lacourt and emailed details. At 11:45am opened the filter to lagoon bypass valve to do routine clarifier cleaning. Closed valve at 1:30pm Emailed ENV reporting of 116m3 bypassed to lagoon. | Schomberg Water Resource Recovery Facility | 2025-10-16
WW-WEST | October | Reviewed UV trending and discussed UV disinfection with Lauren. | Schomberg Water Resource Recovery Facility | 2025-10-16
WW-WEST | October | Decanted sludge thickening tank and transferred remaining sludge to holding tank. Completed daily lab and station check- no new issues added data to SharePoint. Collected regulatory weekly samples. Drained clarifier wash hydrant for winter. | Schomberg Water Resource Recovery Facility | 2025-10-21
WW-WEST | October | Assisted Lauren with final effluent channel clean out. | Schomberg Water Resource Recovery Facility | 2025-10-22
WW-WEST | October | Decanted sludge thickening tank and transferred remaining sludge to holding tank. Collected regulatory weekly samples. Completed daily lab and station check - added data into SharePoint UV train B had a burnt out bulb - replaced. | Schomberg Water Resource Recovery Facility | 2025-10-28
WW-WEST | October | Decanted sludge thickening tank and transferred remaining sludge to holding tank. Completed daily lab and station check - no new issues. - added data into SharePoint. Troubleshooting RAS pump 3 with electricians - placed RAS pump 3 into duty 1 and RAS pump 2 into duty 2 and back up to clarifier 2 to move the scada duty box. Placed RAS pump 1 into manual OOS. continuing it to monitor RAS pump 3 while in duty. Trouble shooting WAS pump 2 with electricians - turned WAS pump 1 into manual off and placed WAS pump 2 into manual on to run instead of pump 1 for wasting. WAS Pump 2 fully cycled with no issues. Placed WAS pump 2 back in Manual OOS and WAS pump 1 back in auto as main WAS pump. | Schomberg Water Resource Recovery Facility | 2025-10-30
WW-WEST | October | Decanted sludge thickening tank. Completed daily lab and station check - no new issues. Added data to SharePoint. | Schomberg Water Resource Recovery Facility | 2025-10-20
WW-WEST | October | On site for aeration blower 1 oil leak. Found a fail input shaft oil seal. Tried tapping it in but very little movement. I topped up the oil and ordered a new seal | Schomberg Water Resource Recovery Facility | 2025-10-27
WW-WEST | October | On site to troubleshoot WAS pump 2 and RAS pump 3 for reported un commanded start /stop issues. | Schomberg Water Resource Recovery Facility | 2025-10-30
WW-WEST | October | Decanted sludge thickening tank and transferred remaining sludge to holding tank. Completed daily lab and station check- no new issues. Entered data into SharePoint. Cleaned TSS probe. Inspected UVs - no issues. | Schomberg Water Resource Recovery Facility | 2025-10-17
WW-WEST | October | On site to troubleshoot alum pump 6 & 7 no flow alarms. After monitoring pumps and reviewing trends, the issue is occurring when the pumps are in low flow periods following a cycle. The flow meter is registering flow well at 80% plus and somewhere below 25% the alum flow detector stops registering flow. Alum truck arrived on site, started offloading until Lauren arrived. Note the variance in pressure from alum pump 6 and pump 7 on the panel. Adjusted alum panel prv from 50 psi down to 30psi. Cleaned flow sensor internals and replaced. Tested for flow -ok- put aluminum pumps back into remote auto and duty selected. Will monitor for next few weeks to determine if issue is resolved or not. | Schomberg Water Resource Recovery Facility | 2025-10-01
WW-WEST | October | Decanted sludge thickening tank. Completed daily lab and station check - filter 3 sand wash clogged again, lanced until cleared and running normally. Added data into SharePoint. Cleaned DO probes and pulled excess rags under alum line in aeration tank. Changed oil on scum pumps 1 and 2. Put back in operation and in duty when completed | Schomberg Water Resource Recovery Facility | 2025-10-15
WW-WEST | October | Aeration blower 2 high temp alarm on scada on arrival, control panel showed VFD fault alarm, reset the VFD and cleared alarms - placed aeration blower 2 back into duty and it ran normally. Checked oil, belts and filter all okay. Left Aeration blower 2 in duty to continue to monitor. Decanted sludge thickening tank and transferred remaining sludge to holding. Completed daily lab and station check - no new issues, entered data into SharePoint. called ROC to inform of PMs being completed in the headworks. Inspected vortex 1 and 2, greased nipples and removed rags from blades. Oil levels good. Operating normally Inspected traveling screen, greased nipples and oil levels good, operating normally Inspected grit dewatering 1 and 2 - both oil levels and grease levels good, removed some build up from 1. Operating normally Inspected screenings compactor. Operating normally Inspected debris auger, cleared excess debris and oil level good. | Schomberg Water Resource Recovery Facility | 2025-10-09
WW-WEST | October | Decanted sludge thickening tank and transferred remaining sludge to holding. Completed daily lab and station check- no new issues added data into SharePoint. Completed JHSC inspection and checked plant for hazardous waste. Cleaned and verified DO probes. | Schomberg Water Resource Recovery Facility | 2025-10-08
WW-WEST | October | Decanted sludge thickening and transferred remaining sludge to holding tank. Completed daily lab and station check- no new issues, added data to SharePoint. Called ROC to inform of work being done on WAS pumps. Completed oil changes on WAS pumps 1 and 2. Inspected couplings. Cleaned TSS probe | Schomberg Water Resource Recovery Facility | 2025-10-10
WW-WEST | October | On site for TSSA upgrade training. | Schomberg Water Resource Recovery Facility | 2025-10-03
WW-WEST | October | Decanted sludge thickening tank and transferred remaining sludge to holding tank Completed daily lab and station check - entered data into SharePoint Called ROC to inform of blower and RAS pump PMs being completed today, Inspected vortex blowers and grit blowers - all ok. Inspected aeration blowers 1-4, belts and filters good, oil levels on blowers 2 and 3 good. Changed oil on blowers 1 and 4. Was able to run blower 4 - still triggering a low pressure alarm, leaving in OOS Inspected RAS pumps 1-3. While changing oil on RAS pump 3 water leaking from oil line - created WO. Under direction changed alum dosing setpoints, changed finale pass to aeration alum dose from 95mg/L to 105mg/L Changed clarifier effluent alum dose from 25mg/L to 12mg/L | Schomberg Water Resource Recovery Facility | 2025-10-02
WW-WEST | October | Decanted sludge holding tank and transferred remaining sludge to holding tank Collected regulatory weekly samples Completed daily lab and station check - entered data into SharePoint. Under direction increased alum dosing to clarifier from 12mg/L to 15mg/L. And increased alum dosing to aeration from 105mg/L to 110mg/L Drained aeration tank condensation lines | Schomberg Water Resource Recovery Facility | 2025-10-07
WW-WEST | October | - reset aeration blower duties | Schomberg Water Resource Recovery Facility | 2025-10-03
WW-WEST | October | Decanted sludge thickening tank and transferred remaining sludge to holding tank. Contractors onsite for clarifier covers installation. Completed daily lab and station check, no new issues added data into SharePoint Inspected and cleaned air compressor 1 and 2, oil levels and belts good. Closed WAS/RAS valve from clarifier 2 and opened WAS/RAS interconnect valve. Placed WAS pump 2 and RAS pump 3 back in auto | Schomberg Water Resource Recovery Facility | 2025-10-06
WW-WEST | October | Decanted sludge thickening tank and transferred remaining sludge to holding tank. Completed daily lab and station check, entered data into SharePoint. Changed oil in RAS pumps 1 and 2 and greased. Inspected and greased WAS pumps, added oil to WAS pump 2 Attended TSSA training. | Schomberg Water Resource Recovery Facility | 2025-10-03
WW-WEST | October | Decanted thickening tank and transferred remaining sludge to holding tank, Completed daily labs and station check, no new issues entered data into SharePoint. Alum delivery onsite at 10:00am, alum tank 1 at 0.84m and alum tank 2 at 0.84m. Began filling tank 1. Alum tank 1 finished filling at 10:32am alum tank 1 now at 2.46m. Began filling tank 2. Completed filling tank 2 at 10:53am tank 2 now at 2.39m. Opened isolation valve between tanks to allow them to equalize. Signed all papers and reviewed certificate of analysis. Cleaned DO probes. | Schomberg Water Resource Recovery Facility | 2025-10-01
WW-WEST | October | Onsite for station check - no new issues, reviewed trends and added data to SharePoint. | Schomberg Dr. Kay Pumping Station | 2025-10-21
WW-WEST | October | Onsite for station check - no new issues. Reviewed trends and entered data into SharePoint. | Schomberg Dr. Kay Pumping Station | 2025-10-17
WW-WEST | October | Onsite for station check - no new issues, revised trends and added data into SharePoint. Worked on comprehensive cleaning work order. | Schomberg Dr. Kay Pumping Station | 2025-10-30
WW-WEST | October | Onsite for station check - no new issues, reviewed trends and entered data into sharepoint | Schomberg Dr. Kay Pumping Station | 2025-10-28
WW-WEST | October | Onsite for station check - no new issues, reviewed trends and added data into SharePoint | Schomberg Dr. Kay Pumping Station | 2025-10-24
WW-WEST | October | Onsite for station check - no new issues. Reviewed trends and added data into SharePoint. | Schomberg Dr. Kay Pumping Station | 2025-10-08
WW-WEST | October | Onsite for station check - no new issues. Reviewed trends and added data into SharePoint. | Schomberg Dr. Kay Pumping Station | 2025-10-15
WW-WEST | October | Onsite for station check - no new issues, reviewed trends and added data into SharePoint | Schomberg Dr. Kay Pumping Station | 2025-10-06
WW-WEST | October | Onsite for station check - no new issues. Reviewed trends and added data into SharePoint. | Schomberg Dr. Kay Pumping Station | 2025-10-10
WW-WEST | October | Onsite for station check - no new issues, reviewed trends and entered data into SharePoint | Schomberg Dr. Kay Pumping Station | 2025-10-03
ROC | October | Angelica Chepiga signing in,weather -1C | ROC General | 2025-10-26
ROC | October | Adam Button signing out | ROC General | 2025-10-17
ROC | October | KSTP- Christian from Ferguson Electric is done on site | ROC General | 2025-10-16
ROC | October | GWTP - Khaled from IAM on site to meet with the contractors for the intake inspection. | ROC General | 2025-10-27
ROC | October | GWTP - Khaled from Iam on site to meet contractors for the intake inspection. | ROC General | 2025-10-28
ROC | October | Adam Button signing in | ROC General | 2025-10-16
ROC | October | MARS- Courtney from Torbear is on site | ROC General | 2025-10-17
ROC | October | YDOC, Donald from Magnum Fire is on site | ROC General | 2025-10-23
ROC | October | MTW3, Drew from Ferguson Electric is on site, doing a TFSA inspection | ROC General | 2025-10-20
ROC | October | MARS - Courtney from Torbear construction on site. | ROC General | 2025-10-28
ROC | October | AUW14 - Jeff from Keyshack leaving site, heading to AURSBS. | ROC General | 2025-10-16
ROC | October | Connor Smith signing in 7C Rainy | ROC General | 2025-10-30
ROC | October | KSTP - Drew from Ferguson electric on site. | ROC General | 2025-10-21
ROC | October | NMSSBP- Pat from Property Services onsite testing fire alarm. 08:23- Finished onsite | ROC General | 2025-10-17
ROC | October | Connor Smith signing in | ROC General | 2025-10-21
ROC | October | SUSP - Jeff from property services leaving site. | ROC General | 2025-10-31
ROC | October | JDSS - Garrick from Ferguson onsite for pipe runs & wire nitrification | ROC General | 2025-10-29
ROC | October | MAPS- Courtney from Torbear finished onsite. | ROC General | 2025-10-17
ROC | October | STETTL - Wes from Stouffville water operations called to inform he will be flushing in the zone two system this afternoon. | ROC General | 2025-10-20
ROC | October | KSETWB, Kevin N from Yorknet is leaving site | ROC General | 2025-10-29
ROC | October | Adeela Khan signing in. Weather: 11C and Clear | ROC General | 2025-10-18
ROC | October | Christian Van Beek signing in. Weather: 13C and sun | ROC General | 2025-10-21
ROC | October | AUPSWS - Drew from Ferguson Electric on site for TFSA testing which required an offload generator test. Arthur L monitoring remotely. | ROC General | 2025-10-20
ROC | October | LSSS, Ben H from property services is on site | ROC General | 2025-10-30
ROC | October | JDSS, Gerric from Ferguson Electric is leaving site | ROC General | 2025-10-29
ROC | October | Christian Van Beek signing out. | ROC General | 2025-10-22
ROC | October | Adeela Khan signing in. Weather: 4C and clear | ROC General | 2025-10-30
ROC | October | MKPSSA - Drew from Ferguson Electric is finished on site | ROC General | 2025-10-30
ROC | October | LSSS - Ben from Property Services is finished on site | ROC General | 2025-10-30
ROC | October | Adeela Khan signing in. Weather: 7C and sunny | ROC General | 2025-10-27
ROC | October | KSSP- Drew from Ferguson leaving site and heading to JDSS | ROC General | 2025-10-28
ROC | October | KSOCMA- Kevin from Yorknet onsite. | ROC General | 2025-10-28
ROC | October | NMW12 - Natalie Paradis leaving site. | ROC General | 2025-10-28
ROC | October | NMETYS - Richard from NT Power notified about power outage at NMETYS. Powering down connections to site. Richard will send email. Notified Ben H. | ROC General | 2025-10-21
ROC | October | SUSSWA - Jeff from Keyshack on site | ROC General | 2025-10-21
ROC | October | KBSP, Ian from AD Project Management is on site | ROC General | 2025-10-20
ROC | October | SUSSWB- Jeff from Keyshack finished onsite. SUSSHS- Jeff heading to site. | ROC General | 2025-10-21
ROC | October | YDOC- Jeff from Keyshack on site KLET27- Chimney CPD on site | ROC General | 2025-10-22
ROC | October | Adam Button signing in 6C Clear | ROC General | 2025-10-22
ROC | October | Pest control attending following sites: KBSP KLW34 KLPSWL KBET27 | ROC General | 2025-10-23
ROC | October | KBSP, ITS is on site | ROC General | 2025-10-20
ROC | October | Christian Van Beek signing in. Weather: 3C and rain. | ROC General | 2025-10-31
ROC | October | MKETFA, David from RCMP is on site | ROC General | 2025-10-21
ROC | October | Connor Smith signing out. | ROC General | 2025-10-31
ROC | October | Adam Button signing in | ROC General | 2025-10-31
ROC | October | Angelica Chepiga signing out | ROC General | 2025-10-26
ROC | October | AUSSYS - Joe O from property services on site. | ROC General | 2025-10-27
ROC | October | MARS - Courtney from Torbear on site for the reservoir rehab project. | ROC General | 2025-10-27
ROC | October | QVSSSC - Jeff from keyshack headed to site. | ROC General | 2025-10-27
ROC | October | AUETFC - Jeff from Keyshack visiting sites, heading to AUPSOH, AURSOH,AUETOH next. | ROC General | 2025-10-16
ROC | October | SEOC4 - Hamed ETO engineering onsite 15:43 - Leaving site | ROC General | 2025-10-22
ROC | October | KBSP, Terry G from Property Services is on site, working on exterior lighting | ROC General | 2025-10-29
ROC | October | Carter D signing in.3D/Clear | ROC General | 2025-10-24
ROC | October | Ethan Ullalkar signing out. | ROC General | 2025-10-24
ROC | October | NMW12- Natalie from IAM onsite. | ROC General | 2025-10-28
ROC | October | SEOC - Hamed finished at site | ROC General | 2025-10-22
ROC | October | Adam Button signing out | ROC General | 2025-10-25
ROC | October | Christian Van Beek signing in. Weather: 19C and clear. | ROC General | 2025-10-19
ROC | October | JDSS - Drew from Ferguson Electric leaving site. | ROC General | 2025-10-28
ROC | October | Gluzen Ramos Ong signing in | ROC General | 2025-10-24
ROC | October | MARS - Courtney (Torbear) on site | ROC General | 2025-10-24
ROC | October | Adeela Khan signing out | ROC General | 2025-10-28
ROC | October | HLETYS - Mark S from process optimization on site. | ROC General | 2025-10-28
ROC | October | Ethan Ullalkar signing out. | ROC General | 2025-10-29
ROC | October | NMETYS- Jeff from Keyshack leaving site. Unable to arm building. Notified Security. | ROC General | 2025-10-17
ROC | October | Ethan Ullalkar signing in. | ROC General | 2025-10-29
ROC | October | Angelica Chepiga signing in | ROC General | 2025-10-21
ROC | October | KSETWB - Ken from ITS in site. | ROC General | 2025-10-21
ROC | October | Connor Smith signing out | ROC General | 2025-10-21
ROC | October | YDOC - Chris from Property services on site for fire testing. | ROC General | 2025-10-16
ROC | October | AUW14- Jeff from Keyshack is on site GWTP- Eric S done on site working on backwash tank 1 LIT **WRONG BOOK** | ROC General | 2025-10-16
ROC | October | JDSS - Phil from AB leaving site. | ROC General | 2025-10-16
ROC | October | JDSS, Drew from Ferguson Electric is on site | ROC General | 2025-10-24
ROC | October | Angelica Chepiga signing out | ROC General | 2025-10-24
ROC | October | NMW136 - harry N from property services on site GWTP - Colin from 360 advanced security leaving site. | ROC General | 2025-10-27
ROC | October | YDOC9 - Jeff from keyshack leaving site. | ROC General | 2025-10-27
ROC | October | SUETDR- Jason from property services is on site | ROC General | 2025-10-17
ROC | October | RHPSPA- Ben from property services is on site KSETDP- Steve from York doors is on site | ROC General | 2025-10-17
ROC | October | JDSS- Stephen from AB leaving site. | ROC General | 2025-10-17
ROC | October | KSETWB - Kevin from Yorknet on site. | ROC General | 2025-10-21
ROC | October | JDSS- Hamid from ETO Engineering offsite. | ROC General | 2025-10-17
ROC | October | Adeela Khan signing in. Weather: 6C and sunny | ROC General | 2025-10-26
ROC | October | QVETQS - Dominic from honeywell leaving site EGSSSC - Jeff from keyshack on site. | ROC General | 2025-10-27
ROC | October | KSETWB - Kevin from Yorknet onsite replacing fibre cable | ROC General | 2025-10-29
ROC | October | SEOC - Ben from PS onsite for HVAC work | ROC General | 2025-10-29
ROC | October | NBSSJA- Ben from Property Services onsite working on supply fan. | ROC General | 2025-10-28
ROC | October | Ethan Ullalkar signing out. | ROC General | 2025-10-22
ROC | October | Connor Smith signing in | ROC General | 2025-10-17
ROC | October | SEOC13- Aqib from Magnum working on fire alarm inspection | ROC General | 2025-10-21
ROC | October | STRS48, Drew from Ferguson Electric is on site 10:40, Drew is finished on site | ROC General | 2025-10-24
ROC | October | Adam Button signing in 10C sunny | ROC General | 2025-10-25
ROC | October | MTW3, Theodor from AB is finished on site | ROC General | 2025-10-24
ROC | October | Pest Control Visiting the following sites; STPSMR, STW12, STETBR, BLETNL, STRS48, BLW3 | ROC General | 2025-10-27
ROC | October | STRS48- Theodore from AB onsite | ROC General | 2025-10-27
ROC | October | MARS, Courtney from Tobare is on site | ROC General | 2025-10-30
ROC | October | JDSS - Stephen from AB piping fuel tank | ROC General | 2025-10-22
ROC | October | STPSMR - Drew from Ferguson electric leaving site. | ROC General | 2025-10-16
ROC | October | RHRSTR, Kevin N from Yorknet is on site | ROC General | 2025-10-30
ROC | October | AUSS- Pat from Property Services heading to site. | ROC General | 2025-10-17
ROC | October | NBSSJA, Anib from Magna Fire is leaving site | ROC General | 2025-10-21
ROC | October | MKPSSA, Amil from Magnum Fire is finished on site | ROC General | 2025-10-30
ROC | October | STPSMR - Drew from Ferguson Electric leaving site. | ROC General | 2025-10-20
ROC | October | Christian Van Beek signing out. | ROC General | 2025-10-20
ROC | October | Connor Smith signing out | ROC General | 2025-10-28
ROC | October | Christian Van Beek signing out. | ROC General | 2025-10-28
ROC | October | VNETAG - YRP Operator on site to check their equipment and complete preventative maintenance. | ROC General | 2025-10-20
ROC | October | SHTP - Drew from Ferguson Electric finished the TFSA testing and leaving site. | ROC General | 2025-10-20
ROC | October | Gluzen Ramos Ong signing out | ROC General | 2025-10-24
ROC | October | GWTP - Kevin from Yorknet on site | ROC General | 2025-10-28
ROC | October | Angelica Chepiga signing out | ROC General | 2025-10-29
ROC | October | STRS48 - Drew from Ferguson onsite | ROC General | 2025-10-22
ROC | October | RHRSTR, Jeff from Keyshack is on site | ROC General | 2025-10-24
ROC | October | Angelica Chepiga signing out | ROC General | 2025-10-24
ROC | October | Carter Dunn Signing In, 7D/Clear | ROC General | 2025-10-21
ROC | October | MARS, Courtney from Tolbare is on site | ROC General | 2025-10-21
ROC | October | BLSS - Amin from Magna on site for fire testing. | ROC General | 2025-10-21
ROC | October | Christian Van Beek signing in. | ROC General | 2025-10-27
ROC | October | RHPSPA - Ben Han on site to work on a pressure transducer | ROC General | 2025-10-31
ROC | October | KCETFS- Jason from Property Services onsite. | ROC General | 2025-10-28
ROC | October | Adam Button signing out | ROC General | 2025-10-22
ROC | October | STPSMR - Drew from Ferguson Electric on site. | ROC General | 2025-10-20
ROC | October | Adam Button signing in 2C clear | ROC General | 2025-10-17
ROC | October | STPSMR, Drew from Ferguson Electric is leaving site | ROC General | 2025-10-29
ROC | October | Adeela Khan signing out | ROC General | 2025-10-27
ROC | October | Adam Button signing in 10C clear | ROC General | 2025-10-24
ROC | October | MARS- Courntey from Torbear is done on site | ROC General | 2025-10-24
ROC | October | Jasat, Zuber from IT called and is rebooting the Finess Phone System. Should still be able to make and receive calls. 02:24- Finished | ROC General | 2025-10-31
ROC | October | JDSS - Garrick from Ferguson Electric on site for generator work. | ROC General | 2025-10-31
ROC | October | KSSP- Hamid from ETO onsite. 15:47- Offsite. | ROC General | 2025-10-17
ROC | October | Adeela Khan signing out | ROC General | 2025-10-18
ROC | October | SECC ,AQUIB S from Magnum Fire is leaving site | ROC General | 2025-10-21
ROC | October | Angelica Chepiga signing out | ROC General | 2025-10-19
ROC | October | HLSSBS- Jeff from Keyshack onsite. | ROC General | 2025-10-27
ROC | October | Jeff from Keyshack visiting following sites; NMSSHS, NMW15, NMETYS, NMET15, NMETHW, NMETIB | ROC General | 2025-10-17
ROC | October | SEOC6/7 - Theodore from AB finished at site | ROC General | 2025-10-22
ROC | October | HLETYS- Mark from Process Optimization offsite. | ROC General | 2025-10-28
ROC | October | QVW12/QVW34/QVETQS/MTSS/MTW12/MTW3/MTETNL/MTSP, PCO operator is visiting these sites | ROC General | 2025-10-24
ROC | October | NMW136 - Harry N from PS leaving site | ROC General | 2025-10-27
ROC | October | STPSMR - Jeff from keyshack on site. | ROC General | 2025-10-28
ROC | October | KSOCMA, KSETDP, KSETWB, KSTP - Jeff from keyshack visiting these sites for door maintenance. | ROC General | 2025-10-20
ROC | October | MAPS, Courtney from Tobare is on site | ROC General | 2025-10-29
ROC | October | Connor Smith signing in 11C Cloudy | ROC General | 2025-10-29
ROC | October | Adeela Khan signing in. Weather: 2C and partly cloudy | ROC General | 2025-10-25
ROC | October | STPSMR - Drew from Ferguson onsite with team for meeting | ROC General | 2025-10-29
ROC | October | Carter Dunn Signing In | ROC General | 2025-10-23
ROC | October | JDSS, Stephen from AB is leaving site | ROC General | 2025-10-23
ROC | October | KSSSQW, TC/Securatask/Amper Electric operators are heading to site as per a Security call. Notified Security that they will need to call the ROC once they arrive on site | ROC General | 2025-10-23
ROC | October | Carter Dunn Signing In, 7D/Clear | ROC General | 2025-10-30
ROC | October | NMTKKC//380 Bayview Parkway//MTSP//AUSS, Jeff from Key Shack will be at these sites today | ROC General | 2025-10-30
ROC | October | QVETQS - Diminic from honeywell on site. HLSSBS - Jeff from keyshack leaving site. | ROC General | 2025-10-27
ROC | October | JDSS- Drew from Ferguson onsite. | ROC General | 2025-10-28
ROC | October | JDSS, Phil from AB is on site | ROC General | 2025-10-21
ROC | October | HMSS - Jeff from keyshack leaving site. | ROC General | 2025-10-28
ROC | October | Angelica Chepiga signing in, weather +11C | ROC General | 2025-10-28
ROC | October | SEOC6/7- Jeff from Keyshack is on site STPS48- Drew from Ferguson electric is done on site | ROC General | 2025-10-23
ROC | October | Ethan U singing in Weather: 7 light rain | ROC General | 2025-10-23
ROC | October | Angelica Chepiga signing in,weather +11C | ROC General | 2025-10-17
ROC | October | Connor Smith signing out | ROC General | 2025-10-17
ROC | October | MARS- Cody from Torbear is onsite | ROC General | 2025-10-16
ROC | October | Adam Button signing out | ROC General | 2025-10-26
ROC | October | STRS48, Stephen from AB is finished on site | ROC General | 2025-10-24
ROC | October | Ethan Ullalkar signing out. | ROC General | 2025-10-16
ROC | October | Adam Button signing out 1C clear | ROC General | 2025-10-16
ROC | October | Angelica Chepiga signing in, weather +21C | ROC General | 2025-10-18
ROC | October | Adam Button signing out | ROC General | 2025-10-23
ROC | October | SHSP - Steve Bickle (LCD Construction, 4169037872) on site | ROC General | 2025-10-24
ROC | October | Carter Dunn Signing Out | ROC General | 2025-10-21
ROC | October | MARS, Courtney from Tolbare is on site | ROC General | 2025-10-20
ROC | October | NMW12- Jeff from Keyshack done on site | ROC General | 2025-10-16
ROC | October | AUW14- Placed P3 in man/on and 1/2/4 in manual **WRONG BOOK** | ROC General | 2025-10-16
ROC | October | Carter Dunn Signing In, 12D/Clear | ROC General | 2025-10-16
ROC | October | Angelica Chepiga signing out | ROC General | 2025-10-16
ROC | October | KCETFS- Jason from Property Services finished onsite. | ROC General | 2025-10-28
ROC | October | YDOC- Jeff from Key shack si done on site | ROC General | 2025-10-23
ROC | October | Connor Smith signing in | ROC General | 2025-10-28
ROC | October | STRS48- Steven from AB onsite. | ROC General | 2025-10-28
ROC | October | Carter Dunn Signing In, 12D/Clear | ROC General | 2025-10-29
ROC | October | KSTP- Gerrick from Ferguson leaving site. | ROC General | 2025-10-17
ROC | October | Adeela Khan signing in. Weather: 11C and sunny | ROC General | 2025-10-20
ROC | October | MARS, Ken from ITS is on site | ROC General | 2025-10-30
ROC | October | KSETWB- Kevin from Yorknet onsite. | ROC General | 2025-10-28
ROC | October | JDSS - Drew from Ferguson Electric leaving site. | ROC General | 2025-10-31
ROC | October | SEOC6/7 - Theodore leaving site | ROC General | 2025-10-29
ROC | October | MAPS- Jeff from Keyshack onsite. 12:30- Offsite | ROC General | 2025-10-28
ROC | October | BVPS - Ken H onsite putting in corporate wifi | ROC General | 2025-10-29
ROC | October | MARS - Courtney from Torbear construction on site. | ROC General | 2025-10-31
ROC | October | YDOC, Aquib S from Magna Fire is leaving site | ROC General | 2025-10-21
ROC | October | Carter Dunn Signing In | ROC General | 2025-10-20
ROC | October | Adeela Khan signing out | ROC General | 2025-10-20
ROC | October | Angelica Chepiga signing in | ROC General | 2025-10-24
ROC | October | SEOC 6/7 Frank from PS onsite for monthly fire alarm testing Filter 1 backwash | ROC General | 2025-10-22
ROC | October | Christian Van Beek signing in. Weather: 1C and clear. | ROC General | 2025-10-28
ROC | October | KSSP - Drew from Ferguson Electric on site. JDSS - Christian and Gerrick from Ferguson Electric on site. | ROC General | 2025-10-28
ROC | October | Connor Smith signing out | ROC General | 2025-10-27
ROC | October | KSTP- Gerrick from Ferguson onsite. | ROC General | 2025-10-17
ROC | October | MKPSSA, Drew from Ferguson Electric is on site | ROC General | 2025-10-30
ROC | October | JDSS, Gerric from Ferguson Electric is on site | ROC General | 2025-10-30
ROC | October | KSTP - Christian from Ferguson electric on site. | ROC General | 2025-10-16
ROC | October | SUSP- Michael from CPD onsite. | ROC General | 2025-10-17
ROC | October | GRSSWA- Khalid from IAM is done on site | ROC General | 2025-10-17
ROC | October | VNETAG - Jason from property services on site. STRS48 - Steven from ABPMC leaving site. | ROC General | 2025-10-28
ROC | October | KBSP, Terry G is leaving site | ROC General | 2025-10-29
ROC | October | Ethan Ullalkar signing out. | ROC General | 2025-10-27
ROC | October | Christian Van Beek signing out | ROC General | 2025-10-27
ROC | October | AUETFC- Dominic from Honeywell onsite. 11:48- Finished onsite. | ROC General | 2025-10-27
ROC | October | Carter Dunn Signing Out | ROC General | 2025-10-17
ROC | October | GRSSWA- Kalid from IAM onsite. | ROC General | 2025-10-17
ROC | October | Ethan U signing in SEOC - Throdore from AB onsite site review | ROC General | 2025-10-27
ROC | October | EGSSSC - Joe O leaving site. | ROC General | 2025-10-27
ROC | October | SHTP - Drew from Ferguson Electric on site for TFSA inspections which includes an off load generator test. Arthus L is monitoring remotely. | ROC General | 2025-10-20
ROC | October | Christian Van Beek signing out. | ROC General | 2025-10-31
ROC | October | MARS - Courtney from Torbear Contracting is finished on site | ROC General | 2025-10-31
ROC | October | Angelica Chepiga signing out | ROC General | 2025-10-21
ROC | October | SUETDR, Jeff from Key Shack is on site 14:48, Jeff leaving site | ROC General | 2025-10-21
ROC | October | KBSP, Stephen from AB is leaving site | ROC General | 2025-10-20
ROC | October | STRS48, Drew from Ferguson Electric is leaving site | ROC General | 2025-10-21
ROC | October | NMSSBP - Joe O from property services on site. YDOC9 - Jeff from Keyshack on site for maintenance. | ROC General | 2025-10-27
ROC | October | MARS- Courtney from Torbear is on site | ROC General | 2025-10-22
ROC | October | MARS- Courtney from Torbear is on site STRS48- Drew from Ferguson Electric is on site | ROC General | 2025-10-23
ROC | October | MKPSSA, Drew from Ferguson Electric is on site | ROC General | 2025-10-29
ROC | October | Carter Dunn Signing Out | ROC General | 2025-10-24
ROC | October | Adeela Khan signing out | ROC General | 2025-10-25
ROC | October | JDSS - Drew from Ferguson electric on site for TSSA work. | ROC General | 2025-10-27
ROC | October | Christian Van Beek signing in. Weather: 13C and rain. | ROC General | 2025-10-22
ROC | October | KSETWB - Kevin from yorknet leaving site. | ROC General | 2025-10-28
ROC | October | Christian Van Beek signing out. | ROC General | 2025-10-19
ROC | October | GWTP - Colin from #60 Security is headed to site. | ROC General | 2025-10-27
ROC | October | STRS48- Jeff from Keyshack offsite. Heading to MTSP | ROC General | 2025-10-28
ROC | October | HMSS - Jeff from keyshack on site. | ROC General | 2025-10-28
ROC | October | Connor Smith signing in 2C Cloudy | ROC General | 2025-10-27
ROC | October | Christian Van Beek signing in. Weather: 11C and rain. | ROC General | 2025-10-20
ROC | October | Carter Dunn Signing Out | ROC General | 2025-10-20
ROC | October | Angelica Chepiga signing in | ROC General | 2025-10-16
ROC | October | JDSS - Phil from AB on site. | ROC General | 2025-10-16
ROC | October | STPSMR, Drew from Ferguson Electric is on site | ROC General | 2025-10-29
ROC | October | SEOC, Ben H from Property Services is leaving site | ROC General | 2025-10-29
ROC | October | KSETWB- Ben from Property services leaving site. | ROC General | 2025-10-21
ROC | October | Angelica Chepiga signing out | ROC General | 2025-10-18
ROC | October | MAPS, Courtney from Torbare is finished on site | ROC General | 2025-10-29
ROC | October | Adeela Khan signing in. Weather: 5C and cloudy | ROC General | 2025-10-31
ROC | October | Ethan Ullalkar signing in | ROC General | 2025-10-22
ROC | October | Ethan Ullalkar signing in | ROC General | 2025-10-22
ROC | October | Adam Button signing out | ROC General | 2025-10-31
ROC | October | STRS48 - Drew from Ferguson electric on site, working on generator. | ROC General | 2025-10-16
ROC | October | SEOC6/7 - Theodore onsite for site inspection | ROC General | 2025-10-29
ROC | October | SEOC4 - Chris from Property services on site for fire testing. | ROC General | 2025-10-16
ROC | October | SEOC6/7- Theo from AB is on site | ROC General | 2025-10-22
ROC | October | SEOC6/7-Theo from AB done on site | ROC General | 2025-10-22
ROC | October | Connor Smith signing out | ROC General | 2025-10-30
ROC | October | KSTP - Garrick from Ferguson Electric on site. | ROC General | 2025-10-20
ROC | October | MTW3, Amid from ETO engineering is leaving site | ROC General | 2025-10-20
ROC | October | LSSS, Ben H from Property Services is on site | ROC General | 2025-10-20
ROC | October | YDOC, Aquib S from Magnum Fire is on site, testing fire system | ROC General | 2025-10-21
ROC | October | SEOC67 - Theodore from AB finished at site | ROC General | 2025-10-27
ROC | October | STRS48 - Jeff from keyshack on site. | ROC General | 2025-10-28
ROC | October | Connor Smith signing in 16C Cloudy | ROC General | 2025-10-11
ROC | October | AUPSWS- Phil from AB onsite. 09:31- Offsite | ROC General | 2025-10-03
ROC | October | MAPS- Courtney from Torbear onsite. | ROC General | 2025-10-08
ROC | October | SEOC Shaft 6-7 - Garrick from Ferguson electric on site. | ROC General | 2025-10-09
ROC | October | KSSP - Phil from Ab onsite working on generator pad, | ROC General | 2025-10-10
ROC | October | STETBR- Jeff from Keyshack finished onsite. | ROC General | 2025-10-01
ROC | October | Jeff from Keyshack visiting the following sites- BVPS, LSSS, MKETFA, MKPSSA, MKRSMR | ROC General | 2025-10-07
ROC | October | STPSMR- Drew from Ferguson Electric is on site | ROC General | 2025-10-08
ROC | October | AUETFC - Dominic from honeywell leaving site. | ROC General | 2025-10-02
ROC | October | SHSP - Drew (Ferguson) KSSP - Phil (AB Mgmnt and Construction) | ROC General | 2025-10-03
ROC | October | YD OCF, Drew from Ferguson Electric is on site | ROC General | 2025-10-06
ROC | October | Adam Button signing out | ROC General | 2025-10-02
ROC | October | Christian Van Beek signing in. | ROC General | 2025-10-02
ROC | October | Adam Button signing in 18C Clear | ROC General | 2025-10-07
ROC | October | HLSSSC - Dominic from Honeywell on site. 14:30 Off site. | ROC General | 2025-10-09
ROC | October | NMTKKC - Cody H from Kingdom construction on site. | ROC General | 2025-10-02
ROC | October | Angelica Chepiga signing out | ROC General | 2025-10-03
ROC | October | SHSP, Steve B from LCD Mechanical is on site | ROC General | 2025-10-14
ROC | October | Angelica Chepiga signing out | ROC General | 2025-10-15
ROC | October | JDSS- Gerrick from Ferguson finished onsite. | ROC General | 2025-10-07
ROC | October | Carter Dunn Signing Out | ROC General | 2025-10-14
ROC | October | Ethan U signing in | ROC General | 2025-10-14
ROC | October | NMPSKC- Phil from AB on site | ROC General | 2025-10-06
ROC | October | Christian Van Beek signing in. Weather: 24C and clear. | ROC General | 2025-10-03
ROC | October | BLSS - Chris from Property services on site for fire alarm testing. | ROC General | 2025-10-15
ROC | October | STPSTL- Jeff from Keyshack leaving site, heading to STETBR | ROC General | 2025-10-01
ROC | October | STRS48- Gerrick from Ferguson finished onsite. | ROC General | 2025-10-01
ROC | October | Christian Van Beek signing out. | ROC General | 2025-10-01
ROC | October | KSTP- Christian from Ferguson Electric onsite. | ROC General | 2025-10-02
ROC | October | Auto-dialer - System general polling failure, acknowledge alarm . No other alarms or issues associated with alarm. Will monitor | ROC General | 2025-10-15
ROC | October | STRS48 - Garric from Ferguson electric off site. | ROC General | 2025-10-01
ROC | October | NMTKKC - Cody from Kingdome construction on site. | ROC General | 2025-10-15
ROC | October | Adam Button signing out | ROC General | 2025-10-14
ROC | October | VNPSAP- Ben from Property Services finished onsite. | ROC General | 2025-10-02
ROC | October | STPSTL- Jeff from Keyshack onsite. | ROC General | 2025-10-01
ROC | October | Christian Van Beek signing out. | ROC General | 2025-10-02
ROC | October | STPSMR- Drew from Ferguson onsite. | ROC General | 2025-10-03
ROC | October | NMETHW - David Ip from ETO engineering on site. | ROC General | 2025-10-02
ROC | October | MTSP - Steve from LCD mechanical on site. | ROC General | 2025-10-15
ROC | October | JFPS-Houman from CPD with contractors on site. KSTP - Garrick from Ferguson electric on site. | ROC General | 2025-10-15
ROC | October | KCETFS- Nick R on site from PPT to work on bell connection system | ROC General | 2025-10-06
ROC | October | MKETFA - Panchai from YR Police on site for monthly inspection. 12:43 Panchai from YR Police off site. | ROC General | 2025-10-15
ROC | October | AUPSWS - Razam from IAM on site. 14:45 Off site. | ROC General | 2025-10-15
ROC | October | Connor Smith signing in 5C Clear | ROC General | 2025-10-09
ROC | October | Ethan Ullalkar signing out. | ROC General | 2025-10-10
ROC | October | SHSP - Drew from Ferguson electric on site. 17:00 Off site | ROC General | 2025-10-10
ROC | October | SEOC OCF - Drew from Ferguson electric off site. | ROC General | 2025-10-15
ROC | October | AUW6- Jeff from Keyshack on site | ROC General | 2025-10-14
ROC | October | RHPSPA- Jeff from Keyshack done on site | ROC General | 2025-10-07
ROC | October | MAPS - Chris from Property services on site for fire alarm testing. | ROC General | 2025-10-15
ROC | October | MTW3 - Jeff from Keyshack off site. | ROC General | 2025-10-15
ROC | October | SHSP - Kevin from Yorknet off site. | ROC General | 2025-10-15
ROC | October | MKRSMR- Johnathan from PCS onsite | ROC General | 2025-10-08
ROC | October | NMTKKC- Cody from Kingdom Construction onsite. | ROC General | 2025-10-07
ROC | October | MTW3 - Jeff from Keyshack on site. SHSP - Kevin from Yorknet on site. | ROC General | 2025-10-15
ROC | October | SEOS67- Teodore from AB on site HLW1 - Jeff from Keyshack leaving site, heading to HLW2 | ROC General | 2025-10-15
ROC | October | Jeff from Keyshack visiting following sites; JFRS, RHPSWA, NREETCR, KCETDS, AUPSRR, AUETAD | ROC General | 2025-10-08
ROC | October | KSTP- Dominic from Honeywell is on site | ROC General | 2025-10-06
ROC | October | MAPS- Vince from Torbear onsite. 10:17- Offsite. | ROC General | 2025-10-03
ROC | October | SHSP - Theodore from Ab has tech onsite 8:01 - Tech from AB leaving site. Heading to SHTP 9:12 - Tech from Ab left site and locked up. Will return at a later time | ROC General | 2025-10-10
ROC | October | KSTP- Gerrick Ferguson Electric onsite. | ROC General | 2025-10-08
ROC | October | Carter Dunn Signing In, 10D/Clear | ROC General | 2025-10-13
ROC | October | Gluzen Ramos Ong signing in KSTP - Gerrick (Ferguson) on site | ROC General | 2025-10-03
ROC | October | STW56- Christian from Ferguson onsite. | ROC General | 2025-10-03
ROC | October | GWTP - Wilson from AECON on site to complete IT maintenance work. | ROC General | 2025-10-02
ROC | October | Adam Button signing out | ROC General | 2025-10-06
ROC | October | Ethan U signing in | ROC General | 2025-10-06
ROC | October | PVSS - Jeff from Keyshack on site. | ROC General | 2025-10-02
ROC | October | MTSS - Scott Wei from York Region IAM leaving site. | ROC General | 2025-10-02
ROC | October | NMTKKC- Free Chlorine Hi Alarm. Went back into normal range. Cleared alarm. | ROC General | 2025-10-01
ROC | October | Adam Button signing out 14C clear | ROC General | 2025-10-06
ROC | October | Adam Button signing in 20C Clear | ROC General | 2025-10-01
ROC | October | KSSP- Phil from AB Construction onsite. | ROC General | 2025-10-02
ROC | October | Ethan Ullalkar signing out. | ROC General | 2025-10-04
ROC | October | Adam Button signing out | ROC General | 2025-10-08
ROC | October | JDSS- Drew from Ferguson Electric is on site | ROC General | 2025-10-08
ROC | October | MKRSMR- Jon from property services is done on site locked and armed | ROC General | 2025-10-08
ROC | October | RHRSTR - Kevin from yorknet off site. NMETYS - David Ip from ETO engineering on site. STW56 - Christian from Ferguson Electric off site. NMTKKC - Cody H from Kingdom construction off site. | ROC General | 2025-10-02
ROC | October | AUSSYS- Jeff from Keyshack going to site. | ROC General | 2025-10-08
ROC | October | KSSSKR, KCETFS, KCETDS, KCW34 - Jeff from Keyshack will be heading to these sites to inspect the locking mechanisms on doorways. | ROC General | 2025-10-02
ROC | October | SHSP- Drew from Ferguson offsite. | ROC General | 2025-10-03
ROC | October | Christian Van Beek signing out. | ROC General | 2025-10-14
ROC | October | NMETYS - Jason from Property services on site for inspection. | ROC General | 2025-10-09
ROC | October | Gluzen Ramos Ong signing out | ROC General | 2025-10-03
ROC | October | KSSP - Phil from AB leaving site. | ROC General | 2025-10-01
ROC | October | Angelica Chepiga signing in, weather +10C | ROC General | 2025-10-01
ROC | October | Adam Button signing out | ROC General | 2025-10-01
ROC | October | STRS48- Drew from Ferguson onsite. 14:23- Offsite. | ROC General | 2025-10-09
ROC | October | Ethan Ullalkar signing out. | ROC General | 2025-10-12
ROC | October | STRS48- Gerrick from Ferguson onsite. | ROC General | 2025-10-02
ROC | October | Connor Smith signing in | ROC General | 2025-10-07
ROC | October | Carter Dunn Signing In | ROC General | 2025-10-14
ROC | October | Ethan U signing in | ROC General | 2025-10-05
ROC | October | MARS, Vince from Torbeart is on site | ROC General | 2025-10-06
ROC | October | MAPS, Drew from Ferguson Electric is on site | ROC General | 2025-10-06
ROC | October | Connor Smith signing out | ROC General | 2025-10-07
ROC | October | Connor Smith signing in 10C Clear | ROC General | 2025-10-08
ROC | October | Connor Smith signing in 10 C Clear | ROC General | 2025-10-02
ROC | October | Angelica Chepiga signing out. | ROC General | 2025-10-09
ROC | October | Ethan U signing in | ROC General | 2025-10-10
ROC | October | Angelica Chepiga signing in | ROC General | 2025-10-09
ROC | October | VNRSKS - Jeff from keyshack on site. | ROC General | 2025-10-02
ROC | October | Connor Smith signing out | ROC General | 2025-10-11
ROC | October | STW12- Jeff from Keyshack onsite. 14:36- Finished onsite. | ROC General | 2025-10-01
ROC | October | Christian Van Beek signing in. | ROC General | 2025-10-01
ROC | October | STW12- Drew from Ferguson offsite. | ROC General | 2025-10-07
ROC | October | Adeela Khan signing out | ROC General | 2025-10-11
ROC | October | BLSS - Jeff from Keyshack on site. | ROC General | 2025-10-01
ROC | October | JDSS, Christian from Ferguson Electric is on site | ROC General | 2025-10-06
ROC | October | STPSTL- Dominic from Honeywell done on site | ROC General | 2025-10-08
ROC | October | MAPS- Stephen B is done on site | ROC General | 2025-10-08
ROC | October | Christian Van Beek signing in. Weather: 25C and sun. | ROC General | 2025-10-04
ROC | October | BLSS- Ken from ITS onsite for network work. | ROC General | 2025-10-02
ROC | October | Carter Dunn Signing In, 11D/Clear | ROC General | 2025-10-08
ROC | October | Ethan Ullalkar signing out. | ROC General | 2025-10-06
ROC | October | Adeela Khan signing in KSOCMA - Kurt from Compnet is on site to continue installing the wifi | ROC General | 2025-10-11
ROC | October | Pest Control visiting the following sites; NBW3, NBSSJA, NBET, NBET27, NBW3, KCSSKR, KCETFS, KCETDS | ROC General | 2025-10-08
ROC | October | Christian Van Beek signing out. | ROC General | 2025-10-04
ROC | October | AUETFC - Dominic from Honeywell on site. | ROC General | 2025-10-02
ROC | October | Ethan Ullalkar signing out. | ROC General | 2025-10-15
ROC | October | STPSMR- Drew from Ferguson Electric is on site | ROC General | 2025-10-15
ROC | October | Angelica Chepiga signing out | ROC General | 2025-10-01
ROC | October | VNPSAP - Ben H from CPD on site to work on a de-humidifier. | ROC General | 2025-10-02
ROC | October | Connor Smith signing out | ROC General | 2025-10-03
ROC | October | JDSS- Theodore from AB onsite. | ROC General | 2025-10-03
ROC | October | KSETWB- Dominic from Honeywell onsite. 09:12- Offsite. | ROC General | 2025-10-03
ROC | October | Connor Smith signing out | ROC General | 2025-10-09
ROC | October | STPSMR - Drew from Ferguson Electric on site for staff fire alarm training. | ROC General | 2025-10-02
ROC | October | SEOC 6/7, Drew from Ferguson Electric is on site | ROC General | 2025-10-14
ROC | October | PVSS, Christian from ferguson electric is finished on site | ROC General | 2025-10-06
ROC | October | BVPS- Ken from ITS onsite. | ROC General | 2025-10-08
ROC | October | KSSP- Wilson from Aecon offsite. | ROC General | 2025-10-01
ROC | October | MTETNL- Jeff from Keyshack is done on site | ROC General | 2025-10-15
ROC | October | RHPSPA- Steve from Keyshack is on site | ROC General | 2025-10-15
ROC | October | Christian Van Beek signing in. Weather: 20C and clear. | ROC General | 2025-10-12
ROC | October | Connor Smith signing out | ROC General | 2025-10-08
ROC | October | KSSP- Phil from AB onsite. | ROC General | 2025-10-01
ROC | October | KSTP - Christian from Ferguson leaving site | ROC General | 2025-10-10
ROC | October | GWTP - Christine Floyd with Georgina Fire doing a tour on site out @ 11:29 | ROC General | 2025-10-03
ROC | October | MTETNL- Jeff from Keyshack is on site | ROC General | 2025-10-15
ROC | October | STPSMR - Gerrick (Ferguson) on site | ROC General | 2025-10-03
ROC | October | Ethan U signing in Weather 15. | ROC General | 2025-10-04
ROC | October | Angelica Chepiga signing in | ROC General | 2025-10-15
ROC | October | KSTP - Christian from Ferguson electric on site. | ROC General | 2025-10-10
ROC | October | MKETFA- Alex from Exel Power is on site | ROC General | 2025-10-15
ROC | October | SHETCS - David Ip from ETO engineering on site. | ROC General | 2025-10-02
ROC | October | JDSS - Phil (AB) offsite | ROC General | 2025-10-03
ROC | October | KSSP- Franco from Property Services offsite. | ROC General | 2025-10-01
ROC | October | MAPS- Courtney from Torbear onsite. | ROC General | 2025-10-09
ROC | October | Ethan Ullalkar signing out. | ROC General | 2025-10-07
ROC | October | SHTP- Theodore from AB onsite. | ROC General | 2025-10-03
ROC | October | JDSS- Phil from AB onsite. | ROC General | 2025-10-03
ROC | October | Christian Van Beek signing out. | ROC General | 2025-10-05
ROC | October | MARS- Courtney from Torbear is on site for south cell lockout. Will be waiting for operator to get to site to proceeded with work | ROC General | 2025-10-14
ROC | October | JDSS- Phil from AB onsite. | ROC General | 2025-10-02
ROC | October | KSSP v- Phil from AB leaving site. | ROC General | 2025-10-10
ROC | October | NMETHW - David Ip leaving site. PVSS - Jeff from keyshack leaving site. Headed to VNETAG. | ROC General | 2025-10-02
ROC | October | RHRSTR- Kevin from Yorknet onsite. | ROC General | 2025-10-02
ROC | October | Connor Smith signing in 16C Cloudy | ROC General | 2025-10-10
ROC | October | Christian Van Beek signing in. Weather: 15C and clear. | ROC General | 2025-10-13
ROC | October | NMETYS - David Ip from ETO off site. | ROC General | 2025-10-02
ROC | October | KSSP, Phil from AB is leaving site | ROC General | 2025-10-14
ROC | October | Connor Smith signing in 10C Clear | ROC General | 2025-10-03
ROC | October | Adam Button signing in 6C clear | ROC General | 2025-10-14
ROC | October | NEMTYS- Jason from Property Services leaving site | ROC General | 2025-10-09
ROC | October | KCETDS, Jeff from Key shack is on site | ROC General | 2025-10-14
ROC | October | Angelica Chepiga signing out | ROC General | 2025-10-10
ROC | October | BLSS- Ken from ITS onsite | ROC General | 2025-10-08
ROC | October | JDSS- Drew from Ferguson onsite. | ROC General | 2025-10-09
ROC | October | STW56 - Christian (Ferguson) offsite | ROC General | 2025-10-03
ROC | October | SEOC6- Theo from AB is done on site | ROC General | 2025-10-15
ROC | October | Ethan Ullalkar signing in | ROC General | 2025-10-12
ROC | October | Connor Smith signing out | ROC General | 2025-10-12
ROC | October | Pest control visiting sites: AURSBS, AUETRR, AUPSRR, AUW14, AUPSOH,AUETOH,AUW5,AUSS,AUW6,AUETFC,AUPSWS. | ROC General | 2025-10-15
ROC | October | GRSSWB - Dominic from Honeywell leaving site. | ROC General | 2025-10-15
ROC | October | Christian Van Beek signing out | ROC General | 2025-10-13
ROC | October | Angelica Chepiga signing in,weather +17C | ROC General | 2025-10-02
ROC | October | Connor Smith signing in 10 C Cloudy | ROC General | 2025-10-01
ROC | October | Adam Button signing in | ROC General | 2025-10-15
ROC | October | MARS- Courtney from Torbear is on site | ROC General | 2025-10-15
ROC | October | Adam Button signing out | ROC General | 2025-10-15
ROC | October | Adam Button signing in | ROC General | 2025-10-08
ROC | October | Adam Button signing out | ROC General | 2025-10-07
ROC | October | Adeela Khan signing out | ROC General | 2025-10-08
ROC | October | Adeela Khan signing in. Weather:15C and raining | ROC General | 2025-10-07
ROC | October | JDSS - Christian from Ferguson electric on site. | ROC General | 2025-10-10
ROC | October | Ethan U signing in Weather 15. | ROC General | 2025-10-15
ROC | October | SEOC OCF - Drew from Ferguson electric on site. | ROC General | 2025-10-15
ROC | October | NMTKKC- Joe D req. to change duty stop from 80 to 75% | All Water System ROC General | 2025-10-27
ROC | October | STETBR - Free chorine low alarms/clear in a few minutes. ET @46%. STETTL at 69%, slowly draining. Phil D requested Activate zone 1 and zone 2 Duty. # Consult. | All Water System ROC General | 2025-10-29
ROC | October | Carter Dunn Signing In, 12D/Clear | All Water System ROC General | 2025-10-29
ROC | October | NMETHW, Joe D heading to site to do sampling | All Water System ROC General | 2025-10-29
ROC | October | STW3 - Rick L onsite looking into effluent analyzer | All Water System ROC General | 2025-10-29
ROC | October | Angelica Chepiga signing out | All Water System ROC General | 2025-10-24
ROC | October | AUMCBA - Parth P & Red B finished at site | All Water System ROC General | 2025-10-29
ROC | October | Angelica Chepiga signing in,weather -1C | All Water System ROC General | 2025-10-26
ROC | October | NMETIB - Deactivated duty 1, as per interim | All Water System ROC General | 2025-10-27
ROC | October | VNPS PD8 - Dan B finished on site. | All Water System ROC General | 2025-10-16
ROC | October | NMETHW, Total/Combined Cl2 Lo Alarm, Tower currently filling, Reviewed trend and the residual is dropping at a steady rate, Lowest it got on the trends, contacted Joe D, directed to disregard at this time as the system is now slowly coming back up however if the residual drops again, he would like a call. Once home, he will review the system Consult | All Water System ROC General | 2025-10-29
ROC | October | RHRSTR- Changed lo setpoint from 60% to 55% and lolo from 55 to 50% as per interim | All Water System ROC General | 2025-10-17
ROC | October | HLETYS, Pre Injection Combined Cl2 lo alarm, Notified Jordan B, Directed to disregard | All Water System ROC General | 2025-10-24
ROC | October | QVW12- Placed well 2 in man/off to avoid hi level at QVETQS | All Water System ROC General | 2025-10-16
ROC | October | Adam Button signing in 2C clear | All Water System ROC General | 2025-10-17
ROC | October | MKRSEM- Called Metro spoke with Brett to stop pumping to reservoir | All Water System ROC General | 2025-10-17
ROC | October | RHRSTR- Changed Cell 1 lo level from 64 to 60 and lolo from 60 to 55 as per interim STW12- Travis W and Joe M on site to fix leak on hypo pump leak | All Water System ROC General | 2025-10-17
ROC | October | YWS + NYWS NORMAL Angelica Chepiga signing out | All Water System ROC General | 2025-10-26
ROC | October | Christian Van Beek signing in. | All Water System ROC General | 2025-10-27
ROC | October | RHMCMD - back to auto. | All Water System ROC General | 2025-10-26
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-26
ROC | October | HLW2 VC - Downstream Pressure Hi alarm came in. Checked site. Duty just deactivated. Pressure kept fluctuating. Called Jacob M. who informed the pressure should come back down when the valve closes. #CONSULT | All Water System ROC General | 2025-10-26
ROC | October | NMETIB - Deactivated duty 1 while NMETHW fills. | All Water System ROC General | 2025-10-27
ROC | October | YWS + NYWS Normal Connor Smith signing out | All Water System ROC General | 2025-10-27
ROC | October | SHTP - Jacob called back about the UVT Low alarm and informed that he has cleared alarm. Jacob informed that if the alarm comes in again but does not interlock the plant, can be reset | All Water System ROC General | 2025-10-27
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-27
ROC | October | KSTKWP - Activated duty in preparation for GWTP Intake Inspection, as per Stephen B. | All Water System ROC General | 2025-10-28
ROC | October | STRS48- Influent Free Chlorine HiHi Alarm. Will monitor. 23:52- Cleared alarm | All Water System ROC General | 2025-10-29
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-30
ROC | October | AUW14- Well 1 Waste Flow Fault, Flow LoLo, Waste Valve Open Alarms. Interlocked well. 01:28- Cleared alarms. Well started up in duty 1. | All Water System ROC General | 2025-10-30
ROC | October | Adeela Khan signing out | All Water System ROC General | 2025-10-30
ROC | October | SHTP- Well 2 pump uncomm start alarm. Well 2pump is off, reset alarm. | All Water System ROC General | 2025-10-17
ROC | October | QVW12 - Influent Free Chlorine Lo alarm came in. Checked site. Wells are running and influent levels are dropping. Called Jason G. but no answer. Will try again 16:05 - Jason G. called back and directed to increase the dosing factor and see if that helps. If this does not work, Jason requested to switch chlorinators as this is an ongoing issue 16:36 - Influent levels did not recover. Called Jason G. but no answer. Will try again 17:05 - Called Jason G. again but no answer 17:14 - Jason Called back and directed to place chlorine pump 1 back to auto and switch chlorinator duties. Will monitor for 15 mins 17:30 - Influent Free levels came back to optimal range and alarm has been cleared #CONSULT | All Water System ROC General | 2025-10-18
ROC | October | GWTP - Stephen B finished at site | All Water System ROC General | 2025-10-27
ROC | October | GWTP Intake Inspection - Stephen B. called to request a top up of the towers in Georgina for the inspection. Stephen gave direction to activate both duties before 05:00 if they are not already active | All Water System ROC General | 2025-10-26
ROC | October | AUW14//AUW57, Placed wells 1/3/4/5 back to auto | All Water System ROC General | 2025-10-30
ROC | October | YWS + NYWS NORMAL | All Water System ROC General | 2025-10-18
ROC | October | STETTL - Outlet Free Chlorine Lo alarm came in. Tower is filling. 10:47 - Free chlorine Levels came back to optimal range. Alarm has cleared | All Water System ROC General | 2025-10-18
ROC | October | NMETIB/NMETHW - Placed NMVCBA at 70 L/s and NMVCIB at 50 L/s as per interim 17:40 - Placed valves back to normal | All Water System ROC General | 2025-10-18
ROC | October | SUETDR- Historian heartbeat alarm came in. Trends okay notified Yash S. Will take a a look on SCADA NMETIB- Deactivated D1 to offset from NMETHW as per shift report | All Water System ROC General | 2025-10-16
ROC | October | AUW14, Placed wells 1/3/5 back to auto | All Water System ROC General | 2025-10-17
ROC | October | Connor Smith signing in | All Water System ROC General | 2025-10-17
ROC | October | VNETAG - Aaron C and Kevin Z working on radio. | All Water System ROC General | 2025-10-16
ROC | October | NMTKKC - Joe D finished on site, placing all chemical pumps back to auto, requested Duty stop back to 75%. | All Water System ROC General | 2025-10-16
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-20
ROC | October | Connor Smith signing in 7C Rainy | All Water System ROC General | 2025-10-30
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-31
ROC | October | BLW3- Joe M finished onsite. | All Water System ROC General | 2025-10-21
ROC | October | AURSBS- Ben H closed AUVCBS and has Jerry Z attending site to hook up portable generator Created CMU 5 W11407539 NRETBR- Will M attending site to hook up portable generator Created CMU 5 W11407546 ANW23- Station turbidity fault alarm came in. Jake M on site working on analyzer #CMU5 | All Water System ROC General | 2025-10-31
ROC | October | AURSBS- Pre Injection total Cl2 lolo.Pre injection monochloramine OOR, pre injection total and free ammonia OOR, post injection free CL2 OOR, post injection free ammonia OOR, post injection total ammonia and historian heartbeat alarms came in. Chem system off with sample pumps OOS as well as no power to site. No dosing on site Jerry Z will be on site soo with portable generator | All Water System ROC General | 2025-10-31
ROC | October | RHRSWA- Activated D1 | All Water System ROC General | 2025-10-17
ROC | October | QVW12 - Rick L and Parth P finished on site. Placed pumps 1 and 2 back to auto. | All Water System ROC General | 2025-10-16
ROC | October | 01:30 BVPS - Rob P called, confirmed all valves have been reopened. Returning BVPS to normal operation. Notified Toronto water (Zoran). Started Duty 1 pumps one in a time. 01:50 Pumps running normal, Res filling. Rob P and Stephen B leaving site. | All Water System ROC General | 2025-10-19
ROC | October | NMMCHW, East Gwillimbury Pressure lolo, notified Both Ben H/Ryan B but aren't aware of anything, placed the valve man/open to help get pressure into the system, Contacted Blair S from EG to see if they have anyone over there but he isn't aware of anything either 08:24, Contacted Dwayne L, directed to place the valve back to man/close as he believes it may be a PIT issue. Will continue to monitor | All Water System ROC General | 2025-10-23
ROC | October | BLW3 - Dan Z on site, isolated well 3 pump, requested disregard all alarms including chlorine alarms until end of the day. | All Water System ROC General | 2025-10-21
ROC | October | Connor Smith signing in | All Water System ROC General | 2025-10-21
ROC | October | STW12- Effluent free Cl2 alarm came in. well not active no water directed to users. Will recover once well starts up KLPSWL- Discharge pressure lo alarm. Slight dip in trends but recovered okay. Cleared alarm | All Water System ROC General | 2025-10-23
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-24
ROC | October | HLW1, CT not Achieved Alarm, Contacted Jordan B who is on site flushing | All Water System ROC General | 2025-10-30
ROC | October | JFPS- Benson S done on site NRETCR- Deactivated D1 | All Water System ROC General | 2025-10-16
ROC | October | 145 HWP ROC- Dominic from Honeywell req access to SCADA server room. Notified John D. Approved access. Granted access using ID badge and key code provided by Courtney F. | All Water System ROC General | 2025-10-17
ROC | October | 145 HWP ROC- Scott from Property services on site to test new keycard access/Door held/forced open alarm to SCADA server room. Notified Mike O. Mike O Approved access. Opened door tested alarm and shut door. | All Water System ROC General | 2025-10-16
ROC | October | NBW3 - Influent free chlorine lolo alarm. Checked site, well activated in schedule mode before shutting down on a lowlow influent free chlorine reading. Trending shows that the reading has recovered. Placed hypo pump 2 back into duty 1 and cleared alarms. Monitored well start. | All Water System ROC General | 2025-10-19
ROC | October | RHMCMD - Placed valve in auto mode. | All Water System ROC General | 2025-10-20
ROC | October | NMETIB - Deactivated duty 1 while NMETHW fills. | All Water System ROC General | 2025-10-20
ROC | October | YWS + NYWS NORMAL | All Water System ROC General | 2025-10-29
ROC | October | NMW136- Treated total/combined Cl2 lo alarm came in recovered after 4 mins cleared alarms | All Water System ROC General | 2025-10-17
ROC | October | VNPS PD7 - Placed Pump 2(Duty 2) to auto as per Interim. | All Water System ROC General | 2025-10-17
ROC | October | STETBR, Activated D1, Free Cl2 is slowly dropping, by activating the duty, this should freshen up the line STW12, Placed wells 1/2 man/on | All Water System ROC General | 2025-10-30
ROC | October | MKPSSA, Placed Pump 2 man/off MKRSMR, Placed valves back to auto MKRSEM, Notified Toronto operator Peter to start filling the res | All Water System ROC General | 2025-10-20
ROC | October | AUPSOH, Jason G on site, testing Temp alarms and running Generator | All Water System ROC General | 2025-10-21
ROC | October | NRETCR - Ryan B onsite, altitude valve closed, inlet valve isolated to check if for waster passing with it closed. Will followup with any pressure alarms at JFPS | All Water System ROC General | 2025-10-29
ROC | October | NMVCIB- Changed flow setpoints from 70 to 40L/s NMVCBA- Changed flow setpoints from 70 to 40L/s BVPS- Jack P heading to site to work on Cl2 analyzer | All Water System ROC General | 2025-10-16
ROC | October | GWTP- Stephen B working on UV2. Directed to call if alarms come in related to work | All Water System ROC General | 2025-10-17
ROC | October | VNMCBA - Parth P & Red B onsite for annual calibrations | All Water System ROC General | 2025-10-29
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-29
ROC | October | QVW12- Treated Free Chlorine HiHi. Wells are off. Value recovered. Cleared alarms. | All Water System ROC General | 2025-10-29
ROC | October | YWS + NYWS NORMAL | All Water System ROC General | 2025-10-18
ROC | October | NMW15 - Yash S completed his work and stated the well can go back into auto mode. Made necessary change. | All Water System ROC General | 2025-10-31
ROC | October | BLW12- Station Turbidity OOR, Fault Alarms. Notified Joe M. He will head to site. | All Water System ROC General | 2025-10-17
ROC | October | AUW57- Jerry Z onsite working on all analyzers, and testing Cl leak alarm. | All Water System ROC General | 2025-10-21
ROC | October | KSETDP, Kevin N from IT is on site | All Water System ROC General | 2025-10-21
ROC | October | HLW2- Treated total/combine chlorine residual Lo alarms, quick drop, value recovered in one reading. Cleared alarms. | All Water System ROC General | 2025-10-29
ROC | October | YWS + NYWS Normal NMETHW - Deactivated duty 1 while NMETIB fills. QVW34 - Deactivated QVW4. | All Water System ROC General | 2025-10-21
ROC | October | GWTP - Clearwell 1 chlorine low alarm. Stephen B on site completing maintenance on the clearwell chlorine analyzer. | All Water System ROC General | 2025-10-20
ROC | October | KSETWB, Ben H from Property services is on site | All Water System ROC General | 2025-10-21
ROC | October | HLW2. Adjusted Cl2 dosing from 160 to 159% | All Water System ROC General | 2025-10-23
ROC | October | AUW14/SHTP - Kingsley M restarting the AUW14N1, and SHTPN1 local SCADA servers. you will get historian heartbeat alarms. QVW34 - Eric S onsite working on flow HART comm alarm | All Water System ROC General | 2025-10-22
ROC | October | MKRSEM - Reservoir low level alarm. Called Toronto Water (Peter) and requested they activate two pumps to fill the reservoir. | All Water System ROC General | 2025-10-22
ROC | October | NMMCHW, Placed MC_MV2 Valve (80mm) man/closed back to normal operation | All Water System ROC General | 2025-10-24
ROC | October | NBW3 - Joe W. cleaning silicate injection points | All Water System ROC General | 2025-10-24
ROC | October | SHTP - Filter 2 and filter 3 turbidity hi alarms. Checked site, filter 1 is completing a backwash sequence. Reset alarms as per the shift report. | All Water System ROC General | 2025-10-21
ROC | October | Angelica Chepiga signing in | All Water System ROC General | 2025-10-24
ROC | October | NMETIB, Deactivated D1 | All Water System ROC General | 2025-10-24
ROC | October | Adam Button signing in 10C sunny | All Water System ROC General | 2025-10-25
ROC | October | QVW12- Adjusted Chlorinator 1 from 111% to 108% and placed well 2 in man/off as QVETQS hi alarm came in RHMCMD- Placed Valve back in auto | All Water System ROC General | 2025-10-25
ROC | October | VNETFD - David T testing flood, eyewash alarms. | All Water System ROC General | 2025-10-16
ROC | October | MKRSMR, Contacted Rob P about where we are at with the isolation as the interim stated to start at 08:30 however it seems to be running a bit late on their end. Rob P confirmed that they acknowledge that they are behind however they are ready to start the isolation. Notified Rob that RO Carter will contact Toronto to place their MKRSMR PD6 pumps man/off. Contacted Medhi from Toronto to place their pumps man/off and informed him that the isolation is ready to take place. Pumps were placed man/off at MKRSMR. Notified Rob P that Toronto and ROC is ready for isolation. MKRSMR, Adjusted duty 1 setpoints so D1 start is now at 56% from 40% and placed MKPSSA pumps 1/2/3 in auto - D1 Start 40% to 56% | All Water System ROC General | 2025-10-29
ROC | October | RHPSPA- Tyler ZJ onsite for generator maintenance. | All Water System ROC General | 2025-10-27
ROC | October | KSTP- Raw water turbidity fault alarm came in. Disregard on shift report | All Water System ROC General | 2025-10-16
ROC | October | Christian Van Beek signing in. Weather: 3 C and rain. | All Water System ROC General | 2025-10-31
ROC | October | MAPS - Tyler ZJ and Dan B on site for pump 4 maintenance. Dan B would like to test run pump 4 for approximately 20-30 minutes. Placed pumps 1,2,3 in manual mode while Dan B tests pump 4 to prevent them from activating. | All Water System ROC General | 2025-10-31
ROC | October | Ethan Ullalkar signing out. | All Water System ROC General | 2025-10-27
ROC | October | HLETYS- pre Injection Cl2 lo alarm came in. Placed Chemical pumps in man/off. Opened waste valve MV1 at 30% Enabled hi lo inlet flow alarms and pre injection total Cl2 hi alarm as per procedure 16:45- HLETYS- Tower inlet flow hi alarm came in adjusted MV1 to 40% Tower draining. 16:50-HLW2- Changed FCV from 30L/s to 35L/s 16:55-HLETYS- Changed MV1 to 30% | All Water System ROC General | 2025-10-16
ROC | October | RHVCEM- Placed valve 100% open as per interim Procedure. | All Water System ROC General | 2025-10-17
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-19
ROC | October | STRS48 - Influent Free Chlorine HiHi alarm came in. Levels came back to optimal range within 10 mins and alarm has cleared | All Water System ROC General | 2025-10-27
ROC | October | HLETYS - Pre-injection combined chlorine low alarm. Initiated the flushing procedure interim. Placed the chemical systems manual/off. Activated necessary alarms for flow management. Adjustments will be made to the flow to waste valve as necessary to maintain optimal flow. | All Water System ROC General | 2025-10-21
ROC | October | NMMCHW- Aaron from town of East Gwillimbury called (365-340-2503). They are on site at Harry Walker and Greenlane isolating mians for standpipe installation. Aaron req valve be placed open to help with pressure. Aaron will call back when operations are down for the day | All Water System ROC General | 2025-10-23
ROC | October | HLW2- Red B and Rick L are on site for annual calibrations. Placed wells in man/off | All Water System ROC General | 2025-10-23
ROC | October | BVPS, Jack P/Pat F on site, working on the surge system, directed to disregard alarms, placed BVPS pumps man/off for operators | All Water System ROC General | 2025-10-23
ROC | October | MKRSMR- Called Brett from Metro to change D1 start to 3.5m and D1 stop to 5.5m from 3.0 to 5.0 m | All Water System ROC General | 2025-10-17
ROC | October | NMW12 - Combined chlorine lo and treated total chlorine lo. Picked back up next reading. Will monitor | All Water System ROC General | 2025-10-23
ROC | October | Christian Van Beek signing out | All Water System ROC General | 2025-10-27
ROC | October | KSTKWP-Ben H called to inform Tyler ZJ is onsite for valving work and may isolate the tower. KSETDP was changed to controlling tower and he notified Stephen B. | All Water System ROC General | 2025-10-28
ROC | October | Gluzen Ramos Ong signing in STW3 - Parth P. finished on site, site still out of service | All Water System ROC General | 2025-10-28
ROC | October | ARPS - Free ammonia fault alarm. Checked site, pumps recently activated along with the chemical dosing system. Trending shows a stable free ammonia reading within normal range. Will monitor system and clear alarm if possible. | All Water System ROC General | 2025-10-22
ROC | October | Patriot Sever- Kingsley M done reset | All Water System ROC General | 2025-10-22
ROC | October | MAPS- Lee F on site req PD7 P2 be placed man/on and PD8 P1 placed man/on. Placed PD8 P2-4 in man and started P1. After 10 mins placed PD7 P2 in man on and 1/3 in man/off | All Water System ROC General | 2025-10-22
ROC | October | JFRS - Place pumps 1-3 man/off. Lee F onsite for vibration. Ryan B onsite for sampling as well | All Water System ROC General | 2025-10-22
ROC | October | HLW2 - Combined chlorine hihi, locked at well. Dropped dosing from 159 to 155 for chlorinator 1 now duty 1. HLETYS - Pre injection combined chlorine hi, jump in reading due to water leaving tower with loss of well. Dropped bac to normal range after well came back on | All Water System ROC General | 2025-10-23
ROC | October | HLW2 - Combined chlorine hi, continues to rise near hihi again Rotated back to chlorinator 2 and dropped dosing to 155 | All Water System ROC General | 2025-10-23
ROC | October | Angelica Chepiga signing in | All Water System ROC General | 2025-10-24
ROC | October | AUW14 - Effluent free chlorine low alarm. Called Jerry Z who is on site and monitoring following some maintenance. | All Water System ROC General | 2025-10-28
ROC | October | QVW34, Divya P on site, Running generator/testing cl2 leak/working on the chemical analyzers. Directed to disregard alarms on site till he is finished | All Water System ROC General | 2025-10-21
ROC | October | GWTP, Stephen B//Chris S working on the Solenoid for the clear wells, directed to disregard alarms on site involving the clear wells | All Water System ROC General | 2025-10-30
ROC | October | AURSBS, Activated D1 | All Water System ROC General | 2025-10-30
ROC | October | RHMCMD- Placed valve in manual 04:53- Placed in auto | All Water System ROC General | 2025-10-31
ROC | October | QVW12- Ryan B leaving site. Cl2 system seems okay to run. Will continue to monitor | All Water System ROC General | 2025-10-31
ROC | October | NMTKKC - Joe D finished and leaving site. | All Water System ROC General | 2025-10-28
ROC | October | YWS + NYWS Normal Connor Smith signing out | All Water System ROC General | 2025-10-28
ROC | October | ANVC- Control panel power failure no comms on site cleared alarm and trends okay AURSBS- Control panel power failure alarm. Both sample pumps stopped. Reset alarms manually started sample pumps. AUPSRR- Power failure on site generator running able to clear alarm after 5 mins BLW12- Power failure on site generator running. contacted Joe M. 13:32- AURSBS- Control panel power failure alarm. Both sample pumps stopped. Reset alarms manually started sample pumps. Would not start. Placed Chemical system in manual Notified Ben H. Will contact Will M and Jerry Z 13:34- NRETBR- Control power panel failure and comms fail on site. Notified Ben H 13:34- AUPSRR- Power failure on site and generator running. Will continue to monitor 13:35- MAPS PD8- Dan B done on site all pumps back in auto | All Water System ROC General | 2025-10-31
ROC | October | STETBR - Free chlorine residual low alarm. Value recovered in two readings. Cleared alarm | All Water System ROC General | 2025-10-26
ROC | October | YWS + NYWS NORMAL | All Water System ROC General | 2025-10-26
ROC | October | Adeela Khan signing in. Weather: 5C and cloudy | All Water System ROC General | 2025-10-31
ROC | October | MKRSEM - Called Toronto Water (Zoran) and requested to stop pumping to reservoir due to high levels | All Water System ROC General | 2025-10-28
ROC | October | YWS + NYWS NORMAL | All Water System ROC General | 2025-10-28
ROC | October | Adeela Khan signing out | All Water System ROC General | 2025-10-21
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-21
ROC | October | SHTP- Filter 3 Turbidity Hi Alarm. Backwash just completed. Cleared alarm as per SCADA report | All Water System ROC General | 2025-10-30
ROC | October | Carter Dunn Signing In, 7D/Clear | All Water System ROC General | 2025-10-30
ROC | October | KSTP- Fin Water Fluoride Res LoLo Alarm. Called Stephen B. Directed to rotate fluoride pumps. Placed pump 2 in duty 1. Will monitor. If value does not come back up, can disregard for the night. CONSULT | All Water System ROC General | 2025-10-30
ROC | October | STETTL - Duty is active, ET draining. STETBR - ET @81%, Duty is active- deactivated duty 1. STW12 - Placed well 2 pump back to auto/currently running. | All Water System ROC General | 2025-10-26
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-27
ROC | October | STPSTL- Stephen B opened SRV. STETTL- Stephen B changed duty setpoints to 45-80% | All Water System ROC General | 2025-10-27
ROC | October | RHRSTR - Reservoir Cell 2 Level Lo alarm came in. Called Rob P. just as a heads up #CONSULT | All Water System ROC General | 2025-10-18
ROC | October | YWS + NYWS NORMAL | All Water System ROC General | 2025-10-19
ROC | October | GWTP, Keswick Header Fluoride hihi, Plant isn't running, called Stephen B but no response, will call again in 5 minutes 10:20, Tried calling a few more times but still no response, Stephen B most likely in the basement of GWTP, sent him a teams message with the info | All Water System ROC General | 2025-10-21
ROC | October | YWS + NYWS NORMAL | All Water System ROC General | 2025-10-26
ROC | October | HLW2 - Downstream Pressure HiHi alarm, Sharon VC just activated on schedule mode. HLW2 VCFCV2 interlocked, placed man/off . Pressure alarms cleared. 17:45 Sharon VC closed/ schedule mode. Placed HLW2 VCFCV2 back to auto. | All Water System ROC General | 2025-10-26
ROC | October | AUW14- Treated Free Chlorine HiHi Alarm. Rotated Ammonia pumps so pump 1 in duty 1. Value recovered. Cleared alarm. | All Water System ROC General | 2025-10-31
ROC | October | KCETFS- Historian Heartbeat Alarm. Notified Chris S. He will look into it. 05:08- Chris C finished and reset alarm. Slight gap in trends. W11405343 CMU5 | All Water System ROC General | 2025-10-31
ROC | October | Adam Button signing in | All Water System ROC General | 2025-10-31
ROC | October | NMW12- Treated Total/ Combined Cl2 lo alarms. Well not active. No water directed to users, will monitor. | All Water System ROC General | 2025-10-26
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-19
ROC | October | NMW15- Yash making changes to target treated total Cl2. Requsted well to be placed in man/off for work | All Water System ROC General | 2025-10-31
ROC | October | NBET27 - Joe W testing hi/lo level MKETFA - Jack P testing hi/lo temp alarm, chlorine maintenance, valve exercise | All Water System ROC General | 2025-10-22
ROC | October | SHTP- UV Transmittance Lo Alarm. Notified Dave T. Requested to reset alarm. CONSULT | All Water System ROC General | 2025-10-30
ROC | October | KCETDS, Activated D1 | All Water System ROC General | 2025-10-30
ROC | October | Angelica Chepiga signing in | All Water System ROC General | 2025-10-16
ROC | October | KLPSWL - Roadwork lose of analyzer, city of Vaughan working on cutting pipeline. Disregard lolo discharge pressure until work in complete | All Water System ROC General | 2025-10-22
ROC | October | MAP8 - Place pump 2 man/off. Place pump 3 man/on shortly after for Lee F | All Water System ROC General | 2025-10-22
ROC | October | NMETHW- Free Cl2 hi alarm came in. Noticeably elevated. Notified Joe D. will attend site. NMTKBS- Joe D done on site. AUPSOH- Placed P3/4 in auto | All Water System ROC General | 2025-10-22
ROC | October | BVPS - Jack P requested Vale chamber suction header Valves 1 and 2 back to auto. | All Water System ROC General | 2025-10-16
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-28
ROC | October | Christian Van Beek signing in. Weather: 1C and clear. | All Water System ROC General | 2025-10-28
ROC | October | STETBR - Free chlorine low alarm. Checked site, free chlorine reading above low alarm setpoint. Trending shows a small dip of the free chlorine reading which recovered quickly. Able to clear alarm. | All Water System ROC General | 2025-10-28
ROC | October | EGMCRW - Ryan B completed work, site back to normal OP | All Water System ROC General | 2025-10-21
ROC | October | AUETFC- Talha H rebooting OIT. Disregard Heartbeat Alarm. 13:30- Talha Finished. Cleared alarm. | All Water System ROC General | 2025-10-27
ROC | October | MTW3 - Patrick F testing chlorine leak and running generator. | All Water System ROC General | 2025-10-16
ROC | October | KSETWB - Tower Inlet and Isolation valve fault alarms came in. Tower is filling. Noticed the valves are flipping between Local, Auto, and manual but valves stayed open. Called Phil D. who informed this is due to a phase loss but does not interfere with the tower filling or draining. Phil directed to disregard these alarms for the night #CONSULT | All Water System ROC General | 2025-10-27
ROC | October | GWTP- Stephen B finished onsite. Trains 5,7,8 will be going through an M Clean. Can change Flow back to 200L/s from 190L/s once completed. | All Water System ROC General | 2025-10-28
ROC | October | MKRSEM - RES filling without pumps running. Called Toronto water(Zoran) he will reduce Kenedy flow. | All Water System ROC General | 2025-10-28
ROC | October | TMC317- PIT OOR alarm. Called Metro spoke with Mehdi. Mehdi informed ROC that they have technicians working on PIT. Req increased flow to MARS | All Water System ROC General | 2025-10-16
ROC | October | QVW12 - Tyler S. called to inform that he is on site and will be working on the chlorine booster pump for QVW1. Tyler would need the well down for approximately an hour. Placed QVW1 man/off and placed QVW4 man/on, as per Gluzen R. Confirmed with Ben H. | All Water System ROC General | 2025-10-30
ROC | October | Christian Van Beek signing out. | All Water System ROC General | 2025-10-22
ROC | October | YWS+NYWS normal | All Water System ROC General | 2025-10-24
ROC | October | SHETCS- Post injection total Cl2 hihi alarm interlocked hypo pumps. Continued to monitor cleared after 5 mins STETTL- Outlet free Cl2 lo alarm came in with D1 active will continue to monitor. Trends tend to recover as higher residual water reaches tower 20:51- STETTL- Outlet free Cl2 recovering alarm cleared | All Water System ROC General | 2025-10-24
ROC | October | Patriot Server- Kingsley M restarting Server | All Water System ROC General | 2025-10-22
ROC | October | STW56 - Travis W onsite | All Water System ROC General | 2025-10-22
ROC | October | NMPSKS. Joe D on site, testing each pump for 15 minutes | All Water System ROC General | 2025-10-21
ROC | October | HLETYS - Pre-injection combined lo, duty off. Confirmed Jacob M onsite for grab sample. Operator aware of fluctuation of inlet reading when filling, duty had been deactivated by operator. Residual came back to normal range | All Water System ROC General | 2025-10-29
ROC | October | MKPSSA - Jack P. working on free chlorine analyzer in response to downward trending. | All Water System ROC General | 2025-10-24
ROC | October | HLW1 - Combine chlorine Low/low alarm, quick drop, value recovered , alarm cleared. Well 1 pump local/off | All Water System ROC General | 2025-10-16
ROC | October | HLETYS, Pre-Injection Combined Cl2 lo, notified Jacob M, he is looking into it 16:12, Directed to disregard however if the lolo comes in, directed to give a call | All Water System ROC General | 2025-10-23
ROC | October | Ethan U singing in Weather: 7 light rain | All Water System ROC General | 2025-10-23
ROC | October | YWS+NYWS normal | All Water System ROC General | 2025-10-24
ROC | October | VNRSKS- Activated D1 | All Water System ROC General | 2025-10-25
ROC | October | GWTP- ZW3 MIT failed alarm came in and shutdown. Disregard on shift report. Emailed east water team of outstanding issue | All Water System ROC General | 2025-10-25
ROC | October | BVPS- Disch free Cl2 hi and combined Cl2lo alarm came in. Jack Notified ROC that this is due to the discharge valve being closed possibly starving analyzer. Jack P will trouble shoot and update ROC of changes made | All Water System ROC General | 2025-10-16
ROC | October | AUETFC- Historian heartbeat alarm outstanding trends okay. Notified Ian W. Will take a look at AUETFC as well as other comms issues in Aurora system that came in at same the time, QVW34- Placed Well 4 in man/on. Influent fre Cl2 hi alarm came in. continued to monitor alarm cleared after 3 mins. | All Water System ROC General | 2025-10-22
ROC | October | QVW12- Influent free Cl2 hi alarm came in. Looks like a quick spike continued to monitor. alarm cleared after 6 | All Water System ROC General | 2025-10-22
ROC | October | NMTKKC- inlet combined Cl2 lo alarm came in. Tank draining and header Cl2 trends look okay. KSTP- Fin water fluoride/tot Cl2 res fault alarm came. Disregard on shift report | All Water System ROC General | 2025-10-24
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-25
ROC | October | HLETYS - Pre-injection combined chlorine, first fill cycle without flushing. Trending back upwards but informed Jacob M as swill reading lo and trending up slowly. Okay to disregard and will take a grab if lolo comes in. HLW2 - Treated total chlorine hihi, locked out well. Switched to chlorinator 1 and able to reset alarm and run well after reading went back to normal range Consult | All Water System ROC General | 2025-10-23
ROC | October | MKRSEM - Request TO (Peter) for 2 pumps | All Water System ROC General | 2025-10-23
ROC | October | STW12- Effluent free Cl2 lo alarm came in. Wells not active no water directed to users. Recovered once D1 activates. Will continue to monitor | All Water System ROC General | 2025-10-25
ROC | October | AURSBS - Activated duty to help lower levels at MARS | All Water System ROC General | 2025-10-28
ROC | October | KSETDP - Inlet Total CL2 HiHi alarm came in. Checked site. Disregarded as per shift report | All Water System ROC General | 2025-10-28
ROC | October | NMTKBS- Joe D onsite to take a sample. Requested to place pumps 3 and 4 in manual to keep tank draining as duty was about to activate. 09:12- Joe D finished. Placed pumps back into auto. | All Water System ROC General | 2025-10-28
ROC | October | MKMCBA - Harsh patel on site. | All Water System ROC General | 2025-10-28
ROC | October | STW3 - Parth P on site for annual calibrations. | All Water System ROC General | 2025-10-28
ROC | October | Angelica Chepiga signing in, weather +11C | All Water System ROC General | 2025-10-28
ROC | October | YWS + NYWS NORMAL | All Water System ROC General | 2025-10-29
ROC | October | SHTP- Well 2 pump uncomm stop alarm. Cleared alarm , P3/4 running in D1/2. | All Water System ROC General | 2025-10-29
ROC | October | KLPSWL - Building Low Temperature alarm came in. Will send an email to the west team | All Water System ROC General | 2025-10-27
ROC | October | MKRSEM - Low level alarm. Called Toronto Water (Peter) and requested they activate two pumps to push flow to MKRSEM. | All Water System ROC General | 2025-10-27
ROC | October | STW3- Chlorine Gas Leak, Chlorine HiHi Alarm. Called Parth P. Onsite for calibrations. Can disregard. | All Water System ROC General | 2025-10-28
ROC | October | MAPS/JFRS- Reverted Maple to Jefferson Feed | All Water System ROC General | 2025-10-17
ROC | October | YWS + NYWS NORMAL | All Water System ROC General | 2025-10-18
ROC | October | QVW12- Treated Free Chlorine HiHi and Combined Chlorine Lo Alarms. Duty deactivated recently, wells not running. Values recovered. Cleared alarms. | All Water System ROC General | 2025-10-18
ROC | October | STETBR, Changed Duty start from 45% to 42% and closed the VC_FCV1 valve as per Stephen B | All Water System ROC General | 2025-10-30
ROC | October | MKPSSA - Artour L. is finished calibrating the diesel LIT | All Water System ROC General | 2025-10-30
ROC | October | NBW3 - Influent free chlorine lolo alarm. Checked site, well activated in schedule mode before being interlocked on the influent free chlorine lolo. Placed well manual off, then rotated the hypo pump duty 1 back to hypo pump 2. Called Jake M to inform of the situation and request permission to re-activate the well. Jake had no objections. Cleared alarm, placed well in auto mode and monitored start up. | All Water System ROC General | 2025-10-20
ROC | October | GWTP - Stephen B called , Keswick Header Fluoride hihi/ spiked due to analyzer maintenance. | All Water System ROC General | 2025-10-21
ROC | October | HLETYS - Pre Injection Combined Chlorine Lo alarm came in. Initiated flushing procedure - Placed chemical pumps man/off - Placed flow to waste valve at 30% - Enabled hi/lo inlet flows alarm - Enabled Tower Total Chlorine Residual Hi Alarm | All Water System ROC General | 2025-10-20
ROC | October | Adeela Khan signing out | All Water System ROC General | 2025-10-20
ROC | October | Carter Dunn Signing In | All Water System ROC General | 2025-10-20
ROC | October | YWS + NYWS Normal Carter Dunn Signing Out | All Water System ROC General | 2025-10-30
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-30
ROC | October | STETBR - Free Chlorine Lo alarm came in. Checked site. Called Stephen B. who directed to wait for duty to activate. | All Water System ROC General | 2025-10-30
ROC | October | NBW3, Eric S is finished on site | All Water System ROC General | 2025-10-29
ROC | October | MKRSEM- Called Toronto (Peter) and requested pumps on. | All Water System ROC General | 2025-10-30
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-30
ROC | October | STETBR - Tower level low alarm. Placed STW1 in manual mode while STETBR fills as per the interim procedure. | All Water System ROC General | 2025-10-20
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-21
ROC | October | NBW3 - Well 7 VFD Fault and Influent Free Chlorine LoLo switch alarms came in. Checked site. Well was running in schedule mode. VFD fault is outstanding. Called Jacob M. who directed to monitor site for half an hour 13:55 - Checked site. Still outstanding. Jacob Called back and will head to site. CMU5 Created W11377078 15:35 - Jacob M. called back to inform that he is on site and has taken grab samples of the influent line, backflushed, reset the VFD and will remain on site to make sure the well starts up with no issues #CONSULT | All Water System ROC General | 2025-10-18
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-18
ROC | October | NMTKKC, Activated D1 AURSOH, Activated D1 | All Water System ROC General | 2025-10-30
ROC | October | MTETNL - Joe M. directed to activate duty | All Water System ROC General | 2025-10-30
ROC | October | QVW34 - Influent Free Chlorine LoLo Switch alarm came in. Checked site. Wells were interlocked. Called Ben H. who is headed to site 12:05 - cmu5 created W11405177 #CMU5 | All Water System ROC General | 2025-10-30
ROC | October | NBW5/6- Dan B called to inform that he is on site today to disconnect well 6. There will be alarms associated with this disconnection that can be disregarded. | All Water System ROC General | 2025-10-27
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-19
ROC | October | KSETDP - Inlet total chlorine hihi alarm. Checked site, system duty recently activated resulting in the reversal of flow and activation of the chlorine system. Disregard as per the shift report and cleared alarms. GWTPLL - Screen 2 diff level loss of echo alarm. Able to clear. GWTP - GAC 2 filter turbidity hi alarm. Checked site, plant recently activated to fill system. Trending shows a spike of the turbidity in GAC 2 on activation. Will monitor for ten minutes. 17:14 - GWTP - GAC 2 filter turbidity hi alarm. Filter turbidity value dropping rapidly. Cleared alarm. | All Water System ROC General | 2025-10-19
ROC | October | KSTKWP / SUETDR - Activated duty 1 for these systems to fill them for the interim procedure. | All Water System ROC General | 2025-10-20
ROC | October | MTETNL - Joe M called and directed to activate duty 1. | All Water System ROC General | 2025-10-20
ROC | October | RHMCMD, Placed valve back to auto | All Water System ROC General | 2025-10-29
ROC | October | MAPS PD8- Placed P1-3 in auto as Lee F is done on site | All Water System ROC General | 2025-10-22
ROC | October | GWTP - Stephen B. noticed that the train 8 was OOS and called to ask the ROC if something occurred throughout the night. Informed that nothing has happened. Stephen B. informed that he initiated the MIT and requested to monitor for 15 mins and record the differential high and low pressures. If MIT fails, Stephen requests a call 12:08 - MIT High Differential pressure 1.60 KPa MIT Low Differential 2.15 KPa | All Water System ROC General | 2025-10-18
ROC | October | STETBR - Free Chlorine Lo alarm came in. Checked site. Trends indicate a dip in free chlorine but is recovering. Will monitor 13:05 - Levels are at an optimal range and alarm has cleared | All Water System ROC General | 2025-10-18
ROC | October | KSTP - Settl water turbidity High alarm, called Stephen B, no answer, will call again later. 18:50 Notified Stephen B about Settl water turbidity High alarm outstanding, Checked Filters turbidity- normal, Stephen B requested to switch PACL pumps, assigned Pump 2 to duty 1. # Consult 20:25 Settl water turbidity High alarm cleared. | All Water System ROC General | 2025-10-18
ROC | October | QVETQS - High level alarm, Duty just deactivated. | All Water System ROC General | 2025-10-18
ROC | October | Ethan U signing in | All Water System ROC General | 2025-10-29
ROC | October | GWTP- Gas chlorinator 5/6 hi vaccuum alarm came in. Notified Stephen B. Stephen B is testing Cl2 system | All Water System ROC General | 2025-10-22
ROC | October | QVW34 - Alex B informed of contact tank ticker not updating or moving with well running. Informed Ian W and looking into issue | All Water System ROC General | 2025-10-22
ROC | October | JFRS - Place pump 1 & 2 man/on. Rotate pump 1 & 2 to duty 1. Place pumps back in auto MAPS/VNPS/GWTP/KSTP- Kingsley M rebooting servers | All Water System ROC General | 2025-10-22
ROC | October | RHPSWA- Placed P1 in man/on KSTP-Donald M on site with Yash to work on high lift power supply panel | All Water System ROC General | 2025-10-17
ROC | October | KSTP- Fin Water Tot Cl2/Fluoride Res Fault. Plant not running, Duty just deactivated, disregard alarms as per shift report | All Water System ROC General | 2025-10-18
ROC | October | GWTP LL, Stephen B on site working on the low lift pump 3 again, power will be cycling throughout the day | All Water System ROC General | 2025-10-20
ROC | October | KSTP - Fin water fluoride low alarm. Checked site, high lift pumps recently deactivated. SCADA report directs to disregard this alarm follow high lift pump start/stop. | All Water System ROC General | 2025-10-31
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-31
ROC | October | AUW14- Placed Wells 2/4 in man/on AUW57- Placed Well 5 in man/on NRETCR- Activated D1 | All Water System ROC General | 2025-10-17
ROC | October | Angelica Chepiga signing in | All Water System ROC General | 2025-10-21
ROC | October | MKPSSA - Jack P will run generator on load, will run 2 pumps. Called Toronto water(Farshad) and requested Pump 12 man/off for the duration of the test. | All Water System ROC General | 2025-10-21
ROC | October | AUPSRR- Post injection free Cl2 hi alarm came in trends look abnormal and reagents were changed earlier today. Notified Jerry Z. Will check site | All Water System ROC General | 2025-10-17
ROC | October | GWTP - GAC 2 Filter Turbidity Hi alarm came in. Checked site. Levels went hi but did not interlock and went back to optimal range. Called Stephen B. who directed to ack/reset and will backwash tomorrow. #CONSULT | All Water System ROC General | 2025-10-20
ROC | October | AUPSRR, Will M on site testing Cl2 leak alrm | All Water System ROC General | 2025-10-21
ROC | October | NMVCBA- Adjusted from 60 to 50L/s | All Water System ROC General | 2025-10-17
ROC | October | QVW23- Alex B on site for generator run and will be running well 3 in manual AUVCAD- Red Band Rick L on site for annual calibrations | All Water System ROC General | 2025-10-23
ROC | October | GWTP- Eric S done on site working on backwash tank 1 LIT | All Water System ROC General | 2025-10-16
ROC | October | STPSMR - Jack P and Dan Z on site for a cylinder change. Jack and Dan will be purging the lines and there may be associated alarms triggered. | All Water System ROC General | 2025-10-20
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-23
ROC | October | QVW34 - Well 3 pump man/stop, back to auto. | All Water System ROC General | 2025-10-18
ROC | October | QVW34- Alex B flushing silicate system. Will have wells local off. Will then later be working on chlorinator 2. | All Water System ROC General | 2025-10-27
ROC | October | NBW5/6 - Well 6 pump comm fail alarm and pump 6 VFD fault alarm. Cole W is aware and will investigate if needed. Cole W will also be running NBW2 and NBW3 in manual throughout the day. | All Water System ROC General | 2025-10-27
ROC | October | RHVCEM - Enabled Fwd Flow Lo alarm. Adjusted Lo/LoLo from 250/200L/s to 100/50L/s to trigger closing valve upon reverse flow | All Water System ROC General | 2025-10-16
ROC | October | GWTP - Stephen B called and directed to activate GWTP tomorrow morning before the shift change. Prior to activating the GWTP, Stephen B has directed to disable to mussel control chlorination. | All Water System ROC General | 2025-10-21
ROC | October | HLETYS, Activated D1 and placed Well 2 back to auto | All Water System ROC General | 2025-10-23
ROC | October | VNPSCD - Chlorine emergency system 1 and 2 closed alarms. David T and Jordan B on site changing cylinders. Disregard alarms. | All Water System ROC General | 2025-10-16
ROC | October | NRETCR -Deactivated Duty 1 @ 80% | All Water System ROC General | 2025-10-16
ROC | October | QVW12- Influent free Cl2 hihi alarm came in reset after 3 mins when trends recovered | All Water System ROC General | 2025-10-24
ROC | October | VNMCBA- Meter Chamber Flood Alarm. Called Harsh P. Can disregard alarms from this chamber while onsite. | All Water System ROC General | 2025-10-27
ROC | October | KCETDS, Activated D1 to prepare for another maple to Jefferson feed RHPSWA, Placed pump 1 man/on to help fill JFRS | All Water System ROC General | 2025-10-16
ROC | October | QVW12- Ben H on site to troubleshoot Cl2 system issues | All Water System ROC General | 2025-10-31
ROC | October | ARPS- Total Ammonia Fault alarm came in. Reading within normal range. Able to reset alarm | All Water System ROC General | 2025-10-31
ROC | October | STRS48- Chlorinator 1/2 failed to close alarm came in. Notified Travis W. on site with Joe M purging Cl2 system | All Water System ROC General | 2025-10-31
ROC | October | KSTP - Fin water total chlorine and Fluoride res fault /HLP recently started- disregard by SCADA review. KSTP - Fin water fluoride res LoLo alarm. Switched fluoride pumps. 01:43 Fin water fluoride res value recovered, cleared alarm. | All Water System ROC General | 2025-10-29
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-18
ROC | October | SHETCS- Hypo P1 uncmn stop alarm came in. reset alarm will continue to monitor | All Water System ROC General | 2025-10-17
ROC | October | ARPS- Ammonia total fault came in trend recovered and reset alarm | All Water System ROC General | 2025-10-22
ROC | October | YWS+NYWS normal | All Water System ROC General | 2025-10-26
ROC | October | YWS + NYWS NORMAL | All Water System ROC General | 2025-10-18
ROC | October | Adeela Khan signing in. Weather: 16C and rain | All Water System ROC General | 2025-10-19
ROC | October | MKPSSA - Jack P completed generator test. Cleaning chlorine analyzers, testing flood alarm and exercising valves. Called Toronto water( Farshad) and requested Pump 12 back to auto. | All Water System ROC General | 2025-10-21
ROC | October | YWS + NYWS NORMAL | All Water System ROC General | 2025-10-17
ROC | October | NMVCBA - Placed back to auto. | All Water System ROC General | 2025-10-18
ROC | October | NBW5 - Turbidity Hi alarm, value not dropping, switched silicate pumps. Silicate pump 1 on duty 1, Silicate pump 2 man/off. | All Water System ROC General | 2025-10-19
ROC | October | MKRSEM - Called Toronto Water (Mehdi) and requested to stop pumping to reservoir MKRSMR - Requested to place the start level to 2.5 m to start deep cycling reservoir, as per Dan Z. | All Water System ROC General | 2025-10-21
ROC | October | RHMCMD - Placed valve man/closed | All Water System ROC General | 2025-10-21
ROC | October | NMW12 - Combined Chlorine Lo Alarm came in. Wells are not running and water is not being directed to users | All Water System ROC General | 2025-10-21
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-22
ROC | October | YWS+NYWS normal | All Water System ROC General | 2025-10-26
ROC | October | Adeela Khan signing in. Weather: 6C and sunny | All Water System ROC General | 2025-10-26
ROC | October | KSETDP - Inlet total chlorine hihi alarm. Checked site, flow into the tower has been low while GWTP is off for an inspection. This results in the chemical system starting and stopping. Chlorine values spike when flow is low into the tower, reset alarms. | All Water System ROC General | 2025-10-27
ROC | October | STW12 - Placed STW2 man/on, as per interim | All Water System ROC General | 2025-10-26
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-19
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-19
ROC | October | NMVCBA - Placed 50l/s man/open to extend NMETIB drain cycle. | All Water System ROC General | 2025-10-26
ROC | October | NMETHW - Activated D1 @ 46% to offset with NMETIB and direct water through EGMCRW to south. Will monitor. | All Water System ROC General | 2025-10-26
ROC | October | HLW1 - Ammonia Pump 1 Fault alarm came in. Checked site. Ammonia pump 2 switched to duty 1 automatically. Called Jacob M. who directed to place pump 1 into man/off for the night #CONSULT | All Water System ROC General | 2025-10-26
ROC | October | GWTP - Phil D and Stephen B on site for turbidity analyzer maintenance | All Water System ROC General | 2025-10-28
ROC | October | AUMCBS - Rick L and Parth P finished and leaving site. | All Water System ROC General | 2025-10-20
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-28
ROC | October | HLW2- Downstream Pressure HiHi Alarm. Sharon valve started up in schedule mode and interlocekd HLW2 VC. Will reset alarm once schedule mode is completed. 14:47- Cleared alarm. Valve went back into duty 1. | All Water System ROC General | 2025-10-28
ROC | October | QVETQS - High level alarm, deactivated Duty 1. | All Water System ROC General | 2025-10-28
ROC | October | STETTL - Tower level Low alarm, area deep cycling ET. | All Water System ROC General | 2025-10-28
ROC | October | MKRSMR - Called Toronto water (Zoran) and requested to change start/stop setpoints for the trial Kennedy Rd 1500mm watermain isolation tomorrow. Start setpoint from 3,0 m to 4,5 m. Stop setpoint from 5,0 m to 5,7 m. As per Interim Memo from Christina Sistilli. | All Water System ROC General | 2025-10-28
ROC | October | KSTP, Fin Water Fluoride Res lolo, notified Donald M, he is going to look into it as he's on site | All Water System ROC General | 2025-10-29
ROC | October | MKETFA, Rob P called to confirm that Toronto has closed their valve on site, notified Rob that ill contact Medhi from Toronto to confirm if the valve is closed or not. Contacted Medhi and informed the ROC that they have operators there and that they are currently closing it and will notify the ROC when it is closed. Contact Rob P that it is currently open and once Toronto notifies the ROC that it is closed, we will give him a call 10:56, Medhi from Toronto called, Notified the ROC that they have closed the valve outside the MKETFA. Notified Rob that Toronto has closed their valve 11:00, Contacted Rob P to hold off on his valve work as Toronto isn't sure if the valve we need closed is the valve that is actually closed | All Water System ROC General | 2025-10-29
ROC | October | QVW12- Influent Free Chlorine HI Alarm. Trending is sporadic but recovering. Emailed Joe D and Central Ops. | All Water System ROC General | 2025-10-30
ROC | October | Ethan Ullalkar signing out. | All Water System ROC General | 2025-10-16
ROC | October | VNPS PD7- Placed P2 in auto as per interim | All Water System ROC General | 2025-10-16
ROC | October | NMW12- Combined and Treated Cl2 lo alarms came in. Wells not active no water directed to users NMW136- Combined and Treated Cl2 lo alarms came in. Wells not active no water directed to users will clear alarms when trends recover | All Water System ROC General | 2025-10-16
ROC | October | MKRSMR, Notified Toronto operator Farshad to change Duty start set point from 3m to 2.5m to allow a deep cycle on the reservoir | All Water System ROC General | 2025-10-21
ROC | October | ARPS- Ammonia total fault alarm, Duty 2 pump just deactivated, trend recovered and reset alarm. | All Water System ROC General | 2025-10-28
ROC | October | STETBR - Free chlorine Low alarm, value recovered in one reading, cleared alarm. ET is filling. | All Water System ROC General | 2025-10-28
ROC | October | QVW12 - Alex B with contractor TSAA running generator on load . | All Water System ROC General | 2025-10-21
ROC | October | NMW136, Jason G on site changing cylinders and working on site, directed to disregard leak alarm | All Water System ROC General | 2025-10-21
ROC | October | SHTP - Filter 3 turbidity hi alarm. Checked site, filter 1 going through a backwash sequence. Reset alarm once as per the shift report. | All Water System ROC General | 2025-10-23
ROC | October | RHPSPA- Enabled all stop duty rotation | All Water System ROC General | 2025-10-23
ROC | October | AUVCAD, Placed valve man/closed for Rick L for calibration | All Water System ROC General | 2025-10-23
ROC | October | MKMCLA, Eric S on site, working on the flow meter, directed to disregard alarms 12:22, Eric S is finished on site | All Water System ROC General | 2025-10-23
ROC | October | AUW14, Placed well 2 man/off for Tyler Z 11:23. Placed well back to auto, Tyler Z finished on site | All Water System ROC General | 2025-10-23
ROC | October | STRS48, Artour L is finished on site | All Water System ROC General | 2025-10-23
ROC | October | HLW2 - Treated free chlorine hihi, ammonia pump 2 running. Rotated to ammonia pump 1. Will monitor | All Water System ROC General | 2025-10-23
ROC | October | KSTP - Raw Water Turbidity Fault alarm came in. Disregarded as per shift report | All Water System ROC General | 2025-10-20
ROC | October | STETBR - Free chlorine residual low alarm. Checked site, duty recently activated. STW2 and STETTL are also active to help improve residuals at STETBR as per the shift report and directions from Stephen B. | All Water System ROC General | 2025-10-31
ROC | October | MTETNL, Phil D on site, testing temp alarm and working on the cl2 analyzer | All Water System ROC General | 2025-10-21
ROC | October | QVW34 - Dan B and Divya P testing Well 3 pump, running to waste. QVW34 -Alex B flushing silicate system. | All Water System ROC General | 2025-10-21
ROC | October | NMVCBA- Placed back in auto | All Water System ROC General | 2025-10-23
ROC | October | MARS, Notified Toronto operator Medhi to go back to normal flow to the res | All Water System ROC General | 2025-10-24
ROC | October | YWS + NYWS NORMAL | All Water System ROC General | 2025-10-17
ROC | October | SHTP - Site hydro fail alarm. Checked site, generator is not running and ATS is pointed to town hydro. Called Benson S who is on site and working through the alarms. | All Water System ROC General | 2025-10-27
ROC | October | NMTKKC- Joe D requested change duty stop from 80 to 75% | All Water System ROC General | 2025-10-28
ROC | October | AURSOH- Activated D1 AUW14- Placed P1/3 in auto AUW57- Placed P5 in auto RHMCMD- Placed Valve in manual RHRSTR- Deactivated D1 | All Water System ROC General | 2025-10-26
ROC | October | QVW34- Influent free Cl2 hi alarm came in looks like spike reading continued to monitor cleared alarm after 3 mins. NRETCR- Activated D1 | All Water System ROC General | 2025-10-16
ROC | October | Initializing Maple to Jefferson run KCPSDS- Placed P1/2 in man/off MAPS PD8- Placed P1-4 in man/off JFPS- Placed MV3 in man/open at 10% AURSBS- Placed RES MV4 in man/closed JFPS- Placed MV3 in man/open at 100% MAPS PD8- Placed P4 in man/on and adjusted speed set point to manual 40% 17:24- QVW34- Influent free Cl2 lo alarm cam in analyzer dropped out. placed well in man off as well interlocked on lolo influent. will continue to monitor and restart if analyzer recovers 17:28- HLETYS- Inlet flow hi alarm came in as Sharon valve opened in Schedule mode. NM East system struggling to fill with QVW34 OOS. Notified Phil D to inquire about placing Sharon valve in man/closed. Phil D okay to close valve #consult | All Water System ROC General | 2025-10-16
ROC | October | Ethan Ullalkar signing out. | All Water System ROC General | 2025-10-22
ROC | October | STETTL - Noted that the tower is flatlining on trends since the duty start setpoint was reached. Unsure if the flatline is a result of system demand, faulty LIT/flow sensors or a PCS communications issue. The logbook states that instrumentation did work on the LIT and flow meter earlier today. Called Phil D for a second opinion. Phil D de-activated the STETBR duty which increased the flow into STETTL. The trends are showing a slight increase in level now. Phil D requested to monitor the site closely and ensure the tower begins to fill with this additional flow. #consult | All Water System ROC General | 2025-10-22
ROC | October | STETTL - Outlet Free chlorine Low alarm, notified Dan Z, she will check SCADA. | All Water System ROC General | 2025-10-16
ROC | October | KSTP - Filter 2 Backwash is OOS alarm came in. Checked site. Plant was running but has interlocked on the Backwash Pump 2 Run Status. Called Stephen B. who directed to wait until washwater tank levels hit 0.7 m. If level is not reached, Stephen would like an email and the filter can remain off until the morning. #CONSULT | All Water System ROC General | 2025-10-20
ROC | October | GWTP, UV Reactor 2 Start/Stop Seq Fault/Lo Water flow/Critical Fault, Notified Stephen B, Directed to place UV2 Man/off for the night and place UV1 in D1 consult | All Water System ROC General | 2025-10-16
ROC | October | JFRS, Deactivated D1 to allow RHRSTR to recover a bit | All Water System ROC General | 2025-10-16
ROC | October | BLETNL- Sean from Town of Stouffville flushing. | All Water System ROC General | 2025-10-17
ROC | October | HLW2- Ric L finished onsite. Placed well back into auto | All Water System ROC General | 2025-10-17
ROC | October | NBW3- Silicate P 1 fault and uncmn stop alarm came in. Placed P1 in man and disabled all stop silicate pump duty rotation. Informed Dave T will investigate today | All Water System ROC General | 2025-10-16
ROC | October | 21:42 RHRSTR - Received Reservoir Cell 1 LoLo alarm. Notified Rob P and Stephen B. Will attend BVPS. # CMU5 W11377115 23:46 Rob P and Stephen B on site reopening valves. | All Water System ROC General | 2025-10-18
ROC | October | 13:37 - HLETYS - still draining with duty active. Cole W. informed he, Jordan B. and Dwayne L. going out to open valving in response. CMU5 W11393310 | All Water System ROC General | 2025-10-24
ROC | October | VNRSKS - activated Duty 1 to help water moving to RH. | All Water System ROC General | 2025-10-16
ROC | October | RHMCMD- Placed valve back in auto. | All Water System ROC General | 2025-10-27
ROC | October | Adeela Khan signing in. Weather: 11C and Clear | All Water System ROC General | 2025-10-18
ROC | October | Angelica Chepiga signing out | All Water System ROC General | 2025-10-18
ROC | October | RHPSPA - Power failure alarm. Checked site, generator is not running and ATS is pointing to ton hydro. Likely a power blip. Reset alarm. JFPS - VC UPS ATS source s2 alarm. Alarm returned to normal status upon triggering. Likely a power blip. Reset alarm. MMW1 - Control panel power failure. Checked site, no pumps running. Trending shows that pump 8 and pump 13 were running when the power failure occurred. Re-activated pump 8 and pump 13 in manual mode. | All Water System ROC General | 2025-10-19
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-30
ROC | October | NMTKKC, Deactivated D1 | All Water System ROC General | 2025-10-30
ROC | October | QVETQS - Redempto B. and Parth P. are on site for annual calibrations 11:50 - Outlet Free CL2 Fault critical alarm came in. Redempto and Partha are still on site calibrating the outlet analyzers | All Water System ROC General | 2025-10-30
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-24
ROC | October | Ethan Ullalkar signing out. | All Water System ROC General | 2025-10-24
ROC | October | Ethan Ullalkar signing out. | All Water System ROC General | 2025-10-29
ROC | October | Carter Dunn Signing Out | All Water System ROC General | 2025-10-17
ROC | October | MKMCAP, MKMCCCW, MKMCTA, MKMCCE- PAC Communication Failure Alarm. Kevin W requested to have an operator attend MKMCAP to check if there is power. Notified Dwayne L who requested to call Rob P to attend site. 11:26- Rob P called. There is a planned Alectra outage in the area. Should be back to normal at 15:00 | All Water System ROC General | 2025-10-17
ROC | October | STW12- Placed P1 in man/on as per interim | All Water System ROC General | 2025-10-17
ROC | October | AURSBS - Power blip , sample pumps not running, restarted sample pumps and cleared alarms. | All Water System ROC General | 2025-10-18
ROC | October | SHTP - Power blip, Raw water pumps not available alarms. Alarms cleared | All Water System ROC General | 2025-10-19
ROC | October | MKPSSA- Jack P onsite working on Free Chlorine Analyzer | All Water System ROC General | 2025-10-27
ROC | October | KCETFS - Arthur L finished his work and leaving site. | All Water System ROC General | 2025-10-27
ROC | October | NMETIB - Activated duty 1 to offset fill cycle from NMETHW. | All Water System ROC General | 2025-10-20
ROC | October | HLETYS - Finished flushing procedure. Reverting system changes. | All Water System ROC General | 2025-10-22
ROC | October | AUPSOH- Joe D requested pumps 3/4 be placed in man/off for sampling at NMTKBS. Placed P3/4 in man/off | All Water System ROC General | 2025-10-22
ROC | October | GWTP- Stephen B and contractor will be running LLP3 | All Water System ROC General | 2025-10-22
ROC | October | KSTP- Fin Water Fluoride Res LoLo Alarm. Donald M is onsite. | All Water System ROC General | 2025-10-27
ROC | October | RHMCMD - Closed valve in manual mode. BVPS - Placed pump 2 and pump 4 in auto mode. | All Water System ROC General | 2025-10-19
ROC | October | VNPS PD8 - Placed pumps 2 and 3 man/off to run one pump on duty start. | All Water System ROC General | 2025-10-16
ROC | October | VNPS PD8- Dan B will run Pump 1 in manual mode for test. | All Water System ROC General | 2025-10-16
ROC | October | Angelica Chepiga signing in,weather +11C | All Water System ROC General | 2025-10-17
ROC | October | AUW57-Placed P5 in auto AUW14- Placed 1/2/4 in auto | All Water System ROC General | 2025-10-17
ROC | October | STETBR - Deactivated duty STW12 - Placed STW1 back to auto STPSTL - Placed both pumps man/off and placed the FCV man/open to 70% as per Stephen B. | All Water System ROC General | 2025-10-30
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-17
ROC | October | AUW14- Activated D1 | All Water System ROC General | 2025-10-16
ROC | October | NMETIB - Inlet flow hi alarm. Checked system and noted that the NMVCBA is open more than expected. Trending shows the valve opened beyond its flow setpoint and is now closing to bring flow back to normal range. Will monitor site to ensure it stabilizes. | All Water System ROC General | 2025-10-19
ROC | October | NMETIB - Deactivated duty 1 while NMETHW fills. | All Water System ROC General | 2025-10-19
ROC | October | QVW3 - Activated QVW3 in manual mode to prevent water from travelling north across EGMCRW. | All Water System ROC General | 2025-10-19
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-23
ROC | October | MARS - Cell 1 level hi alarm. Deactivated RHRSTR/BVPS duty 1 to prevent flow pushing from Richmond Hill to Vaughan. Also activated VNRSKS to drawdown MARS level. | All Water System ROC General | 2025-10-23
ROC | October | MKMCAP/MKMCTA/MKMCCE/MKMCCW- PAC comm loss on site. no power outages reported. Notified Kyle C. Will take a look RHMCEM- No flow registering on flowmeter Notified Kyle C. Will take a look NMVCBA- Closed valve placed in auto QVW12- Alex B on site for silicate hot water flush QVW34- Alex B placed chlorinator 2 in man/off KSTP- Donny M on site for turbidity analyzer maintenance. Plant is off | All Water System ROC General | 2025-10-17
ROC | October | MAPS PD8 - Dan B on site to complete a probe replacement on pump 3. Dan stated that this may trigger an alarm. Placed pump 3 manual off for the duration of the work. | All Water System ROC General | 2025-10-20
ROC | October | STPSMR, Jack P on site doing analyzer cleaning/flushing, directed to disregard | All Water System ROC General | 2025-10-29
ROC | October | MKRSEM - Called Toronto Water (Mehdi) and requested they activate two pumps to push flow to MKRSEM. STETBR - Tower low level alarm. Activates STW1 in manual mode as per the interim procedure. | All Water System ROC General | 2025-10-21
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-22
ROC | October | MARS, Notified Toronto operator Paul to increase the flow to the MARS as the ARPS work is still continuing | All Water System ROC General | 2025-10-30
ROC | October | AUW14 - Treated Free Chlorine HiHi alarm came in. Checked site. Wells just started up. Free chlorine levels came down to optimal range within 10 mins. Alarm has been cleared | All Water System ROC General | 2025-10-31
ROC | October | BLW12, Joe M is finished on site, Turbidity on the high side however should drop | All Water System ROC General | 2025-10-29
ROC | October | STETBR- Free Chlorine Lo Alarm. Known issue. Will monitor. Alarm cleared after a few minutes | All Water System ROC General | 2025-10-29
ROC | October | KSTP, Filter 1 Backwash is OOS alarm, Stephen B directed to disregard as Backwash tank is draining and the cause of the alarm. Also noted, if Fluoride lolo comes in, directed to rotate pumps | All Water System ROC General | 2025-10-30
ROC | October | AUW57- Influent free Cl2 lolo alarm came in on well start up. Did not pass contact tank. Influent residual recovered cleared alarms and placed in man/off and notified Joe D. | All Water System ROC General | 2025-10-31
ROC | October | Adam Button signing in 10C clear | All Water System ROC General | 2025-10-24
ROC | October | Adam Button signing in 7C clear | All Water System ROC General | 2025-10-23
ROC | October | NBW2, Cl2 Gas Leak, Notified David T, They are changing Cl2 Cylinders | All Water System ROC General | 2025-10-23
ROC | October | MTETNL- Town of EG flushing NBW3- Influent free lolo switch alarm came in. Trends recovered cleared alarm STETBR- Free Cl2 lo alarm came in. Notified Dan Z | All Water System ROC General | 2025-10-23
ROC | October | NMW15- Influnet free Cl2 lo alarm came in on well start up trends recovered after 3 mins and alarm cleared | All Water System ROC General | 2025-10-24
ROC | October | NMW12- Treated total Cl2/ Combined Cl2 lo alarm came in. Well not active. No water directed to users | All Water System ROC General | 2025-10-24
ROC | October | YWS+NYWS normal | All Water System ROC General | 2025-10-25
ROC | October | Adeela Khan signing in. Weather: 2C and partly cloudy | All Water System ROC General | 2025-10-25
ROC | October | MKRSEM - Called Toronto Water (Mehdi) and requested to stop pumping to reservoir | All Water System ROC General | 2025-10-25
ROC | October | STETBR- Deactivated duty as STETTL duty deactivated. As per SCADA Report. | All Water System ROC General | 2025-10-28
ROC | October | KSTP - Raw water turbidity fault alarm. Checked site, treatment plant is not active. Low lift pumps not active. Trending shows value in normal range and value is changing which indicates the turbidimeter is active. Able to reset alarm. | All Water System ROC General | 2025-10-22
ROC | October | ARPS - Total ammonia fault alarm. Checked site, pumps are off, no flow from ARPS station. Trending shows total ammonia reading is within normal range. Unable to clear alarm. Will monitor. | All Water System ROC General | 2025-10-22
ROC | October | MKRSEM - Called Toronto Water (Mehdi) and requested they stop pumping to MKRSEM. MKRSMR - Also requested that Mehdi revert the duty start setpoint at MKRSMR from 2.5 to 3.0. | All Water System ROC General | 2025-10-22
ROC | October | Adeela Khan signing in. Weather: 11C and sunny | All Water System ROC General | 2025-10-20
ROC | October | MAPS PD7 - Suction Header Valve PIT HiHi level. Checked site. Trends indicated that pit levels have been increasing since the 17th. Called Phil D. who will take a look 19:17 - Phil called back to inform that he will try to troubleshoot on SCADA and if he is unable to, will attend site 20:23 - Phil D called back to inform that he is headed to site. CMU5 Created W11380798 00:35 - Called Phil D. for an update. Phil informed that he attended site but was unable to fix the issue and will bring it up to the west team tomorrow. Phil informed that the alarms can stay outstanding for the night #CONSULT #cmu5 | All Water System ROC General | 2025-10-20
ROC | October | Angelica Chepiga signing out | All Water System ROC General | 2025-10-21
ROC | October | STPSMR, Pat F/Jack P on site, will be running the generator on site | All Water System ROC General | 2025-10-23
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-23
ROC | October | NMVCBA- Placed valve in man/open at 50 L/s | All Water System ROC General | 2025-10-23
ROC | October | Adam Button signing out 1C clear | All Water System ROC General | 2025-10-16
ROC | October | BVPS - Jack in on site , will isolate the suction and discharge valves. | All Water System ROC General | 2025-10-16
ROC | October | MAPS PD7, Placed pump 3 man/off as VNPS PD7 Pump 2 is in D2 and in auto | All Water System ROC General | 2025-10-20
ROC | October | AURSBS and VNRSKS - Activated duty 1 to help lower levels at MARS | All Water System ROC General | 2025-10-21
ROC | October | RHMCMD - man/close to stop flow to VN. | All Water System ROC General | 2025-10-29
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-22
ROC | October | NMW12- Wells interlocked due to lo combined CL2 lo alarm reset alarm. Wells OOS not cleared contact tank. Called Jay G no answer will call back in 10 9:32-NMW12- Jay G called back and will have someone attends site | All Water System ROC General | 2025-10-16
ROC | October | MAPS PD8- Placed P1-3 in manual and P3 in man/off QVW34- Alex B done on site | All Water System ROC General | 2025-10-16
ROC | October | STPSTL/STETTL - Rick L onsite for annual calibrations AUVCBS - PAC communications alarm, able to clear | All Water System ROC General | 2025-10-22
ROC | October | MKRSEM - Request TO (Mehdi) to drop 2 pumps 17250 Yonge and Min center - Received call from Mike Powel from Yorknet regarding scheduled maintenance outage. Brought down SCADA network in front of 17250 Yonge & Min center. Requested confirmation from Network on-call. No outstanding communication or heartbeat alarm currently. Called and informed Evgeni S of situation. Will take a look on SCADA & confirm | All Water System ROC General | 2025-10-24
ROC | October | QVW34 - Placed QVW3 man/on to help encourage flow through EGMCRW towards Newmarket | All Water System ROC General | 2025-10-25
ROC | October | Adeela Khan signing out | All Water System ROC General | 2025-10-25
ROC | October | HLETYS- Pre injection combined Cl2 lo alarm. Disregard on shift report until lolo comes in. Will monitor | All Water System ROC General | 2025-10-26
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-29
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-29
ROC | October | AURSOH, Deactivated D1, Placed AUW134 in man/on | All Water System ROC General | 2025-10-30
ROC | October | RHRSTR, Activated D1 NMTKBS, Deactivated D1 | All Water System ROC General | 2025-10-30
ROC | October | NRETBR - Chris S called to inform the historian heartbeat alarm at NRETBR has been reset. | All Water System ROC General | 2025-10-31
ROC | October | KSTP - Fin water tot CL2 flouride res fault. Disregard as per shift report | All Water System ROC General | 2025-10-24
ROC | October | MKPSSA - Free chlorine residual hi, pumps are off. Trending appears to be slowly rising. Informed team via email SHTP - Filter 2 & 3 turbidity hi, trends show spike in reading before dropping back to normal range | All Water System ROC General | 2025-10-24
ROC | October | RHMCMD - Man/close valve | All Water System ROC General | 2025-10-24
ROC | October | NMVCBA - Placed valve in auto mode. NMETHW - Deactivated duty 1. | All Water System ROC General | 2025-10-31
ROC | October | SHTP- Well 2 Pump Uncommanded Start. Well not running. Wells 3,4 running in duty 1,2. Cleared alarm. | All Water System ROC General | 2025-10-30
ROC | October | GRTPLL - Low Lift Discharge Turbidity Fault Alarm came in. Checked site and the low lift is not running. Called Stephen B. who informed this can be disregarded as this is a monitoring analyzer and does not impact operations KSTP - Due to the outstanding Clearwell Level low, Stephen B. directed to place the Filtration Control Setpoint to Flow mode and place high lift pump 4 in manual. Directed to wait about half an hour before placing the pump back to auto and placing it back to high lift mode 22:20 - Placed pump back to auto. Stephen directed to activate duty 1 and placed filtration system control setpoint back to high lift mode #CONSULT | All Water System ROC General | 2025-10-20
ROC | October | BLW3 - man/off well 3 pump and activate Duty 1, as per Dan Z. | All Water System ROC General | 2025-10-21
ROC | October | MKPSSA- Phil D on site to 0 span the free Cl2 analyzer. Phil D will be placing pumps in man/off for work | All Water System ROC General | 2025-10-31
ROC | October | MKPSSA- Phil D done on site pumps back in auto | All Water System ROC General | 2025-10-31
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-28
ROC | October | YDSS + YNSS Normal Connor Smith signing out. | All Water System ROC General | 2025-10-31
ROC | October | NRETBR- Historian heartbeat alarm outstanding. Notified Chris S. Will take a look | All Water System ROC General | 2025-10-31
ROC | October | STPSMR, Jack P on site working on the Cl2 analyzers | All Water System ROC General | 2025-10-24
ROC | October | NMTKKC - rotated reform hypo pumps from 2 to 1 for Joe D. troubleshooting | All Water System ROC General | 2025-10-24
ROC | October | HLW2 - discharge pressure hihi intermittent. Confirmed contact tank cleared, placed man/off HLW2 FCV - manual, setpoint 30 to 50% | All Water System ROC General | 2025-10-24
ROC | October | Connor Smith signing in 2C Cloudy | All Water System ROC General | 2025-10-27
ROC | October | Connor Smith signing in | All Water System ROC General | 2025-10-28
ROC | October | MTETNL - Outlet free chlorine hi alarm. Checked site, trending shows that the outlet free chlorine reading spiked to the maximum value in one reading. Called Phil D who is on site. Phil is currently draining the system to waste and expected this outlet analyzer malfunction. Phil will ensure the analyzer is operating correctly when his work is finished. | All Water System ROC General | 2025-10-28
ROC | October | STETBR- Free Chlorine Lo Alarm. Will Monitor. | All Water System ROC General | 2025-10-28
ROC | October | QVW12- Treated Free Chlorine HiHi and Combined Chlorine Lo Alarms. Duty deactivated recently, wells not running. Values recovered. Cleared alarms. | All Water System ROC General | 2025-10-17
ROC | October | RHVCEM - Man/open 70% | All Water System ROC General | 2025-10-16
ROC | October | NBW3- Lee F done on site. Cleared alarms placed well back in auto STETTL- Lo free CL2 residual is due to flushing at STW12 by town of Stouffville. The town has stopped flushing and residuals should improve | All Water System ROC General | 2025-10-16
ROC | October | YWS + NYWS NORMAL | All Water System ROC General | 2025-10-18
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-22
ROC | October | QVW12 - Treated free chlorine hihi alarm. Checked site, well recently de-activated no water being directed to users. Trending shows a spike of the treated free chlorine following well shutdown. Known issue, treated free chlorine reading will drop. Will reset alarm when it returns to normal range. | All Water System ROC General | 2025-10-22
ROC | October | RHRSTR - System duty is not active but reservoir inlet flow meter registering flow entering the reservoir from distribution system pressure. This flow amount is not enough to trigger the rechlorination system. Activated the system duty 1 to increase inlet flow and activate the re-chlor system. | All Water System ROC General | 2025-10-22
ROC | October | ANW23- Joe W on site to run generator and clean analyzers | All Water System ROC General | 2025-10-23
ROC | October | Adam Button signing out | All Water System ROC General | 2025-10-26
ROC | October | QVW34- Activated duty 2 to allow flow to move south through EGMCRW. | All Water System ROC General | 2025-10-26
ROC | October | NMETHW- Combined/Total Chlorine Lo Alarm. Duty not active but tower slightly filling. Will monitor. 01:03- Cleared alarms. 01:47- Combined Chlorine Lo Alarm. Will monitor. | All Water System ROC General | 2025-10-30
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-17
ROC | October | QVETQS - Tower level High alarm, duty just deactivated. NMETIB - Activated Duty 1 to offset with NMETHW. NMVCBA - Placed to auto. | All Water System ROC General | 2025-10-17
ROC | October | MKETFA, Historian Heartbeat, Notified Kyle C, he will look into it CMU5: W11380298 | All Water System ROC General | 2025-10-20
ROC | October | NMVCBA - Placed valve in manual, as per interim 13:17 - Placed valve back to auto | All Water System ROC General | 2025-10-25
ROC | October | RHMCMD - Placed valve man/closed | All Water System ROC General | 2025-10-25
ROC | October | ANW23- RSVR inlet free Cl2 lo alarm came in. Residual okay trends show dip in residual but recovered right away cleared alarm | All Water System ROC General | 2025-10-25
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-21
ROC | October | MTETNL, Rick L is on site, doing annual calibration | All Water System ROC General | 2025-10-29
ROC | October | Carter Dunn Signing In, 7D/Clear | All Water System ROC General | 2025-10-21
ROC | October | KSTP- Stephen B called and requested to place high lift pumps 2,4 in man/off and high lift pump 3 man/on GWTP- Stephen B will lock out plant for intake inspections | All Water System ROC General | 2025-10-27
ROC | October | ARPS, Yash called to inform the ROC that they are ready to do the network testing, directed ROC to contact ARPS to get them to turn off their pumps. Notified ARPS operator David to turn off their pumps. Once pumps are turned off fully, will contact Yash so he can do his work at MARS 09:59, ARPS Pumps are all manual/off, notified Yash S to start his work 11:03, Yash S called saying they are done the network upgrades. Will contact ARPS and inform them that work is now finished. Contacted David from ARPS, David said he could see MARS, directed David to place his pumps back to auto as the work is now complete 11:13, Contacted Yash S to confirm David from ARPS can MARS. Yash informed ROC that there is an error and that isn't possible at this time. Reconnected with David from ARPS and asked if he sees trends, David from ARPS cannot see trends, directed David to place pumps man/off till the issue is resolved. Notified Yash S that he was correct, he is working on the issue | All Water System ROC General | 2025-10-30
ROC | October | QVW12- Placed W2 in man/off as QVETQS is high | All Water System ROC General | 2025-10-24
ROC | October | KSTKWP - deactivated duty 1 as per Stephen B. Stephen B taking GWTP offline for the intake structure inspection. | All Water System ROC General | 2025-10-28
ROC | October | AUW14 - Placed well 3 man/off as its been running all day. Placed well back to auto | All Water System ROC General | 2025-10-31
ROC | October | AUW57, Influent Free Cl2 lolo, contact tank was filled alittle but not much, Well ran for 25 minutes then influent dipped, placed well man/off for the time being, will send email to operator. Well most likely can be ran again if needed. | All Water System ROC General | 2025-10-29
ROC | October | RHVCEM - Man/open to 40% VNRSKS - Changed High level setpoint from 92% to 83% , before duty deactivated as reminder to close RHVCEM to 15%. | All Water System ROC General | 2025-10-16
ROC | October | NMETIB - Deactivated duty as per interim | All Water System ROC General | 2025-10-18
ROC | October | AUPSOH, Placed pumps 3/4 back to auto as per Joe D | All Water System ROC General | 2025-10-29
ROC | October | NBW5 - Turbidity Hi alarm, value not dropping, switched silicate pumps. Silicate pump 1 on duty 1, will monitor. 04:09 Turbidity Hi alarm cleared. | All Water System ROC General | 2025-10-18
ROC | October | Adeela Khan signing out | All Water System ROC General | 2025-10-18
ROC | October | YWS + NYWS NORMAL Angelica Chepiga signing out | All Water System ROC General | 2025-10-19
ROC | October | NMETHW, Joe D is finished on site, Placed QVW12/34 back to auto | All Water System ROC General | 2025-10-29
ROC | October | STETBR - Tower Level Lo alarm came in. Man/started STW12, as per interim | All Water System ROC General | 2025-10-18
ROC | October | ANW23 - RSVR Inlet Free Chlorine LoLo alarms came in. Checked site. Wells 2/3 are interlocked. Alarms have cleared but inlet free chlorine is still LoLo. Called Jacob M. who will log on and take a look #CONSULT | All Water System ROC General | 2025-10-18
ROC | October | VNRSKS - Activated D1. | All Water System ROC General | 2025-10-19
ROC | October | MKRSMR - Called Toronto Water (Peter) and requested they revert the duty start/stop setpoints from 3.5/5.4 to 3.0/5.0. | All Water System ROC General | 2025-10-19
ROC | October | GWTP - ZW3 not all devices in auto mode. Spoke with Phil D who stated that he caused this alarm to prevent an MIT clean while the intake inspection continues. Stephen B still on site. | All Water System ROC General | 2025-10-27
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-27
ROC | October | KSETWB - Chlorine booster pump 1 and 2 fault alarm, tower inlet valve fault and chlorine pump valve fail to open alarms. Inlet valve showing in local and flashing the auto signal, but still open and allowing flow into the tower. The chlorine booster pumps are off and the vavles closed. Able to reset the valve fail to open alarms but the chlorine booster pump faults will not reset. Called Phil D who will check SCADA as soon as possible. #consult | All Water System ROC General | 2025-10-27
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-22
ROC | October | NMTKKC - Joe D. working on chlorine analyzers, adjusted D1 stop from 75 to 80% to keep wells running during work | All Water System ROC General | 2025-10-24
ROC | October | AUPSRR- Post Inj. Free Cl HiHi Alarm. Value recovered. Cleared alarm. | All Water System ROC General | 2025-10-17
ROC | October | JFPS- Benson S on site to run generator and test hi lo temp alarm. Will be stopping pumps on site and restarting them | All Water System ROC General | 2025-10-16
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-28
ROC | October | NMTKBS - Joe D heading to site AUPSOH - Place pump 3 & 4 into manual/off while staggering pumps from stopping as requested by Joe D | All Water System ROC General | 2025-10-29
ROC | October | MMW1 - Rick L , Parth P and Red B on site for annual calibration. | All Water System ROC General | 2025-10-21
ROC | October | VNMVYS- Harsh P onsite. Disregard fault temp and flood alarms. | All Water System ROC General | 2025-10-27
ROC | October | ARPS, Binish from ARPS called, they are changing the ammonia reagents in they analyzers | All Water System ROC General | 2025-10-20
ROC | October | GWTP- Truck Bay Gas Leak Alarm. Called Stephen B. No answer. 11:30- Stephen B called back. He cleared alarm. | All Water System ROC General | 2025-10-27
ROC | October | BLW3- Joe M. called and requested to give David D a call for electrical assistance. Notified David. W11384576 CMU5 for David D | All Water System ROC General | 2025-10-21
ROC | October | VNPS - Mike O on site with Vaughan fire for training. 08:20 - VNPS - Mike O called to inform that the training requires certain hatches to be opened which may result in low temperature alarms. Mike can be called if these alarms come in. | All Water System ROC General | 2025-10-27
ROC | October | ARPS, Contacted ARPS operator Jerry and asked him to revert the duty changes back to normal operation. D3 Start: 68% D3 Stop: 76% D2 Start: 72% D2 Stop: 79% | All Water System ROC General | 2025-10-24
ROC | October | NMVCBA- Changed flow setpoint from 80L/s to 70L/s NMVCIB- Changed flow setpoint from 40L/s to 50L/s QVW12- Placed P2 back in auto | All Water System ROC General | 2025-10-24
ROC | October | VNPS- Cole W finished with chlorine system work. BVPS- Cole W requested to activated duty RHMCMD- Placed valve into auto. | All Water System ROC General | 2025-10-28
ROC | October | GWTP - ZW6 not all devices in auto mode alarm. Stephen B called and directed to disregard this alarm. | All Water System ROC General | 2025-10-28
ROC | October | NBW5 - Redempto B on site for annual calibrations. Red requested that the well be placed manual/off for the duration of the work. Made the necessary change. | All Water System ROC General | 2025-10-27
ROC | October | GWTP - Stephen B cleaning Permeate header chlorine and turbidity analyzers, disregard UVT alarms. | All Water System ROC General | 2025-10-21
ROC | October | Ethan Ullalkar signing in | All Water System ROC General | 2025-10-22
ROC | October | HLETYS- Pre injection combined Cl2 lo. Tower filling intermittently with lo demand. Will continue to monitor and clear alarm when demand picks up. | All Water System ROC General | 2025-10-25
ROC | October | YWS+NYWS normal | All Water System ROC General | 2025-10-25
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-25
ROC | October | KLPSWL- Discharge pressure lo alarm came as ARPS D2 deactivated reset alarm as trends recovered immediately | All Water System ROC General | 2025-10-25
ROC | October | YWS+NYWS normal | All Water System ROC General | 2025-10-25
ROC | October | STETBR - Stephen B called and directed to close the VC-FVC valve when STETBR hits 45%. When this occurs, or if STETTL hits duty 1 start, Stephen has directed to activate both systems at the same time to synchronize the fill cycles. | All Water System ROC General | 2025-10-31
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-20
ROC | October | TMC307 - Flow meter fault alarm. Alarm has been triggering constantly throughout the shift. Called Toronto Water who stated they are unaware of any issues but will schedule a follow up tomorrow during regular hours. | All Water System ROC General | 2025-10-22
ROC | October | KLMCHR- Gary P and Harsh P on site to test flood alarm intrusion alarm | All Water System ROC General | 2025-10-23
ROC | October | STW3, Phil D//Jack P working on the Cl2 system/CL2 lines, directed to disregard alarms from site | All Water System ROC General | 2025-10-30
ROC | October | HLW1 - Jordan B. called back to inform that he is finished on site and that the CT not achieved can be disregarded as the well is local/off | All Water System ROC General | 2025-10-30
ROC | October | Carter D signing in.3D/Clear | All Water System ROC General | 2025-10-24
ROC | October | NMETIB- Activated duty. | All Water System ROC General | 2025-10-28
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-18
ROC | October | YWS + NYWS NORMAL | All Water System ROC General | 2025-10-19
ROC | October | AURSBS - Activated D1 , MARS level High. | All Water System ROC General | 2025-10-19
ROC | October | STETTL, Travis W on site, working on the Cl2 analyzers and testing health and safety alarms, directed to disregard | All Water System ROC General | 2025-10-29
ROC | October | KSTP - Filter 1 Backwash is OOS. Spoke to Stephen B who informed that filter 2 is currently undergoing backwash and alarm should clear after backwash is finished | All Water System ROC General | 2025-10-30
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-30
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-31
ROC | October | BLW3- Antonio from Torbear (416-586-6617)called about a booster pump 2 leak on the process water connection. Notified Joe M will be on site soon to take a look KLMCHR- Chris s on site to change over to cell comms. Will lose comms while work is done | All Water System ROC General | 2025-10-31
ROC | October | QVW12 - Reset alarms associated with the earlier chlorine cylinder change. Monitored well activation. NMETIB - Deactivated duty 1 while NMETHW fills. | All Water System ROC General | 2025-10-28
ROC | October | Gluzen Ramos Ong signing in | All Water System ROC General | 2025-10-16
ROC | October | RHPSWA- Placed P1 in man/off | All Water System ROC General | 2025-10-16
ROC | October | HLW2- changed FCV flow set point to 30L/s | All Water System ROC General | 2025-10-16
ROC | October | NMETIB- Activated D1 to offset from NMETHW as per interim | All Water System ROC General | 2025-10-22
ROC | October | Christian Van Beek signing in. Weather: 13C and rain. | All Water System ROC General | 2025-10-22
ROC | October | YWS + NYWS NORMAL | All Water System ROC General | 2025-10-26
ROC | October | SHTP - Filter 3 Turbidity High alarm, Filter 1 finishing backwash. Cleared alarm as per SCADA review. | All Water System ROC General | 2025-10-26
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-27
ROC | October | HLW2, Combined Cl2 lolo, Well currently off, abnormal drop occurred, residuals came back to normal levels after 2 readings | All Water System ROC General | 2025-10-24
ROC | October | STETBR- Deactivated duty as STETTL duty deactivated. As per SCADA Report. | All Water System ROC General | 2025-10-29
ROC | October | AURSBS- activated D1 to maintain MARS level. | All Water System ROC General | 2025-10-29
ROC | October | HLETYS- Adjusted D1 start from 30% to 26 % | All Water System ROC General | 2025-10-23
ROC | October | MARS/ARPS - Yash S. called to inform that everything has been fixed and to call Peel Water to place their pumps back to auto. Called Peel Water (David) and requested pumps back to auto. 12:40 - Yash called back informing they have encountered an issue and will need the peel pumps back to man/off. Called Peel Water (David) and requested pumps back to man/off | All Water System ROC General | 2025-10-30
ROC | October | AUMCBS - Parth P & Red B onsite Annual calibrations | All Water System ROC General | 2025-10-29
ROC | October | STW3, Effluent Free Cl2 lolo Switch Alarm, Travis W working on the Cl2 analyzers, currently having issues with the effluent analyzer, requested Instrumentation on call, gave him Eric S work number so he can be in contact with him | All Water System ROC General | 2025-10-29
ROC | October | RHMCMD - MARS level has dropped. Closed valve and placed in auto mode. | All Water System ROC General | 2025-10-23
ROC | October | KLMCIA- Rob P on site to test flood ,intrusion and hi lo temp alarms NMETIB- Divya P on site to test flood alarm and perform JHS inspections AUMCBR- Harsh P on site to test flood ,intrusion and hi lo temp alarms | All Water System ROC General | 2025-10-23
ROC | October | STETTL - Outlet Free Chlorine Lo alarm came in. Checked site. Tower is filling. Called Phil D. who directed to activate STETBR duty. #CONSULT | All Water System ROC General | 2025-10-26
ROC | October | Carter Dunn Signing Out | All Water System ROC General | 2025-10-29
ROC | October | YWS + NYWS Normal MARS - Hi level, requested TO (Peter) to drop to min flow VNRSKS - Activate duty 1 | All Water System ROC General | 2025-10-24
ROC | October | NMVCDD, Ben H on site doing some flushing, directed to disregard alarms from site | All Water System ROC General | 2025-10-30
ROC | October | EGMCRW, Pressure lolo alarm, contacted Gary P, he is on site, main is isolated, directed to disregard at this time | All Water System ROC General | 2025-10-30
ROC | October | AURSBS - Activated duty 1 to help lower levels at MARS | All Water System ROC General | 2025-10-20
ROC | October | NMVCBA- Placed valve in man/open at 60L/s | All Water System ROC General | 2025-10-22
ROC | October | QVW34 - Eric S finished at site, leaving well 3 off for the night for further testing in the morning | All Water System ROC General | 2025-10-22
ROC | October | YWS+NYWS normal | All Water System ROC General | 2025-10-25
ROC | October | Adam Button signing out | All Water System ROC General | 2025-10-25
ROC | October | STETBR - Free Chlorine Lo alarm came in. Checked site. Trends indicate a dip in free chlorine levels. After 4 mins, free chlorine levels went back to optimal range and alarm has cleared | All Water System ROC General | 2025-10-25
ROC | October | Gluzen Ramos Ong signing in at 09:30 MKPSSA - activated Duty 1, Dwayne L. informed contractors on site monitoring flow. Stephen B. | All Water System ROC General | 2025-10-30
ROC | October | STRS48 - Artour L. called to inform that he is on site with Drew from Ferguson Electric for diesel tank LIT Commissioning | All Water System ROC General | 2025-10-30
ROC | October | ARPS, Talked with Yash S, he has informed the ROC that his work is now done. Contacted David from ARPS to confirm that they have trends on their end. David confirmed they do, directed David to place his pumps back to normal operation (auto). | All Water System ROC General | 2025-10-30
ROC | October | STPSTL- Phil D requested to place FCV1 valve to 0L/s | All Water System ROC General | 2025-10-27
ROC | October | STPSTL- Phil D requested to adjust FCV1 valve to 0L/s | All Water System ROC General | 2025-10-27
ROC | October | RHMCMD - Closed valve in manual mode. | All Water System ROC General | 2025-10-23
ROC | October | SHTP- KMNO containment flood alarm. Benson S on site cleaning containment area will call when done STW12- Placed P2 in manual for STETBR fill cycle as per interim | All Water System ROC General | 2025-10-23
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-21
ROC | October | Adeela Khan signing in. Weather: 4C and clear | All Water System ROC General | 2025-10-30
ROC | October | MARS, Contacted Toronto operator Paul to increase the flow to the res. Keep the res topped up for the interim that is taking place today | All Water System ROC General | 2025-10-30
ROC | October | SHTP - Well pump 2 uncommanded stop alarm. Checked site, well duty rotated to another pump which activated. Reset alarm. KLMCHR - Chris S finished work and leaving site. | All Water System ROC General | 2025-10-31
ROC | October | KSETDP - Inlet chlorine HiHi spike disregard as per SCADA review. Cleared alarm. | All Water System ROC General | 2025-10-28
ROC | October | QVW34- Eric S on site to test flowmeter replacement AUVCBS-PAC comm fail alarm came in. Comms restored after 5 mins cleared alarm KSETDP- Inlet total Cl2 hihi alarm came in on D1 start. Reset after trends recovered | All Water System ROC General | 2025-10-23
ROC | October | Carter Dunn Signing Out | All Water System ROC General | 2025-10-23
ROC | October | HLW2- Placed Sharon valve back in auto | All Water System ROC General | 2025-10-16
ROC | October | NMVCBA- Placed valve in manual at 50 L/s HLW2- Discharge pressure lo alarm came in. Trends look like its been fluctuating all night NMW12- Treated total and combined CL2 lo alarm came in. Wells not active no water directed to users | All Water System ROC General | 2025-10-17
ROC | October | AUW14- Treated free Cl2 hi alarm came in. Ammonia system not adjusting to increased flow from wells. Placed Well 3 in man off to help trend recover | All Water System ROC General | 2025-10-17
ROC | October | YWS + NYWS NORMAL | All Water System ROC General | 2025-10-18
ROC | October | NMTKKC- JOe D req D1 stop changed from 75% to 85% while he's working on flushing analyzer. Joe D placed all chem pumps in man/off for duration of work | All Water System ROC General | 2025-10-16
ROC | October | MAPS/JFRS- Initiated Maple to Jefferson Feed. | All Water System ROC General | 2025-10-17
ROC | October | AUW57- Combined Cl2 lo alarm came in recovered after 6 mins alarm cleared | All Water System ROC General | 2025-10-22
ROC | October | KSTP - Setl turbidity Hi and HiHi alarm. Value is not Hi, ack/reset. Will monitor. 22:40 Setl turbidity Hi and HiHi alarms in and out. Stephen B requested disregard until tomorrow. | All Water System ROC General | 2025-10-18
ROC | October | STW12 - Placed W2 back in auto, STETBR duty 1 to deactivate NBW5 - Redempto B., and Parth P. doing annual calibrations. Placed W5 man off | All Water System ROC General | 2025-10-24
ROC | October | KSETDP - Patrick F performing w/o including LIT , temp and flood alarms test, cleaning chlorine analyzers and testing chlorine gas leak alarm. | All Water System ROC General | 2025-10-16
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-16
ROC | October | NRETCR, Activated D1 | All Water System ROC General | 2025-10-16
ROC | October | NMETIB, Activated D1 | All Water System ROC General | 2025-10-16
ROC | October | STETBR - Wes from Town of Stouffville flushing in Zone One for 20 minutes. | All Water System ROC General | 2025-10-16
ROC | October | BLW3- Mike from Balantrae Fire Department called to infrom ROC Fire testing on site until 10:00. Notified Dan Z placed well 3 in man/off | All Water System ROC General | 2025-10-16
ROC | October | QVW34 - Treated total chlorine Low alarm, Adjusted Chlorinator 1 dosing factor to 68%, will monitor. | All Water System ROC General | 2025-10-18
ROC | October | Adam Button signing out | All Water System ROC General | 2025-10-23
ROC | October | RHVCEM, Reverse Flow Lo alarm, placed valve set point from 80 to 15 to 0% as flow continued to leave RHRSWA and move to VNRSKS | All Water System ROC General | 2025-10-16
ROC | October | MTW12, Station Turbidity Fault, notified Stephen B, he will look into it shortly CMU5: W11384551 | All Water System ROC General | 2025-10-21
ROC | October | Adam Button signing out | All Water System ROC General | 2025-10-22
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-20
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-20
ROC | October | VNPS PD8 - Reassigned Duties- Pump 1/running in man. to Duty 1, P3 - Duty2, P4- Duty 3, Pump 2 Duty 4. | All Water System ROC General | 2025-10-16
ROC | October | YWS + NYWS Normal Christian Van Beek signing out. | All Water System ROC General | 2025-10-19
ROC | October | LSSS- Amelia from Sewer Use Bylaw requested pump 3 in duty 1 for sampling. *Wrong Book | All Water System ROC General | 2025-10-17
ROC | October | RHMCMD - man/open 300mm bypass to 100% as per Dwayne L. | All Water System ROC General | 2025-10-16
ROC | October | KSETDP - Inlet total CL2 hihi, no signs of reading dropping, rotated to chlorinator 1. Will monitor KSTP - Flouride res lolo. Reading came back up to normal range | All Water System ROC General | 2025-10-29
ROC | October | AUPSRR- Noticed that metro valve was in duty 1 and auto but not open with AURSOH Duty active. Tried reapplying it to duty 1. Would not work. Notified Chris S. He will take a look. 19:50- Chris S called back. Believes could be an electrical issue. Notified Joe D. Reservoir is still filling without valve open. Requested to change minimum Discharge Flow Rate from 20L/s to 15L/s so that chemical system not starting and stopping. Ops will attend site in the morning. 20:04- Chris S suggested to place Metro valve in manual 0L/s. 20:11- Joe D. Placed Minimum Discharge Flow Rate back to 20L/s. Placed Well 3 into duty 1 to help with flow to AUPRRR. W11403709 CMU5 | All Water System ROC General | 2025-10-29
ROC | October | HLW2 - Combined Chlorine LoLo alarm came in and interlocked the well. The tower is not filling, and the well is not running. Checked trends. Noticed this dip has not happened this week. Combined chlorine went down to 0.19 mg/L. Well is about 10% away from activating. Called Jacob M. who informed this may just be a dip. Levels came back to optimal range and alarm cleared within 10 mins #CONSULT | All Water System ROC General | 2025-10-18
ROC | October | VNPS PD8 - no duty 1 pump available, assigned P4 to Duty 1. | All Water System ROC General | 2025-10-16
ROC | October | KSTP- Divya P on site to work on filter turbidity analyzers as well as Cl2 PACL and fluoride system inspections. | All Water System ROC General | 2025-10-16
ROC | October | NMMCHT - Rick L and Parth P on site for a flowmeter calibration. | All Water System ROC General | 2025-10-20
ROC | October | MKRSEM- Called Toronto water( Zoran) and requested to start filling the res. | All Water System ROC General | 2025-10-17
ROC | October | STRS48- Travis W done on site | All Water System ROC General | 2025-10-22
ROC | October | NMETHW - Deactivated duty 1 while NMETIB fills. | All Water System ROC General | 2025-10-20
ROC | October | MKRSMR - Andrew from TO placing pumps in man/off as they exercise young/Kennedy valve In preparation for trial isolation | All Water System ROC General | 2025-10-22
ROC | October | MKRSEM- Called Toronto (Mehdi) and requested pumps off. | All Water System ROC General | 2025-10-31
ROC | October | Christian Van Beek signing in. Weather: 11C and rain. | All Water System ROC General | 2025-10-20
ROC | October | VNPS PD8- Placed P1 in man/off | All Water System ROC General | 2025-10-16
ROC | October | KSTP- Fin Water Tot CL2 Res Fault, Fin Water Fluoride Res Fault Alarm. Disregard as per SCADA Report. | All Water System ROC General | 2025-10-27
ROC | October | HLETYS- Eric S onsite working on hypo tank level transmitter. 14:55- finished on site. | All Water System ROC General | 2025-10-28
ROC | October | AUW14 - Chlorine gas level Hi alarm, Jason G called, small chlorine leak . Disregard alarm, Joe D , Donald M and Jason G on site working on it. | All Water System ROC General | 2025-10-16
ROC | October | NMVCBA- Rob P on site testing flood alarm, hi lo temp and intrusion alarm KLW34- Dave T and Jordan B on site to run generator and test Cl2 leak alarm | All Water System ROC General | 2025-10-23
ROC | October | MKRSEM- Called Metro spoke with Zorhan to start two pumps. | All Water System ROC General | 2025-10-31
ROC | October | NMVCBA- Placed in manual 60L/s | All Water System ROC General | 2025-10-17
ROC | October | GWTP - Train 3 MIT Fail and Shutdown alarms came in again. Called Phil D. who directed to leave train off for the weekend #CONSULT | All Water System ROC General | 2025-10-25
ROC | October | SHTP- Well 2 pump uncomm stop alarm came in. Reset as P3/4 running in D1/2 QVW12- Placed well 2 in auto YWS+NYWS normal | All Water System ROC General | 2025-10-25
ROC | October | MARS / TMC317 - Peter from Toronto Water called to inform they are completing a pump change and there will be a temporary reduction of flow to MARS through TMC317. | All Water System ROC General | 2025-10-27
ROC | October | Angelica Chepiga signing out | All Water System ROC General | 2025-10-29
ROC | October | SHTP - Filter 3 Turbidity Hi alarm came in. Reset as per shift report | All Water System ROC General | 2025-10-20
ROC | October | SHTP, Filter 3 Turbidity Hi Alarm, Filter 2 backwashing, directed to disregard for first time coming in as per shift report | All Water System ROC General | 2025-10-24
ROC | October | QWV34 - Dan B. and Satnam M. working on W3 VFD. Wells already man/off via ops, they will run in manual | All Water System ROC General | 2025-10-24
ROC | October | HLETYS - Outlet flow hihi, inquired with Jordan B. if EG flushing. Similar outlet flows earlier this morning. He informed they're flushing but will look into the flows. Duty currently not active, still 40% away from D1 start. Monitoring. 13:08 - called Blair S., Town of EG. He is not aware of flushing but will confirm and call back. Cole W. aware. 13:11 - Blair S. informed contractor Trisan working along Yonge, hit water main. They will isolate. Notified Cole W. | All Water System ROC General | 2025-10-24
ROC | October | RHMCMD - Placed back to auto. | All Water System ROC General | 2025-10-24
ROC | October | GWTP- Stephen B requested to place UV's and High LIft pumps in manual. | All Water System ROC General | 2025-10-28
ROC | October | Reverting system changes: RHVCEM - to man/open 15% RHMCMD - MV1 back to auto, MV2 man/close RHRSPA- D1 65%-85%, D2 42%-75%, D3 40%-60% | All Water System ROC General | 2025-10-19
ROC | October | YWS + NYWS Normal MKRSEM - Reservoir 1 Level Lo alarm came in. Called Toronto Water (Paul) and requested two pumps on to help fill reservoir 05:41 - Called Toronto Water (Peter) and requested to stop pumping to reservoir | All Water System ROC General | 2025-10-26
ROC | October | HLVCMA - PAC Communication Failure Alarm came in. Checked site. Trending has stopped since 01:55. Called Ian W. but no answer 02:37 - Called multiple times again, but no answer. Left a message | All Water System ROC General | 2025-10-27
ROC | October | RHMCMD - Placed valve man/closed | All Water System ROC General | 2025-10-27
ROC | October | VNPSCD, Jake M on site cleaning the Cl17 analyzers on site | All Water System ROC General | 2025-10-23
ROC | October | YWS+NYWS normal | All Water System ROC General | 2025-10-23
ROC | October | YDSS+YNSS normal | All Water System ROC General | 2025-10-23
ROC | October | BVPS - Deactivated D1 for Cole W, chlorinator work at VNPS | All Water System ROC General | 2025-10-28
ROC | October | NMW12- Silicate Tank 1 Level OOR Alarm. Interlocked both silicate pumps. Notified Ryan B. He is placed wells man/off. 10:21- Ryan B called . Wells are back running. Will likely receive hi turbidity alarm and requested to increase turbidity hihi alarm to prevent wells from interlocking. | All Water System ROC General | 2025-10-27
ROC | October | NMTKKC - Joe D called and directed to increase the duty 1 stop setpoint from 75% to 80%. Joe is completing a hot flush and will trigger the chemscan offline alarm. | All Water System ROC General | 2025-10-28
ROC | October | STETBR - Hit level 45%. Closed the VCFVC as directed by Stephen B and activated duty 1 for STETBR and STETTL. | All Water System ROC General | 2025-10-31
ROC | October | AURSBS - Joe D called and requested a CMU5 for his response to the chlorine leak alarm at AURSBS. Joe requested that Jerry Z also be added to the CMU5. created CMU5#W11407626 AURSBS - Joe D called Parth P for assistance with the chlorine leak detection system. Created a CMU5 for Parth CMU5#W11407634 #CMU5 | All Water System ROC General | 2025-10-31
ROC | October | AUW14- Jason G and Jerry Z onsite working on ammonia pump 2. Disregard related alarms. | All Water System ROC General | 2025-10-28
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-21
ROC | October | MTW12/MTW3 - Place wells in man/on position for Rick L to perform annual calibrations | All Water System ROC General | 2025-10-29
ROC | October | RHMCMD, Placed valve man/closed | All Water System ROC General | 2025-10-29
ROC | October | YWS + NWYS Normal | All Water System ROC General | 2025-10-24
ROC | October | NMTKKC - Activated duty 1. | All Water System ROC General | 2025-10-23
ROC | October | GWTP, Stephen B on site doing a backwash on GAC 2 | All Water System ROC General | 2025-10-23
ROC | October | Carter Dunn Signing Out | All Water System ROC General | 2025-10-24
ROC | October | QVW34 - Placed QVW3 back to auto, as QVETQS Levels are getting high | All Water System ROC General | 2025-10-25
ROC | October | AURSBS- Activated D1 | All Water System ROC General | 2025-10-26
ROC | October | NMTKKC - Joe D called and directed to increase the duty 1 stop setpoint from 75% to 80%. | All Water System ROC General | 2025-10-27
ROC | October | BLW12 - Joe M heading to site . Will be deactivating wells. Disregard well 1 & 2 alarms as working on contact tank | All Water System ROC General | 2025-10-29
ROC | October | QVW34, Placed well 4 man/on to help flow go into the tower and help freshen up the line, Joe D made the recommendation | All Water System ROC General | 2025-10-29
ROC | October | Connor Smith signing in 11C Cloudy | All Water System ROC General | 2025-10-29
ROC | October | Connor Smith signing out | All Water System ROC General | 2025-10-30
ROC | October | QVW12- Treated Free Chlorine HiHi and Combined Chlorine Lo Alarms. Duty deactivated recently, wells not running. Values recovered. Cleared alarms. | All Water System ROC General | 2025-10-21
ROC | October | STW12 - Travis W cleaning chlorine analyzers and turbidity meter, flushing silicate system, chlorine system maintenance. | All Water System ROC General | 2025-10-21
ROC | October | Christian Van Beek signing in. Weather: 13C and sun | All Water System ROC General | 2025-10-21
ROC | October | MTW123- Stephen B finished onsite. Requested to clear outstanding turbidity alarm. Well back into duty 1. | All Water System ROC General | 2025-10-21
ROC | October | YWS + NYWS normal | All Water System ROC General | 2025-10-25
ROC | October | Adeela Khan signing in. Weather: 7C and sunny | All Water System ROC General | 2025-10-27
ROC | October | YWS + NYWS NORMAL | All Water System ROC General | 2025-10-28
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-25
ROC | October | QVW12 + QVW34 - Ben H. informed activating Duty 2 and will confirm maintenance work (Tyler Z.) on well run requirements | All Water System ROC General | 2025-10-30
ROC | October | RHPSPA - Discharge header flow 1 lolo alarm. Checked site, system duty just deactivated. Able to clear alarm. | All Water System ROC General | 2025-10-31
ROC | October | SHTP - UV transmittance low alarm and filter 3 turbidity hi alarm. Called Benson S who will be on site today and will check these alarms. | All Water System ROC General | 2025-10-31
ROC | October | AURSRR - Will M on site for a chlorine leak test. | All Water System ROC General | 2025-10-31
ROC | October | Adam Button signing in 6C Clear | All Water System ROC General | 2025-10-22
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-31
ROC | October | KSTP- Backwash Pump 1 Uncomm Stop Alarm. Pump is in duty 3, Pump 2 is in duty 1. Will email Stephen B. | All Water System ROC General | 2025-10-31
ROC | October | YWS + NYWS Normal Connor Smith signing out | All Water System ROC General | 2025-10-21
ROC | October | GWTP - Disabled low lift chlorination for mussel control and activated system duty 1 as directed by Stephen B last night. | All Water System ROC General | 2025-10-22
ROC | October | NBW3 - Influent Free Chlorine LoLo and LoLo switch alarm came in. Checked site. Noticed that the well activated in schedule mode and then the well interlocked on the LoLo alarm. Called Jacob M. who will take a look 08:50 - Jacob called back to inform he is headed to site. CMU5 Created W11393545 #CONSULT #CMU5 | All Water System ROC General | 2025-10-25
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-25
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-25
ROC | October | AUPSWS-P4 unccomanded stop alarm came in. Able to reset alarm STW12/STPSTL- Generator running alarm came in for both sites. Notified Travis W. Will head to STW12 and check outstanding P1 fault | All Water System ROC General | 2025-10-31
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-22
ROC | October | NMTKKC - Eric S on site for inlet total chlorine analyzer maintenance. | All Water System ROC General | 2025-10-27
ROC | October | QVW34, Tyler Z on site working on well 3 | All Water System ROC General | 2025-10-20
ROC | October | HLW2 - Chlorine room hi/low temperature alarm. Called Jake M who directed to disregard as he turned on the heater today. #consult | All Water System ROC General | 2025-10-28
ROC | October | Gluzen Ramos Ong signing out | All Water System ROC General | 2025-10-24
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-30
ROC | October | NMW12- Danny M on site for Cl2 leak detection test , will be cleaning Cl2 analyzers and turbidity meters as well as JHS inspection s | All Water System ROC General | 2025-10-23
ROC | October | AUPSRR - Post injection combined chlorine lolo and free chlorine hihi. Checked site, trending shows a sudden dip of the combined chlorine and a sudden spike of the free chlorine readings which returned to normal range within one reading interval. Reset alarms. | All Water System ROC General | 2025-10-31
ROC | October | NRETBR- Isolation valve position alarm OOR/ fault alarm came outstanding Notified Will M. Will let Jerry Z know about issue Adam Button signing out | All Water System ROC General | 2025-10-31
ROC | October | NBW3 - Eric S onsite for silicate pump 2. Leak detector replacement and pump head | All Water System ROC General | 2025-10-29
ROC | October | NMVCBA - Back to auto. | All Water System ROC General | 2025-10-26
ROC | October | STW3 - Effluent free chlorine lolo. Site of OOS | All Water System ROC General | 2025-10-28
ROC | October | SHTP - Filter 3 Turbidity Hi alarm, Filter I just completing backwash. Disregard as per SCADA review. UV transmittance low alarm, checked site, normal. Alarm cleared. Only one filter in production. Jacob M will check SCADA. # Consult 23:39 Jacob M called back. He will notify area tomorrow morning about pressure dropping issue/causing turbidity spikes. Requested to clear alarms for the night and send email. | All Water System ROC General | 2025-10-28
ROC | October | AUETAD - Water system fire storage vol low. Noticed duty 1 was dropped to 40% from day operator and change was not reverted. Increase duty 1 start back to 45% | All Water System ROC General | 2025-10-22
ROC | October | MKRSEM - Called Toronto Water (Peter) and requested they deactivate the pumps pushing flow to MKRSEM. | All Water System ROC General | 2025-10-23
ROC | October | SHTP- Filter 2, 3 Turbidity Hi Alarm. Cleared alarm as per SCADA Report UV Transmittance Lo Alarm- Called Jacob M. He will look into it. CONSULT | All Water System ROC General | 2025-10-27
ROC | October | KSETWB - Site Hydro Power Failure came in, along with multiple other alarms came in. Checked site. Tower is now draining. Checked Hydro One's outage map which indicates that there is an outage in the area. Outage Restoration time is approximately 19:45. 19:38 - Tower Isolation Valve Position Signal Error and Tower Inlet Valve Position Signal error alarms are unable to reset. Called Phil D. who informed he will check SCADA but if restoration time exceeds 20:00, to give him a call back as he will have to attend site 20:00 - Restoration time changed to 22:00. Called Phil D. who is headed to site. 20:10 - Site came back and alarms have cleared. Phil will no longer attend site #CONSULT | All Water System ROC General | 2025-10-27
ROC | October | AUW14- Placed P1/3 in man/on AUW57- Placed P5 in man/on | All Water System ROC General | 2025-10-26
ROC | October | YWS+NYWS normal | All Water System ROC General | 2025-10-26
ROC | October | KSTP- Settl water turbidity hihi alarm came in. Checked trends recovered before the alarm came in. Emailed East water team about outstanding alarms | All Water System ROC General | 2025-10-26
ROC | October | MKRSEM - Requested Toronto water(Zoran) start filling res. MARS - Requested Toronto water(Zoran) reduce flow to normal. | All Water System ROC General | 2025-10-29
ROC | October | AUETAD, Eric S on site, working on the Cl2 analyzers, doing calibrations 12:36, Eric S finished on site | All Water System ROC General | 2025-10-29
ROC | October | Christian Van Beek signing out. | All Water System ROC General | 2025-10-23
ROC | October | NRETCR- Ben H on site closing tower inlet while D1 active. Directed to call if pressure issues arise in area STPSMR- Jack P and Patrick F running generator. Testing Cl2 leak and JHs inspections VNPS- Jake M done on site | All Water System ROC General | 2025-10-23
ROC | October | NBET - Historian Heartbeat alarm, trends ok, notified Ian W, will check SCADA. # CMU5 W11393726 | All Water System ROC General | 2025-10-26
ROC | October | YWS + NYWS NORMAL | All Water System ROC General | 2025-10-26
ROC | October | MKRSMR - Res HiHi level switch alarm, disregard as per Memo to fill res for trial Kennedy Road 1500 mm isolation. MKPSSA - Discharge pressure Hi alarm. MKRSMR-MKRSMR to COTFA Permissive alarm. | All Water System ROC General | 2025-10-29
ROC | October | MKRSMR - Duty deactivated, res filling . Deactivated BVPS pumps to reduce flow to res. | All Water System ROC General | 2025-10-29
ROC | October | RHMCMD- man/open to send flow to RH. | All Water System ROC General | 2025-10-29
ROC | October | VNRSKS- Activated D1 | All Water System ROC General | 2025-10-26
ROC | October | YWS+NYWS normal | All Water System ROC General | 2025-10-26
ROC | October | HLW2, Newmarket East zone- Slow communication, HUB 3 server error message, notified Kyle C, he will contact network team. | All Water System ROC General | 2025-10-21
ROC | October | HLETYS - Post injection Total chlorine residual Hi alarm, Adjusted Hypo pump 2 Max flow from 170 to 175 mL/min. Alarm cleared. | All Water System ROC General | 2025-10-18
ROC | October | NMETIB, Deactivated D1 to allow offset NMVCBA, Placed back to 50L/sec NMVCIB, Placed back to 70L/sec | All Water System ROC General | 2025-10-16
ROC | October | HLETYS - Pre Injection Combined Chlorine Lo alarm came in. Initiated flushing procedure - Placed HLETYS Chemical Pumps off - Placed Flow to Waste valves man/open at 30% - Enabled Tower Inlet Flow hi/lo alarms - Enable Tower Total Chlorine Residual Hi alarm as per interim | All Water System ROC General | 2025-10-18
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-18
ROC | October | AUW14- Placed P3 in man/on and 1/2/4 in manual YWS+NYWS normal Adam Button signing out | All Water System ROC General | 2025-10-16
ROC | October | STETBR - Free Chlorine Lo alarm came in. Known issue and levels have risen back to optimal range and alarm has cleared. Will continue to monitor | All Water System ROC General | 2025-10-26
ROC | October | Ethan U signing in NMTKKC - Eric S onsite for replacing colorimeter on inlet total analyzer. | All Water System ROC General | 2025-10-27
ROC | October | AUW57- Influent free Cl2 hihi alarm came in on well start up. Trends recovered and alarm cleared after 3 mins | All Water System ROC General | 2025-10-22
ROC | October | KLPSWL- Rob P returned site back to normal ops. Will be placing pumps back in auto. Adjusted Cl2 analyzer after work had been done and residual should stabilize. Rob P will be leaving site slowly | All Water System ROC General | 2025-10-22
ROC | October | NBW5, Turbidity Hi Alarm, Rotated silicate pumps so pump 1 is in D1. If NTU doesn't recover, will place well man/off for the night and send email to on call operator/area | All Water System ROC General | 2025-10-16
ROC | October | Starting Maple to Jefferson Feed AUW14, Placed well 1 man/on | All Water System ROC General | 2025-10-16
ROC | October | KSTP- Raw Water Turbidity Fault Alarm. Disregard as per SCADA Report | All Water System ROC General | 2025-10-17
ROC | October | RHMCEM- Closed valve in manual | All Water System ROC General | 2025-10-17
ROC | October | MKRSMR - Res High level alrm, Duty setpoints adjusted earlier from 3,0 -5,0 m to 3,5-5,5m. | All Water System ROC General | 2025-10-18
ROC | October | Angelica Chepiga signing out | All Water System ROC General | 2025-10-24
ROC | October | BLW3 - placed in auto | All Water System ROC General | 2025-10-16
ROC | October | Christian Van Beek signing in. Weather: 19C and clear. | All Water System ROC General | 2025-10-19
ROC | October | MTW3- Patrick F onsite for health and safety work orders. Will then be going to MTW12 for hypo delivery and returning to MTW3 for silicate system and turbidimeter maintenance. | All Water System ROC General | 2025-10-17
ROC | October | QVW34 - QVW3 VFD fault alarm. Checked site, well was running in manual mode when the alarm triggered. Leaving alarm outstanding overnight as this well is not a duty 1 well. | All Water System ROC General | 2025-10-19
ROC | October | STETBR - Free chlorine low alarm. Checked site, trending shows a dip of the free chlorine reading which has recovered to above the low alarm setpoint. Cleared alarm and will monitor system through the day. | All Water System ROC General | 2025-10-27
ROC | October | MKPSSA, Artour L on site working with Drew from Ferguson Electric | All Water System ROC General | 2025-10-30
ROC | October | RHPSWA- Placed P2 in man/off | All Water System ROC General | 2025-10-16
ROC | October | KSTP- Raw water turbidity fault alarm came in disregard on shift report | All Water System ROC General | 2025-10-22
ROC | October | KSTKWP - Free chlorine lolo and total chlorine lolo. Called Ryan B who is on site during the tank isolation. The isolation procedure resulted in the drop of the analyzer readings and Ryan is aware. | All Water System ROC General | 2025-10-20
ROC | October | RHRSEM- Adjusted valve position to 15% | All Water System ROC General | 2025-10-17
ROC | October | MAPS PD8- Placed P1-3 in manual KCPSDS- Placed P1/2 in manual off AUW57- Influent free Cl2 lo alarm came in. Recovered after 3 mins cleared alarms | All Water System ROC General | 2025-10-17
ROC | October | NBW5 - Redempto B finished on site. placed well in auto mode. | All Water System ROC General | 2025-10-27
ROC | October | RHVCEM - Man/close to 30 % to help with MARS level | All Water System ROC General | 2025-10-16
ROC | October | KSTP - Filter 1 Backwash is OOS alarm came in. Checked site. Noticed that the filter was interlocked. Called Phil D. who will take a look on SCADA 04:08 - Phil D. called back to inform that the alarm came in due to the filter going into a backwash. Phil gave direction to clear alarm once backwash is complete #CONSULT | All Water System ROC General | 2025-10-28
ROC | October | QVW12, Effluent Free CL2 hihi. Wells interlocked, notified Ben H that the wells now are currently locked out, he will look into it shortly but directed to leave wells off till the slug passes. | All Water System ROC General | 2025-10-30
ROC | October | AUW57 - Donald M. is finished on site and will leave AUW5 man/on. | All Water System ROC General | 2025-10-30
ROC | October | MKRSMR - Jack P on site to complete work orders including chlorine analyzer maintenance, hi/low level tests, flood alarm test and JHSC checks. | All Water System ROC General | 2025-10-28
ROC | October | HLETYS - After 7 hours of flushing, the tower didn't reach the hi level total Cl2 alarm, Pre injection Total chlorine reading - 0,93 mg/l, Combine -0,89mg/l. Adjusted Flow to waste valve from 36 to 30%. Man/started QVW34 Well 3 pump to help with flushing procedure. Notified Jacob M, He is ok to continue flushing for another hour. # Consult | All Water System ROC General | 2025-10-18
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-20
ROC | October | Adeela Khan signing out | All Water System ROC General | 2025-10-28
ROC | October | QVW12 - Chlorine emergency valve closure fault alarm and emergency valve closure active alarm. Ryan B called to inform he is on site for a cylinder change, and these alarms can be disregarded. STETTL - Tower level low alarm. Checked site, area operators are still deep cycling the tower below the usual duty 1 start setpoint. | All Water System ROC General | 2025-10-28
ROC | October | MTETNL - Phil D called to inform that East Gwillimbury operators will be flushing in this Mount Albert system today. Phil D directed to activate system duty. | All Water System ROC General | 2025-10-28
ROC | October | AURSBS, Res is at 55%, Reverting Maple to Jefferson Feed. VNRSKS, Activated D1 RHVCEM, placed valve to 50% | All Water System ROC General | 2025-10-16
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-17
ROC | October | NMTKKC - Chloramine analyzer offline alarm. Alarm returned to normal status almost immediately after triggering. Log book shows Joe D on site. Acknowledged alarm and it reset. | All Water System ROC General | 2025-10-20
ROC | October | YWS + NYWS Normal Christian Van Beek signing out. | All Water System ROC General | 2025-10-20
ROC | October | STW12 - Travis W finished at site | All Water System ROC General | 2025-10-22
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-18
ROC | October | SHTP - Hydro power failure alarm came in. Checked site and noticed that a power blip occurred. All alarms cleared withing 5 mins. | All Water System ROC General | 2025-10-18
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-19
ROC | October | STETBR - Tower Level Hi alarm came in. Placed STW1 back to auto, as per interim | All Water System ROC General | 2025-10-19
ROC | October | VNRSKS and KCETDS - Activated duty to help lower levels at MARS | All Water System ROC General | 2025-10-20
ROC | October | STETTL - Tower Level Lo alarm came in. Called Stephen B. who directed to activate both zone 1 and 2 duties and place STPSTL pumps back to auto | All Water System ROC General | 2025-10-30
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-30
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-29
ROC | October | STW12- Placed wells back into auto as Zone 1 fill cycle completed. | All Water System ROC General | 2025-10-29
ROC | October | RHPSWA- Placed P1 in man/off BVPS- Jack P on site to test eyewash and work on Cl2 analyzer | All Water System ROC General | 2025-10-16
ROC | October | VNPS _ Mike O leaving site with Vaughan fire. | All Water System ROC General | 2025-10-27
ROC | October | MAPS PD7 - Pump 2 uncommanded stop due to a discharge valve 1 uncommanded close alarm. Checked site, duty recently activated to fill VNRSKS. Pump 2 activated and then shut down due to a valve fault. Duty rotated to pump 4. Monitoring station to ensure pump 4 activates. Will clear alarms on pump 2 after pump 4 starts. | All Water System ROC General | 2025-10-27
ROC | October | KSETDP - Inlet total CL2 hihi, known to spike on startups as per shift report. Remains reading hi, rotate to chlorinator 1. Reading dropped to normal range. Disregard | All Water System ROC General | 2025-10-27
ROC | October | KSTP- Fin Water Tot CL2 Res Fault, Fin Water Fluoride Res Fault Alarms. Disregard as per SCADA Report. | All Water System ROC General | 2025-10-31
ROC | October | NMTKKC- Joe D on site to work on chemscan. Will clear alarms associated when done work | All Water System ROC General | 2025-10-31
ROC | October | NMETHW- Ryan B done on site and reverted all system changes | All Water System ROC General | 2025-10-31
ROC | October | STW3 - Travis W on site for a chlorine leak detection test. | All Water System ROC General | 2025-10-31
ROC | October | YWS + NYWS Normal Christian Van Beek signing out. | All Water System ROC General | 2025-10-31
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-17
ROC | October | Carter Dunn Signing Out | All Water System ROC General | 2025-10-20
ROC | October | NMETIB - Timberbank Valve Chamber Flood alarm came in. Rob P. called to inform that he is working on site | All Water System ROC General | 2025-10-30
ROC | October | VNPS - Dan B working on PD8 Pump 1, powering down station for 2 hours. | All Water System ROC General | 2025-10-16
ROC | October | SUETDR- Patrick F testing LIT, temp, flood alarms and cleaning chlorine analyzers. | All Water System ROC General | 2025-10-16
ROC | October | Carter Dunn Signing In, 12D/Clear | All Water System ROC General | 2025-10-16
ROC | October | AURSBS, Activated D1 | All Water System ROC General | 2025-10-16
ROC | October | QVW12, Donald M/Alex B is on site, changing Cl2 cylinders, directed to disregard leak alarms | All Water System ROC General | 2025-10-24
ROC | October | MTW12/3, Pat F on site working on the turbidity analyzers | All Water System ROC General | 2025-10-24
ROC | October | STW12 - Travis W running generator. | All Water System ROC General | 2025-10-21
ROC | October | MKRSEM - Reservoir low level alarm. Deactivated duty 1 at MKRSMR to allow MKRSEM time to recover its level. | All Water System ROC General | 2025-10-31
ROC | October | HLETYS, After 7 hours of flushing, the tower didn't reach the hi level total Cl2 alarm, as per interim procedure, notified Phil D, was directed to place the tower back to normal operation consult | All Water System ROC General | 2025-10-17
ROC | October | SHTP, Filter 3 Turbidity Hi alarm, Filter 1 backwashing, as per shift report directed to disregard for the first time | All Water System ROC General | 2025-10-17
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-17
ROC | October | KSTP, Fin Water Tot Cl2/Fluoride Res Fault, Plant has just recently turned off, as per shift report, directed to disregard | All Water System ROC General | 2025-10-17
ROC | October | GRTPLL - Raw water total chlorine hihi alarm. SCADA review states that this value spikes randomly in the run cycle and can be disregarded for twenty minutes. If the value does not return to normal range in twenty minutes, they request a call out. | All Water System ROC General | 2025-10-31
ROC | October | MKRSEM, notified Toronto operator Andrew to stop pumping to the res | All Water System ROC General | 2025-10-29
ROC | October | SHTP - Filter 1 turbidity hi alarm. Checked site. filter 2 is going through a backwash sequence. Reset alarm once as per the shift report. | All Water System ROC General | 2025-10-22
ROC | October | MARS - High level alarm. Activated AURSBS duty 1 to drawdown the reservoir. | All Water System ROC General | 2025-10-23
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-23
ROC | October | YWS + NYWS NORMAL | All Water System ROC General | 2025-10-19
ROC | October | GRTPLL - low lift discharge turbidity fault alarm. Checked site, low lift pumps not active. Trending shows that the turbidity reading is stable. System is currently full, low lift pumps should not run for several hours. Will monitor the alarm, if it cannot be reset within one hour will call OCO. GRTPLL - Called Stephen B who directed to disregard the alarm. #consult | All Water System ROC General | 2025-10-19
ROC | October | NMVCBA - Placed valve in manual, as per interim 22:41 - Placed valve back to auto | All Water System ROC General | 2025-10-19
ROC | October | RHRSTR- Deactivated D1 ARPS- Total ammonia fault came in. D1 not active and value isnt exceeding hi level alarm will continue to monitor and clear once recovered YWS+NYWS normal | All Water System ROC General | 2025-10-25
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-20
ROC | October | Carter Dunn Signing In | All Water System ROC General | 2025-10-23
ROC | October | RHMCMD - Duty deactivated, placed MC back to auto. | All Water System ROC General | 2025-10-21
ROC | October | RHMCMD- Opened valve in man 100% | All Water System ROC General | 2025-10-25
ROC | October | KCETFS- Artour L, Ian W and Yash S onsite for network work. No impact to operations. | All Water System ROC General | 2025-10-27
ROC | October | NMETIB- Deactivated duty | All Water System ROC General | 2025-10-21
ROC | October | STETTL - Outlet free chlorine low alarm. Checked site, tower is filling. Trending shows the chlorine residual is slowly recovering. Will monitor site. | All Water System ROC General | 2025-10-21
ROC | October | NMVCBA - Placed valve in man, as per interim | All Water System ROC General | 2025-10-18
ROC | October | QVW34 - Activated QVW4 in manual mode to promote flow south across EGMCRW while holland landing system is active. | All Water System ROC General | 2025-10-21
ROC | October | MARS - level hi alarm. Deactivated BVPS, and activated duty 1 at AURSBS to draw down MARS level. | All Water System ROC General | 2025-10-22
ROC | October | RHMCMD - Opened in manual mode to allow flow from Vaughan to Richmond Hill | All Water System ROC General | 2025-10-22
ROC | October | AUW14- Well 1 flow to waste fault. Well running okay no flow to waste during start up. Able to reset alarm. | All Water System ROC General | 2025-10-22
ROC | October | VNETFD - Chris S on site to swap UPS batteries. | All Water System ROC General | 2025-10-31
ROC | October | AUETFC- Talha H working on OIT. Disregard Heartbeat Alarm. | All Water System ROC General | 2025-10-27
ROC | October | NMTKKC - Chloramine analyzer offline alarm. Joe D on site and working on the analyzer. | All Water System ROC General | 2025-10-27
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-22
ROC | October | NMETHW - Joe D heading to site, placed QVW12 man/off for sampling | All Water System ROC General | 2025-10-22
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-18
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-19
ROC | October | HLW2 - Combined chlorine lolo alarm. Checked site, well is not on. Trending shows a dip of the combined chlorine reading which recovered within two reading intervals. Reset alarm. | All Water System ROC General | 2025-10-19
ROC | October | SHTP - Filter 2 and filter 3 turbidity hi alarms. Checked site, filter 1 is going through a backwash sequence. Turbidity values are dropping, will reset the alarm once as per the most recent shift report. If the alarms return will call out. | All Water System ROC General | 2025-10-19
ROC | October | STRS48, Artour L on site with electricians, replacing the generators on site, directed to disregard comm alarms from site NMETHW, Divya P on site working on the heattrace and the Cl2 analyzers | All Water System ROC General | 2025-10-23
ROC | October | STPSMR, Jack/Pat F is finished on site, the are heading to STRS48 to help Travis | All Water System ROC General | 2025-10-23
ROC | October | RHPSRA - Generator warning alarm, disregard as per SCADA review. | All Water System ROC General | 2025-10-26
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-22
ROC | October | RHMCMD - Opened in manual | All Water System ROC General | 2025-10-23
ROC | October | NMMCHW, Placed valve back to man/closed, Aron from EG called saying they are done their work | All Water System ROC General | 2025-10-23
ROC | October | STETBR - Free Chlorine Lo alarm came in. Lower Residuals throughout the night. Called Phil D. who directed to activate duty and to change the Start/Stop setpoint from 40/80 to 55/85 respectively and placed STW2 in manual, as per interim #CONSULT | All Water System ROC General | 2025-10-25
ROC | October | SHTP - Filter 3 Turbidity Hi alarm came in. Ack/reset as per shift report | All Water System ROC General | 2025-10-25
ROC | October | QVW12- Treated Free Chlorine HiHi and Combined Chlorine Lo Alarms. Duty deactivated recently, wells not running. Values recovered. Cleared alarms. | All Water System ROC General | 2025-10-26
ROC | October | NMTKKC, Placed D1 stop from 85 to 75% | All Water System ROC General | 2025-10-24
ROC | October | SHSP - Benson S on site completing maintenance on the chlorine analyzers. KSTKWP - Eric S finished and leaving site. | All Water System ROC General | 2025-10-27
ROC | October | NMTKKC - Joe D on site to clean the inlet total chlorine analyzer. Joe has placed the chemical pumps manual/off. | All Water System ROC General | 2025-10-27
ROC | October | HLETYS - activated Duty 1 STPSTL - Travis W. running generator | All Water System ROC General | 2025-10-24
ROC | October | KCETDS - Talha H working on the OIT and directed to disregard the historian heartbeat alarm. | All Water System ROC General | 2025-10-28
ROC | October | GWTP - Eric S on site to replace the pH probe for the waste wash water system. | All Water System ROC General | 2025-10-28
ROC | October | Angelica Chepiga signing in, weather +21C | All Water System ROC General | 2025-10-18
ROC | October | YWS + NYWS NORMAL | All Water System ROC General | 2025-10-18
ROC | October | NMETHW- Ryan B on site to work on altitude valve. Will be isolating tower. QVETQS is now controlling tower for NM East system. QVETQS- Ryan B activated Duty and opened tie valve. NMETIB- Deactivated D1 NMVCBA- Opened in manual at 30L/s | All Water System ROC General | 2025-10-31
ROC | October | YWS + NYWS NORMAL | All Water System ROC General | 2025-10-29
ROC | October | NMTKKC PAC Minor Fault Alarm. Notified Ian W. He will look into it. | All Water System ROC General | 2025-10-28
ROC | October | MKPSSA- to MKRSMR Communication fail. Stopped Pumps 2 and 3. Alarm cleared on its own. Pumps started back up then Pump 3 shut down on Failed to Start Alarm. Deactivated MKRSMR duty (70%). Cleared alarm. STETTL- to STRS48 Comm Alarm STPSTL- to STETBR Communication Alarm STETBR- to STPSTL Communication Alarm STRS48- to STETTL Comm Alarm All Alarms cleared | All Water System ROC General | 2025-10-30
ROC | October | STETBR - Free chlorine Lo alarms in and out. Notified Phil D. He is aware about lower free chlorine residual and will notify area tomorrow. Requested monitor. # Consult. | All Water System ROC General | 2025-10-26
ROC | October | SHTP - Filter 3 Turbidity hi alarm came back in. Called Jacob M. who directed to place filter into backwash #CONSULT | All Water System ROC General | 2025-10-25
ROC | October | VNETFD- Deactivated duty to help tower cycle better | All Water System ROC General | 2025-10-25
ROC | October | AUW57- influent free Cl2 lo alarm came in on well start up. Cleared after 3 mins trends look okay | All Water System ROC General | 2025-10-25
ROC | October | KSTP- Filter 1 unit filter run volume not trending. Notified Phil D to inquire about how critical this trend is for plant ops. Phil D req call to PCS to take a look. Notified Ian W and created CMU5 W11393593 #CMU5 | All Water System ROC General | 2025-10-25
ROC | October | KSETDP- Inlet Total CL2 HiHi Alarm. Cleared alarm | All Water System ROC General | 2025-10-27
ROC | October | STPSMR- Jack P called. With Joe M on site changing chlorine cylinders. Disregard Gas Detector hihi alarm. | All Water System ROC General | 2025-10-28
ROC | October | QVW12- Treated Free Chlorine HiHi and Combined Chlorine Lo Alarms. Duty deactivated recently, wells not running. Values recovered. Cleared alarms. | All Water System ROC General | 2025-10-28
ROC | October | MAPS- Initiating MARS to JFRS feed as per Procedure | All Water System ROC General | 2025-10-26
ROC | October | YWS + NYWS Normal Adeela Khan signing out | All Water System ROC General | 2025-10-27
ROC | October | HLVCMA- Ian W called and spoke with Adeela K. He will look into outstanding PAC Communication Failure alarm this morning | All Water System ROC General | 2025-10-27
ROC | October | STW12- Communication Loss to STW12. Called Ian W. No answer. Will try again. | All Water System ROC General | 2025-10-27
ROC | October | RHMCMD - Placed valve man/closed | All Water System ROC General | 2025-10-28
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-28
ROC | October | VNPSCD - Chlorine Valve 1 failed to close alarm came in. Checked site. Noticed that valve 1 had faulted and switched to chlorine valve 2. Was able to ack/reset. Will monitor. | All Water System ROC General | 2025-10-31
ROC | October | AURSBS- Activated duty | All Water System ROC General | 2025-10-30
ROC | October | AUETOH- Activated duty NMTKBS- Activated duty | All Water System ROC General | 2025-10-30
ROC | October | Gluzen Ramos Ong signing out | All Water System ROC General | 2025-10-30
ROC | October | Adam Button signing out | All Water System ROC General | 2025-10-17
ROC | October | NRETCR - Power blip, alarms cleared. AUETAD - Power blip, alarms cleared. | All Water System ROC General | 2025-10-18
ROC | October | STW12 - placed pumps 1 and 2 to auto, as per interim. | All Water System ROC General | 2025-10-18
ROC | October | VNPS PD7- Placed P2 in man/off | All Water System ROC General | 2025-10-17
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-21
ROC | October | YWS + NYWS NORMAL | All Water System ROC General | 2025-10-28
ROC | October | YDOC - Terry C & Matt T onsite testing fan vibrations. Man start fan 1 and man stop fan 2 which was in auto | All Water System ROC General | 2025-10-29
ROC | October | YWS + NYWS NORMAL | All Water System ROC General | 2025-10-26
ROC | October | SUETDR - Activated duty 1, as per Stephen B. | All Water System ROC General | 2025-10-27
ROC | October | JFRS - End Maple to JFRS feed | All Water System ROC General | 2025-10-16
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-16
ROC | October | RHPSWA- Placed P 1 in man/on NRETCR- Activated D1 | All Water System ROC General | 2025-10-16
ROC | October | STPSMR - Suction Header Pressure Hi and HiHi alarm. Duty not active. Called Toronto water (Zoran) requested to change Duty stop point at MKRSMR from 5,5 to 5,4m. Duty deactivated. MKRSEM - Requested Toronto water(Zoran) stop filling Res. | All Water System ROC General | 2025-10-18
ROC | October | HLETYS - Adjusted flow to waste valve to promote optimal flow into the tower during the flushing procedure. Will make additional adjustments as necessary until the seven hour flushing window has passed. | All Water System ROC General | 2025-10-20
ROC | October | AUMCBS - Rick L and Parth P on site to calibrate the flow meter. No impact to operations expected. | All Water System ROC General | 2025-10-20
ROC | October | GWTP - Train 8 not all devices in auto mode and hihi level alarm. Called Stephen B who is working on this filter. | All Water System ROC General | 2025-10-20
ROC | October | EGMCRW, Ryan B on site preforming an isolation, if East has low pressure alarms, Ryan B would like to be notified | All Water System ROC General | 2025-10-21
ROC | October | MKRSMR - Sean P working on flood float . | All Water System ROC General | 2025-10-16
ROC | October | KSETDP- Inlet total Cl2 hihi alarm came in. Disregard on shift report | All Water System ROC General | 2025-10-17
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-31
ROC | October | RHMCMD, Placed valve man/closed | All Water System ROC General | 2025-10-30
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-20
ROC | October | AURSBS - Short cycled reservoir to help lower levels at MARS | All Water System ROC General | 2025-10-20
ROC | October | MMW1 - Parth P, Rick L, Red B finished on site. | All Water System ROC General | 2025-10-21
ROC | October | YWS + NYWS NORMAL | All Water System ROC General | 2025-10-16
ROC | October | KLW34- Treated combined and total Cl2 hihi alarms came in. Notified Cole W directed to disregard for the day as these will be impacted by work being done at KLPSWL STW12- Travis W on site for station checks and sampling. E key may set off alarm. | All Water System ROC General | 2025-10-22
ROC | October | MAP7 - Place pumps back in auto MAP8 - Place pump 2 man/start and man/stop pump 1 as requested from Lee F KSTP - Donald M onsite for filter backwash | All Water System ROC General | 2025-10-22
ROC | October | AUW57- Placed well man/on RHPSWA- Placed P1 in man/on | All Water System ROC General | 2025-10-16
ROC | October | GWTP - Stephen B working on GAS 2 and cleaning chlorine analyzers on Sutton and Keswick headers. | All Water System ROC General | 2025-10-21
ROC | October | QVW12- Influent Free HiHi. Recovered back to normal. Cleared alarm. | All Water System ROC General | 2025-10-17
ROC | October | NMETYS- Yash S working on OIT. Disregard heartbeat alarm. 10:05- finished | All Water System ROC General | 2025-10-17
ROC | October | AUPSOH - Site hydro fail alarm and generator running alarm. Checked site, generator is running and ATS is pointed to the generator indicating a power failure. While monitoring the ATS switched back to town hydro, indicating a short hydro fail event. The pumps were running but are inhibited by the changes in power supply. Will monitor site to ensure pumps activate normally. | All Water System ROC General | 2025-10-19
ROC | October | BVPS, Placed pumps back to auto, accidentally started pump 4 when placing it back to auto however it turned off immediately. Jack P/Pat F finished on site | All Water System ROC General | 2025-10-23
ROC | October | KSTKWP- Eric S onsite working on CL17 Free analyzer. | All Water System ROC General | 2025-10-27
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-31
ROC | October | STW3 - Jack P heading to site to test chlorine leak | All Water System ROC General | 2025-10-29
ROC | October | VNPS- Cole W onsite for chlorine system work. May receive a high post injection alarm. Disregard related alarms while onsite. | All Water System ROC General | 2025-10-28
ROC | October | BLETNL- Phil D. onsite working on all analyzers and low temp alarm. | All Water System ROC General | 2025-10-21
ROC | October | STETBR - Deactivated duty as STETTL duty deactivated, as per shift report. Will leave STW12 man/on, as per shift report | All Water System ROC General | 2025-10-27
ROC | October | Gluzen Ramos Ong signing in | All Water System ROC General | 2025-10-24
ROC | October | NMW15- Influent free Cl2 lo alarm came in on well start up. Cleared alarm after trends recovered in 3 mins. | All Water System ROC General | 2025-10-24
ROC | October | MKRSEM-Called Metro spoke with Paul to start two pumps to fill reservoir | All Water System ROC General | 2025-10-25
ROC | October | QVW34- Alex B on site with Mechanical to work on well 3 will be placing well in local for work | All Water System ROC General | 2025-10-22
ROC | October | STPSTL/STETTL - Rick L finished at site | All Water System ROC General | 2025-10-22
ROC | October | VNRSKS - Hi level alarm setpoint back to 92%. RHVCEM - man/open to 80% | All Water System ROC General | 2025-10-16
ROC | October | HLW2 - Combine chlorine LoLo , Treated chlorine lolo alarms. Quick drop. well 2 off, not directing water to users. Value is back in one reading, cleared alarms. | All Water System ROC General | 2025-10-21
ROC | October | NMVCBA- Placed back in auto | All Water System ROC General | 2025-10-22
ROC | October | NMW12 - Combined Chlorine Lo alarm came in. Wells are not running and water is not being directed to users | All Water System ROC General | 2025-10-20
ROC | October | STETBR - Dan Z called to inform that East operations is completing a deep cycle of STETBR. MKRSEM / MKRSMR - Dan Z has also requested a deep cycle of MKRSEM and MKRSMR. Dan Z has directed to deep cycle MKRSEM first using MKPSSA. Made necessary changes. GWTPLL - Yash S on site to complete VFD commissioning for pump 3. May see associated alarms. | All Water System ROC General | 2025-10-20
ROC | October | STW12 - Placed STW2 in auto mode. | All Water System ROC General | 2025-10-22
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-23
ROC | October | HLETYS - Completing flushing procedure. Reverting system changes. | All Water System ROC General | 2025-10-20
ROC | October | Stouffville - Andrew M. from OCWA will be completing flushing in zones 1 and 2 between 08:00-12:00. Andrew will call when this is completed | All Water System ROC General | 2025-10-30
ROC | October | RHMCH7- Harsh P onsite for inspections. Disregard alarms while onsite. | All Water System ROC General | 2025-10-27
ROC | October | MTETNL, Activated D1 for Phil D | All Water System ROC General | 2025-10-23
ROC | October | STETTL, Tower draining while duty is active, notified Travis W, he will be finished his work at STW12 in 20 minutes so we can disregard at this time | All Water System ROC General | 2025-10-21
ROC | October | Christian Van Beek signing out. | All Water System ROC General | 2025-10-28
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-27
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-27
ROC | October | HLETYS - Completed flushing operations without reaching Tower pre injection total chlorine Hi alarm. Man/closed Flow to waste valve, placed chemical pumps to auto, disabled tower inlet flow Hi/lo alarms, disabled TWR AIT2 High alarm. As per interim memo. | All Water System ROC General | 2025-10-18
ROC | October | STETBR - Low level alarm. Placed STW1 in manual on for the fill cycle of STETBR as per the interim procedure. | All Water System ROC General | 2025-10-19
ROC | October | AUW57, Influent Free CL2 lolo, Notified Jerry Z, he will head to site | All Water System ROC General | 2025-10-21
ROC | October | SHTP - Jacob M on site with OP from town of King running fire pumps. | All Water System ROC General | 2025-10-21
ROC | October | KCETDS- Talha H working on OIT. Disregard heartbeat alarm. | All Water System ROC General | 2025-10-28
ROC | October | KSETWB- Historian Heartbeat alarm. Notified Ian W. He will look into it. | All Water System ROC General | 2025-10-28
ROC | October | QVW34- Alex B and Ryan B on site for Cl2, ammonia and silicate system inspection as well as silicate injection points as well as pigtail replacement Cl2 system Will have wells in man/off. QVW12- Rick L and Parth P on site for calibrations. Placed wells man/off NBW3- Lee F onsite for backflow testing. Palced well 7 man/off GWTP- Phil D on site for dehumidifier replacement | All Water System ROC General | 2025-10-16
ROC | October | KLPS27- Historian heartbeat alarm came in notified Artour L. Will take a look on SCADA | All Water System ROC General | 2025-10-16
ROC | October | KLPSWL - Historian Heartbeat alarm, notified Artour L. He will check SCADA. | All Water System ROC General | 2025-10-16
ROC | October | KSTP - Finished Water Fluoride Residual LoLo alarm came in. Checked site. Levels came back to optimal range | All Water System ROC General | 2025-10-20
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-21
ROC | October | MARS, Notified Toronto operator Paul to go back to normal flow through TMC317 RHMCMD, Placed valve back to auto | All Water System ROC General | 2025-10-30
ROC | October | Angelica Chepiga signing out | All Water System ROC General | 2025-10-16
ROC | October | VNPS PD8, Deactivated D2 RHPSWA, Placed pump 2 man/on. RO doing this to help keep RHRSTR stabilize while continuing to fill JFRS | All Water System ROC General | 2025-10-16
ROC | October | MKRSEM, Notified Toronto operator Paul to start filling the res | All Water System ROC General | 2025-10-16
ROC | October | MARS, Notified Toronto operator Paul to go back to normal flow | All Water System ROC General | 2025-10-17
ROC | October | Maple to Jefferson Feed complete, will continue to monitor, if needed, will prepare the system a third time to re do the feed to help day shift operations | All Water System ROC General | 2025-10-17
ROC | October | AURSBS, Activated D1 KCETDS, Activated D1 | All Water System ROC General | 2025-10-17
ROC | October | MMW1- Mon Well 9 level lolo/OOR alarms came in. Notified Dwayne L directed to Inform Eric S, Eric S will Contact Dwayne L to reschedule replacement of LIT | All Water System ROC General | 2025-10-22
ROC | October | MARS- Reverted MARS to JFRS as per procedure | All Water System ROC General | 2025-10-26
ROC | October | NMETIB- Activated D1 to offset from NMETHW as per interim | All Water System ROC General | 2025-10-26
ROC | October | AURSBS - Activated duty 1 to help lower levels at MARS | All Water System ROC General | 2025-10-27
ROC | October | MAPS PD7, Placed Pump 3 back to auto as pump duty rotation placed it back to D1 VNPS PD7, Placed pump 2 in man/off | All Water System ROC General | 2025-10-20
ROC | October | MTW12/MTW3 - Place pumps back in auto, Rick L finished at site | All Water System ROC General | 2025-10-29
ROC | October | BLW12 - Effluent free chlorine hihi, turbidity hi, Wells local/off | All Water System ROC General | 2025-10-29
ROC | October | STW3 - Rick L finished at site | All Water System ROC General | 2025-10-29
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-21
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-24
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-24
ROC | October | YWS + NYWS normal | All Water System ROC General | 2025-10-10
ROC | October | NRETCR - Outlet total chlorine lo, trends show sudden dip but reading returned to normal range | All Water System ROC General | 2025-10-10
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-06
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-08
ROC | October | QVW12- Effluent free Cl2 hi alarm came in looks slightly elevated. Influent free Cl2 within normal range. Trends recovered after 10 mins cleared alarm will continue to monitor | All Water System ROC General | 2025-10-02
ROC | October | STETBR/STETTL- Dan Z called to inform ROC STETBR and STETTL are deep cycling and placed pumps at STPSTL in man and opened the FCV to feed zone 2 via zone 1 | All Water System ROC General | 2025-10-07
ROC | October | AUPSRR - post injection free chlorine hihi alarm. Checked site, chemical pumps appear to be operating normally. Trending shows a sudden spike of the post injection free chlorine reading which returned to normal range within one reading interval. Reset alarm. | All Water System ROC General | 2025-10-03
ROC | October | Gluzen Ramos Ong signing in | All Water System ROC General | 2025-10-03
ROC | October | BVPS- Jack P onsite for generator load test. Will call when wants duty deactivated. Placed RHMCMD in auto. 08:00- Deactivated duty and placed pumps in manual | All Water System ROC General | 2025-10-03
ROC | October | YWS + NYWS NORMAL | All Water System ROC General | 2025-10-10
ROC | October | NMTKBS- Free Cl2 hi alarm came in again under the same conditions as earlier in the night. Will continue to disregard as per Divya P and call out if combined Cl2 lo alarm comes in. | All Water System ROC General | 2025-10-01
ROC | October | KSETWB- Dan B working on gas detector. Disregard related alarms. | All Water System ROC General | 2025-10-01
ROC | October | KLPSWL- David T onsite for PMs. Working on Cl analyzers, turbidimeters, Cl scrubber, health and safety, and flood alarm. | All Water System ROC General | 2025-10-02
ROC | October | Stouffville Water System- Andrew (226-337-7178) from OCWA performing flushing in zones 1 and 2 until around noon. | All Water System ROC General | 2025-10-02
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-10
ROC | October | MARS- Cole W onsite isolating North Cell. Waiting on call back from OCWA to stop pumping and will inform Cole W once pumps are off. 07:51- OCWA Placed ARPS man/off. Notified Cole W. He will continue with valving. Requested to shutdown MAPS PD8 pumps if low suction pressure comes in. KCETDS- Activated duty | All Water System ROC General | 2025-10-08
ROC | October | NMETHW- Deactivated D1 and adjusted the D1 start to 38% to allow Alex B to continue work at QVW12 KCETDS- Yash S done on site gap in trends will be backfilled tomorrow | All Water System ROC General | 2025-10-07
ROC | October | Ethan U signing in | All Water System ROC General | 2025-10-10
ROC | October | NMTKBS - Activated D1 as per interim memo to have NMTKBS at 60% for 10 am. | All Water System ROC General | 2025-10-10
ROC | October | NMW136 - Influent chlorine residual LoLo alarm, quick drop/ recovered. Cleared alarm. | All Water System ROC General | 2025-10-10
ROC | October | AURSBS, Activated D1 to help bring down MARS level NMETHW, Activated D1 QVW3, Placed well man/on since QVW1 is OOS at the moment | All Water System ROC General | 2025-10-13
ROC | October | GWTP - Backwash tan 1 loss of echo alarm. Disregard as per the shift report. GRTPLL - low lift drainage pump 1 overload, stop alarm. Checked site, low lift drainage pump 2 is available and rotated into duty 1. Unable to clear overload alarm. Sent email to OCO and will call out of the second pump faults. | All Water System ROC General | 2025-10-13
ROC | October | BLW3- running in manual mode, placed back to auto as per Patrick F. | All Water System ROC General | 2025-10-01
ROC | October | RHRSTR - Deactivated D1 @80%, notified Toronto water ( Andrew). | All Water System ROC General | 2025-10-10
ROC | October | MKPSSA - Dan Z exercising pumps. | All Water System ROC General | 2025-10-10
ROC | October | QVW12 - Alex placing well 12 pumps off for PRV check, cleaning silicate injection and turbidity meters. | All Water System ROC General | 2025-10-09
ROC | October | HLW2, Influent Free Cl2 hihi, Notified David T who is currently on site, he will take a grab and look into the issue | All Water System ROC General | 2025-10-06
ROC | October | KSETWB- Patrick F on site to test eyewash and perform health and safety inspection. Will be testing Cl2 leak detection test later as well NMTKKC- Header free Cl2 hi alarm. Reservoir filling looks like a spike reading continued to monitor GWTP- raw water Cl2 res hihi alarm came in. Disregard on shift report will monitor for revcovery in next 20 mins NMVCBA- Chris I on site to work on solonoids. Will call when done | All Water System ROC General | 2025-10-06
ROC | October | NBW5- Tim H onsite working on silicate system. | All Water System ROC General | 2025-10-03
ROC | October | GWTP - Stephen B. and Chris S. working on low lift pump 2, back in auto and D2. Req. if hydraulic valve fault comes in to ack+reset and notify them | All Water System ROC General | 2025-10-03
ROC | October | MKRSEM- Called Metro and spoke with Andrew to stop pumping to reservoir | All Water System ROC General | 2025-10-08
ROC | October | VNRSKS- Deactivated D1 as per interim AURSBS- Deactivated D1 as per interim | All Water System ROC General | 2025-10-08
ROC | October | KSTKWP- Divya P on site for Cl2 system inspection, leak test and analyzer maintenance. STRS48- Effluent free Cl2 lolo alarm came in recovered after 1 reading reset alarm | All Water System ROC General | 2025-10-07
ROC | October | MKRSMR, RHRSTR - Called Toronto water (Zoran) for update on The FJ Horgan WTP return to regular operations. Zoran will call us back with update. | All Water System ROC General | 2025-10-10
ROC | October | ANW23- Parth P finished onsite. | All Water System ROC General | 2025-10-07
ROC | October | RHVCEM- Opened from 50 to 100% to try to extend VNRSKS fill cycle for Maple South Cell drawdown. | All Water System ROC General | 2025-10-08
ROC | October | SCADA Single Risk Event, Notified Artour L, he will look into it. | All Water System ROC General | 2025-10-08
ROC | October | RHMCMD- Placed valve man/open to try and push water towards RHRSTR due to Horgan Water Treatment Plant shut down. | All Water System ROC General | 2025-10-09
ROC | October | NMTKKC- Joe D leaving site. | All Water System ROC General | 2025-10-09
ROC | October | AUW57- Influent free Cl2 lo alarm came in recovered after 3 min alarm cleared | All Water System ROC General | 2025-10-06
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-07
ROC | October | AUPSOH- Deactivated D1 as per interim | All Water System ROC General | 2025-10-08
ROC | October | RHPSPA - Jack P heading to site for a diesel generator test. | All Water System ROC General | 2025-10-02
ROC | October | STETBR- Sean from Town of Stouffville flushing in Zone 1 | All Water System ROC General | 2025-10-03
ROC | October | AUETFC- Jerry Z onsite testing temp alarm and eyewash alarm. | All Water System ROC General | 2025-10-02
ROC | October | STPSMR- Gas Detector HiHi. Chlorine Leak occurred. Dan Z onsite. Jack P will assist. CMU5. W11333067 | All Water System ROC General | 2025-10-02
ROC | October | STW12- Influent Free LoLo. Jack P is backflushing and troubleshooting hypo pumps. | All Water System ROC General | 2025-10-02
ROC | October | SHETCS- Out flow hi alarm came in but recovered within a minute. Cleared alarm and will continue to monitor | All Water System ROC General | 2025-10-06
ROC | October | Connor Smith signing in 5 C clear | All Water System ROC General | 2025-10-09
ROC | October | NMW12- Ryan B onsite working on silicate, chlorine and ammonia system. Wells will be man/off. | All Water System ROC General | 2025-10-09
ROC | October | YWS+NYWS normal | All Water System ROC General | 2025-10-02
ROC | October | VNPSAP- Aaron M working on cell modem. | All Water System ROC General | 2025-10-02
ROC | October | Connor Smith signing in 10C Clear | All Water System ROC General | 2025-10-03
ROC | October | SHTP- Benson S onsite for PMs. Generator run, Cl leak and scrubber, and chemical inspection. | All Water System ROC General | 2025-10-07
ROC | October | GWTP - Stephen B requested disregard Low lift alarms. Chris S working on pumps, replacing pressure transmitter. | All Water System ROC General | 2025-10-09
ROC | October | NBET27- Eric S onsite working on Total chlorine analyzer | All Water System ROC General | 2025-10-09
ROC | October | QVW12 - Ammonia Containment flood alarm, Alex B testing . | All Water System ROC General | 2025-10-09
ROC | October | SHETCS- Post Injection hi alarm came in cleared after 2 readings | All Water System ROC General | 2025-10-08
ROC | October | ANW23- Placed wells man/off Interim Procedure. | All Water System ROC General | 2025-10-02
ROC | October | HLETYS - Terminated flushing procedure after 7 hour as per the interim procedure. Closed the flow to waste valve, reverted alarm statuses and placed chemical pumps in auto. Monitored system to ensure normal operations. | All Water System ROC General | 2025-10-04
ROC | October | MAPS PD7- Cole W on site operating P2/3 in local to move more water from south cell. MAPS PD8- P2 stopped on low pressure switch came in. Notified Cole W | All Water System ROC General | 2025-10-08
ROC | October | QVW12w - Redempto B finished annual calibrations and leaving site. | All Water System ROC General | 2025-10-02
ROC | October | RHMCMD- Placed man/closed to stop water going to VN. | All Water System ROC General | 2025-10-03
ROC | October | KSTP - Raw water turbidity fault alarm, disregard as per SCADA review. | All Water System ROC General | 2025-10-03
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-09
ROC | October | Angelica Chepiga signing out | All Water System ROC General | 2025-10-03
ROC | October | HLETYS- Post injection total Chlorine residual and Post injection combine Chlorine residual lo alarms , quick dip in Chlorine residual after re-chlor system shut off for dip in flow, alarms cleared. | All Water System ROC General | 2025-10-03
ROC | October | RHRSWA - Activated D1 to fill res. | All Water System ROC General | 2025-10-03
ROC | October | QVW12- Alex B onsite for work orders. Will have wells Local off. Testing Cl gas detectors, working on all analyzers, health and safety, flow control valve, and generator test and silicate system. 09:30- Power outage occurred so Alex B running generator. Requested to clear chlorine gas detector alarm and activate duty. NMETIB- Deactivated duty to offset with NMETHW | All Water System ROC General | 2025-10-07
ROC | October | AUPSRR- Will M on site to run generator and test Cl2 leak alarm KCETDS- Yash S replacing network switch. Deactivated duty and Yash S will repoint tags so we don't lose trends 09:45-KCETDS- Yash S notified ROC we will lose comms to tower for 20 mins | All Water System ROC General | 2025-10-07
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-11
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-12
ROC | October | GWTP - Backwash tank 1 level low and low low alarms. Low low alarm returned to normal status immediately after triggering. Reset alarm. Backwash tank 1 low level alarm is under the same circumstances as the previous entry. Reset alarm. Backwash pumps and valves are all in manual off/closed. | All Water System ROC General | 2025-10-14
ROC | October | AURSOH, Activated D1 RHMCMD, Placed Man/open | All Water System ROC General | 2025-10-14
ROC | October | HLW2 - Joe W cleaning injection points. Disregard low pressure alarms. | All Water System ROC General | 2025-10-09
ROC | October | YWS + NYWS NORMAL | All Water System ROC General | 2025-10-15
ROC | October | MKRSEM - Request TO to run 2 pumps | All Water System ROC General | 2025-10-15
ROC | October | Ethan U signing in Weather 19. | All Water System ROC General | 2025-10-14
ROC | October | MKRSEM - Request TO (Mehdi) to drop 2 pumps | All Water System ROC General | 2025-10-16
ROC | October | NMW12- Rick L done on site. | All Water System ROC General | 2025-10-07
ROC | October | GWTP- Raw Water Total Chlorine Res HiHi Alarm. Disregard as per SCADA Report | All Water System ROC General | 2025-10-07
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-07
ROC | October | KCETDS - Deactivated duty in preparation for interim tomorrow | All Water System ROC General | 2025-10-07
ROC | October | NMETIB - Deactivate duty 1 NMVCBA - Revert from 60 to 50L/s NMVCIB - Revert from 50 to 70L/s | All Water System ROC General | 2025-10-14
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-14
ROC | October | NMTKBS-ActivatedD1 AURSBS- Activated D1 | All Water System ROC General | 2025-10-15
ROC | October | GWTP - Stephen B working on UVs, requested disregard UV alarms. | All Water System ROC General | 2025-10-15
ROC | October | SHTP- HLP3/4 Disch vlv fault alarms came in. Notified Benson S. Will clear when done exercising valves STPS48- Booster pumps not availble. Notified Dan Z who is monitoring on site wont be down for much longer than 5 mins AURSBS- Chlorine isolation valves 1/2 failed to open alarm came in. Reset alarm | All Water System ROC General | 2025-10-15
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-08
ROC | October | YWS + NYWS Normal GWTP - ZW1 performance yesterday lolo alarm. Checked site, plant is offline. Called Tyson C who directed to place the filter off for the night. Made necessary changes. #consult | All Water System ROC General | 2025-10-04
ROC | October | ARPS- David from Peel called about potential shutdown during planned maintenance and has place all pumps but P5 in man/off. David said he would call back with further updates but pumps may be able to run during PLC updates. 09:03- ARPS- David from Peel Called back P5 will be shutdown in approximately 7 mins and will update ROC with further changes | All Water System ROC General | 2025-10-06
ROC | October | GWTP- Stephen B on site with contractors for generator maintenance will be disconnected for majority of day. Stephen B will call back when done on site | All Water System ROC General | 2025-10-06
ROC | October | Gluzen Ramos Ong signing out | All Water System ROC General | 2025-10-03
ROC | October | Ethan Ullalkar signing out. | All Water System ROC General | 2025-10-15
ROC | October | STETBR- Tower level lo alarm came in. Tower deep cycling | All Water System ROC General | 2025-10-15
ROC | October | NMW12 - Red B, Parth P, Rick L on site for annual calibration. Well12 pump man/on , running for sampling. Red B will contact Ryan B. | All Water System ROC General | 2025-10-01
ROC | October | AURSBS - Sample pump 1 and sample pump 2 uncommanded stop alarm. Checked site, chemical pumps have interlocked and sample pumps that run in manual mode have shut down. Possible power blip scenario as AUSSYS had a power fail alarm. Contacted Divya P to discuss the procedure for re-starting the chemical system. Divya P directed to place the chemical pumps manual/off and then re-start the sample pumps. Made the changes, no obvious issues with the post and pre injection chemical readings. Divya P directed to monitor the system for ten minutes and if there is no observable issues then the chemical pumps can be placed in auto. #consult | All Water System ROC General | 2025-10-03
ROC | October | SHTP- Filter 3 turbidity hi alarm came in after filter 2 backwash reset as per shift report | All Water System ROC General | 2025-10-01
ROC | October | GWTP - Stephen B called to inform he has completed his pump testing. Stephen directed to place the train 8 reject valve in auto mode and initiate a train 8 backwash. Made the necessary changes. | All Water System ROC General | 2025-10-02
ROC | October | ANW23 - Res level LoLo, lockout HLP resulting in discharge pressure lolo. Wells have been off in preparation for step test. Notified Cole W., he is heading to site | All Water System ROC General | 2025-10-03
ROC | October | Carter D signing out | All Water System ROC General | 2025-10-06
ROC | October | GWTP - Chris S finished his work and has cleared all alarms. KSTP - Donald M finished work on site and is leaving KSTP is normal operations. | All Water System ROC General | 2025-10-02
ROC | October | GWTP- Chlorine Pump 1, 2 Not Available Alarm. Stephen B is looking into it. | All Water System ROC General | 2025-10-02
ROC | October | YWS+NYWS normal | All Water System ROC General | 2025-10-01
ROC | October | NMW136- Treated Total/ Combined Cl2 lo alarm came in. Quick dip in trends recovered in 3 mins cleared alarm | All Water System ROC General | 2025-10-01
ROC | October | STW3- Station turbidity alarm came in. Well is in man/off no water directed to users NMTKBS- Free Cl2 residuals returned to normal reset outstanding hihi alarm | All Water System ROC General | 2025-10-01
ROC | October | QVW12- Redempto B onsite for annual calibrations. Requested wells man/off. Notified Divya P. requested to also place QVW34 in manual and activated duty. | All Water System ROC General | 2025-10-02
ROC | October | NMVCPL - Noted higher than normal flows through Poppy Lane valve during the fill cycle of NMETIB. Will monitor site to determine if SCADA will remedy the flow. | All Water System ROC General | 2025-10-04
ROC | October | HLETYS - Post injection combined chlorine hi alarm. Checked site, operations are normal. Shift report states that chemical adjustments may be needed as the tower fills. Increased hypo pump 1 max flow from 95 to 97 and monitored system. | All Water System ROC General | 2025-10-05
ROC | October | HLETYS - post injection combined chlorine hi alarm returned. Increased hypo pump 1 max flow from 97 to 100 as per shift report. | All Water System ROC General | 2025-10-05
ROC | October | VNPSCD - Sani Sump Pump 1, 2 fault alarms came in. Will send an email to central team as per shift report NMW136 - Well 16 Forward Flow Fault alarm came in. Checked site. NMTKKC duty just activated. Informed Divya P. who will take a look #CONSULT | All Water System ROC General | 2025-10-05
ROC | October | MAPS - Jordan B on site for a generator test. | All Water System ROC General | 2025-10-02
ROC | October | VNRSKS - Activated duty to help move water from MARS | All Water System ROC General | 2025-10-10
ROC | October | STW12 - Hypo tank 1 & 2 level hihi. Disregard as per Travis W. Rotate hypo pump 2 duty 1. Rotate silicate pump 2 to duty 1 | All Water System ROC General | 2025-10-10
ROC | October | HLW2 - Yash S working on APN, adjusting radio. | All Water System ROC General | 2025-10-01
ROC | October | QVW12- Influent free Cl2 lo alarm came in. Looks like sudden drop as bank 2 cylinder emptied adjusted chlorinator 2 dosing factor 108 to 110%. Continued to monitor cleared after influent free Cl2 recovered | All Water System ROC General | 2025-10-14
ROC | October | AUMCBS - Flowmeter Fault Alarm came in. Checked site and found that trends are populating and is reading levels passing the flowmeter. Alarm cleared. 16:00 - Checked site and found that the levels have not been populating and alarm is outstanding. Called Rob P. who will take a look 16:37 - Checked Alectra outage map and found that there are none reported. Called Alectra Utilities and spoke to Thomas who informed there are no outages shown in the area. Called Rob P. who is headed to site. CMU5 Created W11336112 18:00 - Rob P. called back to inform that there were no issues found on his end and that there is a beeping coming form the PCS control panel. Called Artour L. who indicated the beeping is likely from the alarm being active and to contact instrumentation. Called Redempto B. who will look into this #CONSULT #CMU5 | All Water System ROC General | 2025-10-05
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-05
ROC | October | HLPSYS- Alex B onsite for generator run and low temp alarm test. | All Water System ROC General | 2025-10-02
ROC | October | YWS + NYWS Normal Connor Smith signing out | All Water System ROC General | 2025-10-02
ROC | October | GWTP- Stephen B called. Maintenance is onsite working on train 1. Disregard all alarms from train 1. | All Water System ROC General | 2025-10-08
ROC | October | STPS48 - Dan Z and Travis W leaving site. | All Water System ROC General | 2025-10-15
ROC | October | RHVCEM - Increase to 75% | All Water System ROC General | 2025-10-15
ROC | October | NBW3 - Influent free lolo. Locked out well on startup. Reading came back in range and able to reset | All Water System ROC General | 2025-10-15
ROC | October | NMTKKC- Joe D finished onsite. | All Water System ROC General | 2025-10-02
ROC | October | KSETWB- Dan B onsite testing Cl leak sensor | All Water System ROC General | 2025-10-03
ROC | October | NRETBR- Yash S working on OIT disregard historian heartbeat alarm until done 14:02- NRETBR- Yash S done working on OIT | All Water System ROC General | 2025-10-14
ROC | October | NMETIB- Parth P and Ric L onsite for annual calibrations. | All Water System ROC General | 2025-10-09
ROC | October | NMTKBS - Leaving duty 1 running as per Jason G, beginning fire flow testing NMPSKC - Place pump 1-6 man/off for fire flow testing and close FCV1 valve as per Jason G 10:05 - Fire flow testing complete. Jason G finished at site. Place NMPSKC pumps/valve back in auto | All Water System ROC General | 2025-10-10
ROC | October | NMETIB- Activated duty | All Water System ROC General | 2025-10-01
ROC | October | NMTKBS- Free Cl2 hihi alarm cleared RHRSWA- Deactivated D1 | All Water System ROC General | 2025-10-02
ROC | October | ANW23- Activated reservoir duty as per interim | All Water System ROC General | 2025-10-02
ROC | October | NBW5 - Turbidity hi. Rotated silicate pump 1 to duty 1 KSTP - Filter 1 backwash OOS. Informed Stephen B, placed highlifts man/off. KSTP - Fin water flouride res fault. Disregard as plant is off Consult | All Water System ROC General | 2025-10-15
ROC | October | AURSOH - Activate duty 1 AUW5 - Place well in man/on | All Water System ROC General | 2025-10-15
ROC | October | YWS + NYWS Normal NMVCBA - Place back in auto | All Water System ROC General | 2025-10-16
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-01
ROC | October | VNPSCD, Jacob M/Jordan B is finished on site | All Water System ROC General | 2025-10-06
ROC | October | STRS48- Patrick F onsite for Cl leak test. Will then be heading to BLW3 for work orders | All Water System ROC General | 2025-10-07
ROC | October | HLETYS - Stop flushing procedure as per interim. Close waste valve and place chem pumps back in auto MARS - Stop maple to JFRS feed. | All Water System ROC General | 2025-10-15
ROC | October | MTETNL- Site Power Failure Alarm. Patrick F will go to site to hook up generator. | All Water System ROC General | 2025-10-02
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-02
ROC | October | Christian Van Beek signing out. | All Water System ROC General | 2025-10-02
ROC | October | BVPS- Jack P finished onsite. Placed pumps back into auto. | All Water System ROC General | 2025-10-03
ROC | October | MAPS- Artour L working on local server. Disregard Comm alarms. | All Water System ROC General | 2025-10-03
ROC | October | NMPSKC- Ryan B on site for flow testing will be running pumps | All Water System ROC General | 2025-10-06
ROC | October | GWTP- Phil D onsite working on SO2 leak detection and Cl leak detection. | All Water System ROC General | 2025-10-07
ROC | October | NRETBR - Ryan B on site to complete work orders including chlorine analyzer maintenance, valve exercising, JHSC checks, PRV inspection and low temperature alarm test. Directed to disregard associated alarms. | All Water System ROC General | 2025-10-02
ROC | October | QVW12- Divya P called. Maintenance is working on ejectors. He will run wells once completed. QVETQS- Divya P performing PMs. Hi/Lo level, deplox and temp alarms. | All Water System ROC General | 2025-10-03
ROC | October | YWS + NYWS Normal Carter Dunn Signing Out | All Water System ROC General | 2025-10-09
ROC | October | BLW3 - Dan Z requested well 3 pump man/off. | All Water System ROC General | 2025-10-09
ROC | October | NBW5 - well 5 pump man/off due to turbidity issues. | All Water System ROC General | 2025-10-09
ROC | October | Connor Smith signing in 16C Cloudy | All Water System ROC General | 2025-10-11
ROC | October | MARS- Cole W called. Work is complete. Called OCWA (David) and requested back to normal pumping | All Water System ROC General | 2025-10-08
ROC | October | MTW12. Station Turbidity Fault/Well 1 and 2 Pump OOS Alarm, MTETNL was draining, close to D1 start, Activated D1 to start filling the tower early. 04:10, While monitoring the site, the towers outlet flow skyrocketed with the pressure also dropping. Since MTW2 is currently interlocked due to the Turbidity fault, ROC notified Phil D. Phil will be heading to site to get well 2 back in operation. After calling Phil D, ROC contacted East Gwillimbury after hour staff Lyn and notified her of the possible main break in EGs system, she will be contacting their operators to inform them of this information 04:27. Sarah from EG called informing the ROC that they are out in the area doing maint/high velocity flushing and this is the reason why the tower outlet skyrocketed so fast. Sarah/EG will be out still doing flushing but they will be reducing the flow. Notified Sarah to call the ROC before flushing happens so YR can be aware of future flushings in the system. Contacted Phil D on what is happening, he isn't worried, will be heading back home CMU5: W11350027 EG Operator Sarah: 9057154398 | All Water System ROC General | 2025-10-09
ROC | October | NMTKBS- Joe D on site for sampling req P3 placed in man/off to allow tank to drain. Placed P3 at AUPSOH in man/off | All Water System ROC General | 2025-10-14
ROC | October | SHTP- Filter 2/3 turbidity hi alarm came in as filter 1 finished backwash sequence. Reset as per shift report. UV transmittance lo alarm came in. Notified Benson S. Will have some one from west water team investigate. EGMCRW- Parth P and Rick L on site for calibrations BLW12- Influent free Cl2 lo alarm came in cleared after 3 mins trends recovered | All Water System ROC General | 2025-10-14
ROC | October | QVW34 - Influent free chlorine lolo switch, well interlocked. Reading came back to normal. Place well back in auto NMETIB - Deactivate duty 1 | All Water System ROC General | 2025-10-04
ROC | October | Angelica Chepiga signing out | All Water System ROC General | 2025-10-09
ROC | October | NBW5 - Turbidity alarm cleared. Placed well 5 pump back to auto. Will monitor and notify area. | All Water System ROC General | 2025-10-10
ROC | October | RHRSWA - Confirmed with Dwayne L Eglin Mills work is complete. Revert site back to normal placing pumps 1-4 back in auto. Leaving in combined mode 50% | All Water System ROC General | 2025-10-10
ROC | October | Angelica Chepiga signing out | All Water System ROC General | 2025-10-10
ROC | October | Angelica Chepiga signing out | All Water System ROC General | 2025-10-01
ROC | October | BLW3- Ric L onsite working on Chlorinator 1. Placed well in manual. | All Water System ROC General | 2025-10-09
ROC | October | NMW136 - Jason G cleaning chlorine analyzers, cleaning injection points. | All Water System ROC General | 2025-10-15
ROC | October | MAPS PD7- Placed P2/3 in manual and stopped P2. VNPS PD7- Activated D2 to test if P2 will run in D2 if VNPS D1 pumps are man/off P2 started up okay. VNRSKS- Deactivated D2 MAPS PD7- Placed P2/3 in auto BVPS- Placed P1 in manual. as Rob P is on site for isolation NMW136- Parth P and Rick L on site for calibrations. Wells are man/off | All Water System ROC General | 2025-10-15
ROC | October | MAPS- PD7 Suction header valve Pit High level alarm. David T will attend site. #CMU 5 W11356705 | All Water System ROC General | 2025-10-10
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-11
ROC | October | Adeela Khan signing out | All Water System ROC General | 2025-10-11
ROC | October | RHMCMD, Placed valve man/closed | All Water System ROC General | 2025-10-13
ROC | October | HLETYS, TWR_AIT2 has not triggered the hi alarm after 7 hours of flushing, notified David T as per interim procedure, directed to revert the tower back to normal operations consult | All Water System ROC General | 2025-10-13
ROC | October | YWS + NYWS Normal GWTP, ZW4 Shutdown, Pat F currently on site and will deal with it | All Water System ROC General | 2025-10-13
ROC | October | Adam Button signing out | All Water System ROC General | 2025-10-15
ROC | October | RHVSEM - Close to 15% | All Water System ROC General | 2025-10-16
ROC | October | BLW3- Dan Z has well man/off and flushing contact tank 2 with distribution water. Heading to BLETNL to sample and will be back on site later to revert changes GWTP- Stephen B on site req call out to PCS oncall for UPS beeping in network room. Notified Artour L who will go to site when done at KSTP | All Water System ROC General | 2025-10-14
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-04
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-04
ROC | October | YWS+NYWS normal | All Water System ROC General | 2025-10-02
ROC | October | NMTKBS- Free Cl2 hihi alarm came in Disregard as per Divya P. Combined Cl2 residual okay on site and free residual at upstream storage AUPSOH has been within normal range for duration of fill cyle | All Water System ROC General | 2025-10-01
ROC | October | SHTP- Filter 2 Post rinse NIT hi alarm came in. Notified Cole W. Directed to enable backwash on filter 2 and clear alarm #consult | All Water System ROC General | 2025-10-02
ROC | October | GWTP- Low lift P2 hydraulic valve faile to open. Notified Tyson C. Directed to place low lift P1 in D1 and P4 in D2. SHTP- Filter 3 turbidity hi alarm came in after filter backwash. Reset as per shift report #consult | All Water System ROC General | 2025-10-02
ROC | October | NMTKKC - Joe D finished and leaving site. Operations normal | All Water System ROC General | 2025-10-02
ROC | October | AUW5 - Place well back in auto | All Water System ROC General | 2025-10-16
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-16
ROC | October | HLW2, Downstream Pressure hihi alarm, Placed Sharon VC in man/closed to deal with the pressure issues | All Water System ROC General | 2025-10-13
ROC | October | AUETFC- Jerry Z deep cycling. Disregard Low Level alarm. | All Water System ROC General | 2025-10-07
ROC | October | HLETYS- Pre injection Cl2 lo alarm came in. Placed all chemical pumps in man/off. Enabled tower inlet hi/lo flow alarms. Enabled Pre injection total Cl2 hi alarm. Opened MV1 in man at 30% as per interim. inlet tower flow hi alarm triggered. Opened MV1 to 40% continued to monitor | All Water System ROC General | 2025-10-07
ROC | October | NMTKKC- Joe D onsite cleaning analyzers and chemscan. Disregard chemscan offline alarm. Will have chemical pumps man/off. Will also be testing temp and eyewash alarms. Requested to adjust duty stop from 75 to 80%. | All Water System ROC General | 2025-10-09
ROC | October | MKRSMR - Called Toronto Water (Paul) and requested a pump on at reservoir to help top up reservoir, in preparation for the FJ Horgan WTP planned shutdown this morning, as per interim procedure | All Water System ROC General | 2025-10-08
ROC | October | STW12 & STW3 - Place wells in man/off position as per interim | All Water System ROC General | 2025-10-04
ROC | October | STETTL/STPSTL, Activated D1 so both towers can fill | All Water System ROC General | 2025-10-06
ROC | October | HLETYS- Pre-Injection Combined Chlorine Lo Alarm. Cole W will start flushing procedure. | All Water System ROC General | 2025-10-09
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-09
ROC | October | RHMCMD - Noticed levels going towards MARS. Placed valve man/closed to conserve water at RHRSTR | All Water System ROC General | 2025-10-09
ROC | October | BLW12- Joe M running generator, cleaning chlorine analyzers. | All Water System ROC General | 2025-10-15
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-13
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-05
ROC | October | KSTP- Donald M on site to wrok on Cl2 and turbidity analyzers | All Water System ROC General | 2025-10-07
ROC | October | MARS- Mehdi from Metro called and has stopped pump to reservoir. AURSBS- Deactivated D1 | All Water System ROC General | 2025-10-15
ROC | October | Christian Van Beek signing in. Weather: 15C and clear. | All Water System ROC General | 2025-10-13
ROC | October | BLW12 - Generator running. Enough diesel for the night, no outage on Hydro One. Will monitor 23:42 - Hydro One outage map shows restoration time to be 2:15. Will monitor | All Water System ROC General | 2025-10-15
ROC | October | NMETIB/NMETHW - Placed NMVCBA at 80 L/s and NMVCIB at 40 L/s, as per interim | All Water System ROC General | 2025-10-11
ROC | October | RHPSWA - man/stop pumps 1 and 2. | All Water System ROC General | 2025-10-15
ROC | October | Carter Dunn Signing Out | All Water System ROC General | 2025-10-14
ROC | October | VNPSAP, VNETAG, VNETFD - Comm fail alarms in and out. Notified Artour L., will check SCADA. 16:00 Artour L requested disregard alarms until he calls back. ETA 5 PM. # CMU5 W11356713 | All Water System ROC General | 2025-10-10
ROC | October | NMETHW- Deactivated duty to offset with NEMTIB | All Water System ROC General | 2025-10-10
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-12
ROC | October | ANW23, Parth P/Rick L finished on site | All Water System ROC General | 2025-10-14
ROC | October | NMETIB- Deactivated D1 to offset from NMETHW as per shift report YWS+NYWS normal | All Water System ROC General | 2025-10-01
ROC | October | QVW12- Treated Free Cl2 hihi/switch and combined Cl2 lo alarm came in wells not active and no water directed to users. Continued to monitor trends recovered and cleared after 3 mins MKRSEM- Called Metro spoke with Paul to stop pumping to reservoir | All Water System ROC General | 2025-10-02
ROC | October | SHTP- Filter 2 turbidity hi alarm , Filter 2 backwashing. | All Water System ROC General | 2025-10-02
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-04
ROC | October | MARS- Cole W on site has south cell inlet closed ARPS- David from Peel called back. and placed all pumps in man/off and use south cell LIT as duty control | All Water System ROC General | 2025-10-08
ROC | October | SHTP- Benson S and Jacob M onsite for UV work, valve exercising, hi/low temp and turbidimeter maintenance. | All Water System ROC General | 2025-10-09
ROC | October | HLETYS - Yash S and Artour L replacing cellular antenna, no COMM fails expected. | All Water System ROC General | 2025-10-09
ROC | October | STW3- Travis W onsite for maintenance on chlorine and turbidity system as well as performing chemical system flush. | All Water System ROC General | 2025-10-09
ROC | October | HLW2 VC FCV2 - Adjusted valve to 20% | All Water System ROC General | 2025-10-09
ROC | October | MKRSEM-Reservoir 1 level lo alarm came in. Called Metro and spoke with Peter to start 2 pumps | All Water System ROC General | 2025-10-01
ROC | October | GWTP- MIT ZW1 High Pressure 3.32KPa, Low Pressure 1.87KPa. Both passed. Stephen B requested to place train back into service. | All Water System ROC General | 2025-10-03
ROC | October | SHTP- Air Compressor 1 Fault Alarm. Benson S and Tim H are working on it. | All Water System ROC General | 2025-10-07
ROC | October | GWTP- Low lift P3 control valve close alarm. LLP3 in standby and plant should not start up until normal operating hours. Emailed East water team about outstanding alarm. | All Water System ROC General | 2025-10-02
ROC | October | YWS + NYWS NORMAL | All Water System ROC General | 2025-10-03
ROC | October | VNPS PD7 - Man/start Pump 2. RHVCEM - Adjusted to 50%. | All Water System ROC General | 2025-10-03
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-03
ROC | October | NRETBR- Yash S on site for network switch replacement. Not controlling tower. Will lose comms on site. Yash S will contact Central team about work | All Water System ROC General | 2025-10-07
ROC | October | Ethan Ullalkar signing out. | All Water System ROC General | 2025-10-06
ROC | October | RHPSPA - Jack P on site with a contractor to complete work on the generator system. Jack stated that he will be running the generator off load and the ROC can expect to see a generator running and a generator not in auto alarms. | All Water System ROC General | 2025-10-02
ROC | October | VNPS- Jacob M onsite for generator run and working on Cl analyzers. | All Water System ROC General | 2025-10-07
ROC | October | Adam Button signing out | All Water System ROC General | 2025-10-14
ROC | October | NRETCR - Deactivate duty 1 | All Water System ROC General | 2025-10-14
ROC | October | HLETPR - Yash S was working on APN/Radio. Completed work, leaving site. | All Water System ROC General | 2025-10-01
ROC | October | GWTP - ZW8 not all devices in auto mode. Stephen B called to inform he is completing pump testing and that all alarms associated with ZW8 can be disregarded. | All Water System ROC General | 2025-10-02
ROC | October | QVW12- Joe D still on site monitoring influent free Cl2 residual as he switched over to cylinder bank 2. Influent free hihi came in as a result | All Water System ROC General | 2025-10-08
ROC | October | QVW12 - Joe D called and directed to placed QVW2 manual/off for the night when the current fill cycle of NMETHW ends due to low chlorine tank levels. | All Water System ROC General | 2025-10-13
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-13
ROC | October | NMETHW - Deactivated duty 1 while NMETIB fills. QVW34 - Deactivated QVW3. | All Water System ROC General | 2025-10-13
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-14
ROC | October | Carter Dunn Signing In | All Water System ROC General | 2025-10-06
ROC | October | SHTP- Filter 1/3 turbidity hi alarm came in after filter 2 backwash sequence completed. Notified Cole W. directed to reset as turbidity in both filters recovered #consult | All Water System ROC General | 2025-10-06
ROC | October | MKRSEM - Noticed both pumps not running. Followed up with TO (Paul). Confirmed they experienced power issues resulting in loss of pumps. In the process of getting them back and will notify with updates | All Water System ROC General | 2025-10-06
ROC | October | GWTP- Stephen B running generator. | All Water System ROC General | 2025-10-02
ROC | October | GWTP - Chris S on site for a low lift valve alarm test. RHPSPA - Sean P on site to complete work on the valves, will be running and shutting down pumps as needed. | All Water System ROC General | 2025-10-02
ROC | October | QVW34 - Activated well 3 in manual mode to provide additional supply to the system and push flow south across ringwell drive. | All Water System ROC General | 2025-10-02
ROC | October | STW12 - Tyson C finished on site, Hypo pump 2 man/of for the night. GWTP - Z4 M-Clean Insufficient chemical alarm, Tyson C requested disregard. | All Water System ROC General | 2025-10-02
ROC | October | NMETIB - Combined chlorine hi, total chlorine hihi. Readings are rising and holding at high level. Informed Divya P of situation, will take a look on SCADA Consult 22:19 - Divya P called back, okay to disregard hihi combined/total while filling, will call back if hihi persists when draining | All Water System ROC General | 2025-10-06
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-07
ROC | October | NMETIB- Combined Chlorine HiHi Alarm. Notified Divya P. He is almost onsite. CONSULT | All Water System ROC General | 2025-10-07
ROC | October | KCETDS- Yash S onsite to replace network switch. Will call back when beginning to confirm if pumps will need to be shut down for work. | All Water System ROC General | 2025-10-07
ROC | October | GWTP- Ernie H onsite for generator load test. | All Water System ROC General | 2025-10-07
ROC | October | NBW3- Influent Free Chlorine LoLo. Interlocked well. 07:40- Residual recovered, Ops reset alarms. | All Water System ROC General | 2025-10-07
ROC | October | AUMCBS- Red B working on flow meter. | All Water System ROC General | 2025-10-07
ROC | October | STW3 - Influent Free Chlorine Lo alarm came in. Well is man/off and water is not being directed to users | All Water System ROC General | 2025-10-08
ROC | October | MKRSEM - Building Flood Alarm came in. Checked site and shift report. Disregarded as per shift report and will send an email to east water | All Water System ROC General | 2025-10-08
ROC | October | VNETAG- Historian heartbeat alarm came notified Artour L. Will take a look | All Water System ROC General | 2025-10-08
ROC | October | Connor Smith signing out | All Water System ROC General | 2025-10-08
ROC | October | STPSMR, Gas Detector hihi/Chlorine Emerg System Active Alarm, Duty is currently active, contacted Joe M, but no response, will call again in 5 minutes 23:00, STETBR, Deactivated D1 23:02, Contacted Phil D as he is covering for East on call at this time (no email was sent about this), Phil D is heading to site, requested Joe D assistance as it is a Cl2 leak. Contacted and notified Joe D, he will give Phil D a call and will head to site. Oct 9 @ 00:56, Phil D/Joe D are finished on site CMU5: W11349798 (Phil D) CMU5: W11349805 (Joe D) | All Water System ROC General | 2025-10-08
ROC | October | GWTP, Low Lift Drainage Pump 1 Overload Alarm, Notified Phil D, directed to disregard at this time. consult | All Water System ROC General | 2025-10-09
ROC | October | RHRSTR- Changed Lo level alarm from 58 to 66% to trigger before BVPS activate as trying not to run due to Horgan Shutdown. | All Water System ROC General | 2025-10-09
ROC | October | AUETFC - Tower % Height Low alarm, Duty is active , two pumps assigned to Duty 1, pumps not running. Placed pump 5 man/off, pump 4 man/on . Reassign pumps duty. P4 to D1, P5 to D2. Notified William M. He is at AUPSWS , will check. 14:00 AUETFC - Deactivated Duty 1 and activated again. Placed pumps 4 and 5 back to auto. Cleared Low level alarm. System back to normal. | All Water System ROC General | 2025-10-09
ROC | October | MKRSEM - Called Toronto Water (Mehdi) and requested they deactivate the pumps pushing flow to MKRSEM. | All Water System ROC General | 2025-10-14
ROC | October | AURSBS - Activated duty 1 to drawdown MARS. | All Water System ROC General | 2025-10-14
ROC | October | Adam Button signing out | All Water System ROC General | 2025-10-02
ROC | October | Christian Van Beek signing in. | All Water System ROC General | 2025-10-02
ROC | October | RHVCMM - man/closed to promote drawdown of RHRSWA, level holding with 1 pump man/on at RHPSPA. RHPSPA - placed P2-4 man/off to prevent additional pumps running in duty due to hi discharge pressure during linear work. Will email affected ops of above changes | All Water System ROC General | 2025-10-03
ROC | October | NMETIB - Inlet flow hi alarm. Checked site, inlet flow is reading high. NMVCBA is opened much more than it should be resulting in higher flow into NMETIB. Placed valve manual closed. Will monitor system to ensure that NMETIB is still filling with valve closed. | All Water System ROC General | 2025-10-04
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-05
ROC | October | VNPSAP, VNETAG, VNETFD- Called Artour L regarding outstanding comm fails. Requested to try and clear alarms but said they make come back in due to repairs in fiber line being performed with estimated time of 0200 20:01- Alarms came back in and interlocked VNPSAP pump with duty active. Tower still filling through valve. Sites are still trending. 20:09- Artour L called back. Evgeny S is looking into it. 21:16- Artour L rebooted and cleared alarms. Sites back to normal. 21:24- Alarms came back in. Notified Artour L. They will continue to look into it. 21:50- Artour L called with an update that nothing else can be done about outstanding comms at this time. Will have to monitor and wait for repairs to be made. W11356750 CMU5 | All Water System ROC General | 2025-10-10
ROC | October | JDSS- Drew from Ferguson Electric is on site **WRONG BOOK** | All Water System ROC General | 2025-10-08
ROC | October | QVW12- Placed P1 in man/off 12:49- QVW12- Placed P1 auto | All Water System ROC General | 2025-10-07
ROC | October | YWS + NYWS NORMAL | All Water System ROC General | 2025-10-09
ROC | October | Connor Smith signing in 10C Clear | All Water System ROC General | 2025-10-08
ROC | October | 12:10 HLW2 - Joe W cleaning chlorine analyzers. | All Water System ROC General | 2025-10-09
ROC | October | BVPS - Called Toronto Water (Brett) for an update. Brett informed that levels are going up slowly but dropping fast at millikin (MKRSEM). Requested the second pump back on at BVPS due to PD9 being active. Brett agreed and will place pump back on shortly. If levels on Toronto Water's end becomes too low, will call give the ROC a call back. Placed pump 3 back on at BVPS to help fill reservoir 01:11 - Called Brett back to inform that the second pump at BVPS has been dropped again due to the shutdown escalating 02:00 - Placed second pump man/off at BVPS as per Jeremy H | All Water System ROC General | 2025-10-10
ROC | October | HLETYS - Post Injection Combine and Total chlorine residual Low and slowly dropping. Only Hypo pump 2 available, Hypo pump 1 man/off, Notified Cole W. Requested Decrease Hypo pump 2 Max flow from 172 to 150 mL/min. Alarms cleared. # Consult | All Water System ROC General | 2025-10-02
ROC | October | STW12 - Placed wells man/on, as per interim procedure | All Water System ROC General | 2025-10-05
ROC | October | MKVCSA - PAC Communication Failure Alarm came in. Waiting 20 mins but site did not come back. Called Artour L. who will take a look 10:29 - Artour L. called back to inform that site is back up and running. Checked site and trending is back #CONSULT | All Water System ROC General | 2025-10-05
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-05
ROC | October | HLETYS - Pre-injection combined chlorine lo. Been dropping since duty activated. Dropped hypo pump 1 max flow dosing back down to 105mL/min. Will monitor residual. This increased post-injection combined going hi due to drop in dosing 23:33 - Begin flushing, man/stop chem pumps and open waste valve as per interim | All Water System ROC General | 2025-10-05
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-11
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-12
ROC | October | EGMCRW, Parth P/Rick L is finished on site | All Water System ROC General | 2025-10-14
ROC | October | QVW12- Influent free Cl2 hi alarm came in looks like influent was dropping for last hour with no alarm triggered. Chlorinator adjusted accordingly causing spike slowly recovering. Continued to monitor. Cleared after 22 mins SHTP- Well 2 uncommanded start alarm came in. Well 2 was not running but was before alarm came in. Well 3 started up in its place. Reset alarm. 01:53- QVW12- Effluent free Cl2 hi alarm as a result of influent spike. continued to monitor. Cleared alarm after trends recovered 02:01-KLMCHR- PAC com failure alarm came in. cleared upon acknowledgment | All Water System ROC General | 2025-10-01
ROC | October | ANW23- RSVR inlet free Cl2 lo alarm came in. Checked trends quick dip and recovered. Reset alarm hypo system running okay | All Water System ROC General | 2025-10-01
ROC | October | GWTP- Sutton header fluoride lo alarm came in. Notified Stephen B. Directed to activate D1 at SUETDR | All Water System ROC General | 2025-10-08
ROC | October | MKRSEM - Request TO (Zoran) to drop both pumps | All Water System ROC General | 2025-10-06
ROC | October | MKRSEM- Dan Z onsite for chlorine analyzer maintenance. | All Water System ROC General | 2025-10-07
ROC | October | NBW37- Tim H onsite working on all analyzers, chemical system, temp alarms, prv, and running diesel generator in the afternoon. | All Water System ROC General | 2025-10-02
ROC | October | MAPS PD8 - Jordan B stated that alarms can be cleared and all MAPS PD8 pumps placed in auto mode. Made necessary changes. | All Water System ROC General | 2025-10-02
ROC | October | HLETYS- Alex B onsite troubleshooting hypo pumps. | All Water System ROC General | 2025-10-03
ROC | October | SHTP- Well 2 pump uncomm start alarm. Well is off reset alarm | All Water System ROC General | 2025-10-08
ROC | October | RHRSWA - Dwayne L. informed Linear team to valve that will likely result in decreased flows from RHPSPA to RHRSWA as a result of ongoing work at Elgin Mills WM break. Made the following changes and emailed Jason G., Divya P., Dwayne L., Rob P., Cole W., and ROC: RHRSWA ? Hi level adjusted from 95% to 90%. RHPSPA - Duty 1 stop adjusted from 86 to 80%. Duty 2 stop adjusted from 80 to 75%. Placed P4 in D4 at RHPSPA to avoid a third pump running if D2 activated. | All Water System ROC General | 2025-10-02
ROC | October | HLETYS- Post Injection Combine Chlorine Low and Total Chlorine Low alarms. Adjusted Hypo pump 2 Max flow from 145 to 140 mL/min to increase chlorine residual. | All Water System ROC General | 2025-10-03
ROC | October | MKRSEM - Requested Toronto water(Peter) stop filling Res. | All Water System ROC General | 2025-10-03
ROC | October | YWS + NYWS NORMAL | All Water System ROC General | 2025-10-03
ROC | October | MAPS PD7 - Placed Pumps 4 &3 man/off. | All Water System ROC General | 2025-10-03
ROC | October | HLETYS - Pre-injection combined chlorine lo. Lowered hypo pump 1 max flow from 105mL/min to 95mL/min to help achieve increase dose to achieve target. Will monitor 14:15 - Pre-injection combined chlorine continues to drop. Preceded with flushing at tower, man/stop chemical pumps, opening waste flow valve to 25%, enabling hi/lo flow alarms on inlet/outlet, and enable tower total chlorine residual hi alarm. Email sent to team/area | All Water System ROC General | 2025-10-04
ROC | October | STETTL- Town of Stouffville called and will be flushing in zone 2 for the next hour. | All Water System ROC General | 2025-10-08
ROC | October | YWS+NYWS normal Adam Button signing out | All Water System ROC General | 2025-10-08
ROC | October | YWS+NYWS normal GWTP- Low lift P3 uncommanded stop alarm came in reset as per Dan Z | All Water System ROC General | 2025-10-01
ROC | October | QVW12- Influent free Cl2 hihi alarm came in. Trends recovered right away and cleared after 3 mins | All Water System ROC General | 2025-10-01
ROC | October | NMW12 - Treated Total/Combined Cl2 lo alarm, duty not active, will continue to monitor. | All Water System ROC General | 2025-10-03
ROC | October | YWS + NYWS NORMAL | All Water System ROC General | 2025-10-03
ROC | October | MKRSEM - Called Toronto Water (Brett) and requested two pumps on at reservoir as levels are low | All Water System ROC General | 2025-10-05
ROC | October | BLW3- Placed well back in auto as per Dan Z | All Water System ROC General | 2025-10-14
ROC | October | SHETCS - Post injection total chlorine residual hihi alarm. Checked site, tower is filling regulatory relief applies. The Hypo pumps have deactivated. Cleared alarms once the chlorine residual reading dropped. | All Water System ROC General | 2025-10-02
ROC | October | MKRSEM- Called Toronto and requested two pumps on. | All Water System ROC General | 2025-10-03
ROC | October | Connor Smith signing in 16C Cloudy | All Water System ROC General | 2025-10-10
ROC | October | MAPS/JFRS- Initiated Maple to Jefferson feed. | All Water System ROC General | 2025-10-10
ROC | October | MKRSMR- Peter from Toronto called and requested to stop pumping early (4.5m) | All Water System ROC General | 2025-10-11
ROC | October | RHPSPA - Pump 4 running in manual mode, disabled pumps duty rotation. | All Water System ROC General | 2025-10-01
ROC | October | GWTP- Joe M onsite working on low lift pump 2. Can also disregard ZW1 and ZW2 not in auto alarms. | All Water System ROC General | 2025-10-01
ROC | October | Adam Button signing out 14C clear | All Water System ROC General | 2025-10-06
ROC | October | QVW12- Placed well 2 in man/off to avoid QVETQS hi alarm and continue to fill NMETHW | All Water System ROC General | 2025-10-01
ROC | October | NMVCBA- Change flow setpoints from 80L/s to 40L/s NMVCIB- Changed flow setpoints from 40L/s to 80L/s NMETIB- Deactivated D1 to offset from NMETHW as per shift report | All Water System ROC General | 2025-10-01
ROC | October | MKRSEM- Called Metro spoke with Brett to stop pumps filling reservoir KSETDP- Inlet total and free Cl2 hihi alarms came in on D1 deactivation. Disregard on shift report HLW1- Combined Cl2 lo alarm came in recovered after 3 mins cleared alarm | All Water System ROC General | 2025-10-01
ROC | October | YWS+NYWS normal Adam Button signing out | All Water System ROC General | 2025-10-01
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-11
ROC | October | QVW3 - Activated well to help increase flow entering NMETHW, as per interim | All Water System ROC General | 2025-10-11
ROC | October | Carter Dunn Signing In, 10D/Clear | All Water System ROC General | 2025-10-13
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-13
ROC | October | STW3- Travis W called and req. place well man/off | All Water System ROC General | 2025-10-01
ROC | October | MKRSEM - Request To (Paul) to put on 2 pumps | All Water System ROC General | 2025-10-06
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-06
ROC | October | STRS48- Travis W on site req high lifts man/off for work. Placed P1/2 in man/off for generator run RHRSTR- Activated D1 | All Water System ROC General | 2025-10-07
ROC | October | Young and Major Mack, CMU5 made for Harsh and Jon for the work they did on October 11 @ 2AM CMU5: W11364792 | All Water System ROC General | 2025-10-14
ROC | October | MAPSN1- Artour L restarting server. RHMCEM- Changed valve set point from 55% to 15% and reverted to split mode | All Water System ROC General | 2025-10-14
ROC | October | NMTKKC- Joe D onsite for work orders. Running generator, hi low temp and health and safety. NMTKBS- Free Chlorine Hi Alarm. Notified Joe D. He will take a look. | All Water System ROC General | 2025-10-02
ROC | October | NMW136 - Station turbidity hi alarm. Checked site, trending shows gradual increase of the turbidity reading. Rotated silicate pump duty to pump 1. NMW12 - Station turbidity hi alarm. Checked site, trending shows the turbidity reading is high but stable. Will monitor site. | All Water System ROC General | 2025-10-04
ROC | October | MARS- Jacob M finished onsite. | All Water System ROC General | 2025-10-03
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-15
ROC | October | RHMCMD - Man/close valve | All Water System ROC General | 2025-10-15
ROC | October | YWS+NYWS normal | All Water System ROC General | 2025-10-01
ROC | October | NMTKBS- Activated D1 as per interim QVW12- Placed Well 2 back in auto | All Water System ROC General | 2025-10-01
ROC | October | Ethan Ullalkar signing out. | All Water System ROC General | 2025-10-04
ROC | October | HLETYS - Post Injection Free Chlorine LoLo. Checked site. Flushing is still ongoing. Spoke to David T. who informed this alarm can be disregarded for the time being #CONSULT | All Water System ROC General | 2025-10-11
ROC | October | MKRSEM - Request TO (Andrew) to drop 2 pumps | All Water System ROC General | 2025-10-12
ROC | October | MKRSEM, Contacted Toronto operator Zoran to stop pumping to the res | All Water System ROC General | 2025-10-09
ROC | October | Angelica Chepiga signing in | All Water System ROC General | 2025-10-09
ROC | October | STRS48 - Travis W working on chlorine analyzer maintenance. Place highlift pump 1 duty 1 as requested | All Water System ROC General | 2025-10-10
ROC | October | MKRSEM - Called Toronto Water (Mehdi) and requested flow to MKRSEM. | All Water System ROC General | 2025-10-13
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-05
ROC | October | MARS- Called Metro spoke with Andrew to go to minimum flow for MARS north cell drawdown 08:00-MARS- North cell isolated south cell outlet open ready to drawdown. 08:00-VNRSKS- Activated D1 08:00-AURSBS- Activated D1 | All Water System ROC General | 2025-10-08
ROC | October | Adam Button signing in 18C Clear | All Water System ROC General | 2025-10-07
ROC | October | GWTP- Stephen B on site to test eye wash stations/Emergency shower, flood alarms and Cl2 Leak detection test | All Water System ROC General | 2025-10-07
ROC | October | RHMCMD- Placed valve back into auto. | All Water System ROC General | 2025-10-09
ROC | October | MTW12 - Station turbidity fault outstanding alarm. Dan Z will attend site. # CMU5 W11353520 | All Water System ROC General | 2025-10-09
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-12
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-12
ROC | October | YWS + NYWS Normal Connor Smith signing out | All Water System ROC General | 2025-10-01
ROC | October | GWTP- Stephen B. requested to deactivate duty and place KSTP high lift pumps back into auto | All Water System ROC General | 2025-10-08
ROC | October | QVW12- Influent free Cl2 lo alarm came in. Chlorinator opening up but influent free still dropping. Continued to monitor. Influent did not improve. Notified Joe D. Joe D will head to site. Created CMU5 W11349667 16:21-QVW12- Joe D on site cylinders freezing up. Joe D will thaw them out and monitor dosing on site #CMU5 | All Water System ROC General | 2025-10-08
ROC | October | STPS48 - Booster pump 2 VFD fault. Informed Travis W, able to reset | All Water System ROC General | 2025-10-10
ROC | October | MAPS- Stephen from AB is on site to work on generator and will be running it but it wont be connected to site | All Water System ROC General | 2025-10-08
ROC | October | QVW12- Joe D finished onsite. Influent reading back to normal. | All Water System ROC General | 2025-10-08
ROC | October | MKRSEM, Notified Toronto operator Brett to start filing the res | All Water System ROC General | 2025-10-08
ROC | October | GWTP- Chris S working on Local Server. Should not have any impact on operations. 13:50- Historian Heartbeat Fail Alarm came in. Called Chris S. No answer. Will try again. | All Water System ROC General | 2025-10-02
ROC | October | YWS + NYWS NORMAL | All Water System ROC General | 2025-10-02
ROC | October | MKPSSA - Dan Z completed work on site. MKRSEM - Deep cycling complete. Called Toronto water (Andrew) and requested to start filling Res. | All Water System ROC General | 2025-10-10
ROC | October | NRETCR - Ryan B. doing w/o including chlorine analyzers, exercising actuator valves, testing eye wash | All Water System ROC General | 2025-10-03
ROC | October | H4AUSSP1- Kyle C restarting server. | All Water System ROC General | 2025-10-03
ROC | October | YWS + NYWS Normal Christian Van Beek signing out. | All Water System ROC General | 2025-10-14
ROC | October | GWTP- Stephen B working on train turbidity analyzers VNETFD- Alex B on site for sampling. Deactivated D1 | All Water System ROC General | 2025-10-14
ROC | October | NMETIB- Deactivated duty | All Water System ROC General | 2025-10-03
ROC | October | STW12, STW3- Placed back into auto for STETBR fill cycle completion YWS + NYWS Normal | All Water System ROC General | 2025-10-03
ROC | October | ARPS - Jerry from OCWA called to inform that a second pump has been placed on to facilitate for necessity downstream as per Jeremy H | All Water System ROC General | 2025-10-10
ROC | October | Christian Van Beek signing out. | All Water System ROC General | 2025-10-01
ROC | October | MARS, Valve House Free Cl Resid hihi alarm, Critical Alarm, David T is on site | All Water System ROC General | 2025-10-09
ROC | October | NMETHW, Activated 1 to offset the towers | All Water System ROC General | 2025-10-09
ROC | October | GWTP- Backwash Tank 1 Level Loss of Echo Alarm. Emailed East OPS. | All Water System ROC General | 2025-10-09
ROC | October | KSETDP - Historian heartbeat alarm. Informed Artour L, will take a look CMU = 11365610 | All Water System ROC General | 2025-10-14
ROC | October | NBW5 - Station turbidity hi. Rotated silicate pump 1 duty 1 | All Water System ROC General | 2025-10-15
ROC | October | KSTKWP - Ernie H testing flood alarm. | All Water System ROC General | 2025-10-10
ROC | October | H2MASPP1 - Artour L beginning server restart. disregard communication alarm | All Water System ROC General | 2025-10-10
ROC | October | NMETIB- Deactivated duty NMVCBA- Adjusted valve from 80 to 40L/s NMVCIB- Adjusted valve from 40 to 80L/s | All Water System ROC General | 2025-10-11
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-11
ROC | October | ANMCBL - Dwayne L and Rob P working on site. Disregard alarms for the duration of the work. | All Water System ROC General | 2025-10-10
ROC | October | YWS + NYWS Normal NMVCBA - Reverted flow setpoint from 60L/s to 40L/s NMVCIB - Reverted flow setpoint from 60L/s to 80 L/s | All Water System ROC General | 2025-10-14
ROC | October | QVW12 - Alex B performing w/o on site including Chlorine and Ammonia system inspection, turbidity meter maintenance. | All Water System ROC General | 2025-10-09
ROC | October | KSTP- Divya P and Donald M onsite for PMs including NTU analyzer, Cl leak, Fluoride and PACL pumps. Can disregard all alarms while onsite. | All Water System ROC General | 2025-10-09
ROC | October | AUPSWS - William M leaving site. Heading to AUPSRR. | All Water System ROC General | 2025-10-09
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-15
ROC | October | YWS + NWYS Normal | All Water System ROC General | 2025-10-13
ROC | October | GWTP, Wash Water Pump 1/2/3 Lockout//Wash Water Suspended Solids hihi/Fault, notified Patrick F, he will look into it 10:18, Pat F heading to site CMU5: W11360943 | All Water System ROC General | 2025-10-13
ROC | October | NMETHW, Deactivated D1, Placed QVW3 back to man/stop | All Water System ROC General | 2025-10-13
ROC | October | TMC307, Flow Meter Fault Alarm, Fault has been coming in all day, notified Toronto Operator Paul that the issue is persistent, he will get his team to look at it on Tuesday | All Water System ROC General | 2025-10-13
ROC | October | STW56- Travis W onsite for PMs including health and safety, Cl and turbidity analyzers, Cl scrubber, leak detection and generator run. | All Water System ROC General | 2025-10-07
ROC | October | Christian Van Beek signing in. Weather: 20C and clear. | All Water System ROC General | 2025-10-12
ROC | October | KSTP - Raw water turbidity fault alarm. Disregard as per SCADA review. | All Water System ROC General | 2025-10-01
ROC | October | NBW5- Placed well in auto as per shift report | All Water System ROC General | 2025-10-01
ROC | October | SHTP / SHETCS - Benson S on site to complete work orders at the treatment plant and the tower including JHSC checks, Chlorine analyzer maintenance at the tower and hi/low temperature checks at the tower. | All Water System ROC General | 2025-10-02
ROC | October | QVW12- Influent Free Chlorine LoLo. Value recovered. Will reset in 10 minutes. | All Water System ROC General | 2025-10-03
ROC | October | MTW3- Turbidity Out of Range Alarm. Patrick F is onsite working on it. | All Water System ROC General | 2025-10-03
ROC | October | Connor Smith signing in | All Water System ROC General | 2025-10-07
ROC | October | SHTP - Post filter total chlorine hi alarm. Called Cole W who directed to reduce the chlorinator 1 dosing factor from 150% to 140% and the chlorinator 2 dosing factor from 184% to 178%. | All Water System ROC General | 2025-10-02
ROC | October | HLETYS - Pre-injection combined chlorine low alarm. Initiated flushing procedure. Placed chemical system manual/off and opened flow to waste valve which will be manipulated as needed for the duration of the flushing sequence. Activated necessary alarms. | All Water System ROC General | 2025-10-14
ROC | October | YWS + NYWS NORMAL | All Water System ROC General | 2025-10-03
ROC | October | Gluzen Ramos Ong signing in 16:00 Signing out 16:30 | All Water System ROC General | 2025-10-02
ROC | October | COMMS: Kyle C. restarted HUB4 at 10:00 | All Water System ROC General | 2025-10-03
ROC | October | KLPSWL - Tyler Z. and David D. working on generators, placed booster pumps 3 and 4 man/off AUW5 - Red B. informed finished chlorinator work, Jerry Z. on site backflushed and running well in manual | All Water System ROC General | 2025-10-03
ROC | October | NMW12 - Station turbidity hi, rotated silicate pump 2 to duty 1 | All Water System ROC General | 2025-10-04
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-04
ROC | October | YWS + NYWS NORMAL | All Water System ROC General | 2025-10-02
ROC | October | STW12- Effluent Turbidity Fault Alarm. Interlocked wells. Notified Dan Z. Someone will address it before end of day. | All Water System ROC General | 2025-10-03
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-04
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-05
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-10
ROC | October | MAPS/JFRS- Reverted Maple to Jefferson Feed. | All Water System ROC General | 2025-10-10
ROC | October | NMW12 - Red B finished on site. | All Water System ROC General | 2025-10-01
ROC | October | NMVCIB- adjusted from 80 to 40L/s. NMVCBA- adjusted from 40 to 60L/s to slow NMETHW drain cycle. | All Water System ROC General | 2025-10-02
ROC | October | Christian Van Beek signing in. Weather: 25C and sun. | All Water System ROC General | 2025-10-04
ROC | October | NMETIB - Combined chlorine hi, trends show a rising spike in reading. Will monitor, reading came down to normal range. Able to clear | All Water System ROC General | 2025-10-06
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-11
ROC | October | RHMCMD- Placed valve back into auto | All Water System ROC General | 2025-10-11
ROC | October | Connor Smith signing out | All Water System ROC General | 2025-10-11
ROC | October | SHTP - Reservoir Total Chlorine Fault alarm came in. Checked site. Called David T. who informed that there may just be low flows to the analyzer and if it does not clear within an hour, to give him a call back and he will head to site to take a look 09:05 - Reservoir Total Chlorine LoLo came in both on SCADA and the dialer. Checked site and trends which confirms that the level is LoLo. Called David T. who will take a look 09:24 - Dave calls back to inform that he tried switching sample pumps, but this did not help the levels. Dave will head to site. CMU5 Created W11356826 #CONSULT #CMU5 | All Water System ROC General | 2025-10-11
ROC | October | Ethan Ullalkar signing out. | All Water System ROC General | 2025-10-07
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-07
ROC | October | HLETYS - Dave T. attended site to take a look at the combined chlorine analyzer. CMU5 created W11356859 Dave also requested to extend the flushing procedure until 18:00 to help with residuals #CMU5 | All Water System ROC General | 2025-10-11
ROC | October | NMETIB- Activated duty | All Water System ROC General | 2025-10-11
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-12
ROC | October | Ethan U signing in Weather 12. | All Water System ROC General | 2025-10-12
ROC | October | AUVCBS- Red B done on site replaced transmitter | All Water System ROC General | 2025-10-07
ROC | October | AUPSRR- Will M on site performing maintenance on analyzers | All Water System ROC General | 2025-10-07
ROC | October | Adeela Khan signing in. Weather:15C and raining | All Water System ROC General | 2025-10-07
ROC | October | Connor Smith signing out | All Water System ROC General | 2025-10-07
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-08
ROC | October | AUMCBS, Flowmeter Fault Alarm, Notified Rob P, he will contact instrumentation and create a work order to get this flow meter fixed | All Water System ROC General | 2025-10-06
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-06
ROC | October | MKRSEM - Brett from Toronto Water called to request to drop one pump at the reservoir due to the Horgan shutdown. One pump has been dropped and will monitor. If levels go below 30%, will give Toronto Water a call back to place that second pump back on BVPS - Brett also requested to drop a pump at Bayview to help with the shutdown. One pump has been dropped on their end and placed pump 3 at BVPS man/off. Will monitor | All Water System ROC General | 2025-10-09
ROC | October | NMETIB- Deactivated D1 NRETBR- Yash S done network switch work. Slight gap in trends will be backfilled tomorrow | All Water System ROC General | 2025-10-07
ROC | October | STPSTL- Placed P1/2 in auto | All Water System ROC General | 2025-10-07
ROC | October | NMETIB/NMETHW - Placed NMVIB at 40 L/s and NMVCBA at 80 L/s as both duties are active, as per interim 23:21 - Reverted changes as NMETHW has deactivated, as per interim | All Water System ROC General | 2025-10-07
ROC | October | HLETYS - After 7 hours of flushing, the tower Total Chlorine Residual did not reach the high level alarm. The Pre Injection total chlorine reached 1.04 mg/L. Placed the Flow to waste valve back to man/closed, placed the tower setpoints back to normal, and placed the chemical pumps back to auto as per interim 22:22 - Spoke to Dave T. who directed to place the HLW2 FCV2 back to 30 L/s #CONSULT | All Water System ROC General | 2025-10-09
ROC | October | NMW136- Parth P, Rick L, Red B, on site for calibrations and troubleshooting flow meter | All Water System ROC General | 2025-10-08
ROC | October | KBET27- Dave T. onsite testing low temp KLPS27- Dave T will then be testing low temp, flood alarm, Cl analyzers and PRV | All Water System ROC General | 2025-10-09
ROC | October | NBW5 - High Turbidity alarm. Switched silicate pumps , Pump 1 to Duty 1, will monitor. | All Water System ROC General | 2025-10-09
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-09
ROC | October | MKRSEM - Brett called back to request to drop the one pump. Reservoir is holding | All Water System ROC General | 2025-10-10
ROC | October | MKRSMR- Called Toronto (Zoran) and requested to change duty start from 2.0 to 3.0m | All Water System ROC General | 2025-10-09
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-10
ROC | October | MKRSMR - TO (Andrew) called to request to drop in pump 12 as near duty stop. Okay to drop pump. No updates regarding Horgan plant yet but they will be updated later in the morning ARPS - Peel (Jerry) called to confirm setpoints from last night. Requested to inform them when Horgan plant is back online | All Water System ROC General | 2025-10-10
ROC | October | QVW34 - Chlorine gas leak/level hihi. Divya P & Alex B onsite for cylinder change. Disregard | All Water System ROC General | 2025-10-10
ROC | October | KSTP- Fin Water Fluoride Res Fault Alarm. Disregard as per SCADA Report | All Water System ROC General | 2025-10-10
ROC | October | JFRS- Noticed LIT Level Trend is flatlining. Notified Artour L. ANVC- Multiple comm alarms. Notified Artour L. He will take a look. W11356778 CMU5 | All Water System ROC General | 2025-10-10
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-11
ROC | October | KSTP- Fin Water Fluoride Res Fault, Fin Water Tot CL2 Res Fault. Disregard as per SCADA Report. | All Water System ROC General | 2025-10-03
ROC | October | Connor Smith signing out | All Water System ROC General | 2025-10-03
ROC | October | MARS, Notified Toronto operator Brett to increase the flow while ARPS does their pump tests HLW2, David T on site, cleaning influent analyzer | All Water System ROC General | 2025-10-06
ROC | October | RHRSWA- Deactivated D1 to help keep P4 running at RHPSPA | All Water System ROC General | 2025-10-01
ROC | October | HLETYS- Post injection total Cl2 lo alarm came in slight dip in Cl2 residual after rechlor system shut off for dip in flow cleared on its own after acknowledgement | All Water System ROC General | 2025-10-01
ROC | October | GWTP- Stephen B called. Maintenance working on train 1. Disregard related alarms. | All Water System ROC General | 2025-10-02
ROC | October | GWTP- Stephen B done on site back to normal ops YWS+NYWS normal | All Water System ROC General | 2025-10-06
ROC | October | AUETAD- Historian heartbeat alarm came in. Trends okay Notified Artour L. Will take a look on SCADA #consult | All Water System ROC General | 2025-10-07
ROC | October | NMVCBA- Placed in manual 40L/s | All Water System ROC General | 2025-10-07
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-11
ROC | October | KSTP- Clearwell Level Lo Alarm. Backwash just completed, will monitor. 23:36- Notified Dan Z. Requested to change Percentage Increase from 5 to 15% under the Filtration System Control Setpoints. Also requested to revert this change after duty deactivates 03:00- Reverted Percentage Increase from 15 to 5% KSTP- Fin Water Fluoride Res LoLo Alarm. Notified Dan Z. Can disregard for this fill cycle. CONSULT | All Water System ROC General | 2025-10-11
ROC | October | STW12 - CT not achieved alarm. Checked site, pumps are shutting down due to system interlock. Placed wells manual off, duty just activated and the tower is filling at a rapid rate without these wells. Called Patrick F who directed to leave the wells manual off for now. Patrick will check the system and attend site later this morning if needed. #consult | All Water System ROC General | 2025-10-13
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-13
ROC | October | Carter Dunn Signing Out | All Water System ROC General | 2025-10-13
ROC | October | HLETYS - Pre-injection combined chlorine low alarm. Contacted Alex B and jake M to inform that the flushing interim procedure is being initiated. Placed the chemical pumps manual off and opened the flow to waste valve to 30%. Will adjust the flow to waste valve as needed to provide optimal flows into the tower. Activated the inlet flow hi/low alarms as per the procedure. | All Water System ROC General | 2025-10-02
ROC | October | QVW34 - Deactivated well pump 3. | All Water System ROC General | 2025-10-02
ROC | October | Adam Button signing in 20C Clear | All Water System ROC General | 2025-10-01
ROC | October | ARPS- Called OCWA (Martin) and requested to change duty 2 start/stop from 78/84% to 72/79%. | All Water System ROC General | 2025-10-11
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-11
ROC | October | AUW57- Influent Free Chlorine HiHi Alarm. Value recovered. Cleared alarm. | All Water System ROC General | 2025-10-11
ROC | October | SHTP- Filter 2,3 Turbidity Hi Alarm. Backwash just completed. Cleared alarms as per SCADA Report. | All Water System ROC General | 2025-10-12
ROC | October | KSTP - finished water total chlorine and fluoride residual fault alarms. Plant is not running, disregard as per the shift report. | All Water System ROC General | 2025-10-13
ROC | October | STW12- Dan Z leaving site. Wells are man on STETBR- Dan Z changed duty stop to 90% | All Water System ROC General | 2025-10-03
ROC | October | GWTP - Raw water total chlorine res hihi. Checked site and reading dropped to normal range right away, just spike in reading | All Water System ROC General | 2025-10-05
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-05
ROC | October | QVW34 - Place well 3 in man/on to help divert flow towards Harry Walker through ringewell | All Water System ROC General | 2025-10-04
ROC | October | MKMCEM- Placed valve from 100% back to 50% | All Water System ROC General | 2025-10-08
ROC | October | HLW2- Influent free Cl2 hihi alarm came in. Notified David T will head back to site | All Water System ROC General | 2025-10-06
ROC | October | VNPSCD, Cl2 Gas Leak Alarm, Jacob M/Jordan B on site, they are dealing with the leak KLW34, Rick L is finished on site NBSP, Marcus R is on site working on the blowers | All Water System ROC General | 2025-10-06
ROC | October | BLW3- Patrick F testing Chlorine Leak alarm. | All Water System ROC General | 2025-10-07
ROC | October | QVW3- Divya P requested to place well back into auto NMVCBA- Placed in manual 20L/s | All Water System ROC General | 2025-10-07
ROC | October | Adeela Khan signing out | All Water System ROC General | 2025-10-08
ROC | October | MAPS- Drew from Ferguson Electric is on site to test generator. Will not be transferring over to generator | All Water System ROC General | 2025-10-08
ROC | October | NMVCBA- Placed man/open 30L/s | All Water System ROC General | 2025-10-08
ROC | October | AUETFC- Cole W called and requested to activate duty MAPS PD8- Placed pumps 2 and 4 in manual to keep pumps going as about to reach duty stop. After placing in manual pump 1 switched into duty 1 and started up. Placed man/off right away long with pump 3. Changed AURSBS duty stop from 85 to 90% | All Water System ROC General | 2025-10-08
ROC | October | Ethan U signing in Weather 29. | All Water System ROC General | 2025-10-05
ROC | October | Adeela Khan signing out | All Water System ROC General | 2025-10-05
ROC | October | NMW12 - Treated Chlorine Lo alarm came in. Checked site. Wells are not running and water is not being directed to users | All Water System ROC General | 2025-10-05
ROC | October | NMTKCBS - Historian heartbeat alarm. Trends are reading okay. Unable to clear. Informed Artour L of heartbeat alarm on OIT collector CMU = 11336141 | All Water System ROC General | 2025-10-05
ROC | October | KSETWB- Dan B and Satnam M onsite. Should not trigger any alarms. | All Water System ROC General | 2025-10-01
ROC | October | YWS+NYWS normal Adam Button signing out | All Water System ROC General | 2025-10-06
ROC | October | NMETHW - Total/combined chlorine lo, tower filling through ringwell, trends show quick drop, will monitor. Analyzer came within range shortly after | All Water System ROC General | 2025-10-07
ROC | October | QVW34- Alex B req. well 3 man/off and well 4 man/on | All Water System ROC General | 2025-10-08
ROC | October | HLW2- Influent Free HiHi. Cleared alarm. | All Water System ROC General | 2025-10-08
ROC | October | YWS+NYWS normal | All Water System ROC General | 2025-10-02
ROC | October | STETBR- Tower level hi alarm came in. Placed STW12 in auto as per interim | All Water System ROC General | 2025-10-02
ROC | October | YWS+NYWS normal | All Water System ROC General | 2025-10-02
ROC | October | HLETYS- 7 hours of flushing complete. TWR AIT 2 Total Hi Chlorine alarm was not triggered. It reached 1.09mg/L. Closed the Waste valve and placed chemical pumps back into auto (hypo pump 1 remains man/off). Tower inlet flow hi/low alarms and total chlorine residual AIT2 have been disabled. Interim Procedure | All Water System ROC General | 2025-10-02
ROC | October | STPSMR - Arthur L on site with East Water ops and Ferguson Electric to commission a new fire suppression system. Arthur directed to disregard the historian heartbeat alarm on site and any alarms related to the fire suppression system. | All Water System ROC General | 2025-10-02
ROC | October | HLETYS - Post-injection free chlorine lolo, Informed Cole W of alarm as we are still flushing okay to disregard Consult | All Water System ROC General | 2025-10-04
ROC | October | HLETYS - Post Inj total and comb cl lo. Checked with Alex B., worked on hypo pumps earlier today. Rotated to hypo pump 2, she will monitor. | All Water System ROC General | 2025-10-03
ROC | October | NBW3- Influent Free Chlorine LoLo Alarm. Interlocked well. Duty not active. Valued recovered. Cleared alarm. Well started up in schedule mode. | All Water System ROC General | 2025-10-09
ROC | October | MAPS- Dan B finished onsite. | All Water System ROC General | 2025-10-09
ROC | October | QVW12 - Treated free chlorine hihi alarm. Checked site, well is off and recently shut down. Treated free chlorine spikes on well shutdown are a known issue. Monitoring site to ensure the free chlorine reading returns to normal range. | All Water System ROC General | 2025-10-04
ROC | October | YWS + NYWS Normal HLETYS - Post injection combined chlorine hi alarm. Increased hypo pump max flow setpoint from 100 to 105 as per the shift report. | All Water System ROC General | 2025-10-05
ROC | October | NMTKBS - Activated duty early in preparation for interim procedure for fire flow testing | All Water System ROC General | 2025-10-10
ROC | October | Adeela Khan signing out | All Water System ROC General | 2025-10-10
ROC | October | NMETYS, Evgeny S working on OIT | All Water System ROC General | 2025-10-06
ROC | October | YWS + NYWS Normal NMTKKC - Ammonia pump 1 failed to start alarm. Checked site, tank is draining so ammonia pumps are needed. Duty rotated to ammonia pump 2 but the ammonia tank for pump 2 is low. While monitoring the ammonia pump 2 shut down likely due to the low ammonia tank level. Immediately reset the ammonia pump 1 fail to start alarm and monitored activation. Ammonia pump 1 started, will monitor site and ensure ammonia pump 1 remains on. | All Water System ROC General | 2025-10-14
ROC | October | GWTP - Backwash tank 1 level lo alarm. Checked site, backwash tank 1 LIT showing a loss of echo alarm which is a disregard on the shift report. Alarms are likely related. Able to reset the low tank level alarm. Loss of echo alarm outstanding as a disregard. | All Water System ROC General | 2025-10-14
ROC | October | STW12 - Travis W called, Hypo pump 1 has small leak, requested Hypo pump 1 to duty 2 , out of duty rotation. Placed Hypo pump 1 man/off. | All Water System ROC General | 2025-10-01
ROC | October | AUPSOH- Jason G called. Lee F working on pump 3. He is placing all pumps man/off. Disregard alarms. | All Water System ROC General | 2025-10-01
ROC | October | STRS48 - Rotated Duty for HL pumps for Travis W. HL Pump 2- Duty 1, HL Pump 1 Duty 2. | All Water System ROC General | 2025-10-01
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-06
ROC | October | HLETYS - Pre Injection Combined Chlorine Lo alarm came in. Checked site. Tower is filling and initiated flushing procedure. - Placed all chemical pumps man/off - Placed flow to waste valve at 30% - Enabled Tower Inlet flow hi/lo alarms - Enabled Tower Total Chlorine Residual Hi alarm 17:50 - Stopped flushing and reverted all changes. Confirmed with Dave T. #CONSULT | All Water System ROC General | 2025-10-11
ROC | October | ARPS - Airport discharge flow lolo alarm. MARS duty 1 deactivated on fill cycle. Normal operations, cleared alarms. | All Water System ROC General | 2025-10-13
ROC | October | AUPSWS - Lee F on site for vibration testing. Lee requested that pump 4 be placed in duty 1. Made necessary changes. | All Water System ROC General | 2025-10-02
ROC | October | STW12- Artour L on site with contractors to work on diesel LIT ANW23- Parth P Red B and Rick L on site for annual calibrations SHTP- filter 2 post rinse NIT hi alarm came in. Notified Benson S NMETHW- Changed D1 start back to 40 % | All Water System ROC General | 2025-10-07
ROC | October | YWS + NYWS normal | All Water System ROC General | 2025-10-08
ROC | October | MARS- Cole Reverting changes to North cell. confirmed flow from Metro can go back to normal flow. Called Metro spoke with Peter to rerun to normal flow | All Water System ROC General | 2025-10-08
ROC | October | NBET27 - Eric S finished on site. | All Water System ROC General | 2025-10-09
ROC | October | STW3- Placed well man/off Interim Procedure | All Water System ROC General | 2025-10-01
ROC | October | YWS+NYWS normal | All Water System ROC General | 2025-10-01
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-08
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-08
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-09
ROC | October | NMETHW - Deactivated duty 1 while NMETIB fills. | All Water System ROC General | 2025-10-04
ROC | October | HLETYS - outlet flow Hi alarm, adjusted VCFCV2 flow. | All Water System ROC General | 2025-10-09
ROC | October | YWS + NYWS NORMAL | All Water System ROC General | 2025-10-09
ROC | October | Aurora Central - Activated duty 1 | All Water System ROC General | 2025-10-10
ROC | October | Young and Major Mack - Harsh P. and Jon O. are headed to site to open the valve, as directed by Jeremy H | All Water System ROC General | 2025-10-10
ROC | October | KSTP - Finished Water Total Chlorine Residual and Finished Water Fluoride Fault alarms came in upon HLP stop. Disregarded as per shift report | All Water System ROC General | 2025-10-08
ROC | October | QVW34- Alex B finished onsite. Requested to place well 4 man/off and run well 3 | All Water System ROC General | 2025-10-08
ROC | October | KCETDS - Jordan B testing temp alarms and cleaning chlorine analyzers. | All Water System ROC General | 2025-10-09
ROC | October | QVW12, Treated Free Cl2 hihi/Combined Cl2 lo, Wells are currently off, system should recover as this is normal when the system just turns off, if analyzers dont recover will notify operator | All Water System ROC General | 2025-10-08
ROC | October | NMW12- Station Turbidity Fault. Interlocked wells. Notified William M. He will attend. | All Water System ROC General | 2025-10-03
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-04
ROC | October | Ethan U signing in Weather 15. | All Water System ROC General | 2025-10-04
ROC | October | JFRS - Deactivated duty 1 and duty 2 to prepare for the Maple to Jefferson Feed. | All Water System ROC General | 2025-10-05
ROC | October | QVW12- Alex B finished onsite Requested wells back into auto. | All Water System ROC General | 2025-10-09
ROC | October | MTETNL - Sara (905 715 4398) from EG water department called, performing High and Low velocity flushing in the area for 6 Hours. Notified Dan Z, she will attend site. | All Water System ROC General | 2025-10-09
ROC | October | Initiating Maple to Jefferson feed. | All Water System ROC General | 2025-10-05
ROC | October | KSTP - Clearwell level lo, level climbing back up NMETIB - Deactivate duty 1 | All Water System ROC General | 2025-10-05
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-15
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-08
ROC | October | RHPSWA - man/started Pump P2 NRETCR - Activated D1. | All Water System ROC General | 2025-10-15
ROC | October | AURSBS - Pre injection Monochloramine LoLo alarm, notified William M., will check. | All Water System ROC General | 2025-10-15
ROC | October | GWTP - Backwash tank 1 level lolo alarm. This alarm is triggering continuously, likely due to faulty LIT sensor associated with the disregarded loss of echo alarm. Due to its continuous triggering and reset to normal alarm status, this alarm will be left outstanding until area operators attend site today. Sent an email to OCO. | All Water System ROC General | 2025-10-14
ROC | October | VNRSKS - Activated duty 1 early to drawdown MARS. | All Water System ROC General | 2025-10-14
ROC | October | Adam Button signing in 6C clear | All Water System ROC General | 2025-10-14
ROC | October | NMTKBS- Joe D called and will be doing deplox analyzer cleaning. 11:20- Joe D finished onsite. | All Water System ROC General | 2025-10-07
ROC | October | MAPS, Mark S from Optimization is on site MAPS, Drew from Ferguson Electric is leaving site MAPS, Ben H from property services is leaving site | All Water System ROC General | 2025-10-06
ROC | October | YWS + NYWS NORMAL | All Water System ROC General | 2025-10-15
ROC | October | MAPS - Dan B on site for generator test. Activated VNRSKS Duty to fill res. before performing gen test. | All Water System ROC General | 2025-10-09
ROC | October | RHPSPA- Jack P on site to run generator on load. Requested 2 pumps at RHPSWA to run at same time as RHPSPA to continue moving water north. RHPSWA- Placed P1 in man/on MARS- Mehdi from Metro Informed ROC testing is done on pump supplying reservoir and Bayview reservoir is no longer isolated both tests on Metros end have been completed | All Water System ROC General | 2025-10-15
ROC | October | RHPSPA- Sean P requested Pump 3 man/on. and Pump 4 man/off 11:05- Sean P requested pump 2 man/on and pump 3 man/off 11:23- Sean P requested pump 1 man/on and pump 2 man/off | All Water System ROC General | 2025-10-02
ROC | October | MARS - Cole W finished exercising valves at MARS. | All Water System ROC General | 2025-10-02
ROC | October | NMVCBP = Set flow to 60 from 40 NMVCIB = Set flow to 60 from 80 | All Water System ROC General | 2025-10-13
ROC | October | Adam Button signing in | All Water System ROC General | 2025-10-15
ROC | October | BLW3 - Dan Z requested P3 back to auto. | All Water System ROC General | 2025-10-09
ROC | October | Initiating MAPS to JFRS feed run - Placed KCPSDS pumps man/off - Placed VNPS PD8 and MAPS PD8 pumps man/off - Placed VC MV3 into man - Placed AURSBS Res MV4 to man and close - Man/start pump 2 at MAPS 05:10 - Reverted all changes | All Water System ROC General | 2025-10-10
ROC | October | NMETIB- Activated D1 at 64% to offset from NMETHW as per shift report NMVCBA- Placed valve back in auto | All Water System ROC General | 2025-10-07
ROC | October | Connor Smith signing out | All Water System ROC General | 2025-10-09
ROC | October | SHTP - Received Chlorine injector 1 and 2 vacuum switch alarm, plant interlocked. Lee F testing back flow preventers on site. Notified Benson S, he will attend site. | All Water System ROC General | 2025-10-10
ROC | October | BLETNL- Mike from the fire department in Ballan Trae to notify of fire training going on in system until 10:00. D1 active and tower halfway through cycle. Notified Patrick F. Placed Well 3 in man/off due to pressure influence from fire training. | All Water System ROC General | 2025-10-07
ROC | October | STPSMR - Arthur L called to inform that the commissioning work for the fire suppression system is completed and all workers are off site. | All Water System ROC General | 2025-10-02
ROC | October | HLETYS - Pre-injection combined chlorine low alarm. Flushing interim procedure is in effect, combined chlorine reading is slowly dropping. Contacted Cole W to inform of the situation and request a plan of action should it continue to drop. YWS - Received a call from Tracy at the Road dispatch department stating that there was complaints from residents regarding the noise of an open excavation covering (Steel Plates). Tracy wanted to know if this open excavation belonged to York Region, contacted both Rob P and Mohsen M from CPD to confirm that this excavation does not belong to YR. Passed this information to Tracy. #Consult | All Water System ROC General | 2025-10-02
ROC | October | MAPS PD7- All pumps faulted on lo pressure switch alarm. Deactivated D1 at VNRSKS | All Water System ROC General | 2025-10-08
ROC | October | Adeela Khan signing in. Weather: 11C and sunny | All Water System ROC General | 2025-10-09
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-09
ROC | October | BLETNL - Sean from Town of Stouffville flushing in the area. Notified Dan Z. | All Water System ROC General | 2025-10-09
ROC | October | NMTKKC - Joe D on site to complete a hot flush of the chemscan analyzer. Joe has placed the chemical pumps off and directed to disregard the chemscan offline alarm. | All Water System ROC General | 2025-10-02
ROC | October | YWS + NYWS Normal Christian Van Beek signing out. | All Water System ROC General | 2025-10-13
ROC | October | MARS, Cell 1 (North) Lvl Lo alarm, Activated D1 at RHRSTR to get the flow moving towards MARS as both MAPS PD7/PD8 are active at this time with Aurora central active as well. Will continue to monitor, if level fails to increase, will deactivate duties at Central. MARS, Contacted Toronto operator Paul to increase the flow to MARS 15:05, Reverted back to normal flow | All Water System ROC General | 2025-10-13
ROC | October | GWTP- Stephen B is draining low lift wetwelll for work on LIT. Requested a call for any other plant issues. Onsite with Red B and Chirs S | All Water System ROC General | 2025-10-09
ROC | October | ANW23, Parth P/Rick L on site doing annual calibrations | All Water System ROC General | 2025-10-14
ROC | October | NMW136- Parth P and Rick L are done on site. Jay G is running well in manual | All Water System ROC General | 2025-10-15
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-12
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-10
ROC | October | NRETCR- Yash S working on network. Will lose comms. Switched controlling tower to NRETBR for duration of work. 14:29- Yash S finished. All alarms cleared. Switched controlling tower back to NRETCR. | All Water System ROC General | 2025-10-07
ROC | October | BVPS- Placed pumps back into auto. Duty not active. | All Water System ROC General | 2025-10-11
ROC | October | MKRSEM - Toronto Water (Paul) called to inform that although FJ Horgan is back, they are still in recovery mode. Paul asked if he could drop the pumps at MKRSEM. Will place pumps back on once Mililken recovers. Confirmed with Dan Z. that this is okay. Pumps have been shut down by Paul #CONSULT | All Water System ROC General | 2025-10-11
ROC | October | RHVCEM - Dwayne L requested VC man/open 100%. | All Water System ROC General | 2025-10-15
ROC | October | NBW2- Effluent free chlorine residual Lo/low alarm. Notified David T. | All Water System ROC General | 2025-10-15
ROC | October | QVW12 - PAC Control Power Fail, Gas Scrubber Overload, Generator Runing and Well 1 Pump VFD Fault alarms came in. Checked site. Wells have faulted and water is not being directed to users. Generator is still running and site is running on generator power. Checked Hydro One website and no outage in the area has been reported QVETQS - System Pressure LoLo alarm came in. Checked site. Trends indicate that the pressure took a dip and came right back. Called Divya P. who will take a look on SCADA 18:55 - Site switched back to hydro power and generator is no longer running. The gas scrubber overload critical alarm is still outstanding and Divya P. will take a look 19:12 - Divya informed that the wells are back in auto and back to normal operations #CONSULT | All Water System ROC General | 2025-10-07
ROC | October | QVW12 - Well 1 VFD fault on start up. Informed Joe D, will head to site CMU = 11356990 | All Water System ROC General | 2025-10-12
ROC | October | Ethan Ullalkar signing out. | All Water System ROC General | 2025-10-12
ROC | October | QVW34 - Deactivated in manual. | All Water System ROC General | 2025-10-12
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-13
ROC | October | HLETYS - Pre-injection combined chlorine low alarm. Initiated flushing procedure. Placed chemical system manual/off and opened flow to waste valve which will be manipulated as needed for the duration of the flushing sequence. Activated necessary alarms. | All Water System ROC General | 2025-10-13
ROC | October | RHMCMD - Place back in auto | All Water System ROC General | 2025-10-14
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-07
ROC | October | QVW34- Placed wells back into auto | All Water System ROC General | 2025-10-08
ROC | October | Carter Dunn Signing In, 11D/Clear | All Water System ROC General | 2025-10-08
ROC | October | NMETIB- Parth P. finished onsite. | All Water System ROC General | 2025-10-09
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-13
ROC | October | NRETCR - Cathodic protection fault alarm. Checked site, operations normal. Sent email to area ops. | All Water System ROC General | 2025-10-13
ROC | October | 09:45-BVPS- Called Brett from Metro of BVPS shutdown and isolation MKMCLA- Upstream pressure lolo notified Cristina S. Will consult Dwayne L as this maybe a be result of BVPS shutdown trial BVPS- Brett from Metro called to inform ROC that isolation of Bayview reservoir is completed | All Water System ROC General | 2025-10-15
ROC | October | BLW3 - Dan Z leaving site. Well 3 pump running in man mode until later today. | All Water System ROC General | 2025-10-15
ROC | October | NMW136- influent free Cl2 hihi alarm came in on well start up Cleared after 3 mins. 21:34- AUW14- Influent free Cl2 hi alarm came in on well start up trends recovered after 3 mins. | All Water System ROC General | 2025-10-01
ROC | October | BLW3 - Joe M requested man/off. Contractor on site working on pipes. | All Water System ROC General | 2025-10-15
ROC | October | STW12- Jack P onsite replacing foot valve on hypo pump 1 KSTP- Donald M onsite changing cylinders. | All Water System ROC General | 2025-10-02
ROC | October | MKRSEM- Toronto (Zoran) called and requested to drop one of the two pumps. Currently at 2.46m. Said to call back and he can run the second pump if reservoir gets too low. | All Water System ROC General | 2025-10-10
ROC | October | QVW12- Treated Free HiHi Chlorine. Wells not running. Value recovered. Cleared alarm. | All Water System ROC General | 2025-10-10
ROC | October | NRETCR - Deactivated D1 @ 81% to help with RHRSTR levels. | All Water System ROC General | 2025-10-09
ROC | October | STRS48 - Travis W and Dan Z on site for gen test. Requested STW5 and STW6 man/off, High lift pumps man/off. | All Water System ROC General | 2025-10-15
ROC | October | VNRSKS- David T on site testing eye wash alarm | All Water System ROC General | 2025-10-15
ROC | October | HLETYS- Artour L on site for UPS replacement | All Water System ROC General | 2025-10-15
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-10
ROC | October | BVPS- Toronto (Zoran) called and req. to shut down one pump. Placed pump 3 man/off. RHRSTR level at 67% (4.72m) | All Water System ROC General | 2025-10-10
ROC | October | MAPS- David T leaving site. | All Water System ROC General | 2025-10-10
ROC | October | NRETCR- Deactivated duty so that JFRS can fill during MAPS/JFRS feed to try and assist RHRSTR while down to one pump at BVPS. | All Water System ROC General | 2025-10-10
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-11
ROC | October | QVW12- Treated Free Chlorine HiHi Alarm. Combined Chlorine Lo Alarm. Wells not running. Values recovered. Cleared alarms. | All Water System ROC General | 2025-10-11
ROC | October | MKRSMR- Peter from Toronto called and requested to stop pumping to help their reservoirs recover from shutdown. Reservoir at 4.5m MKRSEM- Peter from Toronto will start a second pump. | All Water System ROC General | 2025-10-12
ROC | October | GWTP - low lift pump 2 hydraulic valve fail to open alarm. Reset alarm and placed pump in duty 2 as per the shift report. | All Water System ROC General | 2025-10-04
ROC | October | MKRSEM - Called Toronto Water (Zoran) and requested they stop pushing flow to MKRSEM. | All Water System ROC General | 2025-10-04
ROC | October | KSTP- Fin Water Tot CL2 Res Fault Alarm. Disregard as per SCADA Report | All Water System ROC General | 2025-10-10
ROC | October | STW12 - Place wells back in auto as per interim | All Water System ROC General | 2025-10-12
ROC | October | NMETIB - Deactivate duty 1 | All Water System ROC General | 2025-10-12
ROC | October | VNPSAP- Dave T onsite testing flood alarm and low temp. | All Water System ROC General | 2025-10-03
ROC | October | RHPSPA - Building flood alarm, Jack P requested disregard alarm. | All Water System ROC General | 2025-10-15
ROC | October | HLETYS- Post-Injection Combined Chlorine Lo Alarm. Adjusted Hypo Pump 2 Max Flow from 140 to 135mL/min | All Water System ROC General | 2025-10-03
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-07
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-14
ROC | October | ARPS- Total Cl2 hihi and combined Cl2 hi alarms came in as P8 started up trends recovered after 3 mins. Alarms cleared | All Water System ROC General | 2025-10-06
ROC | October | ARPS- David from Peel informed ROC that 3 pumps are in in auto and PLC upgrades have been completed | All Water System ROC General | 2025-10-06
ROC | October | Ethan U signing in Weather 15. | All Water System ROC General | 2025-10-15
ROC | October | Angelica Chepiga signing out | All Water System ROC General | 2025-10-15
ROC | October | NRETCR - Deactivate duty 1 | All Water System ROC General | 2025-10-15
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-15
ROC | October | KSTP - Clearwell level lo. Filter 2 finished backwashing. Will monitor 22:01 - Followed up wtih Stephen B regarding cleawell. Placed filter 2 production mode into flow mode. Issue was due to highlifts being off. Once clearwell is back running will place filter production back in to higlift mode Consult | All Water System ROC General | 2025-10-15
ROC | October | HLETYS- Post injection combined/total Cl2 hi alarm came in. Residuals look slightly elevated but recovered after 6 mins and alarms cleared on their own | All Water System ROC General | 2025-10-06
ROC | October | GWTP- Stephen B working on Train 2 and low lift pump 2. Disregard related alarms. | All Water System ROC General | 2025-10-03
ROC | October | Angelica Chepiga signing in, weather +4C | All Water System ROC General | 2025-10-10
ROC | October | BLW3- Joe M on site to run well in manual and will place back in auto when done | All Water System ROC General | 2025-10-15
ROC | October | AURSBS- Will M on site for Cl2 leak detection test | All Water System ROC General | 2025-10-15
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-15
ROC | October | RHRSTR- Changed lo level alarm from 58% to 64% and lolo level alarm from 45% to 60% RHPSPA- Changed P1/2 to D4 VNPS PD7- Changed P1/3 to D4 would not rotate duties. Notified Kyle C VNPS cannot run pump duties with D1 assigned. Placed pumps 1/3/4 at VNPS PD7 in manual and left P2 in auto to run in D2 Made all changes as per interim | All Water System ROC General | 2025-10-15
ROC | October | NMETIB - Parth P & Rick L onsite for LIT calibrations | All Water System ROC General | 2025-10-10
ROC | October | NMTKBS - Jason G requested deactivate Duty and place pumps 3/4 man/off at AUPSOH . | All Water System ROC General | 2025-10-10
ROC | October | BVPS - Dwayne L called, requested pumps off for Langstaff gateway trial isolation. Deactivated Duty 1 and placed all pumps man/off. | All Water System ROC General | 2025-10-15
ROC | October | HLETYS - Post injection free chlorine lolo alarm. Checked site, tower is currently under the flushing interim procedure. Combined chlorine reading is within expected range. Monitoring system closely. | All Water System ROC General | 2025-10-02
ROC | October | GWTP - Stephen B finished on site, | All Water System ROC General | 2025-10-15
ROC | October | NMETHW - Deactivated duty 1 while NMETIB fills. | All Water System ROC General | 2025-10-03
ROC | October | YWS + NYWS Normal RHPSWA - Activated pump 2 in manual mode to drawdown RHRSWA | All Water System ROC General | 2025-10-04
ROC | October | RHPSWA - Deactivated pump 2. | All Water System ROC General | 2025-10-04
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-04
ROC | October | STW12 - Place man/on as Bethesda duty active | All Water System ROC General | 2025-10-12
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-12
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-12
ROC | October | AUPSOH- Placed P3/4 in auto GWTP- Sodium hypo tank lolo alarm came in resulting in M clean insufficient chemical alarm. Called Stephen B no answer will continue to reach him MKETFA- Jack P onsite for sampling 12:48- GWTP- Stephen B informed ROC hypo will be delivered on Friday and to disregard alarms as M cleans will be resumed when hypo is delivered | All Water System ROC General | 2025-10-14
ROC | October | Christian Van Beek signing in. | All Water System ROC General | 2025-10-01
ROC | October | QVW12- Red B requested wells back into auto | All Water System ROC General | 2025-10-02
ROC | October | QVW34- Placed well 3 in manual. QVW12- Alex B on site with mechanical trying to get diesel generator running. Will call back when contact tank has been passed to place well in man/off NMW12- Placed wells in auto | All Water System ROC General | 2025-10-07
ROC | October | AURSBS - Activated duty 1 to help push water from MARS | All Water System ROC General | 2025-10-10
ROC | October | NMETIB - Activated duty to help offset with NMETHW, as per interim | All Water System ROC General | 2025-10-10
ROC | October | RHMCMD - Placed Valve man/open | All Water System ROC General | 2025-10-10
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-12
ROC | October | NMETHW - Deactivated duty 1 as NMETIB fills. | All Water System ROC General | 2025-10-12
ROC | October | YWS + NYWS Normal KSTP - Finished water fluoride and total chlorine residual fault alarms. Disregard as per the shift report. | All Water System ROC General | 2025-10-12
ROC | October | STW12 - Placed pumps in auto mode as STETBR has filled. | All Water System ROC General | 2025-10-12
ROC | October | NMTKKC- Free Chlorine HI Alarm. Will monitor. 17:05- Cleared alarm. | All Water System ROC General | 2025-10-01
ROC | October | QVW12 - Divya P. informed Chris Iliohan on site working on booster pump 2, W2 is man/off. He will also initiate the QVETQS drawdown | All Water System ROC General | 2025-10-03
ROC | October | STW12 - Dan Z. informed placing man/off for Lee F. working backflow preventor. Also working on hypo pump 2 | All Water System ROC General | 2025-10-03
ROC | October | STPSTL - Discharge Flow LoLo and Pump 2 Low Flow alarm came in. Checked site and found that pump 2 was shutting down and duty 1 rotated to pump 1. Pump 1 started with no issues and flow came back to optimal range. Will send an email to east about this issue | All Water System ROC General | 2025-10-05
ROC | October | BLW3 - Phil D requested well 3 pump back to auto, Rick L completed work on site. | All Water System ROC General | 2025-10-09
ROC | October | MKRSEM- Called Toronto (Paul) and requested pumping. Just one pump for now to help Toronto levels recover due to Horgan shutdown. | All Water System ROC General | 2025-10-11
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-12
ROC | October | MKRSEM - Request TO (Paul) to drop both pumps | All Water System ROC General | 2025-10-07
ROC | October | NMETIB - Combined chlorine hi/total chlorine hi, draining. Informed Divya P. Will head to site first thing in the morning for a grab. Consult | All Water System ROC General | 2025-10-07
ROC | October | NMW12- Ric L called and req. wells man/off for annual calibrations. Confirmed okay with William M. | All Water System ROC General | 2025-10-07
ROC | October | Gluzen Ramos Ong signing in | All Water System ROC General | 2025-10-07
ROC | October | NBW5- Historian Heartbeat Alarm. Interlocked well. Notified Artour L. He will take a look. 13:04- Artour L cleared alarm. | All Water System ROC General | 2025-10-02
ROC | October | AUW5 - Red B. informed onsite to rebuild chlorinator. Man/stopped at 9:08 but realized did not complete CT so started back up until it cleared. Man/stop at 09:32, | All Water System ROC General | 2025-10-03
ROC | October | NRETCR - Ryan B. offsite | All Water System ROC General | 2025-10-03
ROC | October | NMETIB - Rick L and Parth P finished on site. | All Water System ROC General | 2025-10-10
ROC | October | BVPS, Deactivated D1 RHMCMD, Placed valve in manual. This well help water flow from MARS to RHRSTR | All Water System ROC General | 2025-10-09
ROC | October | MKRSEM - Called Toronto Water (Paul) and requested one pump on at reservoir as levels are low, as per Tyson C. 23:38 - Requested 2nd pump on to help fill reservoir | All Water System ROC General | 2025-10-07
ROC | October | HLETYS - Pre-injection Combined Chlorine LoLo alarm came in. Checked site. Called Cole W. who will head to site and take a grab sample. CMU5 Created W11344790 23:20 - Post injection Combined Chlorine Lo alarm came in. Called Cole W. back who informed he is still on site. Directed to continue flushing as long as possible due to low residuals coming in from The Town of East Gwillimbury. Placed flow to waste valve at 40% 04:15 - After 11 hours of flushing, the tower Total Chlorine Residual did not reach the high level alarm. The total chlorine reached 1.27 mg/L. Placed the Flow to waste valve back to man/closed, placed the tower setpoints back to normal, and placed the chemical pumps back to auto #CONSULT #CMU5 | All Water System ROC General | 2025-10-07
ROC | October | NMVCBA - Placed valve back to auto as duty activated, as per interim | All Water System ROC General | 2025-10-07
ROC | October | STW12 - Travis W requested to switch chemical pumps duty. Hypo Pump 1 and Silicate pump 1 to Duty 1. Hypo pump 2 and Silicate Pump 2 to Duty 2. | All Water System ROC General | 2025-10-09
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-05
ROC | October | RHPSPA - Sean P called to state he is finished with the pump inspections. Pump 1 will remain manual/on, placed all other pumps in auto. | All Water System ROC General | 2025-10-02
ROC | October | KSTKWP- Finished onsite. NMETIB- Onsite to verify Free Chlorine Analyzer | All Water System ROC General | 2025-10-07
ROC | October | NMETIB - deactivated D1 to offset with NMETHW. | All Water System ROC General | 2025-10-10
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-13
ROC | October | YWS + NYWS Normal STW12, CT not Achieved, Alarm happened earlier in the morning, Pat F dealt with the issue. CMU5: W11360935 | All Water System ROC General | 2025-10-13
ROC | October | HLETYS - Pose injection combined chlorine hi, increase hypo pump 1 max flow from 105 to 110mL/min 22:50 - increase further to 115mL/min as reading still just around the hi level | All Water System ROC General | 2025-10-05
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-06
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-06
ROC | October | Connor Smith signing in 10 C Cloudy | All Water System ROC General | 2025-10-01
ROC | October | Adam Button signing in | All Water System ROC General | 2025-10-08
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-04
ROC | October | MTW12- Dan Z leaving site. Well is back running. Discharge pressure lolo alarm outstanding due to town flushing. | All Water System ROC General | 2025-10-09
ROC | October | NBW5- Tim H onsite work work orders. Running generator, chlorine and turbidity analyzer maintenance and Cl leak test. | All Water System ROC General | 2025-10-09
ROC | October | RHMCMD - Closed valve in manual mode. | All Water System ROC General | 2025-10-14
ROC | October | Carter Dunn Signing In | All Water System ROC General | 2025-10-14
ROC | October | RHMCMD, Placed valve back to auto | All Water System ROC General | 2025-10-14
ROC | October | NBW5- Cole W called and requested well man/off due to turbidity issues. | All Water System ROC General | 2025-10-03
ROC | October | STW3 - Travis W requested man/start Well 3 pump for sampling. | All Water System ROC General | 2025-10-01
ROC | October | NMW15 - Well 15 pump to auto /currently running as per Divya P. | All Water System ROC General | 2025-10-01
ROC | October | HLW2 - Joe W testing chlorine leak alarm and cleaning turbidity meter. | All Water System ROC General | 2025-10-09
ROC | October | QVW12- Alex B requested to place silicate pump 2 in duty 1 and place both wells in man/on. | All Water System ROC General | 2025-10-09
ROC | October | HLETYS - Flushing procedure is active. Adjusted flow to waste valve from 25% to 15%. Will be making adjustments to the flow to waste valve as needed. | All Water System ROC General | 2025-10-04
ROC | October | YWS + NYWS Normal GWTP - GRTPLL - low lift pump 2 hydraulic valve fail to open alarm. Checked site, plant is not active. Cleared alarm and placed pump 2 in duty 2 as directed by Tyson C. | All Water System ROC General | 2025-10-04
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-04
ROC | October | HLETYS - Adjusting HLW FCV2 flow to maintain ET inlet flow. | All Water System ROC General | 2025-10-02
ROC | October | NMETIB - Duty just activated, Deactivated NMETHW Duty @ 68% | All Water System ROC General | 2025-10-02
ROC | October | NBW5 - Turbidity Hi alarm, will monitor. | All Water System ROC General | 2025-10-02
ROC | October | NMW5 - Turbidity value increasing. Man/stop Well 5 pump . | All Water System ROC General | 2025-10-02
ROC | October | NMTKBS- Joe D on site for sampling req P3 at AUPSOH be placed in man/off to allow tank to drain HLETYS- Ammonia P2 failed to start alarm came in. Cleared upon acknowledgment 12:01-NMTKBS- Joe D req P4 at AUPSOH be placed man/off | All Water System ROC General | 2025-10-08
ROC | October | NMTKBS- Joe D done sampling on site. Placed P3/4 at AUPSOH in auto NBW5- Historian heartbeat alarm notified Artour L. Will take a look on SCADA MAPS PD8- Placed P4 in man/off as AURSBS level approaching hi alarm | All Water System ROC General | 2025-10-08
ROC | October | MAPS PD8- Placed P1-3 in auto MAPS- Dan B on site to run generator all PD7and PD8 pumps are man/off BLETNL- Shawn from town of Whitchurch/Stouffville flushing in area. Notified Joe W. | All Water System ROC General | 2025-10-08
ROC | October | HLETPR- Alex B onsite for PMs. Will be testing chamber temperature alarms. | All Water System ROC General | 2025-10-02
ROC | October | JFPS - lee F on site and requested that pump 1 and pump 2 be placed in duty 1 and pump 3 and pump 4 be shut down. Made changes to pump duties slowly to ensure no water hammer or pressure issues. | All Water System ROC General | 2025-10-02
ROC | October | Ethan Ullalkar signing out. | All Water System ROC General | 2025-10-10
ROC | October | BVPS- Called Toronto water (Farshad) for update, FJ Horgan is offline. Farshad ok to start 2 pumps at duty start and will start MKRSMR pump later ( at duty start 3,0m). RHMCMD remains man/open . | All Water System ROC General | 2025-10-10
ROC | October | Connor Smith signing in 10 C Clear | All Water System ROC General | 2025-10-02
ROC | October | Christian Van Beek signing in. Weather: 24C and clear. | All Water System ROC General | 2025-10-03
ROC | October | STETBR - Activated duty in preparation for swabbing from the Town of Stouffville flushing tonight, as per interim | All Water System ROC General | 2025-10-05
ROC | October | AUPSRR- Post Inj. Free Chlorine HiHi Alarm. Alarm cleared upon acknowledging. | All Water System ROC General | 2025-10-08
ROC | October | NMW136- Parth P Ric L and Midhun A finished onsite. Wells are in auto. | All Water System ROC General | 2025-10-08
ROC | October | GWTP- Stephen B called. Low Lift Pump 2 will be OOS as well as Train 1. ZW4 M-Clean Insufficient Chemical Alarm outstanding. Should clear later. | All Water System ROC General | 2025-10-02
ROC | October | NMPSKC, Artour L on site doing generator training for the site, generator will be ran. Ryan B on site as well KLW34, Rick L on site doing annual calibrations | All Water System ROC General | 2025-10-06
ROC | October | MKRSEM- Called Toronto water (Brett) and requested to start filling Res. | All Water System ROC General | 2025-10-09
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-10
ROC | October | Toronto Water - Called Toronto Water (Brett) for an update. Brett informed they are doing better and one pump over at Horgan has been running since 01:34. Brett has informed that one pump at BVPS can be turned on. BVPS - Placed pump 1 back to auto | All Water System ROC General | 2025-10-10
ROC | October | MARS - Reservoir Valve House Security intrusion alarm. Notified Corp. security. Will send mobile security to check site. | All Water System ROC General | 2025-10-10
ROC | October | MKETFA- Water System Fire Storage Vol Low Alarm. Called Toronto (Zoran) to request a pump on. | All Water System ROC General | 2025-10-10
ROC | October | KSTP- Clearwell level Lo Alarm. Just dipped to low level and alarm cleared. | All Water System ROC General | 2025-10-10
ROC | October | SHTP, Filter 2/3 Turbidity Hi alarm, Filter 1 in backwash, directed to disregard as per shift report. if another hi turb comes in, will contact operator | All Water System ROC General | 2025-10-13
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-13
ROC | October | MTETNL- Outlet Flow Hi Alarm. Duty activated and still losing from tower. Notified Patrick F. Possible that town is flushing. Will monitor for about an hour and call Town of EG if does not improve. | All Water System ROC General | 2025-10-02
ROC | October | KSTKWP - Divya P on site for Cl17 analyzer maintenance. May see associated alarms. | All Water System ROC General | 2025-10-02
ROC | October | Angelica Chepiga signing in,weather +17C | All Water System ROC General | 2025-10-02
ROC | October | QVW12 - Combine chlorine Low alarm , Duty recently deactivated. Combine chlorine value recovered, alarm cleared. | All Water System ROC General | 2025-10-02
ROC | October | RHPSPA - GEN ATS 1 Normal Power NOT OK, Generator warning, and generator running alarms came in. Checked site. Pump 1 is man/on for pressure. When the power was off, kicked pump 1 off. Checked Alectra outage map which indicated an outage occurred at 07:35. No restoration time available. Called Divya P. as shift report only indicates to disregard generator warning alarm. Divya P. directed to place pump 1 man/on and to give him a heads up once restoration has occurred. Generator fuel levels are ok. 09:30 - Power was fully restored at 09:25 and placed pump 1 back to man/on again as the transfer from generator power to hydro power kicked the pump off again. Informed Divya P. #CONSULT | All Water System ROC General | 2025-10-05
ROC | October | NBW3 - Influent Free Chlorine Lo alarm came in. Checked site. Duty is not active but well 7 is running in schedule mode. After 5 mins, free chlorine levels rose back to optimal range and alarm cleared | All Water System ROC General | 2025-10-05
ROC | October | NMVCBA- Placed back in auto GWTP- Matt S working on lowlift pump programming QVW34- Influent free Cl2 hi alarm came in. Cleared after 3 mins | All Water System ROC General | 2025-10-08
ROC | October | AUPSRR - Post injection free chlorine hihi alarm. Checked site, trending shows a small spike of the free chlorine reading which returned to normal range within one reading interval reset alarm. | All Water System ROC General | 2025-10-13
ROC | October | GWTP - Low Lift Discharge Turbidity fault alarm came in. Called Dan Z. who directed to disregard until tuesday morning #CONSULT | All Water System ROC General | 2025-10-11
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-11
ROC | October | NMVCBA- Changed flow setpoint from 40L/s to 60L/s NMVCIB- Changed flow setpoint from 80L/s to 60L/s QVW3- man/on | All Water System ROC General | 2025-10-14
ROC | October | KLPSWL- Tyler Z done on site alarms cleared | All Water System ROC General | 2025-10-06
ROC | October | Ethan U signing in Weather 27. | All Water System ROC General | 2025-10-06
ROC | October | MARS, Valve House Cl Resid Hi alarm, Contacted Toronto operator Brett to see what residual they are putting out, Brett informed ROC that they are looking normal on their end and the total residual that's being sent out at this time is 1.46mg/L. ROC then contacted ARPS. Operator name was Jerry, informed him of the situation and he informed the ROC that their residuals are normal as well, Total being 2.76mg/L and monochloramine being 2.29. ROC then contacted David T to inform him of the situation, he will log into SCADA to investigate further. 01:25, David T is heading to site TMC317 = 1.46 mg/L (Total) ARPS = 2.76mg/L (Total) ARPS = 2.29 (monochloramine CMU5: W11350014 | All Water System ROC General | 2025-10-09
ROC | October | 145 Harry Walker ROC - SCADA Server room access granted via Mike O for the following Apurya T from (Honeywell ) and Scott L (Property Services) for access card replacement | All Water System ROC General | 2025-10-14
ROC | October | BLETNL- Historian heartbeat alarm no trends. Notified Artour L. Will take a look on SCADA | All Water System ROC General | 2025-10-14
ROC | October | SHTP- Reservoir total Cl2 lo alarm came in. Notified Benson S. on site monitoring residual | All Water System ROC General | 2025-10-14
ROC | October | NMTKBS, Placed pump 4 man/off | All Water System ROC General | 2025-10-14
ROC | October | STW3 - Tyson C activated STW3 in manual mode. | All Water System ROC General | 2025-10-02
ROC | October | ARPS- Total ammonia fault came in no pumps active no water directed to users resulting from starting and stopping pumps during PLC upgrades | All Water System ROC General | 2025-10-06
ROC | October | Connor Smith signing out | All Water System ROC General | 2025-10-12
ROC | October | MKRSEM - Called Toronto Water (Peter) and requested two pumps on to push flow to MKRSEM. | All Water System ROC General | 2025-10-02
ROC | October | GRTPLL - Low lift Pum 3 uncomm stop alarm, duty rotated to another pump. Alarm cleared. | All Water System ROC General | 2025-10-02
ROC | October | HLETYS-Adjusted Hypo pump 2 Max flow from 150 to 145 mL/min to increase chlorine residual. | All Water System ROC General | 2025-10-03
ROC | October | GWTP, Stephen B is heading to site to work on Low Lift Pump 3. That pump will be locked out, disregard alarms from LL Pump 3 | All Water System ROC General | 2025-10-14
ROC | October | MTW12- Joe W onsite running well in Local for sample | All Water System ROC General | 2025-10-08
ROC | October | NBW2 - Scrubber gas leak, Eric S tested alarm. | All Water System ROC General | 2025-10-09
ROC | October | STETTL/STETBR- Dan from AQWA is flushing in system | All Water System ROC General | 2025-10-06
ROC | October | ARPS, David from Peel called, Notified the ROC that the pump is back on however they will be starting and stopping their pumps for their testing. Once they are done, they will call back informing the ROC that we can go back to normal operation | All Water System ROC General | 2025-10-06
ROC | October | NMETYS- Evgeny S done work on OIT. AUW57- Influent free hi alarm came in trends recovered after 3 mins alarm cleared | All Water System ROC General | 2025-10-06
ROC | October | NMVCBA- Placed valve manual 40L/s to slow NMETIB down cycle. | All Water System ROC General | 2025-10-03
ROC | October | NMTKKC - Joe D testing temp , flood alarms and working on chemical pumps. Requested Duty 1 stop back to 75%. | All Water System ROC General | 2025-10-09
ROC | October | Gluzen Ramos Ong signing out | All Water System ROC General | 2025-10-07
ROC | October | YWS+NYWS normal | All Water System ROC General | 2025-10-14
ROC | October | NRETCR - Activate duty 1 MARS - Begin Maple to JFRS feed to assist in filling storages while keeping demand from BVPS minimal | All Water System ROC General | 2025-10-15
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-15
ROC | October | NMTKBS- Free CL2 hi alarm came in. Slowly been rising since 16:00. Exceeding hihi alarm and not recovering. Verified analyzer at AUPSOH supplying NMTKBS looks okay. Notified Divya P. Directed to disregard unless the combined lo alarm comes in #consult | All Water System ROC General | 2025-10-01
ROC | October | AUW57- Found well in man/off. No indication of issue on site and no mention of issue with well on Central water shift report. Placed back in auto | All Water System ROC General | 2025-10-01
ROC | October | KSTP - Donald M. running generator | All Water System ROC General | 2025-10-03
ROC | October | AUW14- Jerry Z on site to run diesel and clean analyzers on site | All Water System ROC General | 2025-10-07
ROC | October | AUPSWS- William M onsite for PMs including running generator, hi low temp and flood alarm | All Water System ROC General | 2025-10-09
ROC | October | MAP8 - P4 multilin trip alarm. Informed Jacob M, will look into issue | All Water System ROC General | 2025-10-10
ROC | October | KSTP- Donald M requested to place Hight Lift and Low Lift Pumps man/off. Can disregard chlorine leak alarm. MTW3- Patrick F onsite working on silicate pump 3 | All Water System ROC General | 2025-10-02
ROC | October | STW3 - Place well back in auto | All Water System ROC General | 2025-10-16
ROC | October | GRTPLL - Low lift Drainage chamber Level lolo alarm. Will monitor and clear alarm when level recover. 16:45 GRTPLL- Stephen B requested Low lift Drainage pump 1 back to auto. | All Water System ROC General | 2025-10-09
ROC | October | Toronto Water- Peter called. they are back to normal operations for now. Will leave just the one BVPS pump running to help them recover. Still filling with one pump 74% (5.21m) MKRSEM- Requested a second pump on MKRSMR- Peter requested to fill to 4.5m duty stop instead of 5.0m | All Water System ROC General | 2025-10-10
ROC | October | SHTP- Filter 3 Hi Turbidity Hi Alarm. Backwash was just completed. Cleared alarm as per SCADA Report. | All Water System ROC General | 2025-10-11
ROC | October | Adeela Khan signing in. Weather: 11C and partly cloudy | All Water System ROC General | 2025-10-11
ROC | October | AUPSRR - Post injection free chlorine hihi alarm. Checked site, trending shows a small spike of the post injection free chlorine which returned to normal range within one reading interval. Reset alarm. | All Water System ROC General | 2025-10-13
ROC | October | VNRSKS - Activated duty 1 to draw down MARS | All Water System ROC General | 2025-10-13
ROC | October | NMW15- William M onsite for work orders including analyzer work. Disregard all alarms while onsite. | All Water System ROC General | 2025-10-03
ROC | October | MARS - Jacob M. cleaning Peel analyzers STW12 - Patrick F. attending outstanding ntu fault. CMU W11335682 | All Water System ROC General | 2025-10-03
ROC | October | NMETHW- Joe D heading to site for sampling. Requested QVW12, QVW34 man/off 08:38- Joe D requested wells back into auto | All Water System ROC General | 2025-10-08
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-16
ROC | October | AUPSWS - Lee F finished on site and heading to JFPS. | All Water System ROC General | 2025-10-02
ROC | October | NMTKBS - Historian Heartbeat alarm came in. Called Artour L. who will take a look 08:53 - Artour L. called back to inform that the historian heartbeat has been cleared. CMU5 Created W11356815 #CONSULT #CMU5 | All Water System ROC General | 2025-10-11
ROC | October | QVW34- Placed well 3 into auto | All Water System ROC General | 2025-10-11
ROC | October | SHTP- Gas Analyzer 3 Methane Fault Alarm. Notified Dave T. Directed to disregard until Tuesday. CONSULT | All Water System ROC General | 2025-10-11
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-03
ROC | October | RHMCMD - Man/close valve to keep water in MARS as demand is high KSTP - Rin water fluoride res lolo, level has been having dips periodically, readings came back to normal range | All Water System ROC General | 2025-10-14
ROC | October | KSTKWP- Donald M onsite for chamber work. Placed tower level in calibration mode. Also testing basement flood alarm and working on Cl analyzers. | All Water System ROC General | 2025-10-02
ROC | October | Received call from Stacey (Purcell, PM of commercial bldg on 8540 Keele St (Keele and Langstaff). She informed of suspected leak of private hydrant between two buildings. Call was forwarded by Public Health. She informed she already contacted City of Vaughan, who guided her to call the Region. Confirmed with Gary P. no YR operated hydrants in area. Notified Mike P. (Vaughan). he will follow up with Stacey | All Water System ROC General | 2025-10-09
ROC | October | STRS48- Travis W requested to clear fault alarm on sample pump 1 and place into duty 1 | All Water System ROC General | 2025-10-08
ROC | October | KCETDS - Activated D1. | All Water System ROC General | 2025-10-15
ROC | October | Ethan Ullalkar signing out. | All Water System ROC General | 2025-10-04
ROC | October | Completing Maple to Jefferson Feed. Reverting changes. | All Water System ROC General | 2025-10-05
ROC | October | MARS, Notified Peter from Toronto to go back to normal flow | All Water System ROC General | 2025-10-06
ROC | October | QVETQS- Outlet Total HiHi, Combined Hi Chlorine alarms. Notified Divya P. He is onsite working on analyzers and will take grabs to verify | All Water System ROC General | 2025-10-03
ROC | October | AUETFC - Tower low level alarm. Duty is active, flow out. Notified Joe D, he will check SCADA. | All Water System ROC General | 2025-10-15
ROC | October | RHPSPA - Deactivated Duty 1 RHVCEM - Open to 50% | All Water System ROC General | 2025-10-15
ROC | October | SHTP, Filter 3 Turbidity Hi alarm, Turb spiked from backwash, NTU is dropping back down to normal range, if alarm comes in again, will notify operator as per shift report | All Water System ROC General | 2025-10-08
ROC | October | HLETYS- Artour L done on site NRETBR- Red B done on site | All Water System ROC General | 2025-10-15
ROC | October | Angelica Chepiga signing in,weather +11C | All Water System ROC General | 2025-10-15
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-14
ROC | October | YWS + NYWS Normal NMETHW - Activated duty 1. | All Water System ROC General | 2025-10-05
ROC | October | Christian Van Beek signing out. | All Water System ROC General | 2025-10-05
ROC | October | RHVCEM - Comfirmed with Dwayne L and adjusted VC from 100 to 20%/ | All Water System ROC General | 2025-10-15
ROC | October | RHRSWA- changed D1- from 60%-89% D2- from 66%-79% D3- from 58%-76% as per interim | All Water System ROC General | 2025-10-15
ROC | October | STPS48- Reset alarms and Pumps 1/2 started okay. outlet free Cl2 lo alarm came in but will recover shortly with flow returning to normal | All Water System ROC General | 2025-10-15
ROC | October | NMETIB - Activated duty 1 to keep tower level offset. | All Water System ROC General | 2025-10-02
ROC | October | QVW34 - Place well 3 man/on to assist in flow through ringwell to NMETHW | All Water System ROC General | 2025-10-12
ROC | October | NMETIB - Deactivated duty 1 to keep fill cycle offset from NMETHW. | All Water System ROC General | 2025-10-13
ROC | October | RHRSWA, Jacob M on site, Testing pumps and flood alarms | All Water System ROC General | 2025-10-06
ROC | October | NMTKKC, Talha H resetting OIT | All Water System ROC General | 2025-10-06
ROC | October | STETBR - Travis W cleaning chlorine analyzers, Health and Safety check. | All Water System ROC General | 2025-10-15
ROC | October | MKMCAP - Rob P on site, testing flood alarm. | All Water System ROC General | 2025-10-15
ROC | October | STETBR- Patrick F and Travis W on site to work on altitude valve ANVCPL- Increased flow setpoint from 110L/s from 120L/s 11:06-ANVCPL- Increased flow setpoint from 120L/s from 110L/s | All Water System ROC General | 2025-10-15
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-07
ROC | October | STW12 - Pumps 1&2 man/on for STETBR fill cycle. | All Water System ROC General | 2025-10-01
ROC | October | RHMCMD - man/open 100%. | All Water System ROC General | 2025-10-15
ROC | October | NMTKBS - Free chlorine high alarm. Will M headed to site. | All Water System ROC General | 2025-10-02
ROC | October | MAPS- Cole W onsite for PMs. Exercising pipe gallery valve, Peel inlet valve and North Cell. He is monitoring. | All Water System ROC General | 2025-10-02
ROC | October | Christian Van Beek signing out. | All Water System ROC General | 2025-10-04
ROC | October | GWTP - GAC 2 Filter Turbidity Hi alarm came in. Checked site. Levels have come back to optimal range after a spike | All Water System ROC General | 2025-10-05
ROC | October | NBW5 - Hi turbidity alarm cleared, placed well5 pump back to auto. | All Water System ROC General | 2025-10-03
ROC | October | RHPSPA - Discharge Header pressure Hi alarm. Deactivated D1. Pump 1 running in manual mode. Pressure back to normal. RHVCEM - Adjusted from 15 to 30%. | All Water System ROC General | 2025-10-03
ROC | October | AUETFC - Joe D called, system back to normal. | All Water System ROC General | 2025-10-15
ROC | October | HLETYS - Eric S working on ammonia tank LIT. | All Water System ROC General | 2025-10-15
ROC | October | MTW3 - Patrick F cleaning chlorine analyzers. | All Water System ROC General | 2025-10-15
ROC | October | STRS48- Travis W requested pump 2 in man/on | All Water System ROC General | 2025-10-07
ROC | October | STPS48- Both pumps unavailable STRS48- High lift pump 2 uncommanded stop. Spoke with Travis W. Cleared alarms and placed High lift pumps back into auto | All Water System ROC General | 2025-10-07
ROC | October | Richmond Hill main break- Dwayne L offsite was able to close valve and stop leak as well as pump out chamber. Req one pump at RHPSPA is to remain on until an operator can verfiy if it can be placed back in auto due to pressure concerns in area. | All Water System ROC General | 2025-10-01
ROC | October | AUW14- Influent free Cl2 hi alarm came in on well start up. Trends recovered alarm cleared after 3 mins | All Water System ROC General | 2025-10-01
ROC | October | H1GWTPP1 - Chris S rebooting OIT. | All Water System ROC General | 2025-10-01
ROC | October | RHPSWA - Man/start pump 1 | All Water System ROC General | 2025-10-15
ROC | October | RHPSPA - Man/stop pump 1 JFRS - Begin Maple to JFRS feed | All Water System ROC General | 2025-10-15
ROC | October | STETTL - Jason from Town of Stouffville called, flushing in Zone 2 for a few hours. Duty just activated, tower draining. Deactivated STETBR Duty as per Dan Z. STETBR - Duty start level setpoint changed from 60 to 50%. | All Water System ROC General | 2025-10-15
ROC | October | SHTP - filter 1 turbidity hi alarm. Checked site, filter 2 going through a backwash sequence. Filter 1 trending shows a spike of the filter turbidity which quickly returned to normal range. Reset alarm. | All Water System ROC General | 2025-10-03
ROC | October | NMVCBA- Chris I done on site KLPSWL- Tyler Z on site to work on generator. will call when done KSETDP- Inlet total/free Cl2 hihi alarm came in. Disregard on shift report. Spike on duty start up | All Water System ROC General | 2025-10-06
ROC | October | STPSMR - Jack P and Patrick F changing chlorine cylinders. Disregard chlorine leak alarm for the duration of the work. | All Water System ROC General | 2025-10-15
ROC | October | BLETNL-Shawn from town of Stouffville/ Whitchurch called to inform of flushing in system | All Water System ROC General | 2025-10-15
ROC | October | RHRSWA - Activate duty 1 | All Water System ROC General | 2025-10-15
ROC | October | VNPS PD8- Deactivated D2 | All Water System ROC General | 2025-10-15
ROC | October | Angelica Chepiga signing in, weather +10C | All Water System ROC General | 2025-10-01
ROC | October | NMTKBS- Free Cl2 hihi alarm came in Critical priority alarm. Notified Divya P. Directed to continue to disregard unless combined lo alarm came in #consult | All Water System ROC General | 2025-10-01
ROC | October | STRS48 - Sample Pump 1 Fault alarm came in. Sample Pump 2 kicked on in duty 1 and sample pump 1 faulted and went OOS and unable to reset. Called Tyson C. but no answer. Will try again 20:12 - Tyson C. called back and directed to place sample pump 1 man/off for the night . Tyson C. also directed to place zone 1 and 2 at Stouffville filling at the same time to help with residuals #CONSULT | All Water System ROC General | 2025-10-07
ROC | October | Adam Button signing out | All Water System ROC General | 2025-10-07
ROC | October | YWS + NYWS Normal | All Water System ROC General | 2025-10-05
ROC | October | SHETCS- Benson S on site to work on hypo pumps | All Water System ROC General | 2025-10-15
ROC | October | STPS48 - Dan Z called, contractor finished on site, back to normal OP. Dan Z requested clear alarms, restart pumps and place turbidity meter to calibration mode. Travis W on site, will call when leaving. STRS48 - Dan Z requested Wells 5 and 6 pumps to auto, HL pumps to auto. | All Water System ROC General | 2025-10-15
ROC | October | GWTP- Stephen B notified ROC to disregard Chemical room gas level alarm as delivery in progress. NMW15- Ryan B on site to clean turbidity meter AUW14- Jerry Z and Donald M on site for Cl2 system overhaul. Wells will be in man/off | All Water System ROC General | 2025-10-15
ROC | October | Adeela Khan Signing in. Weather: 14 C and clear | All Water System ROC General | 2025-10-05
ROC | October | KSTP - Fin water flouride res lolo, reading came back up to normal range | All Water System ROC General | 2025-10-05
ROC | October | NMVCBA- Placed in manual at 40L/s | All Water System ROC General | 2025-10-08
ROC | October | KSTP - Fin Water Fluoride LoLo alarm came in. Duty recently activated. Will monitor 20:30 - Levels came back to optimal range | All Water System ROC General | 2025-10-07
ROC | October | MKRSMR- Peter from Metro called Horgan shutdown has been completed. Req D1 start be changes from 3.0m to 2.0m. | All Water System ROC General | 2025-10-08
ROC | October | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-10-29
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-24
ROC | October | 11:59 - Odour Complaint: Public Health Inspector (289-763-8055 lesya.aleksandroff@york.ca) informed strong sewage odour observed along Yonge. Complaint orginated from tenant at 11685 Yonge Street. Lesya informed complaint was forwarded from RH Councillor's office. Notified Daniel K. He will attend and update Lesya of findings. CMU5 W11393252 | All Wastewater System ROC General | 2025-10-24
ROC | October | HMSS- Lauren S onsite for wet well cleaning. Will begin with drawing down cell 1. Disregard related alarms. | All Wastewater System ROC General | 2025-10-27
ROC | October | Adam Button signing in 2C clear | All Wastewater System ROC General | 2025-10-17
ROC | October | YDSS + YNSS Normal Carter Dunn Signing Out | All Wastewater System ROC General | 2025-10-29
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-21
ROC | October | Ethan Ullalkar signing out. | All Wastewater System ROC General | 2025-10-27
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-27
ROC | October | KSSSQW - Dry well supply exhaust fan VFD, odour exhaust, wet well fan exhaust. Called Kevin K, disregard for the night, will take a look in the morning Consult | All Wastewater System ROC General | 2025-10-27
ROC | October | MTSP - Clarifier 1 no RAS pump running alarm. SCADA shows that both clarifiers running, verified with Berry M- Clarifier 1 is offline and draining. Disregard alarm. | All Wastewater System ROC General | 2025-10-26
ROC | October | AUSSYS, Terry R is leaving site, Pumps 2/4 are back in duty. Wet well back in service | All Wastewater System ROC General | 2025-10-30
ROC | October | Angelica Chepiga signing in,weather +11C | All Wastewater System ROC General | 2025-10-17
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-18
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-18
ROC | October | SEOC - OCF Damper Station Flood Switch Alarm came in. Disregarded as per shift report | All Wastewater System ROC General | 2025-10-20
ROC | October | Connor Smith signing in 7C Rainy | All Wastewater System ROC General | 2025-10-30
ROC | October | SUSR - Darren B testing temp alarm. | All Wastewater System ROC General | 2025-10-16
ROC | October | RHAMF1- Kyle C working on commissioning site. Disregard alarms. | All Wastewater System ROC General | 2025-10-17
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-18
ROC | October | Adeela Khan signing out | All Wastewater System ROC General | 2025-10-18
ROC | October | Christian Van Beek signing in. Weather: 1C and clear. | All Wastewater System ROC General | 2025-10-28
ROC | October | NBSP - RAS train 1 flow low alarm. Checked site, trending shows a small dip below the low alarm setpoint. The flow returned to normal range shortly afterward. Cleared alarm. | All Wastewater System ROC General | 2025-10-28
ROC | October | YDOC OCF - Brent St Croix on site for a generator load test. Brent stated that the associated alarms can be disregarded. | All Wastewater System ROC General | 2025-10-28
ROC | October | EGSSSC - Generator coolant temp warning alarms/ cleared right away and followed by diesel failure alarms on the dialer. Emailed Kevin K. | All Wastewater System ROC General | 2025-10-29
ROC | October | Adam Button signing out | All Wastewater System ROC General | 2025-10-17
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-17
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-29
ROC | October | KBSP - Filter Influent channel 1 level HiHi alarm, quick spike, cleared alarm. | All Wastewater System ROC General | 2025-10-18
ROC | October | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-10-18
ROC | October | MTSP- Chris R on site trouble shooting alum pumps and diverting to lagoon for UV maintenance for majority of day | All Wastewater System ROC General | 2025-10-23
ROC | October | AUSS - Christine from Security will be on site and entering the SCADA room 12:58 - Christine is finished on site | All Wastewater System ROC General | 2025-10-30
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-30
ROC | October | KSSP, Mike B on site testing the chemical system, directed to disregard until he is finished on site | All Wastewater System ROC General | 2025-10-21
ROC | October | AUSSYS- Power failure on site with generator running. NO issues on site. Will contoinue to monitor | All Wastewater System ROC General | 2025-10-31
ROC | October | KBSP - Filter influent channel 1 level hihi alarm. Checked site, trending shows a spike of the filter influent channel level which is dropping quickly. Able to reset alarm. | All Wastewater System ROC General | 2025-10-21
ROC | October | NBSP- Gavin W on site for generator run | All Wastewater System ROC General | 2025-10-16
ROC | October | AUSSSR - Chris R responded to line 1 alarm. Created CMU = 11403623 | All Wastewater System ROC General | 2025-10-29
ROC | October | YDSS+YNSS normal Adam Button signing out | All Wastewater System ROC General | 2025-10-16
ROC | October | Adeela Khan signing in. Weather: 7C and sunny | All Wastewater System ROC General | 2025-10-27
ROC | October | EGSSSC, Neil O on site, doing wet well cleaning | All Wastewater System ROC General | 2025-10-21
ROC | October | PVSS - Historian heartbeat alarm. Checked site, operations are normal, no clear impact to trends. Unable to reset alarm. Called Ian W who will check the system. | All Wastewater System ROC General | 2025-10-27
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-21
ROC | October | Adeela Khan signing out | All Wastewater System ROC General | 2025-10-21
ROC | October | KBSP- Lance J onsite testing the filter bypass float alarm. | All Wastewater System ROC General | 2025-10-21
ROC | October | LSSS, Placed pump 3 in D1 for Amelia from EME | All Wastewater System ROC General | 2025-10-24
ROC | October | Connor Smith signing in 2C Cloudy | All Wastewater System ROC General | 2025-10-27
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-22
ROC | October | Patriot Sever- Kingsley M done reset | All Wastewater System ROC General | 2025-10-22
ROC | October | Adam Button signing out | All Wastewater System ROC General | 2025-10-23
ROC | October | KSSP-Mem Basement MUA-9 Temp switch- disregard as per SCADA review. | All Wastewater System ROC General | 2025-10-29
ROC | October | AUSS - Pump 2 disch valve LV2 fail to open alarm. Checked site, duty rotated to pump 4 which is operating normally. Reset alarm. | All Wastewater System ROC General | 2025-10-31
ROC | October | NMSSBP- Wet well 1/2 Hydrostatic/Ultrasonic hi alarms , duty 2 just activated. Cleared alarms. | All Wastewater System ROC General | 2025-10-28
ROC | October | KBSP - Filter influent channel 1 hihi level alarm. Checked site, trending indicates a rise of the filter influent channel which is returning to normal range. Able to reset alarm. | All Wastewater System ROC General | 2025-10-27
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-27
ROC | October | Angelica Chepiga signing in | All Wastewater System ROC General | 2025-10-21
ROC | October | KBSP - Lance J testing head works and tertiary sump flood alarms. | All Wastewater System ROC General | 2025-10-16
ROC | October | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-10-18
ROC | October | AUSSYS - Power failure and wetwell high alarms on the dialer. Checked SCADA. All trends normal. | All Wastewater System ROC General | 2025-10-18
ROC | October | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-10-19
ROC | October | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-10-19
ROC | October | Christian Van Beek signing in. | All Wastewater System ROC General | 2025-10-27
ROC | October | Angelica Chepiga signing in | All Wastewater System ROC General | 2025-10-16
ROC | October | YDOC3 - Chris R on site. | All Wastewater System ROC General | 2025-10-16
ROC | October | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-10-17
ROC | October | Angelica Chepiga signing in | All Wastewater System ROC General | 2025-10-24
ROC | October | YDOCF- Brent S onsite for generator maintenance. Will also be working on fans. | All Wastewater System ROC General | 2025-10-27
ROC | October | SHSP- Lauren S on site to run generator | All Wastewater System ROC General | 2025-10-16
ROC | October | LSSS - Kingsley restarting server, disregard heartbeat alarm | All Wastewater System ROC General | 2025-10-22
ROC | October | KSSP, Cam B on site, working on the UV channel 2 | All Wastewater System ROC General | 2025-10-30
ROC | October | Christian Van Beek signing out. | All Wastewater System ROC General | 2025-10-22
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-22
ROC | October | HMSS - Bar screen 2 fault, currently OOS & in local as recorded on site logbook from yesterday | All Wastewater System ROC General | 2025-10-29
ROC | October | Ethan Ullalkar signing out. | All Wastewater System ROC General | 2025-10-24
ROC | October | NMVCBP - FM valve FM2 overtorque. Called Neil O, he is on site, will check. | All Wastewater System ROC General | 2025-10-21
ROC | October | YDSS+YNSS normal | All Wastewater System ROC General | 2025-10-24
ROC | October | YDSS+YNSS normal | All Wastewater System ROC General | 2025-10-25
ROC | October | EGSSSC- Parth P and Rick L on site for annual calibrations | All Wastewater System ROC General | 2025-10-16
ROC | October | RHAMF - Unit 1 recirculating pump 1 overload, pump 2 running. Called Barry M no response, left voicemail. 22:42 - Barry M called back and okay to disregard Consult | All Wastewater System ROC General | 2025-10-23
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-23
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-24
ROC | October | NBSP- Inlet level hihi and Loss of echo came in. Checked trends quick spike and recovered and trending normally. Reset alarms. YDSS+YNSS normal | All Wastewater System ROC General | 2025-10-25
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-27
ROC | October | YDSS + YNSS normal | All Wastewater System ROC General | 2025-10-28
ROC | October | NBSP - Marcus R on site to continue work on the aeration tanks. Marcus will be manipulating the RAS flow to the aeration tanks which may produce associated alarms. Marcus R directed to disregard these associated alarms. | All Wastewater System ROC General | 2025-10-28
ROC | October | AUSSSR- Line 2 Valve Overtorque. Line 1 already OOS. Notified Central East OPS. W11400017 CMU5 for Marcos T and Chris R. | All Wastewater System ROC General | 2025-10-28
ROC | October | Angelica Chepiga signing in, weather +11C | All Wastewater System ROC General | 2025-10-28
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-19
ROC | October | SUSP - UV lamp fail and UV low intensity alarms. Shift report directs to disregard the lamp fail alarms. The plant recently stopped diverting to lagoon and initiated filter feed flow. Called Kevin K who is on site and stated the alarms were expected and operations are normal. | All Wastewater System ROC General | 2025-10-20
ROC | October | YDSS + YNSS Normal Adeela Khan signing out | All Wastewater System ROC General | 2025-10-27
ROC | October | YDSS + YNSS Normal Christian Van Beek signing out. | All Wastewater System ROC General | 2025-10-19
ROC | October | KSSP - Recirculation Pump 1 No flow alarm. Checked site. Called Mike B. who will take a look 04:00 - Mike called back to inform that this can be disregarded for a couple hours and an operator will attend site #CONSULT | All Wastewater System ROC General | 2025-10-21
ROC | October | AUSSSR - Lane 1 valve Overtorque and Line 1 valve failed to close alarms - emailed Barry M. | All Wastewater System ROC General | 2025-10-29
ROC | October | NBSP - Filter Reject Sump level Low alarm, value dropped for one reading and recover. Alarm cleared. | All Wastewater System ROC General | 2025-10-29
ROC | October | MTSP - Aeration tank 2 dissolved oxygen low alarm. Checked site, two blowers are active in auto mode and the third blower is OOS in local/off. While monitoring the DO reading increased above low alarm setpoint. Cleared alarm. | All Wastewater System ROC General | 2025-10-20
ROC | October | YDSS + YNSS normal | All Wastewater System ROC General | 2025-10-20
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-20
ROC | October | Carter Dunn Signing In | All Wastewater System ROC General | 2025-10-20
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-28
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-21
ROC | October | HLSSBS - Chase J on site and will be triggering a flood alarm. | All Wastewater System ROC General | 2025-10-27
ROC | October | SHSP, David D on site working on WAS2//RAS3 pumps | All Wastewater System ROC General | 2025-10-30
ROC | October | Angelica Chepiga signing in, weather +21C | All Wastewater System ROC General | 2025-10-18
ROC | October | Adam Button signing out | All Wastewater System ROC General | 2025-10-31
ROC | October | GRSSWA - Neil O & Chase J onsite for hi level testing in wet well. WIll be entering wet well for testing | All Wastewater System ROC General | 2025-10-29
ROC | October | NMSSHS- Generator running alarm came in. Checked site no power loss alarms cleared once generator shutdown. | All Wastewater System ROC General | 2025-10-22
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-18
ROC | October | SUSP - Man/start WAS pump 1 an behalf of Kevin K | All Wastewater System ROC General | 2025-10-22
ROC | October | KSSSQW- Chase J on site to test high wet well and overflow alarms | All Wastewater System ROC General | 2025-10-22
ROC | October | KSSP, SHTP, KBSP, MTSS - Kingsley M rebooting these servers as well | All Wastewater System ROC General | 2025-10-22
ROC | October | KSSP- Dave D on site to wrok on odor control sump pit hi level float | All Wastewater System ROC General | 2025-10-23
ROC | October | KCSSKR - Power restored, generator off | All Wastewater System ROC General | 2025-10-23
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-31
ROC | October | AUSS - Wet well 2 ultrasonic LoLo alarm came in along with Hydrostatic lo alarms came in. Checked site. Levels came back to optimal range and alarms have cleared | All Wastewater System ROC General | 2025-10-21
ROC | October | NMSSEQ - Kingsley M rebooting server, disregard hearbeat alarm | All Wastewater System ROC General | 2025-10-22
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-27
ROC | October | BLSS - Wetwell 1 bubbler hihi alarms, Lance J. testing, he will clear | All Wastewater System ROC General | 2025-10-24
ROC | October | SECC, HVAC General Alarm, Notified Philip R, he will head to site | All Wastewater System ROC General | 2025-10-21
ROC | October | SUSSSR- David D done on site | All Wastewater System ROC General | 2025-10-23
ROC | October | SUSP - Lagoon hydrostatic level hihi outstanding, notified Chris C., informed he is on site, visual of chamber okay. | All Wastewater System ROC General | 2025-10-24
ROC | October | SEOC - OCF Damper Station Flood switch. Disregard as per shift report | All Wastewater System ROC General | 2025-10-24
ROC | October | Angelica Chepiga signing out | All Wastewater System ROC General | 2025-10-24
ROC | October | KSSP - Power failure alarms, UV critical failure alarms. Called Mike B, he is running generator, will clear all alrms. | All Wastewater System ROC General | 2025-10-16
ROC | October | Angelica Chepiga signing out | All Wastewater System ROC General | 2025-10-24
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-24
ROC | October | YDSS+YNSS normal | All Wastewater System ROC General | 2025-10-24
ROC | October | LSSS- Amelia from Sewer Use Bylaw requested pump 3 in duty 1 for sampling. | All Wastewater System ROC General | 2025-10-17
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-25
ROC | October | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-10-18
ROC | October | Adeela Khan signing in. Weather: 16C and rain | All Wastewater System ROC General | 2025-10-19
ROC | October | SUSP - UV system critical fault alarm, notified Kevin K, he will check. | All Wastewater System ROC General | 2025-10-21
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-31
ROC | October | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-10-17
ROC | October | YDSS+YNSS normal | All Wastewater System ROC General | 2025-10-26
ROC | October | YDSS+YNSS normal | All Wastewater System ROC General | 2025-10-26
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-23
ROC | October | MTSP - Historian Heartbeat alarm. Checked site, operations appear normal, trends are not affected. Unable to clear alarm. Called Ian W who will check the system. Created CMU5#W11388166 #consult #CMU5 | All Wastewater System ROC General | 2025-10-23
ROC | October | KBSP - RAS pump 4 no flow alarm. Checked site, RAS pump 4 is interlocked on a no flow alarm. Able to reset alarm, monitored pump activation. Pump interlocked again due to no flow. RAS pump 4 possibly clogged. Contacted Dan H who directed to leave the pump interlocked and disregard for the night. Placed pump manual/off. #consult | All Wastewater System ROC General | 2025-10-23
ROC | October | Angelica Chepiga signing in,weather -1C | All Wastewater System ROC General | 2025-10-26
ROC | October | KSSP - Supernatant tank 1 HiHi alarm, 2 pumps running, alarm cleared. | All Wastewater System ROC General | 2025-10-26
ROC | October | *WRONG BOOK* | All Wastewater System ROC General | 2025-10-28
ROC | October | NBSP - Dan H called, Aeration tank 1 DO back to normal. | All Wastewater System ROC General | 2025-10-26
ROC | October | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-10-26
ROC | October | YDSS + YNSS normal | All Wastewater System ROC General | 2025-10-26
ROC | October | KSSSQW - Site hydro Power failure and all pumps VFD Fault alarms came in. Generator Running alarm also came in. Checked site. Hydro Power fail was able to clear along with generator running. Pump 2, 3, 4 VFD faults are outstanding and pump 1 is running in ultrasonic mode. Called Kevin K. who will take a look. 20:18 - Kevin K. called back to inform that he is headed to site. CMU5 Created W11397959 21:15 - Kevin K. called back to inform that all alarms have been cleared and he is finished on site #CONSULT #CMU5 | All Wastewater System ROC General | 2025-10-27
ROC | October | KCSSKRS- Talha H working on OIT. Disregard Heartbeat alarm. 11:05- Work completed. Cleared alarm. | All Wastewater System ROC General | 2025-10-28
ROC | October | KSSP - Odour sump hi hi level alarm. Called Cam B who is on site and will investigate. | All Wastewater System ROC General | 2025-10-28
ROC | October | Christian Van Beek signing out. | All Wastewater System ROC General | 2025-10-28
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-30
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-31
ROC | October | KBSP - Aeration basin 2 suspended solids fault alarm. Checked site, trending shows a sudden spike of the suspended solids reading to the max value which resulted in a reading fault. The reading quickly dropped to normal range. Able to clear alarm. | All Wastewater System ROC General | 2025-10-20
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-23
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-28
ROC | October | EGSSSC - Kevin K onsite confirming generator can run and will address the dialer alarm | All Wastewater System ROC General | 2025-10-29
ROC | October | SEOC/SEOC10 - No outage on map from Elexicon, Chris S inquiring about power confirming power. Requested Phil R to confirm power at site, will head to site | All Wastewater System ROC General | 2025-10-29
ROC | October | KBSP- Filter Influent Ch1 lvl hi alarm came in. Checked trends. Trends recovered quickly noticed the channel level is slightly elevated. Emailed West wastewater team about outstanding issue and alarm | All Wastewater System ROC General | 2025-10-22
ROC | October | YDSS+YNSS normal | All Wastewater System ROC General | 2025-10-23
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-24
ROC | October | KBSP - Aeration tank solids fault alarm. Checked site, trending shows a spike of the suspended solids reading which quickly returned to normal range. reset alarm. | All Wastewater System ROC General | 2025-10-19
ROC | October | AUSS- Terry R called to notifiy ROC that Cell 1 is back in operation. P3 can be run in manual to drawdown wet well while cell 2 is isolated for cleaning | All Wastewater System ROC General | 2025-10-22
ROC | October | Ethan Ullalkar signing out. | All Wastewater System ROC General | 2025-10-22
ROC | October | Christian Van Beek signing in. Weather: 13C and rain. | All Wastewater System ROC General | 2025-10-22
ROC | October | Adam Button signing out | All Wastewater System ROC General | 2025-10-22
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-16
ROC | October | NMSSBP - Diesel tank Hihi level alarm. Disregard as per the shift report. | All Wastewater System ROC General | 2025-10-17
ROC | October | Carter D signing in.3D/Clear | All Wastewater System ROC General | 2025-10-24
ROC | October | YDSS+YNSS normal | All Wastewater System ROC General | 2025-10-23
ROC | October | SHSP - Compressor 1 E.stop, PIT2 LoLo, recovered. Attempted to contact Lauren S., who signed on this morning and logged on site to assist contractors with compressors; no answer. Monitoring | All Wastewater System ROC General | 2025-10-24
ROC | October | Ethan Ullalkar signing out. | All Wastewater System ROC General | 2025-10-29
ROC | October | Connor Smith signing in | All Wastewater System ROC General | 2025-10-17
ROC | October | KBSP - Young J on site and will be deactivating wash pumps 1,2,3. May see associated alarms. | All Wastewater System ROC General | 2025-10-27
ROC | October | YDSS + YNSS normal | All Wastewater System ROC General | 2025-10-20
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-24
ROC | October | Angelica Chepiga signing out | All Wastewater System ROC General | 2025-10-16
ROC | October | LSSS- Amelia from EME is on site for sampling and req P6 to run. Rotated P6 into D1 and activated D1 | All Wastewater System ROC General | 2025-10-31
ROC | October | Connor Smith signing out | All Wastewater System ROC General | 2025-10-17
ROC | October | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-10-26
ROC | October | Patriot Server- Kingsley M restarting Server | All Wastewater System ROC General | 2025-10-22
ROC | October | NBSP - Marcus R. is on site and will be working on the DO sensors. Requested to disregard all DO related alarms until work is complete | All Wastewater System ROC General | 2025-10-30
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-17
ROC | October | Carter Dunn Signing Out | All Wastewater System ROC General | 2025-10-17
ROC | October | RHAMF- Process exhaust fan failed to start alarm outstanding. Notified Phil R directed to disregard all alarms from site | All Wastewater System ROC General | 2025-10-16
ROC | October | Christian Van Beek signing in. Weather: 19C and clear. | All Wastewater System ROC General | 2025-10-19
ROC | October | KBSP - Filter Influent Ch 1 Level HiHi alarm came in. Checked site. Level came back to optimal range within 2 mins. | All Wastewater System ROC General | 2025-10-27
ROC | October | YDSS + YNSS Normal KBSP - RAS combined no flow alarm. Checked site, RAS pump 2 is running and showing flow. Trending indicates normal operations. RAS pump 4 failed earlier in the night and Dan H directed to leave it OOS. Contacted Dan H who directed to disregard the alarm. 04:33 - KBSP - Dan H called back and directed to activate RAS pump 3. Placed RAS pump 3 in auto and confirmed flow is measured on the flow meter. RAS pump 4 remains Manual/off under suspicion of being clogged. #consult | All Wastewater System ROC General | 2025-10-23
ROC | October | KSSP- Cam B onsite testing headworks and basement gas monitors. | All Wastewater System ROC General | 2025-10-17
ROC | October | Bayview and Steeles- Phil R investigating odor complaint req. CMU5 to complete form. Created CMU5 W11387843. #CMU5 | All Wastewater System ROC General | 2025-10-22
ROC | October | Angelica Chepiga signing out | All Wastewater System ROC General | 2025-10-29
ROC | October | KSSSQW - Pump 2 uncommanded stop. Ack/reset Adeela Khan signing out | All Wastewater System ROC General | 2025-10-30
ROC | October | KBSP - Filter influent channel 1 level hihi alarm. Checked site, trending shows another spike of the influent channel level which quickly dropped below the alarm setpoint. cleared alarm. | All Wastewater System ROC General | 2025-10-22
ROC | October | AUSSYS - Terry R called to inform he has placed all pumps manual off to increase the wet well level. Terry has directed to disregard the hi and hihi level alarms if they come in | All Wastewater System ROC General | 2025-10-31
ROC | October | MTSP- Marcos T on site with contractor to work on Clarifier 1 | All Wastewater System ROC General | 2025-10-22
ROC | October | Adam Button signing in 10C clear | All Wastewater System ROC General | 2025-10-24
ROC | October | Adeela Khan signing in. Weather: 11C and sunny | All Wastewater System ROC General | 2025-10-20
ROC | October | YDSS + YNSS Normal Christian Van Beek signing out. | All Wastewater System ROC General | 2025-10-20
ROC | October | YDSS + YNSS Normal Connor Smith signing out | All Wastewater System ROC General | 2025-10-28
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-23
ROC | October | Ethan Ullalkar signing out. | All Wastewater System ROC General | 2025-10-16
ROC | October | AUEQSJ, Cell 2 Level hihi, Directed to disregard as person shift report | All Wastewater System ROC General | 2025-10-24
ROC | October | Christian Van Beek signing in. Weather: 13C and sun | All Wastewater System ROC General | 2025-10-21
ROC | October | Connor Smith signing in 11C Cloudy | All Wastewater System ROC General | 2025-10-29
ROC | October | KSSP, Mike B on site working on the filters, directed to disregard filter alarms on site | All Wastewater System ROC General | 2025-10-30
ROC | October | MTSP - Clarifier 1 no RAS pump running alarm. Checked site, RAS pump 1 is operating and flow is registering. SCADA review states that Clarifier 1 has been isolated and placed OOS for contractor work. | All Wastewater System ROC General | 2025-10-31
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-24
ROC | October | YDSS + YNSS Normal AUSSSR - Line 1 Overtorque alarm came in. Checked site. Line 2 and 3 are still available. Emailed Central east team Adeela Khan signing out | All Wastewater System ROC General | 2025-10-28
ROC | October | Adam Button signing in | All Wastewater System ROC General | 2025-10-31
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-28
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-30
ROC | October | Connor Smith signing in | All Wastewater System ROC General | 2025-10-28
ROC | October | Carter Dunn Signing In, 12D/Clear | All Wastewater System ROC General | 2025-10-16
ROC | October | Adeela Khan signing in. Weather: 11C and Clear | All Wastewater System ROC General | 2025-10-18
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-21
ROC | October | NMSSBP- P1 discharge valve failed to open. D1 not active. Reset alarm | All Wastewater System ROC General | 2025-10-26
ROC | October | NBSP - Dan H called about outstanding Aeration Basin 1 Back DO LoLo alarm. Alarm on disregard list on SCADA review. Dan H will attend site and check. | All Wastewater System ROC General | 2025-10-26
ROC | October | KBSP- Filter inlet channel 1/2 hi alarm came in recovered quickly. Notified Lance J cleared alarm and req call back if to comes back in | All Wastewater System ROC General | 2025-10-17
ROC | October | AUSS- P4 discharge valve failed t open alarm. Reset alarm | All Wastewater System ROC General | 2025-10-17
ROC | October | SUSSHS, Chris C/David D on site, entering the wet well, disregard wet well hi alarm 11:38. SUSSWB, Chris C/David D on site, entering the wet well, disregard wet well hi alarm. They are finished at SUSSHS. | All Wastewater System ROC General | 2025-10-29
ROC | October | NBSP- Marcus R onsite working on RAS pumps. Disregard related alarms. | All Wastewater System ROC General | 2025-10-27
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-31
ROC | October | Adeela Khan signing in. Weather: 5C and cloudy | All Wastewater System ROC General | 2025-10-31
ROC | October | Carter Dunn Signing In, 7D/Clear | All Wastewater System ROC General | 2025-10-21
ROC | October | SEOC4/8/12/SEBR/SEDC, PAC Comm Fail, Notified Ian W, he will look into it | All Wastewater System ROC General | 2025-10-29
ROC | October | LSSS - Activate duty 1 to run pump 3 for sampling upon request | All Wastewater System ROC General | 2025-10-22
ROC | October | MTSP - Thickening tank level fault alarm, disregard as per SCADA review. | All Wastewater System ROC General | 2025-10-19
ROC | October | AUSS - Conveyor 1,2,3 not in auto alarms and bar screen 1,2 not in auto alarms as well as channel inlet 1,2 gat valve fault alarms all triggered at same time. Likely a power blip, generators are not on. Able to clear all alarms. AUEQSJ - pump 1 moisture alarm, pump 1 leakage alarm, pump 1 hi temp alarm and site hydro fail alarm. Likely a power blip. Able to reset the hydro fail alarm. ISS pump 1 is currently manual/off and interlocked on unrelated alarms. Leaving alarms outstanding and will send email to OCO. | All Wastewater System ROC General | 2025-10-19
ROC | October | NBSP- Vortex 1 water scour uncommanded close alarm. Reset alarm once as per shift report. | All Wastewater System ROC General | 2025-10-27
ROC | October | JDSS, Brent St Q on site, working on the sewage pumps, directed to disregard pump alarms till he is finished | All Wastewater System ROC General | 2025-10-24
ROC | October | LSSS - Ameila from sewer use by law on site to collect a sample. Amelia requested that pump3 be activated to collect the sample. Placed pump 3 duty 1. | All Wastewater System ROC General | 2025-10-27
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-20
ROC | October | KSSP - Membrane Basement MUA - 9 Temp Switch Low alarm came in. Disregarded as per shift report | All Wastewater System ROC General | 2025-10-27
ROC | October | NMMCHT, Rick L is finished on site | All Wastewater System ROC General | 2025-10-20
ROC | October | KCSSKR - Generator running status. Informed Dan H, will monitor and follow back up in 30min as requested Consult | All Wastewater System ROC General | 2025-10-23
ROC | October | YDSS + YNSS normal | All Wastewater System ROC General | 2025-10-27
ROC | October | LSSS- Bar Screen 2 Fault Alarm. Notified Phil R. He will look into it. | All Wastewater System ROC General | 2025-10-17
ROC | October | NBSP - Lance J. called to inform that he is finished on site and he is unable to resolve the lo DO. Lance would like a call back if the DO dips below 0.5 mg/L or the aeration flow is less than 1400. | All Wastewater System ROC General | 2025-10-19
ROC | October | SUSP, UV Ch 1/2 Fault Alarms, Contacted Kevin K, Kevin K informed the ROC that they are bypassing to lagoon | All Wastewater System ROC General | 2025-10-21
ROC | October | YDSS+YNSS normal | All Wastewater System ROC General | 2025-10-25
ROC | October | NMSSBP - Diesel Tank Level HiHi alarm came in. Disregarded as per shift report | All Wastewater System ROC General | 2025-10-27
ROC | October | HMSS- Bar Screen 2 Fault Alarm. Notified Lauren S. She will contact Lance J. Lance J called. He is leaving site soon and Gavin W will remain onsite. | All Wastewater System ROC General | 2025-10-27
ROC | October | RHAMF1, Electrical/Mechanical Exhaust Fan Damper 1/2 Failed to close alarm, notified Chris R, directed to disregard | All Wastewater System ROC General | 2025-10-23
ROC | October | SUSSWB- David D done on site all alarms cleared | All Wastewater System ROC General | 2025-10-23
ROC | October | AUSS- Bar Screen 1 mot in auto alarm came in. Notified Barry M. Heading to site created CMU5 W11387972 #CMU5 | All Wastewater System ROC General | 2025-10-22
ROC | October | Adeela Khan signing out | All Wastewater System ROC General | 2025-10-20
ROC | October | NBSSJA - Generator running and Pump 1 VFD Fault alarm came in. Checked site. Generator alarms cleared within 10 mins. Pump 1 VFD alarm is outstanding. Called Lance J. but no answer. Will call soon 13:30 - Lance J. called back and informed he will head to site. CMU5 Created W11377071 #CONSULT #CMU5 | All Wastewater System ROC General | 2025-10-18
ROC | October | SHSP - UV System Minor fault alarm, UV bank 1 B is running, disregard alarm as per SCADA report. | All Wastewater System ROC General | 2025-10-26
ROC | October | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-10-26
ROC | October | AUSSYS- Generator running alarm came in. Checked site all pumps faulted. Reset alarms | All Wastewater System ROC General | 2025-10-31
ROC | October | KBSP, Aer Basin 1 Back DO Fault, Aeration Tank 1 OOS as per shift report | All Wastewater System ROC General | 2025-10-29
ROC | October | HLSSBS- Generator running status alarm after power blip will reset when generator shuts down | All Wastewater System ROC General | 2025-10-23
ROC | October | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-10-29
ROC | October | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-10-29
ROC | October | KSSSQW - Site Hydro Power Failure alarm came in. Checked site. Generator is not running and site is still running on hydro power. Trends are okay. Alarm has been cleared | All Wastewater System ROC General | 2025-10-25
ROC | October | EGSSSC, Generator 1 Low Coolant Temp/Generator Fault alarm, notified Kevin K, directed to disregard | All Wastewater System ROC General | 2025-10-29
ROC | October | Gluzen Ramos Ong signing out | All Wastewater System ROC General | 2025-10-30
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-26
ROC | October | Gluzen Ramos Ong signing out | All Wastewater System ROC General | 2025-10-24
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-30
ROC | October | SHSP - Site hydro fail and clarifier rake drive cut out. Called Lauren S who is on site and responding to the alarms. | All Wastewater System ROC General | 2025-10-27
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-25
ROC | October | YWS + NYWS Normal Connor Smith signing out. | All Wastewater System ROC General | 2025-10-31
ROC | October | AUSS, Terry R/Jackie S is finished on site, Wetwell 1 OOS for the night | All Wastewater System ROC General | 2025-10-20
ROC | October | YDOC - Terry C & Matt T onsite testing for vibration. Man/start fan 1 for testing. 12:55 - Man/stop fan 1 | All Wastewater System ROC General | 2025-10-29
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-21
ROC | October | YDSS + YNSS | All Wastewater System ROC General | 2025-10-23
ROC | October | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-10-29
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-25
ROC | October | KSSP- Odour sump hihi level alarm outstanding Notified Keven K directed to disregard #consult | All Wastewater System ROC General | 2025-10-23
ROC | October | Carter Dunn Signing Out | All Wastewater System ROC General | 2025-10-23
ROC | October | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-10-18
ROC | October | SHSSDK - Power blip occurred and generator running alarm came in. Checked site and found that site is connected to hydro power | All Wastewater System ROC General | 2025-10-18
ROC | October | Adam Button signing out 1C clear | All Wastewater System ROC General | 2025-10-16
ROC | October | MTSP- Thickening tank level fault. Disregard on shift report | All Wastewater System ROC General | 2025-10-26
ROC | October | SUSSWB - Low Battery /Low battery restored multiple alarms on the dialer. Checked SCADA. All trends normal. Pump 1 is running. Will monitor. 16:55 Called Kevin K, no answer. Will call again later. 17:10 Kevin K called, Notified about alarms on the dialer, electrician will attend site tomorrow. Disregard alarm for now. # Consult. | All Wastewater System ROC General | 2025-10-26
ROC | October | KBSP- Dan H. Requested Emergency Vac Truck. Called Wessuc (Dane). He will contact Dan H. for more details. | All Wastewater System ROC General | 2025-10-27
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-16
ROC | October | Ethan U singing in Weather: 7 light rain | All Wastewater System ROC General | 2025-10-23
ROC | October | Angelica Chepiga signing in | All Wastewater System ROC General | 2025-10-24
ROC | October | LSSS - Brent S working on generator. | All Wastewater System ROC General | 2025-10-16
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-19
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-18
ROC | October | YDSS + YNSS normal | All Wastewater System ROC General | 2025-10-19
ROC | October | LSSS - Surge Tank 1 Level Hi/HiHi alarm came in. Checked site. Noticed levels are within normal range. Trends indicate a spike but levels are now back to optimal range. Alarms have been cleared | All Wastewater System ROC General | 2025-10-19
ROC | October | SECC- Phil working on sump pump maintenance. Disregard related alarms. | All Wastewater System ROC General | 2025-10-21
ROC | October | KSSP- Cam B is on site with Electrical to work on alum system AUSS- Red B and Eric S on site to work on P3 flowmeter | All Wastewater System ROC General | 2025-10-17
ROC | October | YDSS + YNSS normal | All Wastewater System ROC General | 2025-10-19
ROC | October | KSSP, Cam B on site working on the turbidity analyzers on the filters, directed to disregard alarms on site | All Wastewater System ROC General | 2025-10-29
ROC | October | SHSP - UV System Minor Fault alarm came in. Checked site. One back is running. Disregard as per shift report | All Wastewater System ROC General | 2025-10-18
ROC | October | NBSP- RAS Train 1 flow lolo. Notified Lance J. They are putting aeration tank 2 back online. Will call when done on site | All Wastewater System ROC General | 2025-10-16
ROC | October | Bayview OCF - Fan not running alarm triggered on the dialer. Called Phil R who will attend site. Created CMU5#W11377299 #consult # CMU5 | All Wastewater System ROC General | 2025-10-19
ROC | October | JDSS- Neil O onsite testing flood alarm and low temp. | All Wastewater System ROC General | 2025-10-27
ROC | October | Angelica Chepiga signing out | All Wastewater System ROC General | 2025-10-21
ROC | October | SUSSWB David D on site doing pump testing | All Wastewater System ROC General | 2025-10-23
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-17
ROC | October | NMSSBP - Diesel Tank Level Hi alarm came in. Disregarded as per shift report | All Wastewater System ROC General | 2025-10-25
ROC | October | Adam Button signing in 10C sunny | All Wastewater System ROC General | 2025-10-25
ROC | October | YDSS+YNSS normal | All Wastewater System ROC General | 2025-10-25
ROC | October | NBSP - Aeration Basin 2 Back DO Lo alarm came in. Checked site and shift report. Shift report indicates a call out for Lo DO. Called Dan H. who will attend site. CMU5 Created W11393783 #CONSULT #CMU5 | All Wastewater System ROC General | 2025-10-26
ROC | October | SUSP - Div EQ tank 3 way valve fault and over torque alarm. Called Chris C who is aware and operating the valve. | All Wastewater System ROC General | 2025-10-27
ROC | October | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-10-19
ROC | October | SHSP- Bill V onsite for maintenance on Aeration Blower 1. | All Wastewater System ROC General | 2025-10-27
ROC | October | AUSSYS- Ultrasonic HiHi Alarm. Site is offline. Notified Chris C to confirm. Can disregard CONSULT | All Wastewater System ROC General | 2025-10-29
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-30
ROC | October | Connor Smith signing in | All Wastewater System ROC General | 2025-10-21
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-29
ROC | October | Carter Dunn Signing Out | All Wastewater System ROC General | 2025-10-24
ROC | October | Ethan U signing in | All Wastewater System ROC General | 2025-10-29
ROC | October | Adeela Khan signing in. Weather: 4C and clear | All Wastewater System ROC General | 2025-10-30
ROC | October | SHSP- Screen room O2 conc hi alarm came in. reset as it recovered right away. | All Wastewater System ROC General | 2025-10-25
ROC | October | HLSSBS- Diesel Containment/Sump Flood Alarm. Notified Kevin K. Can disregard CONSULT | All Wastewater System ROC General | 2025-10-31
ROC | October | YDSS S+ YNSS Normal Connor Smith signing out | All Wastewater System ROC General | 2025-10-21
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-22
ROC | October | SUSP- Chris C on site hydro 1 doing high voltage testing on site today. Plant will be running on generator. Notified Chris C of outstanding alarms caused by power disruptions and will clear on site. Maintenance will be for the duration of the day | All Wastewater System ROC General | 2025-10-22
ROC | October | KSSSQW- P1 lo flow alarm came in. Placed in man/off and rotated duty. Emailed North wastewater team | All Wastewater System ROC General | 2025-10-26
ROC | October | Adam Button signing in 6C Clear | All Wastewater System ROC General | 2025-10-22
ROC | October | AUSS, Terry R/Jackie S on site doing wet well cleaning NMVCBP, EGSSSC Valve Overtorque/Fault, Notified Mike B, ROC notified that maint is on site working on valve 2 | All Wastewater System ROC General | 2025-10-20
ROC | October | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-10-28
ROC | October | NBSP - Dan H left site. Aeration blowers 1 and 2 man/on until tomorrow. RAS train 1 flow low alarm- Value should recover, Dan H will check SCADA later. | All Wastewater System ROC General | 2025-10-26
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-30
ROC | October | NMSSBP - Mech screen 1 emergency stop alarm. Checked site, screen is in local off. Screen 2 running. Called Marcos T who is on site and working on screen 1. | All Wastewater System ROC General | 2025-10-31
ROC | October | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-10-26
ROC | October | Christian Van Beek signing out. | All Wastewater System ROC General | 2025-10-23
ROC | October | NBSP- Vortex 1 water scour uncmd close. reset as per shift report | All Wastewater System ROC General | 2025-10-23
ROC | October | GRSSWA - Redempto B and Parth P on site for annual calibrations | All Wastewater System ROC General | 2025-10-31
ROC | October | KBSP - Aer. basin back DO fault, not included in shift report. Informed Dan H, disregard Consult | All Wastewater System ROC General | 2025-10-22
ROC | October | YDSS+YNSS normal | All Wastewater System ROC General | 2025-10-22
ROC | October | *WRONG BOOK* | All Wastewater System ROC General | 2025-10-27
ROC | October | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-10-18
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-26
ROC | October | Gluzen Ramos Ong signing in at 09:30 LSSS - Christine F. on site with Fire Monitoring. She informed will be entering SCADA room and John Dimarco is aware. Out @ 12:13 | All Wastewater System ROC General | 2025-10-30
ROC | October | Christian Van Beek signing in. Weather: 11C and rain. | All Wastewater System ROC General | 2025-10-20
ROC | October | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-10-18
ROC | October | KSSSQW - Pump 3 low flow alarm, Placed pump man/off. Reassigned Duty 1 to Pump 4, will send email to Mike B. | All Wastewater System ROC General | 2025-10-19
ROC | October | Ethan Ullalkar signing out. | All Wastewater System ROC General | 2025-10-27
ROC | October | Christian Van Beek signing out | All Wastewater System ROC General | 2025-10-27
ROC | October | KBSP - Aeration Basin 2 Solids fault alarm. Called Young J. who informed that he is working on the aeration basin and will clear the alarms shortly | All Wastewater System ROC General | 2025-10-30
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-18
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-20
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-30
ROC | October | AUSSSR- AYSIX Historian Heartbeat alarm came in. Was able to reset and Trends okay YDSS+YNSS normal | All Wastewater System ROC General | 2025-10-25
ROC | October | SHSP - Site hydro power failure alarm came in and generator running status came in along with multiple other alarms. Checked site. Likely a power blip as all alarms cleared except for clarifier 1 rake drive cut out. Will monitor 08:15 - Alarm stayed outstanding and called Lance J. who will attend site. CMU5 Created W11377048 #CONSULT #CMU5 | All Wastewater System ROC General | 2025-10-18
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-29
ROC | October | NBSP - Vortex air lift uncommanded close alarm. Reset alarm once as per the shift report. | All Wastewater System ROC General | 2025-10-20
ROC | October | PVSS - Gavin W on site for a hi wet well alarm test. | All Wastewater System ROC General | 2025-10-27
ROC | October | HMSS - Bar screen 2 fault. Informed Dan H, will head to site tonight CMU = 11397923 | All Wastewater System ROC General | 2025-10-27
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-17
ROC | October | YDSS + YNSS Normal Christian Van Beek signing out | All Wastewater System ROC General | 2025-10-31
ROC | October | AUSSYS - Site hydro power failure alarm came in. Checked site. Noticed that the site is no longer running on generator power and switched back to hydro power. Generator is still running. 19:38 - Generator is no longer running and site is back to normal operations | All Wastewater System ROC General | 2025-10-31
ROC | October | HLSSBS, Neil O on site doing wet well cleaning | All Wastewater System ROC General | 2025-10-21
ROC | October | KSSP- Aeration Tank 1 Inlet DO Fault Alarm. Notified Cam B. Mike B is working on it. | All Wastewater System ROC General | 2025-10-17
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-22
ROC | October | SHSP - Power blip, Clarifier 1 Rake Drive cut out outstanding. Notified Lance J , will attend site. # CMU5 W11377230 SHSSDK - Power blip, Generator started. Station back to normal power. | All Wastewater System ROC General | 2025-10-19
ROC | October | AUSS- P6 discharge valve MV3 failed to open alarm came in. Reset alarm | All Wastewater System ROC General | 2025-10-24
ROC | October | YDSS+YNSS normal | All Wastewater System ROC General | 2025-10-25
ROC | October | KBSP- Aer basin 2 solids fault alarm came in. Trending okay and within range. Emailed West Waste Water team about outstanding alarm. | All Wastewater System ROC General | 2025-10-25
ROC | October | Carter Dunn Signing In | All Wastewater System ROC General | 2025-10-23
ROC | October | Adeela Khan signing in. Weather: 2C and partly cloudy | All Wastewater System ROC General | 2025-10-25
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-25
ROC | October | Carter Dunn Signing Out | All Wastewater System ROC General | 2025-10-21
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-21
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-22
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-22
ROC | October | Adam Button signing in 7C clear | All Wastewater System ROC General | 2025-10-23
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-19
ROC | October | AUEQST - Cell 2 hi level, hydrostatic level reading below 0, trends show sudden spike before returning within normal range. Able to clear alarm | All Wastewater System ROC General | 2025-10-24
ROC | October | AUSSSR - Line 1 valve Overtorque alarm, Line 1 & 3 are in good standing, disregard | All Wastewater System ROC General | 2025-10-24
ROC | October | Gluzen Ramos Ong signing in | All Wastewater System ROC General | 2025-10-28
ROC | October | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-10-28
ROC | October | YDSS + YNSS Normal Adeela Khan signing out | All Wastewater System ROC General | 2025-10-25
ROC | October | NBSP- Marcus R working on RAS Pump 3. Disregard no flow alarm. | All Wastewater System ROC General | 2025-10-27
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-31
ROC | October | Adam Button signing out | All Wastewater System ROC General | 2025-10-25
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-25
ROC | October | EGSSSC - Generator failure alarm on the dialer. No alarms on SCADA, all trends ok. | All Wastewater System ROC General | 2025-10-29
ROC | October | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-10-26
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-19
ROC | October | YDSS+YNSS normal | All Wastewater System ROC General | 2025-10-26
ROC | October | Adam Button signing out | All Wastewater System ROC General | 2025-10-26
ROC | October | YDSS+YNSS NORMAL Angelica Chepiga signing out | All Wastewater System ROC General | 2025-10-26
ROC | October | Carter Dunn Signing In, 7D/Clear | All Wastewater System ROC General | 2025-10-30
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-20
ROC | October | NMSSBP - Discharge flow LoLo alarm. Pump 4 running 25% speed. No flow. Reassigned duty 1 to pump 1. Placed Pump 4 man/off and emailed area. | All Wastewater System ROC General | 2025-10-28
ROC | October | Carter Dunn Signing In, 12D/Clear | All Wastewater System ROC General | 2025-10-29
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-17
ROC | October | NBSP - Aeration DO low with two blowers running alarm triggered. Checked site, two blowers are running and the trending shows the DO dropping. Consulted the interim procedure which states to consult the OCO if two blowers are running and the DO does not recover. Called Lance J who will check SCADA and determine if a site visit is required. 15:56 - NBSP - Lance J will attend site to make adjustments. Created CMu5#W11377289 #consult #CMU5 | All Wastewater System ROC General | 2025-10-19
ROC | October | YDSS + YNSS normal | All Wastewater System ROC General | 2025-10-21
ROC | October | AUSSYS, Terry R on site, drawing down wet well, will be doing a wet well cleaning, disregard lo/lolo level alarms | All Wastewater System ROC General | 2025-10-29
ROC | October | Angelica Chepiga signing out | All Wastewater System ROC General | 2025-10-18
ROC | October | KSSSQW - Boiler 1 fault alarm. Checked site, boiler 1 pump showing in local off. The hydronic pumps that direct flow to the boiler are currently active in local on. Contacted Mike B who directed to disregard. While on the phone with Mike, informed them of the pump 3 low flow alarms which resulted in Angelica C placing pump 3 manual/off. Mike stated that fi another pump is showing low flow he would like to be contacted to make a decision. | All Wastewater System ROC General | 2025-10-19
ROC | October | YDSS + YNSS normal | All Wastewater System ROC General | 2025-10-19
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-19
ROC | October | AUSS- Red B and Eric S done on site. Chris R will attend site to prime P3 and test new flowmeter | All Wastewater System ROC General | 2025-10-17
ROC | October | NMSSBP - Diesel tank Hihi level alarm. Disregard as per the shift report. | All Wastewater System ROC General | 2025-10-18
ROC | October | Angelica Chepiga signing out | All Wastewater System ROC General | 2025-10-19
ROC | October | MTSS - Barry M on site for a wet well cleaning today. Barry requested to disregard all associated alarms. | All Wastewater System ROC General | 2025-10-27
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-31
ROC | October | EGSSSC- Parth P done on site KSSP- Scum Chamber 2 lo alarm. Disregard on shift report NBSP- Vortex air lift uncommanded close alarm came in reset as per shift report YDSS+YNSS normal | All Wastewater System ROC General | 2025-10-16
ROC | October | NBSP - Vortex 1 water scour uncommanded close alarm. Reset alarm as per shift report. | All Wastewater System ROC General | 2025-10-20
ROC | October | Gluzen Ramos Ong signing in | All Wastewater System ROC General | 2025-10-24
ROC | October | AUSS- P2 discharge valve 2 failed to open reset and uncommanded close came in as a result. Reset alarm | All Wastewater System ROC General | 2025-10-25
ROC | October | RHAMF- Mech room exhaust fan2 uncommanded open and damper 1 failed to close. Able to reset | All Wastewater System ROC General | 2025-10-22
ROC | October | Connor Smith signing out | All Wastewater System ROC General | 2025-10-30
ROC | October | JDSS - Chase J testing hi level alarm SUSSHS - Darren B & Kevin K onsite, running each pump at 100%, | All Wastewater System ROC General | 2025-10-22
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-22
ROC | October | EGSSSC - Wet well 1 hydrostatic level lolo and OOR alarms. Checked site, LIT2 is reading a negative number, trending shows a sheer drop. Clearly an LIT issue. This is not the controlling LIT. Will monitor site to ensure normal operations. | All Wastewater System ROC General | 2025-10-22
ROC | October | Bayview Steeles OCF - Phil R called and requested a CMU5 for the odour complaint he is investigating. Created CMU5#W11400409 #CMU5 | All Wastewater System ROC General | 2025-10-28
ROC | October | SHSP - Vortex O2 Conc HiHi alarm . Previously was disregard by Dan H. Will email area. | All Wastewater System ROC General | 2025-10-28
ROC | October | RHAMF1, Control Panel Entry Alarm//Process Room Exhaust Fan 1 Damper Failed to close alarm, Notified Philip R, directed to disregard consult | All Wastewater System ROC General | 2025-10-20
ROC | October | HMSS - Daniel H. called back to inform that he was unable to fix the issue with bar screen 2 and has created a followup CMU for maintenance. Daniel informed that the bar screen 2 fault can be disregarded for the night until maintenance can take a look in the morning | All Wastewater System ROC General | 2025-10-27
ROC | October | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-10-19
ROC | October | YDSS + YNSS Normal Carter Dunn Signing Out | All Wastewater System ROC General | 2025-10-30
ROC | October | Ethan Ullalkar signing in | All Wastewater System ROC General | 2025-10-22
ROC | October | Christian Van Beek signing in. Weather: 3C and rain. | All Wastewater System ROC General | 2025-10-31
ROC | October | Adeela Khan signing in. Weather: 6C and sunny | All Wastewater System ROC General | 2025-10-26
ROC | October | SHSP - Vortex O2 Conc Hi alarm came in. Checked site. Called Dan H. but no answer as he is at NBSP. will try again soon 22:54 - Called Dan H. again who directed to disregard alarm for the night #CONSULT | All Wastewater System ROC General | 2025-10-26
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-27
ROC | October | Carter Dunn Signing Out | All Wastewater System ROC General | 2025-10-20
ROC | October | Adeela Khan signing out | All Wastewater System ROC General | 2025-10-10
ROC | October | SEOC- Dan K on site for generator run | All Wastewater System ROC General | 2025-10-07
ROC | October | YDSS+YNSS normal | All Wastewater System ROC General | 2025-10-02
ROC | October | KSSP - Supernatant flow low and low low alarms. Checked site, operations appear normal. Disregarded as per shift report. | All Wastewater System ROC General | 2025-10-03
ROC | October | NBSP- Marcus R onsite isolating aeration tank 2. Disregard related alarms. | All Wastewater System ROC General | 2025-10-07
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-04
ROC | October | MTSP - Sludge thickening tank level fault alarm. Disregard as per the shift report. | All Wastewater System ROC General | 2025-10-04
ROC | October | Adeela Khan signing in. Weather: 11C and sunny | All Wastewater System ROC General | 2025-10-09
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-05
ROC | October | KBSP - Eric S finished on site. | All Wastewater System ROC General | 2025-10-01
ROC | October | SUSSHS- Darren B on site for generator run | All Wastewater System ROC General | 2025-10-06
ROC | October | QVSSSC- Chris C. leaving site. Can disregard sump pump fail and sump flood alarm if they come in again. Call for dry well flood alarm. | All Wastewater System ROC General | 2025-10-07
ROC | October | SEOC- David D onsite for generator work and load test. | All Wastewater System ROC General | 2025-10-01
ROC | October | NMSSBP- Terry R onsite running generator. | All Wastewater System ROC General | 2025-10-02
ROC | October | KSSP- Neil O heading to site to test chemical containment flood alarms. | All Wastewater System ROC General | 2025-10-08
ROC | October | SUSP- Haul waste P1 OOS alarm came in. Called Chris C. Chase J and Bill V working on pumps. Chris C will clear alarms before leaving site | All Wastewater System ROC General | 2025-10-08
ROC | October | NMVCBP - Nill O and Chase J testing Sump flood alarm. | All Wastewater System ROC General | 2025-10-09
ROC | October | NBSP- Gavin W onsite with Trojan working on UVs. Can disregard related alarms. | All Wastewater System ROC General | 2025-10-09
ROC | October | AUSS- P1 discharge valve failed to open alarm came in cleared alarm but valve seems to be stuck. Continued to monitor valve closed YDSS+YNSS normal. | All Wastewater System ROC General | 2025-10-02
ROC | October | Adam Button signing out | All Wastewater System ROC General | 2025-10-02
ROC | October | YDOC - Phil R running generator. | All Wastewater System ROC General | 2025-10-09
ROC | October | SHSP - Lauren S on site to complete maintenance on all grit, aeration and sludge blowers and RAS pump maintenance. | All Wastewater System ROC General | 2025-10-02
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-04
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-05
ROC | October | Angelica Chepiga signing out | All Wastewater System ROC General | 2025-10-03
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-11
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-12
ROC | October | Adam Button signing out | All Wastewater System ROC General | 2025-10-14
ROC | October | SUSP - Basin 2 Decanter VFD Fault alarm, Darren B on site monitoring, maintenance working on Basin 2. | All Wastewater System ROC General | 2025-10-09
ROC | October | Ethan U signing in Weather 15. | All Wastewater System ROC General | 2025-10-15
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-16
ROC | October | Adam Button signing in | All Wastewater System ROC General | 2025-10-15
ROC | October | NMVCIB- adjusted valve to manual 30L/s 17:35- adjusted to 40L/s | All Wastewater System ROC General | 2025-10-07
ROC | October | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-10-15
ROC | October | NMSSHS- Marcos T on site for workorders will call when done | All Wastewater System ROC General | 2025-10-15
ROC | October | KBSP, UV Ch2 Common Major Alarm, Critical Alarm, notified Young J, he is currently on site and will investigate the issue | All Wastewater System ROC General | 2025-10-06
ROC | October | AUSS, Placed pump 6 in D1 for Matt T for pump maint | All Wastewater System ROC General | 2025-10-14
ROC | October | Gluzen Ramos Ong signing out | All Wastewater System ROC General | 2025-10-03
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-14
ROC | October | Christian Van Beek signing in. Weather: 24C and clear. | All Wastewater System ROC General | 2025-10-03
ROC | October | KSSP- Mike B working on chemical pumps. Disregard related alarms. | All Wastewater System ROC General | 2025-10-02
ROC | October | Connor Smith signing in 10C Clear | All Wastewater System ROC General | 2025-10-03
ROC | October | QVSSSC- Chris C onsite for generator run and health and safety work orders. Contractor and Electricians will also be performing generator work. | All Wastewater System ROC General | 2025-10-03
ROC | October | Carter D signing out | All Wastewater System ROC General | 2025-10-06
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-09
ROC | October | YDSS + YNSS normal | All Wastewater System ROC General | 2025-10-10
ROC | October | Connor Smith signing in 10 C Cloudy | All Wastewater System ROC General | 2025-10-01
ROC | October | KBSP- UV Ch. 2 Common Major Alm. Notified Yonge J. Trojan Contractor is working on it. | All Wastewater System ROC General | 2025-10-01
ROC | October | KSSP- ZW4 Shutdown on turbididty OOR alarm. Notified Chris C. Directed to disregard alarm #consult | All Wastewater System ROC General | 2025-10-02
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-15
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-01
ROC | October | NMSSHS- Marcos T on site to test eyewashes and run generator | All Wastewater System ROC General | 2025-10-06
ROC | October | NMSSBP - Terry R finished on site, normal operations. | All Wastewater System ROC General | 2025-10-02
ROC | October | MTSS- Barry M on site testing generator | All Wastewater System ROC General | 2025-10-06
ROC | October | AUSS- P2 MV4 MV3 and MV2 failed to open. Reset alarms | All Wastewater System ROC General | 2025-10-06
ROC | October | KSSP, UV Ch 2 Bank 2A Adjacent Lamp Fail, As per North Wastewater shift report, directed to disregard at this time | All Wastewater System ROC General | 2025-10-09
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-04
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-05
ROC | October | *WRONG BOOK* | All Wastewater System ROC General | 2025-10-05
ROC | October | Angelica Chepiga signing in, weather +4C | All Wastewater System ROC General | 2025-10-10
ROC | October | RHAMF - Mechanical room exhaust fan damper 1 & 2 failed, called Terry R. okay to disreagrd but will take a look as well MTSP - Ras pump 1 fault. Clarifier 2 no RAS pump running alarm. Informed Barry M, is aware and looking into issue now | All Wastewater System ROC General | 2025-10-10
ROC | October | SHSSDK - Lauren S running generator and testing temp alarms. | All Wastewater System ROC General | 2025-10-01
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-09
ROC | October | Connor Smith signing in 5 C clear | All Wastewater System ROC General | 2025-10-09
ROC | October | Angelica Chepiga signing in | All Wastewater System ROC General | 2025-10-09
ROC | October | KSSP - Chase J cleaning trains turbidity meters and working on UVs, requested disregard trains not in auto and UV alarms. | All Wastewater System ROC General | 2025-10-15
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-06
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-11
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-13
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-13
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-04
ROC | October | SEOC67- Phil R onsite running generator. | All Wastewater System ROC General | 2025-10-02
ROC | October | SUSP- Chris C done on site | All Wastewater System ROC General | 2025-10-07
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-16
ROC | October | YDSS+YNSS normal KBSP- Plant 1 influent flow OOR alarm came in disregard on shift report. Cleared on its own | All Wastewater System ROC General | 2025-10-01
ROC | October | BLSS- Screen up stream level hihi/ Screen diff level hi alarm came . Checked trends looks like LIT is acting up and can be disregard as per shift report as past trends indicate similar conditions | All Wastewater System ROC General | 2025-10-07
ROC | October | Adam Button signing out | All Wastewater System ROC General | 2025-10-07
ROC | October | Adeela Khan signing in. Weather:15C and raining | All Wastewater System ROC General | 2025-10-07
ROC | October | LSSS - Amilia from sewer use bylaws onsite. Requested pump 3 to run. Rotate pump3 to duty 1 | All Wastewater System ROC General | 2025-10-10
ROC | October | JDSS- Channel grinder fault and e stop alarm came in as well as high wet well alarm came in on dialer. Notified Cam B. Neil O. is north pumping stions this week. Was not able to reset alarm. Called Neil O. Will check site when done at KSSSQW | All Wastewater System ROC General | 2025-10-07
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-13
ROC | October | KSSP - Aeration Tank 1,2 Inlet and Outlet DO Fault and OOR alarms came in. Checked site. Called Neil O. who will take a look 11:40 - Neil Calls back and requests a call to PCS on call Artour L. CMU5 Created for Artour L. W11356843 11:45 - Neil calls back to inform that the DO levels are now being shown and alarms have cleared. Neil informed he will continue to monitor #CONSULT #CMU5 | All Wastewater System ROC General | 2025-10-11
ROC | October | AUSS- Generator 1,2,3 Not in Auto Alarms. Cleared upon acknowledging. | All Wastewater System ROC General | 2025-10-11
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-12
ROC | October | SHSP, Lauren S on site working on the sludge holding tanks and will be testing the sump pit alarms, may also work on the Scum tanks, directed to disregard | All Wastewater System ROC General | 2025-10-14
ROC | October | KBSP- Filter 1/2 influent channel alarm outstanding. notified Young J. Young J cleared alarms and is still working on site #consult | All Wastewater System ROC General | 2025-10-01
ROC | October | KCSSKR- P1 failed to start alarm came in followed by P3 uncommanded stop followed by a fault alarm all while P2 was running in D1. Reset all alarms but P3 fault still outstanding. Placed P3 in man/off and emailed west waste water team. Will continue to monitor | All Wastewater System ROC General | 2025-10-02
ROC | October | YDSS+YNSS normal | All Wastewater System ROC General | 2025-10-02
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-03
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-07
ROC | October | NBSP - vortex 2 water scour uncommanded close alarm. Reset alarm as per the shift report. | All Wastewater System ROC General | 2025-10-04
ROC | October | KSSSQW- Neil O onsite for work orders. Running generator, health and safety, flood alarm, and pump test. 11:130 Finished onsite. | All Wastewater System ROC General | 2025-10-07
ROC | October | Ethan Ullalkar signing out. | All Wastewater System ROC General | 2025-10-06
ROC | October | AUSS - Rick L. and Parth P. calibrating surge tank level | All Wastewater System ROC General | 2025-10-03
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-14
ROC | October | SEOC - David D completed work on generator. Back to auto. | All Wastewater System ROC General | 2025-10-01
ROC | October | NBSP- Marcus R requested to disable DO calibration mode. | All Wastewater System ROC General | 2025-10-08
ROC | October | Christian Van Beek signing in. Weather: 15C and clear. | All Wastewater System ROC General | 2025-10-13
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-13
ROC | October | YDSS+YNSS normal Adam Button signing out | All Wastewater System ROC General | 2025-10-06
ROC | October | YDSS + YNSS Normal Connor Smith signing out | All Wastewater System ROC General | 2025-10-01
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-05
ROC | October | LSSS, applied the rotated duty so that pump 6 is in duty 1 for the water resource team | All Wastewater System ROC General | 2025-10-06
ROC | October | KBSP - Young J running generator and testing eyewash alarm. | All Wastewater System ROC General | 2025-10-01
ROC | October | AUSSR- Line 2 Valve Overtorgue Alarm. Two other lines available. Emailed Central East WW Team. | All Wastewater System ROC General | 2025-10-09
ROC | October | SEOC Damper Station Flood Switch , Hydrogen Peroxide tank 2 level low switch - Daniel K requested disregard alarms. | All Wastewater System ROC General | 2025-10-01
ROC | October | Connor Smith signing out | All Wastewater System ROC General | 2025-10-08
ROC | October | Gluzen Ramos Ong signing in | All Wastewater System ROC General | 2025-10-07
ROC | October | NBSP-Marcus R on site to work on aeration basin 1 DO probe | All Wastewater System ROC General | 2025-10-08
ROC | October | LSSS- Matt T onsite for maintenance on pumps 3 and 5. Changed duties so that they are in duty 4 and 5 and placed man/off. | All Wastewater System ROC General | 2025-10-09
ROC | October | KBSP - Young J running generator and performing Air Blowers inspection. | All Wastewater System ROC General | 2025-10-09
ROC | October | Ethan U signing in Weather 15. | All Wastewater System ROC General | 2025-10-04
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-11
ROC | October | Adam Button signing in | All Wastewater System ROC General | 2025-10-08
ROC | October | KSSP- Ras combined no flow alarm came in. WAS system active in manual. OPs wasting on site | All Wastewater System ROC General | 2025-10-08
ROC | October | Christian Van Beek signing out. | All Wastewater System ROC General | 2025-10-05
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-05
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-12
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-06
ROC | October | MTSP- Thickening Tank Level Fault Alarm. Disregard as per SCADA Report. | All Wastewater System ROC General | 2025-10-12
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-09
ROC | October | SUSP - Chris C called to inform of a special operating strategy that is required while SUSP SBR's rotate in fill/drain cycles for maintenance. SBR 1 is being drained to be taken offline and SBR 2 is being filled after being taken offline previously for maintenance. As directed by Chris C, the air valves and blowers for SBR 1 and 2 will be manual operated multiple times every hour to maintain DO values for the microorganisms. Will be making necessary changes throughout the night, using this log entry as an overarching entry for all changes made under this operating strategy. | All Wastewater System ROC General | 2025-10-03
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-03
ROC | October | KBSP - Filter Sluice Gate 3 Open failed alarm came in. Checked site. Filter 4 is open in auto. Called Young J. who directed to ack/reset alarm #CONSULT | All Wastewater System ROC General | 2025-10-05
ROC | October | AUSSYS - Site hydro power fail alarm. Checked site, no pumps interlocked, generator is not running and ATS pointing to town hydro. Likely a power blip, operations normal, reset alarm. | All Wastewater System ROC General | 2025-10-03
ROC | October | Christian Van Beek signing out. | All Wastewater System ROC General | 2025-10-02
ROC | October | Connor Smith signing in 16C Cloudy | All Wastewater System ROC General | 2025-10-10
ROC | October | KCSSKR - Generator Running Status alarm came in. Checked site and found that generator is running and site is connected to generator power. Called Young J. who will take a look 17:12 - Site switched back to hydro power and alarm has cleared #CONSULT | All Wastewater System ROC General | 2025-10-05
ROC | October | KSSP- Franco from Property Services onsite for HVAC work. | All Wastewater System ROC General | 2025-10-01
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-11
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-14
ROC | October | Ethan U singing in Weather: 19c | All Wastewater System ROC General | 2025-10-14
ROC | October | Carter Dunn Signing Out | All Wastewater System ROC General | 2025-10-14
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-12
ROC | October | SUSP- Chase J requested Emergency Vac Truck for basin cleaning. Notified WESSUC (Dane). They can respond in 1 hour 45 minutes. Informed Chase. | All Wastewater System ROC General | 2025-10-01
ROC | October | JDSS - Channel grinder e-stop alarm. Called Chris C who will head to site. | All Wastewater System ROC General | 2025-10-02
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-14
ROC | October | YDSS+YNSS normal | All Wastewater System ROC General | 2025-10-01
ROC | October | NBSSJA - Marcus R testing Eyewash alarm. | All Wastewater System ROC General | 2025-10-01
ROC | October | KSSP- ZW2 shutdown/maintenance clean aborted drain tank hi and membrane tank lo alarms came in notified Cam B will take a look on site | All Wastewater System ROC General | 2025-10-08
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-11
ROC | October | KBSP- Filter Inf Ch. 1 Lvl HiHi Alarm. Alarm cleared. | All Wastewater System ROC General | 2025-10-11
ROC | October | SHSP, UV System Minor Fault, Banks are still running, as per shift report, directed to disregard | All Wastewater System ROC General | 2025-10-13
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-05
ROC | October | LSSS- Amalie from Sewer Use By law called and requested Pump 6 in duty 1 for sampling. 09:50- Unable to sample from Pump 6. Requested pump 3 in duty 1 | All Wastewater System ROC General | 2025-10-08
ROC | October | NMSSBP- Wet Well Area Gas Alarm, Wet Well H2S HiHi Alarm. Disregard as per SCADA Report. Emailed Central East Waste Water. | All Wastewater System ROC General | 2025-10-07
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-12
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-12
ROC | October | KBSP - Eric S working on Filter 3 Head loss. Disregard alarm. | All Wastewater System ROC General | 2025-10-01
ROC | October | MTSS - Kyle R with contractor completed work on generator. Back to normal. | All Wastewater System ROC General | 2025-10-01
ROC | October | LSSS - Placed P6 in D1 for EME sampling (Amelia G) | All Wastewater System ROC General | 2025-10-03
ROC | October | BLSS- Theodore from AB is on site to work on generator and will be running it but it wont be connected to site OPs are aware of work on site | All Wastewater System ROC General | 2025-10-08
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-08
ROC | October | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-10-03
ROC | October | Adam Button signing in 6C clear | All Wastewater System ROC General | 2025-10-14
ROC | October | KBSP- Filter Inf. Ch1. Lvl HiHi Alarm. Alarm cleared right away. | All Wastewater System ROC General | 2025-10-11
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-07
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-10
ROC | October | HMSS - Historian heartbeat alarm, John D made aware | All Wastewater System ROC General | 2025-10-10
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-12
ROC | October | NMSSBP- P3 lo seal water pressure alarm outstanding P3 OOS. Notified Dan K will take a look later today. Cleared alarm | All Wastewater System ROC General | 2025-10-07
ROC | October | HLSSBS- Hydrogen Sulphide High High Alarm. Notified Neil O. Can disregard. | All Wastewater System ROC General | 2025-10-01
ROC | October | Connor Smith signing in 10 C Clear | All Wastewater System ROC General | 2025-10-02
ROC | October | NBSP- RAS combined no flow alarm came in. Disregard on shift report | All Wastewater System ROC General | 2025-10-14
ROC | October | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-10-02
ROC | October | SUSP - Basin 2 lolo level alarm. Checked site, basin 2 is offline for repairs according to the shift report. | All Wastewater System ROC General | 2025-10-02
ROC | October | Christian Van Beek signing in. Weather: 25C and sun. | All Wastewater System ROC General | 2025-10-04
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-04
ROC | October | AUSSMP - Bar Screen 1 General and Bar Screen 1 Not in auto alarms came in. Checked site. Bar screen 1 is in local. Called Daniel K. who is headed to site. CMU5 Created W11336085 14:45 - Daniel K. called back to inform that he is on site but requests another operator to assist with isolating. 14:48 - Called Young J. who will head to site shortly. CMU5 Created W11336095 16:27 - Daniel called back to inform that maintenance will need to attend site later this week to fix the bar screen. Daniel informed that bar screen 1 will stay OOS for the night #CONSULT #CMU5 | All Wastewater System ROC General | 2025-10-05
ROC | October | KBSP- Scum Pump 1 No Flow Alm. Both pumps interlocked due to this alarm. Will email Dan H | All Wastewater System ROC General | 2025-10-10
ROC | October | YDSS+YNSS normal | All Wastewater System ROC General | 2025-10-06
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-07
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-07
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-10
ROC | October | YDSS + YNSS Normal Connor Smith signing out | All Wastewater System ROC General | 2025-10-02
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-08
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-08
ROC | October | NBSP- RAS Train 1 Flow Signal Error. Notified Young J. He will look into it. Confirmed RAS Pump1 and 3 to remain man/on | All Wastewater System ROC General | 2025-10-07
ROC | October | AUSSSR - Daniel K. called to inform that he cleared the Line over torque alarm and if it does come back in, it can be disregarded. Daniel K. requested a call if there are no lines available | All Wastewater System ROC General | 2025-10-05
ROC | October | AUSS - Eric S working on FM3. | All Wastewater System ROC General | 2025-10-10
ROC | October | SUSP - Filter to lagoon flow HiHi, Filter feed pumps not available alarms - Chris C on site pumping down EQ tank. Requested disregard alarms for now. | All Wastewater System ROC General | 2025-10-10
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-10
ROC | October | Ethan Ullalkar signing out. | All Wastewater System ROC General | 2025-10-10
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-10
ROC | October | YDSS+YNSS NORMAL Angelica Chepiga signing out | All Wastewater System ROC General | 2025-10-10
ROC | October | Connor Smith signing out | All Wastewater System ROC General | 2025-10-03
ROC | October | NBSP- Marcus R. onsite working on DO sensors. Will also be doing maintenance on aeration blowers, and sludge blowers. | All Wastewater System ROC General | 2025-10-02
ROC | October | YDSS + YNSS normal | All Wastewater System ROC General | 2025-10-05
ROC | October | *WRONG BOOK* | All Wastewater System ROC General | 2025-10-05
ROC | October | Connor Smith signing out | All Wastewater System ROC General | 2025-10-11
ROC | October | Ethan Ullalkar signing out. | All Wastewater System ROC General | 2025-10-07
ROC | October | NMSSBP - Terry R on site and has completed the flood alarm test. Terry will be completing the generator test on approximately thirty minutes. | All Wastewater System ROC General | 2025-10-02
ROC | October | Angelica Chepiga signing in,weather +17C | All Wastewater System ROC General | 2025-10-02
ROC | October | KSSSQW - Pump 2 flow low alarm. Checked site, pump is running at 0% speed. Trending shows some abnormal speed changes however one pump on site has already been placed OOS. Will monitor site through the night. | All Wastewater System ROC General | 2025-10-13
ROC | October | NBSSJA - Marcus R running generator. | All Wastewater System ROC General | 2025-10-01
ROC | October | KBSP- Aer Basin 1 Back DO LoLo. Notified Young J. Tank is still empty. Disregard. | All Wastewater System ROC General | 2025-10-03
ROC | October | Ethan U signing in Weather 29. | All Wastewater System ROC General | 2025-10-05
ROC | October | HLSSBS- Chase J on site for generator run | All Wastewater System ROC General | 2025-10-07
ROC | October | AUSS - pump 6 discharge header MV4 failed to open alarm. Checked site, duty rotated to pump 2 which is operating normally. Reset alarm. | All Wastewater System ROC General | 2025-10-02
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-02
ROC | October | NBSP, Marcus R is on site working on the blowers | All Wastewater System ROC General | 2025-10-06
ROC | October | YDSS+YNSS normal | All Wastewater System ROC General | 2025-10-02
ROC | October | KSSP- Neil O testing gas alarms. Disregard related alarms. | All Wastewater System ROC General | 2025-10-02
ROC | October | NBSP - Marcus R. working on RAS pump 3 | All Wastewater System ROC General | 2025-10-03
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-04
ROC | October | NBSP - Vortex #2 Air Lift Uncommanded Close alarm came in. Ack/reset as per shift report | All Wastewater System ROC General | 2025-10-05
ROC | October | YDSS+YNSS normal Adam Button signing out | All Wastewater System ROC General | 2025-10-01
ROC | October | MTSP - Kyle R onsite for maintenance on generator | All Wastewater System ROC General | 2025-10-10
ROC | October | BLSS- Lance J. on site running generator and testing drywell flood and building temp alarms and will call when done JDSS- Garrick from Ferguson Electric is on site to pull PAC panel cords from generator no alarms expected will call when done | All Wastewater System ROC General | 2025-10-06
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-14
ROC | October | EGSSSC- Chase J onsite for generator run and health and safety work orders. | All Wastewater System ROC General | 2025-10-07
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-06
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-06
ROC | October | AUSSYS- Daniel K running generator and testing drywell flood alarm | All Wastewater System ROC General | 2025-10-03
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-07
ROC | October | Bayview OCF, Philip R on site replacing the filter, the Fan will be off for a short period of time | All Wastewater System ROC General | 2025-10-06
ROC | October | AUSS- Terry R on site testing drywell flood | All Wastewater System ROC General | 2025-10-06
ROC | October | KSSP- Neil O on site for UV system maintenance | All Wastewater System ROC General | 2025-10-08
ROC | October | SHSP - Lauren S working on headworks and aeration blower 2 , requested disregard alarms. | All Wastewater System ROC General | 2025-10-09
ROC | October | LSSS- Amelie from Sewer Use Bylaw req. pump 6 on for sampling. | All Wastewater System ROC General | 2025-10-01
ROC | October | YDSS+YNSS normal | All Wastewater System ROC General | 2025-10-01
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-08
ROC | October | YDSS + YNSS Normal HMSS, Pump 3/5 in ultrasonic mode, notified Dan H, directed to disregard at this time as it should clear however if it comes in again, he would like a call consult | All Wastewater System ROC General | 2025-10-08
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-10
ROC | October | QVSSSC- Kyle R finished onsite. | All Wastewater System ROC General | 2025-10-03
ROC | October | KSSP -Cam B working on sludge blowers. | All Wastewater System ROC General | 2025-10-15
ROC | October | SHSP - Lauren S working on WAS pumps. | All Wastewater System ROC General | 2025-10-10
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-05
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-07
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-07
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-03
ROC | October | Connor Smith signing in 16C Cloudy | All Wastewater System ROC General | 2025-10-11
ROC | October | Connor Smith signing in 10C Clear | All Wastewater System ROC General | 2025-10-08
ROC | October | NBSP- Vortex 1 air lift uncmn close reset as per shift report | All Wastewater System ROC General | 2025-10-08
ROC | October | KSSP - Neil O working on channel aeration blowers. | All Wastewater System ROC General | 2025-10-10
ROC | October | SHSP- Kingsley M restarting iFix on site directed to disregard historian heartbeat alarm. No service interruption expected | All Wastewater System ROC General | 2025-10-15
ROC | October | Angelica Chepiga signing out | All Wastewater System ROC General | 2025-10-15
ROC | October | LSSS - Matt T finished on site. | All Wastewater System ROC General | 2025-10-09
ROC | October | MTSP- Barry M onsite running generator. | All Wastewater System ROC General | 2025-10-01
ROC | October | NMSSBP- P4 discharge valve failed to close alarm outstanding reset | All Wastewater System ROC General | 2025-10-14
ROC | October | NBSP- Sludge thickener hi alarm outstanding. Notified Dan H of alarm directed to disregard #consult | All Wastewater System ROC General | 2025-10-14
ROC | October | YDSS+YNSS NORMAL Angelica Chepiga signing out | All Wastewater System ROC General | 2025-10-09
ROC | October | YDBR - F2 Biofilter Drain pH HiHi alarm came in. Checked site and shift report. Called Daniel K. who directed to disregard alarm #CONSULT | All Wastewater System ROC General | 2025-10-05
ROC | October | AUSS - Pump 6 Disc MV2 Failed to Open alarm. Checked site, pump duty ahs rotated to another pump. Duty is not active. Operations appear normal, reset alarm. | All Wastewater System ROC General | 2025-10-13
ROC | October | YDSS + YNSS Normal NMSSBP - Diesel tank hihi level alarm. Disregard as per the shift report. AUSS Generator 1,2,3 not in auto alarm. Alarm status changed to normal immediately following the alarm trigger. Operations appear normal on SCADA. Reset alarms. | All Wastewater System ROC General | 2025-10-13
ROC | October | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-10-03
ROC | October | Adam Button signing in 18C Clear | All Wastewater System ROC General | 2025-10-07
ROC | October | NMSSHS - Chris R testing Drywell flood and temp alarms. | All Wastewater System ROC General | 2025-10-09
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-15
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-09
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-11
ROC | October | KSSP - Aeration Tank 2 Outlet DO Lo alarm came in. Checked site and noticed that DO levels are back within range | All Wastewater System ROC General | 2025-10-11
ROC | October | AUSSSR- Line 2 over torque alarm came in .Notified Chris R and will investigate | All Wastewater System ROC General | 2025-10-15
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-11
ROC | October | Ethan U signing in Weather 12. | All Wastewater System ROC General | 2025-10-12
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-12
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-08
ROC | October | MTSP- Kevin S requested to enable batch wasting. Has his OIC direction. | All Wastewater System ROC General | 2025-10-09
ROC | October | NMTKKC- Joe D onsite cleaning analyzers and chemscan. Disregard chemscan offline alarm. Will have chemical pumps man/off. Will also be testing temp and eyewash alarms. Requested to adjust duty stop from 75 to 80%. *Wrong Book | All Wastewater System ROC General | 2025-10-09
ROC | October | LSSS - Satham M testing/ working on bar screen. | All Wastewater System ROC General | 2025-10-15
ROC | October | KBSP- UV critical alarm. Notified Yonge J. Contractors still working on it. He will inform when they are finished. | All Wastewater System ROC General | 2025-10-01
ROC | October | YDSS+YNSS normal | All Wastewater System ROC General | 2025-10-01
ROC | October | SEOC OCF- David D finished onsite. | All Wastewater System ROC General | 2025-10-02
ROC | October | NBSP - Marcus R working on air compressors. | All Wastewater System ROC General | 2025-10-02
ROC | October | KCSSKR - Power Failure alarm came in on the dialer and Generator Running Status alarm came in. Checked site. Noticed that generator is running but site is not running on generator power. 19:19 - Generator is no longer running and alarm has cleared | All Wastewater System ROC General | 2025-10-09
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-15
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-13
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-14
ROC | October | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-10-02
ROC | October | SEOC - OCF Damper Station CO2 Low alarm , disregard as per SCADA review. | All Wastewater System ROC General | 2025-10-15
ROC | October | AUSS - Rick L. and Parth P. finished working on surge tank. All alarms cleared | All Wastewater System ROC General | 2025-10-03
ROC | October | HMSS- P1 emergency stop/current OOR/ Bearing hi temp. Notified Lance J. On site to isolate force main 1 to work on P2 check valve | All Wastewater System ROC General | 2025-10-07
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-13
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-15
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-04
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-08
ROC | October | HMSS- Lance J onsite testing metro overfllow, hi wet well level and sump flood alarm. Also running generator. | All Wastewater System ROC General | 2025-10-01
ROC | October | Ethan Ullalkar signing out. | All Wastewater System ROC General | 2025-10-15
ROC | October | Ethan Ullalkar signing out. | All Wastewater System ROC General | 2025-10-12
ROC | October | KBSP - Aeration basin 2 solids fault alarm. Checked site, operations appear normal. Trending shows a spike of the suspended solids reading which quickly returned to normal range. Cleared alarm. | All Wastewater System ROC General | 2025-10-12
ROC | October | KSSSQW - Pump 2 flow low alarm. Checked site, no pumps running. Alarm comes in when pump stops and duty rotation is set to trigger on a pump stop. Cleared alarm and any following iterations. | All Wastewater System ROC General | 2025-10-14
ROC | October | EGSSSC - Kingsley M testing PAC Commfail alarm. | All Wastewater System ROC General | 2025-10-01
ROC | October | KBSP- Yonge J running generator to test alarms. Requested to disregard UV Ch2. Common Minor Alm and Filter Infl Ch 1 Lvl HiHi Alarm | All Wastewater System ROC General | 2025-10-01
ROC | October | QVSSSC- Dry Well Sump pump fail/flood alarm came in. Notified Chris C. heading to site. Created CMU5 W11344709 #CMU5 | All Wastewater System ROC General | 2025-10-07
ROC | October | Carter Dunn Signing In, 11D/Clear | All Wastewater System ROC General | 2025-10-08
ROC | October | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-10-09
ROC | October | HLSSBS - Rick L and Parth P on site for annual calibration. | All Wastewater System ROC General | 2025-10-10
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-12
ROC | October | MTSS - Kyle R with contractor working on generator. Disregard generator offline alarm /generator alarms. | All Wastewater System ROC General | 2025-10-01
ROC | October | SUSP - Called Chris C regarding continued plan/operations of aeration blowers for SBR. No response, Continuing to manually operate blowers every 20min as instructed from shift report and operator 14:38 - Chris C called back, SBR 1 now in maintenance mode now that its low enough. Will be offline for the weekend. SPR2 will be back in service but decant arm will be parked. Will call for any hi level in SBR and okay to spill to decant tank in event as per Chris C 14:56 - Chris C requested PCS support. Informed Artour L for assistance with Chris C work on blowers and SBR CMU = 11335937 | All Wastewater System ROC General | 2025-10-04
ROC | October | KSSP- UV ch 2 bank 2a adjacent lamp fail alarm came in disregard on shift report | All Wastewater System ROC General | 2025-10-08
ROC | October | NBSP - Vortext #2 Air Scour Uncommanded Close alarm came in. Ack/reset as per shift report Adeela Khan signing out | All Wastewater System ROC General | 2025-10-05
ROC | October | SEOC4- Phil R onsite for generator run. | All Wastewater System ROC General | 2025-10-02
ROC | October | AUSS - Pump 2 W disc header MV3 fail to close alarm. Checked site, pump has shut down and duty rotated to another pump. Reset alarm. | All Wastewater System ROC General | 2025-10-13
ROC | October | Carter Dunn Signing In, 10D/Clear | All Wastewater System ROC General | 2025-10-13
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-05
ROC | October | AUSS- P2 disc MV2 failed to open aalrm came in again P@ hasnt run in 2 days due to MV2 issue. Notified Chris R. Chris R will make a workorder to check it out today. Placed P2 in man off | All Wastewater System ROC General | 2025-10-08
ROC | October | JDSS- Neil O onsite for generator run and eyewash alarm test. | All Wastewater System ROC General | 2025-10-08
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-04
ROC | October | Ethan Ullalkar signing out. | All Wastewater System ROC General | 2025-10-04
ROC | October | AUSSMP - Channel inlet gate closed and fault alarms came in. Daniel K. is on site with Young J. and are isolating bar screen 1 | All Wastewater System ROC General | 2025-10-05
ROC | October | MTSP - Thickening tank level fault alarm. Disregard as per the shift report. AUSSSR - Line 1 valve over torque and fail to close alarm. Checked site, valve showing as travelling on SCADA. Line 1 inlet showing as unavailable, likely due to ongoing commissioning efforts. Line 2 and 3 are available. Unable to clear overtorque alarm. Sent email to OCO. AUSS - Pump 4 disc MV2 Fail to open alarm. Disregard if it can be cleared as per shift report. Cleared alarm. | All Wastewater System ROC General | 2025-10-14
ROC | October | Gluzen Ramos Ong signing in | All Wastewater System ROC General | 2025-10-03
ROC | October | SUSSWB- Darren B on site for generator run | All Wastewater System ROC General | 2025-10-08
ROC | October | SHSP- Lauren S working on RAS and WAS pumps. Disregard related alarms. | All Wastewater System ROC General | 2025-10-03
ROC | October | NBSP- Marcus R onsite testing filter drain sump alarm. | All Wastewater System ROC General | 2025-10-09
ROC | October | SUSSHS, Kevin K on site doing pump maint | All Wastewater System ROC General | 2025-10-14
ROC | October | SUSP- UV System Major Fault Alarm. Called Chris C. Chase J and electricians working on it. | All Wastewater System ROC General | 2025-10-02
ROC | October | AUSSSR - Line 2 overtorque. Called Dan K, disregard over the weekend as long we we have line 1 & 3. Consult | All Wastewater System ROC General | 2025-10-04
ROC | October | HLSSBS - Rick L & Parth P finished at site | All Wastewater System ROC General | 2025-10-10
ROC | October | Christian Van Beek signing in. | All Wastewater System ROC General | 2025-10-02
ROC | October | NBSP- Process Bld. Sanitary Sump HiHi Float. Called Marcus R. No answer. Will try again. 13:06- Marcus R will take a look. | All Wastewater System ROC General | 2025-10-02
ROC | October | SHSP - RAS pump 3 general alarm. Outstanding alarm from earlier today. Checked log book, Lauren S took the RAS pump OOS due to a water leak in the oil lines. | All Wastewater System ROC General | 2025-10-02
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-13
ROC | October | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-10-03
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-05
ROC | October | Adam Button signing out 14C clear | All Wastewater System ROC General | 2025-10-06
ROC | October | NMSSBP- Forcemain 1 Fault Alarm. Called Marcos T. Requested to call Daniel K. Called Daniel K. Requested to call Terry R. Called Terry R. No answer. | All Wastewater System ROC General | 2025-10-08
ROC | October | Carter Dunn Signing Out | All Wastewater System ROC General | 2025-10-13
ROC | October | Carter Dunn Signing In | All Wastewater System ROC General | 2025-10-06
ROC | October | PVSS, Gavin W on site testing the generator | All Wastewater System ROC General | 2025-10-06
ROC | October | NBSP- RAS train flow lo alarm came in. Recovered right away and no longer in lo flow condition. Emailed West wastewater team about outstanding alarm | All Wastewater System ROC General | 2025-10-06
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-11
ROC | October | Adeela Khan signing out | All Wastewater System ROC General | 2025-10-11
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-11
ROC | October | Ethan U signing in Weather 27. | All Wastewater System ROC General | 2025-10-06
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-12
ROC | October | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-10-03
ROC | October | YDSS + YNSS Normal Christian Van Beek signing out. | All Wastewater System ROC General | 2025-10-14
ROC | October | MTSS - Kyle R finished on site. No outstanding alarms. | All Wastewater System ROC General | 2025-10-10
ROC | October | EGSSSC - Diesel failure on dialer, Check site, generator in good standing | All Wastewater System ROC General | 2025-10-06
ROC | October | KCSSKR- Gavin W on site for generator run, dialer test and to test diesel containment float and hi lo temp alarms | All Wastewater System ROC General | 2025-10-08
ROC | October | YDSS + YNSS Normal Carter Dunn Signing Out | All Wastewater System ROC General | 2025-10-09
ROC | October | NBSSJA-Marcus R on site to test Station flood alarm, Sump pit hi alarm, Temp hi/lo alarm and doing check valve inspections will call when done | All Wastewater System ROC General | 2025-10-06
ROC | October | Carter Dunn Signing In | All Wastewater System ROC General | 2025-10-14
ROC | October | JDSS- Neil O onsite shutting down Odour Control | All Wastewater System ROC General | 2025-10-07
ROC | October | SUSP- Chris C on site for generator run | All Wastewater System ROC General | 2025-10-07
ROC | October | YDOC- Artour L onsite for commissioning of diesel tank LIT | All Wastewater System ROC General | 2025-10-07
ROC | October | Connor Smith signing out | All Wastewater System ROC General | 2025-10-09
ROC | October | Gluzen Ramos Ong signing out | All Wastewater System ROC General | 2025-10-07
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-15
ROC | October | SEOC - OCF Damper station flood & OCF water unusual flow rate, disregard as per shift report | All Wastewater System ROC General | 2025-10-15
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-15
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-10
ROC | October | Adeela Khan signing in. Weather: 11C and partly cloudy | All Wastewater System ROC General | 2025-10-11
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-13
ROC | October | LSSS - Pump 4 valve fault/overtorque. Placed pump in man/off and emailed area | All Wastewater System ROC General | 2025-10-15
ROC | October | GRSSWA - Nill O running generator and testing flood alarm and dialer alarm. | All Wastewater System ROC General | 2025-10-09
ROC | October | Humber Odour Control Facility - Frank I. (416 564 9862) from Region of Peel Wastewater called to inform of a sensor that gave him a critical alarm at around 4AM. HMSS wet well pumps had just shut down at 04:19 when Frank received the critical alarm and wanted to understand what HMSS was doing when this alarm came in. | All Wastewater System ROC General | 2025-10-11
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-11
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-03
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-14
ROC | October | SEOC- Barry M onsite for generator load test. | All Wastewater System ROC General | 2025-10-02
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-07
ROC | October | YDSS+YNSS normal Adam Button signing out | All Wastewater System ROC General | 2025-10-08
ROC | October | QVSSSR, Jeff from keyshack is on site | All Wastewater System ROC General | 2025-10-06
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-06
ROC | October | YDBR - F2 make up flow OOR alarm. Disregard as per the shift report. | All Wastewater System ROC General | 2025-10-04
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-04
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-04
ROC | October | SUSP - Continuing Chris C strategy of manual operations for blowers and iar valve operations. Opening/closing air valve and manually start/stop blowers as required every 20min following a 20 min rest time as requested | All Wastewater System ROC General | 2025-10-04
ROC | October | wrong book | All Wastewater System ROC General | 2025-10-01
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-09
ROC | October | LSSS- Phil D on site testing sump pit hi alarm and inadvertently cause surge tank alarms but cleared them | All Wastewater System ROC General | 2025-10-15
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-05
ROC | October | Adeela Khan Signing in. Weather: 14 C and clear | All Wastewater System ROC General | 2025-10-05
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-12
ROC | October | Connor Smith signing out | All Wastewater System ROC General | 2025-10-12
ROC | October | YDSS + YNSS Normal Christian Van Beek signing out. | All Wastewater System ROC General | 2025-10-13
ROC | October | NBSP- Vortex 1 Water Scour uncmd close alarm came in. Reset as per shift report | All Wastewater System ROC General | 2025-10-14
ROC | October | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-10-15
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-12
ROC | October | Christian Van Beek signing in. Weather: 20C and clear. | All Wastewater System ROC General | 2025-10-12
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-12
ROC | October | KSSSQW - Pump 4 flow low alarm. Checked site, operations are normal but trending shows that the pump speed and vibration are erratic. Triggered duty rotation, placed pump manual off and set pump to OOS. | All Wastewater System ROC General | 2025-10-12
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-13
ROC | October | NMEQBP- Historian Heartbeat Alarm. Notified Artour L. He will look into it. 14:55- Kingsley M is working on this. | All Wastewater System ROC General | 2025-10-01
ROC | October | Connor Smith signing in | All Wastewater System ROC General | 2025-10-07
ROC | October | Angelica Chepiga signing in,weather +11C | All Wastewater System ROC General | 2025-10-15
ROC | October | Adam Button signing out | All Wastewater System ROC General | 2025-10-15
ROC | October | SECC - Yash S completing a functional test and has requested that the low level alarm for SECC tank 2 be disregarded. | All Wastewater System ROC General | 2025-10-02
ROC | October | Christian Van Beek signing out. | All Wastewater System ROC General | 2025-10-04
ROC | October | SHSP- Chris S on site to work on air compressors. Dan H on site as well | All Wastewater System ROC General | 2025-10-14
ROC | October | KSSP- Cam B on site to work on membrane blowers | All Wastewater System ROC General | 2025-10-14
ROC | October | AUSSSR - Line 1 Valve overtorque alarm, will notify area. | All Wastewater System ROC General | 2025-10-03
ROC | October | SHSP- RAS/WAS drain sump high float alarm came in. notified Dan H. Dan H has left site but someone from team will attend KSSSQW Cam B working on P4 | All Wastewater System ROC General | 2025-10-14
ROC | October | YDSS+YNSS normal | All Wastewater System ROC General | 2025-10-01
ROC | October | Christian Van Beek signing out. | All Wastewater System ROC General | 2025-10-01
ROC | October | SUSP - Basin 1 ph lolo alarm. Basin is offline and empty. Disregard alarm. | All Wastewater System ROC General | 2025-10-05
ROC | October | Adeela Khan signing out | All Wastewater System ROC General | 2025-10-08
ROC | October | Angelica Chepiga signing in, weather +10C | All Wastewater System ROC General | 2025-10-01
ROC | October | KSSP- Ron from ITS onsite for wifi work. | All Wastewater System ROC General | 2025-10-01
ROC | October | KBSP- Filter 1 influent channel hihi alarm came in. Notified Young J will check on site AUSS- Wet well 3 LIT3 lolo alarm came in. Looks like LIT is acting sporadically. LIT4 is controlling and trending normally. Will continue to monitor and email central-east wastewater team of LIT issues #consult | All Wastewater System ROC General | 2025-10-01
ROC | October | KBSP- UV Ch2 uncommanded start alarm. Notified Young J informed ROC maintenance is on site working on UV faults | All Wastewater System ROC General | 2025-10-08
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-05
ROC | October | RHAMF- Jon C on site | All Wastewater System ROC General | 2025-10-14
ROC | October | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-10-04
ROC | October | SUSP - Chris C called to inform that the pumping stations are being diverted to the lagoon at SUSP, SBR 2 is operating. Chris has directed to disregard the SBR2 hi level alarm but to call the hihi level alarm. | All Wastewater System ROC General | 2025-10-04
ROC | October | Connor Smith signing out | All Wastewater System ROC General | 2025-10-07
ROC | October | Ethan U signing in | All Wastewater System ROC General | 2025-10-10
ROC | October | YWS + NYWS Normal | All Wastewater System ROC General | 2025-10-06
WEST | October | Onsite for station check and to collect weekly micro and Q4 samples W11330537 W11246998 Activated duty remotely Checked residuals mg/l Pre res @1400 Free analyzer 3,39 grab 3.40 Post res @1358 Free analyzer 1.72 grab 1.60 Treated HL @1415 Free analyzer 1.66 grab 1.69 Total grab 1.90 | Ansnorveldt Wells 2, 3 & Reservoir | 2025-10-29
WEST | October | -on site to complete station check -well duty not active -verified analyzers: 13:50 - post reservoir FCL analyzer = 1.57 mg/L Grab = 1.62 mg/L 13:53 - treated water FCL analyzer = 1.56 mg/L 13:53 - treated water grabs: Free chlorine = 1.60 mg/L Total chlorine = 1.77 mg/L -checked equipment -reviewed trends -recorded readings in PWQ sheet -no issues found -filled hypo tanks 32/32 L to 42/43 L | Ansnorveldt Wells 2, 3 & Reservoir | 2025-10-20
WEST | October | In to Complete Station Check and to collect bacti sample w11316318 Residuals Treated Free Grab: 1.69mg/L, Analyzer 1.72mg/L Total 1.97mg/L Post Reservoir Free grab 1.72mg/L, Analyzer 1.74mg/L Pre Reservoir Free grab 3.80mg/L, Analyzer 3.81mg/L No other issues on site | Ansnorveldt Wells 2, 3 & Reservoir | 2025-10-22
WEST | October | In to Complete Station Check Residuals Treated Free Grab: 1.58mg/L, Analyzer 1.58mg/L Post Reservoir Free grab 1.68mg/L, Analyzer 1.63mg/L No other issues on site | Ansnorveldt Wells 2, 3 & Reservoir | 2025-10-17
WEST | October | In to Complete Station Check Residuals Treated Free Grab: 1.85mg/L, Analyzer 1.70mg/L Adjusted treated total from 1.70-1.85mg/L after multiple grabs Post Reservoir Free grab 1.92mg/L, Analyzer 1.96mg/L No other issues on site | Ansnorveldt Wells 2, 3 & Reservoir | 2025-10-24
WEST | October | Onsite for station check Duty not active Checked residuals mg/l Post res @1351 Free analyzer 1.86 grab 1.81 Treated HL @1350 Free analyzer 1.80 grab 1.72 Total grab 1.96 Flushed ntu analyzer, station ntu fault came in. Message on unit said "dryer" did eventually clear | Ansnorveldt Wells 2, 3 & Reservoir | 2025-10-31
WEST | October | In to Complete Station Check Residuals Treated Free Grab: 1.75mg/L, Analyzer 1.74mg/L Post Reservoir Free grab 1.78mg/L, Analyzer 1.74mg/L No other issues on site | Ansnorveldt Wells 2, 3 & Reservoir | 2025-10-27
WEST | October | Onsite to perform annual maintenance/calibrations. Put the devices in calibration mode. Devices were done as below: High lift FIT, Pre-Reservoir AIT. Asked ROC to activate duty in order to calibrate Pre- Reservoir AIT. ROC activated the duty and both wells were running. Took a multiple grab samples and adjusted analyzer accordingly. Grab sample - 3.56 mg/l, AL Pre Res AIT - 3.58 mg/l. Put everything back in service. All the related alarms were cleared. No issues. Informed ROC, armed the building and left the site. | Ansnorveldt Wells 2, 3 & Reservoir | 2025-10-14
WEST | October | Informed ROC. Onsite to perform annual maintenance/calibrations. Used the calibration mode during the work. Devices were done as below: Post Reservoir AIT, WEL2_FIT, WEL3_FIT, WEL2_LIT, WEL3_LIT. Took a grab multiple grab samples. No adjustments required. Grab Sample - 1.53 mg/l , POST AIT - 1.52 mg/l. Put everything back in service. All the related alarms were cleared. No issues. Informed ROC, armed the building and left the site. | Ansnorveldt Wells 2, 3 & Reservoir | 2025-10-07
WEST | October | Responding to HLPs interlocked on Lolo reservoir, then post-reservoir, treated analyzer Lolo interlocks. Chlorine analyzers are fed from HLPs and system pressure (unable to feed sample water to analyzers if pressure is low). Requested PCS on call to bypass Reservoir Lolo interlock. Ran HLPs local to restore pressure and clear Chlorine analyzer Lolo interlocks, returned to auto once Reservoir Lolo interlock cleared. Requested PCS to temporarily mask Reservoir Lolo interlock to allow HLPs to run in auto until wells could increase reservoir level. Analyzer verification: Mg/L 0907 Treated G: FCl 1.41 A: FCl 1.20 0907 Post-Reservoir G: FCl 1.33 A: FCl 1.31 Pre-Reservoir (inlet) 1325 G: FCl 3.38 A: FCl 3.40 1352 G: FCl 3.14 A: FCl 3.16 Treated turbidimeter spiking due to air purging from high point of HL piping (can see air blasting out of drain line). Started W3 step test 0920. Run w3 local on to prevent interlocks during step test. Adjust FCV to produce 0.85l/s step 1. Step 2 1.20l/s Step 3 1.50l/s Exceeding w3 PTTW for purposes of well step testing, permitted within PTTW. Pre-Reservoir analyzer not receiving sampling flow due to lack of backpressure. Not adjusting backpressure valve yet to prevent analyzer and doing issues when returning to normal operation post step test. Completed 1 hour quiet period post step test. Place wells 2, 3 back to auto and monitor startup. Verify dosing via Reservoir inlet analyzer (see above) Inlet analyzer residuals are fluctuating, backpressure valve may require adjustment to smooth out sample flow and readings. Will monitor over weekend and adjust if necessary. Notified PCS on-call that reservoir Lolo interlock could be returned to normal. | Ansnorveldt Wells 2, 3 & Reservoir | 2025-10-03
WEST | October | -on site to complete station check -activated well duty for station check -hypo pump # 2 running at 42%, 4.9 rpm, DF = 125% -verified analyzers: 13:32 - post reservoir FCL analyzer = 1.71 mg/L Grab = 1.61/1.63/1.64 mg/L 13:38 - adjusted post reservoir analyzer to 1.63 mg/L based on average of 3 grabs 13:38 - treated water FCL analyzer = 1.62 mg/L 13:38 - treated water grabs: Free chlorine = 1.62 mg/L Total chlorine = 1.80 mg/L 13:44 - reservoir inlet FCL analyzer = 3.45 mg/L Grab = 3.42 mg/L -checked equipment -reviewed trends -recorded readings in PWQ sheet -no issues found | Ansnorveldt Wells 2, 3 & Reservoir | 2025-10-10
WEST | October | On site to complete station check and collect bacti sample (W11298614) checked trends:all okay -Topped up hypo tanks combined 33L to 43L -verified analyzers: Influent (Pre-Reservoir) Free Chlorine @ 14:33 Grab: 3.24 mg/L Analyzer: 3.50 mg/L Effluent (Post-Reservoir) Free Chlorine @ 14:25 Grab: 1.53 mg/L Analyzer: 1.57 mg/L Treated Free Chlorine @ 14:25 Grab: 1.49 mg/L Analyzer: 1.52 mg/L Treated Total Chlorine @ 14:25 Grab: 1.870 mg/L entered data into PD sheet Equipment okay | Ansnorveldt Wells 2, 3 & Reservoir | 2025-10-14
WEST | October | -on site to complete station check and to collect samples -sample work order # W11278549 -activated well duty -hypo pump # 1 running at 46%, 5.3 rpm, DF = 135% -verified analyzers: 13:34 - treated water FCL analyzer = 1.24 mg/L 13:34 - treated water grab: Free chlorine = 1.39/1.40/1.40 mg/L Total chlorine = 1.57 mg/L 13:41 - adjusted treated water analyzer to 1.40 mg/L based on average of 3 grabs 13:42 - collected weekly treated water micro sample 13:43 - collected weekly well # 2 raw water micro sample 13:43 - collected weekly well #3 raw water micro sample 13:48 -post reservoir analyzer = 1.74 mg/L Grab = 1.39/1.41/1.43 mg/L 13:52 - adjusted post reservoir analyzer to 1.41 mg/L based on average of 3 grabs 13:54 - reservoir inlet FCL analyzer = 3.15 mg/L Grab = 3.10 mg/L -checked equipment -reviewed trends -recorded readings in PWQ sheet -no issues found -filled hypo tanks 34/34L to 43/43 L | Ansnorveldt Wells 2, 3 & Reservoir | 2025-10-08
WEST | October | On site to complete station check and collect bacti sample (W11256350). -verified analyzers: Influent (Pre-Reservoir) Free Chlorine @ 11:00 Grab: 3.58 mg/L Analyzer: 3.56 mg/L Effluent (Post-Reservoir) Free Chlorine @ 11:03 Grab: 1.31 mg/L Analyzer: 1.30 mg/L Treated Free Chlorine @ 11:06 Grab: 1.15 mg/L Analyzer: 1.13 mg/L Treated Total Chlorine @ 11:06 Grab: 1.43 mg/L -checked equipment -checked trends -Topped up hypo tanks combined 56L to 92L -entered data into PD sheet | Ansnorveldt Wells 2, 3 & Reservoir | 2025-10-01
CENTRAL | October | -Performed station check - logged station readings into PWQ sheet Grab: treated total=2.68mg/L free=0.08mg/L@9:00 Analyzer: treated total=2.55mg/L free=0.03mg/L -Checked Depolox reagents - OK -Collected weekly BacT sample YD #W11331191 & in-house water quality samples | Aurora (East) First Commerce Elevated Tank | 2025-10-29
CENTRAL | October | -Collected NDMA sample YD #W11365118 | Aurora (East) First Commerce Elevated Tank | 2025-10-28
CENTRAL | October | -Performed station check - logged into PWQ sheet Grab: total=2.56mg/L free=0.05mg/L@15:50 Analyzer: total=2.58mg/L free=0.00mg/L -Collected weekly BacT sample YD W11279411 & NDMA sample YD #W11247982 -Checked Depolox reagents - OK | Aurora (East) First Commerce Elevated Tank | 2025-10-08
CENTRAL | October | -Performed station check - logged station readings into PWQ sheet Grab: free=0.05mg/L total=2.72mg/L@8:35 Analyzer: free=0.00mg/L total=2.61mg/L -Collected weekly BacT sample YD #W11299316, quarterly sample YD #W11247334, in-house water samples -Checked Depolox reagents - OK -Zeroed and Calibrated free analyzer based 3 grab tests | Aurora (East) First Commerce Elevated Tank | 2025-10-14
CENTRAL | October | -Finished the following work orders *Depolox analyzer maintenance *Portable generator test *Ventilation system inspection *Dehumidifier inspection *Tested low temp alarm *Performed H&S inspection *Heat trace inspection | Aurora (East) First Commerce Elevated Tank | 2025-10-02
CENTRAL | October | Station and equipment check Take weekly BacT sample and grabs @ 8:50 am from Outlet Total: 2.48 mg/l Free: 0.05 mg/l Also advanced monitoring readings on PD sheets ET ops normal | Aurora (East) First Commerce Elevated Tank | 2025-10-01
CENTRAL | October | On-site for a station and equipment check, no issues found. Entered all readings into PWQ sheet. Investigated building temp alarm, heaters turned off. Alarm did not specify high or low temp. Turned on all heaters, verified operation. Will continue to monitor remotely | Aurora (East) Wellington Pumping Station | 2025-10-27
CENTRAL | October | On-site for a station and equipment check. No issues found All readings entered in to PWQ sheet | Aurora (East) Wellington Pumping Station | 2025-10-17
CENTRAL | October | On-site for a station and equipment check, no issues found. All readings entered into PWQ sheet. | Aurora (East) Wellington Pumping Station | 2025-10-31
CENTRAL | October | Station and equipment checked, no issues found. All readings entered in to PWQ sheet. | Aurora (East) Wellington Pumping Station | 2025-10-10
CENTRAL | October | Vibration testing and grease both motors Pump 20 shots of grease both motors High vibration motor 5 | Aurora (East) Wellington Pumping Station | 2025-10-02
CENTRAL | October | Station Check (no issues found) | Aurora (East) Wellington Pumping Station | 2025-10-03
CENTRAL | October | Station and equipment checked, no issues found. All meter readings entered in to PWQ sheet | Aurora (East) Wellington Pumping Station | 2025-10-14
CENTRAL | October | On-site to perform various WO's Notified ROC panel -Generator testing under load :Hours start 364.3 Hours end 365.4 :Fuel start 2040L Fuel end 2004L :Oil pressure 49 psi :Water temp 170'f :Battery 31v :Oil temp 140'f :Volts 600 ;Hertz 60.1 -Building Temp Alarm test completed -Building Flood alarm test completed -Fuel Containment test completed -Overhead Hoist inspected -Pump and motor visual inspection completed -Pump bypass valve exercised -HVAC visual inspection completed -Air valve flushed and inspected -JHSC inspection completed -Surge system isolation valves exercised, (all valves) -Comprehensive housekeeping completed | Aurora (East) Wellington Pumping Station | 2025-10-09
CENTRAL | October | -Finished the following work orders *H&S inspection *Depolox analyzer maintenance *Eye wash station inspection | Aurora (North) Orchard Heights Elevated Tank | 2025-10-27
CENTRAL | October | -Performed station check - logged station readings into PWQ sheet Grab: free=0.08mg/L total=2.76mg/L@10:45 Analyzer: free=0.06mg/L total=2.88mg/L -Collected weekly BacT sample YD #W11299316, quarterly sample YD #W11247278, in-house water samples -Checked Depolox reagents - OK | Aurora (North) Orchard Heights Elevated Tank | 2025-10-14
CENTRAL | October | Re and re check valve Tried to isolate can not isolate Work called off | Aurora (North) Orchard Heights Elevated Tank | 2025-10-01
CENTRAL | October | Station and equipment check Take weekly BacT samples and grabs @ 12:35 pm Total: 2.47 mg/l Free: 0.05 ng/l ET ops normal | Aurora (North) Orchard Heights Elevated Tank | 2025-10-01
CENTRAL | October | -Performed station check - logged into PWQ sheet Grab: total=2.90mg/L free=0.06mg/L@9:10 Analyzer: total=2.81mg/L free=0.05mg/L -Collected weekly BacT sample YD W11279411 -Topped up Depolox KI solution | Aurora (North) Orchard Heights Elevated Tank | 2025-10-08
CENTRAL | October | Check chlorine removing line piping Clean out drain from chlorine removing system and flush | Aurora (North) Orchard Heights Elevated Tank | 2025-10-09
CENTRAL | October | On-site for a station and equipment check, no issues found. Chemical levels and systems ok. Topped up ammonia day tank 2 Added green and grey reagents in chemscan Verified analyzers, all readings and grabs entered into PWQ sheet | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-10-17
CENTRAL | October | Onsite to respond to CL2 leak alarm and chlorine halogen valve closure alarms Upon arrival, reopened all CL2 cylinders- no chlorine leak detected Reopened all CL2 cylinders and reset all halogen valves- reset alarms via scada Prior to reopening res discharge valve and placing chemical system back into auto, took grabs to verify analyzers: Pre (16:15): Grabs: Free- 0.00, Total- 2.00, Mono- 1.73, FA- 0.09, TA- 0.43 Analyzers: Free- 0.06, Total- 1.93, Mono- 1.89, FA- 0.08, TA- 0.36 Post (16:25): Grabs: Free- 0.04, Total- 2.20, Mono- 1.93, FA- 0.08, TA- 0.46 Analyzers: Free- 0.05, Total- 1.99, Mono- 2.07, FA- 0.10, TA- 0.38 At 16:36- placed chemical system back into auto, and ROC placed res discharge valve back into auto- will monitor while onsite Chlorine gas leak may have been caused by faulty gas sensor- informed Parth (inst) of sporadic gas detector trending- Parth will come to site to investigate further * Station back to normal operations- informed ROC, I will continue to monitor station via scada | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-10-31
CENTRAL | October | On-site for station check and weekly micro sampling (W11316238) work orders. Grab/analyzer results as follows (mg/L): Pre-Injection/Reservoir Outlet: Free Cl (09:31): G: 0.05 A: 0.04 Total Cl (09:31): G: 1.92 A: 1.90 Post-Injection: Free Cl (09:41): G: 0.05 A: 0.03 Total Cl (09:42): G: 1.92 A: 1.89 Collected micro sample. Entered station readings into shared PD excel file. Checked station and equipment, no new issues found. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-10-22
CENTRAL | October | On-site for station check Recordings in PWQ sheet Filled ammonia tank 2 Station ok | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-10-24
CENTRAL | October | Onsite for a station and equipment check, no issues found Chemical systems and levels ok. Topped up ammonia day tank 2 While verifying analyzers, power failure occurred. Temp generator set-up. Station isolated by B Hess, remotely | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-10-31
CENTRAL | October | on-site for a station and equipment check, no issues found Chemical systems and levels inspected verified that CL2 bank 1 empty, despite scale reading 9.5kg topped up ammonia day tank 1 Analyzers verified, all readings and grabs entered into PWQ sheet General cleaning | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-10-27
CENTRAL | October | Cylinder change on bank 1 with R Bewley | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-10-29
CENTRAL | October | On-site for station and equipment check, no issues found Verified analyzers, entered all readings and grabs into PWQ sheet. Chemical systems and levels ok, topped up ammonia day tank 1 | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-10-20
CENTRAL | October | On-site for JHSC inspection And comprehensive housekeeping. No issues found | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-10-16
CENTRAL | October | Replaced right chlorine cylinder with Jason Garnett. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-10-16
CENTRAL | October | Station Check (no issues found) input data to PWQ Verified Depolox (mg/L): 10:05 Pre Free: Grab 0.05. A 0.05 Total: Grab 1.89, A 1.88 10:18 Post: Free: Grab 0.04, A 0.03 Total: Grab 1.95, A 1.92 Chemscan: Topped up grey, green & yellow 10:15 Samples #11256552, #11256262, & operational | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-10-01
CENTRAL | October | Christian from ROC called for power blip @ AURSBS @ 7:12pm on 03-10-25, interlocking chemical pumps, asked him to place chemical pumps in Manual off and run sample pumps for 10 mins first and then turn chemical pumps back to auto in order to avoid spike at post injection side. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-10-04
CENTRAL | October | Ammonia S. Delivery (3 pallets) Ammonia Tank#2 new batch (before: 20.1CM (226l))(after 114.8cm(1285L)) | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-10-02
CENTRAL | October | Onsite for station and equipment check . Door to ammonia sulphate room is broken open. Unable to lock. Notified acting Team Lead J Garnett. He will be onsite within 20 mins to assess. Verified analyzers, all grabs and readings entered in to PWQ sheet. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-10-06
CENTRAL | October | On-site for station and equipment check, no issues found Chemical levels and systems ok Topped up ammonia day tank 2 Cylinder change bank 1 with J Zhang Verified analyzers, all grabs and readings entered in to PWQ sheet | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-10-10
CENTRAL | October | Station Check (no issues found) Input data to PWQ Verified Depolox (mg/L) 13:10 Pre: Free: Grab 0.03, A 0.05 Total: Grab 1.94, A 1,91 13:20 Post: Free: Grab 0.06, A 0.07 Total: Grab 3.05, A 3.10 Depolox: topped up distilled/KI & Acetate for both | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-10-03
CENTRAL | October | On-site for station and equipment check, no issues found. Chemical systems and levels ok. Topped up ammonia day tank 1. Weekly bacti sample taken. Verified analyzers, all measurements and grabs entered in to PWQ sheet | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-10-08
CENTRAL | October | On-site for station and equipment check, no issues found. Turned on heaters. Took weekly bacti and semi-operational samples taken Verified analyzer, all grabs and readings entered into PWQ sheet | Aurora (Southwest) Allenvale Elevated Tank | 2025-10-29
CENTRAL | October | On-site for station check and weekly micro sampling (W11316238) work orders. Grab/analyzer results as follows (mg/L): Free Cl (10:30): G: 0.06 A: 0.04 Total Cl (10:30): G: 2.06 A: 2.06 Collected micro sample. Entered station readings into shared PD excel file. Free Ammonia grab of 0.1mg/L, adjusted D1 from 45-60% to 40-60% to drawdown ET further, will return setpoints remotely later today. No new issues found, will monitor Free Ammonia residuals. | Aurora (Southwest) Allenvale Elevated Tank | 2025-10-22
CENTRAL | October | Attending site to check Free chlorine analyzer using too much electrolyte (W11333253). Re-seated membranes and re-filled electrolyte reservoir with new bottle. Old electrolyte was disposed of - it appeared less viscous than usual. ROC was notified before and after maintenance was performed. | Aurora (Southwest) Allenvale Elevated Tank | 2025-10-29
CENTRAL | October | Station Check (no issues found) 11:25 Verified Depolox (mg/L): Free: Grab 0.06, A 0.04 Total: Grab 2.04, A 1.97 Deplox: -new KI/distilled reagent -topped up Acetate -topped up electrolyte 11:40 Samples: #11256262, #11256552, & operational | Aurora (Southwest) Allenvale Elevated Tank | 2025-10-01
CENTRAL | October | Station and equipment checked, no issues found Verified analyzer, entered all readings and grabs in to PWQ sheet Weekly bacti sample taken | Aurora (Southwest) Allenvale Elevated Tank | 2025-10-08
CENTRAL | October | Station and equipment checked, no issues found. Weekly bacti, Q4?s and operational samples taken Verified analyzer, all readings amd grabs entered in to PWQ sheet | Aurora (Southwest) Allenvale Elevated Tank | 2025-10-14
CENTRAL | October | Work orders: #11280869 H.trace #11281213 jhs #11281756 low temp. #11282104 eywash #11282452 P. gen. #11280807 Deplox maint. 14:44 Verified (mg/l) Free: Grab 0.05, A 0.04 Total: Grab 2.02, A 1.97 | Aurora (Southwest) Allenvale Elevated Tank | 2025-10-02
CENTRAL | October | -Performed station - logged station readings into PWQ sheet -Checked Depolox reagents - OK | Aurora Orchard Heights Pumping Station & Reservoir | 2025-10-27
CENTRAL | October | -Performed station check - logged station readings into PWQ sheet -Checked Depolox reagents - OK | Aurora Orchard Heights Pumping Station & Reservoir | 2025-10-20
CENTRAL | October | On site to complete station check - Reservoir draining - Entered data into Process Data sheets - Equipment all good - Trends all good - Reagents all good - No other issues Treated free Cl @ 2:31pm G: 0.07mg/L A: 0.03mg/L Treated total Cl @ 2:37pm G: 2.78mg/L A: 2.85mg/L | Aurora Orchard Heights Pumping Station & Reservoir | 2025-10-23
CENTRAL | October | -Performed station check - logged station readings into PWQ sheet -Checked Depolox reagents - OK | Aurora Orchard Heights Pumping Station & Reservoir | 2025-10-17
CENTRAL | October | -Performed station check - logged station readings into PWQ sheet -Checked ChemScan reagents - OK | Aurora Orchard Heights Pumping Station & Reservoir | 2025-10-31
CENTRAL | October | Onsite to complete workorders Informed ROC (Carter D) Diesel test run completed with load no issues JHSC inspection complete Analyzer maintenance Grabs @ 12:35 pm Total: 2.90 mg/l Free: 0.02 mg/l No adjustments required reagents ok Station ops normal | Aurora Orchard Heights Pumping Station & Reservoir | 2025-10-21
CENTRAL | October | -Performed station check - logged station readings into PWQ sheet -Checked Depolox reagents - OK | Aurora Orchard Heights Pumping Station & Reservoir | 2025-10-03
CENTRAL | October | -Performed station check -Checked Depolox reagents | Aurora Orchard Heights Pumping Station & Reservoir | 2025-10-10
CENTRAL | October | Station and equipment check Took grabs @ 2:00 pm Total: 3.10 mg/l Free: 0.02 mg/l Reagents ok Ops normal | Aurora Orchard Heights Pumping Station & Reservoir | 2025-10-06
CENTRAL | October | Onsite to investigate future shutdown plan No valving today Ops normal | Aurora Orchard Heights Pumping Station & Reservoir | 2025-10-03
CENTRAL | October | -Performed station check - logged station readings into PWQ sheet Grab: free=0.07mg/L total=3.00mg/L@10:05 Analyzer: free=0.02mg/L total=2.74mg/L -Collected weekly BacT sample YD #W11299316, quarterly sample YD #W11247278, in-house water samples -Checked Depolox reagents - OK -Calibrated total analyzer based 3 grab tests | Aurora Orchard Heights Pumping Station & Reservoir | 2025-10-14
CENTRAL | October | Onsite with Lee F to repair p3 check valve, informed ROC site would be offline Could not isolate to repair, will reschedule Also take weekly BacT samples and grabs @ 13:10 Total: 2.86 mg/l Free: 0.05 mg/l Reagents ok Ops back to normal | Aurora Orchard Heights Pumping Station & Reservoir | 2025-10-01
CENTRAL | October | -Responded hi post free - Upon arrival, post free analyzer reading=0.21mg/L - Performed grab test, post free=0.09mg/L - Reviewed logbook - Post free reagents changed today - Replace the reagents and primed the analyzer - analyzer reading=0.10mg/L | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2025-10-17
CENTRAL | October | On-site for a station and equipment check, no issues found. Weekly bacti and semi operational samples taken Chemical levels and systems ok Verified analyzers, all readings and grabs entered into PWQ sheet | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2025-10-29
CENTRAL | October | On-site for station check Recordings in PWQ sheet Reagents ok Filled ammonia tank 1 | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2025-10-24
CENTRAL | October | On-site for station check and weekly micro sampling (W11316238) work orders. Replaced Reservoir Outlet Free Cl and Pre-Injection Total Cl CL17 analyzer reagents. Grab/analyzer results as follows (mg/L): Pre-Injection: Free Cl (08:02): G: 0.05 A: 0.05 Total Cl (08:03): G: 1.57 A: 1.56 Post-Injection: Free Cl (08:12): G: 0.04 A: 0.06 Total Cl (08:13): G: 1.54 A: 1.52 Z3: Free Cl (08:21): G: 0.07 A: 0.08 Total Cl (08:27): G: 2.32 A: 2.29 Reservoir Outlet: Free Cl (08:31): G: 0.06 A: 0.07 Total Cl (08:32): G: 2.32 A: 2.28 Collected micro sample. Checked station and equipment, no new issues found. Site readings in shared PD excel file. | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2025-10-22
CENTRAL | October | On site to assist in troubleshooting recent issues with the metro valve. Found control relays in the scada cabinet malfunctioning. Replaced relays with heavier duty relays. | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2025-10-30
CENTRAL | October | On-site for cl2 cylinder change with J Zhang. Tested and reset cl2 leak alarms. | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2025-10-21
CENTRAL | October | On-site for a station and equipment check, no issues found. Chemical systems and levels ok, topped up ammonia day tank 1. Verified analyzers, all readings and grabs entered in to PWQ sheet. Changed reagents in Zone 3 free and total, and post injection free | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2025-10-17
CENTRAL | October | Station and equipment checked, no issues found. Verified analyzers and entered all readings and grabs in to PWQ sheet. | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2025-10-06
CENTRAL | October | Station and equipment checked, no issues found Verified Weekly bacti, Q4?s and operational samples taken. Analyzers verified, all readings and grabs entered in to PWQ sheet | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2025-10-14
CENTRAL | October | Station Check (no issues found) input data to PWQ Verified CL17s (mg/L) 8:20 Pre-Inj: Free: Grab 0.05, A 0.05 Total: Grab 1.45, A 1.46 8:30 Post-Inj: Free: Grab 0.08, A 0.09 Total: Grab 2.68, A 2.74 8:40 Reservoir: Free: Grab 0.06, A 0.08 Total: Grab 2.30, A 2.24 9:30 Zone 3: Free: Grab 0.06, A 0.05 Total: Grab 2.30, A 2.25 Samples #11256262, #11256552, & operational Chemscan: topped up green, & distilled | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2025-10-01
CENTRAL | October | Station and equipment checked, no issues found Chemical systems and levels ok Verified analyzers, all readings and grabs entered in to PWQ sheet | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2025-10-10
CENTRAL | October | Changed Cl2 bank B with Joe Williams. | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2025-10-02
CENTRAL | October | Station Check (no other issues found) input data to PWQ Verified CL17s (mg/l): 9:34 Pre: Free: Grab 0.07, A 0.05 Total: Grab 1.52, A 1.48 9:43 Post: Free: Grab 0.07, A 0.09 Total: Grab 2.54, A 2.59 9:54 Reservoir: Free: Grab 0.05, A 0.08 Total: Grab 2.22, A 2.22 (new reagents) 10:20 Zone 3: Free: Grab 0.05, A 0.06 Total: Grab 2.30, A 2.24 10:53 Adjusted Cl2:Amm ratio from 4.4 to 4.5 Free ammonia Before: 0.10 mg/L , After: 0.02mg/L Ammonia Tank #2 (new batch) | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2025-10-03
CENTRAL | October | Station and equipment checked, no issues found Chemical levels and systems inspected, ok Weekly baci sample taken Verified analyzers, all grabs and readings emtered in to PWQ sheet pre F @ 1404 g:0.09 a:0.08 pre T @1406 g:2.20 a:2.26 Post F @ 1410 g:0.10 a:0.07 Post T @ 1413 g:2.18 a:2.28 Zone 3 1414 T a: 2.24 g:2.19 F a :0.06 g:0.09 Outlet T a:2.23 g:2.22 F a:0.07 g:0.10 | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2025-10-08
CENTRAL | October | -Performed station check - logged station readings into PWQ sheet -Changed treated total reagents | Aurora Well 5 | 2025-10-31
CENTRAL | October | -Performed station check - logged station readings into PWQ sheet -Checked CL17 reagents - OK -Collected in-house water quality samples | Aurora Well 5 | 2025-10-27
CENTRAL | October | Topped up NaSi tank to 3820L. | Aurora Well 5 | 2025-10-27
CENTRAL | October | Onsite w/ Jerry Z to rebuild ejector #2, found small piece of plastic in throat piece, removed debris and changed diaphragm and all ?O? rings Re installed and test ran chlorine train 2 with no issues, placed back in service Ops normal | Aurora Well 5 | 2025-10-28
CENTRAL | October | -Changed chlorine cylinder | Aurora Well 5 | 2025-10-17
CENTRAL | October | Topped up NaSi tank 2277 to 3044L. | Aurora Well 5 | 2025-10-27
CENTRAL | October | -Responded influent free lolo alarm - upon arrival, influent free analyzer reading=0.40mg/L - performed grab test influent free=0.47mg/L - checked chlorinator - chlorinator #2 not dosing - put chlorinator #2 offline - will rebuild ejector #2 later - backflushed contact tank until influent free=0.80mg/L - reset alarms and restarted well 5 in manual - well ran normally -Finished the following work orders *Chlorine leak test *Deep well exhaust valve inspection *CL17 analyzer maintenance *Turbidimeter maintenance *Exhaust fan inspection *H&S inspection *Chemical system inspection | Aurora Well 5 | 2025-10-21
CENTRAL | October | Onsite to investigate lolo influence chlorine lockout with Jerry Z. 09:25 influence free grab 2.18. Analyzer 2.22. Tested chlorine system with no issues. Well interlocked after analyzer dropped one reading. Analyzer and chlorine system ok. Water has chlorine and ok. 09:30 ran well in manual to test. No issues found. | Aurora Well 5 | 2025-10-30
CENTRAL | October | Adjusted flow setting from 60 to 45 L/s. | Aurora Well 5 | 2025-10-16
CENTRAL | October | -Performed station check - logged station readings into PWQ sheet -Checked CL17 reagents - OK | Aurora Well 5 | 2025-10-17
CENTRAL | October | -Performed station check - logged station readings into PWQ sheet -Changed treated free reagents -Collected in-house water quality sample | Aurora Well 5 | 2025-10-20
CENTRAL | October | -Performed station check - logged station readings into PWQ sheet Grab: free=0.17mg/L total=2.98mg/L influent free=2.74mg/L effluent free=2.52mg/L Analyzer: free=0.13mg/L total=3.02mg/L influent free=2.70mg/L effluent free=2.53mg/L -Collected weekly BacT sample YD #W11317110 -Checked CL17 reagents - OK | Aurora Well 5 | 2025-10-22
CENTRAL | October | -Performed station check - logged station readings into PWQ sheet Grab: treated total=2.94mg/L free=0.21mg/L@13:10 Influent free=2.76mg/L effluent free=2.54mg/L Analyzer:treated total=2.96mg/L free=0.13mg/L Influent free=2.69mg/L effluent free=2.46mg/L -Checked CL17 reagents - OK -Collected weekly BacT sample YD #W11331191 -Isolated contact tank and cleaned silicate injection point 1 due to low silicate dosage and high turbidity | Aurora Well 5 | 2025-10-29
CENTRAL | October | -Backflushed contact tank and restarted well 5 after chlorinator rebuilt -Performed station check - logged station readings into PWQ sheet -Checked CL17 regents - OK -Topped up drip oil reservoir | Aurora Well 5 | 2025-10-03
CENTRAL | October | Station and equipment check Take weekly BacT sample and grabs at 10:10 am Treated Total: 2.64 mg/l Treated Free: 0.10 mg/l Chemicals/reagents ok No adjustments required All other readings on PD sheets Ops normal | Aurora Well 5 | 2025-10-01
CENTRAL | October | -Performed station check = logged station readings into PWQ sheet -Checked CL17 reagents - OK | Aurora Well 5 | 2025-10-10
CENTRAL | October | -Performed station check - logged station readings into PWQ sheet Grab: treated total=2.74mg/L free=0.20mg/L@12:00 influent free=2.52mg/L effluent free=2.32mg/L Analyzer: treated total=2.74mg/L free=0.12mg/L influent free=2.69mg/L effluent free=2.33mg/L -Checked CL17 reagents - OK -Calibrated influent free analyzer based on 3 grab tests -Collected weeky BacT sample YD #W11299316, quarterly samples YD #11247264 | Aurora Well 5 | 2025-10-14
CENTRAL | October | -Performed station check - logged into PWQ sheet Grab: treated total=2.80mg/L free=0.17mg/L@10:10 influent free=2.72mg/L effluent free=2.48mg/L Analyzer: total=2.92mg/L free=0.12mg/L influent free=2.73mg/L effluent free=2.45mg/L -Collected weekly BacT sample YD W11279411 & in-house water quality sample -Changed influent free reagents | Aurora Well 5 | 2025-10-08
CENTRAL | October | Rebuild and calibrated both chlorinators. Put back in service. Operator Jerry back flush the line. | Aurora Well 5 | 2025-10-03
CENTRAL | October | Station and equipment check Took grabs @ 10:45 am wells not running Treated Total: 2.26 mg/l Treated Free: 0.05 mg/l Changed chlorine cylinder w/ Angelica Chemicals/reagents ok Ops normal | Aurora Well 5 | 2025-10-06
CENTRAL | October | -Performed station check | Aurora Well 6 | 2025-10-27
CENTRAL | October | -Performed station check | Aurora Well 6 | 2025-10-20
CENTRAL | October | Onsite for station check: Collected Ballymore BV sample Station/equipment- Ok | Aurora Well 6 | 2025-10-20
CENTRAL | October | Station and equipment check Well 6 remains OFFLINE Ops mormal | Aurora Well 6 | 2025-10-03
CENTRAL | October | Station and equipment check Site OFFLINE as per norm JHSC inspection complete no issues Ops normal | Aurora Well 6 | 2025-10-08
CENTRAL | October | -Performed station check | Aurora Well 6 | 2025-10-14
CENTRAL | October | -Performed station check - logged station readings into PWQ sheet Grab: treated total=3.06mg/L free=0.20mg/L@12:00 Influent free=2.64mg/L effluent free=2.64mg/L Analyzer:treated total=3.07mg/L free=0.13mg/L Influent free=2.60mg/L effluent free=2.54mg/L -Checked CL17 reagents - OK -Collected weekly BacT sample YD #W11331191 | Aurora Wells 1-4 Water Treatment Plant | 2025-10-29
CENTRAL | October | -Performed station check - logged station readings into PWQ sheet -Checked Depolox reagents - OK *Performed chemical system inspection | Aurora Wells 1-4 Water Treatment Plant | 2025-10-17
CENTRAL | October | Receive bulk silicate and assist with chlorine overhaul | Aurora Wells 1-4 Water Treatment Plant | 2025-10-16
CENTRAL | October | Onsite to complete chlorine system repair. Rebuilt chlorine injectors and lines. Replaced regulators. 10:00 tested and found minor chlorine leak. Shut off system and scrubbers activated. Notified roc. Found leak and tightened fitting. Treated with no further issues. 11:00 placed system back in auto. | Aurora Wells 1-4 Water Treatment Plant | 2025-10-16
CENTRAL | October | Onsite for treated station check: Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok Onsite for raw station check: Station/equipment- Ok | Aurora Wells 1-4 Water Treatment Plant | 2025-10-24
CENTRAL | October | -Performed station check - logged station readings into PWQ sheet -Checked CL17 reagents - OK -Collected in-house water quality sample | Aurora Wells 1-4 Water Treatment Plant | 2025-10-20
CENTRAL | October | -Performed chlorine system overhaul - cannot finish the job and will continue tomorrow- locked chlorine boosters out | Aurora Wells 1-4 Water Treatment Plant | 2025-10-16
CENTRAL | October | -Changed chlorine cylinders | Aurora Wells 1-4 Water Treatment Plant | 2025-10-20
CENTRAL | October | -Performed station check - logged station readings into PWQ sheet -Checked CL17 reagents - OK -Collected in-house water quality samples -Changed chlorine cylinders | Aurora Wells 1-4 Water Treatment Plant | 2025-10-27
CENTRAL | October | -Performed station check - logged station readings into PWQ sheet -Checked CL17 reagents - OK -Increased Cl: N ratio from 3.7 to 3.9 due to high FA | Aurora Wells 1-4 Water Treatment Plant | 2025-10-31
CENTRAL | October | Activated well 3 in manual to help maintain au central supply during outer outages at aursbs. | Aurora Wells 1-4 Water Treatment Plant | 2025-10-31
CENTRAL | October | Safety person for chlorine cylinders change | Aurora Wells 1-4 Water Treatment Plant | 2025-10-01
CENTRAL | October | -Performed station check - logged station readings into PWQ sheet Grab: treated free=0.20mg/L total=2.94mg/L@14:35 influent free=2.56mg/L effluent free=2.50mg/L Analyzer: treated free=0.13mg/L total=3.00mg/L influent free=2.56mg/L effluent free=2.45mg/L -Collected weekly BacT sample YD #W11299316, quarterly sample YD #W11247250, in-house water samples -Checked Depolox reagents - OK | Aurora Wells 1-4 Water Treatment Plant | 2025-10-14
CENTRAL | October | -Finished the following work orders *Air relief valve inspection *PRV maintenance *H&S inspection *CL17 analyzer maintenance *Turbidimeter maintenance *Diesel generator test run Pre-run inspection - good Hour Start 83.60 Stop 84.80 Fuel Start 7470L Stop 7502 Generator operating stats while under load (P2 and P3): RPM- 1800 Oil pressure-79psi Oil temp- 188 F Coolant temp- 179 F Fuel pressure- 103psi Fuel temp- 89F Frequency- 60 Hz Voltage- 603 V Amperage- 168 A Once test run completed, placed generator back into auto as per normal operations- informed ROC * | Aurora Wells 1-4 Water Treatment Plant | 2025-10-07
CENTRAL | October | Station and equipment check Take weekly BacT sample and grabs @ 14:55 Treated Total: 2.50 mg/l Treated Free: 0.12 mg/l Wells running in manual for sample collection All other readings on PD sheets Changed chlorine cylinders with Lee F, right bank Chemicals/reagents ok Wells placed back in auto Ops normal | Aurora Wells 1-4 Water Treatment Plant | 2025-10-01
CENTRAL | October | -Performed station check - logged into PWQ sheet Grab: treated total=2.96mg/L free=0.15mg/L@13:05 influent free=2.64mg/L effluent free=2.52mg/L Analyzer: total=3.07mg/L free=0.13mg/L influent free=2.60mg/L effluent free=2.54mg/L -Collected weekly BacT sample YD W11279411 & in-house water quality sample -Checked CL17 reagents - OK | Aurora Wells 1-4 Water Treatment Plant | 2025-10-08
CENTRAL | October | Ammonia S. (1 pallet) delivery | Aurora Wells 1-4 Water Treatment Plant | 2025-10-02
CENTRAL | October | Station and equipment check Took grabs @ 12:55 pm Treated Total: 2.64 mg/l Treated Free: 0.10 mg/l *wells just activated readings still climbing Topped up ammonia tank 2 Chemicals/reagents ok Checked Raw side visual inspection ok Ops normal | Aurora Wells 1-4 Water Treatment Plant | 2025-10-06
CENTRAL | October | -Changed chlorine cylinders -Performed station check - logged station readings into PWQ sheet -Changed influent free reagents | Aurora Wells 1-4 Water Treatment Plant | 2025-10-10
EAST | October | On site for preventative maintenance Closed station suction and discharge valves at the request of Metro Toronto and the ORO to facilitate a leak test on the Toronto side Found the discharge valve closure starved the free chlorine analyzer so opened the discharge valves and purged the air from the water main Disregard the low combined chlorine reading as it is due to the isolation of the discharge header and reduced sample flow and is not indicative of a true low chlorine residual. Zero calibrated the free chlorine analyzer and verified, results below. Verified analyzers, 11:30, mg/L FCl G 0.05; A 0.08 TCl G 1.40; A 1.36 Completed Dehumidifier cleaning and inspection Ventilation system inspection Pipe support visual inspection Deplox analyzer maintenance Flood alarm test Sump pump maintenance JHSC inspection Inspected suction chamber for water, attempted to pump down with a trash pump with inadequate head. Observed suction chamber cycled appropriately with the station sump Station and equipment okay | Bayview Pumping Station | 2025-10-16
EAST | October | On site for suction chamber inspection, exercise of suction valves and flood alarms: Placed pumps to manual off Performed CSE into suction chamber with Jack Palmer. Triggered flood alarms and exercises suction valves - informed ROC. Exercised surge valves in discharge chamber and performed chamber inspection. Equipment back to auto Cleared alarms, station ok | Bayview Pumping Station | 2025-10-23
EAST | October | On site for station check Verified chlorine analyzers, 14:05, in mg/L Free Cl - G 0.06; A 0.09 Total Cl - G 1.60; A 1.65 Reviewed station trends and inspected equipment - okay Recorded observations in the shared PWQ sheet Station and equipment okay | Bayview Pumping Station | 2025-10-27
EAST | October | On site for station check Station not running at time of station check Verified analyzers, 11:37, in mg/L Free Cl: G 0.07; A 0.09 Total Cl: G 1.69; A 1.66 Reviewed station trends, inspected equipment, station okay | Bayview Pumping Station | 2025-10-20
EAST | October | On site for station check Verified chlorine analyzers, 14:10, in mg/L Free Cl - G 0.06; A 0.08 Total Cl - G 1.58; A 1.59 Inspected station equipment Recorded observations in the shared PWQ sheet Station and equipment okay | Bayview Pumping Station | 2025-10-24
EAST | October | Returned to site to zero and span calibrate the free chlorine flow through cell again, 14:50 Free chlorine, in mg/L G 0.06 A 0.06 Total chlorine, in mg/L G 1.39 A 1.33 Adjusted to match grab average Station and equipment okay | Bayview Pumping Station | 2025-10-16
EAST | October | On site to complete station check. At 12:34 cleared all outstanding alarms on site. No OOS equipment On site. HVAC fault alarm issue being looked into by contractor. Time: 12:45 Grab (mg/l) Analyzer (mg/l) Free: 0.14 0.15 Total: 1.48 1.52 Checked trends and site. Verified analyzers with grabs. | Bayview Pumping Station | 2025-10-31
EAST | October | On site for station check Recorded observations and chlorine residuals in the shared PWQ sheet Station and equipment okay | Bayview Pumping Station | 2025-10-17
EAST | October | On site to check station and equipment. Pump duty is not active upon arrival. Switched pump duty so that P1 and P3 are in duty 1. Station readings and chlorine grabs are in PWQ sheet. Reviewed trends, station is under normal operation. | Bayview Pumping Station | 2025-10-06
WEST | October | Onsite for station check Pd8 duty active Checked residuals mg/L Pd7 @1317 Total analyzer 1.57 grab 1.84 Free analyzer 0.00 grab 0.03 Adjusted Total analyzer based on average of multiple grabs | East Vaughan Teston Pumping Station | 2025-10-24
WEST | October | On site to complete station check. Free chlorine Grab: 0.02mg/L Analyzer: 0.00mg/L Total chlorine Grab: 1.72mg/L Analyzer 1.86mg/L Reagents all ok | East Vaughan Teston Pumping Station | 2025-10-31
WEST | October | On site to replace damaged and malfunctioning power factor correction components for PD8 pump 1. Also completed Station electrical p.m. by checking and topping up distilled water in the 125 V DC battery system as well as Rotork actuator batteries. | East Vaughan Teston Pumping Station | 2025-10-16
WEST | October | Onsite for station check Duties not active Checked residuals mg/l @1317 Total analyzer 1.61 grab 1.35 Free analyzer 0.00 grab 0.02 Adjusted total analyzer based on average of multiple grabs | East Vaughan Teston Pumping Station | 2025-10-17
WEST | October | On site for chlorine cylinder change | East Vaughan Teston Pumping Station | 2025-10-16
WEST | October | On site to complete station check. Free chlorine Grab: 0.04mg/L Analyzer: 0.01mg/L Total chlorine Grab: 1.59mg/L Analyzer 1.63mg/L Reagents all ok | East Vaughan Teston Pumping Station | 2025-10-06
WEST | October | Onsite to complete work orders Completed monthly generator run Start Fuel Bulk tank 50.7% 6918.8 L Day tank 72.2% 1820L Hrs 230.7 Stop Fuel Bulk tank 49.2% 6649.3 L Day tank 78.7% 1988 L Hrs 232.2 Completed depolox maintenance Electrolyte, grit, and reagents ok Grabs Total analyzer 1.65 grab 1.70 Free analyzer 0.00 grab 0.01 | East Vaughan Teston Pumping Station | 2025-10-07
WEST | October | Onsite for station check Checked residuals mg/l Pd7 @1104 Total analyzer 1.75 grab 1.82 Free analyzer 0.01 grab 0.05 Reagents ok | East Vaughan Teston Pumping Station | 2025-10-03
WEST | October | In to complete station check. Site remains Offline. No issues. | Holland Landing East Elevated Tank | 2025-10-20
WEST | October | On site to complete PMs. Notified ROC of relevant alarms. Chamber work completed with Jacob. -Tested chamber low temp alarm -Tested chamber flood alarm -Inspected chamber valve gallery: all good -Inspected altitude valve: all good -exercised and closed drain valve: all good -Inspected and turned on heater for the year -Completed JHSC inspection: all good -Tested equipment shed low temp alarm -Ran generator: all good | Holland Landing East Elevated Tank | 2025-10-02
WEST | October | Onsite for station check Checked residuals mg/l @1247 Total grab 0.80 Free grab 0.05 | Holland Landing Sherwood Pumping Station | 2025-10-31
WEST | October | On site to complete station check. Free Chlorine 0.06mg/L Total Chlorine 1.06mg/L No issues on site | Holland Landing Sherwood Pumping Station | 2025-10-24
WEST | October | On site to complete station check. Free Chlorine 0.09mg/L Total Chlorine 1.09mg/L No issues on site | Holland Landing Sherwood Pumping Station | 2025-10-17
WEST | October | On site to complete station check. Free Chlorine 0.07mg/L Total Chlorine 1.36mg/L No issues on site | Holland Landing Sherwood Pumping Station | 2025-10-27
WEST | October | In to complete station check. Enter data into PWQ. No issues. | Holland Landing Sherwood Pumping Station | 2025-10-20
WEST | October | On site to complete PMs. Notified ROC of relevant alarms. -Completed JHSC inspection for pumping station and tower --Tested low temp alarm -Test ran diesel generator: Hours before run: 1425.3 hrs Fuel before run: 86.7 cm / 704 L Run start @ 10:45 Loading periodically as pumps maintain pressure Run end @ 11:52 (cooldown ended at 11:57) Hours after run: 1426.5 hrs Fuel after run: 85.9 cm / 698 L | Holland Landing Sherwood Pumping Station | 2025-10-02
WEST | October | On site to complete station check. Free Chlorine @ 10:10: 0.04 mg/L Total Chlorine @ 10:10: 1.38 mg/L -Pump 2 running -Entered data into PD sheet -Checked trends | Holland Landing Sherwood Pumping Station | 2025-10-03
WEST | October | On site to complete station check. Free Chlorine 0.05 mg/L Total Chlorine 0.85 mg/L No issues on site | Holland Landing Sherwood Pumping Station | 2025-10-15
WEST | October | -on site to complete station check -checked equipment -reviewed trends -pump #1 hours = 35146.6 -pump #2 hours = 7640.2 -pump #3 hours = 7211.0 -pump #4 hours = 2129.7 11:20 - collected grab sample: Free chlorine = 0.03 mg/L Total chlorine = 1.43 mg/L -recorded readings in PWQ sheet -no issues found | Holland Landing Sherwood Pumping Station | 2025-10-10
WEST | October | -on site to complete station check -checked equipment -reviewed trends 14:28 - collected grab sample: Free chlorine = 0.03 mg/L Total chlorine = 1.03 mg/L -recorded readings in PWQ sheet -no issues found | Holland Landing Sherwood Pumping Station | 2025-10-06
WEST | October | In to complete station check. Site is offline for rehab. Enter data into PWQ. Analyzer reagent levels good. Effluent cl17 reagents may need changed by wed, Fri. No issues. | Holland Landing Well No. 1 | 2025-10-20
WEST | October | On site for station check - site offline for rehab Residuals Treated Total Grab: 1.92mg/L Analyzer: 1.87mg/L Treated Free Grab: 0.06mg/L, Analyzer: 0.04mg/L IWS on site to reinstall pump Reagents all ok | Holland Landing Well No. 1 | 2025-10-27
WEST | October | On site for station check - site offline for rehab Residuals Treated Total Grab: 2.22mg/L Analyzer: 2.19mg/L Treated Free Grab: 0.06mg/L, Analyzer: 0.06mg/L Effluent Free Grabs: 0.11mg/L, Analyzer: 0.10mg/L Influent Free Grabs: 0.05mg/L, Analyzer: 0.03mg/L Changed out effluent reagents | Holland Landing Well No. 1 | 2025-10-22
WEST | October | Onsite for station check Site offline pending results Checked residuals mg/l Influent free @0958 Free analyzer 0.03 grab 0.03 Effluent free @1000 Free analyzer 0.06 grab 0.07 Treated @1002 Total grab 2.07 grab 2.00 Free analyzer 0.04 grab 0.05 Cleared back flush needed interlock because well is still isolated and never ran to waste | Holland Landing Well No. 1 | 2025-10-31
WEST | October | Work orders: #11258977 scrubber #11259030 scrubber samples #11261290 cl2 kit #11259142 cl2 leak #11259712 jhs #11260647 turb #11259299 CL17s maint. 13:44 Verified CL17s (mg/L) Influent Free: Grab 0.05, A 0.05 Effluent Free: Grab 0.04, A 0.03 Treated: Free Grab 0.05, A 0.02 Total: Grab 1.77, A 1.77 | Holland Landing Well No. 1 | 2025-10-16
WEST | October | Changed/replaced unit heater contactor. Tested Ok | Holland Landing Well No. 1 | 2025-10-22
WEST | October | On site for station check - site offline for rehab Residuals Treated Total Grab: 2.38mg/L Analyzer: 2.36mg/L Treated Free Grab: 0.06mg/L, Analyzer: 0.06mg/L Effluent Free Grabs: 0.11mg/L, Analyzer: 0.10mg/L Influent Free Grabs: 0.05mg/L, Analyzer: 0.03mg/L | Holland Landing Well No. 1 | 2025-10-17
WEST | October | On site for station check - site offline for rehab Residuals Treated Total Grab: 2.12mg/L Analyzer: 2.13mg/L Treated Free Grab: 0.06mg/L, Analyzer: 0.05mg/L Effluent Free Grabs: 0.14mg/L, Analyzer: 0.12mg/L Influent Free Grabs: 0.05mg/L, Analyzer: 0.03mg/L Reagents all ok | Holland Landing Well No. 1 | 2025-10-24
WEST | October | -on site to complete station check -well offline for rehabilitation -checked equipment -reviewed trends -CL17 reagents ok -verified chlorine analyzers: 09:35 - Treated water analyzers: FCL = 0.05 mg/L TCL = 2.25 mg/L 09:35 - Treated water grabs: FCL = 0.09 mg/L TCL = 2.30 mg/L -recorded readings in PWQ sheet -no issues found | Holland Landing Well No. 1 | 2025-10-08
WEST | October | -on site to complete station check -well offline for rehabilitation -checked equipment -reviewed trends -CL17 reagents ok -verified chlorine analyzers: 10:29 - Treated water analyzers: FCL = 0.05 mg/L TCL = 2.18 mg/L 10:29 - Treated water grabs: FCL = 0.00 mg/L TCL = 2.24 mg/L 10:39 - Influent FCL Analyzer = 0.04 mg/L 10:39 - Influent grab: Free chlorine = 0.02 mg/L 10:40 - Effluent FCL Analyzer = 0.08 mg/L 10:40 - Effluent grab: Free chlorine = 0.11 mg/L -recorded readings in PWQ sheet -no issues found | Holland Landing Well No. 1 | 2025-10-10
WEST | October | On site to complete station check. Site is offline and isolated. Influent Free Chlorine @ 9:10 Grab: 0.01 mg/L Analyzer: 0.04 mg/L Effluent Free Chlorine @ 9:08 Grab: 0.09 mg/L Analyzer: 0.10 mg/L Treated Free Chlorine @ 9:05 Grab: 0.08 mg/L Analyzer: 0.06 mg/L Treated Total Chlorine @ 9:05 Grab: 2.36 mg/L Analyzer: 2.34 mg/L -Data entered into PD sheet | Holland Landing Well No. 1 | 2025-10-03
WEST | October | -on site to complete station check -well offline for rehabilitation -checked equipment -reviewed trends -replaced treated CL17 reagents -verified chlorine analyzers: 11:02 - Treated water analyzers: FCL = 0.07 mg/L TCL = 2.40 mg/L 11:02 - Treated water grabs: FCL = 0.05 mg/L TCL = 2.44 mg/L 11:07 - Influent FCL Analyzer = 0.05 mg/L 11:07 - Influent grab: Free chlorine = 0.05 mg/L 11:11 - Effluent FCL Analyzer = 0.11 mg/L 11:11 - Effluent grab: Free chlorine = 0.13 mg/L -recorded readings in PWQ sheet -no issues found | Holland Landing Well No. 1 | 2025-10-06
WEST | October | On site to complete station check. Verified analyzers: Influent Free Chlorine @ 12:38 Grab: 3.08 mg/L Analyzer: 3.16 mg/L Effluent Free Chlorine @ 12:37 Grab: 2.86 mg/L Analyzer: 2.87 mg/L Treated Free Chlorine @ 12:28 Grab: 0.16 mg/L Analyzer: 0.16 mg/L Treated Total Chlorine @ 12:28 Grab: 3.22 mg/L Analyzer: 3.22 mg/L Sharon Valve Total Chlorine @ 12:45 Grab: 2.38 mg/L -Checked trends -Entered data into PD sheet -Topped up ammonia tank 1 | Holland Landing Well No. 2 | 2025-10-20
WEST | October | Onsite for cl2 delivery Received 12 full 12 empties taken away | Holland Landing Well No. 2 | 2025-10-28
WEST | October | On site for station check Residuals Treated Total Grab: 2.98mg/L Analyzer: 3.43-2.98mg/L Treated Free Grab: 0.15mg/L, Analyzer: 0.19mg/L Effluent Free Grabs: 2.62mg/L, Analyzer: 2.59mg/L Influent Free Grabs: 3.06mg/L, Analyzer: 3.11mg/L Performed advanced monitoring (SL1000) Total Chlorine 2.87mg/L Mono 2.49mg/L FA 0.13mg/L TA 0.63mg/L Sharon Valve grab Total Chlorine 1.2mg/L Adjusted treated total from 3.43-2.98mg/L after multiple grabs No other issues on site | Holland Landing Well No. 2 | 2025-10-24
WEST | October | Onsite for annual calibrations Informed ROC. ROC contacted operations. Operations placed well in manual off Used cal mode on scada during the work Instruments calibrated: NIT, WITs, FITs, Chlorinators, Cl2 leak detectors, chemical LITs, WELL LIT. Noticed scada alarm from previous night for discharge PIT. Discharge PIT failed calibration and was replaced with new. Configured and calibrated. Replaced right side chlorine cylinder (it was empty) Chlorine analyzers still outstanding. Will return to complete them Informed ROC, let them know to put duty back to auto Armed building and left site | Holland Landing Well No. 2 | 2025-10-17
WEST | October | On site for station check and bacti sample w11316468 Residuals Treated Total Grab: 2.98mg/L Analyzer: 2.97mg/L Treated Free Grab: 0.10mg/L, Analyzer: 0.14mg/L Effluent Free Grabs: 2.68mg/L, Analyzer: 2.67mg/L Influent Free Grabs: 3.14mg/L, Analyzer: 3.07mg/L Performed advanced monitoring (SL1000) Total Chlorine 2.79mg/L Mono 2.55mg/L FA 0.00mg/L TA 0.49mg/L Sharon Valve grab Total Chlorine 2.44mg/L Changed out influent free reagents | Holland Landing Well No. 2 | 2025-10-22
WEST | October | Topped up silicate from 30.5cm to 96.4cm. | Holland Landing Well No. 2 | 2025-10-30
WEST | October | On site for cylinder change | Holland Landing Well No. 2 | 2025-10-23
WEST | October | On site for station check and bacti sample w11298896 Residuals Treated Total Grab: 1.76mg/L Analyzer: 1.73mg/L Treated Free Grab: 0.03mg/L, Analyzer: 0.05mg/L Effluent Free Grabs: 0.10mg/L, Analyzer: 0.13mg/L Influent Free Grabs: 2.28mg/L, Analyzer: 2.25mg/L Changed out treated free reagents Inst on site for calibrations | Holland Landing Well No. 2 | 2025-10-17
WEST | October | Informed ROC. Performed annual calibration and put instruments in Cal mode while doing the tasks. Devices done were four AITs. Took grabs at the sample line. Influent free AIT1=1.65 mg/l Grab=1.61mg/l Effluent free AIT2 = 1.84 mg/l Grab=1.85 mg/l Treated free AIT3=0.03 mg/l Grab=0.05 mg/l Treated total AIT4=1.47 mg/l Grab=1.49 mg/l All alarms were cleared after the job. No other issues encountered. ROC run the well and everything looked good. | Holland Landing Well No. 2 | 2025-10-23
WEST | October | Onsite for station check and to collect weekly micro and Q4 samples W11330838 W11247012 Activated duty Checked residuals mg/L Influent Free @1042 Analyzer 2.76 grab 2.80 Effluent free @1044 Analyzer 2.36 grab 2.36 Treated @1051 Total analyzer 2.76 grab 2.70 Free analyzer 0.17 grab 0.18 Sl1000 MCl 2.34 f nh3 0.07 t nh3 0.53 Sharon feed @1057 Total grab | Holland Landing Well No. 2 | 2025-10-29
WEST | October | Details: On site for station check Residuals Treated Total Grab: 1.46mg/L Analyzer: 1.41mg/L Treated Free Grab: 0.5mg/L, Analyzer: 0.03mg/L Effluent Free Grabs: 0.16mg/L, Analyzer: 0.15mg/L Influent Free Grabs: 2.58mg/L, Analyzer: 2.63mg/L Topped up ammonia tank 2 from 17-80cm | Holland Landing Well No. 2 | 2025-10-27
WEST | October | -on site to respond to influent hihi alarms -verified influent analyzer: 11:36 - analyzer = 3.92 grab = 3.18/3.32/3.24 mg/L 11:43 - adjusted influent analyzer to 3.25 mg/L based on average of 3 grabs -will monitor | Holland Landing Well No. 2 | 2025-10-06
WEST | October | Changed chlorine cylinder B with Jacob Muzzin. | Holland Landing Well No. 2 | 2025-10-02
WEST | October | On site to complete station check. Influent Free Chlorine @ 13:18 Grab: 3.14 mg/L Analyzer: 3.22 mg/L Effluent Free Chlorine @ 13:21 Grab: 2.72 mg/L Analyzer: 2.76 mg/L Treated Free Chlorine @ 13:23 Grab: 0.18 mg/L Analyzer: 0.15 mg/L Treated Total Chlorine @ 13:23 Grab: 3.18 mg/L Analyzer: 3.16 mg/L Sharon Valve Total Chlorine @ 13:25 Grab: 2.30 mg/L -Checked trends -Data entered into PD sheet | Holland Landing Well No. 2 | 2025-10-03
WEST | October | -on site to complete station check and to collect samples -well running in auto -cl2 booster pump # 1 running at 190 psi -chlorinator # 1 70% open dosing 73 ppd, vac = -680 mbar, DF = 160% -silicate pump # 1 running at 36%, 21.9 rpm -ammonia pump # 2 running at 76%, 80 psi, 140 strokes / min -checked equipment -reviewed trends -replaced treated TCL CL17 reagents -filled ammonia tank #1 75 L to 365 L 08:34 - Sharon Valve grab: TCL = 1.81 mg/L MCL = 0.89 mg/L TNH3 = 0.40 mg/L FNH3 = 0.22 mg/L Temp = 12.4 -verified chlorine analyzers: 08:46 - Treated water analyzers: FCL = 0.13 mg/L TCL = 3.17 mg/L 08:46 - Treated water grabs: FCL = 0.10 mg/L TCL = 3.20 mg/L MCL = 2.87 mg/L TNH3 = 0.65 mg/L FNH3 = 0.09 mg/L Temp = 11.2 08:57 - collected weekly treated water micro sample - W/O # W11278715 08:57 - collected weekly raw water micro sample - W/O # W11278715 -increased ammonia pump #2 max flow setpoint 105 to 108 ml/min 09:03 - Influent FCL Analyzer = 3.26 mg/L 09:03 - Influent grab: Free chlorine = 3.20 mg/L 09:08 - Effluent FCL Analyzer = 2.74 mg/L 09:08 - Effluent grab: Free chlorine = 2.74 mg/L -recorded readings in PWQ sheet -no issues found | Holland Landing Well No. 2 | 2025-10-08
WEST | October | Increased chlorinator #1 df 157 to 159% | Holland Landing Well No. 2 | 2025-10-13
WEST | October | Increased chlorinator 2 DF 157 to 159% | Holland Landing Well No. 2 | 2025-10-11
WEST | October | -on site to complete station check -well running in auto -completed cylinder change -filled ammonia tank #2 89 L to 381 L -cl2 booster pump # 1 running at 190 psi -chlorinator # 1 70% open dosing 72 ppd, vac = -680 mbar, DF = 160% -silicate pump # 1 running at 36%, 21.9 rpm -ammonia pump # 2 running at 75%, 75 psi, 140 strokes/min -checked equipment -reviewed trends -replaced effluent CL17 reagents -adjusted flow to influent chlorine analyzer causing reading to spike -verified analyzer: 09:12 - Influent FCL Analyzer = 4.09 mg/L 09:12 - Influent grab: Free chlorine = 3.30/3.38/3.42 mg/L 09:21 - adjusted influent analyzer to 3.37 mg/L based on average of 3 grabs 09:25 - Sharon Valve grab: TCL = 1.45 mg/L MCL = 0.74 mg/L TNH3 = 0.39 mg/L FNH3 = 0.24 mg/L -verified chlorine analyzers: 09:36 - Treated water analyzers: FCL = 0.15 mg/L TCL = 3.31 mg/L 09:36 - Treated water grabs: FCL = 0.13 mg/L TCL = 3.34 mg/L MCL = 2.87 mg/L TNH3 = 0.64 mg/L FNH3 = 0.08 mg/L 09:39 - Effluent FCL Analyzer = 2.85 mg/L 09:39 - Effluent grab: Free chlorine = 2.88 mg/L -put sharon valve into duty 1, collected grab: TCL = 1.68 mg/L MCL = 0.82 mg/L TNH3 = 0.40 mg/L FNH3 = 0.24 mg/L -recorded readings in PWQ sheet -influent analyzer has low signal warning, shut down well and cleaned analyzer -verified analyzer after clean: 10:36 - analyzer = 2.81 grab = 3.00/3.00/2.98 10:41 - adjusted influent analyzer to 2.99 mg/L based on average of 3 grabs -will monitor | Holland Landing Well No. 2 | 2025-10-06
WEST | October | -on site to complete station check -well running in manual -completed cylinder change -cl2 booster pump # 2 running at 165 psi -chlorinator # 1 68% open dosing 70 ppd, vac = -480 mbar, DF = 157% -silicate pump # 2 running at 35%, 21.8 rpm -ammonia pump # 2 running at 59%, 75 psi, 116 strokes/min -checked equipment -reviewed trends -CL17 reagents ok 09:15 - Sharon Valve grab: TCL = 2.15 mg/L MCL = 1.38 mg/L TNH3 = 0.40 mg/L FNH3 = 0.13 mg/L Temp = 12.0 -verified chlorine analyzers: 09:27 - Influent FCL Analyzer = 3.11 mg/L 09:27 - Influent grab: Free chlorine = 3.04 mg/L 09:35 - Effluent FCL Analyzer = 2.60 mg/L 09:35 - Effluent grab: Free chlorine = 2.68 mg/L 09:46 - Treated water analyzers: FCL = 0.12 mg/L TCL = 3.02 mg/L 09:46 - Treated water grabs: FCL = 0.17 mg/L TCL = 3.10 mg/L MCL = 2.58 mg/L TNH3 = 0.55 mg/L FNH3 = 0.04 mg/L -recorded readings in PWQ sheet -no issues found -well returned to auto | Holland Landing Well No. 2 | 2025-10-10
WEST | October | On site for cylinder change | Holland Landing Well No. 2 | 2025-10-15
WEST | October | #11292616 scrubber #11292891 cL2 leak #11295249 silicate (performed draw down, no change) #11294654 turb maint. #11293236 prv #11293582 prv #11294453 hi/lo temp #11294576 jhs #11293069 CL17s 12:25 Verified (mg/L) Influent : Free Grab 2.4, A 2.07 Effluent: Free Grab 0.32, A 0.34 Treated: Free Grab 0.05, A 0.05 Total: Grab 1.51, A 1.49 12:16 Activated Duty 13:10 High Influent Free analyzer (4.20mg/l) Took grabs and adjusted to 3.60 | Holland Landing Well No. 2 | 2025-10-09
WEST | October | On site to complete station check and collect bacti sample (W11256752). Influent Free Chlorine @ 13:23 Grab: 3.30 mg/L Analyzer: 3.21 mg/L Effluent Free Chlorine @ 13:29 Grab: 2.78 mg/L Analyzer: 2.71 mg/L Treated Free Chlorine @ 13:35 Grab: 0.08 mg/L Analyzer: 0.13 mg/L Treated Total Chlorine @ 13:35 Grab: 3.18 mg/L Analyzer: 3.22 mg/L Sharon Valve Total Chlorine @ 13:51 Grab: 2.48 mg/L -Checked trends -Data entered into PD sheet | Holland Landing Well No. 2 | 2025-10-01
WEST | October | On site for station check and bacti sample w11298896 Residuals Treated Total Grab: 2.38mg/L Analyzer: 2.44mg/L Treated Free Grab: 0.10mg/L, Analyzer: 0.12mg/L Effluent Free Grabs: 2.07mg/L, Analyzer: 2.03mg/L Influent Free Grabs: 3.10mg/L, Analyzer: 3.12mg/L Performed advanced monitoring (SL1000) Total Chlorine 2.33mg/L Mono 2.04mg/L FA 0.01mg/L TA 0.51mg/L Topped up ammonia tank 2 from 16-80cm | Holland Landing Well No. 2 | 2025-10-14
WEST | October | On site to complete station check Verified analyzers @0935 Pre-injection Free chlorine Grab: 0.06mg/L Analyzer: 0.08mg/L Total chlorine Grab: 1.98mg/L Analyzer: 1.99mg/L Post-Injection Free chlorine Grab: 0.08mg/L Analyzer: 0.08mg/L Total chlorine Grab: 1.92mg/L Analyzer: 2.16mg/L *just started draining will come down* | Holland Landing West Elevated Tank | 2025-10-17
WEST | October | On site to complete station check and to collect bacti sample w11316468 Verified analyzers @0845 Pre-injection Free chlorine Grab: 0.05mg/L Analyzer: 0.05mg/L Total chlorine Grab: 1.41mg/L Analyzer: 1.34mg/L SL1000 FCL 0.09mg/L TCL 1.28mg/L Mono 0.65mg/L FA 0.21mg/L TA 0.30mg/L Post-Injection Free chlorine Grab: 0.06mg/L Analyzer: 0.09mg/L Total chlorine Grab: 3.08mg/L Analyzer: 3.49mg/L adjusted to 3.08mg/L after multiple grabs SL1000 TCL 2.73mg/L Mono 2.29mg/L FA 0.00mg/L TA 0.44mg/L Tank TCL 0.82mg/L Mono 0.34mg/L Nitrite 0.004mg/L FA 0.27mg/L TA 0.34mg/L Reagents all ok Adjusted inlet free ammonia from 0.3-0.2mg/L No issues on site | Holland Landing West Elevated Tank | 2025-10-22
WEST | October | #11365114 MDMA resample (8:15) 8:10 Verified Depoplox (mg/L) Pre: Free: Grab 0.03, A 0.04 Total: Grab 0.96, A 1.01 Post: Free: Grab 0.04, A 0.04 Total: Grab 0.96, A 0.92 | Holland Landing West Elevated Tank | 2025-10-28
WEST | October | On site to receive hypo delivery | Holland Landing West Elevated Tank | 2025-10-17
WEST | October | On site to complete station check Verified analyzers @10:45 Pre-injection Free chlorine Grab: 0.05mg/L Analyzer: 0.06mg/L Total chlorine Grab: 1.48mg/L Analyzer: 1.51mg/L SL1000 Mono 0.32mg/L FA 0.26mg/L TA 0.32mg/L Post-Injection Free chlorine Grab: 0.05mg/L Analyzer: 0.08mg/L Total chlorine Grab: 2.72mg/L Analyzer 2.68mg/L SL1000 TCL 2.68mg/L Mono 2.14mg/L FA 0.12mg/L TA 0.54mg/L Tank TCL 0.64mg/L Mono 0.25mg/L Nitrite 0.005mg/L FA 0.33mg/L TA 0.38mg/L Reagents all ok | Holland Landing West Elevated Tank | 2025-10-27
WEST | October | Back on site to retest post injection after 30mins of ammonia dosage change Post-Injection SL1000 TCL 2.72mg/L Mono 2.37mg/L FA 0.14mg/L TA 0.61mg/L Adjusted inlet free ammonia to 0.25mg/L Post-Injection SL1000 TCL 2.85mg/L Mono 2.42mg/L FA 0.10mg/L TA 0.57mg/L | Holland Landing West Elevated Tank | 2025-10-22
WEST | October | Attending site to check Ammonia and Hypo tank LITs (W11236093). It appears that the ammonia tank level trend has been good for the past few weeks. The Hypo Tank LIT was replaced and configured. All associated alarms were cleared and the ROC was notified before and after maintenance work. | Holland Landing West Elevated Tank | 2025-10-28
WEST | October | On site to complete station check. Enter data into PWQ. Analyzer reagent levels good. Inspect chemical hits, no issues. Adjust dosing SP: ammonia inlet SP from 0.25 to 0.30mg/L based on pre and post Fnh3 grabs. Cl2:fnh3 ratio previously adjusted to 4.2 from 4.5. No issues. | Holland Landing West Elevated Tank | 2025-10-20
WEST | October | Ran hypo pumps back to tank to troubleshoot dosing concerns. No setpoint changes made. | Holland Landing West Elevated Tank | 2025-10-03
WEST | October | On site to collect bacti sample (W11256752). Free chlorine @ 9:07 Grab: 0.06 mg/L Total chlorine @ 9:07 Grab: 1.62 mg/L -Sample taken while tower draining | Holland Landing West Elevated Tank | 2025-10-01
WEST | October | Increased target residual 3.15 to 3.40 mg/L | Holland Landing West Elevated Tank | 2025-10-13
WEST | October | Increased target residual 3.15 to 3.40 mg/l | Holland Landing West Elevated Tank | 2025-10-14
WEST | October | On site to complete station check and to collect back sample Verified analyzers @13:40: Pre-injection Free chlorine Grab: 0.06 mg/L Analyzer: 0.06 mg/L Total chlorine Grab: 1.50mg/L Analyzer: 1.53mg/L Post-Injection Free chlorine Grab: 0.06 mg/L Analyzer: 0.06 mg/L Total chlorine Grab: 1.71mg/L Analyzer: 1.73mg/L Tank TCL 0.77mg/L Mono 0.25mg/L FA 0.28mg/L TA 0.33mg/L | Holland Landing West Elevated Tank | 2025-10-14
WEST | October | On site to complete station check. Verified analyzers: Pre-injection Free chlorine @ 14:26 Grab: 0.06 mg/L Analyzer: 0.03 mg/L Total chlorine @ 14:26 Grab: 0.83 mg/L Analyzer: 0.85 mg/L Post-Injection Free chlorine @ 14:36 Grab: 0.06 mg/L Analyzer: 0.06 mg/L Total chlorine @ 14:42 Grab: 3.00 mg/L Analyzer: 2.91 mg/L -Entered data into PD sheet -Checked trends | Holland Landing West Elevated Tank | 2025-10-01
WEST | October | -On-site to complete station check -activated system duty -checked equipment -reviewed trends -depolox reagents ok -rechlor active, reform and boost -hypo pump #2 running at 23%, 49 strokes/min, 54 psi -ammonia pump # 1 running at 4%, 10 strokes/min, 52 psi -verified chlorine analyzers: 11:35 - Grabs from tank: Free Chlorine = 0.04 mg/L Total Chlorine = 1.36 mg/L MCL = 0.30 mg/L TNH3 = 0.26 mg/L FNH3 = 0.20 mg/L NO2 = 0.002 mg/L NO3 = 0.00 mg/L temp = 13.9 11:52 - Pre injection Analyzer readings: Free Chlorine = 0.05 mg/L Total Chlorine = 1.53 mg/L 11:52 - Pre injection Grabs: Free Chlorine = 0.02 mg/L Total Chlorine = 1.20/1.14/1.14 mg/L MCL = 0.36 mg/L TNH3 = 0.26 mg/L FNH3 = 0.19 mg/L -reduced incoming free ammonia setpoint from 0.30 to 0.25 mg/L 12:14 - adjusted pre injection TCL analyzer to 1.16 mg/L based on average of 3 grabs 12:22 - Post injection Analyzer readings: Free Chlorine = 0.07 mg/L Total Chlorine = 3.02 mg/L 12:22 - Post injection Grabs: Free Chlorine = 0.05 mg/L Total Chlorine = 3.06 mg/L MCL = 2.30 mg/L TNH3 = 0.51 mg/L FNH3 = 0.05 mg/L -recorded readings in PWQ sheet -no issues found -placed dechlorination pucks in drain chamber | Holland Landing West Elevated Tank | 2025-10-10
WEST | October | -On-site to complete station check -system duty active -checked equipment -reviewed trends -depolox reagents ok -rechlor active, reform and boost -hypo pump #1 running at 36%, 66 strokes/min, 52 psi -ammonia pump # 1 running at 12%, 29 strokes/min, 52 psi 12:23 - Grabs from tank: Free Chlorine = 0.02 mg/L Total Chlorine = 1.19 mg/L MCL = 0.33 mg/L TNH3 = 0.31 mg/L FNH3 = 0.25 mg/L NO2 = 0.001 mg/L NO3 = 0.0 mg/L temp = 16.8 -verified chlorine analyzers: 12:33 -Pre injection Analyzer readings: Free Chlorine = 0.05 mg/L Total Chlorine = 1.11 mg/L 12:33 -Pre injection Grabs: Free Chlorine = 0.07 mg/L Total Chlorine = 1.14 mg/L MCL = 0.34 mg/L TNH3 = 0.36 mg/L FNH3 = 0.29 mg/L 12:45 - Post injection Analyzer readings: Free Chlorine = 0.09 mg/L Total Chlorine = 3.37 mg/L 12:45 - Post injection Grabs: Free Chlorine = 0.06 mg/L Total Chlorine = 3.60/3.66/3.66/3.62 mg/L MCL = 2.64 mg/L TNH3 = 0.46 mg/L FNH3 = 0.00 mg/L 13:02 - adjusted post injection TCL analyzer to 3.64 mg/L based on average of 4 grabs -recorded readings in PWQ sheet -completed drawdown on hypo pump #2 - max flow = 172 ml/min -adjusted SCADA max flow setpoint 120 to 172 ml/min -completed drawdown on hypo pump #1 - max flow = 167 ml/min -adjusted SCADA max flow setpoint 115 to 167 ml/min -adjusted hypo pump #2 max flow setpoint from 172 to 140 ml/min to target post injection TCL residual of 3.15 mg/L -adjusted hypo pump #1 max flow setpoint from 167 to 140 ml/min to target post injection TCL residual of 3.15 mg/L -completed drawdown on ammonia pump #2 - max flow = 155 ml/min, scada setpoint = 157 ml/min -completed drawdown on ammonia pump #1 - max flow = 100 ml/min, scada setpoint = 100 ml/min 14:13 - pre injection grabs: MCL = 0.44 TNH3 = 0.40 FNH3 = 0.31 -increased inlet free ammonia setpoint 0.25 to 0.30 mg/L 14:25 - post injection grabs, ammonia pump #2 running: MCL = 2.05 TNH3 = 0.47 FNH3 = 0.07 14:44 - post injection grabs, ammonia pump #1 running: MCL = 2.12 TNH3 = 0.47 FNH3 = 0.05 -found tower isolation valves fully opened, should be in tapered position for proper mixing. Adjusted valves and post injection residual increased -increased both hypo pump max flow setpoints 140 to 170 ml/min -site back to normal operation, will monitor | Holland Landing West Elevated Tank | 2025-10-06
WEST | October | Lowered hypo tank LOLO level from 15 to 5 cm | Holland Landing West Elevated Tank | 2025-10-13
WEST | October | -On-site to complete station check and collect samples -system duty active, tower =55 % -checked equipment -reviewed trends -filled depolox reagents -rechlor active, reform and boost -hypo pump #1 running at 28%, 57 strokes/min, 52 psi -ammonia pump # 1 running at 9%, 18 strokes/min, 54 psi -verified chlorine analyzers: 10:09 - Grabs from tank: Free Chlorine =0.05 mg/L Total Chlorine = 1.47 mg/L MCL = 0.44 mg/L TNH3 = 0.36 mg/L FNH3 = 0.27 mg/L NO2 = 0.002 mg/L NO3 = 0.003 mg/L temp = 15.4 10:19 - Pre injection Analyzer readings: Free Chlorine = 0.05 mg/L Total Chlorine =1.40 mg/L 10:19 - Pre injection Grabs: Free Chlorine = 0.06 mg/L Total Chlorine = 1.41 mg/L MCL = 0.50 mg/L TNH3 = 0.40 mg/L FNH3 = 0.30 mg/L 10:29 - Post injection Analyzer readings: Free Chlorine = 0.08 mg/L Total Chlorine = 3.23 mg/L 10:29 - Post injection Grabs: Free Chlorine = 0.05 mg/L Total Chlorine = 3.18 mg/L MCL = 2.21 mg/L TNH3 = 0.50 mg/L FNH3 = 0.06 mg/L -recorded readings in PWQ sheet -no issues found -filled ammonia tank 215 L to 321 L -deactivated system duty to collect samples 11:33 - grab sample: Free Chlorine = 0.03 mg/L Total Chlorine = 1.80 mg/L 11:37 - collected weekly regulatory micro sample - W/O # W11278715 11:37 - collected Q4 NDMA sample - W/O # W11247870 -collected operational ATP and iron sequestration samples -activated system duty to complete fill cycle -replaced ammonia pump #2 check valves with degassing check valves -completed draw down - pump max flow = 111 ml/min, adjusted scada setpoint from 157 to 110 ml/min -put pump into duty 1 to test and collected post injection grab: MCL = 2.23 TNH3 = 0.50 FNH3 = 0.06 -placed dechlorination pucks in drain chamber | Holland Landing West Elevated Tank | 2025-10-08
WEST | October | Filled hypo tank 13.86 cm to 34.09 cm | Holland Landing West Elevated Tank | 2025-10-15
WEST | October | -on site to verify analyzers 18:20 -Pre injection Analyzer readings: Total Chlorine = 1.97 mg/L 18:20 -Pre injection Grabs: Total Chlorine = 1.40/1.47/1.44 mg/L 18:32 - adjusted pre injection TCL analyzer to 1.44 mg/L based on average of 3 grabs 18:35 -Post injection Analyzer readings: Total Chlorine = 1.38 mg/L 18:35 -Post injection Grabs: Total Chlorine = 1.41 mg/L | Holland Landing West Elevated Tank | 2025-10-12
WEST | October | Decreased target residual 3.40 to 3.15 mg/l | Holland Landing West Elevated Tank | 2025-10-15
WEST | October | Onsite to complete work orders Changed minimum flow start set point from 20 to 10l/s Hypo Pump 1 ran to sight glass 190 ml/min Pump 2 ran to sight glass 180ml/min When duty activated tried to run hypo pump 1 Was not dosing correctly low post inj total and combined alarms came in Adjusted max flow set point from 167 to 105 L\s Ammonia Pump 1 to sight glass Average 105 ml/min Pump 2 to sight glass Average 120 ml/min Topped up acetate buffer in cl2 analyzer Changed eye wash solution in wash in pipe gallery Dechlor added to chamber | Holland Landing West Elevated Tank | 2025-10-02
WEST | October | Responding to pre-inj Lolo combined chlorine alarm. Notified by ROC at 2049 once Lolo alarm triggered. Relief for continuous monitoring analyzers applies to Pre-Inj analyzer. Residuals: mg/L 2138 Pre-inj G: FCl 0.04 TCL 0.36 A: FCl 0.01 TCL 0.33 Based on grabs, analyzer readings were accurate when combined residual was reading below 0.25mg/L with less than 0.05mg/L FCl. Adjusted Flow to Waste valve from 40 to 30%, ET drained to 22%. Increased FCV2 to 30L/s. Added dechlor pucks to carboy diffuser in stormsewer chamber. AWQI170271 S2A filed, MECP SAC, MOH notified for low FCl, Combined Cl residuals based on analyzer readings over significant time period. Would not be reportable for YR based on not directing water to users, directing low residual water to waste pre-emptively. Filed on behalf of EG for best practice. request ROC to continue flushing past 7 hours if practical, discontinue flushing if Lo tower alarm level reached (21%). | Holland Landing West Elevated Tank | 2025-10-07
WEST | October | On site to complete station check and resolve low combined post injection chlorine alarms. Fixed valving issue. Adjusted hypo pump 2 max flow from 130 mL/min to 120 mL/min. Verified analyzers: Pre-injection Free chlorine @ 14:14 Grab: 0.02 mg/L Analyzer: 0.03 mg/L Total chlorine @ 14:14 Grab: 0.90 mg/L Analyzer: 0.89 mg/L Post-Injection Free chlorine @ 14:25 Grab: 0.08 mg/L Analyzer: 0.08 mg/L Total chlorine @ 14:25 Grab: 3.33 mg/L Analyzer: 3.29 mg/L -Entered data into PD sheet -Checked trends | Holland Landing West Elevated Tank | 2025-10-03
WEST | October | Increased target residual 3.4 to 3.5 mg/L | Holland Landing West Elevated Tank | 2025-10-11
WEST | October | Reverted dosing setpoints to normal | Holland Landing West Elevated Tank | 2025-10-12
WEST | October | -observed from remote SCADA that pre-injection combined chlorine was less than 0.25 mg/L and free chlorine less than 0.05 mg/L while flushing distribution system at start of tower fill cycle. Water was being directed to waste and not directed to users -low chlorine analyzer readings occurred from 13:14 to 13:47, still within one hour distribution system continuous analyzer regulatory relief window. Combined chlorine reading reached minimum of 0.22 mg/L -arrived on site and collected grab samples: 14:06 - pre-injection analyzer readings: Free chlorine = 0.01 mg/L Total Chlorine = 0.29 mg/L 14:06 - grabs : Free chlorine = 0.02 mg/L Total chlorine = 0.40/0.39/0.40 mg/L 14:18 - adjusted pre injection total chlorine analyzer to 0.40 mg/L based on average of 3 grabs -grab samples indicate pre-injection total chlorine analyzer was falsely reading low during this period -based on chlorine response procedure and regulatory relief for continuous monitoring chlorine analyzers in distribution system filing AWQI is not required -added dechlorination pucks to drain chamber -opened flushing valve to 40% | Holland Landing West Elevated Tank | 2025-10-11
WEST | October | Initiated Interim Procedure - HLETYS Water Quality Flushing based on Pre-Inj Combined Cl low alarm. Also changed Reverse Flow Alarms: HiHi - from 95 to 80L/s and ENABLED Hi - from 80 to 15L/s -Purpose is to have an actionable alarm during interim flushing if the tower is draining to system. Changed Pre-Injection Combined Cl alarm SP from 0.65 to 0.80mg/L to mitigate lower residuals in EG system. | Holland Landing West Elevated Tank | 2025-10-09
WEST | October | -increased target residual from 3.15 to 3.40 mg/L -both hypo pumps under dosing, decreased hypo pump # 1 max flow setpoint from 170 to 140 ml/min to achieve target dose -increased post injection combined chlorine high alarm from 3.40 to 3.60 mg/L | Holland Landing West Elevated Tank | 2025-10-11
WEST | October | Onsite for station check Duty active Checked residuals mg/l @1140 Total grab 1.74 Free grab 0.04 | Jefferson Pumping Station & Reservoir | 2025-10-24
WEST | October | Onsite for station check Checked residuals mg/l @1123 Total grab 1.98 Free grab 0.00 | Jefferson Pumping Station & Reservoir | 2025-10-17
WEST | October | On site to complete station check. Free Chlorine Grab: 0.05mg/L Total Chlorine Grab: 1.70mg/L No issues on site | Jefferson Pumping Station & Reservoir | 2025-10-21
WEST | October | Pumping Station Check (no issues found) Input data to PWQ 14:00 CL2 grab residuals (mg/L) Free: 0.05 Total: 1.77 | Jefferson Pumping Station & Reservoir | 2025-10-31
WEST | October | Onsite for station check Duty active Checked residuals mg/l @1158 Total grab 1.81 Free grab 0.04 | Jefferson Pumping Station & Reservoir | 2025-10-27
WEST | October | On site for scheduled PM workorders. informed ROC about the works being done. Completed following work orders. W11292540 JFPS, Sump Pit System Inspection, Jefferson WPS. W11293152 JFPS, Actuated Valves Exercise & Inspection. W11293552 JFPS, Pump & Motor Inspection W11294012 JFPS, Ventilation System Inspection W11294022 JFPS, Low Temperature Alarm Test W11294249 JFPS, Check Valve Service & Inspection W11294378 JFPS, Dehumidifier Inspection & Cleaning W11293460 JFRS, JHSC Health and Safety Inspection W11292526 JFPS, Standby Power Generator Test Run and Run Hours log. Pre check Battery okay- 26.5 V Coolant- Okay Oil - Okay Before Start Start time- 10:07 Run time- 646.4 hr Fuel level-6746L/126.4cm Ran Pump 3&4 in manual After Stop Stop time- 11:14 Run time- 647.6 hr Fuel level-6677L/125.2cm | Jefferson Pumping Station & Reservoir | 2025-10-16
WEST | October | On site for station check and to collect bacti sample wo#11330673 and quarterly sample w11247208 Residuals East Cell cell:@ 0855 Free: 0.05mg/L Total 1.63mg/L SL1000 readings Total Cl: 1.66mg/L Total NH3: 0.41mg/L Free NH3: 0.09mg/L NH2Cl: 1.58mg/L NO2: 0.000mg/L No issues on site | Jefferson Pumping Station & Reservoir | 2025-10-29
WEST | October | Onsite for station check and to collect weekly micro sample W11316454 WEst cell @1228 Total grab 1.71 Free grab 0.06 Sl1000 mcl 1.65 F nh3 0.08 T nh3 0.40 East Cell @1234 Total grab 1.69 Free grab 0.03 | Jefferson Pumping Station & Reservoir | 2025-10-22
WEST | October | Onsite for station check and to collect weekly micro sample W11298750 East cell @1448 Total grab 1.86 Free grab 0.05 Sl1000 Mcl 1.61 No2 0.001 F nh3 0.09 T nh3 0.41 West cell @1452 Total grab 1.75 Free grab 0.05 Pumping station grab @1500 Total grab 1.79 Free grab 0.01 | Jefferson Pumping Station & Reservoir | 2025-10-14
WEST | October | Onsite for station check Duty active Checked residuals mg/l @1241 Total grab 1.80 Free grab 0.05 | Jefferson Pumping Station & Reservoir | 2025-10-06
WEST | October | On site for station check and to collect bacti sample wo#11256486 Residuals East Cell cell:@ 09:30 Free: 0.05mg/L Total 1.76mg/L SL1000 readings Free Cl: 0mg/L Total Cl: 1.78mg/L Total NH3: 0.40mg/L Free NH3: 0.08mg/L NH2Cl: 1.60mg/L NO2: 0.000mg/L No issues on site | Jefferson Pumping Station & Reservoir | 2025-10-01
WEST | October | On site to complete station check. Free Chlorine Grab: 0.04mg/L Total Chlorine Grab: 1.41mg/L | Jefferson Pumping Station & Reservoir | 2025-10-03
WEST | October | On site for the following JFRS, External Venting Screens Inspection, Jefferson RES (1M) JFPS, Check Valve Service & Inspection, Jefferson WPS (3M) JFRS, Eye Wash Cleaning & Solution Replacement, Jefferson RES (6M) JFRS, Flood Alarm Test Jefferson Valve House (1M) JFRS, Dehumidifier Inspection & Cleaning, Jefferson, Valve House (1M) JFRS, Sump Pit System Inspection, Jefferson Valve House (1M) JFRS, Sump Pit System Inspection, Jefferson RES (1M) JFRS, Ventilation System Inspection, Jefferson Valve House (1M) | Jefferson Pumping Station & Reservoir | 2025-10-07
WEST | October | Onsite for station check Duty active Checked residuals mg/l @1128 Total grab 1.79 Free grab 0.03 | Jefferson Pumping Station & Reservoir | 2025-10-10
WEST | October | Vibration testing Grease motor bearings 20 shots each | Jefferson Pumping Station & Reservoir | 2025-10-02
WEST | October | Onsite for station check Duty not active Checked residuals mg/L @1417 Total grab 1.95 Free grab 0.01 no issues observed | King City Dufferin Booster Pumping Station | 2025-10-16
WEST | October | -on site to complete station check -system duty active, pump 1 running -checked equipment -reviewed trends -recorded readings in PWQ sheet -pump #1 hours = 6750.1 -pump #2 hours = 6394.7 -checked residuals: 09:54 - Grabs: Free Chlorine = 0.02 mg/L Total Chlorine = 2.06 mg/L -no issues found | King City Dufferin Booster Pumping Station | 2025-10-31
WEST | October | Onsite for station check Duty active Checked residuals mg/l @1054 Total grab 1.92 Free grab 0.05 | King City Dufferin Booster Pumping Station | 2025-10-24
WEST | October | Test backflow preventer Passed | King City Dufferin Booster Pumping Station | 2025-10-23
WEST | October | Station Check (no issues found) Input data to PWQ 12:30 Cl2Grab Residual (mg/L) Free: 0.10 Total: 2.01 | King City Dufferin Booster Pumping Station | 2025-10-21
WEST | October | -on site to complete station check -activated duty for station check, pump 1 running -checked equipment -reviewed trends -recorded readings in PWQ sheet -pump #1 hours = 6742.0 -pump #2 hours = 6389.0 -checked residuals: 09:30 - Grabs: Free Chlorine = 0.04 mg/L Total Chlorine = 1.91 mg/L -no issues found | King City Dufferin Booster Pumping Station | 2025-10-27
WEST | October | On site for station check Grabs Free 0.05mg/L Total 1.76mg/L No other issues on site | King City Dufferin Booster Pumping Station | 2025-10-10
WEST | October | On site for station check Grabs Free 0.05mg/L Total 1.87mg/L No other issues on site | King City Dufferin Booster Pumping Station | 2025-10-03
WEST | October | On site for the following KCPSDS, VFD Air Filter Change, King City WPS (3M) KCPSDS, Pump & Motor Inspection, King City WPS (3M) KCPSDS, Critical Air Valve Flush and Inspection, King City WPS (1M) KCPSDS, Hoist System Inspection, King City WPS (3M) All ok | King City Dufferin Booster Pumping Station | 2025-10-09
WEST | October | On site to complete station check. Free chlorine @ 9:10 Grab: 0.05 mg/L Total chlorine @ 9:10 Grab: 1.92 mg/L -No pumps running -Data entered into PD sheet -Checked trends | King City Dufferin Booster Pumping Station | 2025-10-14
WEST | October | On site for station check Grabs Free 0.05mg/L Total 1.71mg/L No other issues on site | King City Dufferin Booster Pumping Station | 2025-10-06
WEST | October | Test backflow preventer Passed | King City Dufferin Elevated Tank | 2025-10-23
WEST | October | -On-site to complete station check and collect samples -system duty not active -checked equipment -reviewed trends -CL17 reagents ok -verified chlorine analyzers: 15:05 - Analyzer readings: Free Chlorine = 0.05 mg/L Total Chlorine = 1.94 mg/L 15:05 - Grabs: Free Chlorine = 0.03 mg/L Total Chlorine = 1.87 mg/L MCL = 1.81 mg/L TNH3 = 0.45 mg/L FNH3 = 0.10 mg/L NO2 = 0.001 mg/L temp = 12.3 C 15:09 - collected weekly regulatory micro. sample - W/O # W11330551 -collected quarter #4 samples - W/O # W11247712 -recorded readings in PWQ sheet -no issues found | King City Dufferin Elevated Tank | 2025-10-29
WEST | October | CL17 new reagents for both (full prime for free analyzer) housekeeping 13:23 Verified CL17 (mg/l) Free: Grab 0.09, A 0.10 Total: Grab 1.96, A 2.02 | King City Dufferin Elevated Tank | 2025-10-21
WEST | October | Under the direction of Cole Warnica, Worked along side Network Analyst Kevin Wen and Aaron Magsakay, replaced a Network switch to Cisco IE3300 inside a Network Cabinet. Provided 24 VDC power to new switch from 24VDC power supply. Informed the ROC regarding possible comm fail alarm. There is a trend gap on SCADA between 9:45 AM pm to 10:19 AM due to this work. After the replacement, checked all the ports and reset the comm alarms. Site came back to normal after the installation | King City Dufferin Elevated Tank | 2025-10-07
WEST | October | On site to complete station check and weekly bacti sampling W11298628 -Verified analyzer: Free chlorine @ 8:45 Grab: 0.06 mg/L Analyzer: 0.07 mg/L Total chlorine @ 8:47 Grab: 1.99 mg/L Analyzer: 1.86 mg/L Adjusted analyzer based on average of 3 grabs. Analyzer read 1.99 mg/L afterwards. -Checked trends | King City Dufferin Elevated Tank | 2025-10-14
WEST | October | Onsite for station check and to collect weekly micro sample W11278687 Tower draining Checked residuals mg/l @1433 Total analyzer 1.72 grab 1.82 Free analyzer 0.07 grab 0.03 Sl1000 Mcl 1.75 F nh3 0.06 T nh3 0.40 No2 0.001 | King City Dufferin Elevated Tank | 2025-10-08
WEST | October | Onsite for the following KCETDS, JHSC Health and Safety Inspection, King City Dufferin St E1 KCETDS, Manual Valve, Exercise, King City Dufferin St ET (2M) KCETDS, CL17 Chlorine Analyzer, Maintenance, King City Dufferin St ET (1M) KCETDS, Inlet/Outlet Heat Trace System, Inspection, King City Dufferin St ET (1M) KCETDS, Actuated Valve, Exercise & Inspection, King City Dufferin St ET (1M) KCETDS, Dehumidifier, Cleaning & Inspection, King City Dufferin St ET (1M) KCETDS, Ventilation System, Inspection, King City Dufferin St ET (1M) KCETDS, Low Temperature Alarm Test, King City Dufferin ST ET (1M) No issues on site | King City Dufferin Elevated Tank | 2025-10-09
WEST | October | On site for station check and to collect bacti sample wo# w11256364 Residuals@ 1030 colorimeter Analyzer Total 1.85mg/L Total Grab: 1.82mg/L Analyzer Free 0.08mg/L Free Grab: 0.06mg/L Operational Sampling (SL1000) Total Cl: 1.88mg/L Total NH3: 0.47mg/L Free NH3: 0.11mg/L NH2CL: 1.83mg/L NO2: 0.001mg/L Reagents ok No issues on site | King City Dufferin Elevated Tank | 2025-10-01
WEST | October | On site to collect ndma sample w11365080 Analyzer reading free 0.05mg/L Total 1.95mg/L Grabs free 0.05mg/L total 1.98mg/L | King City Fisher Elevated Tank | 2025-10-28
WEST | October | -On-site to complete station check and collect samples -system duty not active -checked equipment -reviewed trends -depolox reagents ok -verified chlorine analyzers: 14:00 - Analyzer readings: Free Chlorine = 0.05 mg/L Total Chlorine = 2.04 mg/L 14:00 - Grabs: Free Chlorine = 0.03 mg/L Total Chlorine = 1.70/1.74/1.72 mg/L 14:10 - adjusted total chlorine analyzer to 1.72 mg/L based on average of 3 grabs SL1000 Readings: MCL = 1.62 mg/L TNH3 = 0.45 mg/L FNH3 = 0.13 mg/L NO2 = 0.000 mg/L temp = 12.5 C 14:11 - collected weekly regulatory micro. sample - W/O # W11330551 -collected quarter #4 samples - W/O # W11247040 -recorded readings in PWQ sheet -no issues found | King City Fisher Elevated Tank | 2025-10-29
WEST | October | -on site to complete work orders -completed PRV Valve, Inspection -completed JHSC?Health?and?Safety?Inspection -completed Inlet/Outlet Heat Trace System, Inspection -completed Siemens Depolox 5/Micro 2000, Chlorine Analyzer, Maintenance -completed Low Temperature Alarm, Test -completed Portable Gasoline Generator, Test -completed Sensing Line Heat Trace Sytem, Inspection -completed High & Low Water Level Alarm, Test -completed altitude valve inspection -filled depolox reagents -site back to normal operation | King City Fisher Elevated Tank | 2025-10-16
WEST | October | -On-site to complete station check and collect samples -system duty not active, tower = 73 % -checked equipment -reviewed trends -depolox reagents ok -verified chlorine analyzers: 08:53 - Analyzer readings: Free Chlorine = 0.06 mg/L Total Chlorine = 1.98 mg/L 08:53 - Grabs: Free Chlorine = 0.03 mg/L Total Chlorine = 1.97 mg/L SL1000 Readings: MCL = 1.90 mg/L TNH3 = 0.47 mg/L FNH3 = 0.09 mg/L NO2 = 0.000 mg/L temp = 16.3 C 08:57 - collected weekly regulatory micro. sample - W/O # W11316440 -collected operational ATP sample -recorded readings in PWQ sheet -no issues found | King City Fisher Elevated Tank | 2025-10-22
WEST | October | On site to complete station check and weekly bacti sampling W11298628. -Verified analyzer: Free chlorine @ 9:32 Grab: 0.03 mg/L Analyzer: 0.06 mg/L Total chlorine @ 9:32 Grab: 1.87 mg/L Analyzer: 1.83 mg/L -Checked trends | King City Fisher Elevated Tank | 2025-10-14
WEST | October | On site for station check and to collect bacti sample wo# w11256364 Residuals@ 11:10colorimeter Total Grab: 1.68mg/L Analyzer Total 1.71mg/L Free Grab: 0.05mg/L Analyzer Free 0.07mg/L Operational Sampling (SL1000) Total Cl: 1.68mg/L Total NH3: 0.46mg/L Free NH3: 0.11mg/L NH2CL: 1.78mg/L NO2: 0.000mg/L Reagents all okay No issues on site | King City Fisher Elevated Tank | 2025-10-01
WEST | October | Onsite for station check and to collect weekly micro sample and Q4 ndma W1278687 W11247954 Tower draining @1408 Total analyzer 1.66 grab 1.83 Free analyzer 0.06 grab 0.06 Adjusted total analyzer based on average of multiple grabs Sl1000 Mcl 1.70 F nh3 0.09 No2 0.001 | King City Fisher Elevated Tank | 2025-10-08
WEST | October | -On-site to complete station check and collect samples -deactivated system duty -checked equipment -reviewed trends 10:04 - collected grab sample: Free Chlorine = 0.03 mg/L Total Chlorine = 2.08 mg/L MCL = 2.01 mg/L TNH3 = 0.49 mg/L FNH3 = 0.10 mg/L NO2 = 0.000 mg/L temp = 11.6 C 10:07 - collected weekly regulatory micro. sample - W/O # W11330687 -collected quarter #4 samples - W/O # W11247096 -recorded readings in PWQ sheet -no issues found | Kleinburg Elevated Tank | 2025-10-29
WEST | October | -On-site to complete station check and collect samples -deactivated system duty, tower = 80 % -checked equipment -reviewed trends 12:56 - collected grab sample: Free Chlorine = 0.07 mg/L Total Chlorine = 2.08 mg/L MCL = 2.04 mg/L TNH3 = 0.50 mg/L FNH3 = 0.10 mg/L NO2 = 0.000 mg/L temp = 16.9 C 13:01 - collected weekly regulatory micro. sample - W/O # W11316705 -collected operational ATP sample -recorded readings in PWQ sheet -no issues found | Kleinburg Elevated Tank | 2025-10-22
WEST | October | -on site to collect quarter 4 NDMA resample W11365116 08:46 - collected grab: FCL = 0.02 mg/L TCL = 2.02 mg/L 08:50 - collected sample -no issues | Kleinburg Elevated Tank | 2025-10-28
WEST | October | -On-site to complete station check and collect sample -deactivated system duty -checked equipment -reviewed trends 12:39 - collected grab sample: Free Chlorine = 0.03 mg/L Total Chlorine = 2.01 mg/L MCL = 2.03 mg/L TNH3 = 0.54 mg/L FNH3 = 0.14 mg/L temp = 18.8 C 12:44 - collected weekly regulatory micro. sample - W/O # W11256500 -collected operational ATP sample -recorded readings in PWQ sheet -no issues found | Kleinburg Elevated Tank | 2025-10-01
WEST | October | -on site to complete work orders -informed ROC of work -completed Low Temperature Alarm, Test -completed Gasoline Generator, Test Run -completed JHSC Health and Safety Inspection -completed Dehumidifier, Cleaning & Inspection -completed Inlet/Outlet Heat Trace System, Inspection -completed Facility Outfall Inspection and Cleaning -no issues | Kleinburg Elevated Tank | 2025-10-09
WEST | October | On site to complete station check and collect weekly bacti sample W11298764. -Took grab samples: Free chlorine @ 14:11 Grab: 0.07 mg/L Total chlorine @ 14:11 Grab: 2.02 mg/L -Checked trends -Entered data into PD sheet | Kleinburg Elevated Tank | 2025-10-14
WEST | October | Onsite for station check and to collect weekly micro sample and Q4 ndma W11247968 W11278901 Checked residuals mg/l @1304 Total grab 2.09 Free grab 0.03 Sl1000 Mcl 1.96 F nh3 0.07 T nh3 0.46 No2 0.001 | Kleinburg Elevated Tank | 2025-10-08
WEST | October | -on site to complete station check -system duty active, pumps 2 and 3 running -checked equipment -reviewed trends -recorded readings in PWQ sheet -analyzer reagents ok -verified chlorine analyzers: 13:59 - Analyzer readings: Free Chlorine = 0.04 mg/L Total Chlorine = 2.07 mg/L 13:59 - Grabs: Free Chlorine = 0.00 mg/L Total Chlorine = 2.12 mg/L -no issues found | Kleinburg HWY 27 Booster Pumping Station | 2025-10-31
WEST | October | Onsite to complete station check Duty active Checked residuals mg/l @0957 Total analyzer 2.17 grab 2.10 Free analyzer 0.04 grab 0.03 | Kleinburg HWY 27 Booster Pumping Station | 2025-10-16
WEST | October | -on site to complete station check -system duty not active -checked equipment -reviewed trends -recorded readings in PWQ sheet -filled analyzer reagents -pump #1 hours = 16757.1 -pump #2 hours = 16840.3 -pump #3 hours = 17544.4 -verified chlorine analyzers: 13:28 - Analyzer readings: Free Chlorine = 0.04 mg/L Total Chlorine = 2.10 mg/L 13:28 - Grabs: Free Chlorine = 0.05 mg/L Total Chlorine = 2.13 mg/L -no issues found | Kleinburg HWY 27 Booster Pumping Station | 2025-10-24
WEST | October | Onsite to complete station check Duty not active Checked residuals mg/l @1429 Total analyzer 2.09 grab 2.10 Free analyzer 0.04 grab 0.03 | Kleinburg HWY 27 Booster Pumping Station | 2025-10-20
WEST | October | Check pump 4 gearbox Signed out whisper lane PS | Kleinburg HWY 27 Booster Pumping Station | 2025-10-21
WEST | October | -on site to complete station check -system duty active, pumps 2 and 3 running -checked equipment -recorded readings in PWQ sheet -analyzer reagents ok -verified chlorine analyzers: 09:52 - Analyzer readings: Free Chlorine = 0.04 mg/L Total Chlorine = 2.23 mg/L 09:52 - Grabs: Free Chlorine = 0.05 mg/L Total Chlorine = 2.15 mg/L -no issues found | Kleinburg HWY 27 Booster Pumping Station | 2025-10-03
WEST | October | On site to complete station check. -No pumps running -Verified analyzers: Free Chlorine @ 14:27 Grab: 0.09 mg/L Analyzer: 0.04 mg/L Total Chlorine @ 14:27 Grab: 2.12 mg/L Analyzer: 2.09 mg/L -Entered data into PD sheet | Kleinburg HWY 27 Booster Pumping Station | 2025-10-14
WEST | October | -on site to complete work orders -informed ROC of work -completed Sump Pit System, Inspection -completed Flood Alarm, Test -completed Low Temperature Alarm, Test -completed Storm Sump Pump, Maintenance -completed JHSC Health and Safety Inspection -completed Pressure Relief Valve, Inspection -completed Bypass Valve Actuator, Exercise & Inspection -completed Altitude Valve, Inspection -completed Bypass Manual Valve, Exercise -completed Chlorine Analyzer, Maintenance -verified analyzers after maintenance: 13:48 - Analyzer readings: Free Chlorine = 0.03 mg/L Total Chlorine = 2.15 mg/L 13:48 - Grabs: Free Chlorine = 0.04 mg/L Total Chlorine = 2.02/2.02/1.99 mg/L 13:57 - adjusted total chlorine analyzer to 2.01 mg/L based on average of 3 grabs -completed Pump & Motor, Inspection -no issues, site back to normal operation | Kleinburg HWY 27 Booster Pumping Station | 2025-10-09
WEST | October | Station Check (no issues found) input data to PWQ 10:15 Verified Depolox (mg/L): Free: Grab 0.04, A 0.04 Total: Grab 2.16, A 2.21 (topped up acetate and KI/distilled reagents) | Kleinburg HWY 27 Booster Pumping Station | 2025-10-06
WEST | October | On-site for station check Checked residuals Total Analyzer 2.10mg/L Grab 2.12mg/L Free Analyzer 0.04mg/L Grab 0.05mg/L Reagents - all ok No known issues | Kleinburg HWY 27 Booster Pumping Station | 2025-10-10
WEST | October | Onsite for station check Duty not active Checked residuals mg/l @1354 Total analyzer 2.40 grab 2.34 Free analyzer 0.03 grab 0.03 Reagents ok | Kleinburg Whisper Lane Booster Pumping Station | 2025-10-20
WEST | October | completed Eye Wash, Solution Replacement | Kleinburg Whisper Lane Booster Pumping Station | 2025-10-23
WEST | October | -on site to complete station check -checked equipment -reviewed trends -analyzer reagents ok -recorded readings in PWQ sheet -verified chlorine analyzers: 12:06 - Analyzer readings: Free Chlorine = 0.04 mg/L Total Chlorine = 1.67 mg/L 12:06 - Grabs: Free Chlorine = 0.03 mg/L Total Chlorine = 1.79/1.77/1.77 mg/L 12:16 - adjusted total chlorine analyzer to 1.78 mg/L based on average of 3 grabs -no other issues found | Kleinburg Whisper Lane Booster Pumping Station | 2025-10-24
WEST | October | Reverted all valving back to open in station. Put pumps back into remote. Took a residual at 5:15 pm. Free - 0.01 mg/l Total - 2.01 mg/l The analyzer was reading Free - 0.01 mg/l Total - 2.22 mg/l Adjusted the readings to reflect grab readings. *made correction to log entry of the analyzer total reading.* | Kleinburg Whisper Lane Booster Pumping Station | 2025-10-22
WEST | October | Check pump 4 gearbox Grease breaking down to a liquid wiped out as much as possible and put two new tubes of grease back in | Kleinburg Whisper Lane Booster Pumping Station | 2025-10-21
WEST | October | On site to isolate KLPSWL and KLW34 discharge WM for contractors to cut in new isolation valve outside of facility compound. Isolated discharge at T1423 VC2 (east valve). Isolated discharge P1-4 valves and PRV discharge isolation in station. Confirmed isolation through discharge PIT. Notified ROC of isolation work, alarms, and treated analyzers likely impacted due to no pressure on discharge line during isolation. p1-4 placed local off. KLW34, KLPSWL treated analyzers may also spike on total/combined when returned to service, due to analyzer reagents dosing without sample water. Residuals: mg/L 0854 KLPSWL Grab FCl 0.04 tcl 1.89 | Kleinburg Whisper Lane Booster Pumping Station | 2025-10-22
WEST | October | -on site to complete station check -checked equipment -reviewed trends -analyzer reagents ok -recorded readings in PWQ sheet -verified chlorine analyzers: 12:06 - Analyzer readings: Free Chlorine = 0.03 mg/L Total Chlorine = 1.79 mg/L 12:06 - Grabs: Free Chlorine = 0.04 mg/L Total Chlorine = 1.83 mg/L -no issues found | Kleinburg Whisper Lane Booster Pumping Station | 2025-10-27
WEST | October | -on site to complete station check -checked equipment -reviewed trends -analyzer reagents ok -recorded readings in PWQ sheet -verified chlorine analyzers: 10:22 - Analyzer readings: Free Chlorine = 0.00 mg/L Total Chlorine = 2.09 mg/L 10:22 - Grabs: Free Chlorine = 0.03 mg/L Total Chlorine = 2.05 mg/L -no issues found | Kleinburg Whisper Lane Booster Pumping Station | 2025-10-03
WEST | October | Station Check (no issues found) input data to PWQ 11:16 Verified Deplolx (mg/L): Free: Grab 0.04, A 0.00 (adjusted to match grabs) Total: Grab 1.96, A 2.02 (topped up acetate) | Kleinburg Whisper Lane Booster Pumping Station | 2025-10-06
WEST | October | -on site to complete work orders -informed ROC of work -completed High/Low Temperature Alarm Test -completed Flood Alarm, Test -completed Hoist System Inspection -completed Manual Valve, Exercise -created follow up work order for pump #4 suction valve gearbox oil leak -completed Pump and Motor, Inspection -completed Siemens Depolox 5/Micro 2000, Chlorine Analyzer, Maintenance: -verified analyzers after maintenance: 13:50 - Analyzer readings: Free Chlorine = 0.00 mg/L Total Chlorine = 2.23 mg/L 13:50 - Grabs: Free Chlorine = 0.03 mg/L Total Chlorine = 2.16 mg/L -no issues, site back to normal operation | Kleinburg Whisper Lane Booster Pumping Station | 2025-10-02
WEST | October | On-site for station check Checked residuals Total Analyzer 2.04mg/L Grab 2.08mg/L Free Analyzer -0.00mg/L Grab 0.04mg/L Zero cal free and adjusted to 0.04mg/L Reagents all okay Site running in schedule mode No issues | Kleinburg Whisper Lane Booster Pumping Station | 2025-10-10
LINEAR | October | Informed ROC. Onsite to perform annual calibrations and troubleshoot well 9 level OOR alarm. Restarted well 9 LIT and readings came back to normal. No issues. Put the devices in calibration mode. Devices were done as below. (PIT, FIT, well LITs). Put everything back in service. All the related alarms were cleared. No issues. Informed ROC, armed the building and left the site. | Major MacKenzie and Newkirk Road Dewatering Wells | 2025-10-21
LINEAR | October | Totalizer: 4,777,17 m3 Discharge pressure: 30.43 Kpa Flow Rate: 11.5 l/s Monitoring well: OOR Well 8 RPM: 2448 AMP: 5.5 %: 42 Level:208.1 masl Well 13 RPM: 2113 AMP: 4.9 %: 21 Level: 205.8 masl | Major MacKenzie and Newkirk Road Dewatering Wells | 2025-10-27
LINEAR | October | Details: Totalizer: 476640 m3 Discharge pressure: 32.32 Kpa Flow Rate: 11.6 l/s Monitoring well: OOR (Work order submitted to Instrumentation) Well 8 RPM: 2449 AMP: 5.5 %: 42 Level:208.1 masl Well 13 RPM: 2111 AMP: 4.9 %: 21 Level: 205.9 masl Monitoring well#9 out of range Everything else under normal operations | Major MacKenzie and Newkirk Road Dewatering Wells | 2025-10-16
LINEAR | October | Totalizer: 477232 m3 Discharge Pressure: 31.14 kPa Flow Rate: 11.5 L/s Monitoring Well Level: *Out Of Range* Well 8: RPM: 2449 Amp: 5.5 %: 42 Level: 208.2 masl Well 13: RPM: 2112 Amp: 4.9 %: 21 Level: 205.9 masl Station under normal operations - Monitoring Well is still out of range*** | Major MacKenzie and Newkirk Road Dewatering Wells | 2025-10-22
LINEAR | October | Totalizer: 475632 m3 Discharge pressure: 32.82 Kpa Flow Rate: 11.6 l/s Monitoring well: OOR (Work order submitted to Instrumentation) Well 8 RPM: 2449 AMP: 5.5 %: 42 Level:208.2 masl Well 13 RPM: 2110 AMP: 4.9 %: 21 Level: 205.9 masl Station OK (Monitoring Well OOR). Station check performed remotely. | Major MacKenzie and Newkirk Road Dewatering Wells | 2025-10-06
WEST | October | Onsite for station check and to collect weekly micro sample W11316454 West cell @1335 Total grab 2.03 Free grab 0.05 Sl1000 Mcl 1.76 F nh3 0.11 T nh3 0.45 No2 0.000 East cell @1338 Total grab 1.93 Free grab 0.05 | Maple North Reservoir | 2025-10-22
WEST | October | On site for station check and to collect bacti sample wo# w11330673 and quarterly w11247124 Residuals @ 13:15 colorimeter *East Cell* Total Grab: 1.98mg/L Free Grab: 0.05mg/L Operational Sampling (SL1000) Total Cl: 2.01mg/L Total NH3: 0.47mg/L Free NH3: 0.12mg/L NH2CL: 1.79mg/L No issues on site | Maple North Reservoir | 2025-10-29
WEST | October | On site for station check and to collect bacti sample wo# w11256486 Residuals @ 11:55 colorimeter *East Cell* Total Grab: 1.57mg/L Free Grab: 0.05mg/L Operational Sampling (SL1000) Total Cl: 1.56mg/L Total NH3: 0.41mg/L Free NH3: 0.09mg/L NH2CL: 1.61mg/L NO2: 0.000mg/L No issues on site | Maple North Reservoir | 2025-10-01
WEST | October | Onsite for station check and to collect weekly micro sample W11298750 East cell @1124 Total grab 1.81 Free grab 0.04 Sl1000 Mcl 1.67 F nh3 0.11 T nh3 0.44 No2 0.000 West cell @1127 Total grab 1.71 Free grab 0.04 | Maple North Reservoir | 2025-10-14
WEST | October | On site for station check and to collect bacti sample wo# w11278701 Residuals @ 13:25 colorimeter *West Cell* Total Grab: 1.48mg/L Free Grab: 0.05mg/L Operational Sampling (SL1000) Total Cl: 1.48mg/L Total NH3: 0.4mg/L Free NH3: 0.12mg/L NH2CL: 1.44mg/L NO2: 0.000mg/L No issues on site | Maple North Reservoir | 2025-10-08
WEST | October | On site for the following VNRSKS, JHSC Health and Safety Inspection, North Maple RES (1M) VNRSKS, Sump Pump, Inside Inspection & Maintenance, North Maple RES (1M) VNRSKS, Air Release Valve, Flush, North Maple RES (1M) VNRSKS, 5 Tonne Hoist System, Inspection, North Maple RES (3M) VNRSKS, External Venting Screens, Inspection, Maple North RES (3M) | Maple North Reservoir | 2025-10-15
WEST | October | onsire for station check Checked residuals mg/L pd7 @1339 Total analyzer 1.90 grab 1.84 Free analyzer 0.05 grab 0.07 pd8 @1346 Total analyzer 2.20 grab 2.20 Free analyzer 0.02 grab 0.06 | Maple Pumping Station | 2025-10-16
WEST | October | On site responding to hihi PD7 pit alarm. CMU5 W11380798 HiHi PD7 Pit Alarm. Arrived on site to find pit is quite full still well below the top of the chamber. Looks like sump pump is no longer working. Will inform team tomorrow about what was found. | Maple Pumping Station | 2025-10-20
WEST | October | -on site to complete station check -PD7 pump 1 and PD8 pump 4 OOS -checked equipment -reviewed trends -recorded readings in PWQ sheet Verified analyzers: 10:59 - PD7 Analyzer readings: Free Chlorine = 0.06 mg/L Total Chlorine = 2.20 mg/L 10:59 - PD7 Grabs: Free Chlorine = 0.04 mg/L Total Chlorine = 2.17 mg/L 11:03 - PD8 Analyzer readings: Free Chlorine = 0.02 mg/L Total Chlorine = 2.17 mg/L 11:03 - PD8 Grabs: Free Chlorine = 0.03 mg/L Total Chlorine = 2.16 mg/L -no issues found | Maple Pumping Station | 2025-10-31
WEST | October | Onsite for station check Checked residuals mg/L Pd7 @1051 Total analyzer 2.22 grab 2.13 Free analyzer 0.06 grab 0.02 Pd8 @1058 Total analyzer 2.17 grab 2.09 Free analyzer 0.02 grab 0.05 | Maple Pumping Station | 2025-10-27
WEST | October | -on site to complete station check -checked equipment -reviewed trends -recorded readings in PWQ sheet -PD7 pump 4 OOS, PD8 pump 1 OOS Verified analyzers: 10:43 - PD7 Analyzer readings: Free Chlorine = 0.05 mg/L Total Chlorine = 2.05 mg/L 10:43 - PD7 Grabs: Free Chlorine = 0.03 mg/L Total Chlorine = 1.91/1.86/1.88 mg/L 10:53 - adjusted PD7 total chlorine analyzer to 1.88 mg/L based on average of 3 grabs 10:54 - PD8 Analyzer readings: Free Chlorine = 0.02 mg/L Total Chlorine = 1.91 mg/L 10:54 - PD8 Grabs: Free Chlorine = 0.05 mg/L Total Chlorine = 1.93 mg/L -tested diesel fuel transfer pumps -no other issues found | Maple Pumping Station | 2025-10-24
WEST | October | On site to respond to PD8 P4 multilin trips. Reviewed multilin alarm history. Found possible loose connection in junction box for pump drive end bearing RTD temperature sensor. Repaired possible loose connection and tested pump. Test was fine, put pump back in service. | Maple Pumping Station | 2025-10-31
WEST | October | Vibration testing Completed 6 pumps | Maple Pumping Station | 2025-10-22
WEST | October | On site to test generator system for proper parallelling operation. | Maple Pumping Station | 2025-10-09
WEST | October | On site for the following work orders MAPS_MAEP_GEN_GEN1, Diesel Generator 1 Test Run, Maple WPS (1M) MAPS_MAEP_GEN_GEN2, Diesel Generator 2 Test Run, Maple WPS (1M) Fuel start 555L/814L Bulk 31561L Fuel stop 442L/686L Bulk 31556L Hours start gen 1 466.8hrs gen 2 479.7hrs Stop gen 1 468.1hrs gen 480.9 hrs VFD Air Filter Change - all ok AC unit back up test - all ok MAPS screen inspection - all ok MAPS sump inspection Gen flood alarm - can remove grate in formed TL Siemens Depolox maintenance - all ok Fuel transfer pump - all ok JHSC inspection - all ok Maps discharge/Suction valves Maps ARV Check valve grease - all ok No issues on site. | Maple Pumping Station | 2025-10-02
WEST | October | Onsite for station check Pd7 Duty active @1356 Total analyzer 1.85 grab 1.79 Free analyzer 0.04 grab 0.06 Pd8 Duty not active @1400 Total analyzer 2.05 grab 2.06 Free analyzer 0.02 grab 0.03 | Maple Pumping Station | 2025-10-03
WEST | October | Vibration testing PD 7 3 and 4 PD8 1 and 2 | Maple Pumping Station | 2025-10-02
WEST | October | Onsite for station check Checked residuals mg/l Pd7 @1022 Total analyzer 2.11 grab 2.14 Free analyzer 0.05 grab 0.01 Pd8 @1025 Total analyzer 2.12 grab 2.04 Free analyzer 0.02 grab 0.05 | Maple Pumping Station | 2025-10-10
WEST | October | -on site to respond to pd7 suction header valve pit high level alarm -adjusted sump pump and pit started draining -cleared alarms -reset pd8 pump 4 multilin, leaving pump OOS | Maple Pumping Station | 2025-10-10
WEST | October | On site to Complete Station Check. Residuals PD8 Total Grab: 1.86mg/L, Analyzer: 1.82mg/L PD8 Free Grab: 0.04mg/L, Analyzer: 0.02mg/L PD7 Total Grab: 1.75mg/L, Analyzer: 1.73mg/L PD7 Free Grab: 0.05mg/L, Analyzer: 0.04mg/L no issues on site | Maple Pumping Station | 2025-10-06
WEST | October | Onsite for station check Pd7 duty active Pd7 @0955 Total analyzer 1.80 grab 1.79 Free analyzer 0.05 grab 0.04 Pd8 @0958 Total analyzer 1.96 grab 1.97 Free analyzer 0.02 grab 0.03 Pd8 pump4 in man off | Maple Pumping Station | 2025-10-14
WEST | October | -completed Process Sump Pump & Drain Valve, Exercise | Maple Pumping Station | 2025-10-15
WEST | October | Under the supervision of Cole Warnica, Worked along side network analyst Kevin Wen and Aaron on site to replace York- peel firewall in the MARS building ROC contacted the Peel region to put Peel Pumps in Manual. York to peel Comm fail alarm was expected on SCADA After replacement, comm alarm was reset and peel pumps put back in Auto. | Maple South Reservoir | 2025-10-30
WEST | October | Onsite for station check and to collect weekly micro sample W1136454 Checked residuals mg/l North cell @1432 Total grab 2.11 Free grab 0.06 Sl1000 Mcl 1.81 F nh3 0.11 T nh3 0.46 No2 0.001 Peel @1426 Total analyzer 1.85 grab 1.85 Free grab 0.05 Metro feed @1427 Total analyzer 1.79 grab 1.83 Free analyzer 0.02 grab 0.06 | Maple South Reservoir | 2025-10-22
WEST | October | Onsite to assist contractor with draining south cell With direction from C.Warnica removed lock and opened reservoir drain valves. Locked out north cell drain cell to keep closed Verified flow in chamber in property Added dechlor to chamber | Maple South Reservoir | 2025-10-17
WEST | October | Onsite to collect Q4 ndma resample W11365081 @0853 Total grab 1.77 Free grab 0.05 Tested wash down pump with contractor | Maple South Reservoir | 2025-10-28
WEST | October | On site for station check and to collect bacti sample wo#w11330673 and quarterly w11247082 Peel Total Grab: 2.10mg/L, Analyzer: 2.14mg/L Metro Total Grab: 2.17mg/L, Analyzer: 2.28mg/L Metro Free Grab: 0.05mg/L, Analyzer: 0.02mg/L Residuals north cell:@ 13:50 Free: 0.06mg/L Total 1.85mg/L SL1000 readings Total Cl: 2.12mg/L NH2Cl: 1.86mg/L Reagents - changed out peel cl17 reagents No issues on site | Maple South Reservoir | 2025-10-29
WEST | October | On-site to drawdown MARS south cell in preparation for draining and isolation. Worked with ROC. Peel OCWA shutdown pumping at ARPS to accommodate drawdown of south cell. TO reduced pumping. Utilized MAPS PD7, PD8, KC PD to drawdown south cell with YPFM inlet isolated, North Cell temporarily isolated. Run PD7 pumps 2, 3 with discharge valves in local open to bypass PDIT switch alarms to reach <1m in south cell. LOTO south cell YPFM inlet isolation, inlet/outlet Keele 600 WM isolations to south cell. PD7 / PD8 pumps returned to normal operation and alarms cleared. ARPS pumping started approx 1400. Opened south cell drains to sump pumps and inspected sumps running. Added dechlor pucks to storm water sump pump chamber. No other issues. Will begin process of shelving alarms associated with offline cell etc. | Maple South Reservoir | 2025-10-08
WEST | October | Cleaned Peel feed cl17 total analyzer Grabs before Analyzer 2.05 grab 3.04 Grabs after Analyzer 2.08 grab 2.07 | Maple South Reservoir | 2025-10-03
WEST | October | In to complete PMs and test isolation for upcoming draining of South cell. Exercised South and North cell isolation valves (inlet / outlet) in pipe gallery. Exercised drain valves for south reservoirs. Test ran drain sump pumps. Exercised South cell YFPM isolation valve (P03P04 Y21). Valve stuck closed (not recognizing valve position when control panel HMI switched to open position). Exercised Keele 600 WM isolations (chambers in driveway) with Linear. Entered Y21 to exercise and test YPFM isolation valves. All valves returned to normal operation. Analyzer verification 1300 Peel Grab: Total Cl 1.76 Analyzer: Total Cl 1.88 Toronto Grab: FCl 0.03 tcl 1.79 Analyzer: FCl 0.06 tcl 1.75 Span calibrate: peel analyzer Cl17 Total Cl from 1.88 to 1.78mg/L based on grabs. Completed PMs: Air valves, flush Siemens Depolox analyzer maintenance Cl17 maintenance Main line inlet valves exercise Sump pump south reservoir, inspection Isolating valve box cover, inspection external venting screen, inspection Ventilation and dehumidifier, inspection | Maple South Reservoir | 2025-10-02
WEST | October | -on site to respond to valve house free chlorine hihi alarms 02:53 - analyzer readings : FCL = 0.39 mg/L TCL = 1.65 mg/L 02:53 - grabs : FCL = 0.01/0.03/0.03 mg/L TCL = 1.71 mg/L -completed zero calibration on free chlorine analyzer then span calibrated to 0.02 mg/L -no further issues | Maple South Reservoir | 2025-10-09
WEST | October | On site for station check and to collect bacti sample wo#w11278701 Peel Total Grab: 1.68mg/L, Analyzer: 1.73mg/L Metro Total Grab: 1.55mg/L, Analyzer: 1.57mg/L Metro Free Grab: 0.05mg/L, Analyzer: 0.05mg/L Residuals South cell:@ 12:20 Free: 0.05mg/L Total 1.54mg/L SL1000 readings Total Cl: 1.54mg/L Total NH3: 0.40mg/L Free NH3: 0.10mg/L NH2Cl: 1.55mg/L NO2: 0.001mg/L Reagents - all okay No issues on site | Maple South Reservoir | 2025-10-08
CENTRAL | October | Onsite to respond to free CL2 hi alarm- informed by ROC: Took grab to verify analyzer (13:54): Grab: 0.05 Analyzer: 0.24 Adjusted free analyzer from 0.24 to 0.05 based on grabs (0.05, 0.06, 0.05) * Station/equipment- Ok | Newmarket (East) Harry Walker Elevated Tank | 2025-10-22
CENTRAL | October | On site to complete Q4 NDMA resample (W11365092). Contractor (Landmark) on site. | Newmarket (East) Harry Walker Elevated Tank | 2025-10-28
CENTRAL | October | Onsite for station check/collect weekly samples- WO# W11330491: Sample results (08:00): Free- 0.09, Total- 1.92 * Adjusted total analyzer from 1.78 to 1.92 based on multiple grabs (1.92, 1.90, 1.92) * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Newmarket (East) Harry Walker Elevated Tank | 2025-10-29
CENTRAL | October | On-site to assist with altitude valve commissioning. Isolated ET at 09:21 as per altitude valve commissioning plan via ETO (consultant) and changed system controlling ET to QVETQS with QVETQS tie valve man/open. Flow to Cl analyzer cut off at 09:21 when ET isolated. Commissioning plan required flow through altitude valve be drained to overflow, placed dechlorination pucks in outfall. Devine technician attempted to commission valve but determined that repairs are needed to be made to the altitude valve. Returned flow to Cl analyzer and verified at 11:55 as follows (mg/L): Free Cl: G: 0.06 A: 0.04 Total Cl: G: 2.56 A: 2.44 (adjusted to 2.56mg/L based on grab samples) System returned to normal operation at 12:05. Found that one of the analogue pressure gauges needs replacement during attempted commissioning, ETO will get replacement. No other new issues found while on-site. Informed ROC. | Newmarket (East) Harry Walker Elevated Tank | 2025-10-31
CENTRAL | October | On site to complete preventative maintenance work orders. - Tower duty active when arrived - Informed ROC - Did inspection of depolox analyzer - electrolyte gel amount higher than water level- grit sand swirling- membrane total chlorine motor moving good - free chlorine reservoir cell looks clean, Membrane Total chlorine motor has electrolyte gel above water level - motor free of bubbles and depolox reagents looking all ok - verified depolox down below - Performed heat trace test - Completed JHSC - Did general housekeeping of site - Did dehumidifier inspection - No new issues found Treated Total Cl grab @ 11:17am G: 2.74mg/L A: 2.74mg/L Free Cl grab @ 11:18am G: 0.04mg/L A: 0.05mg/L | Newmarket (East) Harry Walker Elevated Tank | 2025-10-23
CENTRAL | October | Onsite for station check/collect samples- WO# W11256304 & W11256566: Sample results (08:42): Free- 0.00, Total- 2.42 * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Newmarket (East) Harry Walker Elevated Tank | 2025-10-01
CENTRAL | October | Onsite for station check/collect samples- WO# W11279425 & W11247842: Sample results (08:32): Free- 0.00, Total- 2.00 * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Newmarket (East) Harry Walker Elevated Tank | 2025-10-08
CENTRAL | October | Onsite for station check/collect samples- WO# W11298568 & W11247558: Sample results (07:38): Free- 0.03, Total- 1.68 * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Newmarket (East) Harry Walker Elevated Tank | 2025-10-15
CENTRAL | October | Onsite for station check/collect weekly sample- WO# W11330491: Sample results (12:15): Free- 0.04, Total- 1.74 * At 10:42- took inlet grabs to verify inlet CL17 analyzers (Filling): Grabs: Free- 0.08, Total- 2.60 Analyzers: Free- 0.07, Total- 2.30 At 10:46- adjusted inlet total CL17 analyzer from 2.28 to 2.60 based on multiple grabs (2.60, 2.58, 2.60) * Replaced inlet free CL17 reagents At 13:05- took grab to verify inlet total analyzer (Draining): Grab: 1.58 Analyzer: 1.78 Adjusted analyzer from 1.78 to 1.58 based on multiple grabs (1.58, 1.58, 1.57) * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Chemscan reagents- Ok Station/equipment- Ok | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2025-10-29
CENTRAL | October | Onsite to complete chemscan outlet/header hot water flush- informed ROC | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2025-10-16
CENTRAL | October | Attending site to check inlet Total chlorine analyzer (W11397868). Could not find anything wrong with analyzer - Operations is noticing that when filling, the grabs are higher than the analyzer. Replaced colorimeter and verified reading. Redempto Balaga and Parth Patel joined me on site to assist. Notified Joe DeMarco. He will check the analyzer later this week during a fill cycle and follow up if needed. ROC notified before and after work was performed. | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2025-10-27
CENTRAL | October | Onsite for station check: Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Chemscan reagents- Ok Station/equipment- Ok | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2025-10-17
CENTRAL | October | Onsite for station check: While verifying analyzers, unable to adjust inlet total analyzer due to high slope value- informed Eric S, will attend station to investigate further. Performed maintenance/cleaning on inlet total analyzer, and replaced inlet total CL17 reagents * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Chemscan reagents- Ok Station/equipment- Ok | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2025-10-27
CENTRAL | October | Onsite for station check/collect sample- WO# W11317124: Sample results (11:25): Free- 0.06, Total- 1.35 * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Chemscan reagents- Ok Station/equipment- Ok | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2025-10-22
CENTRAL | October | Onsite for station check: Replaced header total CL17 reagents * At 10:15- took chemscan header FA grab (filling): Grab- 0.22 Analyzer- 0.31 Adjusted chemscan header FA to 0.22 as per grabs Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Chemscan reagents- Ok Station/equipment- Ok | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2025-10-31
CENTRAL | October | Onsite for station check: Upon arrival, noticed inlet total residual reading lower than normal operations during res fill cycle. Replaced Watson Marlow tubing in both hypo pump #1 and hypo pump #2. Cleaned and flushed both hypo pump #1 and pump #2 injection points. Performed chemical drawdown on both hypo pump #1 and hypo pump #2 to ensure proper dosing. Once maintenance completed on hypo pump #1 and hypo pump #2, the intel total reading started to climb/return to normal operations- will continue to monitor via scada Replaced inlet total CL17 reagents * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Chemscan reagents- Ok Station/equipment- Ok | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2025-10-24
CENTRAL | October | Install 4 inch pressure gauges | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2025-10-07
CENTRAL | October | Onsite to complete assigned work orders- informed ROC: H/S inspection High/Low temp tests Flood alarm test Ventilation inspection Heater inspection CL17 analyzer maintenance Chemscan analyzer maintenance Hypo injection point cleaning Chemical storage tank inspection Altitude valve inspection Cell drain valve inspection Facility outfall inspection Performed station housekeeping Performed on-call scada review check Station/equipment- Ok | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2025-10-09
CENTRAL | October | Onsite for station check: Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Chemscan reagents- Ok Station/equipment- Ok | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2025-10-06
CENTRAL | October | Onsite for station check/collect samples- WO# W11256304 & W11256566: Sample results (12:52): Free- 0.07, Total- 1.61 * Received hypo delivery * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Chemscan reagents- Ok Station/equipment- Ok | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2025-10-01
CENTRAL | October | Onsite for station check/collect samples- WO# W11298568 & W11247516: Sample results (13:42): Free- 0.03, Total- 1.50 * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Chemscan reagents- Ok Station/equipment- Ok | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2025-10-14
CENTRAL | October | Onsite to perform chemscan outlet/header hot water flush- informed ROC * | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2025-10-02
CENTRAL | October | Placed pumps in manual to assist with TSSA training to transfer utility power to gen power and back to utility, everything back to normal/Auto. | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2025-10-06
CENTRAL | October | Diesel training Run fire pumps. Try to increase l/s opened flow valve 100% very little increase. Replace pressure gage's on 1 5 and 6 | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2025-10-06
CENTRAL | October | Onsite for station check/collect sample- WO# W11279425: Sample results (13:52): Free- 0.01, Total- 1.65 * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Chemscan reagents- Ok Station/equipment- Ok | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2025-10-08
CENTRAL | October | Onsite for station check: Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Chemscan reagents- Ok Station/equipment- Ok | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2025-10-10
CENTRAL | October | Onsite to complete assigned work orders: Received hypo delivery Hypo pump inspections Ammonia pump inspections Station/equipment- Ok | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2025-10-15
CENTRAL | October | Onsite for station check: Replaced header free CL17 reagents * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Chemscan reagents- Ok Station/equipment- Ok | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2025-10-03
CENTRAL | October | Station and equipment check ET remains OFFLINE as per normal ops No issues | Newmarket (London) Yonge Street Elevated Tank | 2025-10-27
CENTRAL | October | Station and equipment check ET remains OFFLINE as per normal ops Ops ok | Newmarket (London) Yonge Street Elevated Tank | 2025-10-17
CENTRAL | October | Station and equipment check ET remains offline Check heat trace line all ok ET ops everything normal | Newmarket (London) Yonge Street Elevated Tank | 2025-10-20
CENTRAL | October | General housekeeping and sump pump inspection. | Newmarket (London) Yonge Street Elevated Tank | 2025-10-03
CENTRAL | October | Did comprehensive housekeeping of NMETDD & well 14 house. No issues found | Newmarket (Northeast) Davis Drive Elevated Tank | 2025-10-23
CENTRAL | October | On-site to flush from well 14, Flushed ~206000L | Newmarket (Northeast) Davis Drive Elevated Tank | 2025-10-30
CENTRAL | October | On-site for station check Flushed 91,000L in well 14. Water loss reported in W11400075 JHSC inspection completed Station ok | Newmarket (Northeast) Davis Drive Elevated Tank | 2025-10-28
CENTRAL | October | On-site for a station and equipment check. Site offline, no issues found | Newmarket (Northeast) Davis Drive Elevated Tank | 2025-10-21
CENTRAL | October | Onsite for station check/collect weekly sample- WO# W11330491: Sample results (09:25): Free- 0.05, Total- 2.78 * Adjusted total analyzer from 2.53 to 2.78 based on multiple grabs (2.78, 2.80, 2.78) * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Newmarket (Southeast) Ivsbridge Elevated Tank | 2025-10-29
CENTRAL | October | Onsite for station check/collect sample- WO# W11317124: Sample results (09:18): Free- 0.04, Total- 2.44 * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Newmarket (Southeast) Ivsbridge Elevated Tank | 2025-10-22
CENTRAL | October | On site to complete preventative maintenance work orders informed ROC. - Tower draining @ 58% @13.1L/s - Did general housekeeping - Did JHSC of site - Did heat trace test Completed - Did flood alarm test - Did portable gen test - Did inspection of depolox analyzer - electrolyte gel amount higher than water level- grit sand swirling- membrane total chlorine motor moving good - free chlorine reservoir cell looks clean, Membrane Total chlorine motor has electrolyte gel above water level - motor free of bubbles and depolox reagents looking all ok - verified depolox down below - No other issues found Treated Total Cl grab @ 1:47pm G: 2.36mg/L A: 2.40mg/L Free Cl grab @ 1:47pm G: 0.02mg/L A: 0.01mg/L | Newmarket (Southeast) Ivsbridge Elevated Tank | 2025-10-23
CENTRAL | October | Onsite for station check/collect sample- WO# W11279425: Sample results (10:30): Free- 0.04, Total- 2.70 * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Newmarket (Southeast) Ivsbridge Elevated Tank | 2025-10-08
CENTRAL | October | On site to check/verify depolox analyzer as combined & treated chlorine kept on rising while filling yesterday evening and also while draining today early morning. After coming on site noticed not enough water reaching to analyzer, cannot see water coming out of overflow tubing. When came on site tower was draining and water was being directed to users combined chlorine was 4.86mg/L @7:24am but it is analyzer issue, I verified the analyzer by doing grabs and adjusted the analyzer based of my avg grabs now working on the flow issue. Water safe to drink Treated total @ 7:29am G: 2.62, 2.64, 2.70mg/L A: 4.83mg/L - adjusted analyzer to match avg grabs to 2.65mg/L Opened the PRV to clean it and placed it back Joseph D Marco on site to assist, Waited few minutes for depolox to stabilize the total & free Cl readings before doing grabs. Tower currently filling @ 9:00am Grabs @ 9:20am Treated total G: 2.60, 2.66, 2.70mg/L A: 1.32mg/L - adjusted analyzer to match avg grabs to 2.65mg/L Treated free G: 0.08mg/L A: 0.08mg/L No other issues found | Newmarket (Southeast) Ivsbridge Elevated Tank | 2025-10-07
CENTRAL | October | ROC called @ 9:45pm when NMIBET filling total Cl 3.88mg/L @9:38pm and combined Cl climbing to 3.84mg/L @9:38pm, bringing total Cl hi alarm and combined Cl hihi alarm so asked them to call me if they see combined Cl 3.75mg/L and climbing while tower draining. No other issues | Newmarket (Southeast) Ivsbridge Elevated Tank | 2025-10-06
CENTRAL | October | Onsite to calibrate TWR_LIT. Informed ROC. Put TWR_LIT in calibration mode. Performed calibration. Put the TWR_LIT back in service. All the related alarms were cleared. No issues. Informed ROC, armed the building and left the site. | Newmarket (Southeast) Ivsbridge Elevated Tank | 2025-10-10
CENTRAL | October | Onsite for station check/collect samples- WO# W11256304 & W11256566: Sample results (10:32): Free- 0.01, Total- 2.56 * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Newmarket (Southeast) Ivsbridge Elevated Tank | 2025-10-01
CENTRAL | October | Onsite for station check/collect samples- WO# W11298568 & W11247530: Sample results (08:55): Free- 0.00, Total- 2.50 * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Newmarket (Southeast) Ivsbridge Elevated Tank | 2025-10-15
CENTRAL | October | Onsite for station check/collect sample- WO# W11317124: Sample results (12:50): Free- 0.00, Total- 2.40 * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Newmarket (West) Bathurst Tank | 2025-10-22
CENTRAL | October | Onsite to collect NDMA resample- WO# W11365079: Sample results (09:05): Free- 0.09, Total- 2.34 * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Newmarket (West) Bathurst Tank | 2025-10-28
CENTRAL | October | Onsite for station check/collect weekly sample- WO# W11330491: Sample results (14:12): Free- 0.06, Total- 2.22 * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Newmarket (West) Bathurst Tank | 2025-10-29
CENTRAL | October | Onsite to complete assigned work orders- informed ROC: H/S inspection Dechlorination puck dispenser inspection Depolox analyzer maintenance Sump system inspection Performed station housekeeping Station/equipment- Ok | Newmarket (West) Bathurst Tank | 2025-10-07
CENTRAL | October | On-site due to high high free CL2 Drained, cleaned and added new ?grit? Three grabs from analyzer waste line. Grabs were 1) 0.00 2) 0.01 3) 0.01 Analyzer reading 0.30mg/L Adjusted to 0.01mg/L Will continue to monitor remotely | Newmarket (West) Bathurst Tank | 2025-10-02
CENTRAL | October | Onsite for station check/collect samples- WO# W11279425 & W11247996: Sample results (12:20): Free- 0.04, Total- 2.32 * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Newmarket (West) Bathurst Tank | 2025-10-08
CENTRAL | October | Onsite for station check/collect samples- WO# W11298568 & W11247572: Sample results (12:22): Free- 0.02, Total- 2.30 * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Newmarket (West) Bathurst Tank | 2025-10-14
CENTRAL | October | On-site for station and equipment checked, no issues found Weekly bacti sample and operational sample taken Verified analyzer, entered all readings and grabs in PWQ sheet. | Newmarket (West) Bathurst Tank | 2025-10-01
CENTRAL | October | Onsite for station check: Station/equipment- Ok | Newmarket Kirby Pumping Station | 2025-10-24
CENTRAL | October | Onsite for station check: Station/equipment- Ok | Newmarket Kirby Pumping Station | 2025-10-17
CENTRAL | October | Onsite to complete assigned work orders- informed ROC: Completed traffic protection online course * Pump and motor inspections Discharge actuator inspections Station/equipment- Ok | Newmarket Kirby Pumping Station | 2025-10-21
CENTRAL | October | Onsite for station check: Station/equipment- Ok | Newmarket Kirby Pumping Station | 2025-10-29
CENTRAL | October | Onsite for station check: Station/equipment- Ok | Newmarket Kirby Pumping Station | 2025-10-20
CENTRAL | October | Onsite for station check: Station/equipment- Ok | Newmarket Kirby Pumping Station | 2025-10-31
CENTRAL | October | Onsite to complete assigned work orders- informed ROC: H/S inspection Low temp test Ventilation inspection Manual valve exercise Flow control valve inspection PRV inspection Hoist inspection Performed station housekeeping Generator test run: Start time- 11:48 Stop time- 12:54 Start hours- 21.30 Stop hours- 22.45 Start fuel- Full 7/8 Stop fuel- Full 7/8 Generator operating stats (under load P#2): Engine- 1800 rpm Oil pressure- 37 psi Coolant temp- 172 F Frequency- 60 Hz Voltage- 601 V Amperes- 27 A Fuel pressure- 4.06 psi No abnormalities during generator test run- placed generator back into auto once test run completed * Station/equipment- Ok | Newmarket Kirby Pumping Station | 2025-10-02
CENTRAL | October | Onsite for station check: Station/equipment- Ok | Newmarket Kirby Pumping Station | 2025-10-15
CENTRAL | October | Onsite for station check: Central operators onsite with contractor for generator upgrades/training * Station/equipment- Ok | Newmarket Kirby Pumping Station | 2025-10-06
CENTRAL | October | Onsite for station check: Completed on-call scada review Station/equipment- Ok | Newmarket Kirby Pumping Station | 2025-10-10
CENTRAL | October | On-site with CMS Tyler Zimmerman-Jones and Lee Ferguson to flow test P5/6. Ran Pumps 5/6 and observed operation, returned station to normal operation. Found some pressure gauge valves need replacing, Lee F to replace. Contractors on-site with YR PCS for generator fuel LIT commissioning. Informed ROC. | Newmarket Kirby Pumping Station | 2025-10-06
CENTRAL | October | Onsite for station check: Station/equipment- Ok | Newmarket Kirby Pumping Station | 2025-10-03
CENTRAL | October | On-site to acknowledge and reset interlock on wells due to lolo treated total cl2, notified by J Garnett (on-call operator) Analyzer reading 1.91mg/L upon arrival. Reset wells. Interlock removed. Wells are in manual off. We?ll continue to monitor remotely | Newmarket Well 1 & 2 | 2025-10-16
CENTRAL | October | Station and equipment check Take weekly BacT samples W 11316280 and grabs @ 8:30 am Treated Total: 2.95 mg/l Treated Free: 0.10 mg/l Chemicals/ reagents ok Ops normal | Newmarket Well 1 & 2 | 2025-10-22
CENTRAL | October | Station and equipment check Take weekly BacT sample W11331205 and grabs @ 8:50 am Treated Total: 3.10 mg/l Treated Free: 0.13 mg/l Analyzer Total: 3.03 mg/l Analyzer Free: 0.15 mg/l Chemicals/reagents ok All other readings on PD sheets Ops normal | Newmarket Well 1 & 2 | 2025-10-29
CENTRAL | October | Station and equipment check Took grabs @ 11:30 am (running) Treated Total: 2.88 mg/l Treated Free: 0.13 mg/l No adjustments required Changed CL17 reagent "Treated Total" Topped up ammonia tank 2 Replaced PRV on silicate system, P1 side (primed and set to 70-80 psi) Changed chlorine cylinders with Joe D (left bank) Ops normal | Newmarket Well 1 & 2 | 2025-10-27
CENTRAL | October | Station and equipment check Took grabs @ 9:55 am (running) Treated Total: 2.89 mg/l Treated Free: 0.10 mg/l Analyzer Total: 2.89 mg/l Analyzer Free: 0.13 mg/l No adjustments required Changed CL17 reagent "Influent free" Chemicals/reagents ok Ops normal | Newmarket Well 1 & 2 | 2025-10-31
CENTRAL | October | Remotely enabled Silicate tank level OOR alarm as tank level now below 120cm span (119.4cm). | Newmarket Well 1 & 2 | 2025-10-28
CENTRAL | October | Topped up NaSi day tanks 585 to 1090L. | Newmarket Well 1 & 2 | 2025-10-17
CENTRAL | October | On-site for station check. Grab/analyzer results as follows (mg/L): Influent Free Cl (10:30): G: 2.52 A: 2.57 Effluent Free Cl (10:32): G: 2.44 A: 2.45 Treated Free Cl (10:33): G: 0.10 A: 0.14 Treated Total Cl (10:34): G: 2.80 A: 2.87 Checked station and equipment, no new issues found. Entered readings into shared PD excel file. | Newmarket Well 1 & 2 | 2025-10-24
CENTRAL | October | Station and equipment check Take operational samples and grabs @ 9:55 am Treated Total: 2.96 mg/l Treated Free: 0.12 mg/l Topped up ammonia tank 1 Chemicals/reagents ok Tested silicate containment flood alarm - ok Ops normal | Newmarket Well 1 & 2 | 2025-10-20
CENTRAL | October | On site to complete work orders: 08:50 placed wells 1 and 2 in manual off. 09:02 Notified ROC of work to be completed. 09:08 Chlorine gas detector test. Alarm triggered and shut off system activated with no issues. Placed all chlorine/turb analyzers in calibration mode. 09:30 Chlorine analyzer maintanance. 10:10 Turbidity analyzer calibration/vial cleaning. 10:24 verified chlorine analyzers (mg/L): Influent free chlorine grab: 2.38. Analyzer: 2.37. Effluent free chlorine grab: 0.81. Analyzer: 0.85. Treated free chlorine grab: 0.06. Analyzer: 0.09. Treated total chlorine grab: 2.38. Analyzer: 2.38. JHSC inspection. No issues. 10:45 Silicate injection point 1 and 2 flush. Placed dechlorination at outfall and flushed 5 cubic meters. Low temp silicate room alarm came in. Powered on station heaters. Well 1 and 2 deep well exhaust maintenance. Comprehensive site cleaning. 13:44 placed wells 1 and 2 back to auto. No new issues on site. | Newmarket Well 1 & 2 | 2025-10-23
CENTRAL | October | Delivered 475L of Sodium Silicate to top up NaSi day tanks (46cm/tank). | Newmarket Well 1 & 2 | 2025-10-01
CENTRAL | October | On-site for station check, in-house operational sampling, weekly micro sampling (W11299330) and Q4 quarterly sampling (W11247474) work orders. Wells running upon arrival. Changed Effluent Free Cl CL17 analyzer reagents. Grab/analyzer results as follows (mg/L): Influent Free Cl (10:58): G: 2.66 A: 2.60 Effluent Free Cl (11:00): G: 2.48 A: 2.47 Treated Free Cl (11:01): G: 0.14 A: 0.11 Treated Total Cl (11:01): G: 2.90 A: 2.96 Collected site treated and raw samples. Entered site readings into shared PD excel file. No new issues found while on-site. | Newmarket Well 1 & 2 | 2025-10-14
CENTRAL | October | On-site for station check, return NaSi P1 to service and change Cl2 bank B with Joe Demarco. Changed Cl2 bank B with Joe Demarco. Replaced NaSi P1 PSV and able to run pump locally but not via SCADA. Appears to be issue with electrical outlet. CMS Tyler Zimmerman Jones came to site to correct issue, replaced relay, able to run pump normally now. Adjust max flow from 220-215mL/min for NaSi P1 and returned pump to service. Backflushed with dechlorination measures in place following prime of NaSi P1 line, site returned to normal operation. Donald Moses on-site and topped up NaSi day tanks. Entered station readings into shared PD excel file. Batched ammonia tank 2. No other new issues found while on-site. | Newmarket Well 1 & 2 | 2025-10-10
CENTRAL | October | On-site for assigned work orders, informed ROC. Placed Wells local/off and completed NaSi system inspection/maintenance. Primed/verified NaSi P2 max flow following injection line maintenance. Completed Cl2 system monthly inspection. Back flushed with dechlorination measures in place. Returned system to normal operation and started Wells in remote/man to observe operation. Completed ammonia system inspection, adjusted max flow for P1/2 to 200mL/min. No other new issues found. NaSi P1 remains OOS. Returned Wells to remote/auto - Wells shutdown as duty not called for. | Newmarket Well 1 & 2 | 2025-10-09
CENTRAL | October | Informed ROC. -Performed annual calibration and put instruments in Cal mode while doing the tasks. Devices done were AITs, NIT, WIT, chlorine gas sensors and chlorinators. -Configured the new Silicate LIT max span to 120cm. Level reading matched SCADA. -All alarms were cleared after the job. Operator William run the well and no issues encountered. | Newmarket Well 1 & 2 | 2025-10-01
CENTRAL | October | Station and equipment checked, no issues found Chemical levels and systems inspected, ok Verified analyzers, all grabs and readings emtered in to PWQ sheet influent F @1118 g:2.60 a:2.68 Effluent F @1120 g:2.36 a:2.35 Treated F @1122 g:0.14 a:0.12 Treated T @1124 g:3.00 a:2.97 temp 11.6 | Newmarket Well 1 & 2 | 2025-10-03
CENTRAL | October | Back on-site to troubleshoot NaSi system. Found NaSi P1 PSV needs to be replaced, will source parts and create WO to replace. Unplugged NaSi P1, pump can be ran if discharge line plumbed to P2 side of chemical panel board. No other new issues found. | Newmarket Well 1 & 2 | 2025-10-08
CENTRAL | October | On-site due to wells interlocked by no flow alarm on turbidity meter. Conner from ROC notified me if the issue. At the direction of Redempto from instrumentation, I disabled flow sensor on meter. Cleared interlock onOIT panel, wells back in to service. Will create a WO to replace flow sensor | Newmarket Well 1 & 2 | 2025-10-03
CENTRAL | October | Log entry from on-site time 07:47-08:40 October 8 2025: On-site for station check and weekly micro sampling (W11278511) work orders. NaSi calculated dosage of 10.6mg/L, target 13.5mg/L. NaSi P1 man/off - visually inspected, no obvious signs of issue. Will return to troubleshoot NaSi system and return NaSi P1 to service - turbidity currently reading normal.Grab/analyzer results as follows (mg/L): Influent Free Cl (08:09): G: 2.50 A: 2.58 Effluent Free Cl (08:11): G: 2.40 A: 2.37 Treated Free Cl (08:16): G: 0.10 A: 0.11 Treated Total Cl (08:17): G: 2.84 A: 2.91 Collected all samples. Checked station and equipment, no other new issues found. | Newmarket Well 1 & 2 | 2025-10-08
CENTRAL | October | Flushed 60m3 via main to storm with dechlorination measures in place, total Cl grab at 15:00 1.12mg/L. | Newmarket Well 14 | 2025-10-09
CENTRAL | October | Onsite for station check: Station offline * Station/equipment- Ok | Newmarket Well 14 | 2025-10-07
CENTRAL | October | Station and equipment check Took grabs @ 8:40 am (running) Treated Total: 2.74 mg/l Treated Free: 0.11 mg/l Chemicals/reagents ok Ops normal | Newmarket Well No. 15 | 2025-10-27
CENTRAL | October | Station and equipment check Take weekly BacT sample W11331205 and grabs @ 8:10 am Treated Total: 2.86 mg/l Treated Free: 0.10 mg/l Analyzer Total: 2.82 mg/l Analyzer Free: 0.12 mg/l No adjustments required Chemicals/reagents ok Ops normal | Newmarket Well No. 15 | 2025-10-29
CENTRAL | October | Station and equipment check Took grabs @ 8:40 am (not running) Treated Total: 2.00 mg/l Treated Free: 0.05 mg/l Chemicals/reagents ok Ops normal | Newmarket Well No. 15 | 2025-10-31
CENTRAL | October | -on site to change the well house ex fan thermostat. Ernie and myself changed it and confirmed operation. Under direction of oic | Newmarket Well No. 15 | 2025-10-28
CENTRAL | October | Onsite with Alex B for chlorine cylinder change, Left side Ops normal | Newmarket Well No. 15 | 2025-10-29
CENTRAL | October | Onsite with Joe D for chlorine cylinder change Right side Ops normal | Newmarket Well No. 15 | 2025-10-21
CENTRAL | October | On-site for station check. Grab/analyzer results as follows (mg/L): Influent Free Cl (11:19): G: 2.56 A: 2.74 (adjusted analyzer to 2.74mg/L based on average grab) Effluent Free Cl (11:21): G: 2.64 A: 2.58 Treated Free Cl (11:22): G: 0.13 A: 0.14 Treated Total Cl (11:23): G: 3.02 A: 3.15 Checked station and equipment, no new issues found. Entered readings into shared PD excel file. | Newmarket Well No. 15 | 2025-10-24
CENTRAL | October | Topped up NaSi day tank 209 to 392L. | Newmarket Well No. 15 | 2025-10-17
CENTRAL | October | Back onsite to replace CL17 reagent (influent Free Analyzer) Station ops ok, Duty not active | Newmarket Well No. 15 | 2025-10-22
CENTRAL | October | Station and equipment check Took grabs and operational samples @ 8:30 am Treated Total: 2.95 mg/l Treated Free: 0.12 mg/l Topped up ammonia tank 1 Chemicals/reagents ok Ops normal | Newmarket Well No. 15 | 2025-10-20
CENTRAL | October | Station and equipment check Duty just activated during check Took grabs @ 8:35 am Treated Total: 2.36 mg/l Treated Free: 0.10 mg/l Chemicals/reagents ok All other readings entered on PD sheets Ops normal | Newmarket Well No. 15 | 2025-10-17
CENTRAL | October | Station and equipment check Take weekly BacT sample W11316280 and grabs @ 8:00 am Treated Total: 3.10 mg/l Treated Free: 0.12 mg/l Chemicals/reagents ok Ops normal | Newmarket Well No. 15 | 2025-10-22
CENTRAL | October | Station and equipment checked, no issues found Chemical levels and systems inspected, ok Deep well exhaust inspeced CL2 GAs detector tested Verified analyzers, all grabs and readings emtered in to PWQ sheet influent F @0847 g:2.70 a:2.63 Effluent F @0851 g:2.48 a:2.56 Treated F @0853 g:0.11 a:0.14 Treated T @0900 g:3.08 a:3.04 temp 11.2 | Newmarket Well No. 15 | 2025-10-03
CENTRAL | October | On-site for assigned work orders, informed ROC. Placed W15 man/off and completed turbidimeter maintenance, returned Well to remote/auto following completion of maintenance. Changed Cl2 bank A with Joe Demarco. Completed general housekeeping. No new issues found while on-site. | Newmarket Well No. 15 | 2025-10-15
CENTRAL | October | On-site for station check, in-house operational sampling, weekly micro sampling (W11299330) and Q4 quarterly sampling (W11247488) work orders. Placed Well 15 in remote/man/on prior to arrival for sampling. Grab/analyzer results as follows (mg/L): Influent Free Cl (12:05): G: 2.64 A: 2.56 Effluent Free Cl (12:08): G: 2.48 A: 2.45 Treated Free Cl (12:09): G: 0.13 A: 0.14 Treated Total Cl (12:10): G: 2.92 A: 2.95 Collected site treated and raw samples. Entered site readings into shared PD excel file. No new issues found while on-site. Returned W15 to auto, shutdown as duty not called for. | Newmarket Well No. 15 | 2025-10-14
CENTRAL | October | Topped up silicate tank from 88L to 387 L. | Newmarket Well No. 15 | 2025-10-10
CENTRAL | October | On-site for station check and weekly micro sampling (W11278511) work orders. Grab/analyzer results as follows (mg/L): Influent Free Cl (10:08): G: 2.78 A: 2.69 Effluent Free Cl (10:10): G: 2.50 A: 2.46 Treated Free Cl (10:15): G: 0.11 A: 0.14 Treated Total Cl (10:15): G: 2.88 A: 2.97 Collected samples. Checked station and equipment, no other new issues found. | Newmarket Well No. 15 | 2025-10-08
CENTRAL | October | on-site for various WO's -Silicate lines flushed, injector pulled, drawdown complete, both pumps ok -Ammonia pumps and lines inspected, drawdown complete, both pumps ok -Chlorinators visually inspected and chlorine system inspected, ok -Analyzer maintenance completed -JHSC Inspection completed | Newmarket Well No. 15 | 2025-10-02
CENTRAL | October | On-site for station check. Switched to ammonia tank 1 and batched ammonia tank 2. Replaced Treated total/free Cl CL17 analyzer reagents. Station readings in shared PD excel file. Checked station and equipment, no new issues found. | Newmarket Well No. 15 | 2025-10-10
CENTRAL | October | Station and equipment check Took grabs @ 11:35 am (running) Treated Total: 2.78 mg/l Treated Free: 0.10 mg/l Mono: 2.30 mg/l TA: 0.55 mg/l FA: 0.09 mg/l * Adjusted CL2:Ammonia ratio at 11:40 AM from 4.1 to 4,2 (waited 1 hour) Took SL1000 readings @ 12:40 PM Mono: 2.28 mg/l TA: 0.50 mg/l FA: 0.05 mg/l No further changes made, well shutdown at duty stop aprox. 12:45 pm Chemicals/reagents ok General housekeeping Ops normal | Newmarket Wells 13-16 | 2025-10-31
CENTRAL | October | Filled NaSi tank 2109L to 2870L. Property services on-site to repair cl2 room door sill. | Newmarket Wells 13-16 | 2025-10-27
CENTRAL | October | On-site for station check. Grab/analyzer results as follows (mg/L): Influent Free Cl (08:56): G: 2.54 A: 2.54 Effluent Free Cl (08:57): G: 2.02 A: 2.10 Treated Free Cl (08:58): G: 0.06 A: 0.10 Treated Total Cl (08:59): G: 2.78 A: 2.65 Checked station and equipment, no new issues found. Station not running while on-site, entered readings into shared PD excel file. | Newmarket Wells 13-16 | 2025-10-24
CENTRAL | October | Onsite to complete Maximo workorders No issues Ops normal | Newmarket Wells 13-16 | 2025-10-16
CENTRAL | October | Station and equipment check Take weekly BacT samples W11316280 and grabs @ 9:45 am Treated Total: 2.80 mg/l Treated Free: 0.10 mg/l Chemicals/ reagents ok Replaced Parker fitting on silicate injection point 2, small leak. Also cleaned floor in Ammonia tank room. Ops normal | Newmarket Wells 13-16 | 2025-10-22
CENTRAL | October | Tested CL2 leak - ok Informed ROC (Carter D) Changed CL2 cylinders right bank with Joe D, had small leak, tightened all - could not find leak after Station ops normal | Newmarket Wells 13-16 | 2025-10-21
CENTRAL | October | Station and equipment check Took grabs @ 9:30 am (running) Treated Total: 2.80 mg/l Treated Free: 0.12 mg/l No adjustments required Topped up ammonia tank #1 Turned heater on in well 13, cleared low temp alarm Chemicals/reagents ok Ops normal | Newmarket Wells 13-16 | 2025-10-27
CENTRAL | October | Filled NaSi tank 2787 to 3576L. | Newmarket Wells 13-16 | 2025-10-29
CENTRAL | October | Station and equipment check Take weekly BacT samples W11331205 and grabs @ 10:10 am Treated Total: 2.80 mg/l Treated Free: 0.13 mg/l Analyzer Total: 2.79 mg/l Analyzer Free: 0.14 mg/l No adjustments required Changed CL17 reagent ?Treated Total analyzer? Chemicals/reagents ok Ran well 13 in manual to get RAW sample Ops normal | Newmarket Wells 13-16 | 2025-10-29
CENTRAL | October | Station and equipment check Took grabs @ 11:00 am (running) Treated Total: 2.70 mg/l Treated Free: 0.12 mg/l Changed reagent CL17 treated free All other readings on PD sheets Topped up ammonia tank #2 Ops nornal | Newmarket Wells 13-16 | 2025-10-17
CENTRAL | October | Topped up NaSi tank 1890L to 2656L. | Newmarket Wells 13-16 | 2025-10-17
CENTRAL | October | On-site for station check and weekly micro sampling (W11278511) work orders. NaSi P2 remains man/off. Grab/analyzer results as follows (mg/L): Influent Free Cl (09:07): G: 2.70 A: 2.75 Effluent Free Cl (09:08): G: 2.58 A: 2.60 Treated Free Cl (09:11): G: 0.14 A: 0.14 Treated Total Cl (09:11): G: 2.94 A: 2.90 Collected site treated and W13 raw samples. Instrumentation on-site for annual cals, power cycled to W16 flow meter but Instrumentation techs determined sensor needs to be replaced. Will return to collect W16 raw samples once Instrumentation replaces flow sensor. Checked station and equipment, no other new issues found. | Newmarket Wells 13-16 | 2025-10-08
CENTRAL | October | On-site for station check. NaSi P2 pressure gauge lower than normal operation, will remain man/off/OOS until further investigation can take place. Unable to clear flow fault on NMW16 flow meter, will create WO for instrumentation to investigate. Entered station readings into shared PD excel file. Replaced Effluent Free Cl CL17 analyzer reagents. Grab/analyzer results as follows (mg/L): Influent Free Cl (14:19): G: 2.64 A: 2.73 Effluent Free Cl (14:21): G: 2.54 A: 2.53 Treated Free Cl (14:23): G: 0.11 A: 0.14 Treated Total Cl (14:24): G: 2.78 A: 2.83 Checked station and equipment, no other new issues found. | Newmarket Wells 13-16 | 2025-10-06
CENTRAL | October | Station and equipment checked, no issues found Chemical levels and systems inspected, ok Topped up ammonia day tank 2 Weekly Bacti samples taken Topped up motor mineral oil Well 13 Verified analyzers, all grabs and readings emtered in to PWQ sheet influent F @ 0822 g:2.68 a:2.67 Effluent F @0826 g:2.46 a:2.51 Treated F @ 0828 g:0.11 a:0.13 Treated T @ 0830 g:2.82 a:2.85 temp 11.7 | Newmarket Wells 13-16 | 2025-10-01
CENTRAL | October | Onsite to complete CL2 cylinder change * | Newmarket Wells 13-16 | 2025-10-02
CENTRAL | October | Station and equipment checked, no issues found Chemical levels and systems inspected, ok Changed diaphram in NaSi pump 2, primed line and put back in to service Verified analyzers, all grabs and readings emtered in to PWQ sheet influent F @1411 g:2.80 a:2.79 Effluent F @1413 g:1.88 a:1.97 Treated F @ 1415 g:0.17 a:0.13 Treated T @ 1418 g:2.62 a:2.58 temp 11.2 | Newmarket Wells 13-16 | 2025-10-03
CENTRAL | October | Back on-site to run W16 to collect weekly micro sample (W11278511). Batched ammonia tank 1. Ran W16 in remote/man following work done by Instrumentation. Monitored operation. Rotated W16 to D1, W13 to D2. Collected W16 raw water sample and returned Well to remote/auto, shutdown as duty not called for. | Newmarket Wells 13-16 | 2025-10-08
CENTRAL | October | On-site for station check, in-house operational sampling, weekly micro sampling (W11299330) and Q4 quarterly sampling (W11247460) work orders. W16 running in remote/auto upon arrival. Grab/analyzer results as follows (mg/L): Influent Free Cl (09:33): G: 2.55 A: 2.65 (adjusted to 2.55mg/L based on average of 3 grabs) Effluent Free Cl (09:36): G: 2.40 A: 2.36 Treated Free Cl (09:38): G: 0.09 A: 0.13 Treated Total Cl (09:39): G: 2.68 A: 2.69 Collected site treated samples and W16 raw samples. Adjusted Cl:AMM ratio from 4.1 to 4.0 based on FA grab of 0.09mg/L, new grab of 0.06mg/L, will monitor. Switched to run W13 in remote/man for sampling. Site readings in shared PD excel file. Collected W13 samples, returned W13 to auto and will return W16 to auto once duty 1 deactivates (current 72%). No new issues found while on-site. | Newmarket Wells 13-16 | 2025-10-14
CENTRAL | October | Onsite to perform annual calibrations/maintenance. Put the devices in calibration mode. Devices were done as below: Influent, effluent, treated free AITs, Ammonia and silicate tank LIT, NIT,PIT. Took a multiple grab samples and no adjustments required. Treated free AIT - 0.07 mg/l, Grab samples- 0.08 mg/l Effluent AIT - 2.53 mg/l, Grab sample - 2.52 mg/l Influent AIT - 2.61 mg/l grab samples-2.59 mg/l. There was a fault on WELL 16 flowmeter. Replaced transmitter. No luck. Removed faulty eprom and reprogrammed the device. No more issues. Please contact instrumentation if fault comes back again while we wait for parts to arrive from factory. All the related alarms were cleared and no issues. Ryan ran the well 16 and flowmeter was reading as expected. No issues. Informed ROC, armed the building and left the site. | Newmarket Wells 13-16 | 2025-10-08
CENTRAL | October | On-site for station check. Entered station readings into shared PD excel file. Adjusted NaSi P1 max flow to 255mL/min and P2 to 290mL/min based on max flow test. Found NaSi Injection point 2 appears clogged, routed P2 to Injection point 1, point 2 will need to be pulled and cleaned next week. No other new issues found while on-site , both NaSi pumps in remote/auto. | Newmarket Wells 13-16 | 2025-10-10
CENTRAL | October | Onsite with instrumentation to complete maximo workorders Informed ROC (Angelica) Placed wells manual OFF during work Pulled both silicate injection points and cleaned, tested both points back in operation Test ran Well 16 in manual with no issues, wells back to auto after calibrations | Newmarket Wells 13-16 | 2025-10-15
CENTRAL | October | Informed ROC. Onsite to perform annual calibration/maintenance. Put the devices in calibration mode. Devices were done as below: Treated Total AIT, Well LITs, Well FITs, weigh scale, chlorine Gas detectors, Chlorinators. Took a multiple grab samples. No adjustments required. Grab sample - 2.17 mg/l, treated Total AIT - 2.16 mg/l Installed new EPROM for Well 16 flowmeter and programmed it. No issues. Put the devices back in service. All the related alarms were cleared. Jason started the well. No issues. Informed ROC, armed the building and left the site. | Newmarket Wells 13-16 | 2025-10-15
WEST | October | Station Check (no issues found) | Nobleton Booster Pumping Station | 2025-10-31
WEST | October | In to complete station check. Pump running, no issues. | Nobleton Booster Pumping Station | 2025-10-27
WEST | October | Station check (no issues found) | Nobleton Booster Pumping Station | 2025-10-17
WEST | October | Onsite for station check Pump appears to be running Chamber dry Site secure No issues observed | Nobleton Booster Pumping Station | 2025-10-20
WEST | October | Station Check (no issues found) | Nobleton Booster Pumping Station | 2025-10-24
WEST | October | -on site for station check -chamber dry/pumps running | Nobleton Booster Pumping Station | 2025-10-03
WEST | October | -on site to complete station check -chamber lid secure, chamber dry, pump running -no issues | Nobleton Booster Pumping Station | 2025-10-14
WEST | October | -on site for station and JHSC inspection -pumps running site dry | Nobleton Booster Pumping Station | 2025-10-10
WEST | October | Station Check (no issues found) Input data to PWQ 11:30 Verified Depolox (mg/L) Free: Grab 1.29, A 1.37 (adjusted to match grabs) Total: Grab 1.47, A 1.23 (adjusted to match grabs) 11:45 #11316332 & operational samples | Nobleton North Elevated Tank | 2025-10-22
WEST | October | #11314458 created to check main disconnect #1131821 Heat T #11311999 drain v #11312010 low t #11312111 De-H #11312335 eyewash #11316771 P. gen #11311634 jhs #11311634 air v #11311788 Depolox 12:55 Verified mg/l) Free: Grab 1.32, A 1.06 (adjusted to match grabs) Total: Grab 1.72, A 1.94 (adjusted to match grabs) Topped up acetate | Nobleton North Elevated Tank | 2025-10-07
WEST | October | -on site to complete station check and weekly bacti W11256192 -checked trends: all ok -entered readings in PWQ: all ok -verified analyzers 11:35 -analyzer free: 1.22mg/l grab: 1.32mg/l - adjusted -analyzer total: 1.61mg/l grab: 1.63mg/l -reagents all ok -adjusted flow to total analyzer reader -no other issues | Nobleton North Elevated Tank | 2025-10-01
WEST | October | - Create W11341011 for total reading for instrumentation | Nobleton North Elevated Tank | 2025-10-06
WEST | October | -On-site to complete station check and collect sample -system duty not active, tower = 63 % -checked equipment -reviewed trends -depolox reagents ok -verified chlorine analyzers: 08:45 - Analyzer readings: Free Chlorine = 1.57 mg/L Total Chlorine = 1.29 mg/L 08:45 - Grabs: Free Chlorine = 1.53 mg/L Total Chlorine = 1.67/1.65/1.67 mg/L 08:51 - collected weekly regulatory micro. sample - W/O # W11298484 08:54 - adjusted total chlorine analyzer to 1.66 mg/L based on average of 3 grabs -recorded readings in PWQ sheet -no other issues found | Nobleton North Elevated Tank | 2025-10-14
WEST | October | -on site to investigate odour -checked south electrical chamber - found lid had shifted - repositioned and is now secured -odour has significantly reduced in valve room -took chlorine grab 13:20 -analyzer free: 2.05mg/l grab: 1.54mg/l - adjusted -analyzer total: 1.32mg:l grab: 1.70mg/l - adjusted -reagents all ok | Nobleton North Elevated Tank | 2025-10-10
WEST | October | -on site for station check and weekly bacti W11278563 -checked trends: all ok -entered reading in PWQ: all ok -verified analyzer 09:00 -analyzer free: 0.99mg/l grab: 1.40mg/l - adjusted -analyzer total: 1.43mg/l grab: 1.60mg/l - adjusted -reagents all ok -informed team lead of smell in tower - issue being escalated -no other issues | Nobleton North Elevated Tank | 2025-10-08
WEST | October | Attending site to check Total chlorine analyzer (W11341011). Found Total probe electrolyte membrane was plugged up. Replaced electrolyte in Total probe and verified reading against DPD grab average - adjusted Total residual reading to 1.57mg/L. Free analyzer was also checked - added cleaning grit, performed zero calibration and span calibration - adjusted Free residual reading to 1.49mg/L using DPD grab average. ROC was notified before and after work was performed. | Nobleton North Elevated Tank | 2025-10-09
WEST | October | Station Check (no issues found) Input data to PWQ 10:35 Verified Depolox (mg/L) Free: Grab 1.32, A 1.11 (adjusted to match grabs) Total: Grab 1.65, A 1.60 10:35 #11330407, #11246955 weekly and Q4 samples | Nobleton South Elevated Tank | 2025-10-29
WEST | October | Station Check (no issues found) Input data to PWQ 9:20 Verified Depolox (mg/L) Free: Grab 1.30, A 1.06 (adjusted to match grabs) Total: Grab 1,52, 1.56 Depolox (distilled/KI top up) #11316332 & operational samples | Nobleton South Elevated Tank | 2025-10-22
WEST | October | -on site for station check and weekly bacti W11256192 -checked trends: all ok -entered readings in PWQ -verified analyzers 10:55 -analyzer free: 1.15mg/l grab: 1.31mg/l - adjusted -analyzer total: 1.53mg/l grab: 1.72mg/l - adjusted -reagents all ok -no issues | Nobleton South Elevated Tank | 2025-10-01
WEST | October | -on site for station check and weekly bacti W11278563 -checked trends: all ok -entered reading in PWQ: -verified analyzer 09:40 -analyzer free: 1.04mg/l grab: 1.34mg/l - adjusted -analyzer total: 1.67mg/l grab: 1.69mg/l -reagents all ok | Nobleton South Elevated Tank | 2025-10-08
WEST | October | -On-site to complete station check and collect sample -system duty not active, tower = 67 % -checked equipment -reviewed trends -depolox reagents ok -verified chlorine analyzers: 12:51 - Analyzer readings: Free Chlorine = 1.15 mg/L Total Chlorine = 1.66 mg/L 12:51 - Grabs: Free Chlorine = 1.53/1.55/1.54 mg/L Total Chlorine = 1.72 mg/L 12:56 - adjusted free chlorine analyzer to 1.54 mg/L based on average of 3 grabs 12:58 - collected weekly regulatory micro. sample - W/O # W11298484 -recorded readings in PWQ sheet -no issues found | Nobleton South Elevated Tank | 2025-10-14
WEST | October | #11280692 sump #11281347 jhs #11282001 drain #11282022 heat t #11282033 sensor heat t #11282072 eyewash #11282093 low temp #11281124 gen #11281314 Depolox 10:45 verified (mg/L) Free: Grab 1.36, A 1.32 Total: Grab 1.82, A 1.88 Topped up acetate & distilled/KI | Nobleton South Elevated Tank | 2025-10-07
WEST | October | Station Check (no issues found) Input data to PWQ 13:40 Verified CL17s (mg/L) Influent Free: Grab 1.80, A 1.83 Effluent Free: Grab 1.60, A 1.66 Total Grab 2.11 13:50 #11316332 Samples | Nobleton Well 2 | 2025-10-22
WEST | October | Onsite for station check Well running in manual Checked residuals mg/L Influent @1208 Free analyzer 1.84 grab 1.74 Effluent @1211 Free analyzer 1.60 grab 1.67 Total grab 1.87 Regents ok Stopped well Flushed ntu analyzer | Nobleton Well 2 | 2025-10-20
WEST | October | Station Check (no issues found) Input data to PWQ 13:50 well manual on 14:10 Verified CL17s (mg/L) Influent: Free Grab 1.82, A 1.94 (adjusted to match grabs) Effluent Free: Grab 1.76, A 1.72 Total Grab 2.03 14:20 #11247054 & 11330407 weekly and Q4 (raw/treated) samples 14:43 well auto off | Nobleton Well 2 | 2025-10-29
WEST | October | Station Check (no issues found) input data to PWQ 13:45 Verified CL17s (mg/L) Influent Free: Grab 1.85, A 1.90 Effluent Free: Grab 1.68, A 1.65 Total Grab 1.93 | Nobleton Well 2 | 2025-10-24
WEST | October | On site for cylinder change | Nobleton Well 2 | 2025-10-23
WEST | October | Station Check (no issues found) Input data to PWQ 15:05 Verified CL17s (mg/l) Influent Free: Grab 1.50, A 1.50 Effluent Free: Grab 1.55, A1.54 Total Grab: 1.85 | Nobleton Well 2 | 2025-10-17
WEST | October | Station Check (no issues found) Input data to PWQ 12:40 Verified CL17s (mg/L) Influent: Free Grab 1.84, A 1.83 Effluent: Free Grab 1.66, A 1.70 Total: 2.07 | Nobleton Well 2 | 2025-10-31
WEST | October | Attending site to replace scrubber chlorine leak sensor (W11344619). Replaced sensor and cleared alarms. ROC was notified before and after work was performed. | Nobleton Well 2 | 2025-10-09
WEST | October | Test backflow preventers While testing stopped water flow to analyzer Both passed | Nobleton Well 2 | 2025-10-15
WEST | October | Topped up silicate tank Start 40.21 cm Stop 72.15 cm Ran silicate pumps didn?t noticed any obvious issues Flushed ntu analyzer Effluent grab @1242 Free analyzer 1.50 grab 1.40 | Nobleton Well 2 | 2025-10-15
WEST | October | -on site to complete following work orders -JHSC inspection: all ok -silicate system inspection: check/rod cleaned and system reprimed -chlorine analyzer maintenance: cleaned and verified -influent analyzer 11:55: 1.89mg/l grab: 1.86mg/l -effluent analyzer 11:50: 1.68mg/l grab: 1.68mg/l -reagents all ok -NTU cleaning and calibration: all ok -chlorine leak test- all ok - notice outside sensor broken created W11344619 -deep well exhaust inspection: all ok | Nobleton Well 2 | 2025-10-07
WEST | October | -on site for station check -checked trends: all ok -entered readings in PWQ: silicate low -pump 1 airlocked - purged air - replaced tubing element in pump 2 -verified analyzer -influent 10:45: 1.80mg/l grab: 1.78mg/l -effluent 10:50: 2.09mg/l grab: 2.12mg/l -total grab: 2.48mg/l -change effluent reagents -no issues | Nobleton Well 2 | 2025-10-10
WEST | October | -on site to complete station check -checked trends: all ok -entered PWQ readings -verified analyzer -influent 13:25: 1.87mg/l grab: 1.97mg/l - adjusted -effluent 13:30: 1.79mg/l grab: 1.82mg/l -total grab: 2.13mg/l -reagents all ok | Nobleton Well 2 | 2025-10-06
WEST | October | -on site for station check -checked trends: all ok -entered readings in PWQ -verified analyzers -influent 11:45: 1.87mg/l grab: 1.80mg/l - adjusted -effluent 11:50: 1.54mg/l grab: 1.64mg/l - adjusted -total grab: 2.12mg/l -reagents all ok -no issues | Nobleton Well 2 | 2025-10-03
WEST | October | -on site to complete station check -checked trends: all ok -entered readings in PWQ: all ok -verified analyzers -influent 10:15: 1.87mg/l grab: 1.89mg/l -effluent 10:20: 1.62mg/l grab: 1.60mg/l -total grab: 2.05mg/l -reagents all ok | Nobleton Well 2 | 2025-10-01
WEST | October | -on site for station check and weekly bacti W11278563 -checked trends: all ok -entered reading in PWQ: all ok -verified analyzer -influent 13:00: 1.84mg/l grab: 1.80mg/l -effluent 13:05: 1.64mg/l grab: 1.66mg/l -total grab: 1.97mg/l -reagents all ok | Nobleton Well 2 | 2025-10-08
WEST | October | Onsite for station check Well running in manual Checked residuals mg/L Influent @11:15 Free analyzer 2.01 grab 2.04 Effluent @11:17 Free analyzer 1.61 grab 1.61 Total grab 1.89 Stopped well Regants ok Primed hypo pump 2 | Nobleton Wells 3 & 7 | 2025-10-20
WEST | October | Station Check (no issues found) Input data to PWQ 10:35 Verified CL17s (mg/l) Influent: Free Grab 1.61, A 1.50 (adjusted to match grabs) Effluent: Free Grab 1.60, A 1.50 (adjusted to match grabs) Silicate Tank top up Hypo Tank top up Silicate Pump duty changed to All Stop (pump 1 duty 1) (will monitor turbidity) 11:15 well duty activated | Nobleton Wells 3 & 7 | 2025-10-31
WEST | October | Onsite to investigate well vfd not available/fault and low influent alarm causing well to be interlocked Checked residuals mg/l @1443 Influent analyzer 0.34 grab 0.31 Started back flush @1456 Primed both hypo pumps @1510 Influent free analyzer 0.96 grab 0.91 Stopped back flush @1512 Approximately 16m3 Reset vfd fault Started well in manual @1521 Stopped well @1542 | Nobleton Wells 3 & 7 | 2025-10-18
WEST | October | Station Check (no issues found) Input data to PWQ Verified CL17s (mg/L) 11:55 Influent Free: Grab 1.97, A 2.00 11:10 Effluent Free: Grab 1.54, A 1.56 Total Grab 1.70 Reagents changed for both # 113002220 Silicate injection points cleaned | Nobleton Wells 3 & 7 | 2025-10-24
WEST | October | Onsite to investigate lolo influential alarm interlocking the well Checked residuals mg/l @1010 Influent free analyzer 0.12 grab 0.09 @1039 Influent analyzer 0.91 grab 1.15 @1011 Started back flush Dechlor added to chamber @1041 stopped back flush Approximately 31m3 @1043 Started well in manual Well shut down on lolo influent But trend came back up and restarted @1046 @1103 stopped well | Nobleton Wells 3 & 7 | 2025-10-25
WEST | October | Station Check (no issues found) input data to PWQ Topped up hypo day tanks 10:25 Verified CL17s (mg/L) Influent Free: Grab 1.46, A 1.48 Effluent Free: Grab 1.50, A 1.54 Total Grab: 1.70 Silicate Pump #1 -replaced diaphragm, performed draw down (180 ml/min, no change) -placed in auto, in duty all stop -accidently broke the leak sensor, generated w/o #11376779 for repair | Nobleton Wells 3 & 7 | 2025-10-17
WEST | October | On site to Receive Hypo delivery. Filled 21 Carboy jugs and topped up hypo tank 1 - 64.59cm/99.36cm, tank 2 -64.28 cm/94 cm | Nobleton Wells 3 & 7 | 2025-10-21
WEST | October | Attending site to replace broken diaphragm rupture sensor on silicate pump#1 (W11376779). Well was in local-off during maintenance. Replaced sensor and primed pump. ROC was notified before and after maintenance work. | Nobleton Wells 3 & 7 | 2025-10-29
WEST | October | Test backflow preventers Team lead had ROC put wells in manual off for testing Both passed Called ROC had well 7 back in auto | Nobleton Wells 3 & 7 | 2025-10-16
WEST | October | Station Check (no issues found) Input data to PWQ 12:30 Verified CL17s (mg/L) Influent Free: Grab 2.10, A 2.10 Effluent Free: Grab 1.78, A 1.79 Total Grab: 2.02 12:40 #11316332 samples | Nobleton Wells 3 & 7 | 2025-10-22
WEST | October | In to receive hypo delivery. Day tanks topped up and carboys filled. | Nobleton Wells 3 & 7 | 2025-10-27
WEST | October | In to complete station check. Run w7 manual to monitor system. Enter data into PWQ. Adjust effluent Cl17 span cal from 2.01 to 1.85mg/L based on grab. Analyzer reagent levels good. Place w7 back to auto. Adjust NaSi pump max flows down 5ml/min | Nobleton Wells 3 & 7 | 2025-10-27
WEST | October | -on site to complete station check and weekly bacti W11256192 -checked trends: all ok -entered readings in PWQ: silicate low adjusted silicate pump speed -verified analyzer -influent 09:35: 2.03mg/l grab: 2.05mg/l -effluent 09:40: 1.65mg/l grab: 1.74mg/l - adjusted -total grab: -reagents all ok -small leak on silicate pump 2 cleaned and tightened pump head -tested | Nobleton Wells 3 & 7 | 2025-10-01
WEST | October | On site to complete station check and collect weekly bacti W11278563 -checked trends: all ok -entered reading in PWQ: all ok -verified analyzer -influent 13:30: 2.03mg/l grab: 2.00mg/l -effluent 13:35: 1.92mg/l grab: 1.82mg/l - adjusted -total grab: 1.98mg/l -reagents all ok | Nobleton Wells 3 & 7 | 2025-10-08
WEST | October | -on site to complete following work order -informed ROC -silicate system inspection: all ok -hypo system inspection: all ok -deep well exhaust inspection: all ok -low temp alarm test: all ok -PRV exercise: all ok -analyzer cleaning/verification -effluent analyzer 11:15: 1.72mg/l grab: 1.74mg/l -influent analuzer 11:20: 1.54mg/l grab: 1.58mg/l -reagents all ok -JHSC inspection: spill kit needs replacing -ran diesel generator -start time: 366.2 hrs -stop time: 367.3 hrs -diesel level: 888L | Nobleton Wells 3 & 7 | 2025-10-02
WEST | October | -on site for station check -checked trends: all ok -entered readings in PWQ: all ok -verified analyzers -influent 13:00: 1.95mg/l grab: 1.94mg/l -effluent 13:05: 1.72mg/l grab: 1.70mg/l -total grab: 1.86mg/l -reagents all ok -topped up hypo 164/164 - 240/240L - tank 2 LIT not reading - overfilled tank - should return/tanks equalized -no issues | Nobleton Wells 3 & 7 | 2025-10-03
WEST | October | -on site to complete station check -checked trends: all ok -entered readings in PWQ: all ok -verified analyzer -influent 11:40: 1.56mg/l grab: 1.60mg/l -effluent 11:45: 1.67mg/p grab: 1.64mg/l -total grab: 1.90mg/l -reagents all ok -topped up hypo- 135/134 - 181/179l | Nobleton Wells 3 & 7 | 2025-10-10
WEST | October | -on site for station check -checked trends: all ok -entered readings in PWQ: all ok -verified analyzer -influent 11:55: 1.93mg/l grab: 1.96mg/l -effluent 12:00: 1.68mg/l grab: 1.69mg/l -total grab: 1.84mg/l -reagents all ok -topped up hypo 127/126l-240/240L | Nobleton Wells 3 & 7 | 2025-10-06
WEST | October | Test backflow preventers Unable to test well 7 running Test will shut down well due to no flow to analyzers | Nobleton Wells 3 & 7 | 2025-10-15
WEST | October | -On-site to complete station check and collect weekly micro. samples -sample work order # W11298484 -well #3 OOS -well # 7 running in manual -received hypo delivery, tanks 88/85 L to 245/213 L -hypo pump #1 running at 30%, 59 strokes/min, 106 psi, DF = 66.25% -silicate pump #2 running at 59%, 69 strokes/min, 98 psi -checked equipment -reviewed trends -CL17 reagents ok -verified chlorine analyzers: 09:35 - Influent Analyzer = 1.94 mg/L 09:35 - Influent grab: Free chlorine = 2.06/2.14/2.08 mg/L 09:43 - adjusted influent analyzer to 2.09 mg/L based on average of 3 grabs 10:04 - Effluent Analyzer = 1.68 mg/L 10:04 - Effluent grab: Free chlorine = 1.66 mg/L Total chlorine = 1.91 mg/L 10:07 - collected weekly treated water micro. sample 10:07 - collected weekly well #7 raw water micro. sample -recorded readings in PWQ sheet -no issues found -well back into auto | Nobleton Wells 3 & 7 | 2025-10-14
WEST | October | On site to disconnect well 6 and coil up cabling as requested. | Nobleton Wells 5 & 6 | 2025-10-27
WEST | October | Station Check (no issues found) Input data to PWQ 11:40 Verified CL17s (mg/L) Influent: Free Grab 2.58, A 2.62 Effluent: Free Grab 1.84, A 1.79 Total Grab 2.54 11:55 #11330407 & #11247068 weekly & Q4 (well 5 raw&treat) CL17 (new reagents) Chlorine regulator (B side) placed back in standby | Nobleton Wells 5 & 6 | 2025-10-29
WEST | October | Station Check (no issues found) Input data to PWQ 13:10 Verified CL17s (mg/l) Influent Free: Grab 2.60, A 2.69 Effluent Free: Grab 1.98, A 2.07 Total Grab: 2.50 13:20 #11316332 samples | Nobleton Wells 5 & 6 | 2025-10-22
WEST | October | On site for cylinder change | Nobleton Wells 5 & 6 | 2025-10-23
WEST | October | Station Check (no other issues found) Input data to PWQ 12:10 Verified CL17 (mg/L) Influent Free: Grab 2.09, A 2.13 Effluent Free: Grab 1.85, A 1.95 Total Grab 2.30 Created work order for Effluent Free CL17 (keypad not working)#11393261 Station manual off upon arrival (calibrations being done) | Nobleton Wells 5 & 6 | 2025-10-24
WEST | October | Informed ROC. Performed annual calibration and put instruments in Cal mode while doing the tasks. Devices done were AITs, NIT and well LIT. Took grabs at the sample line. Influent free AIT1=1.86 mg/l Grab=1.87 mg/l Effluent free AIT2 = 1.75 mg/l Grab=1.77 mg/l All alarms were cleared after the job. No other issues encountered. | Nobleton Wells 5 & 6 | 2025-10-27
WEST | October | Station Check (no issues found) Input data to PWQ 12:52 Verified CL17s (mg/l) Influent Free: Grab 1.60, A 1.64 Effluent Free: Grab 1.35, A 1.39 Total Grab 1.61 | Nobleton Wells 5 & 6 | 2025-10-17
WEST | October | Onsite for station check well running in manual Checked residuals mg/L Influent @0945 Free analyzer 2.66 grab 2.66 Total grab 3.30 Effluent @0948 Free analyzer 2.03 grab 2.13 Total grab 2.38 Stopped well Flushed ntu analyzer Topped up silicate | Nobleton Wells 5 & 6 | 2025-10-20
WEST | October | Station Check (no issues found) Input data to PWQ 12:00 Verified CL17s (mg/l) Influent: Free Grab 2.40, A2.60 (adjusted to match grabs) Effluent: Free Grab 1.90, A 1.91 Total: Grab 2.60 Influent CL17 (new reagents) | Nobleton Wells 5 & 6 | 2025-10-31
WEST | October | Informed ROC. Performed annual calibration and put instruments in Cal mode while doing the tasks. Devices done were FIT, PIT, LITs, WIT, chlorinator and gas sensors. All alarms were cleared after the job. No other issues encountered. | Nobleton Wells 5 & 6 | 2025-10-24
WEST | October | In to complete station check. INST currently completing calibrations. MAINT disconnected w6 for CPD project, PCS working on alarms / programming to prevent interlocks to W5 while W6 OOS. | Nobleton Wells 5 & 6 | 2025-10-27
WEST | October | -on site to troubleshoot silicate system and station check -flushed silicate chemical lines/inspected check valves and cleaned NTU vial -inspected silicate tank - mixed silicone solution and reprimed pumps -placed statin back to normal operation -checked trends: all ok -entered readings in PWQ: all ok -verified analyzer -influent 10:30: 2.61mg/l grab: 2.60mg/l -effluent 10:35: 2.20mg/l grab: 2.16mg/l -total grab: 2.80mg/l -reagents all ok -tested silicate pump 2 - not working - changed tubing - while reprising line pull 2 failed - no power -tried cycling power - not working - create work order - W11341237 | Nobleton Wells 5 & 6 | 2025-10-06
WEST | October | -on site for station check and silicate troubleshooting -cleaned checks valve, rods and flushed lines -tested and reprimed both pumps -checked trends: all ok -entered readings in PWQ: -verified analyzers -influent 10:25: 2.70mg/l grab: 2.74mg/l -effluent 10:30: 2.08mg/l grab: 2.10mg/l -total grab: 2.84mg/l -reagents all ok -man/started wells to test silicate system no other issues - tested both pumps - silicate pump 1 working - pump 2 man/off -Benson S on site to change cylinder 60.5kg- 128.5kg - no other issues | Nobleton Wells 5 & 6 | 2025-10-03
WEST | October | -on site to troubleshoot silicate issue -pump 2 OOS - found P1 check valve clogged and line clogged | Nobleton Wells 5 & 6 | 2025-10-07
WEST | October | -on site to perform following work order -diesel run -diesel start:254:10 -diesel stop: 255:18 -diesel level: 457/446L -JHSC inspection: all ok -chlorine inspection: all ok -NTU calibration and clean: all ok -chlorine analyzer maintenance and verification -influent 12:05: 2.30mg/l grab: 2.34mg/l -effluent 12:00: 2.26mg/l grab: 2.28mg/l -reagents all ok -emergency chlorine kit inspection: all ok -silicate system inspection: replaced pump 2 suction line from hard pipe to pump - tested at 100% - SCADA showing 16% but running at 100% on pump - informed Eric S (Instrumentation) - Eric S on site at 13:30 to adjust pump scaling - tested all ok -PRV exercise: opened numerous times this month all ok -chlorine leak alarm: all ok -scrubber inspection: all ok -dehumidifier inspection: all ok | Nobleton Wells 5 & 6 | 2025-10-09
WEST | October | -on site for station check and weekly bacti W11278563 -checked trends: clean injection point again and ran well -entered reading in PWQ: low silicate -verified analyzer -influent 11:55: 2.67mg/l grab: 2.64mg/l -effluent 12:00: 2.28mg/l grab: 2.26mg/l -total grab: 2.80mg/l -reagents all ok -switch pump 1 to hard pipe suction line | Nobleton Wells 5 & 6 | 2025-10-08
WEST | October | Attending site to check silicate pump#2 issue (W11341237). Pump has suffered an electronic failure and the motor is not responding. Replaced pump and configured. Suspecting that there is an air leak on the suction side of the pump that is preventing it from priming. Tim will try to locate the leak tomorrow. | Nobleton Wells 5 & 6 | 2025-10-08
WEST | October | -on site for station check and silicate troubleshooting -silicate pump 2 roller was jammed - readjusted tubing element - tested -checked trends: all ok -entered reading im PWQ: all ok -verified analyzer -influent 09:45: 2.61mg/l grab: 2.64mg/l -effluent 09:50: 2.16mg/l grab: 2.18mg/l -total grab: 2.50mg/l -reagents all ok | Nobleton Wells 5 & 6 | 2025-10-10
WEST | October | Test backflow preventers Both Passed | Nobleton Wells 5 & 6 | 2025-10-15
WEST | October | -on site for station check, troubleshoot silicate system and weekly bacti W11256192 -cleaned foot valve on both chemical lines - pump 1 screen clogged - removed screen - pump 2 suction line clogged - cleared line -chemical chemical lines 2 check valve passing - cleaned/tested -reprimed both pumps -verified analyzers -influent 13:30: 2.64mg/l grab: 2.60mg/l -effluent 13:50: 2.28mg/l grab: 2.30mg/l -total grab:2.70mg/l -changed influent reagents -Dave T on site to replace silicate line 2 with 5/8 chemical line | Nobleton Wells 5 & 6 | 2025-10-01
CENTRAL | October | On site to complete station check and collect weekly bacti sample (W11316294). Verified analyzers: Inlet Free chlorine @ 7:46 Grab: 0.08 mg/L Analyzer: 0.04 mg/L Total chlorine @ 7:46 Grab: 2.68 mg/L Analyzer: 2.63 mg/L Outlet Free chlorine @ 7:40 Grab: 0.06 mg/L Analyzer: 0.14 mg/L Adjusted analyzer based on average of 3 grabs. Analyzer read 0.06 mg/L afterwards. Total chlorine @ 7:36 Grab: 2.19 mg/L Analyzer: 2.28 mg/L -Entered data into PD sheet -Checked trends -Returned QVW12 to auto | Queensville Elevated Tank | 2025-10-22
CENTRAL | October | On site to complete station check, collect weekly bacti sample (W11330505), and collect operational samples (W11330747). Verified analyzers: Inlet Free chlorine @ 8:29 Grab: 0.01 mg/L Analyzer: 0.04 mg/L Total chlorine @ 8:40 Grab: 2.70 mg/L Analyzer: 2.51 mg/L Adjusted analyzer based on average of 3 grabs. Analyzer read 2.70 mg/L afterwards. Outlet Free chlorine @ 8:01 Grab: 0.05 mg/L Analyzer: 0.05 mg/L Total chlorine @ 8:01 Grab: 2.26 mg/L Analyzer: 2.31 mg/L -Entered data into PD sheet -Checked trends | Queensville Elevated Tank | 2025-10-29
CENTRAL | October | On site to complete weekly bacti samples WO#11256318. - Tower draining when arrived - Entered data into PD sheets & collected samples - Check trends all okay - Checked reagents - Equipment all okay - No other issues found Inlet: Free Cl grab @ 8:58am G: 0.09mg/L A: 0.04mg/L Treated Total Cl grab @ 8:58am G: 2.78mg/L A: 2.70mg/L Outlet: Free Cl grab @ 9:02am G: 0.04mg/L A: 0.04mg/L Treated Total Cl grab @ 9:02am G: 2.44mg/L A: 2.38mg/L | Queensville Elevated Tank | 2025-10-01
CENTRAL | October | On site to complete preventative maintenance work orders. Informed ROC - Tower draining when arrived - Did depolox analyzer maintenance- outlet treated total Cl analyzer went hihi after cleaning it to around 5.00mg/L 11:50am water was being directed to users but the gradual increase only happened due to me performing PM on the analyzer and verified it and had to adjust based of avg grabs to 2.42mg/L - analyzer adjusted to 2.28mg/L @11:53am - will monitor - It?s still rising slowly so will do another grabs to verify treated total Cl analyzer @ 12:05pm A:2.90mg/L , G: 2.36mg/L adjusted based on avg grabs to 2.36mg/L. (Had to adjust the flow at micro2000 for total Cl reading- will Monitor remotely) - Outlet free Cl @12:08pm A:0.10mg/L G:0.04mg/L - adjusted analyzer based on avg grabs to 0.04mg/L - Inlet total Cl analyzer 12:15pm A:2.46mg/L G: 2.48,Free Cl A:0.03mg/L G:0.04mg/L - Did hi Lo temp test - Did portable gen test run - Did ventilation inspection - Did dehumidifier cleaning and inspection - Did hi Lo water level test - Did JHSC of site | Queensville Elevated Tank | 2025-10-03
CENTRAL | October | On site to complete station check, collect weekly bacti sample (W11278525), and collect Q4 NDMA sample (W11247884). Verified analyzers: Inlet Free chlorine @ 8:04 Grab: 0.09 mg/L Analyzer: 0.14 mg/L Total chlorine @ 8:27 Grab: 2.84 mg/L Analyzer: 2.34 mg/L Adjusted analyzer based on average of 3 grabs. Analyzer read 2.84 mg/L afterwards. Outlet Free chlorine @ 7:55 Grab: 0.03 mg/L Analyzer: 0.04 mg/L Total chlorine @ 7:55 Grab: 2.40 mg/L Analyzer: 2.33 mg/L -Entered data into PD sheet -Checked trends | Queensville Elevated Tank | 2025-10-08
CENTRAL | October | On site to reverify analyzers. Inlet Free chlorine @ 8:25 Grab: 0.06 mg/L Analyzer: 0.03 mg/L Total chlorine @ 8:34 Grab: 2.86 mg/L Analyzer: 2.41 mg/L Adjusted analyzer based on average of 3 grabs. Analyzer read 2.86 mg/L afterwards. Outlet Free chlorine @ 8:35 Grab: 0.07 mg/L Analyzer: 0.12 mg/L Total chlorine @ 8:43 Grab: 2.46 mg/L Analyzer: 2.93 mg/L Adjusted analyzer based on average of 3 grabs. Analyzer read 2.46 mg/L afterwards. | Queensville Elevated Tank | 2025-10-10
CENTRAL | October | On site to adjust/verify outlet analyzer Outlet Treated total @2:35pm A:1.80mg/L - adjusted analyzer to match grabs avg to 2.36mg/L G:2.36mg/L Treated free @ 2:54pm A: 0.08mg/L G: 0.05mg/L No new issues found | Queensville Elevated Tank | 2025-10-03
CENTRAL | October | On site to complete station check, collect weekly bacti sample (W11298582), collect operational samples (W11298824) and collect Q4 samples (W11247614). Verified analyzers: Inlet Free chlorine @ 8:40 Grab: 0.00 mg/L Analyzer: 0.03 mg/L Total chlorine @ 8:40 Grab: 2.74 mg/L Analyzer: 2.81 mg/L Outlet Free chlorine @ 8:26 Grab: 0.08 mg/L Analyzer: 0.13 mg/L Total chlorine @ 8:30 Grab: 2.15 mg/L Analyzer: 2.25 mg/L -Entered data into PD sheet -Checked trends | Queensville Elevated Tank | 2025-10-15
CENTRAL | October | On site to complete part of the station check. -Topped up ammonia tank 1 -Topped up silicate day tanks 381L -> 819L | Queensville Wells No. 1 and 2 | 2025-10-27
CENTRAL | October | On site to finish the station check and collect weekly bacti samples (W11330505). Verified analyzers: Influent Free Chlorine @ 10:12 Grab: 3.10 mg/L Analyzer: 2.95 mg/L Effluent Free Chlorine @ 10:14 Grab: 2.80 mg/L Analyzer: 2.68 mg/L Treated Free Chlorine @ 10:20 Grab: 0.17 mg/L Analyzer: 0.21 mg/L Treated Total Chlorine @ 10:17 Grab: 3.32 mg/L Analyzer: 3.19 mg/L -Entered data into PD sheet -Checked trends | Queensville Wells No. 1 and 2 | 2025-10-29
CENTRAL | October | Onsite to wrap up annual calibrations. Informed ROC. ROC placed duty to manual off Instruments calibrated: WITs, Chlorine leak detectors, Chlorinators Cleared associated alarms ROC placed duty back to auto Informed ROC, armed building and left site | Queensville Wells No. 1 and 2 | 2025-10-16
CENTRAL | October | On site to run generator and well for TSSA upgrade tests as well as complete PMs. Notified ROC of relevant alarms. -Contractors on site for TSSA upgrades tests Generator hours before run: 615.3 Diesel level: 82.9cm ¦ 1411L Test started at 9:19 Placed on load at 9:26 Tested ended at 10:32 Generator finished cooldown at 10:35 Hours after run: 616.6 Diesel level: 80.2cm ¦ 1359L -Flushed silicate lines with heated system water -Reprimed silicate line 2 since the injection point was pulled earlier in the month -Added dechlor to waste chamber then depressurized the raw main via isolating the contact chamber and opening the waste valve -Pulled silicate injection point 1 and cleaned it -Reprimed silicate line 1 -Backflushed a small amount to clear excess silicate -Hihi influent free alarm caused by silicate in the sample line. Primed analyzer to flush the line. Issue resolved -Returned wells to manual, ran well 1 manually to test silicate dosing -Returned both wells to auto | Queensville Wells No. 1 and 2 | 2025-10-21
CENTRAL | October | Changed chlorine cylinder bank A with Ryan. | Queensville Wells No. 1 and 2 | 2025-10-20
CENTRAL | October | On site to complete station check and collect weekly bacti sample (W11316294). Verified analyzers: Influent Free Chlorine @ 9:17 Grab: 2.86 mg/L Analyzer: 2.94 mg/L Effluent Free Chlorine @ 9:51 Grab: 2.70 mg/L Analyzer: 2.79 mg/L Treated Free Chlorine @ 9:12 Grab: 0.20 mg/L Analyzer: 0.21 mg/L Treated Total Chlorine @ 9:25 Grab: 3.36 mg/L Analyzer: 3.24 mg/L -Entered data into PD sheet -Checked trends | Queensville Wells No. 1 and 2 | 2025-10-22
CENTRAL | October | On site to complete station check and collect operational samples (W11309368). -Topped up silicate 182L -> 805L -Topped up ammonia tank 1 Verified analyzers: Influent Free Chlorine @ 10:00 Grab: 2.80 mg/L Analyzer: 2.88 mg/L Effluent Free Chlorine @ 9:54 Grab: 2.66 mg/L Analyzer: 2.77 mg/L Treated Free Chlorine @ 9:38 Grab: 0.17 mg/L Analyzer: 0.21 mg/L Treated Total Chlorine @ 9:38 Grab: 3.20 mg/L Analyzer: 3.23 mg/L -Entered data into PD sheet -Checked trends | Queensville Wells No. 1 and 2 | 2025-10-20
CENTRAL | October | On site to complete chlorine cylinder change with Ryan B. Changed bank B. Triggered chlorine leak alarm during process ? notified ROC. Reset halogen system. All good. | Queensville Wells No. 1 and 2 | 2025-10-28
CENTRAL | October | On site to complete station check. Verified analyzers: Influent Free Chlorine @ 12:52 Grab: 2.80 mg/L Analyzer: 2.90 mg/L Effluent Free Chlorine @ 13:05 Grab: 2.75 mg/L Analyzer: 2.91 mg/L Adjusted analyzer based on average of 3 grabs. Analyzer read 2.77 mg/L afterwards. Treated Free Chlorine @ 12:41 Grab: 0.27 mg/L Analyzer: 0.22 mg/L Treated Total Chlorine @ 12:41 Grab: 3.21 mg/L Analyzer: 3.29 mg/L -Entered data into PD sheet -Checked trends -Topped up ammonia tank 2 | Queensville Wells No. 1 and 2 | 2025-10-17
CENTRAL | October | On site to finish the station check. Verified analyzers: Influent Free Chlorine @ 14:46 Grab: 2.72 mg/L Analyzer: 2.76 mg/L Effluent Free Chlorine @ 14:42 Grab: 2.62 mg/L Analyzer: 2.67 mg/L Treated Free Chlorine @ 14:44 Grab: 0.16 mg/L Analyzer: 0.21 mg/L Treated Total Chlorine @ 14:44 Grab: 3.10 mg/L Analyzer: 3.13 mg/L -Entered data into PD sheet -Checked trends | Queensville Wells No. 1 and 2 | 2025-10-27
CENTRAL | October | Chris Iliohan Tyler Smith in to change flow control valve on chlorine booster pump 1 found blocked fitting in the piping re replace piping and test. Now able to control pressure | Queensville Wells No. 1 and 2 | 2025-10-30
CENTRAL | October | On site to complete station check. Verified analyzers: Influent Free Chlorine @ 8:56 Grab: 2.90 mg/L Analyzer: 2.84 mg/L Effluent Free Chlorine @ 8:55 Grab: 2.84 mg/L Analyzer: 2.78 mg/L Treated Free Chlorine @ 8:49 Grab: 0.18 mg/L Analyzer: 0.22 mg/L Treated Total Chlorine @ 8:49 Grab: 3.18 mg/L Analyzer: 3.27 mg/L -Entered data into PD sheet -Checked trends -Changed chlorine cylinder bank B with Donny M. -Topped up silicate day tanks 315L -> 784L -Topped up ammonia tank 2 | Queensville Wells No. 1 and 2 | 2025-10-24
CENTRAL | October | Onsite for station check: Received CL2 cylinder delivery: 16 received, 16 returned * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok | Queensville Wells No. 1 and 2 | 2025-10-31
CENTRAL | October | On-site with Ben Hess to troubleshoot chlorine dosing issues from last night. Reviewed trends. Inspected Cl2 system, tightened ball valve fitting and adjusted Cl2 booster pump pressure to 225psi for both pumps. Backflushed with dechlorination measures in place to following system inspection. Cleaned Influent Cl analyzer. Found turbidity analyzer needs descant replaced, will create WO for instrumentation. Returned system to normal operation and ran W2 in remote/man to test Cl2 system. Rotated booster pumps/chlorinators while W2 running, system appears to operate normally. Will monitor. Informed ROC. System in auto. | Queensville Wells No. 1 and 2 | 2025-10-31
CENTRAL | October | On site to receive sodium silicate delivery. Filled silicate bulk tank 34.7cm -> 86.8cm | Queensville Wells No. 1 and 2 | 2025-10-24
CENTRAL | October | On site to complete station check and collect weekly bacti sample (W11278525). Verified analyzers: Influent Free Chlorine @ 9:30 Grab: 2.98 mg/L Analyzer: 3.02 mg/L Effluent Free Chlorine @ 9:37 Grab: 2.84 mg/L Analyzer: 2.75 mg/L Treated Free Chlorine @ 9:41 Grab: 0.25 mg/L Analyzer: 0.21 mg/L Treated Total Chlorine @ 9:51 Grab: 3.14 mg/L Analyzer: 3.19 mg/L -Entered data into PD sheet -Checked trends | Queensville Wells No. 1 and 2 | 2025-10-08
CENTRAL | October | On site to perform station check & to collect weekly bacti samples WO11256318, created WO for chlorine cylinder pigtail replacement needed. W11331512 - Wells duty active on arrival - Entered readings into Process data sheet - Reagents all good - Trends all good - Equipment all okay CLBP 1 manual off - Dosage all good topped up silicate day tanks & NH3 TK1 - No new issues found Influent free Cl @ 11:05am G: 2.98mg/L A: 2.93mg/L Effluent free Cl @ 11:03am G: 2.86mg/L A: 2.89mg/L Treated free Cl @ 11:07am G: 0.25mg/L A: 0.23mg/L Treated total Cl @ 11:07am G: 3.40mg/L A: 3.34mg/L | Queensville Wells No. 1 and 2 | 2025-10-01
CENTRAL | October | On site to complete station check, collect weekly bacti sample (W11298582), collect operational samples (W11290975) and collect Q4 samples (W11247586). Also on site to start well 1 after maintenance addressed VFD fault. Well put back in service at 11:25 Verified analyzers: Influent Free Chlorine @ 12:52 Grab: 2.98 mg/L Analyzer: 2.96 mg/L Effluent Free Chlorine @ 12:45 Grab: 2.88 mg/L Analyzer: 2.94 mg/L Treated Free Chlorine @ 12:48 Grab: 0.18 mg/L Analyzer: 0.22 mg/L Treated Total Chlorine @ 12:38 Grab: 3.28 mg/L Analyzer: 3.27 mg/L -Entered data into PD sheet -Checked trends -Changed chlorine cylinder bank B with Sean (maintenance) -Topped up ammonia tank 1 -Changed treated total and treated free reagents -Ryan fixed silicate transfer pump, topped up day tanks 272L -> 751L | Queensville Wells No. 1 and 2 | 2025-10-15
CENTRAL | October | Received chlorine cylinders 12 full and 12 empty going out. | Queensville Wells No. 1 and 2 | 2025-10-03
CENTRAL | October | Onsite to take silicate from bulk tank Tried to run transfer pump Pump did not work shaft not rotating Tried to prime with water Was not successful, with breaker off tried to rotate with hand it did move both directions But did not rotate when powered on Left in local off with guard off | Queensville Wells No. 1 and 2 | 2025-10-15
CENTRAL | October | On-site with Donald Moses to change Cl2 cylinders and investigate Well 1 VFD fault. Found Chlorine bank A not switched over and scale tare off, reset tare, no Cylinder change required currently. Found Well 1 VFD faulted on overcurrent, reset and placed both Wells in remote/auto. No other new issues found while on-site. | Queensville Wells No. 1 and 2 | 2025-10-14
CENTRAL | October | On site to complete PMs. Notified ROC of relevant alarms. -Inspected and cleaned dechlor puck dispenser -Inspected chlorine system visually and tested regulators: due to recent freezing of bank A, cylinders in bank A still are not able to be drawn from. Currently running with both regulators in service, but the supply is coming from bank B based on regulator testing. Bank A regulator put out of service to aid in defrosting. No other issues found -Inspected ammonia system: checked PD sheets to confirm accurate dosage, inspected panel and tested flood alarm, topped up ammonia tank 2 -Calibrated turbidimeter: all good -Placed dechlor in outfall for the following work orders -Performed maintenance on surge anticipator valve -Put wells in local, isolated contact chamber, and depressurized raw main to pull silicate injection point 2 and perform maintenance. Returned system to normal condition and had ROC run wells manually to test dosing with silicate pump and injection point 2. Had ROC return the wells to auto when finished. | Queensville Wells No. 1 and 2 | 2025-10-09
CENTRAL | October | On site for annual calibrations Informed ROC. ROC placed wells in manual off Used cal mode on scada during the work Instruments calibrated: LITs, FITs, PIT, NIT and AITs No adjustments made to AITs. As found and as left are the same Bypassed flow sensor on influent free AIT due to contamination causing continuous sample flow Also showed HACH issues with CL17sc , concerning flow Cleared all associated alarms Asked ROC to run the wells. Monitored for a while. No issues Armed building and left site | Queensville Wells No. 1 and 2 | 2025-10-02
CENTRAL | October | On site to complete station check. Influent Free Chlorine @ 14:59 Grab: 3.02 mg/L Analyzer: 2.99 mg/L Effluent Free Chlorine @ 14:40 Grab: 2.83 mg/L Analyzer: 2.94 mg/L Treated Free Chlorine @ 14:46 Grab: 0.18 mg/L Analyzer: 0.23 mg/L Treated Total Chlorine @ 14:46 Grab: 3.36 mg/L Analyzer: 3.35 mg/L -Data entered into PD sheet -Checked trends -Reported ventilation causing well to run hot to J. Garnett. | Queensville Wells No. 1 and 2 | 2025-10-06
CENTRAL | October | On site to fill silicate truck for delivery to Mount Albert and Ballentrae: Bulk tank = 66.47 cm ?> 59.62 cm (Approx. = 850 L) | Queensville Wells No. 1 and 2 | 2025-10-02
CENTRAL | October | Onsite to respond to low influent free CL2, influent free gradually declining- informed by ROC: Upon arrival, noticed chlorine cylinders on bank A completely frozen- causing the influent residual to drop gradually Turned on chlorine room heater and placed regulator on chlorine bank B in service (drawdown mode) Influent residual recovered shortly after- adjusted chlorinator #2 dosing factor from 130% to 110% as per normal operations Informed ROC- will continue to monitor station via scada Station/equipment- Ok | Queensville Wells No. 1 and 2 | 2025-10-08
CENTRAL | October | On site to complete PMs. Notified ROC of relevant alarms. -Changed chlorine cylinders bank B with Donny -Topped up silicate day tanks combined 214L -> 807L -Performed chlorine gas detector test -Performed maintenance on both deep well exhaust valves -Topped up ammonia tank 1 -Ran generator - Started as a genuine power fail, put switch in test mode to keep generator running and put the generator on load gen started at 9:16 Run hours previous: 611.8 Fuel previous: 1510L ¦ 88.4 cm On load @ 9:35 Off load @ 10:42 Generator ATS returned to auto @ 10:44 Generator ATS returned to test @ 11:56 to allow well 1 to run despite generator switchover/utility power supply issues (maintenance contacted and on side to address this via created work order W11344597) Successfully switched to utility power @ 12:40 Generator stopped @ 12:43 Runtime after: 615.2 Fuel after: 1399L ¦ 82.1 cm -Performed chlorine analyzer maintenance -Verified analyzers: Influent Free Chlorine @ 11:27 Grab: 2.98 mg/L Analyzer: 2.91 mg/L Effluent Free Chlorine @ 11:30 Grab: 0.22 mg/L Analyzer: 0.25 mg/L Treated Free Chlorine @ 11:32 Grab: 0.17 mg/L Analyzer: 0.15 mg/L Treated Total Chlorine @ 11:43 Grab: 2.88 mg/L Analyzer: 2.85 mg/L -Changed reagents for influent free chlorine analyzer -Performed maintenance on flow control valve -Received chlorine delivery: 12 full in, 12 empty out -Performed JHSC inspection: all good | Queensville Wells No. 1 and 2 | 2025-10-07
CENTRAL | October | On site to complete station check. Verified analyzers: Influent Free Chlorine @ 13:36 Grab: 2.78 mg/L Analyzer: 2.84 mg/L Effluent Free Chlorine @ 13:58 Grab: 2.80 mg/L Analyzer: 2.98 mg/L Adjusted analyzer based on average of 3 grabs. Analyzer read 2.89 mg/L afterwards. Treated Free Chlorine @ 13:10 Grab: 0.17 mg/L Analyzer: 0.22 mg/L Treated Total Chlorine @ 13:27 Grab: 3.40 mg/L Analyzer: 3.33 mg/L -Entered data into PD sheet -Checked trends -Topped up silicate day tanks 38 -> 80cm -Change chlorine cylinder bank A with Divya | Queensville Wells No. 1 and 2 | 2025-10-10
CENTRAL | October | On-site to investigate NaSi transfer pump issues (see previous elog entry by Jacob Muzzin). Adjusted shaft and installed guard, pump running normally. Topped up NaSi day tanks. | Queensville Wells No. 1 and 2 | 2025-10-15
CENTRAL | October | Placed chlorine bank A back in operation as the primary draw source. | Queensville Wells No. 1 and 2 | 2025-10-10
CENTRAL | October | When turned well 2 off noticed Chlorinator took more time to lower chlorine dosage causing influent free Cl2 spike @ 2:20pm to 4.72mg/L but it came back right after one reading. No other issues found. | Queensville Wells No. 1 and 2 | 2025-10-01
CENTRAL | October | On site to start the wells in duty after maintenance replaced ejector with new parts. Will monitor remotely. No other issues found. CLBP1 can be used in emergency, currently in manual off. | Queensville Wells No. 1 and 2 | 2025-10-03
CENTRAL | October | On site to finish the station check and collect weekly bacti samples (W11330505). Verified analyzers: Influent Free Chlorine @ 11:51 Grab: 2.70 mg/L Analyzer: 2.67 mg/L Effluent Free Chlorine @ 11:50 Grab: 2.46 mg/L Analyzer: 2.53 mg/L Treated Free Chlorine @ 11:46 Grab: 0.12 mg/L Analyzer: 0.17 mg/L Treated Total Chlorine @ 11:53 Grab: 3.22 mg/L Analyzer: 3.09 mg/L -Entered data into PD sheet -Checked trends | Queensville Wells No. 3 and 4 | 2025-10-29
CENTRAL | October | On site to continue inspection of chlorine dosing issue. Ran well manually with chlorinator 1, no issues found. Well returned to auto once contact tank cleared. Also replaced treated free analyzer reagents. | Queensville Wells No. 3 and 4 | 2025-10-17
CENTRAL | October | On site to perform preventative maintenance work orders, informed ROC, electrical team on site to troubleshoot Well3 VFD issue, they have fixed the problem and want to run well 3 water to waste, to test the well performance before placing it back online. I closed valve going to distribution and opened valve going to waste to check how the well runs. When Dan B tried running well 3 to waste there was some disruption @ VFD again so they had to stop the run and open all electrical again to find out what when wrong. Well 3 remains manual off till fixed and well 4 can be used and it?s in duty 2. Donald M on site to top up silicate day tanks - Did chlorine analyzer maintenance - verified down below - Did NTU analyzer maintenance - Did JHSC of site - Did chlorine leak test - Did flow control valve exercise for well 4 - Did PRV testing - Did deep well exhaust valve exercise for both wells - Topped up mineral oil at well 4 - No new issues found Influent free Cl @ 2:24pm G: 2.66mg/L A: 2.60mg/L Effluent free Cl @ 2:26pm G: 0.08mg/L A: 0.10mg/L Treated free Cl @ 2.25pm G: 0.07mg/L A: 0.05mg/L Treated total Cl @ 2:26pm G: 2.07mg/L A: 2.01mg/L | Queensville Wells No. 3 and 4 | 2025-10-21
CENTRAL | October | On site while instrumentation calibrates new flow meter on well 3 and to run generator test. With Eric, placed well 3 flow meter in calibration mode so he could calibrate it. Test was successful and I removed it from calibration mode after. Gen hrs before run: 700h 53m Combined fuel before run: 1305L Test started at 9:53 Well 3 started at 9:58 Well 3 ended at 11:07 Test ended at 11:09 Gen cooldown ended at 11:14 Gen hrs after run: 702h 15m Combined fuel after run: 1268L Placed well 3 in duty 2, well 4 in duty 3. Returned wells to auto. | Queensville Wells No. 3 and 4 | 2025-10-23
CENTRAL | October | Attending site to perform a flowmeter verification on the well 3 FIT (W11390522). Flowmeter passed the verification testing. Operator Alex Bell ran the wells on generator power and the FIT appears to be functioning without issue. ROC was notified before and after work was performed. | Queensville Wells No. 3 and 4 | 2025-10-23
CENTRAL | October | On site to complete station check. Verified analyzers: Influent Free Chlorine @ 14:28 Grab: 2.60 mg/L Analyzer: 2.67 mg/L Effluent Free Chlorine @ 14:26 Grab: 2.50 mg/L Analyzer: 2.49 mg/L Treated Free Chlorine @ 14:25 Grab: 0.14 mg/L Analyzer: 0.15 mg/L Treated Total Chlorine @ 14:25 Grab: 3.21 mg/L Analyzer: 3.09 mg/L -Entered data into PD sheet -Checked trends -Returned wells to auto | Queensville Wells No. 3 and 4 | 2025-10-24
CENTRAL | October | Under direction of OIC Dan Zhou On site for: - silicate truck fill Start cm 20.02 cm Stop cm 12.26 cm | Queensville Wells No. 3 and 4 | 2025-10-16
CENTRAL | October | Switched duty for wells 3 and 4 so well 4 can run in duty 2 while well 3 is manual off due to VFD fault. | Queensville Wells No. 3 and 4 | 2025-10-20
CENTRAL | October | On site to complete station check and investigate influent free analyzer jumpy readings. -Inspected analyzer and chlorine system with J. Garnett. No issue found with analyzer. Placing chlorinator 2 into manual-off for now, returning wells to auto. Put well 3 into duty 2, well 4 in duty 3. -Topped up silicate day tanks 247L -> 504L Verified analyzers: Influent Free Chlorine @ 9:08 Grab: 1.65 mg/L Analyzer: 1.67 mg/L Effluent Free Chlorine @ 8:59 Grab: 0.14 mg/L Analyzer: 0.10 mg/L Treated Free Chlorine @ 8:58 Grab: 0.03 mg/L Analyzer: 0.04 mg/L Treated Total Chlorine @ 8:58 Grab: 2.01 mg/L Analyzer: 2.00 mg/L -Entered data into PD sheet -Checked trends | Queensville Wells No. 3 and 4 | 2025-10-17
CENTRAL | October | On site to complete station check and collect weekly bacti sample (W11316294). Verified analyzers: Influent Free Chlorine @ 12:06 Grab: 2.64 mg/L Analyzer: 2.62 mg/L Effluent Free Chlorine @ 11:57 Grab: 2.50 mg/L Analyzer: 2.61 mg/L Treated Free Chlorine @ 11:48 Grab: 0.16 mg/L Analyzer: 0.18 mg/L Treated Total Chlorine @ 11:48 Grab: 3.33 mg/L Analyzer: 3.24 mg/L -Entered data into PD sheet -Checked trends Helping maintenance (Dan and Satnam) test the new VFD on well 3, under guidance of Ben Hess. Notified ROC. Placed well 4 in manual-off then local. Placed chemical pumps in manual-off. Isolated contact chamber and valved well 3 to waste. No water directed to system during testing. Returned valving to normal, chemical system returned to auto, returned well 3 and 4 to manual-off. Testing well 3, running well via SCADA. Turned off speed deviation alarm for Dan as he troubleshot the speed deviation. Adjusted speed setpoint of well manually to test setpoint and analog feedback for Dan. Well operating normally, but leaving well pump 3 speed deviation alarm off for maintenance to revisit with PCS. Volume tracker for contact chamber in SCADA not displaying properly ? Contacted PCS (Ian Williams) and determined it to be an electronic communication to SCADA issue, since the onsite totalizer was operational. Well operating normally and CT was achieved. Turned off well for maintenance to address the flow totalizer communication issue. HART comm alarm came in after Dan and Satnam removed the flow totalizer to cycle power. Returned well 4 to auto (no issues with well 4 flow totalizer). | Queensville Wells No. 3 and 4 | 2025-10-22
CENTRAL | October | On site to fine tune speed set points and parameters. Worked with PCS to tune and test speed settings on VFD for well 3 in relation to the drive being replaced. | Queensville Wells No. 3 and 4 | 2025-10-24
CENTRAL | October | On site to respond to failed well 3 VFD. Removed and replaced VFD and tested for proper operation. Had trouble with VFD speed command and feedback signal. Will need to work with PCS to fix that issue. Spoke to operations and recommended to leave the speed deviation alarm toggled off for the time being. | Queensville Wells No. 3 and 4 | 2025-10-22
CENTRAL | October | On site to complete station check, flush silicate lines, and troubleshoot chlorinator 2. Notified ROC of relevant alarms. -Placed wells in manual-off then local -Placed silicate pumps in manual -Added dechlor to drain chamber -Opened waste valve slightly while flushing injection points then while repriming the silicate lines -Ran chlorinator 2 locally to troubleshoot dosage -Adjusted ammonia tank 1 hihi alarm to 89cm. Enabled hihi alarms for ammonia tank 1 and 2 LITs. -Topped up ammonia tank 1 -Ran chlorinator 2 locally to troubleshoot with Ben. No issues found. Returned well to manual and operated it with manual dosing. Switched to auto dosing ? issue potentially reemerged, so switched to chlorinator 1. Verified analyzers: Influent Free Chlorine @ 14:14 Grab: 2.74 mg/L Analyzer: 2.63 mg/L Effluent Free Chlorine @ 14:12 Grab: 2.34 mg/L Analyzer: 2.35 mg/L Treated Free Chlorine @ 14:11 Grab: 0.18 mg/L Analyzer: 0.15 mg/L Treated Total Chlorine @ 14:16 Grab: 3.04 mg/L Analyzer: 2.91 mg/L -Entered data into PD sheet -Checked trends | Queensville Wells No. 3 and 4 | 2025-10-27
CENTRAL | October | On site to complete station check and collect operational samples (W11309368). Verified analyzers: Influent Free Chlorine @ 11:15 Grab: 2.68 mg/L Analyzer: 2.62 mg/L Effluent Free Chlorine @ 11:12 Grab: 2.68 mg/L Analyzer: 2.71 mg/L Treated Free Chlorine @ 10:57 Grab: 0.14 mg/L Analyzer: 0.17 mg/L Treated Total Chlorine @ 10:57 Grab: 2.26 mg/L Analyzer: 3.35 mg/L -Entered data into PD sheet -Checked trends | Queensville Wells No. 3 and 4 | 2025-10-20
CENTRAL | October | On site to complete PMs. Notified ROC of relevant alarms. Placed wells in manual off and local. Changed chlorine cylinder pigtail in bank B (W11356619) with Ryan. Changed chlorine cylinders bank B with Ryan as well. -Inspected chlorine system for bank B while changing pigtail with Ryan. Inspected bank A afterwards. Ran both booster pumps and tested chlorinators in local. No issues found. -Placed dechlor in waste drain then backflushed to remove chlorine added through system test -Inspected and performed maintenance on the silicate system. Depressurized raw main to pull and clean both injection points. No issues found. Running wells afterwards in manual to confirm appropriate dosing -Inspected and performed maintenance on well 4 deep well exhaust valve, no issues found -Inspected ammonia system. Performed drawdowns. No setpoints adjusted. Tested flood alarm. No issues found Leaving wells in manual as directed by ROC for feeding NMETHW | Queensville Wells No. 3 and 4 | 2025-10-16
CENTRAL | October | On-site for station check Recordings in PD sheet Changed influent Cl-17 reagent Adjusted influent free analyzer Adjusted treated total analyzer Station ok | Queensville Wells No. 3 and 4 | 2025-10-31
CENTRAL | October | Changed Cl2 pigtail bank B cylinder 4 and changed Cl2 bank B with Alex Bell (OIT/under direction of OIC) - Wells local/off, purged system of Cl2 and primed system following pigtail swap, no known issues. Alex remains on-site. | Queensville Wells No. 3 and 4 | 2025-10-16
CENTRAL | October | On site to complete station check, collect weekly bacti sample (W11298582), collect operational samples (W11290975) and collect Q4 samples (W11247600). Verified analyzers: Influent Free Chlorine @ 9:42 Grab: 2.76 mg/L Analyzer: 2.74 mg/L Effluent Free Chlorine @ 9:40 Grab: 2.68 mg/L Analyzer: 2.60 mg/L Treated Free Chlorine @ 9:26 Grab: 0.13 mg/L Analyzer: 0.16 mg/L Treated Total Chlorine @ 9:26 Grab: 3.15 mg/L Analyzer: 3.15 mg/L -Entered data into PD sheet -Checked trends | Queensville Wells No. 3 and 4 | 2025-10-15
CENTRAL | October | Rotated W3/4 duties to W3 D3 and W4 D2, Wells in remote/auto. | Queensville Wells No. 3 and 4 | 2025-10-15
CENTRAL | October | Received chlorine cylinder delivery 8full 8empty going out. Did station check data into PD sheet. No new issues found. | Queensville Wells No. 3 and 4 | 2025-10-03
CENTRAL | October | On site to complete station check. Influent Free Chlorine @ 13:06 Grab: 2.56 mg/L Analyzer: 2.60 mg/L Effluent Free Chlorine @ 13:14 Grab: 0.17 mg/L Analyzer: 0.21 mg/L Treated Free Chlorine @ 12:51 Grab: 0.01 mg/L Analyzer: 0.05 mg/L Treated Total Chlorine @ 13:01 Grab: 2.17 mg/L Analyzer: 2.04 mg/L Adjusted analyzer based on average of 3 grabs. Analyzer read 2.17 mg/L afterwards. -Data entered into PD sheet -Checked trends | Queensville Wells No. 3 and 4 | 2025-10-06
CENTRAL | October | Collected well 4 raw sample at 12:45 to complete W11278525 weekly bacti sampling. | Queensville Wells No. 3 and 4 | 2025-10-08
CENTRAL | October | On site to perform station check @ to collect weekly bacti samples WO11256318. Swap duties for well 3/4 W3=D2 & W4=D3. - Wells duty active on arrival - Entered readings into Process data sheet & collected samples - Reagents all good- replaced effluent free reagents - Trends all good - Equipment all okay - Dosage all good - No new issues found Influent free Cl @ 12:57pm G: 2.86mg/L A: 2.63mg/L adjusted analyzer to 2.86mg/L based on avg grabs Effluent free Cl @ 12:56pm G: 2.82mg/L A: 2.90mg/L Treated free Cl @ 1:03pm G: 0.18mg/L A: 0.19mg/L Treated total Cl @ 1:03pm G: 3.52mg/L A: 3.51mg/L | Queensville Wells No. 3 and 4 | 2025-10-01
CENTRAL | October | On site to complete station check. Verified analyzers: Influent Free Chlorine @ 11:34 Grab: 2.74 mg/L Analyzer: 2.37 mg/L Adjusted analyzer based on average of 3 grabs. Analyzer read 2.38 mg/L afterwards. Effluent Free Chlorine @ 11:17 Grab: 0.12 mg/L Analyzer: 0.10 mg/L Treated Free Chlorine @ 11:19 Grab: 0.02 mg/L Analyzer: 0.05 mg/L Treated Total Chlorine @ 11:19 Grab: 2.08 mg/L Analyzer: 2.09 mg/L -Entered data into PD sheet -Checked trends -Changed treated total chlorine analyzer reagents | Queensville Wells No. 3 and 4 | 2025-10-10
WEST | October | Pumping Station Check Chlorine Grab (mg/L): Free: 0.05 Total: 1.74 No issues on site | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2025-10-31
WEST | October | Onsite for station check Checked residuals mg/l @1217 Total grab 1.63 Free grab 0.06 | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2025-10-27
WEST | October | Pumping Station Check Chlorine Grab (mg/L): Free: 0.04 Total: 1.41 No issues on site | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2025-10-21
WEST | October | On site for station check and weekly sample W11278701 and quarterly w11247180 West cell @1005 Chlorine Free grab 0.04mg/L Total grab 1.08mg/L Sl1000 Total Chlorine 1.00mg/L FA 0.14mg/L TA 0.33mg/L Mono 1.01mg/L N 0.001mg/L | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2025-10-29
WEST | October | Onsite for station check Checked residuals mg/l @1147 Total grab 1.34 Free grab 0.01 | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2025-10-17
WEST | October | Onsite for station check and to collect weekly micro sample W11316454 Reservoir filling Checked residuals mg/l West cell @0946 Total grab 1.17 Free grab 0.04 Sl1000 Mcl 1.06 F nh3 0.13 T nh3 0.34 No2 0.01 East cell @0949 Total grab 1.07 Free grab 0.05 | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2025-10-22
WEST | October | Onsite for station check Checked residuals mg/l @1147 Total grab 1.54 Free grab 0.04 | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2025-10-10
WEST | October | Pumping Station Check Chlorine Grab (mg/L): Free: 0.05 Total: 1.32 No issues on site | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2025-10-03
WEST | October | Onsite for station check and to collect weekly sample W11256486 East cell @1428 Total grab 1.14 Free grab 0.04 Sl1000 Mcl 1.02 F nh3 0.13 T nh3 0.33 No2 0.000 West cell @1432 Total grab 1.13 Free grab 0.05 | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2025-10-01
WEST | October | weekly sample W11278701 West cell @0950 Chlorine Free grab 0.04mg/L Total grab 1.11mg/L Sl1000 Total Chlorine 0.99mg/L FA 0.14mg/L TA 0.31mg/L Mono 0.90mg/L N 0mg/L | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2025-10-08
CENTRAL | October | On-site for a station and equipment check, no issues found. Heaters turned on Verified analyzers?s, all readings and grabs entered into PWQ sheet. Operational and bacti sample taken | Richmond Hill Bloomington Elevated Tank | 2025-10-29
CENTRAL | October | On-site for housekeeping and general inspection. Changed both sets of reagents in both analyzers. | Richmond Hill Bloomington Elevated Tank | 2025-10-21
CENTRAL | October | On-site for station check and weekly micro sampling (W11316360) work orders. Grab/analyzer results as follows (mg/L): Outlet Free Cl Grab (12:19): 0.04 Outlet Total Cl (12:19): G: 1.52 A: 1.50 Inlet Free Cl Grab (12:27): 0.04 Inlet Total Cl (12:31): G: 1.71 A: 1.73 Collected micro sample from Outlet sample tap. Entered station readings into shared PD excel file. Will continue to monitor Free Ammonia residuals, outlet Grab at 12:20 of 0.13mg/L. Found ARV passing (minor), unable to get valve to seat properly but appears to still be functional, left valve in service and created WO to rebuild or replace valve. No other new issues found. | Richmond Hill Bloomington Elevated Tank | 2025-10-22
CENTRAL | October | Onsite to sample WO# W11364952 F 0.08 T 1.51 | Richmond Hill Bloomington Elevated Tank | 2025-10-15
CENTRAL | October | Station and equipment checked, no issues found Verified analyzers, entered all readings and grabs in to PWQ sheet Weekly bacti, Q4?s and operational samples taken | Richmond Hill Bloomington Elevated Tank | 2025-10-14
CENTRAL | October | Station Check (no issues found) input data to PWQ Verified CL17s (mg/L): 12:33 Outlet: Free: Grab 0.03 Total: Grab 1.46, A 1.45 12:50 Inlet: Free: Grab 0.06 Total: Grab 1.69, A 1.74 12:45 samples #11256392 & operational | Richmond Hill Bloomington Elevated Tank | 2025-10-01
CENTRAL | October | Under the direction of Divy Patel, Worked along side Network Analyst Kevin Wen and Aaron Magsakay, replaced a Network switch to Cisco IE3300 inside a Network Cabinet. Provided 24 VDC power to new switch from existing fuse. Removed the unused iNet Radio. Informed the ROC regarding possible comm fail alarm. There is a trend gap on SCADA between 11:33 AM to 12:00 PM due to this work. After the replacement, checked all the ports and reset the comm alarms. Site back came back to normal. | Richmond Hill Bloomington Elevated Tank | 2025-10-07
CENTRAL | October | -Collected resample YD#11356477 Grab: outlet free=0.05mg/L total=1.52mg/L@14:05 Analyzer: outlet total=1.46mg/L -Checked CL17 reagents - OK | Richmond Hill Bloomington Elevated Tank | 2025-10-10
CENTRAL | October | On-site for assigned work orders, informed ROC. Completed JHSC inspection, air relief valve flush/inspection, heat trace system inspection and recirculation pump inspection - found that pump does not appear to pump when called for, created follow up WO for CMS to address and left pump local/off with repair order tag on pump panel. Started chlorine analyzer maintenance at 10:36, ET filling. Completed PRV inspection/test with dechlorination measures in place. Verified CL17 analyzers following cleaning as follows (mg/L): Inlet Total Cl (11:12): G: 1.79 A: 1.82 Outlet Total Cl (11:17): G: 1.48 A: 1.52 Completed manual/actuated valve exercise, temperature alarm test, ventilation system inspection and general housekeeping. No other new issues found while on-site. | Richmond Hill Bloomington Elevated Tank | 2025-10-02
CENTRAL | October | On-site for station and equipment check, no issues found. Weekly backing sample taken By-weekly operational sample taken with SL1000. Analyzers verified, entered all readings and grabs in to PWQ sheet. Recorded both hydro meters, external and internal (solar panels) and sent readings to J Garnett as requested | Richmond Hill Bloomington Elevated Tank | 2025-10-08
CENTRAL | October | Informed ROC. Performed annual calibration and put instruments in Cal mode while doing the tasks. Devices done were AITs, FIT, PIT, LIT and LCV. Took grabs at the sample line. Inlet total chlorine AIT1=1.77 mg/l Grab=1.76 mg/l Outlet total chlorine AIT2= 1.51 mg/l Grab=1.50mg/l All alarms were cleared after the job. No other issues encountered. | Richmond Hill Bloomington Elevated Tank | 2025-10-15
CENTRAL | October | On-site for station check and weekly micro sampling (W11316360) work orders. Replaced CL17 analyzer reagents for Inlet/Outlet Total Cl analyzers. Grab/analyzer results as follows (mg/L): Outlet Free Cl Grab (14:02): 0.05 Outlet Total Cl (12:19): G: 1.55 A: 1.52 Inlet Free Cl Grab (14:13): 0.05 Inlet Total Cl (14:14): G: 1.71 A: 1.74 ROC rotated pumps at JFPS for Lee Ferguson to complete work on-site at JFPS. Collected micro sample from outlet sample tap. Checked station and equipment, no new issues found. | Richmond Hill Coon's Elevated Tank | 2025-10-22
CENTRAL | October | On-site for general housekeeping. | Richmond Hill Coon's Elevated Tank | 2025-10-21
CENTRAL | October | Assisted Will Mather with weekly micro sampling W11330579 (see previous elog entry) and onsite to investigate outlet check valve. Isolated ET inlet and activated system D1. Observed ET filling via the outlet ~20L/s while ET inlet isolated via LCV and 450mm butterfly valve V3. Returned site to normal operation and created follow up WO to have CMS rebuild the outlet check valve. Informed ROC/Team Lead. No other new issues found while on-site. | Richmond Hill Coon's Elevated Tank | 2025-10-29
CENTRAL | October | On-site for assigned work orders, informed ROC. Completed JHSC inspection, heat trace system inspection, air relief valve inspection, PRV inspection/test with dechlorination measures in place, low temperature alarm test, recirc pump inspection/test, ventilation system inspection, manual valve exercise and actuated valve exercise (JFPS man/off for duration of exercise and returned to auto following work). Outlet Total Cl Grab (09:34): 1.52mg/L Started CL17 analyzer maintenance at 09:37. Verified CL17 analyzers following cleaning as follows (mg/L): Outlet Total Cl (10:16): G: 1.55 A: 1.58 Inlet Total Cl (10:50): G: 1.54 A: 1.38 (adjusted to 1.54 based on average of 3 grabs) Inlet Total Cl CL17 analyzer slow to recover to normal operating range following cleaning, will monitor. Completed housekeeping, no new issues found while on-site. | Richmond Hill Coon's Elevated Tank | 2025-10-03
CENTRAL | October | Station Check (no issues found) input data to PWQ Verified CL17s (mg/L) 14:10 Inlet: Free: Grab 0.03 Total: Grab 1.72, A 1.71 14:00 Outlet: Free: Grab 0.04 Total: Grab 1,72, A 1.75 14:05 Sample #11256392 & operational | Richmond Hill Coon's Elevated Tank | 2025-10-01
CENTRAL | October | On-site for station and equipment check, no issues found. Weekly bacterium sample taken. Bi-weekly operational sample taken with a ph of 8.01 Verified analyzers, entered all readings and grabs I. To PWQ sheet. | Richmond Hill Coon's Elevated Tank | 2025-10-08
CENTRAL | October | Under the direction of Divy Patel, Worked along side Network Analyst Kevin Wen and Aaron Magsakay, replaced a Network switch to Cisco IE3300 inside a Network Cabinet. Provided 24 VDC power to new switch from unused fuse. Informed the ROC regarding possible comm fail alarm. There is a trend gap on SCADA between 2:07 PM to 2:25 PM due to this work. After the replacement, checked all the ports and reset the comm alarms. Site back to normal after installation. | Richmond Hill Coon's Elevated Tank | 2025-10-07
EAST | October | On site for station check Collected grab samples, 12:58 Free Cl 0.06 mg/L Total Cl 1.54 mg/L Inspected station and equipment Completed housekeeping work order Station and equipment okay | Richmond Hill Pugsley Pumping Station | 2025-10-24
EAST | October | On site to complete station check. Cleared outstanding alarms at 13:57. No OOS equipment. Time: 14:00 Grab (mg/l) Free: 0.04 Total: 1.52 Checked site and trends. | Richmond Hill Pugsley Pumping Station | 2025-10-31
EAST | October | On site for station check Recorded observations and chlorine grabs in the shared PWQ sheet Station and equipment okay | Richmond Hill Pugsley Pumping Station | 2025-10-17
EAST | October | On site to complete station check, station running Grab samples, 10:45, in mg/L Free Cl: 0.04 Total Cl: 1.47 Reviewed station trends and inspected equipment, station and equipment okay | Richmond Hill Pugsley Pumping Station | 2025-10-20
EAST | October | On site at 0830 to investigate the generator low fuel alarm. Before starting called ROC to infor them that we will be causing alarms from our work at 0900. We placed generator into manual and disconnected battery. We found that the low fuel float was not correctly set at a proper height and when the fuel gets to 60% in the tank it causes nuisance alarms for a gen warning. We for the time being bypassed the float leaving the low low that will trip the generator into a fault at 20% low fuel. When complete we placed the get back to auto and reconnected battery at 1000. We test ran to confirm operation and cleared alarms. Under direction of oic. | Richmond Hill Pugsley Pumping Station | 2025-10-27
EAST | October | On site to receive diesel fuel delivery Fuel level Start 198.9 cm/ 5563 L Stop 238.5 cm/ 6672 L Finished on site - station okay | Richmond Hill Pugsley Pumping Station | 2025-10-16
EAST | October | On site for station check and preventative maintenance Diesel generator test run, on load Hours Start 369.2 Stop 370.6 Fuel Start 5585 L Stop 5562 L Pumps on for generator run Start 11:58 Stop 13:05 Grabs, 12:50, in mg/L FCl 0.08 TCl 1.37 Exercised pump suction valves Performed pump inspection Tested flood alarm Completed shared PWQ sheet Completed diesel generator semi annual maintenance Completed station check Completed control panel lights inspection Completed JHSC inspection Generator warning alarm outstanding Station and equipment okay | Richmond Hill Pugsley Pumping Station | 2025-10-15
EAST | October | On site for electrical pm. Called ROC, spoke with Christian, to notify them that I will be turning off the pumps in order to open doors for inspection. Call ROC, spoke with Conner to start pump 3 and turn off pump 4 at 10:43 am Call ROC, spoke with Conner to start pump 2 and turn off pump 3 at 11:05 am Called ROC, spoke with Conner to start pump 1 and turn off pump 2 at 11:20 am. Called ROC, spoke with Christian and informed him that we completed our scans and they can return to normal operations at 11:35 am. | Richmond Hill Pugsley Pumping Station | 2025-10-02
EAST | October | Power blip on Sunday morning 5/10/25 around 7:29am for couple hours generator ran pre liter: 5717.75 post liter: 5567.95 no outstanding alarm except gen warning alarm. Informed East Area they will have a look today. When power blip happened pump was running in manual ROC called after the pump interlocked and asked them to run the pump after few mins of gen started and do the same once utility power comes back. No other issues | Richmond Hill Pugsley Pumping Station | 2025-10-06
EAST | October | On site to check station and equipment. Pump 1 is man/on due to distribution valving arrangement. Station readings and chlorine grabs are in PWQ sheet. Reviewed trends, no concerns. Generator warning alarm is outstanding to low fuel level. Fuel top up is in the que. | Richmond Hill Pugsley Pumping Station | 2025-10-10
WEST | October | On site for station check and W11247740 Q4 Water Samples W11330635 Micro Sampling (without HPC) Switched KMNO4 pump duty from pump 1 to 2 for dosing calculations. Check trends- All okay Verified Analyzers. Reservoir- Grab Total Cl2:3.78 mg/L, Analyzer- 3.77 mg/L Post filter- Grab Total Cl2:2.40 mg/L, Analyzer- 2.41 mg/L 13:20-HighLift- Grab free:0.02 mg/L, Grab Total Cl2:3.28 mg/L, Analyzer- 3.30 mg/L conduced inhouse lab. Entered values in PWQ sheet. Equipment okay. | Schomberg Water Treatment Plant & Wells 2-4 | 2025-10-29
WEST | October | -on site to complete station check and lab - plant duty active, activated high lift duty -wells 2 and 3 in duty - KMnO4 pump 1 running at 20.9%, 62 psi - chlorinator 1 74% open, df 140%, 0.69 kg/hr, vac = -660 mbar - chlorinator 2 33% open, df 164%, 0.32 kg/hr, vac = -830 mbar - recorded data in PWQ sheet - checked equipment - CL17 reagents ok - reviewed trends - no issues found -completed wells 2,3,4 station checks -verified analyzers: 09:42 - high lift treated water TCL analyzer = 3.31 mg/L 09:42 - high lift treated water grab: FCL = 0.00 mg/L TCL = 3.32 mg/L Mono = 3.08 mg/L 09:56 - reservoir TCL analyzer = 3.72 mg/L 09:56 - reservoir grab: TCL = 3.68 mg/L Mono = 3.27 mg/L 10:05 - post filter TCL analyzer = 2.44 mg/L 10:05 - post filter grab: TCL = 2.40 mg/L -filled KMnO4 tank #2 15.9 cm to 82.0 cm -cleaned high lift turbidimeter vial -completed lab, results in PWQ sheet | Schomberg Water Treatment Plant & Wells 2-4 | 2025-10-20
WEST | October | Switched KMNO4 pump duty from pump 2 to pump 1 for dosing calculations. | Schomberg Water Treatment Plant & Wells 2-4 | 2025-10-28
WEST | October | Cleaned KMNO4 containment area. | Schomberg Water Treatment Plant & Wells 2-4 | 2025-10-23
WEST | October | Completed the following work orders informed ROC before works being done. W11311644 SHTP W2 JHSC Health and Safety Inspection W11312561 SHTP W2, Actuated Valve, Exercise W11312550 SHTP W2, High/Low Temperature Alarm, Test Changed Cl2 Cylinders with J. Muzzin | Schomberg Water Treatment Plant & Wells 2-4 | 2025-10-21
WEST | October | On site for Station Check Check trends- All okay Verified Analyzers. Reservoir- Grab Total Cl2:3.80 mg/L, Analyzer- 3.84 mg/L Post filter- Grab Total Cl2:2.40 mg/L, Analyzer- 2.41 mg/L Highlift- Grab Total Cl2:3.39 mg/L, Analyzer- 3.33 mg/L Reagents all good. Conducted in house lab analysis. Entered values in PWQ sheet Equipment okay. | Schomberg Water Treatment Plant & Wells 2-4 | 2025-10-17
WEST | October | On site for Station Checks Check trends- All okay Topped up KMNO4 Tank 1- 25.7 cm/ 94.9 cm Verified Analyzers. Reservoir- Grab Total Cl2:3.88 mg/L, Analyzer- 3.82 mg/L Post filter- Grab Total Cl2:2.30 mg/L, Analyzer- 2.33 mg/L Highlift- Grab Total Cl2:3.32 mg/L, Analyzer- 3.26 mg/L Conducted in house lab analysis. Entered values in PWQ sheet Equipment okay. | Schomberg Water Treatment Plant & Wells 2-4 | 2025-10-31
WEST | October | On site for Station Check, weekly micro samples W11316482 W11313066 SHTP W2, eye wash, cleaned and solution replaced. Check trends- All okay Verified Analyzers. Reservoir- Grab Total Cl2:3.72 mg/L, Analyzer- 3.82 mg/L Post filter- Grab Total Cl2:2.32 mg/L, Analyzer- 2.34 mg/L 12:55-HighLift- Grab free:0.00 mg/L, Grab Total Cl2:3.34 mg/L, Analyzer- 3.38 mg/L conduced inhouse lab. Entered values in PWQ sheet Equipment okay. | Schomberg Water Treatment Plant & Wells 2-4 | 2025-10-22
WEST | October | Check trends- All okay W11325527 SHTP, Schomberg WTP Turbidity Analyzer cleaned and calibrated W11325720 SHTP, Rotate reservoir cells and sample pump lines Rotated from South to North Cell, Sample pump 1 to 2 Topped up KMNO4 Tank 2- 15.67 cm/81.71 cm Troubleshooted KMNO4 pumps with C. Warnica changed rollers for both pumps, changed pump 2 tube. Changed max flow setpoints of pumps based on draw down readings. Pump 1 from 400 mg/L to 460 mg/L pump 2 from 400 mg/L to 412 mg/L Verified Analyzers. Reservoir- Grab Total Cl2:3.80 mg/L, Analyzer- 3.84 mg/L Post filter- Grab Total Cl2:2.34 mg/L, Analyzer- 2.42 mg/L HighLift- Grab free:0.00 mg/L, Grab Total Cl2:3.20 mg/L, Analyzer- 3.15 mg/L Entered values in PWQ sheet Equipment okay. | Schomberg Water Treatment Plant & Wells 2-4 | 2025-10-27
WEST | October | Onsite to run fire pumps with king township flushing hydrants Placed high lift pumps 12&5 in local When tower outlet flow increased opened valve and then started fire pump 3 gradually increased valve position until approximately 100l/s Tapered valve closed and turned off pump Repeating the sequence with pump 4 Placed high lifts back to auto Drained kmno tanks mad cleaned Filled them eachwith 62cm When plant was running Caused fault on kmno pump1 while pump2 was interlocked causing plant to interlock. Restarted plant but fire storage low alarm came in as well as reservoir low Manipulated plant to run high lifts and fill reservoir, eventually stopping high lift duty . Reduced high lift start set point from 15 to 10% Remotely cleared fire storage low alarm and changed high lift start back to 15% | Schomberg Water Treatment Plant & Wells 2-4 | 2025-10-21
WEST | October | On site for Station Checks Check trends- All okay Cleaned filter turbidity meter vials to lower the turbidity values. Verified Analyzers. Reservoir- Grab Total Cl2:3.84 mg/L, Analyzer- 3.77 mg/L Post filter- Grab Total Cl2:2.34 mg/L, Analyzer- 2.40 mg/L Highlift- Grab Total Cl2:3.15 mg/L, Analyzer- 3.13 mg/L Reservoir Reagents changed. Conducted in house lab analysis. Entered values in PWQ sheet Equipment okay. | Schomberg Water Treatment Plant & Wells 2-4 | 2025-10-24
WEST | October | On site for scheduled PM work orders. Informed ROC about the works being done. Topped up KMNO4 Tank 1-15.43cm/82.21cm Completed the following Workorders W11272193 SHTP, Filters 1-3, Turbidity Analyzer TU5300, Maintenance and Calibration W11274735 SHTP_UVD, UVT lens cleaning and unit flush W11272870 SHTP, KMnO4 Injection Point Cleaning. W11282300 SHTP, Fire Pumps and Motors, Inspection W11281075 SHTP, UV Reactors, Sensor Check -completed sensor check on UV#1 and UV#3 -started UV#2 in local with cooling valves open - no issues, all sensors passed W11294543 SHTP, Dehumidifier Cleaning & Inspection W11294464 SHTP, Electric Actuated Valves Inspection W11294481 SHTP, Exhaust Fan Inspection W11294552 SHTP, Dehumidifier Inspection W11295415 SHTP, Pump and Motor Inspection W11294508 SHTP, Check Valves Inspection W11294524 SHTP, Valves Exercise, Schomberg WTP W3&4 W11312580 SHTP, Low/High Temperature Alarm, Test -activated plant duty - no issues, site back to normal operation | Schomberg Water Treatment Plant & Wells 2-4 | 2025-10-09
WEST | October | Onsite for the following work order. Informed ROC about the works being done. W11259672 SHTP, JHSC Health and Safety Inspection W11261479, SHTP, Rotate chlorinator 4 duty put chlorinator 1 as raw water chlorinator. Topped up KMNO4 tank 1- 15.40cm/81.66cm | Schomberg Water Treatment Plant & Wells 2-4 | 2025-10-02
WEST | October | Details: On site for Station Check Check trends- All okay Verified Analyzers. Reservoir- Grab Total Cl2:3.90 mg/L, Analyzer- 3.92 mg/L Post filter- Grab Total Cl2:2.44 mg/L, Analyzer- 2.44 mg/L Highlift- Grab Total Cl2:3.46 mg/L, Analyzer- 3.44 mg/L Received Cl2 delivery- 12 full received / 12 empty returned Entered values in PWQ sheet Equipment okay. | Schomberg Water Treatment Plant & Wells 2-4 | 2025-10-10
WEST | October | On site for station check and weekly bacti sampling W11256448, iron and manganese raw and filter samples W11215710, W11256610 check trends, all okay. Manually initiated Filter 3 backwash, vial cleaned and calibrated Filter 3 Turbidity analyzer to reduce to Turbidity value. 12:30 -Highlift sample Grab Free Cl2-0.04 mg/l Grab total Cl2- 3.40 mg/l Verified analyzers Reagents all good Conducted in-house lab analysis Entered all values in pwq sheet equipment okay | Schomberg Water Treatment Plant & Wells 2-4 | 2025-10-01
WEST | October | On site for Station Check, weekly micro samples W112988712 Check trends- All okay W11291357 SHTP, Schomberg WTP Turbidity Analyzer W11291546 SHTP, Rotate reservoir cells and sample pump lines Rotated from North to South Cell, Sample pump 2 to 1 Verified Analyzers. Reservoir- Grab Total Cl2:3.80 mg/L, Analyzer- 3.79 mg/L Post filter- Grab Total Cl2:2.42 mg/L, Analyzer- 2.47 mg/L 11:20-HighLift- Grab free:0.02 mg/L, Grab Total Cl2:3.36 mg/L, Analyzer- 3.34 mg/L conduced inhouse lab. Entered values in PWQ sheet Equipment okay. | Schomberg Water Treatment Plant & Wells 2-4 | 2025-10-14
WEST | October | On site for Station Check Check trends- All okay W11270566 - Schomberg WTP Turbidity Analyzer Verified Analyzers. Reservoir- Grab Total Cl2:3.94 mg/L, Analyzer- 3.86 mg/L Post filter- Grab Total Cl2:2.36 mg/L, Analyzer- 2.45 mg/L Highlift- Grab Total Cl2:3.24 mg/L, Analyzer- 3.23 mg/L Highlift Analyzer Reagent replaced. Topped up KMNO4 Tank 2- 15.52cm/82.96cm Entered values in PWQ sheet Equipment okay. | Schomberg Water Treatment Plant & Wells 2-4 | 2025-10-06
WEST | October | Test backflow preventers 5 passed just 8 inch one left | Schomberg Water Treatment Plant & Wells 2-4 | 2025-10-10
WEST | October | -on site to respond to post UV chlorine residual LOLO and fault alarms -found sample pump #2 discharge line leaking causing low flow to analyzer -replaced pump lines -verified analyzer: 11:22 - analyzer = 3.83 mg/L Grabs = 4.00/3.96/4.10 mg/L 11:33 - adjusted analyzer to 4.02 mg/L based on average of 3 grabs -reduced chlorinator #2 dosage factor 178 to 175 % -will monitor -filled KMnO4 tank #2 84 L to 379 L | Schomberg Water Treatment Plant & Wells 2-4 | 2025-10-11
WEST | October | Onsite for the following work orders Informed ROC about the works being done. Changed cylinders with T.Hudson W11259060 SHTP, Chlorine Cylinder Emergency Repair Kit Inspection W11259106 SHTP, Chlorine Leak Detector, Test W11261364 SHTP, Chemical System Inspection - Chlorine W11272677 SHTP, Compressed Air System, Inspection Air compressor 1 blasting out air from the filter unit. unit turned off, closed bottom left valve to the compressor tank. informed team lead. CMU created W11344717 W11273829 SHTP, CL-17sc Analyzer, Maintenance W11272186 SHTP, Backwash Sump Tank System, Inspection W11292859 SHTP, Diesel Generator Test Run Pre check Battery okay- 26 V Coolant- Okay Oil - Okay Before Start Start time- 10:35 Run time- 530.6 Fuel level Tank 1- 1882L/96.6cm Tank 2- 1877L/96.4cm After Stop Stop time- 11:55 Run time- 532.1 Fuel level Tank 1-1864L/95.7cm Tank 2- 1857L/95.3cm | Schomberg Water Treatment Plant & Wells 2-4 | 2025-10-07
WEST | October | On site for Station Check Check trends- All okay attended- W11317689 TSSA Upgrade Project - Operator Training for Schomberg WTP Verified Analyzers. Reservoir- Grab Total Cl2:3.74 mg/L, Analyzer- 3.78 mg/L Post filter- Grab Total Cl2:2.46 mg/L, Analyzer- 2.50 mg/L Highlift- Grab Total Cl2:3.35 mg/L, Analyzer- 3.36 mg/L Reagents All good. Entared values in PWQ sheet Equipment okay. | Schomberg Water Treatment Plant & Wells 2-4 | 2025-10-03
WEST | October | Test backflow preventer 8 inch passed | Schomberg Water Treatment Plant & Wells 2-4 | 2025-10-14
WEST | September | Entry made to capture site hydro power failure alarm triggered at 0415. Appears to have been a power dip that caused plant shutdown. No UV alarms appear to have been triggered, no low dose during shutdown. | Schomberg Water Treatment Plant & Wells 2-4 | 2025-09-16
WEST | October | On site for Station Check, weekly micro samples W11278729, NDMA samples W11247912 Check trends- All okay Verified Analyzers. Reservoir- Grab Total Cl2:3.80 mg/L, Analyzer- 3.73 mg/L Post filter- Grab Total Cl2:2.40 mg/L, Analyzer- 2.46 mg/L 11:45-HighLift- Grab free:0.02 mg/L, Grab Total Cl2:3.46 mg/L, Analyzer- 3.51 mg/L conduced inhouse lab. Entered values in PWQ sheet Equipment okay. | Schomberg Water Treatment Plant & Wells 2-4 | 2025-10-08
WEST | October | Onsite for Scheduled PM work orders. Changed post filter Cl2 analyzer Reagents Topped up KMNO4 Tank 1- 15.69 cm/82.93 cm Completed the following work orders. W11272918 SHTP, Transfer Pump and Motor Inspection. W11273095 SHTP, Transfer Pump Isolation Valves, Exercise. W11273083 SHTP, Transfer Pump Air Relief Valves, Inspection. W11282211 SHTP, High Lift Discharge Check Valves, Service and Inspection. W11282229 SHTP, High Lift Manual Valves, Exercise. W11282248 SHTP, High Lift Actuated Valves, Exercise and Inspection. W11282265 SHTP, High Lift Discharge Pressure Relief Valve, Inspection and Test. W11282284 SHTP, High Lift Pumps, Inspection. W11281767 SHTP, Valve, Butterfly, Surge Tank Isolation, Exercise. | Schomberg Water Treatment Plant & Wells 2-4 | 2025-10-15
WEST | October | Onsite to collect resample of Q4 ndma @1011 Total grab 1.78 Free grab 0.03 | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2025-10-28
WEST | October | Onsite for station check Duty not active Pre @1336 TCL analyzer 1.62 grab 1.60 Fcl analyzer 0.02 grab 0.04 Mcl analyzer 1.58 grab 1.56 F nh3 analyzer 0.10 grab 0.07 T nh3 analyzer 0.45 grab 0.37 Post @1345 TCL analyzer 1.62 grab 1.61 Fcl analyzer 0.02 grab 0.02 Mcl analyzer 1.77 grab 1.71 F nh3 analyzer 0.04 grab 0.09 T nh3 analyzer 0.44 grab 0.43 Reagents ok | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2025-10-17
WEST | October | On site for station check and to collect weekly bacti sample w11330673 and quarterly sample w11247194 Reservoir @1100 am North Cell Sample Tap: Total: 1.61mg/L Free: 0.05mg/L SL1000 TCL 1.67mg/L Mono 1.79mg/L FA 0.07mg/L TA 0.43mg/L West Cell Sample Tap: Total: 1.88mg/L Free: 0.07mg/L South Cell Sample Tap: Total: 1.88mg/L Free: 0.06mg/L Rechlor @11:35 Pre inj (mg/L) Fcl Analyzer: 0.00; Grab: 0.07 TCL Analyzer: 1.68; Grab: 1.55 Fa Analyzer: 0.08; Grab: 0.11 Ta Analyzer: 0.42; Grab: 0.41 Mcl Analyzer: 1.59; Grab: 1.53 Post inj Fcl Analyzer: 0.02; Grab: 0.05 TCL Analyzer: 2.04; Grab: 2.08 Fa Analyzer: 0.03; Grab: 0.10 Ta Analyzer: 0.44; Grab: 0.44 Mcl Analyzer: 1.90; Grab: 1.74 Adjusted post total depolox from 1.78-2.08mg/L after multiple grabs | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2025-10-29
WEST | October | In to complete overhaul of chlorine gas system. Notified ROC of alarms associated with PM work. Purged chlorine system and replaced regulators ejectors, manifold pigtails, PE tubing, ball valves. Reinstated PVC cl2 gas tubing with new Asahi chemline ball valves. Cut out and replaced Ipex ball valves to standardize. Vacuum tests good. Ran BVPS to activate and test chlorine system from approx 1300 to 1416. No issues. Spare 500ppd regulators on site in case of later issues. Original gas tubing (5/8) left on site temporarily in case of emergency use. | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2025-10-28
WEST | October | Onsite for station check Rechlor Duty not active Pre @1312 TCL analyzer 1.72 grab 1.70 Fcl analyzer 0.01 grab 0.01 F nh3 analyzer 0.11 grab 0.18 T nh3 analyzer 0.46 grab 0.47 Mcl analyzer 1.58 grab 1.51 Post @1322 TCL analyzer 1.92 grab 1.90 Fcl analyzer 0.02 grab 0.03 F nh3 analyzer 0.04 grab 0.08 T nh3 analyzer 0.41 grab 0.45 Mcl analyzer 2.05 grab 1.88 | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2025-10-27
WEST | October | Onsite for station check Rechlor Duty not active Pre @1338 TCL analyzer 1.67 grab 1.68 Fcl analyzer 0.01 grab 0.04 F nh3 analyzer 0.12 grab 0.12 T nh3 analyzer 0.47 grab 0.43 Mcl analyzer 1.65 grab 1.53 Post @1349 TCL analyzer 1.87 grab 1.92 Fcl analyzer 0.02 grab 0.01 F nh3 analyzer 0.02 grab 0.07 T nh3 analyzer 0.42 grab 0.43 Mcl analyzer 1.97 grab 1.86 | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2025-10-24
WEST | October | On site for station check Rechlor Pre inj (mg/L) Fcl Analyzer: 0.00; Grab: 0.04 TCL Analyzer: 1.74; Grab: 1.93 Fa Analyzer: 0.08; Grab: 0.10 Ta Analyzer: 0.44; Grab: 0.41 Mcl Analyzer: 1.66; Grab: 1.61 Post inj Fcl Analyzer: 0.02; Grab: 0.04 TCL Analyzer: 2.29; Grab: 2.32 Fa Analyzer: 0.02; Grab: 0.06 Ta Analyzer: 0.44; Grab: 0.44 Mcl Analyzer: 2.12; Grab: 1.94 | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2025-10-31
WEST | October | Onsite for station check and to collect weekly micro sample W11316454 Res North cell @1059 Total grab 1.80 Free grab 0.03 Sl1000 Mcl 1.70 F nh3 0.11 T nh3 0.45 No2 0.000 South cell @1104 Total grab 1.91 Free grab 0.05 West cell @1106 Total grab 1.89 Free grab 0.05 Rechlor Duty not active Pre @1123 TCL analyzer 1.76 grab 1.77 Fcl analyzer 0.01 grab 0.05 F nh3 analyzer 0.07 grab 0.08 T nh3 analyzer 0.46 grab 0.41 Mcl analyzer 1.75 grab 1.68 Post @1133 TCL analyzer 1.86 grab 1.86 Fcl analyzer 0.02 grab 0.03 F nh3 analyzer 0.04 grab 0.12 T nh3 analyzer 0.43 grab 0.45 Mcl analyzer 1.97 grab 1.71 | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2025-10-22
WEST | October | Onsite for station check Duty not active @1356 Pre TCL analyzer 1.55 grab 1.63 Fcl analyzer 0.02 grab 0.03 Mcl analyzer 1.50 grab 1.49 F nh3 analyzer 0.10 grab 0.12 T nh3 analyzer 0.46 grab 0.42 @1406 TCL analyzer 1.63 grab 1.72 Fcl analyzer 0.02 grab 0.03 Mcl analyzer 1.78 grab 1.63 F nh3 analyzer 0.04 grab 0.11 T nh3 analyzer 0.43 grab 0.43 Topped up ammonia tank 2 | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2025-10-10
WEST | October | Checked residuals mg/l Duty not active Pre TCL analyzer 1.59 grab 1.58 Fcl analyzer 0.03 grab 0.02 Mcl analyzer 1.52 grab 1.45 Tnh3 analyzer 0.44 grab 0.37 F nh3 analyzer 0.11 grab 0.09 Post @1253 TCL analyzer 1.87 grab 1.86 Fcl analyzer 0.02 grab 0.04 Mcl analyzer 1.96 grab 1.86 Tnh3 analyzer 0.47 grab 0.44 F nh3 analyzer 0.03 grab 0.08 Topped up distilled for chemscan Reagents ok Topped up ammonia tank 1 | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2025-10-03
WEST | October | Onsite for station check and to collect weekly micro sample w11289750 Reservoir grabs North @1336 Total grab 1.74 Free grab 0.06 Sl1000 Mcl 1.63 No2 0.000 T nh3 0.44 F nh3 0.12 South @1338 Total grab 1.82 Free grab 0.07 West cell @1342 Total grab 1.84 Free grab 0.06 Rechlor Pre @1351 TCL analyzer 1.66 grab 1.72 Fcl analyzer 0.02 grab 0.04 Mcl analyzer 1.61 grab 1.52 F nh3 analyzer 0.10 grab 0.11 T nh3 analyzer 0.45 grab 0.41 Post @1406 TCL analyzer 1.88 grab 1.91 Fcl analyzer 0.02 grab 0.00 Mcl analyzer 1.98 grab 1.85 F nh3 analyzer 0.02 grab 0.06 T nh3 analyzer 0.44 grab 0.43 Reagents ok | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2025-10-14
WEST | October | On site for station check and to collect weekly back same w11278701 and NDMA quarterly sample w11247940 Reservoir @10:40 am North Cell Sample Tap: Total: 1.88 mg/L Free: 0.06 mg/L Rechlor Pre inj (mg/L) Fcl Analyzer: 0.03; Grab: 0.04 TCL Analyzer: 1.65; Grab: 1.58 Fa Analyzer: 0.12; Grab: 0.10 Ta Analyzer: 0.47; Grab: 0.41 Mcl Analyzer: 1.59; Grab: 1.58 Post inj Fcl Analyzer: 0.02; Grab: 0.04 TCL Analyzer: 1.91; Grab: 1.91 Fa Analyzer: 0.03; Grab: 0.05 Ta Analyzer: 0.49; Grab: 0.51 Mcl Analyzer: 2.00; Grab: 1.86 No issues on site - reagents and chemicals all ok | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2025-10-08
WEST | October | Changed tubing element in ammonia pump 1 Ran to sight glass @50% 230 ml/min Changed tubing element in ammonia pump 1 Ran to sight glass @50% 220 ml/min Did monthly maintained on depolox cl2 analyzers Electrolyte, grit and reagents ok Grabs Pre Total analyzer 1.80 grab 1.86 Free analyzer 0.03 grab 0.03 Post Total analyzer 2.11 grab 2.18 Free analyzer 0.03 grab 0.05 Completed jhsc no issues | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2025-10-07
LINEAR | October | Attending site to check FIT due to suspected issue with FIT (W11390468). Operations suspects that there is flow but it is not registering on the flowmeter. Transmitter passed functional verification. Will arrange to inspect the flowtube in the chamber next week. Associated alarms were cleared. ROC was notified before and after work. | Linear Water System | 2025-10-23
LINEAR | October | AUMCBS Onsite for annual calibrations Informed ROC Used cal mode on scada Cannot enter chamber due to trees/bushes restricting access Focused on FIT. FIT failed verification on insulation. Need to enter chamber to troubleshoot Will return after trees are cut and removed Informed ROC and left site | Linear Water System | 2025-10-20
LINEAR | October | AUMCBS & VNMCBA Informed ROC. Onsite to perform annual calibration. Put the devices in calibration mode. Devices were done as below: MC_PITs and MC_FITs. Put the devices back in service. All the related alarms were cleared. No issues. Informed ROC and left the site | Linear Water System | 2025-10-29
LINEAR | October | Isolated water main on Nashville in Vaughan to change out a mainline valve and air valve. Upon completion of the work the main was recharged and flushed. A residual of Total - 1.97 mg/l and Free - 0.06 mg/l was achieved. The watermain was put back in service. | Linear Water System | 2025-10-28
LINEAR | October | Water Access Point, VAC, 61-01A Air valve replacement. Chlorine residual after new AV Total: 1.73 mg/l Free: 0.06 mg/l | Linear Water System | 2025-10-16
LINEAR | October | Inspected AV?s replacement. Took residual Free - 0.07 mg/l Total - 1.25 mg/l | Linear Water System | 2025-10-21
LINEAR | October | Isolated a portion of the watermain on Whisper Lane from the Whisper Lane pumping station to English Daisy court. Supporting Capital project work of installation of a new mainline valve. Upon completion of installation the main was filled and flushed and a residual was taken Free - 0.03 mg/l Total - 1.79 mg/l and the watermain was put back in service. | Linear Water System | 2025-10-22
LINEAR | October | AUVCAD Onsite for annual calibrations Informed ROC Created CSE permit Used cal mode on scada during the work Instruments calibrated: PITs, FIT and FCV Cleared associated alarms Informed ROC and closed CSE No issues Left site | Linear Water System | 2025-10-23
LINEAR | October | Failed DV in Chamber 57-02 on Elgin Mills and Edward in Richmond Hill (400 mm DI Pipe). Main was isolated on October 1st for repair of DV. New valve installed on October 3, but isolation zone was expanded to the west Chamber 59-02 to accommodate the replacement of a leaking Main Line Valve in Chamber 59-01 (Yorkland / Elgin Mills). A ML to the south on chamber 52-20 on Enford and a ML on the 600mm at chamber T1231-04 was closed as well. | Linear Water System | 2025-10-06
LINEAR | October | Watermain isolated from chamber number 3490133-11D to 3490133-11A for few hours for the Air Valve mods work. We closed West mainline at 3490133-11D and east mainline at 3490133-11A. | Linear Water System | 2025-10-09
LINEAR | October | AUMCBS-intermittent flow forward error shown in SCADA but there were no errors in the actual transmitter. Asked PCS Artour and it did not tell any errors as well in Hart communication. Thus, not able to conclude what causes it. Replaced the flow transmitter and configured it. Put back in service. We will keep on monitoring it. | Linear Water System | 2025-10-07
LINEAR | October | Isolated a portion of PD5 water main at Langstaff and Hwy 27 from Hwy27 to Line Rd. Assisted with air valve and isolation valve replacement. After replacing the equipment main was put back in to service and the COV flushed the line. Took a residual Free-0.03 mg/l Total-2.09 mg/l | Linear Water System | 2025-10-07
LINEAR | October | Recharged watermain on Elgin Mills from Yonge to Edward. Flushed. Took residuals. Free - 0.03 mg/l Total -1.58 mg/l Put watermain back in service. | Linear Water System | 2025-10-09
LINEAR | October | EGMCRW Informed ROC. Onsite to perform annual calibrations. Put the devices in calibration mode and performed annual calibrations. Put everything back in service. All the related alarms were cleared. No issues. Informed ROC and left the site | Linear Water System | 2025-10-14
WW-NORTH | October | Attended for testing of newly installed pinch valve 2 Opened isolation valve and placed pinch valve 2 in duty Observed valve sequence - valve faulted on overtorque on shut down Returned pinch valve 1 back to duty 1 Dave (electrical) came to site and made some adjustments and after running the duty and two pumping cycles passed with no alarms Placed pinch valve 2 back into duty. | Newmarket Pinch Valves | 2025-10-21
WW-NORTH | October | On site to replace FM2 MV1 pinch valve actuator. Removed old actuator, installed new replacement. Actuator wiring needs to be completed and the actuator needs to be programmed and tested. | Newmarket Pinch Valves | 2025-10-16
WW-NORTH | October | On site to test pinch valve #2 with operations, after completing the wiring and installation. Adjusted close and open torque to 95%. Tested in auto and observed two cycles. Valve is good and back in service. | Newmarket Pinch Valves | 2025-10-21
WW-NORTH | October | Switched duties from pinch valve 1 to pinch valve 2 to flush # 2 before it is isolated for repair Tuesday | Newmarket Pinch Valves | 2025-10-09
WW-NORTH | October | Attended for scheduled work orders Inspected pinch valves - returned ROC valve to service and isolated EGSSSC valve for next week's work, opened valve to drain and then left local closed Tested sump pit high level alarm Flushed air relief valves. | Newmarket Pinch Valves | 2025-10-09
WW-WEST | October | Enabled RAS timer at Set auto wasting for 8 batches, between 09:00 and 11:00 for a total of 20 m3 per train. Completed small lab. All numbers good, but ammonia about 1 mg/L all around. Partook in the fine air balancing act to increase and even out DO on the three passes of train 2. Added 2 bags soda ash to train 2. Picked rags from tank surface and valve stem. | Nobleton Water Resource Recovery Facility | 2025-10-19
WW-WEST | October | Completed the daily lab work and station check Closed the clarifier inlet gates to continue filling aer tank 2 Decanted and then emptied the sludge thickening tank Batch wasted 10m3 from each clarifier added 3 bags of soda ash to aeration tank 1 Test ran the generator Completed the JHSC inspection Once aer tank 2 was about 3/4 full, opened the RAS valve to tank 2 Closed RAS valve to tank 1 Opened the aer inlet gate to tank 2 and closed the inlet gate to tank 1 in to begin draining tank 1 Opened the clarifier inlet gates Placed submersible pumps into tank 1 to empty into tank 2 Placed the DO analyzer for tank 2 back in the tank Placed tank 2 back in service and took tank 1 out of service on SCADA Changed DO analyzer duty selection to tank 2 | Nobleton Water Resource Recovery Facility | 2025-10-16
WW-WEST | October | In to Complete Reg. Sampling and Scheduled WOs. Notified ROC. Activated Submersible Pump in Aer. Tank #1, Transferring Solids to Aer. Tank #2 Inlet. Added Soda Ash to Both Aer. Tanks ?> 1 Bag Each. Deactivated Submersible Pump Transferring Solids from Aer. Tank #1 to Tank #2. Opened RAS Valve #4 and Closed RAS Valve #3 in Manual. Placed RAS Pumps #2 and 3 in Manual, Manual Speed @ 0%. Returning Solids from Clarifier #1 to Aer. Tank #2 for Seeding and Balancing Purposes. Sludge Transfer Valve Manual Open, Transferred Thickened Sludge. Transfer Valve Returned to Manual Closed. Opened RAS Valve #3 and Closed RAS Valve #4 in Manual. Returned RAS Pumps #1 and 2 to Auto. Cleared Associated Alarms. Placed Scum Pump #1 in Manual On. Completed Clarifier Scum Tank Drawdown. Returned Scum Pump #1 to Auto and Service. Opened Aer. Tank Outlet Interconnect Valve. Closed Aer. Tank #1 Effluent Gate Valve. Placed RAS Valve #1 in Manual, Manual Speed @ 100% for Clarifier #1 Drawdown Process in Preparation for CPD Work. Hosed and Flushed Clarifiers #1 and 2 Weirs, Launders and Scum Troughs. Placed Clarifier #1 Drive Rake in Manual Off. RAS Pump #2 Manual Off. RAS Valve #4 Manual Open. Opened RAS Valve #2 and Closed RAS Valve #1 in Manual. Placed RAS Pump #3 in Manual On, Manual Speed @ 50%, Supplying Aer. Tanks #1 and 2. | Nobleton Water Resource Recovery Facility | 2025-10-28
WW-WEST | October | Completed the station check and daily lab work Added 3 bags of soda ash to aeration tank 2 Cleaned the fe/uv channel Inspected the uv system Inspected the facility outfall | Nobleton Water Resource Recovery Facility | 2025-10-21
WW-WEST | October | DO levels running high, switch aeration blowers from manual to auto. Blower 1 in duty 1/running. | Nobleton Water Resource Recovery Facility | 2025-10-27
WW-WEST | October | Aeration basin 1 DO was found to be low (sub 0.20mg/L) since Friday Oct 24th at 5:30PM. Increased air flow to side 1 and decreased side 2. Have blowers 1 & 2 running in manual to establish DO. Will allow DO to reach homeostasis before making any more adjustments. Manual DO probe was reading approximately 0.5mg/L higher than online probe. DO currently at 1.72mg/L and climbing. Added 1 bag of soda ash to each aeration basin. | Nobleton Water Resource Recovery Facility | 2025-10-26
WW-WEST | October | Completed the station check and daily lab work Continued pumping aer tank 1 into 2 Added 4 bags of soda ash to aeration tank tank 2 Received alum delivery, bringing the level up to 3.5m Removed solids from aer tank 2 | Nobleton Water Resource Recovery Facility | 2025-10-17
WW-WEST | October | Removed floating solids from aeration tank. Bled condensation from air lines. | Nobleton Water Resource Recovery Facility | 2025-10-22
WW-WEST | October | Complete small lab due to low do occurrence in aeration basin 1. Final pH: 7.19 @ 17.0 degrees Celsius Final ammonia is unmeasurable with low range kit (too elevated for range). Plant is not nitrifying. Test clarifier 2 for ammonia to determine if aeration tank 2 is nitrifying. Clarifier 2 ammonia is 0.025ppm. Set up 2 submersible pumps in aeration tank 2 to pump into aeration tank 1 to reseed the tank. Also valves RAS from clarifier 2 to aeration 1 (will do this for approx 2hrs). Submersible pumps can remain overnight. DO in tank 1: 2.43mg/L and tank 2: 6.64mg/L. Unsure if the do is balanced or not with valving because oxygen demand is quite high on tank 1 side. Lots of air flow. There could also be some solids imbalances with the aeration inlet gates recently adjusted which may be effecting the oxygen demand. Will reestablish notification before fine tuning solids and air. Notified management on call of issue as well as area supervisor. Also informed ROC to call for any low DO alarms. This is reflected in the SCADA review as well. | Nobleton Water Resource Recovery Facility | 2025-10-26
WW-WEST | October | In to Complete Scheduled WOs. Placed RAS Pump #3 in Manual Off. Closed RAS Valve #3 in Manual. Activated RAS Pump #1 in Manual, Manual Speed @ 100% for Clarifier #1 Drawdown. Returned RAS Pump #3 to Auto. Enabled Batch Waste Set-point. RAS Pump #3 Auto Off in Preparation for Wasting @ 09:00. WAS Valve #3 Manual Open. Assembled and Installed Megalift into Filter #3, Transferring Sand from Filter #3 to Filter #2 for Inspection. Added Soda Ash to Both Aer. Tanks ?> 1 Bag Each. Clarifier #1 Drawdown Complete. RAS Pump #1 Manual Off. WAS Pump #2 Manual On and Off Intermittently for Wasting. Wasting Complete, WAS Valve #3 Manual Closed. Reset Batch Wasting Set-point. Wasted 30 m3 from Clarifier #2. RAS Valve #3 Manual Open. RAS Pump #3 in Manual On, Manual Speed @ 50%, Supplying Aer. Tanks #1 and 2. Deactivated Filter #3 Megalift Sand Transfer Process. | Nobleton Water Resource Recovery Facility | 2025-10-29
WW-WEST | October | Completed the station check and daily lab work Added 3 bags of soda ash Removed floating debris from aer tank 2 | Nobleton Water Resource Recovery Facility | 2025-10-22
WW-WEST | October | Added 2 bags of soda ash to train 2. Plugged in pumps to transfer from tank 1 to aeration tank 2. | Nobleton Water Resource Recovery Facility | 2025-10-18
WW-WEST | October | Responding to low DO alarm. Eliminated as much air flow as possible to tank 1. Found a small leak on the inlet side air valve to aeration tank 1, pass 2. Tightened bolts on all air valves. All three passes of train 2 air valves are open enough to not limit air flow. Blowers putting out typical air flow. Receiving slightly elevated flow from pumping station, but not unusual for this time of day. Tank is receiving all the air we can give it. Nothing more to be done at this time. | Nobleton Water Resource Recovery Facility | 2025-10-19
WW-WEST | October | Completed the station check and daily lab work Closed the aer outlet gates to continue filling tank 1 Unplugged RAS pump 1 Added 3 bags of soda ask to aer tank 2 Batch wasted 20m3 from each clarifier | Nobleton Water Resource Recovery Facility | 2025-10-24
WW-WEST | October | Test backflow preventers Passed | Nobleton Water Resource Recovery Facility | 2025-10-16
WW-WEST | October | Decanted the sludge thickening tank Collected the weekly samples | Nobleton Water Resource Recovery Facility | 2025-10-21
WW-WEST | October | In to Complete Scheduled WOs. Lowered and Activated Decant Pump. Decant Complete. Raised and Deactivated Decant Pump. Sludge Transfer Valve Local Open, Transferred Thickened Sludge. Transfer Valve Returned to Manual Closed. Placed RAS Pump #3 in Manual Off. Enabled Batch Waste Set-point in Preparation for Wasting @ 13:45. WAS Valve #3 Manual Open. Added Soda Ash to Both Aer. Tanks ?> 1 Bag Each. WAS Pump #2 Manual On and Off Intermittently for Wasting. Wasting Complete, WAS Valve #3 Manual Closed. Reset Batch Wasting Set-point. Wasted 30 m3 from Clarifier #2. RAS Pump #3 in Manual On, Manual Speed @ 50%, Supplying Aer. Tanks #1 and 2. | Nobleton Water Resource Recovery Facility | 2025-10-31
WW-WEST | October | Completed the station check and daily lab work Emptied the sludge holding tank Batch wasted 20m3 from each clarifier Added 3 bags of soda ash to aeration tank 2 Continued pumping aer tank 1 into tank 2 Removed rags and floating debris from aer tank 2 and inlet gate | Nobleton Water Resource Recovery Facility | 2025-10-20
WW-WEST | October | Set up 2 pumps to transfer from tank 2 to tank 1. | Nobleton Water Resource Recovery Facility | 2025-10-23
WW-WEST | October | Comprehensively cleaned walkways on aeration tanks. Maintained DO probes. Bled condensation from aeration tank air lines. Assisted Gavin cleaning rags from RAS pumps 1 and 3. | Nobleton Water Resource Recovery Facility | 2025-10-22
WW-WEST | October | Closed the aer tank outlet gates to start filling tank 1 Completed the station check and daily lab work Added 3 bags of soda ash Adjusted air valves to aerate both tanks Verified the do probes Removed rags from the aeration tank and inlet gate Reopened the aer tank outlet gates to resume regular operation until tomorrow | Nobleton Water Resource Recovery Facility | 2025-10-23
WW-WEST | October | Test backflow preventers One failed installed rubber repair kit Retested passed other 2 passed | Nobleton Water Resource Recovery Facility | 2025-10-17
WW-WEST | October | In to Complete Scheduled WOs. Notified ROC. RAS Pumps #3 in Manual @ 100% Speed for Testing Purposes. Returned to Auto and Duty. Lowered and Activated Decant Pump. Decant Complete. Raised and Deactivated Decant Pump. Sludge Transfer Valve Manual Open, Transferred Thickened Sludge. Transfer Valve Returned to Manual Closed. Added Soda Ash to Aer. Tanks ?> 1 Bag Each. Adjusted Aer. Tank Blower Duty Set-points: Duty #1 Min. DO: 1.95 ?> 2.10 mg/L. Placed Submersible Pump in Aer. Tank #1, Transferring Solids to Aer. Tank #2 Inlet. Placed RAS Pump #3 in Manual Off @ 12:20 in Preparation for Wasting. WAS Valve #2 Manual Open. WAS Pump #1 Manual On. Wasting Complete, WAS Pump #1 Manual Off, WAS Valves #3 Manual Closed. Wasted 15 m3 from Clarifier #1. RAS Pump #3 Returned to Auto. Adjusted Aer. Tank #1 and 2 Inlet Gate Valves to Original Levels. Adjusted Aer. Tank DO Distribution Valves. Notified On-Call Staff. | Nobleton Water Resource Recovery Facility | 2025-10-27
WW-WEST | October | Assisted Gavin with tank changeover. Unplugged rags from submersible pump. Collected rags from aeration tank 1 outlet. Removed DO probe from tank 1 and placed in bucket of water. Set alum pump 1 in manual off. Set alum pump 2 and 3 in auto. Set pump 2 to standby to train 2 in alum stepping on SCADA. This directs all alum from pumps 2 and 3 to tank 2. Adjusted alum dosage to train 2 to 230 mg/L (from 210 mg/L) to match the setting from train 1. Adjusted aeration air valves to manage air flow while tank levels are fluctuating. Shut off RAS pumps until clarifiers receive flow. Tank 2 full and flowing over weir at 17:10. Tank 2 DO reading 2.83. Tank 1 receiving enough air to keep solids suspended. Turned RAS pumps on when clarifiers filling. Notified ROC of adjustments. | Nobleton Water Resource Recovery Facility | 2025-10-16
WW-WEST | October | In to Complete Scheduled WOs. Notified ROC. Re-Initiated Filter #3 Megalift, Transferring Sand from Filter #3 to Filter #2 for Inspection. Placed RAS Pump #3 in Manual Off. Enabled Batch Waste Set-point in Preparation for Wasting @ 07:20. WAS Valve #3 Manual Open. Sludge Transfer Valve Manual Open, Transferred Thickened Sludge. Transfer Valve Returned to Manual Closed. WAS Pump #2 Manual On and Off Intermittently for Wasting. Added Soda Ash to Both Aer. Tanks ?> 1 Bag Each. Completed Aer. DO Sensor Maintenance. Placed Probes in Calibration Mode. Cleaned and Inspected Units, No Issues Found. Returned to Service. Wasting Complete, WAS Valve #3 Manual Closed. Reset Batch Wasting Set-point. Wasted 40 m3 from Clarifier #2. RAS Pump #3 in Manual On, Manual Speed @ 50%, Supplying Aer. Tanks #1 and 2. Throttled RAS Valve #4 by 40% for Flow Distribution Equalization. Deactivated Filter #3 Megalift Sand Transfer Process. | Nobleton Water Resource Recovery Facility | 2025-10-30
WW-WEST | October | RAS pumps back into normal flows as of 2:35pm. Submersible pumps continue to run. DO in both basins approximately 2.4mg/L with 2 blowers in manual. | Nobleton Water Resource Recovery Facility | 2025-10-26
WW-WEST | October | In to Complete Reg. Sampling and Scheduled WOs. Notified ROC. Lowered and Activated Decant Pump. Placed RAS Pumps #1 and 3 in Manual, Manual Speed @ 100% for Testing Purposes. Returned to Auto, Auto Speed. Decant Complete. Raised and Deactivated Decant Pump. Sludge Transfer Valve Manual Open, Transferred Thickened Sludge. Transfer Valve Returned to Manual Closed. Enabled Batch Waste Set-point. RAS Pumps Auto Off in Preparation for Wasting @ 08:25. WAS Valves #2 and 3 Manual Open. WAS Pumps #1 and 2 Manual On and Off Intermittently for Wasting. Wasting Complete, WAS Valves #2 and 3 Manual Closed, RAS Pumps #1-3 in Manual Off. Reset Batch Wasting Set-point. Wasted 20 m3 from Each Clarifier. Conducted Aer. Tank #2 Isolation and Drawdown in Preparation for Scheduled CPD Work. Aer. Tank Outlet Interconnect Valve Manual Open, Aer. Tank #2 Inlet Gate Manual Closed. Submersible Pumps Returning Aer. Tank #2 Outlet Flow to Aer. Tank Inlet Channel. RAS Train #2 Discharge Valve Manual Closed, RAS Valve #3 Local Open. RAS Pumps #1 and 3 Manual On @ 0% Speed. Clarifiers #1 and 2 Returning Via RAS Train #1, Aer. Tank #2 Placed OOS. Cleared Associated Alarms. Placed Alum Pump #3 in Manual Off. Rotated Alum Pump #2 to Standby for Aer. Tank #1. Adjusted Aer. Tank #1 Outlet Alum Dosage Set-point by 75% to Compensate for Additional Flow: 210.00 ?> 368.00 mg/L Added Soda Ash to Aer. Tank #1 ?> 2 Bags. Removed Aer. Tank #2 DO Sensor and Stored Properly Until CPD Work Completed. Reduced Aer. Tank #2 Air Flow Until Tank Drawdown Complete. | Nobleton Water Resource Recovery Facility | 2025-10-07
WW-WEST | October | Ladder has been installed by outside contractor in aeration tank 2. Begin refilling with mixed liquor from aeration tank 1. Clarifier inlets are both closed. Once aeration tank 2 is 2/3 full, we will redirect RAS from both clarifiers to aeration tank 2, open aeration inlet gate to # 2 and close 1. Then we will begin pumping down aeration tank 1 with submersible pumps into tank 2. | Nobleton Water Resource Recovery Facility | 2025-10-15
WW-WEST | October | In to Complete Scheduled WOs. Notified ROC. WAS Valves #2 and 3 Manual Open. Enabled Batch Waste Set-point. RAS Pumps Auto Off in Preparation for Wasting @ 08:00. Lowered and Activated Decant Pump. Added Soda Ash to Both Aer. Tanks ?> 1 Bag Each. Decant Complete. Raised and Deactivated Decant Pump. Sludge Transfer Valve Manual Open, Transferred Thickened Sludge. Transfer Valve Returned to Manual Closed. WAS Pumps #1 and 2 Manual On and Off Intermittently for Wasting. Wasting Complete, WAS Valves #2 and 3 Manual Closed. Reset Batch Wasting Set-point. Wasted 20 m3 from Each Clarifier. Placed RAS Pumps #1 and 2 in Manual, Manual Speed @ 100% for Testing Purposes. Returned to Auto, Auto Speed. Completed RAS Pump #3 Inspection and Clean Out. Removed Debris and Obstructions from Suction Line. Tested in Local with No Issues. Returned to Service, Duty #1. Cleared Associated Alarm. | Nobleton Water Resource Recovery Facility | 2025-10-03
WW-WEST | October | In to Complete Scheduled WOs. RAS Pumps Manual Off in Preparation for Wasting @ 08:25. WAS Valves #2 and 3 Manual Open. Lowered and Activated Decant Pump. Decant Complete. Raised and Deactivated Decant Pump. Sludge Transfer Valve Manual Open, Transferred Thickened Sludge. Transfer Valve Returned to Manual Closed. Added Soda Ash to Aer. Tank #1 ?> 2 Bags. Adjusted Aer. Tank #1 Blower Duty Set-points: Duty #1 Min. DO: 1.85 ?> 1.95 mg/L, Duty #1 Min. DO Time: 3.00 ?> 1.5 mins. WAS Pumps #1 and 2 Manual On and Off Intermittently for Wasting. Wasting Complete, WAS Valves #2 and 3 Manual Closed, Wasted 10 m3 from Clarifier #1 and 5 m3 from Clarifier #2. RAS Pumps #1 and 3 Manual On Independently @ 100% Speed for Testing Purposes. Returned Both to Manual On Simultaneously @ 0% Speed. Adjusted Aer. Tank #1 Outlet Alum Dosage Set-point Based on In-House Laboratory Results: 368.00 ?> 349.00 mg/L. Completed Aer. Tank #1 DO Sensor Inspection. Placed Probe in Calibration Mode. Cleaned and Inspected Unit,No Issue Found. Returned to Service. | Nobleton Water Resource Recovery Facility | 2025-10-08
WW-WEST | October | Unplugged pumps pumping down aeration tank 2x only for them to plug again under. A minute each time. Level is approx 1ft5inches from bottom. Unplugged pumps. | Nobleton Water Resource Recovery Facility | 2025-10-11
WW-WEST | October | Batch wasting mode enabled Was pumps in auto to begin wasting at 9am for a total of 40m3. Pumped out scum tank. | Nobleton Water Resource Recovery Facility | 2025-10-12
WW-WEST | October | In to Complete Scheduled WOs. Notified ROC. Completed Filter Drain Sump System Inspection. Tested Pumps and HiHi Alarm Via Floats. Confirmed Reception by the ROC. Returned to Service. Cleared Associated Alarm. Completed Clarifier #1 and 2 Inspections. Drive Chains OK. Topped Up Both Gear Box Oil Reservoirs. No Other Issues Found. Returned to Service. | Nobleton Water Resource Recovery Facility | 2025-10-09
WW-WEST | October | In to Complete Scheduled WOs. Notified ROC. WAS Valves #2 and 3 Manual Open. Enabled Batch Waste Set-point. RAS Pumps Auto Off in Preparation for Wasting @ 08:05. Lowered and Activated Decant Pump. Added Soda Ash to Both Aer. Tanks ?> 1 Bag Each. Decant Complete. Raised and Deactivated Decant Pump. Sludge Transfer Valve Manual Open, Transferred Thickened Sludge. Transfer Valve Returned to Manual Closed. WAS Pumps #1 and 2 Manual On and Off Intermittently for Wasting. Wasting Complete, WAS Valves #2 and 3 Manual Closed. Reset Batch Wasting Set-point. Wasted 20 m3 from Each Clarifier. Placed RAS Pumps #1 and 2 in Manual, Manual Speed @ 100% for Testing Purposes. Returned to Auto, Auto Speed. Cleared Associated Alarms. Completed Aer. DO Sensor Maintenance. Placed Probes in Calibration Mode. Cleaned and Inspected Units, No Issues Found. Returned to Service. Completed Sanitary Sump System Inspection. Cleaned and Organized Floats. Tested HiHi Float Alarm. Confirmed Reception by the ROC. No Other Issues Found. Cleared Associated Alarm and Returned to Service. Completed Sludge Holding Tank Blower #1 and 2 Inspections. Belts, Filters and Oil Reservoirs Ok. Returned to Service. Cleared Associated Alarms. Completed Compressor #1 and 2 Inspections. Belts, Filters and Oil Reservoirs Ok. Returned to Service. Cleared Associated Alarms. Placed Scum Pump #2 in Manual On for Scum Tank Drawdown. Drawdown Complete, Returned Scum Pump #2 to Auto and Service. | Nobleton Water Resource Recovery Facility | 2025-10-02
WW-WEST | October | Added 1 bag of soda ash to each aeration tank | Nobleton Water Resource Recovery Facility | 2025-10-04
WW-WEST | October | Decanted sludge thickening tank and transferred thickened sludge to holding tank. Turn on second submersible pump in offline aeration to speed up drainage. Pulled rags from aeration inlet and floating at end of second pass. Collect samples and complete in house labs Added 2 bags of soda ash to aeration tank 1. Shut off RAS pumps 1 & 3 (in manual) for batch wasting. Wasted 55m3 and put RAS pumps 1&3 back in manual. Completed station checks and rounds Labs and data entered into SharePoint. | Nobleton Water Resource Recovery Facility | 2025-10-10
WW-WEST | October | Completed the station check and daily lab work Added 3 bags of soda ash to aeration tank 2 Unplugged both air lifts in sand filter 4 | Nobleton Water Resource Recovery Facility | 2025-10-09
WW-WEST | October | Added 2 x 25kg bags of soda ash to aeration basin. Cleared rags from aeration inlet gate stem. | Nobleton Water Resource Recovery Facility | 2025-10-12
WW-WEST | October | Completed the station check and daily lab work Decanted and then emptied the sludge holding tank added 2 bags of soda ash to aeration tank 1 Closed the clarifier inlet valves in the morning to start filling aeration tank 2 Reopened the clarifier inlet valves in the afternoon and placed 2 submersible pumps in tank 1 to pump to tank to so it will continue to fill overnight Bled the condensate out of the aeration tank lines Cleaned the aeration tank outlet weirs Batch wasted 30m3 from each clarifier | Nobleton Water Resource Recovery Facility | 2025-10-15
WW-WEST | October | Wasting completed - 50m3 total. Put RAS pumps 1 & 3 back in manual/on. Shut off was pumps. Complete small lab on final effluent. Based on pH dropping and phosphorus being low - reduced alum from 315mg/l to 230mg/L. Entered lab results in SharePoint spreadsheet. | Nobleton Water Resource Recovery Facility | 2025-10-12
WW-WEST | October | In to Complete Scheduled WOs. Placed RAS Pumps #1 and 3 in Manual, Manual Speed @ 100% for Testing Purposes. Returned to Auto, Auto Speed. Enabled Batch Waste Set-point. RAS Pumps Auto Off in Preparation for Wasting @ 08:25. WAS Valves #2 and 3 Manual Open. Lowered and Activated Decant Pump. Added Soda Ash to Both Aer. Tanks ?> 1 Bag Each. Decant Complete. Raised and Deactivated Decant Pump. Sludge Transfer Valve Manual Open, Transferred Thickened Sludge. Transfer Valve Returned to Manual Closed. WAS Pumps #1 and 2 Manual On and Off Intermittently for Wasting. Wasting Complete, WAS Valves #2 and 3 Manual Closed. Reset Batch Wasting Set-point. Wasted 20 m3 from Each Clarifier. Placed RAS Pumps #1 and 3 in Manual, Manual Speed @ 100% for Testing Purposes. Returned to Auto, Auto Speed. Completed Aer. Blowers #1-3 Inspections. Filters and Belts OK. Topped Up Blowers #1 and 3 Oil Reservoirs. No Other Issues Found. Returned to Service. Cleared Associated Alarms. | Nobleton Water Resource Recovery Facility | 2025-10-06
WW-WEST | October | Transferred sludge thickening tank to sludge holding tank. Shut off RAS pumps 1 & 3. Put WAS pumps in auto to begin batch wasting at 9am. Total to be wasted is 50m3. | Nobleton Water Resource Recovery Facility | 2025-10-12
WW-WEST | October | In to Complete Scheduled WOs. WAS Valves #2 and 3 Manual Open. Enabled Batch Waste Set-point. RAS Pumps Auto Off in Preparation for Wasting @ 08:10. Lowered and Activated Decant Pump. Decant Complete. Raised and Deactivated Decant Pump. Sludge Transfer Valve Manual Open, Transferred Thickened Sludge. Transfer Valve Returned to Manual Closed. WAS Pumps #1 and 2 Manual On and Off Intermittently for Wasting. Wasting Complete, WAS Valves #2 and 3 Manual Closed. Reset Batch Wasting Set-point. Wasted 20 m3 from Each Clarifier. Added Soda Ash to Both Aer. Tanks ?> 1 Bag Each. Placed RAS Pumps #1, 2 and 3 in Manual, Manual Speed @ 100% for Testing Purposes. Returned to Auto, Auto Speed and Service. Cleared Associated Alarms. Rotated RAS Pump Duties. RAS Pumps #2 in Duty #1, RAS Pump #3 in Duty #3. | Nobleton Water Resource Recovery Facility | 2025-10-01
WW-WEST | October | Completed the station check and daily lab work Added 3 bags of soda ash to aeration tank 1 Removed rags from the aeration inlet and floating in the tank Inspected the screenings compactor, vortex 1 and 2, debris auger and grit dewatering screw Batch wasted 30m3 from clarifier 1 and 26m3 from clarifier 2 | Nobleton Water Resource Recovery Facility | 2025-10-14
WW-WEST | October | Attending site to reduce the time between D.O. air-clean cycle times from every 1 hour to every 4 hours. Clean duration remains at 120 seconds. This change was applied to both D.O. analyzers. | Nobleton Water Resource Recovery Facility | 2025-10-08
WW-CEAST | October | -On site to perform a station check. | Markham Leslie Pumping Station | 2025-10-31
WW-CEAST | October | On site for pump 4 no flow. Found the discharge valve to be damaged internally. We will need to return to repair or replace the valve | Markham Leslie Pumping Station | 2025-10-28
WW-CEAST | October | Station check complete and the readings have been entered in the sharepoint. Changed out bin for the weekend. Installed sampling hose for EME staff taking covid sample | Markham Leslie Pumping Station | 2025-10-24
WW-CEAST | October | Station check complete and the readings have been entered into the sharepoint. Switched out the rag bin, hosed down screen room floor | Markham Leslie Pumping Station | 2025-10-27
WW-CEAST | October | -On site to complete work orders. -Completed station check and site walkthrough. -Entered station readings into SharePoint. -Checked drywell, drained condensate from air compressor tanks. -Air compressors inspection and cleaning completed. -Checked screen room, changed out rag bin, placed bins out for pick up, flushed screw press drain lines, swept floor. -Bar screen bin removal completed. -Pumps 1 and 4 OOS. | Markham Leslie Pumping Station | 2025-10-22
WW-CEAST | October | -On site to complete work orders. -Entered station readings into SharePoint. -Checked drywell. -Hoist inspection completed. -Drained condensate from air compressors. -Checked screen room, changed out rag bin, replaced bins following pick up, hosed down screw press drain lines, cleaned rags off bar screens. -Screw conveyor cleaning and lubrication completed. -Station check completed. -Forcemain header valve and actuator, exercise and inspection completed. Fully exercised South, North, and Header Tie Valves. South Forcemain Valve stuck at 98% open with an Overtorque Alarm. Unable to get valve to open further, will have to continue work. On valve at a later date. -RS pump inspection completed. Pumps 1 and 4 OOS. -Pump 2: 940L/s at 0%, 1420L/s at 50%, 1815L/s at 100%. -Pump 3: 1320L/s, -Pump 5: 940L/s at 0%, 1400L/s at 50%, 1765L/s at 100%. -Pump 6: 1135L/s. -Check valves inspection completed. -Air relief valves inspection completed. -Pumps 1 and 4 OOS. South Forcemain Overtorque Alarm outstanding at 98% open. | Markham Leslie Pumping Station | 2025-10-17
WW-CEAST | October | On site to assist with generator 3 troubleshoot with WAJAX/CMS. Troubleshoot pump 4 discharge valve overtorque. Confirmed valve overtorque at 95% open position, and would not close beyond 95%. Fully opened P4 discharge valve in L and ran pump 4 in hand mode for about 30 seconds, no flow output observed. I suspect this valve is actually closed. Created CMU3 for CMS to investigate. Pump 4 in Local/OFF with both suction/discharge closed/LOTO. Seal water valve is also closed to P4. Confirmed nothing more coming out from drainage hose @ 14:40pm. Blow off open on P4. Talked to WAJAX, still investigating the voltage drop issue with gen 3. Dave D(CMS) still on-site for WAJAX. | Markham Leslie Pumping Station | 2025-10-16
WW-CEAST | October | On site to assist Wajax with generator 3 repair. Wajax technician completed repairs to generator 3. Generator 3 is ready to go back in service according to the Wajax technician. Cleared all alarms on all generators and left in auto duty. | Markham Leslie Pumping Station | 2025-10-16
WW-CEAST | October | -On site to complete work orders. -Station check completed, readings entered into SharePoint. -Checked dry well. -Air compressors inspection and cleaning completed. -BAS check completed, no alarms present on system. -Checked screen room, changed out rag bin, placed bins out for removal, flushed screw press drain lines, bar screen oil full, swept rags off floor. -Bar screen bin removal completed. -Pumps 1 and 4 remain OOS. | Markham Leslie Pumping Station | 2025-10-29
WW-CEAST | October | -Back on site to respond to Bar Screen 2 Fault Alarm reported by ROC. -Reset fault and ran Bar Screen 2 in hand. Rake is noticeably crooked and bearings are fairly noisy while bar screen is in operation. -Had D. Kim attend site and isolated inlet gate to Bar Screen 2. Placed bar screen 2 OOS and created work request for maintenance team to troubleshoot issue further. | Markham Leslie Pumping Station | 2025-10-17
WW-CEAST | October | -On site to perform a station check. -Entered station readings into SharePoint. -Checked drywell, drained condensate from air compressor tanks. -Reset Earth Fault on AHU-1, unit now running in auto again. -Pumps 1-6 seal water strainer inspection completed. -Checked screen room, changed out rag bin, bar screen oil full, flushed screw press drain lines. -Pumps 1 and 4 remain OOS. -South Forcemain Valve Fault outstanding, Overtorque at 98% open. | Markham Leslie Pumping Station | 2025-10-20
WW-CEAST | October | On site to work on barscreen #2. Found barscreen out of alignment. Adjust tension on chains and align rake. Ran tested and put back into service. | Markham Leslie Pumping Station | 2025-10-28
WW-CEAST | October | Onsite to perform Pump pm on raw sewage pumps 2,3,5,6 Contacted cpo put pump 3,5 in manual off. Pumps 2,3,4,5,6 available in Auto | Markham Leslie Pumping Station | 2025-10-09
WW-CEAST | October | -On site to perform a station check. -Entered station readings into SharePoint. -Checked drywell, drained condensate from air compressor tanks. -Rotated sump pump duties. -Checked screen room, changed out rag bin, placed bins out for pick up, flushed screw press drain lines, bar screen oil full. -Pump 1 and Generator 3 remain OOS. -Pumps 2-6 in auto and available. | Markham Leslie Pumping Station | 2025-10-08
WW-CEAST | October | -On site to complete work orders. -Station readings entered into SharePoint. -Checked drywell. -Air compressors inspection and cleaning completed. -Checked screen room, changed out rag bin, cleared out blockage in screw press drain lines. Topped up bar screen oil, swept floor. -Bar screen bin removal completed. -Station check completed. -BAS inspection completed. -Dry well sump put high level alarm test completed and confirmed by ROC. -Surge tank transmitter lines flushing completed, flushed air and sewage lines on both pressure and level sensors. -Reset all alarms caused from work on site. -Pumps 2-6 in auto and available. -Pump 1 remains OOS, Generator 3 remains OOS. | Markham Leslie Pumping Station | 2025-10-15
WW-CEAST | October | On site to assist mechanics with pump PM?s on Pumps 2,3,5,6 Pump two is waiting on cabinet handle Pump six requires a UPS replacement as batteries are not holding a charge for more then 30 minutes after recently replacing the batteries. All pumps back in auto with no faults showing. | Markham Leslie Pumping Station | 2025-10-09
WW-CEAST | October | -On site to complete work orders. -Station check completed, readings entered into SharePoint. -Checked drywell. -Air compressors, inspection and cleaning completed. -Checked screen room, changed out rag bin, flushed screw press drain lines, topped up bar screen oil. -Bar screen removal completed for pick-up tomorrow. -Monthly diesel generator test run completed, readings entered into SharePoint. -Diesel generator 3 remains OOS, only generators 1 and 2 ran during the monthly test. -11:01 - Transferred site to generator power. -12:26 - Transferred site back to utility power. -Gen 1: Start time: 213:33, Stop time: 215:03, Run time: 1:30hrs. -Gen 2: Start time: 98:36, Stop time: 100:06, Run time: 1:30hrs. -Gen 3 hours remain at 88:09, generator OOS. -Monthly JHSC H&S inspection completed. -BAS check completed, acknowledged and reset old alarms, no active alarms. -Pump 1 OOS, Pumps 2-6 in auto and available. | Markham Leslie Pumping Station | 2025-10-01
WW-CEAST | October | Took station readings and entered into SharePoint,, put bins back into the screening room and flushed out the bottom of the auger, also switched the bins out for the weekend. Checked both compressors oil/ belts - OK and drained the water from the holding tanks, exercised the drain valves on the surge tanks and also inspected both tanks - all looks good. Rolled up the hose that?s been on the floor and cleaned up the area a bit. Inspected the sump pit and activated pump - all good,, flushed the bubblers - no issues and checked the BAS system for the building. Checked the screens on the odour control unit - all good and set up a new sample line on pump 6 for the weekly samples. Station running under normal ops - pump 1 is still OOS waiting on parts. All alarms were cleared. | Markham Leslie Pumping Station | 2025-10-10
WW-CEAST | October | -On site to perform a station check. -Entered station readings into SharePoint. -Checked drywell, drained condensate from air compressor tanks.. -Checked screen room, replaced rag bins following pick-up, changed out bin for the weekend, flushed screw press drain lines. -Generator 3 OOS, Pump 1 OOS. -Pumps 2-6 in auto and available. | Markham Leslie Pumping Station | 2025-10-03
WW-CEAST | October | On site to wire pump seal water valves on pump 2 and pump 5. | Markham Leslie Pumping Station | 2025-10-03
WW-CEAST | September | Took station readings and entered into SharePoint,,, put bins out for pick up and washed out screens for Bayview again. Checked both compressors and also the BAS system - all good. Station running under normal ops - Pump 1 is OOS. | Markham Leslie Pumping Station | 2025-09-24
WW-CEAST | October | -On site to complete work orders. -Hosed down dirty mist eliminator filters from Bayview Steeles OCF in screen room. -Checked screen room, changed out rag bins, flushed screw press drain lines, bar screen oil topped up. Cleaned rags off floor. -Station readings entered into SharePoint. -Checked drywell, drained condensate from air compressor tanks. -Seal water strainer inspection and cleaning completed. -Diesel generator 3 OOS. -Pumps 1 OOS. -Pumps 2-6 in auto and available. | Markham Leslie Pumping Station | 2025-10-06
EAST | October | On site for station check. Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 1.54mg/l FCL Analyzer: 1.50mg/l Effluent Free Cl2 grab residual: 1.47mg/l FCL Analyzer: 1.50mg/l Effluent Total Cl2 grab residual: 1.73mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Mount Albert Wells 1 & 2 | 2025-10-27
EAST | October | 08:30hrs: Cleaned Influent and Effluent HACH Cl17 Analyzers. Collected Cl2 grab residuals to verify Analyzers after cleaning: Influent Cl2 grab: 1.51mg/l Analyzer: 1.57 mg/l Effluent Cl2 grab: 1.47mg/l Analyzer: 1.55mg/l Conducted Generator Test Run Diesel Generator Run Monthly Test @09:05 hrs Start Runtime: 09:05hrs Runtime Hrs: 198.35hrs Fuel Start: 12.0cm/790.6L Stop Runtime: 10:20hrs, Runtime Hrs: 199.70hrs Fuel Stop: Generator Performance Data recorded below: Battery Cell Levels: OK Battery Terminals/Cables: Ok Oil and Coolant: Ok Amps: 35 Volts: 601 Hertz: 60 RPM: 1799 Oil Pressure: 392KPA Oil Temp: NA Water temp: 79 C Ran Well 2 during generator test run under load. No issues during utility to emergency switchover and back. Conducted Hi/Low Temp alarm test. JHSC Inspection completed. Travis Wyatt on site: Silicate day tank filled up to 110cm. Conducted Silicate and Hypo Pump inspections and inspected/cleaned injection points. | Mount Albert Wells 1 & 2 | 2025-10-16
EAST | October | On site for station check. Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 1.97mg/l FCL Analyzer: 1.95mg/l Effluent Free Cl2 grab residual: 1.78mg/l FCL Analyzer: 1.77mg/l Effluent Total Cl2 grab residual: 2.09mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Mount Albert Wells 1 & 2 | 2025-10-31
EAST | October | Onsite to respond to turbidity interlock on well. Well interlocked on vial clarity. Cleaned vial, flushed out sample line and returned turb analyzer to service. Notified ROC to clear and reset alarm. No issues. | Mount Albert Wells 1 & 2 | 2025-10-21
EAST | October | Topped up silicate from 41.5cm to 109.5cm. | Mount Albert Wells 1 & 2 | 2025-10-30
EAST | October | On site for station check. Collected weekly micro samples (W11316266) and Quarterly Samples (W11247446). Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 2.00mg/l FCL Analyzer:1.94mg/l 09:25hrs: Effluent Free Cl2 grab residual: 1.61mg/l FCL Analyzer: 1.61mg/l Effluent Total Cl2 grab residual: 1.94mg/l Ran Well #1 in local to waste (not into distribution) to collect raw samples. Ensured chemical pumps were off and isolated from distribution system while running well. Back to local off when complete. Well used for emergency purposes only. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Mount Albert Wells 1 & 2 | 2025-10-22
EAST | October | On site for station check. Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 1.84mg/l FCL Analyzer:1.91mg/l Effluent Free Cl2 grab residual: 1.71mg/l FCL Analyzer: 1.69mg/l Effluent Total Cl2 grab residual: 2.00mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. *Silicate dose lower than normal. Noticed Silicate P2 not doing properly. Had to remove injection point and replace ?ball? in check valve as it was getting stuck closed. Silicate P2 now dosing as required. | Mount Albert Wells 1 & 2 | 2025-10-20
EAST | October | On site for station check. Collected weekly micro samples (W11330477). Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 1.93mg/l FCL Analyzer:1.89mg/l 12:20hrs: Effluent Free Cl2 grab residual: 1.74mg/l FCL Analyzer: 1.72mg/l Effluent Total Cl2 grab residual: 2.00mg/l Ran Well #1 in local to waste (not into distribution) to collect raw samples. Ensured chemical pumps were off and isolated from distribution system while running well. Back to local off when complete. Well used for emergency purposes only. Well #1 raw sample collected @ 12:45hrs. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Mount Albert Wells 1 & 2 | 2025-10-29
EAST | October | Under Direction of OIC Dan Zhou On site for silicate delivery: Before fill- 23.0 cm After fill- 111.1 cm | Mount Albert Wells 1 & 2 | 2025-10-16
EAST | October | On site for station check and equipment verification Duty is not active - MTETNL level - 74% Recorded station readings in PWQ sheets Verified analyzer readings with grab residuals - no adjustments needed Received Hypo delivery: Start: 31.1 cm / 30.7 cm Stop: 90.2 cm / 89.4 cm Visual inspection of chemical systems Reviewed trends, equipment ok Station ok | Mount Albert Wells 1 & 2 | 2025-10-17
EAST | October | On site for station check and equipment verifications Tower level - 62% and duty is not active Recorded station readings in PWQ sheets Verified analyzer readings with grab chlorine residuals - no adjustments needed Visual inspection of chemical systems - all ok Turbidity analyzer maintenance from 09:20 to 09:40 Reviewed trends, equipment OOS: None Station ok | Mount Albert Wells 1 & 2 | 2025-10-24
EAST | October | On site for station check and equipment verifications Duty is active on arrival - MTETNL level - 70% Recorded station readings in PWQ sheets Verified analyzer readings with grab chlorine residuals - no adjustments needed Visual inspection of chemical systems - all ok Reviewed trends, equipment OOS: none Station ok | Mount Albert Wells 1 & 2 | 2025-10-10
EAST | October | On site for station check, weekly micro sampling (W11256290) and monthly manganese sampling (W11257547) Duty is active - MTETNL level - 71% Well #2 running in D1 - 22 L/s, 326 kpa Recorded station readings in PWQ sheets Chemical systems: Hypo P1 dosing at 29%, 73.8 mL/min, DF = 109% Silicate P1 dosing at 37%, 69.6 mL/min Verified analyzer readings with grab chlorine residuals: Influent: @13:59 Grab free: 1.88 mg/L / Analyzer: 1.94 mg/L Effluent: @14:03 Grab free: 1.58 mg/L / Analyzer: 1.55 mg/L Grab total: 1.91 mg/L NTU: 0.14 Collected well #2 raw sample and treated samples @14:06 Manual stopped well #2 @14:16. Placed chemical pumps to man/off and started well #1 in local to waste @14:18 Collected well #1 raw sample @14:41, stopped well #1 and placed chemical pumps back to auto Placed well #2 back to auto @14:48 Reviewed trends, equipment OOS: None Station ok | Mount Albert Wells 1 & 2 | 2025-10-01
EAST | October | On site for station check, weekly micro sampling (W11298554) Duty is active - MTETNL level - 70% Well #2 running in D1 - 22 L/s, 322 kpa Recorded station readings in PWQ sheets Chemical systems: Hypo P1 dosing at 31%, 76.9 mL/min, DF = 113% Silicate P1 dosing at 37%, 69.6 mL/min Verified analyzer readings with grab chlorine residuals: Influent: @11:53 Grab free: 1.94 mg/L / Analyzer: 1.98 mg/L Effluent: @11:57 Grab free: 1.50 mg/L / Analyzer: 1.51 mg/L Grab total: 1.75 mg/L NTU: 0.068 Collected well #2 raw sample and treated samples @12:00 Manual stopped well #2 @12:08 Local started well #1 to waste @12:14 - placed chemical pumps to manual off Stopped well #1 @12:37 - placed chemical pumps back to auto Reviewed trends, equipment OOS: None Station ok | Mount Albert Wells 1 & 2 | 2025-10-14
EAST | October | Topped up silicate tank: 22.01 cm ?> 103.32 cm | Mount Albert Wells 1 & 2 | 2025-10-02
EAST | October | On site to respond to turbidity fault alarm. Vial clarity error is outstanding on the turbidity meter. Cleaned turbidity meter?s sample vial. Reset alarm and started well 2. Discharge pressure lolo alarm (220kpa) is triggered. Town of EG is flushing in their system. Informed ROC. | Mount Albert Wells 1 & 2 | 2025-10-09
EAST | October | Station Check (no issues found) Input data to PWQ 9:10 Well #1 local on for raw sample (verified valving to waste & chem. pumps in manual off) 9:40 #11278497 well 1 raw sample, well in local off 9:43 Well duty activated 10:00 CL17s verified (mg/L): Influent: Free Grab 1.82, A 1.83 Treated: Free: Grab 1.43, A 1.43 Total Grab 1.73 9:15 #11278497 Well 2 raw & treated samples | Mount Albert Wells 1 & 2 | 2025-10-08
EAST | October | On site for station check. Collected weekly micro samples (W11316266) and Quarterly Samples (W11247446). Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 1.82mg/l FCL Analyzer:1.78mg/l 09:00hrs: Effluent Free Cl2 grab residual: 1.67mg/l FCL Analyzer: 1.66mg/l Effluent Total Cl2 grab residual: 1.90mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Mount Albert Well 3 | 2025-10-22
EAST | October | On site for station check. Collected weekly micro samples (W11330477) and Methane RW samples (W11393041 Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 1.82mg/l FCL Analyzer: 1.84mg/l 11:15hrs: Effluent Free Cl2 grab residual: 1.74mg/l FCL Analyzer: 1.71mg/l Effluent Total Cl2 grab residual: 1.88mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Mount Albert Well 3 | 2025-10-29
EAST | October | On site for station check. Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 1.85mg/l FCL Analyzer:1.80mg/l Effluent Free Cl2 grab residual: 1.70mg/l FCL Analyzer: 1.65mg/l Effluent Total Cl2 grab residual: 1.89mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Mount Albert Well 3 | 2025-10-20
EAST | October | On site for monthly maintenance - informed ROC - Diesel generator test run and hours log: Started @13:53: Hours: 372:36, Fuel: 93.1/92.5cm. Ran well #3 during test run, under generator power. Stopped @15:05: Hours: 373:48, Fuel: 92.4/91.7 cm. No issues with transfer / test run on generator. See attached generator run sheet in log entry attachments - Chlorine leak detector test - Chlorine scrubber inspection Equipment back to auto, station ok | Mount Albert Well 3 | 2025-10-16
EAST | October | On site for station check and equipment verifications and to complete monthly PMs - JHSC health and safety inspections - Chlorine emergency kit inspection - Sodium silicate system inspection and injection point flush - verified silicate pumps with drawdowns, no issues - Well pump and motor grease Recorded station readings in PWQ sheets Verified analyzer readings with grab residuals - no adjustments needed Equipment OOS: None, reviewed trends Station ok | Mount Albert Well 3 | 2025-10-17
EAST | October | On site for station check. Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 1.79mg/l FCL Analyzer: 1.84mg/l Effluent Free Cl2 grab residual: 1.66mg/l FCL Analyzer: 1.73mg/l Effluent Total Cl2 grab residual: 1.90mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Mount Albert Well 3 | 2025-10-31
EAST | October | On site for station check and equipment verifications Duty is active - tower level - 61% Well #3 running at 30 L/s, 387 kpa Recorded station readings in PWQ sheets Verified analyzer readings with grab residuals Chemical systems: Chlorinator #1 dosing @33%, DF = 51%, Silicate P1 dosing at 41%, 63.3 mL/min Placed well to manual off for Turbidity analyzer maintenance from 11:05 to 11:24 Changed CL-17 reagents Reviewed trends, equipment OOS: none Placed well #3 back to auto Station ok | Mount Albert Well 3 | 2025-10-24
EAST | October | On site for station check. Exercised isolation valve in station. Collected Cl2 Scrubber samples while on site. Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 1.53mg/l FCL Analyzer: 1.59mg/l Effluent Free Cl2 grab residual: 1.53mg/l FCL Analyzer: 1.55mg/l Effluent Total Cl2 grab residual: 1.79mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Mount Albert Well 3 | 2025-10-27
EAST | October | On site to work on silicate P2 which faulted on Sept 30th. Faulted due to diaphragm rupture. - Replaced diaphragm, check valves and o rings and cleaned sensor with hot water - Reprimed P2 and tested to cal column, no further issues - Placed pump back to auto and activated well 3 @15:05 - no further issues | Mount Albert Well 3 | 2025-10-02
EAST | October | On site for station check and weekly micro sampling (W11298554) Well #3 running in manual - 30 L/s, 380 kpa Recorded station readings in PWQ sheets Chemical systems inspection: Chlorinator #1 dosing at 33%, 16.4 PPD, DF = 50% Silicate P2 dosing at 41%, 62.3 mL/min Verified analyzer readings with grab residuals - no adjustments needed Influent: @13:28 Grab free: 1.84 mg/L / Analyzer: 1.79 mg/L Effluent: @13:31 Grab free: 1.73 mg/L / Analyzer: 1.68 mg/L Grab total: 1.99 mg/L NTU: 0.061 Collected micro samples @12:35 for raw and treated water Placed well 3 back to auto Reviewed trends, equipment OOS: None Station ok | Mount Albert Well 3 | 2025-10-14
EAST | October | Station Check (no issues found) Input data to PWQ 11:05 Verified CL17s (mg/L): Influent: Free: Grab 1.76, A 1.80 Treated: Free: Grab 1.72, A 1.69 Total Grab 1.95 11:10 #11278497 Raw & Treated samples | Mount Albert Well 3 | 2025-10-08
EAST | October | Topped up silicate tank: 76.64 cm ?> 85.72 cm | Mount Albert Well 3 | 2025-10-02
EAST | October | On site for station check, weekly micro sampling (W11256290) and monthly manganese sampling (W11257547) Duty is active - MTETNL level - 66% Well #3 running in D1 - 30 L/s, 393 kpa Recorded station readings in PWQ sheets Chemical systems: Chlorinator #2 dosing at 31%, DF = 47%, 15.5 PPD Silicate P1 dosing at 41%, 62.5 mL/min Verified analyzer readings with grab chlorine residuals Influent: @12:50 Grab free: 1.79 mg/L / Analyzer: 1.77 mg/L Effluent: @12:53 Grab free: 1.71 mg/L / Analyzer: 1.68 mg/L Grab total: 1.96 mg/L NTU: 0.104 Collected micro samples W3 @12:55 Reviewed trends, equipment OOS: Silicate P2, requires diaphragm replacement Station ok | Mount Albert Well 3 | 2025-10-01
EAST | October | Arrived on site to find silicate injection point #2 snapped off and blown off. Water has been spraying. Removed broken injection line and isolated ball valve on the discharge header. Unclear how long it?s been broken for. Was able to assemble new injection quill on site, and install on injection line 2. Reprimed line and tested silicate system. Activated system duty @11:40 to test well operation and silicate system Completed station check and equipment verifications Recorded readings in PWQ sheets Reviewed trends, chemical systems all ok Verified chlorine analyzer readings with grab residuals - all ok Conducted weekly turbidity analyzer maintenance, informed ROC Completed weekly discharge valve exercise Station ok | Mount Albert Well 3 | 2025-10-03
EAST | October | On site to complete station check. Time: 09:10 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.68 1.63 Time: 09:13 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.66 1.60 Total: 2.01 No outstanding alarms. No OOS equipment. Verified analyzers on site. Checked site and trends. Entered data into PWQ sheet. | Mount Albert Well 3 | 2025-10-06
EAST | October | On site to refill eyewash station | Mount Albert North Elevated Tank | 2025-10-27
EAST | October | On site for station check. Collected weekly micro samples (W11316266) and Quarterly Samples (W11247446). Verification of HACH CL17 Chlorine Analyzers: 10:25hrs: Free CL2 grab residual: 1.30mg/l FCL Analyzer: 1.28mg/l Total Cl2 grab residual: 1.41mg/l Checked station readings and verified Cl2 analyzer. All information in PWQ sheet. Checked site and equipment. Equipment out of service: None. | Mount Albert North Elevated Tank | 2025-10-22
EAST | October | On site to complete following work orders: W11294147 Altitude Valve Inspection. W11294136 Drain Valve Exercise. W11294122 Manual Valve Exercise. W11294111 Low Temp Alarm Test. W11294102 Inlet/Outlet Heat Trace Insp. W11294089 Sump Pit System Insp. W11293322 JHSC Inspection. W11294696 Portable Gasoline Generator Test. W11292717 Chlorine Analyzer Maintenance. At 09:55 replaced CL-17 chlorine analyzer reagents. Taking grabs to verify analyzer on site. Time: 10:25 Grab (mg/l) Analyzer (mg/l) Free: 1.45 1.39 Verified analyzer with grabs all ok. No issues with work orders on site. Back on site to investigate the water main issue. W11384069 Water main Investigation. Met with EG and co-ordinated with them about flushing the main in front of tower. | Mount Albert North Elevated Tank | 2025-10-21
EAST | October | On site for station check. Collected weekly micro samples (W11330477). Verification of HACH CL17 Chlorine Analyzers: 13:30hrs: Free CL2 grab residual: 1.36mg/l FCL Analyzer: 1.31mg/l Total Cl2 grab residual: 150mg/l Checked station readings and verified Cl2 analyzer. All information in PWQ sheet. Checked site and equipment. Equipment out of service: None. | Mount Albert North Elevated Tank | 2025-10-29
EAST | October | Onsite for annual calibrations Informed ROC Used cal mode in scada during calibrations Asked ROC to place well pumps in manual during LIT calibration Calibrated LIT, FIT, PIT and AIT Took grabs A = 1.30mg/L G = 1.27mg/L No adjustment made Asked ROC to return well pumps back to auto and informed them that I was done on site Armed building and left site | Mount Albert North Elevated Tank | 2025-10-29
EAST | October | On site to help EG with flushing the main. While flushing analyzer went to a 5.00mg/l. This is due to the hi NTU content of the water causing a false reading. Also wells are active drain valve is open and we are pulling from the system to waste. Took a grab at 09:30 and got 1.99mg/l analyzer is currently reading incorrectly. Took grab at 09:43 reading is 1.49mg/l analyzer is 1.52mg/l. Water is clear with no more hi NTU which caused the false chlorine spike. Waterloo is going through the drain and hydrant on sight and wells have been active during this flushing. Sodium thiosulphate has also been used for dechlor while this flushing has been happening. Took another grab at 10:27 grab is 1.39mg/l and analyzer is 1.37mg/l. At 11:40 shut down flushing through the hydrant reopened inlet valve for the tower and closed the drain valve at the tower. Wasted approximately 84.6m3 while flushing. | Mount Albert North Elevated Tank | 2025-10-28
EAST | October | On site to close distribution valve from Ridge Gate Creacent that connects to the tower while Town of EG conducts unidirectional flushing. | Mount Albert North Elevated Tank | 2025-10-30
EAST | October | On site for station check, weekly micro sampling (W11256290) and monthly manganese sampling (W11257547) Tower level - 64% and draining at 12 L/S Recorded station readings in PWQ sheets Verified analyzer reading with grab chlorine residuals @11:48 Grab free: 1.25 mg/L / Analyzer: 1.20 mg/L Grab total: 1.42 mg/L Collected samples @11:50 from outlet Reviewed trends, equipment ok Station ok | Mount Albert North Elevated Tank | 2025-10-01
EAST | October | ROC called @08:32 regarding power fail alarm and UPS offline. Arrived on site, Sean P and Ernie H (electricians) working on site SCADA also shows blown fuse alarm in PAC panel. Electrical replaced the blown fuse and the site power came back. No further issues on site | Mount Albert North Elevated Tank | 2025-10-02
EAST | October | Station Check (no issues found) input data to PWQ 8:30 Verified CL17 (mg/L): Free: Grab 1.25, A 1.22 Total Grab 1.42 8:35 #11278497 & operational samples | Mount Albert North Elevated Tank | 2025-10-08
EAST | October | Under Direction of OIC (Dan Zhou) On Site for; - Perform station checks Grabs @ 11:11 hrs. FCl: 0.70 mg/L TCL: 0.87 mg/L Equipment OOS: none Station Running Nominally | Stouffville Zone 1 Booster Pumping Station | 2025-10-20
EAST | October | Onsite for annual calibrations Informed ROC and operations Operation placed duty to manual off Used cal mode on scada during the work Instruments calibrated: Suction and Discharge PITs, FIT and diesel LIT Cleared associated alarms Informed operations. Operations placed duty to auto Station running, no issues Left site | Stouffville Zone 1 Booster Pumping Station | 2025-10-22
EAST | October | Deativated Zone 1 duty. STETBR level is 67%. | Stouffville Zone 1 Booster Pumping Station | 2025-10-21
EAST | October | On site to complete station check. SRV is open to allow zone 1 water into zone 2 to drain zone 1 tower faster to improve residuals. Time: 09:55 Grab (mg/l) Free: 0.65 Total: 0.77 Verified site with grabs. Checked site. Will monitor the SRV offsite while zone 1 drains. | Stouffville Zone 1 Booster Pumping Station | 2025-10-27
EAST | October | Under Direction of OIC (Dan Zhou) On Site for; - Perform station checks Grabs @ 09:40 hrs. FCl: 0.96 mg/L TCL: 1.10 mg/L Equipment OOS: none Station Running Nominally | Stouffville Zone 1 Booster Pumping Station | 2025-10-17
EAST | October | 07:55 - 09:56 Opened FCV at 59L/s. | Stouffville Zone 1 Booster Pumping Station | 2025-10-23
EAST | October | 15:13 - 15:40 opened FCV at 50 l/s. | Stouffville Zone 1 Booster Pumping Station | 2025-10-21
EAST | October | Deactivated duty for Instrumentation team?s work. 10:48 Re-activated duty. | Stouffville Zone 1 Booster Pumping Station | 2025-10-22
EAST | October | Under Direction of OIC (Stephen Baidy) On Site for; - Perform station checks - Inspect and Exercise butterfly Valves - Generator Test Run Grabs @ 13:54 hrs. FCl: 1.04 mg/L TCL: 1.19 mg/L Generator Test: Start hours: 499.2 Start time: 13:27 hrs. *Generator Faulted (Second test in a row - generator test in September had the same issue), on start up after switching to test on the ATS the generator looses power on start up and shuts down due to AC sensing loss.* Reset generator manually on generator dash panel and generator started up and maintained. ATS switched back to auto @ 14:12 hrs. @14:29 Power switched back to main supply, generator still in cooldown. @ 14:33 Cooldown done Stop Hours: 500.3 Stop Time: 14:33 hrs. Start Fuel: 669.1 L Stop Fuel: 660.5 L Pre run checks; Battery Cell Levels: Ok Battery Terminals and Cables: Ok Oil Level: Ok Coolant Level: Ok Fluid Leaks: Ok Coolant Recirculating pump: Ok Faulty Gauges: Ok @ 14:48 BP1 Manual ON BP2 Manual off - Under Load of BP1 and Station power. Operating Current: 52 Amps Operating Frequency: 60.1 Hz Operating Voltage: 600 Volts, Engine speed: 1802 RPM Water/coolant Temp: 176 C Oil Pressure: 58 psi Engine Temp: 100 F Oil Temp: 215 F @ 14:37 Returned BP1 and BP2 back to Auto Equipment OOS: none Facility OK | Stouffville Zone 1 Booster Pumping Station | 2025-10-24
EAST | October | Under Direction of OIC (Stephen Baidy) On Site for; - Perform station checks - Respond to ROC call about power outage, and generators running Grabs @ 14:20 hrs. FCl: 0.79 mg/L TCL: 0.86 mg/L Gnerator is running, booster pumps 1 and 2 are off in auto. @ 14:43 650 L of Diesel left. Equipment OOS: none Facility OK | Stouffville Zone 1 Booster Pumping Station | 2025-10-31
EAST | October | 09:09 Placed pumps man/off. Opened FCT to 30 l/s. Deep cycling STETBR to 40%. Informed ROC. 11:47 Closed FCV. Placed pumps back to auto. | Stouffville Zone 1 Booster Pumping Station | 2025-10-20
EAST | October | Under Direction of OIC (Dan Zhou) On Site for; - Perform station checks Grabs @ 09:40 hrs. FCl: 1.11 mg/L TCL: 1.27 mg/L Equipment OOS: none Station Running Nominally | Stouffville Zone 1 Booster Pumping Station | 2025-10-10
EAST | October | Performed facility station check Data in PWQ sheet Grab @ 10:40 FCl = 1.00 mg/L TCl = 1.16 mg/L Duty: Active Equipment OOS: none Station ok | Stouffville Zone 1 Booster Pumping Station | 2025-10-03
EAST | October | Placed pumps man/off. Opened FCV to 50 l/s. Informed ROC that will revert the station to normal at the end of the shift. | Stouffville Zone 1 Booster Pumping Station | 2025-10-07
EAST | October | Under Direction of OIC (Dan Zhou) On Site for; - Perform station checks Grabs @ 10:27 hrs. FCl: 1.16 mg/L TCL: 1.44 mg/L Equipment OOS: none Station Running Nominally | Stouffville Zone 1 Booster Pumping Station | 2025-10-06
EAST | October | On site for station check Recorded grabs and verified analyzers in the shared PWQ sheet. Disregard the sim free chlorine residual drop, caused by temporarily starving the analyzer collecting a grab sample Station and equipment okay | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-10-22
EAST | October | 08:48hrs: Made adjustment to duty start/stop for residual improvement in zone1 system. Start from 50% down to 45% Stop from 95% down to 80% No issues | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-10-27
EAST | October | On site for preventative maintenance work orders with Patrick Fobert, informed Carter Dunn and Gluzen Ramos Completed Manual valve exercise Air valve flush Station housekeeping Chlorine cylinder emergency kit inspection Pump and motor inspection Generator test run Chlorine leak test JHSC inspection Chlorine scrubber inspection Crane inspection Generator test run: performed pre inspection and tested generator on load with two pumps Hours Start 453.7 Stop 454.9 Fuel Start 3005/2835 L Stop 3005/2779 L Run statistics: 26.7 battery voltage 1804 RPM 684/ 706 F exhaust temp 58 PSI oil pressure 178 F oil temperature 172 F coolant temperature Hoist system controller not connected ? will inquire with CMS Fuel fire suppression system fault generated on power transfer but cleared- okay to disregard Station and equipment okay, station returned to normal operation | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-10-23
EAST | October | On site for station check Shut down pump station to clean effluent free and total chlorine analyzers, 9:11 Verified chlorine analyzers with the station off and recorded observations in the shared PWQ sheet, 9:40, in mg/L Influent total Cl ? G 1.43, A 1.34 - Adjusted to match average of grabs Effluent free Cl ? G 1.95, A 1.97 Effluent total Cl ? G 2.78, A 2.78 Simulated free Cl ? G 1.72, A 1.81 Disregard suction header pressure hi alarm ? MKRSMR floating higher than normal (5.75M duty stop) to accommodate Kennedy isolation Inspected station equipment ? all okay | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-10-29
EAST | October | On site for station check Station readings and chlorine analyzer verification in shared PWQ, as follows in mg/L Verified analyzers, 9:20 Influent total Cl G 1.33 A 1.36 Effluent free Cl G 2.10 A 2.21 Adjusted to match average of grabs Effluent total Cl G 4.40 A 4.49 Simulated free Cl G 1.87 A 1.9 Inspected equipment, reviewed station trends, station okay and secure. | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-10-20
EAST | October | On site for chlorine cylinder bank 2 change with Joe Mazza Purged chlorine manifold prior to work. Chlorine leak occurred during cylinder change. Informed Connor Smith (RO) that we are on site working to address. Okay to disregard chlorine leak alarm Monitored startup, station and equipment okay | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-10-28
EAST | October | On site for station check Verified analyzers, 8:55, in mg/L Influent total Cl - G 1.37; A 1.44 Effluent free Cl - G 1.87; A 1.90 Effluent total Cl - G 2.72; A 2.64 Simulated free Cl - G 1.90; A 1.97 Inspected station equipment Reviewed station trends Station and equipment okay | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-10-27
EAST | October | On site to complete station check. Cleared outstanding alarms on site at 09:16. Pump 4 OOS only used as jockey pump. Influent Time: 09:35 Grab (mg/l) Analyzer (mg/l) Total: 1.23 1.27 SIM Time: 09:35 Grab (mg/l) Analyzer (mg/l) Free: 1.91 1.97 Effluent Time: 09:37 Grab (mg/l) Analyzer (mg/l) Free: 1.93 1.93 Effluent Time: 09:40 Grab (mg/l) Analyzer (mg/l) Total: 2.66 2.71 Verified analyzers with grabs. Checked site and trends. | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-10-31
EAST | October | On site for assigned station check Chlorine residuals in completed PWQ sheet Adjusted effluent free chlorine analyzer to match average of grabs, 10:50, mg/L Grab: 1.97; Analyzer: 2.19 Station and equipment okay | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-10-17
EAST | October | On site for station check and chlorine analyzer cleaning Informed RO Carter Dunn of chlorine analyzer cleaning, station placed in manual off Verified analyzers after cleaning, 9:35, in mg/L Influent total Cl - G 1.38; A 1.39 Effluent free Cl - G 2.82; A 2.80 Effluent total Cl - G 3.88; A 3.84 Simulated free Cl - G 2.38; A 2.32 Recorded observations in shared PWQ, inspected station and equipment Returned station to service at approximately 10:05 Station and equipment okay | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-10-24
EAST | October | On site to check station and equipment. System duty is active. Changed target chlorine from 2.1 mg/l to 2.2 mg/l. Chlorinator 2 DF = 81%, it is running at 43%, 58 kg/d. Chlorine booster pump 2 discharge pressure = 240 psi. Reviewed trends, station is under normal operation. | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-10-08
EAST | October | Tyson, Phil and Jack changed chlorine cylinders for the left bank. Deactivated duty and placed pumps man/off for Artour?s PCS work. Placed pumps back to auto. | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-10-02
EAST | October | On site to receive chlorine cylinders with Patrick F. Received 21 full, returned 21 empties. Performed station checks while on site. Switched pump duty so that Pump 1 and 2 are in duty 1. Chlorine grabs and station readings are entered in PWQ sheet. Changed flow set point from 150 l/s to 140 l/s. Target chlorine dose from 2.0 mg/l to 2.1 mg/l. Reviewed trends, station is under normal operation. Activated duty before leaving site to ensure operation. No issue. | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-10-07
EAST | October | On site to check station and equipment. pump duty is not active. Chlorine grabs and station readings are entered in PWQ sheet. Reviewed trends, station is under normal operation. | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-10-10
EAST | October | Under direction of OIC, Danielle Zhou. Worked with contractors to commission and test fire suppression SCADA IO. Updated OIT while plant was not running. Updated SCADA screens to reflect the changes. | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-10-02
EAST | October | On site for station check Reviewed station trends - okay Checked station pumps and pipe gallery for leaks - all okay Verified analyzers, 14:28, in mg/L Influent total Cl G 1.37 A 1.37 Simulated free Cl G 1.59 A 1.59 Effluent free Cl G 1.57 A 1.61 Effluent total Cl G 2.13 A 2.17 Station and equipment okay | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-10-03
EAST | October | Vibration testing Unable to run pumps tower to full | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-10-08
EAST | October | Performed facility station check Data in PWQ sheet Grabs @ 11:50 Influent TCl = 1.33 mg/L Analyzer = 1.36 mg/L SIM FCl= 1.67 mg/L Analyzer = 1.69 mg/L Effluent FCl = 1.77 mg/L Analyzer = 1.76 mg/L TCl = 2.38 mg/L Analyzer = 2.33 mg/L (replaced analyzer reagents) Equipment OOS: pump 4 (jockey pump) Station ok | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-10-01
EAST | October | CMU5 W11349798 STPSMR Chlorine Leak. On site responding to a chlorine leak that caused the station to shut down and interlock. Called Joe Demarco as backup for this. Cleared alarms and put station back to normal. Started station again at 00:36 checked cylinders and vents found no issues possible false alarm will inform team tomorrow of issues. | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-10-09
EAST | October | Attended site for chlorine cylinder change and fuel fire suppression system training. | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-10-02
EAST | October | 11:39 Chlorine leak alarm. System duty is off when it happened. Jack P. arrived on site to trouble shoot the leak. Could not find the leak. Opened all cylinders, activated duty and tested vacuum switches, no issues identified. | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-10-02
EAST | October | On site to complete chlorine cylinder change. Start: 44/0.0kg Stop: 44/68kg No issues with cylinder change. | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-10-09
EAST | October | On site for chlorine cylinder change and backflush, informed RO Angelica Chlorine cylinder change: Triggered chlorine leak alarm, 1.0ppm, isolated cylinders and allowed scrubber to clear the space. Reset halogen system and scrubber after changing chlorine bank 1, tare?d scale and placed chlorine system back in service. Backflush: Pumps manual off Opened WPS_DH1_MV1 Added dechlor pucks at catch basin Opened manual valve on main line under the stairs and flushed the surge valve by bypassing the pilots Closed WPS_DH1_MV1, reset alarms and placed the station back in service Informed ROC work is complete and off site, station and equipment okay | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-10-15
EAST | October | On site for station check Verified analyzers, 9:03, in mg/L Influent total Cl G 1.22 A 1.25 Effluent free Cl G 2.32 A 2.24 Increased analyzer to match average of grabs Effluent total Cl G 4.28 A 4.32 Simulated free Cl G 1.92 A 1.94 Checked station and equipment, reviewed trends, no observed issues | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-10-14
EAST | October | On site to take grabs. After multiple grabs were taken adjusted the CL-17 analyzer free residual at 11:39 from 0.59mg/l to 0.64mg/l. Deactivating duty to drain back to system to allow for more zone 1 ET water to drain to system to deep cycle zone 1 ET for better residuals. | Stouffville Zone 2 Elevated Tank | 2025-10-27
EAST | October | Under Direction of OIC (Dan Zhou) On site for; - Station Checks - Regulatory Sampling, Q4 sampling (W11247642), Micro (W11316346) - Operational Sampling Regulatory samples taken @ 13:14 hrs. Data in PWQ Excel Workbook Grabs @ 13:14 hrs. FCl: 1.17 mg/L TCL: 1.34 mg/L Analyzer FCl: 1.15 mg/L Tower Duty ON (Filling) Equipment out of Service: None | Stouffville Zone 2 Elevated Tank | 2025-10-22
EAST | October | Activated duty for Zone 2 ET at 13:25 to bring residuals up after deep cycling tower. | Stouffville Zone 2 Elevated Tank | 2025-10-27
EAST | October | Under Direction of OIC (Dan Zhou) On site for; - Station Checks - Regulatory Sampling, Micro (W11330565) - Monthly PM?s; JHSC inspection for STETTL/STW3/STPSTL, AIT maintenance, sump pit inspection, housekeeping, manual valve exercise, by pass valve exercise, heat trace inspection Regulatory samples taken @ 11:50 hrs. Data in PWQ Excel Workbook Grabs @ 11:50 hrs. FCl: 0.98 mg/L TCL: 1.11 mg/L Analyzer FCl: 0.99 mg/L AIT Maintenance Start Clean @ 12:00 hrs. Stop clean @ 12:26 hrs. @ 12:34 hrs. Grab to verify AIT FCl: 0.97 mg/L Analyzer FCl: 0.99 mg/L Tower Draining Equipment out of Service: None | Stouffville Zone 2 Elevated Tank | 2025-10-29
EAST | October | Onsite for annual calibrations Informed ROC and operations Used cal mode on scada during the work Instruments calibrated: AIT, FIT, LCV (@100%) and LIT Operations placed duty pumps in manual for LIT calibration Took grabs A = 1.10mg/L G = 1.10mg/L No adjustments made Informed operations. Duty pumps back to auto Informed ROC, armed building and left site | Stouffville Zone 2 Elevated Tank | 2025-10-22
EAST | October | On site to collect NDMA sample (W11364802) 09:05hrs: Collected Cl2 grab residuals: FCL: 0.78mg/l FCL Analyzer: 0.79mg/l TCL: 0.88mg/l | Stouffville Zone 2 Elevated Tank | 2025-10-28
EAST | October | Under Direction of OIC (Dan Zhou) On site for; - Regulatory Sampling, micro (W11256378), Flouride (W11256580) - Station checks Regulatory samples taken @ 11:20 hrs. Data in PWQ Excel Workbook Grabs @ 11:20 hrs. FCl: 1.47 mg/L TCL: 1.66 mg/L Analyzer FCl: 1.44 mg/L Tower Duty Off (Draining) Equipment out of Service: None | Stouffville Zone 2 Elevated Tank | 2025-10-01
EAST | October | Changed duty start from 60% to 40% for deep cycling. | Stouffville Zone 2 Elevated Tank | 2025-10-07
EAST | October | Under Direction of OIC (Dan Zhou) On site for; - Regulatory Sampling, micro (W11278577), NDMA (W11247828) - Station checks - Operational Sampling: Iron (Toal and Filtered), ATP Regulatory samples taken @ 09:20 hrs. Data in PWQ Excel Workbook Grabs @ 09:20 hrs. FCl: 1.29 mg/L TCL: 1.47 mg/L Analyzer FCl: 1.25 mg/L Tower Duty ON (Filling) Equipment out of Service: None | Stouffville Zone 2 Elevated Tank | 2025-10-08
EAST | October | Changed duty set point for zone 1 ET at 10:55 from 55-85% to 45-70% this is to help with residuals in the system. Will continue to monitor off site. | Stouffville Zone 1 Elevated Tank | 2025-10-27
EAST | October | Had to deactivate duty due to zone 2 ET flat lining. Deactivated duty at 20:35. | Stouffville Zone 1 Elevated Tank | 2025-10-22
EAST | October | Under Direction of OIC (Stephen Baidy) On site for; - Station Checks - Regulatory Sampling, Micro (W11330565) Reg. Sample taken @ 13:38 hrs. Grabs @ 13:38 hrs. FCl: 1.20 mg/L TCl: 1.42 mg/L Analyzer: FCl: 1.30 mg/L Equipment OOS: None Facility OK | Stouffville Zone 1 Elevated Tank | 2025-10-29
EAST | October | Check backflow preventer Mo asset tag assigned asset number 90634 | Stouffville Zone 1 Elevated Tank | 2025-10-08
EAST | October | Under Direction of OIC (Dan Zhou) On site for; - Station Checks - Regulatory Sampling, micro (W11256378), Flouride (W11256580) Reg. Sample taken @ 11:56 hrs. Grabs @11:56 hrs. FCl: 1.07 mg/L TCl: 1.22 mg/L Analyzer: FCl: 1.08 mg/L Equipment OOS: None Facility operating nominally. | Stouffville Zone 1 Elevated Tank | 2025-10-01
EAST | October | Under Direction of OIC (Dan Zhou) On site for; - Station Checks - Regulatory Sampling: micro (W11278577) - Operational Sampling: ATP, Iron (total and filtered) Reg. Sample taken @ 08:35 hrs. Grabs @ 08:35 hrs. FCl: 1.28 mg/L TCl: 1.44 mg/L Analyzer: FCl: 1.35 mg/L Equipment OOS: None Facility operating nominally. | Stouffville Zone 1 Elevated Tank | 2025-10-08
EAST | October | On site to complete station check. Collecting weekly Bac-t Sample. W11298642 Weekly Bac-t Sample. Time: 14:40 Grab (mg/l) Analyzer (mg/l) Free: 1.26 1.25 Total: 1.46 Cleared all outstanding alarms at 14:33. Checked site and trends. Verified analyzers with grabs all ok. | Stouffville Zone 1 Elevated Tank | 2025-10-14
EAST | October | On site for station check and sampling Micro sampling, YD # W11330593, as well as nitrification monitoring sample, collected from the North cell at 11:00. Verified the total chlorine analyzer at the time, in mg/L Free Cl grab: 0.07 Total Cl grab: 1.40 Total Cl analyzer: 1.51 Adjusted analyzer to match average of grabs Recorded observations in the shared PWQ and reviewed station trends. Station and equipment okay | Markham PD6 Reservoir | 2025-10-29
EAST | October | On site to fix station flood float | Markham PD6 Reservoir | 2025-10-16
EAST | October | On site for station check and sampling while station is draining Collected samples and verified total chlorine analyzer, 10:45, Sample YD #s: W11247166, W11316374 Free Cl: grab: 0.05 mg/L Total Cl: grab: 1.30; analyzer: 1.38 Recorded observations and advanced operational monitoring results in the shared PWQ sheet Station and equipment okay | Markham PD6 Reservoir | 2025-10-22
EAST | October | On site for preventative maintenance work orders, informed RO Christian Van Beek that he is to disregard alarms for the duration of this work Completed Chlorine analyzer maintenance East hatch clean up Sump pump test Dehumidifier inspection and cleaning High low water level alarm test Station flood alarm test JHSC inspection External venting screens inspection Air valve inspection Station and equipment okay | Markham PD6 Reservoir | 2025-10-28
EAST | October | On site to check station and collect sample. Reservoir is on a draining cycle. 2 of the emergency lights are beeping. Followed up with Property Services Branch since they have serviced the recently. 09:32 grab chlorine residual from north cell, FCL = 0.05 mg/l, TCL = 1.46 mg/l. Analyzer total reading = 1.46 mg/l. Collect bac-t sample. YD W11278605 Performed advanced monitoring with SL1000. See PWQ sheet for details. Reviewed trends, no major concerns. Will request ROC to deep cycle the reservoir. | Markham PD6 Reservoir | 2025-10-08
EAST | October | On site for station check and operational monitoring & regulatory sampling: Micro (W11256406) Data in PWQ sheet Sample and grabs collected from NORTH cell @ 12:55 FCL: 0.02 mg/L TCL: 1.36 mg/L Analyzer TCl: 1.39 mg/L Reservoir Level = 49% Draining @ 425 L/s Station ok | Markham PD6 Reservoir | 2025-10-01
CENTRAL | October | Attending site to add diaphragm rupture sensors to both fluoride pumps. Caused alarm on pump#2 while installing sensor. Donny Moses assisted in getting fluoride pumps back to normal operation. Low fluoride alarm came in (and Chlorine analyzer alarm because the fluoride probe is part of the chlorine analyzer system). Alarms were cleared and system is back to normal operation. | Keswick Water Treatment Plant | 2025-10-27
CENTRAL | October | On site to complete preventative maintenance work orders, Informed ROC. When arrived noticed Filter 1 BKWS OOS alarm outstanding on SCADA from yesterday night 8:36pm, it appears that both filter went back wash together since Filter 2 started first the backwash tank level was full and when filter 1 started it?s backwash it interlocked because of backwash tank level hi. This morning around 7:30am when backwash tank level dropped below 0.80m filter 1 backwash was initiated. Ryan B changed clear well start set point to 4m from 4.1m and adjusted clear well cut off set point to 4.2m from 4.3m. Ryan B changed filtration set points from high lift mode to flow mode to top up clear well and once it was filled set points were placed back to normal setting. While doing maintenance on PACL pumps pre injection free Cl hihi switch alarm came in @ 13:45 for a reading then it slowly came down. PACL P1 OOS for night discharge line replacement. Informed on call OP. Did shoreline observation @ 14:40 - Plant not running when arrived - Did filter performance check all ok - Ryan B did general housekeeping in High Lift room & I did housekeeping in low lift pump room - Placed Low lift pumps in manual off to do NTU analyzer cleaning and maintenance for raw water also turned settling tanks drain valve in manual during the cleaning. Placed back to normal and 30 mins apart after cleaning was done @ 12:20pm - No issues found | Keswick Water Treatment Plant | 2025-10-16
CENTRAL | October | Onsite for station check. Placed high lifts in manual off. Outstanding low lift p3 alarm and backwash pump 1 alarm. Nothing found on vfd. Cleared alarms and placed back in service. Turbidity trend of the filter effluent has decreased on start up to below 0.17 ntu spike. Disabled FTW on start up and placed effluent valves to run on flow mode. 09:56 accidentally toggled filter 2 backwash. Immediately aborted. Backwash oos alarm triggered due to high level in wash water holding tank and low clear well level. Cleared alarm with no issues. 10:27 flushed raw water sample line. Topped up pacl day tanks. 11:14 placed high lifts back in auto. Filter 2 required a reset to switch into production mode. Completed station rounds. Verified analyzers and entered data into process and lab datasheets sheets. No issues remaining on site. | Keswick Water Treatment Plant | 2025-10-31
CENTRAL | October | Assisted Divya Patel (see previous elog entry) with PMs. Site returned to normal operation following work, PACl P1 OOS for discharge line replacement, on-call OP informed, no other new issues found while on-site. Contractors on-site for ongoing TSSA upgrades. | Keswick Water Treatment Plant | 2025-10-16
CENTRAL | October | Onsite for station check. 09:30 station off in standby. Replace low lift chlorine analyzer reagents. Adjusted high lift flow set point from 90 to 100 l/s. Place high lift p2 and p3 to duty 1. 10:00 Completed filter performance review, both 100%. Found SCADA UFRV calculation not working. Notified Chris Scott. Will not affect plant operations. Phil D. Remotely placed high lifts in manual off and activated Georgina duty 1. Filters began to Filter to waste even with high lifts off. After filter 1 committed ftw I disabled the FTW as turbidity spike in start up have been trending lower readings. 11:10 places high lifts back in auto. 11:20 filter 2 turbidity increased quickly and I re enabled ftw on filter 1. 11:21 filter 2 hi hi turb alarm trigger reached at 0.36 ntu. Effluent valve completed closing. Some small amount of water at this turbidity may have passed effluent before closing but not enough to register as overall filter performance remains at 100%. 14:30. I reenabled FTW on filter 1. Filter 2 backwash service OOS triggered while filter 1 undergoing backwash due to headless. Reset filter 1 FTW and filter 2 backwash proceeded. Post chlorine cylinder 2 changed with Ben Hess. Completed station round, verified data and recorded in process sheets. No issues remaining. | Keswick Water Treatment Plant | 2025-10-24
CENTRAL | October | Did in house lab, station check and completed outstanding PM?s from yesterday informed ROC, (Please see log entry from Donald M) No other issues found. | Keswick Water Treatment Plant | 2025-10-17
CENTRAL | October | 07:50 remotely placed high lifts in manual off. Filter top turbidity probe is giving erratic readings and will investigate when I get to site. | Keswick Water Treatment Plant | 2025-10-21
CENTRAL | October | Completed filter performance check: filter #1- 100%, filter #2- 100% | Keswick Water Treatment Plant | 2025-10-30
CENTRAL | October | Filter Performance reviewed, both filters 100% | Keswick Water Treatment Plant | 2025-10-27
CENTRAL | October | Completed filter performance check: filter 1- 100%, filter 2- 100% | Keswick Water Treatment Plant | 2025-10-31
CENTRAL | October | Checked filter performance, both 100% | Keswick Water Treatment Plant | 2025-10-24
CENTRAL | October | Onsite for station check. Filter 1 back wash is interlocked due to clear well water reserve to low and waste wash water holding tank level to high. Adjusted filter to waste flow rate from 35 l/s to 30 l/s to decrease wasted water loss. Adjusted high lift mode set point flow rate increase from 5% to 10% to increase rate of clear well filling. 09:20 rotated wash water transfer pump duty to pump 1 as it transfers water and can empty wash water holding tank faster. 10:20 manually ran filter 1 effluent valve to top up clear well. 11:13 filter 2 backwash interlock cleared and backwash. Filter 1 placed back in auto. 11:21 verified raw water analyzers. 11:52 clear well Lo alarm triggered as filter 1 backwashed. Wash stage already complete and backwash completed with no issues. 12:12 verified treated water analyzer. Free chlorine grab 1.71. Analyzer 1.66. Total chlorine grab 1.98. Analyzer. 1.95. Collected lab and process data, entered information into process sheets. Filter performance review, no issues and both filters at 100%. No issues remain on site. | Keswick Water Treatment Plant | 2025-10-20
CENTRAL | October | Filter performance check for Oct 22/23 both days 100% | Keswick Water Treatment Plant | 2025-10-23
CENTRAL | October | Filter performance reviewed both filters 100% Adjusted flow to turbidimeter, air in tubing was causing higher than normal treated water turbidity. | Keswick Water Treatment Plant | 2025-10-28
CENTRAL | October | Under direction of OIC Daily filter performance review via scada @ 9:15 PM both 100% all ok | Keswick Water Treatment Plant | 2025-10-16
CENTRAL | October | Under direction of OIC, daily filter performance review via scada both filters 100% all ok @ 3:40 PM | Keswick Water Treatment Plant | 2025-10-17
CENTRAL | October | Onsite for station check. Outstanding alarms: low lift pump 3 vfd not ready. Raw water turbidity fault, settled water turbidity fault , treated water total/fluoride analyzer faulted (due to low fluoride on shut down). 09:13 high lift p3 is in manual on, activated by ROC as gwtp offline for the day. Placed high lift p4 on in able to reach setpoint of 100 L/s. Notified ROC. Topped up pacl day tanks. Low lift p3 vfd has no errors/faults. Reset SCADA alarm with no issues. Low lift raw sample pump discharge flange leaking, causing low flow fail to turbidity analyzer. Tightened and analyzer fault cleared. 11:25 filter 2 backwashed due to head loss. Did not go back into production. Placed high lifts back in auto. Activated Georgina duty 1. Notified roc and Stephen Baidy (gwtp operator). Filter top settled water sample pump tubing element leaking. Replaced. 11:52 Cleaned turbidity probe. Cleared settled water turbidity alarms. 12:12 Eric S onsite and added fluoride dosing pump leak detection settings. Fluoride pumped 2 stopped during upgrade and lolo treated water fluoride alarm triggered. 12:16 toggled to fluoride p1. Eric placed p2 back into service. Tested with no further issue?s. 14:20 adjusted chlorine post injection manual dosage from 152 to 145% (typo corrections). Completed lab work, verified analyzers and entered data into process sheets. No issues remaining on site. | Keswick Water Treatment Plant | 2025-10-27
CENTRAL | October | Onsite for station check and sampling. COC W11330621. Outstanding treated water fault with fluoride analyzer reading low on startup. Fluoride residual improved shortly to typical reading and cleared alarm. Topped up fluoride and pacl day tanks. 09:45 collected raw water samples 11:20 collected treated water samples. Verified analyzer (mg/l): Treated free chlorine grab: 1.77 analyzer : 1.73. Treated Total chlorine grab: 1.98/2.00/1.98 Analyzer 2.17. Adjusted analyzer to match grab average. Reviewed filter daily performance. Both filters 100% and no issues. Collected process and lab data, entered into process sheets. Completed shoreline observation. No issues found. | Keswick Water Treatment Plant | 2025-10-29
CENTRAL | October | Completed filter performance check: filter 1- 100%, filter 2- 100% | Keswick Water Treatment Plant | 2025-10-29
CENTRAL | October | Onsite for station check. Plant high lifts in manual off. 09:30 Reconnected pacl 1 discharge line and fitting. Placed back in service. 10:13 calibrated filter 1 and 2 effluent turbidity analyzer. Notified roc of work. 10:53 calibrated treated water turbidity analyzer. Cleaned settled water turbidity probe. 12:20 shoreline observation ok. 13:20 changed post chlorine cylinder A with Divya Patel. Completed station rounds and verified analyzers. Entered data into process and data sheets. Yash onsite to work on high lift pump signalling. Chris Scott made adjustments to the chlorine system calculation to match region standard. Manual post chlorine discharge seeping changed from 78 to 156 %. Actual dosage has not changed. Tested by placing high lifts back in auto at 13:53. Adjusted duty stop from 85 to 87%. Verified chlorinator and rotameter numbers match typical readings. 14:30 adjusted system duty back to 85% tower fill. No issues found. | Keswick Water Treatment Plant | 2025-10-17
CENTRAL | October | On site to complete station check and to collect weekly bacti samples W11316402, to collect Algea, Microcystin, geomib samples W11316224 & to collect GLIP samples W11316741. Donald M on site to assist. - We started manual concurrent backwash for Filter 1 @ 10:44am we informed ROC - following intelex procedure - Plant running when arrived - Entered data into PWQ sheet & collected samples - Donald M did in house lab - Did filter performance check all ok - Topped up PACL day tank - Topped up fluoride day tank - Topped up PACL wash water tank - No issues found Treated Free Cl2 @ 10:00am G: 1.80mg/L A: 1.83mg/L Treated total Cl2 10:00am G: 2.19mg/L A: 2.19mg/L | Keswick Water Treatment Plant | 2025-10-22
CENTRAL | October | Under direction of OIC (Ben H) Filter performance review via scada for yesterday Oct 21, 2025 Both filters 100% all day | Keswick Water Treatment Plant | 2025-10-22
CENTRAL | October | Onsite to investigate outstanding settled water turbidity high high alarm. The settled water analyzer trend is erratic and spikes to 25 ntu during last run cycle at 06:13. 12:00 station high lifts currently in manual off Finished water fluoride and total chlorine faulted. 12:15 placed settled water channel lit and turb probe in calibration mode. Cleaned sensors. Lowered channel level by opening settled water drain valves and placing low lifts in manual off. Cleaned channel. Placed analyzers back in service and pumps back to auto. 13:20 manually started station to test analyzer during production. 14:90 tested turbidity. Grab:0.206 ntu. Analyzer: 0.105 ntu. Analyzer appears stable and with no issues. Treated fluoride and total analyzer faulted due to low fluoride reading when station offline. No other issues remain. Placed high lifts back in auto. Adjusted post injection chlorine dosing from 156 to 152%. | Keswick Water Treatment Plant | 2025-10-21
CENTRAL | October | Did Daily Filter turbidity Performance Review check all ok. | Keswick Water Treatment Plant | 2025-10-02
CENTRAL | October | Did Daily Filter turbidity Performance Review check all ok. | Keswick Water Treatment Plant | 2025-10-01
CENTRAL | October | Did Daily Filter turbidity Performance Review check all ok. | Keswick Water Treatment Plant | 2025-10-03
CENTRAL | October | Completed filter performance check: filter #1- 100%, filter #2- 100% | Keswick Water Treatment Plant | 2025-10-08
CENTRAL | October | Onsite to complete station check and sampling. COC W11278455 and W11278633. Found low lift p1 and p3 both in duty 1. Placed p3 in duty 3. 08:53 collected low lift raw samples. Divya Patel on site. 10:23 completed shoreline observation. Completed filter performance check. Both at 100% and no issues. 11:02 Divya collected treated water samples and Verified treated water analyzer (mg/l) Free chlorine grab 1.49. Analyzer 1.53. Total chlorine grab 1.76/1.78/1.81. Analyzer 1.98. Adjusted total to match grab average. Fluoride grab 0.66. Analyzer 0.68. Turbidity grab 0.083 ntu. Analyzer 0.087 ntu. 13:00 Completed filter top free chlorine analyzer maintenance. Verified analyzer. Free Grab 0.02 analyzer 0.02. Completed PRV inspection and maintenance. Exercised valve. Replaced post injection right chlorine cylinder. Topped up Pacl and fluoride day tanks. Completed station rounds, lab work and entered data into process sheets. 13:48 Divya P left site. No other new issues found. | Keswick Water Treatment Plant | 2025-10-08
CENTRAL | October | Completed filter performance check: Filter #1- 100%, Filter #2- 100% | Keswick Water Treatment Plant | 2025-10-09
CENTRAL | October | Reviewed filter performance trends for September 25 and 30 2025. Both filter performance 100%, no issues. | Keswick Water Treatment Plant | 2025-10-09
CENTRAL | October | Onsite to complete work orders. Chris T and Tyler S onsite to repair raw water sample line. 09:30 places all low and high lift pumps in manual off. 09:40 low lift chlorine analyzer maintenance. Replaced settled water chlorine analyzer Maintenance completed repair to raw water line. Reconnected turbidity and ph analyzer to raw water line. Placed back in service. Created work order for maintenance to investigate raw water sample pump for lower then typical flow. 10:39 verified low lift analyzer (mg/l): Free 0.03. Analyzer: 0.02 Total: 0.08. Analyzer: 0.13. 10:58 cleaned and verified clear well influence analyzer. Free 1.33. Analyzer: 1.29. 11:11 cleaned and verified treated free chlorine analyzer. Free 1.33. Analyzer: 1.28. 11:35 Cleaned and verified total analyzer. Total grab 1.72. Analyzer: 1.77. 12:50 cleaned and calibrated fluoride analyzer. Grab 0.66 mg/l. Adjusted analyzer offset to match. 13:15 places all pumps back in auto. Started duty 1. To test analyzer in service. 13:50 treated torso grabs. 1.62/1.60/1.60. Analyzer: 1.74 adjusted to match grabs. Fluoride grab 0.81. Analyzer 0.83. No other new issues found. | Keswick Water Treatment Plant | 2025-10-07
CENTRAL | October | On site to complete preventative maintenance work orders. With Donald M & informed ROC. - Plant running when arrived - Did air blower inspection - Did Chlorine inspection check - Did emergency repair kit check - Did JHSC of site - Did general housekeeping of lab and kitchen and ground floor - Did wash water transfer pump maintenance - Did tuber settler tank cleaning - No issues found | Keswick Water Treatment Plant | 2025-10-09
CENTRAL | October | On site to complete station check and in house lab, Ferguson electric team on site to drill holes for pulling wires for PAC panel, internet & security. - Plant not running when arrived - Did filter performance check all ok - Topped up PACL in day tanks - No issues found Treated Free Cl2 @ 10:33am G: 1.53mg/L A: 1.49mg/L Treated total Cl2 10:33am G: 1.89mg/L A: 1.83mg/L | Keswick Water Treatment Plant | 2025-10-10
CENTRAL | October | 09:40 onsite for station check, shoreline observation, and sampling. Coc W11298698, w11298512, W11247926. 10:27 collected raw water samples. Verified low lift analyzer and entered data into process sheets. Topped up pacl and fluoride day tanks. 10:30 shoreline observation. No issues. 12:40 Collected treated water samples. Verified treated analyzer (mg/l): Free chlorine grab 1.73. Analyzer 1.68. Total chlorine grab 2.04. Analyzer 2.00. Fluoride grab 0.625 analyzer 0.72. Adjusted fluoride analyzer to match grab. Filter daily performance check. No issues. | Keswick Water Treatment Plant | 2025-10-14
CENTRAL | October | Onsite to complete station check and run diesel generator. High lift pumps are in manual off. Raw water turbidity fualt alarm triggerd due to low sample flow. Adjusted sample flow higher and cleared alarm. Placed lo lift pumps in manual off. 10:48 Notified ROC of generator test. Preinspection of generator oil, battery and coolant levels ok. Initiated test. Generator fuel 2021 L. Generator hours 915.9 Power tranfer tripped chlorine halogen fault alrm, generator ATS not in auto, and filter 1 and 2 backwash power inturrupted alarms triggered. No backwash was occuring and reset all alarms 11:24 placed low and high lift pumps back in auto. High lift pump 4 faulted with low flow. Reset and pump 3 ran with no issues. 12:33 Power blip occured while still on diesel generator and triggered all ususal alarms during a power transfer but source power resumed running on generator. Notified maintenance team lead Tyler Z. Placed low and high lifts back in manual off. 13:19 fluoride grab (mg/1): 0.613. Analyzer: 0.73. Adjusted offset to better match grab. 13:30 completed generator test. Fuel: 1971 generator hours: 916.7. Generator actually ran for over 2 hours and 40 minutes but the generator hour meter reads 0.8 hours. Completed station rounds and lab work and entered data into process sheets. Topped up day PACL tanks. Chrome 13:56 placed all low and high lifts back to auto. No other issues found on site. | Keswick Water Treatment Plant | 2025-10-03
CENTRAL | October | Completed filter performance check: Filter #1- 100%, Filter #2- 100% | Keswick Water Treatment Plant | 2025-10-10
CENTRAL | October | Completed filter performance check: Filter #1- 100%, Filter #2- 100% | Keswick Water Treatment Plant | 2025-10-14
CENTRAL | October | Did in house lab and help Donald M with station check and did temporary fix to raw water going into NTU & pH analyzer. | Keswick Water Treatment Plant | 2025-10-06
CENTRAL | October | As directed by OIC Ben H Daily filter performance review via scada, both filters 100% All ok (15:45). | Keswick Water Treatment Plant | 2025-10-15
CENTRAL | October | Onsite for station check and sampling. COC include: Q4 - w11215761 Micro - W11256434 Microcystic - w11256248 The/backwash - w11256220 08:54 station offline and duty 1 standby. Outstanding raw water turbidity fault alarm from sept 30 at 11:06. Adjusted sample flow up and cleared alarm. 09:18 initiated filter 2 backwash. 09:31 completed shoreline observation. No issues. Completed filter performance review. F1 and f2 are 100%. No issues. 10:00 collected backwash effluent raw sample. 1010 collected raw water samples. Verified analyses and entered data into lab data sheets. Topped up day pacl and fluoride chemical tanks. 11:16 Activated duty 1 to start plant. 11:35 collected prefiltration DOC raw water sample. 11:45 collected post filtration doc raw water sample. 11:55 collected backwash effluent treated sample. 12:05 collected treated water samples and verified analyzers (mg/l) Free chlorine grab 1.75. Analyzer 1.70 Total chlorine grab 2.01. Analyzer 2.05. Recorded lab and process data into spreadsheets. No new issues found on sites. | Keswick Water Treatment Plant | 2025-10-01
CENTRAL | October | Did Daily Filter turbidity Performance Review check all ok. | Keswick Water Treatment Plant | 2025-10-07
CENTRAL | October | Onsite to change pre and post chlorine cylinders with Divya Patel. 13:47 chlorine leak alarm triggered when testing regulator to confirm vent failed. Notified ROC and had them shut down Lo and high lifts. Replace regulator. Changed cylinder with no more issues. Reset chlorine emergency shut off valve reset. 14:05 places Lo and high lift pumps back in auto. Manually triggered filter to water on each filter. High lift pump 2 vfd faulted (fan cooling) on start up. Reset vfd with no further issues. Adjusted raw water sample pump speed higher as flow to raw water turn is low. Cleared alarm with no issues. | Keswick Water Treatment Plant | 2025-10-02
CENTRAL | October | Did Daily Filter turbidity Performance Review check all ok. | Keswick Water Treatment Plant | 2025-10-06
CENTRAL | October | Reviewed daily/monthly filter performance - both filters at 100% for the month, all okay | Keswick Water Treatment Plant | 2025-10-13
CENTRAL | October | Onsite with Divya Patel to perform station check. 11:30 high lifts are in manual off. Outstanding treated total chlorine and fluoride analyzer fault. No issues found. Cleared alarm. Outstanding raw water turbidity fault. 12:00 found the discharge piping to the raw water sample pump cracked. Created w11341279 for maintenance to repair. Moved raw ph and turbidity analyzer to discharge off low lift header for the meantime. Notified Dan Zhou and ROC of issues. SCADA raw water analyzer is now reading high, around 1.0 ntu as the analyzer is reading water from the discharge side of low lift pumps. 13:40 places high lift pumps back in auto. Cleared fluoride air lock in pump 1. Topped up daytime pacl tanks. Replace influence clear well free and treated free chlorine analyzer reagents. Collected water samples and completed lab work. Entered data into pwq and lab data sheets. No other issues found. | Keswick Water Treatment Plant | 2025-10-06
EAST | October | On site for station check, weekly micro sampling (W11317177) and Q4 sampling (W11247778) Tower level - 78% and filling at 39.5 L/s Recorded station readings in PWQ sheets Verified analyzer reading with grab residuals @11:15 Grabs free: 1.54, 1.52, 1.54 mg/L / Analyzer: 1.67 mg/L - adjusted based on grabs Grab total: 1.85 mg/L Collected samples @11:20 (Micro and Q4) Collected operational ATP sample for in-house lab Reviewed trends, equipment OOS: none Station ok | Sutton Elevated Tank | 2025-10-22
EAST | October | On site for station check and weekly micro sampling (W11331242) Tower level - 89% and filling at 28 L/s Recorded station readings in PWQ sheets Verified analyzer readings with grab residuals @11:25 Grab free: 1.81 mg/L / Analyzer: 1.78 mg/L Grab total: 2.15 mg/L Collected micro sample @11:28 Reviewed trends, equipment OOS: None Station ok | Sutton Elevated Tank | 2025-10-29
EAST | October | On site to complete station check. Collecting weekly Bac-t Sample. Collecting VOC samples. W11257466 Weekly Bac-t Sample. W11257438 VOC Samples. Time: 10:25 Grab (mg/l) Analyzer (mg/l) Free: 1.10 1.16 Total: 1.31 Verified analyzer with grabs. Checked site and trends. | Sutton Elevated Tank | 2025-10-01
EAST | October | On site to complete station check. Collecting weekly Bac-t Sample. W11279514 Weekly Bac-t Sample. Time: 10:25 Grab (mg/l) Analyzer (mg/l) Free: 1.14 1.18 Total: 1.43 Verified analyzer with grabs. Checked site and trends. No outstanding alarms on site. No OOS equipment on site. | Sutton Elevated Tank | 2025-10-08
EAST | October | On site for station check and weekly micro sampling (W11331256) Tower level - 82% and filling at 15 L/s Recorded station readings in PWQ sheets Verified analyzer readings with grab chlorine residuals - no adjustments needed Inlet: @10:20 Grab free: 2.20 mg/L / Analyzer: 2.19 mg/L Grab total: 2.48 mg/L / Analyzer: 2.59 mg/L Outlet: @10:25 Grab free: 1.83 mg/L / Analyzer: 1.76 mg/L Grab total: 2.46 mg/L / Analyzer: 2.43 mg/L Collected micro sample @10:31 from outlet Reviewed trends, equipment OOS: None Station ok | Keswick Deer Park Elevated Tank | 2025-10-29
EAST | October | On site for monthly maintenance - informed ROC - Portable gasoline generator test - Low temperature alarm test - Heat trace inspection - JHSC health and safety inspection - Manual valves exercises - Ventilation inspection - Housekeeping - Chlorine analyzer maintenance (inlet and outlet) Verified analyzer readings with grab chlorine residuals: Inlet: @09:53 Grab free: 1.58 mg/L / Analyzer: 1.63 mg/L Grab total: 2.04 mg/L / Analyzer: 1.99 mg/L Outlet: @10:00 Grab free: 1.67 mg/L / Analyzer: 1.69 mg/L Grab total: 2.03 mg/L / Analyzer: 2.11 mg/L Equipment all back to normal, informed ROC Station ok | Keswick Deer Park Elevated Tank | 2025-10-16
EAST | October | On site to complete station check. Time: 09:40 Inlet Grab (mg/l) Analyzer (mg/l) Free: 1.80 1.75 Total: 2.18 2.20 Time: 09:45 Outlet Grab (mg/l) Analyzer (mg/l) Free: 1.75 1.79 Total: 2.20 2.29 Verified analyzers with grabs all ok. Checked site and trends. No OOS equipment. No outstanding alarms. | Keswick Deer Park Elevated Tank | 2025-10-24
EAST | October | On site for station check and equipment verifications Duty is not active - tower level - 71% and draining at 22 L/S Recorded station readings in PWQ sheets Verified analyzer readings with grab chlorine residuals - made the following adjustments Inlet free: 1.71 mg/L ?-> 1.80 mg/L Reviewed trends, equipment ok Station ok | Keswick Deer Park Elevated Tank | 2025-10-20
EAST | October | On site to complete station check. Collecting weekly Bac-t Samples. Collecting VOC samples. W11257480 Weekly Bac-t Sample. W11257452 VOC Samples. Time: 09:35 Inlet Grab (mg/l) Analyzer (mg/l) Free: 1.64 1.66 Total: 2.01 1.94 Time: 09:40 Outlet Grab (mg/l) Analyzer (mg/l) Free: 1.65 1.68 Total: 1.94 1.99 Verified analyzers with grabs. Checked site and trends. | Keswick Deer Park Elevated Tank | 2025-10-01
EAST | October | On site to complete station check. Collecting weekly Bac-t Samples. W11279528 Weekly Bac-t Samples. Time: 09:35 Inlet Grab (mg/l) Analyzer (mg/l) Free: 1.64 1.69 Total: 1.96 1.91 Time: 09:40 Outlet Grab (mg/l) Analyzer (mg/l) Free: 1.63 1.67 Total: 1.93 1.97 Verified analyzers with grabs all ok. Checked site. | Keswick Deer Park Elevated Tank | 2025-10-08
EAST | October | On site to complete station check. Time: 09:15 Inlet Grab (mg/l) Analyzer (mg/l) Free: 1.74 1.76 Total: 2.14 2.07 Time: 09:20 Outlet Grab (mg/l) Analyzer (mg/l) Free: 1.76 1.80 Total: 2.02 2.10 No outstanding alarms on site. No OOS equipment on site. Verified analyzers with grabs all ok. | Keswick Deer Park Elevated Tank | 2025-10-03
CENTRAL | October | Attending site to check Free Chlorine analyzer issue (W11393045). Push buttons were found to be failing. Replaced analyzer push-button switches and verified reading. All associated alarms were cleared. ROC was notified before and after maintenance work. | Keswick West Park Reservoir | 2025-10-27
CENTRAL | October | On-site to assist York Region Linear OPs Gary Peters and Harsh Patel with trial isolation for air valve work. Informed ROC. Changed system controlling storage to KSETWB. Isolated tank from distribution system at 10:20. In order to achieve full isolation, MV2 was closed as it appears MV1 passing slightly, this caused analyzers to read incorrectly from 11:55 to 13:06 (verified analyzers below, mg/L) when MV2 was opened following successful trail isolation period. Free Cl (13:06): G: 1.37 A: 1.36 Total Cl (13:06): G: 1.64 A: 1.69 Opened isolation valves at 13:17 following Cl analyzer verification and returned tank to be the controlling storage for the system. System returned to normal operation. Will create WO for CMS to adjust limits on MV1/MV2 as MV2 received over torque alarm on initial closing, and MC1 appears to be passing. No other new issues found while on-site. | Keswick West Park Reservoir | 2025-10-20
CENTRAL | October | On site to complete station check. - Tower level draining @78% @54L/s - Entered data into PD sheet - Check trends all okay - Checked reagents - Equipment all okay - No issues found Free Cl grab @ 8:31am G: 1.41mg/L A: 1.47mg/L Treated Total Cl grab @ 8:30am G: 1.64mg/L A: 1.66mg/L | Keswick West Park Reservoir | 2025-10-17
CENTRAL | October | On site to complete station check & to collect weekly bacti samples W11317316 - Tower level draining @80% @35L/s - Entered data into PD sheet & collected samples - Adjusted chlorine manual setpoint from 122% to 120% for both Chlorinators - Check trends all okay - Checked reagents - Equipment all okay - No issues found Free Cl grab @ 2:29pm G: 1.52mg/L A: 1.57mg/L Treated Total Cl grab @ 2:29pm G: 1.73mg/L A: 1.74mg/L | Keswick West Park Reservoir | 2025-10-22
CENTRAL | October | Onsite to complete station check. 08:22 Reservoir level at 78% and draining at 1 l/s. 08:26. Verified analyzer (mg/l). Free chlorine: 1.48 Analyzer: 1.48. Total Chlorine grab: 1.77. Analyzer: 1.78. No other new issues found. | Keswick West Park Reservoir | 2025-10-27
CENTRAL | October | Onsite to complete station check and sampling. 08:04 Reservoir level at 80% and draining at 40 l/s. 08:12. Verified analyzer (mg/l) and collected sample. Free chlorine: 1.43/1.46/1.46 Analyzer: 1.56. Adjusted to match grab average. Total Chlorine grab: 1.78. Analyzer: 1.82 No other new issues found. | Keswick West Park Reservoir | 2025-10-29
CENTRAL | October | On site at 1100 to investigate mv4 passing while closed and mv3 torque fault. We called Ben Hess to confirm that we will be operating the valves. He placed the woodbine tower as the control tower for the duration of our work. I called ROC to inform them of our work happening. We tested mv4 closed and witnessed 4 L/s of Flow still on the flow meter. Ernesto then adjusted the close limits on the valve till we saw no flow when valve was closed. Placed valve into remote and tested two cycles on the valve to confirm fix. Left mv 4 in manual open on scada. We then tested mv3 an noticed it faulted on over torque before reaching its closed limit. We placed it in manual and Ernesto again adjusted the limit on the close status so valve would have no flow and not cause a fault. We cleared alarms on mv 3 @1215 and tested two cycles of the valve to confirm fix left valve into remote and manual open on scada. Under direction of oic. | Keswick West Park Reservoir | 2025-10-28
CENTRAL | October | On site to complete station check. Ernesto from Electrical team on site to check exhaust fan in the chamber another mate is coming soon to assist him. - Tower level draining @66% @96L/s - Entered data into PD sheet - Check trends all okay - Checked reagents - Equipment all okay - No issues found Free Cl grab @ 8:32am G: 1.25mg/L A: 1.27mg/L Treated Total Cl grab @ 8:32am G: 1.50mg/L A: 1.49mg/L | Keswick West Park Reservoir | 2025-10-10
CENTRAL | October | Did CL17 analyzer cleaning and verification also primed it after cleaning it. Treated free @11:29am G: 1.36mg/L A: 1.24mg/L - adjusted analyzer to 1.36mg/L to match grabs Treated total Cl @11:33am G: 1.63mg/L A: 1.64mg/L Informed ROC before & after doing work. | Keswick West Park Reservoir | 2025-10-02
CENTRAL | October | Onsite to complete station check. Changed chlorine analyzer reagent. 09:40 Reservoir level at 74% and draining at 51 l/s. 09:45. Verified analyzer (mg/l): Free chlorine: 1.42. Analyzer: 1.41 Total Chlorine grab: 1.71. Analyzer:1.67 Adjusted manual chlorine dosing factor from 125% to 122. Chlorine room vestibule supply fan and basement supply fan remain OOS.. Building flood alarm remains OOS. No new issues found. | Keswick West Park Reservoir | 2025-10-03
CENTRAL | October | On site to complete preventative maintenance work orders informed ROC. - Tower draining when arrived - Did CL17 analyzer cleaning & verification down below - Did chlorine system inspection and chlorine leak testing - Did general housekeeping of site - Did JHSC of site - Did portable gen run test - No other issues found Free Cl grab @ 11:40am G: 1.29mg/L A: 1.30mg/L Treated Total Cl grab @ 11:40am G: 1.54mg/L A: 1.52mg/L | Keswick West Park Reservoir | 2025-10-07
CENTRAL | October | Onsite to complete station check. 07:33 Reservoir level at 78% and draining at 61 l/s. 07:38. Verified analyzer (mg/l): Free chlorine: 1.36. Analyzer: 1.38 Total Chlorine grab: 1.59. Analyzer: 1.60 No new issues found. | Keswick West Park Reservoir | 2025-10-06
CENTRAL | October | Onsite to complete station check and sampling. COC W11257710 and W11257696 07:48 Reservoir level at 77% and draining at 76 l/s. 07:55. Verified analyzer and collected samples. Free chlorine: 1.39. Analyzer: 1.40 Total Chlorine grab: 1.64. Analyzer: 1.70. No new issues found. | Keswick West Park Reservoir | 2025-10-01
CENTRAL | October | On site to make repairs to the chamber supply fan, the chamber flood float switch, and the chlorine room vestibule supply fan. | Keswick West Park Reservoir | 2025-10-10
CENTRAL | October | On site to complete station check and to collect weekly bacti samples WO# W11279653. - Tower level draining @75% @54L/s - Entered data into PD sheet - Check trends all okay - Checked reagents - Equipment all okay - No issues found Free Cl grab @ 8:10am G: 1.31mg/L A: 1.32mg/L Treated Total Cl grab @ 8:10am G: 1.55mg/L A: 1.54mg/L | Keswick West Park Reservoir | 2025-10-08
CENTRAL | October | Onsite with Divya Patel to inspect basement chamber. Flushed tank level transmitter. Inspected sump, chlorine booster pumps and motorized valves. No issues. Basement flood switch failed to trigger. Created W11333079 for maintenance. Basement supply fan and chlorine room vestibule supply fan failed to operate. Created W11333032 for maintenance. No other issues found. | Keswick West Park Reservoir | 2025-10-02
EAST | October | On site for station check. Collected weekly micro samples (W11330463). Verification of HACH CL17 Chlorine Analyzer: 10:10hrs: Free CL2 grab residual: 1.07mg/l FCL Analyzer: 1.10mg/l Total Cl2 grab residual: 1.23mg/l Checked station readings and verified Cl2 analyzer. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Musselman's Lake Elevated Tank | 2025-10-29
EAST | October | Station Check (no issues found) Input data to PWQ 11:05 Verified CL17 (mg/L) Free: Grab 1.07, A 1.05 Total Grab 1.18 12:05 #11278483 & operational samples | Musselman's Lake Elevated Tank | 2025-10-08
EAST | October | On site to check station and equipment. Tower is on a draining cycle upon arrival. 11:15 grab chlorine residual from outlet, FCL = 1.07 mg/l, TCL = 1.14 mg/l. Analyzer free = 0.99 mg/l. 11:15 Collected bac-t sample, YD# W11298540. 11:32 Activated system duty. Tower duty start changed to 50% from 72% for deep cycling. Fire storage alarm is triggered due to the change. Reviewed trends, system is under normal operation. | Musselman's Lake Elevated Tank | 2025-10-14
EAST | October | On site for station check and weekly micro sampling (W11256276) Tower level - 86% and draining at 18 L/s Recorded station readings in PWQ sheets Verified analyzer reading with grab chlorine residuals: Grab free: 1.11 mg/L / Analyzer: 1.11 mg/L Grab total: 1.24 mg/L Collected micro sample @08:37 from outlet Reviewed trends, equipment ok Station ok | Musselman's Lake Elevated Tank | 2025-10-01
EAST | October | Back on site to take chlorine grabs through the new fire hydrant. 11:55 grab free = 1.30 mg/l. Grab total = 1.51 mg/l. 12:00 Stopped flushing. Closed the secondary valve for the new fire hydrant. The new contact tank and piping remains isolated from the system by chamber 1 isolation valve. Informed ROC to placed Well 3 back to auto. | Musselman's Lake Elevated Tank | 2025-10-14
EAST | October | On site for station check and equipment verifications Woodbine ET is controlling ET for today, west park tank is isolated for trial isolation for today. Duty is not active - tower level is 74% and draining at 96 L/s Recorded station readings in PWQ sheets Verified analyzer readings with grab chlorine residuals - made the following adjustments Inlet free: 1.66 mg/L ?-> 1.78 mg/L Reviewed trends, equipment ok Station ok | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2025-10-20
EAST | October | On site for station check and weekly micro sampling (W11331256) Tower level - 79% and filling at 26.5 L/s Recorded station readings in PWQ sheets Header: (09:15 Free Grab: 1.78 Mg/L / Analyzer Free: 1.56 mg/L - Adjusted analyzer based on grabs Total Grab: 2.16 Mg/L / Analyzer Total: 2.32 Mg/L - Adjusted analyzer based on grabs Inlet: (09:20) Free Grab: 1.94 Mg/L / Analyzer Free: 1.63 mg/L - Adjusted analyzer based on grabs Total Grab: 2.30 Mg/L / Analyzer Total: 2.28 Mg/L Outlet (09:24) Free Grab: 1.79 Mg/L / Analyzer Free: 1.57 mg/L Total Grab: 2.14 Mg/L / Analyzer Total: 2.26 Mg/L Collected micro sample from header @09:28 Reviewed trends, equipment ok Station ok | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2025-10-29
EAST | October | On site for station check, weekly micro sampling (W11317191) and Q4 sampling (W11247404) Tower level - 78% and filling at 14 L/s Recorded station readings in PWQ sheets Verified analyzer readings with grab residuals Header grabs / analyzers: @09:55 Free grab: 1.44 mg/L / 1.38 mg/L Total grab: 1.77 mg/L / 1.77 mg/L Adjusted inlet total analyzer from 2.27 to 2.12 mg/L @10:13 Collected samples from header @10:05 (Q4 and micro) Collected operational ATP sample for in-house lab Reviewed trends, equipment OOS: none Station ok | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2025-10-22
EAST | October | On site to change chlorine cylinders. Start: 0.0/54.5kg Stop: 68/54.5kg No issues on site. | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2025-10-22
EAST | October | On site for station check and to complete monthly PMs Recorded station readings in PWQ sheets - Chlorine analyzer maintenance (depolox) Started @10:10, completed @10:50 Verified analyzer readings after chlorine analyzer maintenance: Header: @10:19 Grab free: 1.10, 1.11, 1.10 mg/L / Analyzer: 1.02 mg/L - adjusted to 1.10 mg/L based on grabs Grab total: 1.41 mg/L / Analyzer: 1.35 mg/L Inlet: @10:24 Grab free: 1.57 mg/L / Analyzer: 1.42 mg/L - adjusted based on grabs Grab total: 1.90 mg/L / Analyzer: 1.92 mg/L Outlet: @10:30 Grab free: 1.12, 1.12 mg/L / Analyzer: 1.06 mg/L - adjusted based on grabs Grab total: 1.40, 1.41 mg/L / Analyzer: 1.31 mg/L - Adjusted based on grabs - Chlorine leak detector and safety equipment test - Chlorine scrubber checks - Actuated valve exercises - Manual valve exercises - Ventilation system inspection - Chlorine system inspections - Observed that residuals had been dropping over the last few days, left cylinder had emptied recently. Found that right side chlorine cylinder, opened cylinder and chlorine started dosing properly again - JHSC health and safety inspection - Portable gasoline generator Reviewed trends, equipment ok Informed ROC, station ok | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2025-10-06
EAST | October | On site to complete station check. Collecting weekly Bac-t Sample. W11279528 Weekly Bac-t Sample. Time: 08:40 Header Grab (mg/l) Analyzer (mg/l) Free: 1.40 1.35 Total: 1.65 1.73 Time: 08:45 Inlet Grab (mg/l) Analyzer (mg/l) Free: 2.14 2.07 Total: 2.80 2.71 Time: 08:47 Outlet Grab (mg/l) Analyzer (mg/l) Free: 1.33 1.38 Total: 1.70 1.79 No outstanding alarms on site. No OOS equipment on site. Checked site and trends. Verified analyzers with grabs. | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2025-10-08
EAST | October | On site to complete installation of chlorine tank valve closure system. System not yet in service. Tank valve closure actuators are stowed in their holders on the wall until administrative approval is given for the system to be placed in service. Tested chlorine leak sensor to verify proper operation of system. | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2025-10-03
EAST | October | On site to complete station check. Collecting weekly Bac-t Sample. Collecting VOC samples. W11257480 Weekly Bac-t Sample. W11257452 VOC Samples. Time: 08:55 Header Grab (mg/l) Analyzer (mg/l) Free: 1.20 1.14 Total: 1.54 1.52 Time: 09:00 Inlet Grab (mg/l) Analyzer (mg/l) Free: 1.32 1.35 Total: 1.79 1.78 Time: 09:03 Outlet Grab (mg/l) Analyzer (mg/l) Free: 1.15 1.19 Total: 1.55 1.47 Verified analyzers with grabs all ok. Checked site. | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2025-10-01
EAST | October | On site to complete station check. Time: 08:45 Header Grab (mg/l) Analyzer (mg/l) Free: 1.07 1.00 Total: 1.44 1.37 Time: 08:50 Inlet Grab (mg/l) Analyzer (mg/l) Free: 1.45 1.41 Total: 1.84 1.86 Time: 08:53 Outlet Grab (mg/l) Analyzer (mg/l) Free: 1.11 1.06 Total: 1.36 1.33 Verified analyzers with grabs. Checked station and trends. No equipment OOS. | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2025-10-03
EAST | October | On site for station check Chlorine residuals in the shared PWQ sheet, verified analyzers Reviewed station trends and recorded diesel generator tank fuel level Station and equipment okay, facility secure. | Markham Pumping Station | 2025-10-17
EAST | October | On site to complete station check. No OOS equipment. No outstanding alarms. Time: 10:45 Grab (mg/l) Analyzer (mg/l) Free: 0.05 -0.07-0.02 Total: 1.22 1.19 Called ROC at 10:48 to inform them I will be putting pumps in manual and zeroing and Span calibrating analyzer at 10:50. After span calibrating and zeroing analyzer, analyzer came back at 0.02mg/l at 10:57. After multiple grabs were taken analyzer did not need to be adjusted because it is within range of grab which is 0.05mg/l. At 10:59 started putting pumps back to auto to continue to fill McCowan Rd Reservoir. Informed ROC that pumps were back to auto at 11:01. | Markham Pumping Station | 2025-10-31
EAST | October | On site for station check Verified chlorine analyzers, 10:20, in mg/L Free Cl - G 0.07; A -0.01 Zero and span calibrated free chlorine analyzer as it was reading OOR Total Cl - G 1.45; A 1.38 Increased the total Cl analyzer to match average of grabs Inspected equipment, reviewed station trends Recorded observations in the shared PWQ sheet Station and equipment okay | Markham Pumping Station | 2025-10-27
EAST | October | On site for station check, pump 2 running in manual on to assist with MKRSEM drawdown. Verified chlorine analyzers and entered readings into the shared PWQ sheet, 10:00, in mg/L Free Cl: G 0.08; A 0.08 Total Cl: G 1.22; A 1.27 Reviewed station trends, inspected equipment, site secure. Station and equipment okay | Markham Pumping Station | 2025-10-20
EAST | October | On site for preventative maintenance work orders Generator test run: Performed pre inspection of generator and fuel system, informed RO Angelica of generator test run, she will liaise with Metro Toronto to place Milliken PD6 manual off for duration of load test. Disregard control panel power fail alarm and generator running status alarm Test start time 8:20 Test end time 9:45 Hours Start 580.7 hours Stop 582.1 hours Fuel Start 800/ 770 L Stop 730/ 710 L Gen stats, 9:31 55 PSI oil pressure 207 F oil temperature 189 F coolant temperature 27.7 battery voltage 1801 RPM 795 F exhaust temperature Informed Angelica diesel generator test run concluded at 9:50 and requested she contact Toronto to place Milliken PD6 P12 back to auto. Diesel generator is okay, no observed issues during generator test run loaded with 2 pumps Completed: Housekeeping Deplox analyzer maintenance Flood alarm test Valve exercise Health and safety inspection Pump and motor inspection Dehumidifier cleaning and inspection Finished on site, station and equipment okay, station is secure | Markham Pumping Station | 2025-10-21
EAST | October | On site for station check Verified analyzers, 12:00, in mg/L Free Cl, G 0.05; A 0.18 - zero and span calibrated to match average of grabs Total Cl, G 1.37; A 1.36 Inspected station and equipment Recorded observations in the shared PWQ sheet Station and equipment okay | Markham Pumping Station | 2025-10-24
EAST | October | On site to check station and equipment. All pumps are man/off as normal operation. Chlorine grabs and station readings are in PWQ sheet. 11:10 Performed cal zero on chlorine analyzer to reset free chlorine residual. After that, analyzer free was reading 0.02 mg/l. Reviewed trends, no concerns. Generator?s LIT remains OOS. | Markham Pumping Station | 2025-10-08
EAST | October | On site for station check Verified chlorine analyzers, 11:04, in mg/L FCl G 0.05, A 0.02 TCl G 1.21, A 1.20 Completed shared PWQ sheet, reviewed station trends, inspected equipment - okay | Markham Pumping Station | 2025-10-15
EAST | October | On site for station check, preventative maintenance work orders and sampling Completed Hi/ lo water level test Sump pit inspection Eye wash cleaning and solution replacement JHSC inspection Chlorine analyzer maintenance Valve inspection Dehumidifier inspection and cleaning Low temperature alarm test Heat trace system inspection Heat trace turned on for winter season Sample YD # W11316374 and W11247152 Collected BacT and Quarterly samples at 14:30, verified chlorine analyzers, in mg/L Free Cl G: 0.05; A: 0.02 Total Cl G: 1.66; A: 1.74 Station and equipment okay | Markham Milliken Elevated Tank | 2025-10-22
EAST | October | On site for station check and sampling Micro sampling, YD # W11330593, as well as nitrification monitoring sample, collected while draining, 12:50, and verified chlorine analyzers, in mg/L Free Cl grab: 0.05 Free Cl analyzer: 0.01 Total Cl grab: 1.74 Total Cl analyzer: 1.92 Adjusted total chlorine analyzer to match average of grabs Recorded observations in the shared PWQ and reviewed station trends. Acknowledging building low temperature alarm - turned station heater and supplementary space heater on Station and equipment okay | Markham Milliken Elevated Tank | 2025-10-29
EAST | October | On site for station check and operational monitoring & regulatory sampling: Micro (W11256406) Data in PWQ sheet Sample and grabs collected at 14:40 Grabs FCL: 0.02 mg/L TCL: 1.59 mg/L Analyzer FCL: 0.00 mg/L TCL: 1.61 mg/L Flow: Draining 155 L/s @ 76% (2404 m3) Equipment OOS: none Station ok | Markham Milliken Elevated Tank | 2025-10-01
EAST | October | On site for station check and sample collection Collected samples at 13:00 and verified chlorine analyzers, mg/L FCl G 0.10, A 0.16 - adjusted to match average of grabs TCl G 1.56, A 1.60 BacT YD W11298670 Unable to access shared PWQ sheet so values for advanced monitoring recorded below, in mg/L Mono 1.41 FA 0.10 TA 0.38 Nitrite 0.00 pH 7.99 Temperature 17.9oC Checked station and equipment - all okay | Markham Milliken Elevated Tank | 2025-10-14
EAST | October | On site to check station and collect sample. Tower is on a draining cycle. 12:29 grab chlorine residual from header, FCL = 0.03 mg/l, TCL = 1.69 mg/l. Analyzer free = 0.00 mg/l, total reading = 1.64 mg/l. 12:29 Collect bac-t sample. YD W11278605 Performed advanced monitoring with SL1000. See PWQ sheet for details. Reviewed trends, station is under normal operation. | Markham Milliken Elevated Tank | 2025-10-08
EAST | October | On site for NDMA sample collection (W11364819). 08:35hrs: Cl2 grab residuals: FCL: 0.10mg/l Analyzer FCL: 0.13mg/l TCL: 1.32mg/l Analyzer TCL: 1.31mg/l | Markham PD5 Reservoir | 2025-10-28
EAST | October | On site for station check and sampling Sampling YD #: W11316374, W11247138 Collected samples from the West cell while the storage was draining, 11:45, and verified chlorine analyzer, in mg/L Free Cl: Grab: 0.06; Analyzer: 0.02 Total Cl: Grab: 1.25; Analyzer: 1.26 East cell is offline for rehab. Station and equipment okay | Markham PD5 Reservoir | 2025-10-22
EAST | October | On site for station check and sampling Micro sampling, YD # W11330593, as well as nitrification monitoring sample, collected from the West cell, 11:40, and verified chlorine analyzers, in mg/L Free Cl grab: 0.08 Free Cl analyzer: 0.13 Adjusted free chlorine analyzer to match average of grabs Total Cl grab: 1.27 Total Cl analyzer: 1.32 East cell offline for rehab Recorded observations in the shared PWQ and reviewed station trends. Station and equipment okay | Markham PD5 Reservoir | 2025-10-29
EAST | October | On site for following work orders: JHSC inspection Water level hi/low test Chlorine analyzer maintenance External venting screen inspection House keeping The light is out in analyzer room, will replace the bulb on a later date. 14:30 Performed chlorine grabs from west cell after analyzer maintenance Grab free = 0.02 mg/, grab total = 1.33 mg/l. Analyzer free = 0.01 mg/l, total = 1.34 mg/l. The site is occupied by contractor due to CPD project. Only basic cleaning/inspection is done. East Cell and dehumidifier remain OOS. | Markham PD5 Reservoir | 2025-10-07
EAST | October | On site to check station and collect sample. Reservoir is on a draining cycle. 10:20 grab chlorine residual from west cell, FCL = 0.01 mg/l, TCL = 1.39 mg/l. Analyzer free = 0.01 mg/l, total = 1.39 mg/l. 10:20 Collect bac-t sample. YD W11278605 10:22 Collected NDMA sample, YD W11247898. Performed advanced monitoring with SL1000. See PWQ sheet for details. Flood alarm is outstanding. No actual flood. Communicated with contractor (Jeff from Brook) that he will arrange the sump pit to be pumped out. Reviewed trends, no major concerns. East cell and dehumidifier remain OOS. | Markham PD5 Reservoir | 2025-10-08
EAST | October | On site for station check and sample collection Collected samples at 11:05 from the West cell and verified chlorine analyzers, mg/L FCl G 0.05, A 0.02 TCl G 1.19, A 1.24 Adjusted total chlorine analyzer to match average of grabs BacT YD W11298670 Unable to access shared PWQ sheet so values for advanced monitoring recorded below, in mg/L Mono 1.10 FA 0.10 TA 0.32 Nitrite 0.000 pH 8.02 Temperature 17.5oC Checked station and equipment - all okay | Markham PD5 Reservoir | 2025-10-14
EAST | October | On site for station check and operational monitoring & regulatory sampling: Micro (W11256406) Data in PWQ sheet Sample and grabs collected from WEST cell @ 13:45 Grabs FCL: 0.04 mg/L TCL: 1.27 mg/L Analyzers FCL: 0.01 mg/L TCL: 1.28 mg/L Reservoir Level = 50% Draining EAST cell offline for capital project Station ok | Markham PD5 Reservoir | 2025-10-01
EAST | October | Under direction of OIC (Dan Zhou) On-site for; - station checks Data in PWQ excel Workbook Influent Water Grab @ 10:28 hrs. FCl: 0.82 mg/L Grab @ 10:30 hrs. FCL: 0.82 mg/L Grab @ 10:33 hrs. FCl: 0.84 mg/L ??> Ave= 0.826 *0.83 mg/L Adjusted Influent AIT to 0.83 mg/L Analyzer FCl: 0.75 mg/L Treated Water (Effluent) Grabs @ 10:15 hrs. Grab @ 10:19 hrs. FCl: 0.86 mg/L Grab @ 10:21 hrs FCl: 0.85 mg/L Grab @ 10:23 hrs. FCl: 0.87 mg/L ??> Ave= 0.86 mg/L Adjusted FCl Effluent AIT to 0.86 mg/L TCl: 1.01 mg/L Analyzer FCl: 0.81 mg/L Changed Buffer and Indicator reagents for Influent and Effluent AIT?s. Alarms; - Influent LO and Effluent LO - due to well 3 being OOS, Well cannot be put in to service until Well 7 development confirmed. May experience LO Influent and Effluent Alarm until this point. Equipment OOS: Well 3 Facility?s equipment Duty off due to Well 7 development. | Stouffville Well 3 | 2025-10-17
EAST | October | On its to complete station check. Lo effluent chlorine alarm ack and reset and Lo influent chlorine alarm ack and reset, these alarms will be coming in for the duration of the well 3 shut down. Well 3 is the only equipment that is OOS. Time: 10:55 Influent Grab (mg/l) Analyzer (mg/l) Free: 0.85 0.77 Time: 11:00 Effluent Grab (mg/l) Analyzer (mg/l) Free: 0.64 0.61 Total: 0.77 Verified analyzers on site with grabs all ok. Checked site and trends. | Stouffville Well 3 | 2025-10-27
EAST | October | Finished installing pvc replacement piping on chlorine booster pumps. Pressurized system and checked for leaks. No other issues to report, returned to service. | Stouffville Well 3 | 2025-10-29
EAST | October | Under direction of OIC (Stephen Baidy) On-site for; - station checks - Silicate Receiving (2300 Kg approx. 1703 L) Data in PWQ excel Workbook Influent Water Grab @ 11:48 hrs. FCl: 0.71 mg/L Analyzer FCl: 0.70 mg/L Treated Water (Effluent) Grabs @ 11:48 hrs. FCl: 0.70 mg/L TCl: 0.85 mg/L Analyzer FCl: 0.69 mg/L Sodium Silicate Mass, 1.35 kg/L Order 2300 Kg x 1L/1.35 Kg = 1703.7 L Therefore approx. 1703.7 L of Sodium Silicate Target Total in Subgrade tank: 4364 L Start cm: 55.8 Start V: 2661 L Stop cm: 92.8 Stop V: 4422 L Kg Received: 2377.4 Kg L Received: 1761 L Alarms; - Influent LO and Effluent LO - due to well 3 being OOS, Well cannot be put in to service until Well 7 development confirmed. May experience LO Influent and Effluent Alarm until this point. Equipment OOS: Well 3 Facility?s equipment Duty off due to Well 7 development. | Stouffville Well 3 | 2025-10-24
EAST | October | Under direction of OIC (Dan Zhou) On-site for; - station checks - Chlorine Leak detector test Data in PWQ excel Workbook Influent Water Grab @ 15:06 FCl: 0.85 mg/L Analyzer FCl: 0.83 mg/L Effluent (Treated Water) Grab @ 15:06 FCl: 0.82 mg/L TCL: 0.92 Analyzer: FCl: 0.83 Chlorine Leak detector test failed with 2 different puffers multiple times. P.Fobert made work order W11407596 instrumentation to come and address early next week prior to well start up. *Closed both Chlorine Cylinders. Alarms; - Influent LO and Effluent LO - due to well 3 being OOS, Well cannot be put in to service until Well 7 development confirmed. May experience LO Influent and Effluent Alarm until this point. - AIT2 (Effluent), see notes above. Equipment OOS: Well 3, Chlorine Booster Pumps Facility?s equipment Duty off due to Well 7 development. | Stouffville Well 3 | 2025-10-31
EAST | October | Isolated chlorine booster pumps from system, both pumps currently in off position. Removed Inlet side of both pumps due to cracked PVC fittings and valves. Will finish up installation of new PVC pipe work tomorrow. | Stouffville Well 3 | 2025-10-28
EAST | October | Informed ROC. Well OOS. Onsite to perform annual calibration. Put the devices in calibration mode. Devices were done as below : Chlorine Room devices, Influent and effluent AIT, Well NIT, Well LIT, Silicate LIT, Well PIT and FIT. Took a multiple grab samples. No adjustment required. All the related alarms were cleared. No issues. Informed ROC, armed the building and left the site. | Stouffville Well 3 | 2025-10-28
EAST | October | On site with Jack Palmer to complete chlorine line, ejector and regulator change out. W11369106 Chlorine Line Change. Informed ROC of work being completed at 11:32. Purged system, depressurized system and was able to complete work being done. Disregard alarms and any changes in trends due to work orders being completed. No other issues on site. Repressurized system and chlorine tested lines. No leaks or issues found. Put system back to normal and left chlorine booster pumps in local. | Stouffville Well 3 | 2025-10-30
EAST | October | Under direction of OIC (Dan Zhou) On-site for; - station checks - Operational Samples, FE, Temp,turb,FCl,TCl Data in PWQ excel Workbook Influent Water Grab @ 10:28 hrs. FCl: 0.83 mg/L Analyzer FCl: 0.84 mg/L Treated Water (Effluent) Grabs @ 10:15 hrs. Grab @ 10:19 hrs. FCl: 0.87 mg/L TCl: 1.03 mg/L Analyzer FCl: 0.86 mg/L Alarms; - Influent LO and Effluent LO - due to well 3 being OOS, Well cannot be put in to service until Well 7 development confirmed. May experience LO Influent and Effluent Alarm until this point. Equipment OOS: Well 3 Facility?s equipment Duty off due to Well 7 development. | Stouffville Well 3 | 2025-10-20
EAST | October | Under direction of OIC (Dan Zhou) On-site for; - station checks Data in PWQ excel Workbook Influent Water Grab @ 12:06 hrs. FCl: 0.76 mg/L Analyzer FCl: 0.74 mg/L Treated Water (Effluent) Grabs @ 12:06 hrs. FCl: 0.81 mg/L TCl: 0.96 mg/L Analyzer FCl: 0.79 mg/L Alarms; - Influent LO and Effluent LO - due to well 3 being OOS, Well cannot be put in to service until Well 7 development confirmed. May experience LO Influent and Effluent Alarm until this point. Equipment OOS: Well 3 Facility?s equipment Duty off due to Well 7 development. | Stouffville Well 3 | 2025-10-22
EAST | October | Under direction of OIC (Dan Zhou) On-site for; - station checks - Silicate system inspection and maintenance Data in PWQ excel Workbook @ 10:04 hrs. upon arrival influent analyzer in error state. Exited error state, then exit to restart. Tried to exit and restart again, failed. Switched analyzer on and off, remained in error state. @ 10:37 hrs. Called ROC and let them know about the A/D error state of Effluent AIT2 Asset # 00017704 @ 10:39 called Eric (On-Call instrumentation), they will have someone look at it today. Informed Acting team lead Stephen Baidy. Influent Water Grab @ 10:49 FCl: 0.75 mg/L Analyzer FCl: 74 mg/L Effluent Grab @ 10:49 hrs. FCl: 0.83 mg/L TCL: 0.96 mg/L Flushed silicate lines. Alarms; - Influent LO and Effluent LO - due to well 3 being OOS, Well cannot be put in to service until Well 7 development confirmed. May experience LO Influent and Effluent Alarm until this point. - AIT2 (Effluent), see notes above. Equipment OOS: Well 3, AIT2 Effluent analyzer Facility?s equipment Duty off due to Well 7 development. | Stouffville Well 3 | 2025-10-29
EAST | October | Under direction of OIC (Dan Zhou) On-site for; - station checks Data in PWQ excel Workbook Influent Water Grab @ 10:44 hrs. Grab FCl: 2.70 mg/L Analyzer FCl: 2.70- mg/L Treated Water (Effluent) Grabs @ 10:44 hrs. Grabs FCl: 2.72 mg/L TCl: 2.92 mg/L Analyzer FCl: 2.67 mg/L Equipment OOS: None Facility and equipment operating nominally. | Stouffville Well 3 | 2025-10-01
EAST | October | Under direction of OIC (Dan Zhou) On-site for; - station checks Data in PWQ excel Workbook Influent Water Grab @ 10:25 hrs. Grab FCl: 1.42 mg/L Analyzer FCl: 1.38 mg/L Treated Water (Effluent) Grabs @ 09:07 hrs. Grabs FCl: 1.06 mg/L TCl: 1.30 mg/L Analyzer FCl: 1.04 mg/L *Switched Soft Starter to Local Equipment OOS: None Facility and equipment Duty off due to Well 7 development. | Stouffville Well 3 | 2025-10-08
EAST | October | Under direction of OIC (Dan Zhou) On-site for; - station checks Data in PWQ excel Workbook Influent Water Grab @ 12:29 hrs. Grab FCl: 0.81 mg/L Analyzer FCl: 0.75 mg/L Treated Water (Effluent) Grabs @ 12:29 hrs. Grabs FCl: 0.95 mg/L TCl: 1.16 mg/L Analyzer FCl: 0.96 mg/L Alarms; - Influent Lo - due to well 3 being OOS, Well cannot be put in to service until Well 7 development confirmed. May experience LO Alarm until this point. Equipment OOS: Well 3 Facility?s equipment Duty off due to Well 7 development. | Stouffville Well 3 | 2025-10-14
EAST | October | Under direction of OIC (Dan Zhou) On-site for; - station checks Data in PWQ excel Workbook Influent Water Grab @ 09:14 hrs. Grab FCl: 1.18 mg/L Analyzer FCl: 1.18 mg/L Treated Water (Effluent) Grabs @ 09:14 hrs. Grabs FCl: 0.97 mg/L TCl: 1.20 mg/L Analyzer FCl: 1.03 mg/L Equipment OOS: Well 3 Facility?s equipment Duty off due to Well 7 development. | Stouffville Well 3 | 2025-10-10
EAST | October | 16:45 Placed well in manual on | Stouffville Well 3 | 2025-10-02
EAST | October | On-site for station check and regulatory samples: Micro (W11331398) & Q4 (W11247656) Sample collection time- Raw and Treated @ 10:05 Data in PWQ sheet Influent Water Grab @ 10:05 FCl: 2.76 mg/L Analyzer FCl: 2.73 mg/L Treated Water Grab @ 10:05 FCl: 2.64 mg/L TCl: 2.93 mg/L Analyzer FCl: 2.69 mg/L Equipment OOS: none Station ok | Stouffville Well 3 | 2025-10-03
EAST | October | Under direction of OIC (Dan Zhou) On site for: - Sodium Silicate system inspection and maintenance, injection quill cleaning and hot water flush - Charge Silicate system with water to prevent damage to silicate pumps/lines/connectors and injector - Chlorine analyzer Maintenance and cleaning (influent and Effluent AIT) - Turbidity analyzer maintenance/cleaning/calibration - Chemical system inspection (chlorine) - Well 3 Bore Hole inspection Started chlorine analyzer maintenance on AIT 1 and 2 Start Clean @ 09:53 hrs. Exited Clean @ 10:38 hrs. Effluent (Treated Water) AIT verification Grab @ 11:01 hrs. FCl: 1.00 mg/L TCl: 1.17 mg/L Analyzer FCl: 0.95 mg/L Influent AIT verification Grab @ 11:04 hrs. FCl: 1.15 mg/L Analyzer FCl: 1.12 mg/L Turbidity Analyzer Maintenance and clean: Clean start @ 11:11 hrs. Exited Clean @ 11:20 hrs. Sodium Silicate system flush: Flushed entire silicate system with hot water, from foot a valve to injection point (to prevent any damage to lines and equipment while system is off for Well 7 development. Once flushed with hot water noticed diaphragms on both pumps had cracks in them, replaced diaphragms on both pumps. Performed back flush @ 13:00 hrs. Equipment OOS: Well pump 3. Well 3 duty off due to Well 7 production. | Stouffville Well 3 | 2025-10-09
EAST | October | Under direction of OIC (Stephen Baidy) On-site for; - Station checks Data in PWQ excel Workbook Influent Water Grab @ 09:44 hrs. Grab FCl: 3.78 mg/L Analyzer FCl: 3.71 mg/L Treated Water (Effluent) Grabs @ 09:44 hrs. Grabs FCl: 2.26 mg/L TCl: 2.80 mg/L Analyzer FCl: 2.31 mg/L @ 10:26 hrs Equipment OOS: None Facility OK | Stouffville Well 1 & 2 | 2025-10-31
EAST | October | Under direction of OIC (Stephen Baidy) On-site for; - Station checks - Regulatory Sampling micro (W11330565) Data in PWQ excel Workbook Influent Water Grab @ 09:15 hrs. Grab FCl: 3.62 mg/L Analyzer FCl: 3.65 mg/L Treated Water (Effluent) Grabs @ 09:15 hrs. Grabs FCl: 2.36 mg/L TCl: 2.88 mg/L Analyzer FCl: 2.33 mg/L Equipment OOS: None Facility OK | Stouffville Well 1 & 2 | 2025-10-29
EAST | October | On site to receive hypo delivery. Start level: 782L/775L Stop Level: 1381/1381L | Stouffville Well 1 & 2 | 2025-10-28
EAST | October | Under direction of OIC (Dan Zhou) On-site for; - Station checks - Silicate Receiving (4300 Kg, approx. 3185 L) Data in PWQ excel Workbook Influent Water Grab @ 10:29 hrs. Grab FCl: 3.70 mg/L Analyzer FCl: 3.72 mg/L Treated Water (Effluent) Grabs @ 10:29 hrs. Grabs FCl: 2.17 mg/L TCl: 2.70 mg/L Analyzer FCl: 2.22 mg/L Sodium Silicate Order: Silicate Mass, 1.35 kg/L Order 4300 Kg x 1L/1.35 Kg = 3186.3 L Therefore approx. 3186.3 L of Sodium Silicate Target Total in Subgrade tank: 4847 L Start cm:32.2 Start V: 1662 L Stop cm: 95.1 Stop V: 4911 L Kg Received: 4386 Kg L Received: 3249 L Equipment OOS: None Facility OK | Stouffville Well 1 & 2 | 2025-10-24
EAST | October | Placed well 2 in duty 1. Flow set point changed to 21 l/s for both well 1 and 2. | Stouffville Well 1 & 2 | 2025-10-22
EAST | October | Changed the chlorine target set point from 3.6 to 3.7 mg/l. | Stouffville Well 1 & 2 | 2025-10-20
EAST | October | Under direction of OIC (Dan Zhou) On-site for; - Station checks - Receive Hypo Delivery (1500L) - Operational Sampling: Fe, temp, turb, FCl, TCL Data in PWQ excel Workbook Influent Water Grab @ 09:22 hrs. Grab FCl: 3.76 mg/L Analyzer FCl: 3.77 mg/L Treated Water (Effluent) Grabs @ 09:22 hrs. Grabs FCl: 2.14 mg/L TCl: 3.58 mg/L Analyzer FCl: 2.14 mg/L Changed Buffer and analyzer reagents on influent and effluent AIT. Equipment OOS: None Facility Operating Nominally | Stouffville Well 1 & 2 | 2025-10-20
EAST | October | Under direction of OIC (Dan Zhou) On-site for; - Station checks - Regulatory Sampling, Q4 sampling (W11247642), Micro (W11316346) Data in PWQ excel Workbook Regulatory samples taken @ 09:15 Influent Water Grab @ 09:15 hrs. Grab FCl: 3.70 mg/L Analyzer FCl: 3.72 mg/L Treated Water (Effluent) Grabs @ 09:15 hrs. Grabs FCl: 2.17 mg/L TCl: 2.70 mg/L Analyzer FCl: 2.22 mg/L Equipment OOS: None Facility Operating Nominally | Stouffville Well 1 & 2 | 2025-10-22
EAST | October | @ 13:12 ROC called about power outage at STW12. On site for power outage, VFD fault, generator running alarm @ 13:33 Arrived On-Site and Reset VFD for Well pump 1 , generator is running, chemical pumps and analyzers are running. @ 13:42 hrs. Joe Mazza restarted Well pumps 1 and 2 remotely. Station Running on Generator power. 1101 L of Diesel remaining @ 13:53 hrs. hydro one expects power to be on around 16:00 hrs. Station running OK on generator power. | Stouffville Well 1 & 2 | 2025-10-31
EAST | October | Under direction of OIC (Dan Zhou) On-site for; - Station checks Data in PWQ excel Workbook Influent Water Grab @ 11:52 hrs. Grab FCl: 2.14 mg/L Analyzer FCl: 2.18 mg/L Treated Water (Effluent) Grabs @ 11:52 hrs. Grabs FCl: 2.14 mg/L TCl: 3.20 mg/L Analyzer FCl: 2.18 mg/L @ 12:39 hrs. Called Roc to let them know I am shutting well 1 and 2 off and putting in manual off for injection quill repair (leaking at cracked compression fitting component). Repaired Injection Quill with Joe Mazza. @ 13:33 hrs. Returned Well Duty to Auto. Equipment OOS: None Facility Operating Nominally | Stouffville Well 1 & 2 | 2025-10-17
EAST | October | On site to complete station check. Time: 12:35 Influent Grab (mg/l) Analyzer (mg/l) Free: 3.60 3.70 Time: 12:40 Effluent Grab (mg/l) Analyzer (mg/l) Free: 2.09 2.08 Total: 2.66 Verified analyzers with grabs all ok. Checked site and trends. Well 2 is in manual on to help with residuals in the system. No outstanding alarms on site. No OOS equipment. | Stouffville Well 1 & 2 | 2025-10-27
EAST | October | Placed well 1 to auto duty 2. Well 2 flow set point changed to 30 l/s. It is man/on. | Stouffville Well 1 & 2 | 2025-10-22
EAST | October | Under direction of OIC (Dan Zhou) On site for: - Sodium Silicate system inspection and maintenance, injection quill cleaning and hot water flush - Chlorine analyzer Maintenance and cleaning (influent and Effluent AIT) - Turbidity analyzer maintenance/cleaning/calibration - Chemical system inspection and maintenance (chlorine) - Well 3 Bore Hole inspection - JHSC Health and Safety Checks - Generator Test Run @ 08:42 hrs. Put Wells 1 and 2 in manual off for PM?s Started chlorine analyzer maintenance on AIT 1 and 2 Start Clean @ 08:44 hrs. Exited Clean @ 09:25 hrs. Effluent (Treated Water) AIT verification Grab @ 09:39 hrs. FCl: 1.51 mg/L Analyzer FCl: 1.52 mg/L Influent AIT verification Grab @ 09:43 hrs. FCl: 1.95 mg/L Analyzer FCl: 1.98 mg/L Turbidity Analyzer Maintenance and clean: Clean start @ 09:27 hrs. Exited Clean @ 09:37 hrs. @ 11:29 hrs. Placed wells back in auto, well 1 ON Generator Test Run: Start Fuel: 1110 L Stop Fuel: Start Hours: 651.0 Stop Hours: 652.2 Pre run checks; Battery Cell Levels: Ok Battery Terminals and Cables: Ok Oil Level: Ok Coolant Level: Ok Fluid Leaks: NO Coolant Recirculating pump: Ok Faulty Gauges: NO @ 12:05 hrs. Put wells 1 and 2 in manual off for transfer test switch @ 12:13 hrs. Switched ATS to Test for generator power @ 12:28 hrs. Placed generator under facility load Well pump 2 in Manual ON @ 12:58 hrs. Checked generator operating parameters *under load* Operating Current: 67 Amps Operating Frequency: 60 Hz Operating Voltage: 585 Volts/ kilowatts Engine speed: 1750 RPM Water/coolant Temp: 148 f Oil Pressure: 25 psi Oil Temperature: 180 f @ 13:03 Put Well Pump 2 in manual off to switch ATS @ 13:09 hrs. Switched ATS to Normal @ 13:30 Generator finished cool down cycle. @ 13:33 Placed Well pumps 1 and 2 back in Auto. Equipment OOS: None Facility OK | Stouffville Well 1 & 2 | 2025-10-21
EAST | October | Under direction of OIC (Dan Zhou) On-site for; - Station checks - Regulatory Sampling, micro (W1127857) Data in PWQ excel Workbook Influent Water Grab @ 11:24 hrs. Grab FCl: 3.62 mg/L Analyzer FCl: 3.61 mg/L Treated Water (Effluent) Grabs @ 11:24 hrs. Grabs FCl: 2.30 mg/L TCl: 2.92 mg/L Analyzer FCl: 2.24 mg/L Called team Lead Dan Zhou to; @ 11:42 hrs. Switch silicate pump duty to silicate pump 2 from Silicate pump 1 to give pump 1 a rest (it has very warm and humming loudly) @ 11:45 hrs. Hypo Pump 2 air locked, while still on the phone with Dan Zhou, @ 11:47 hrs. switched duty to hypo pump 1 and placed hypo pump 2 into 10% pump speed - released air from air relief valve, it resolved the airlock issue @ 11:55 hrs. Placed hypo pump 2 back in duty as hypo pump one is very warm and could use a rest *During the duration of Well 7 being developed STW12 will be ON since STW3 will be OFF, manual duty rotate of hypo pumps and silicate pumps necessary to rest the pumps.* Monitored hypo pump 1 functionality until 12:15 hrs. Pump OK Equipment OOS: None Facility and equipment operating nominally. | Stouffville Well 1 & 2 | 2025-10-08
EAST | October | Re and re backflow preventer and install new main shut off LOTO wells remove backflow preventer and cut out main shut off install new backflow and shut off Test backflow preventer Passed | Stouffville Well 1 & 2 | 2025-10-03
EAST | October | Under direction of OIC (Dan Zhou) On-site for; - Station checks - Regulatory Sampling, Micro (11256378) - Receive Hypo Order Regulatory Samples Taken @ 09:09 Data in PWQ excel Workbook Influent Water Grab @ 09:09 hrs. Grab FCl: 3.68 mg/L Analyzer FCl: 3.62 mg/L Treated Water (Effluent) Grabs @ 09:09 hrs. Grabs FCl: 2.30 mg/L TCl: 3.10 mg/L Analyzer FCl: 2.24 mg/L *Noticed pinhole leak on Hypo Pump 1 foot valve line. Adam from ROC noticed sporadic influent Chlorine residual. @ 09:40 hrs. Called ROC and placed hypo pump pump 1 in manual off, out of auto duty rotate and in duty 3. Patched line to be fixed next day. Equipment OOS: Hypo Pump 1 *(see above note) Facility and equipment operating nominally. | Stouffville Well 1 & 2 | 2025-10-01
EAST | October | ROC called @05:25 for CT not achieved alarm, on well startup: Requested ROC to leave wells in man/off until morning. - Reviewed trends @07:45, found that the wells had started @05:17 and interlocked @05:20. Before the wells started, the effluent free chlorine was reading 0.55 mg/L - The effluent free of 0.55 mg/L was pulled back from distrubtion during the time that the wells were off, as it was reading 0.55 mg/L before the wells activated. - When the wells started up, and they got up to combined flow of ~ 40 L/s, the effluent cl2 of 0.55 mg/L was not enough to meet CT achieved. The effluent reqired at the time was 0.57 mg/L. However, it was water that was already treated, not water that had just came through the CT tank. CT had previously been achieved on distribution water. And as the wells were only running for 3 minutes, it was not enough time for raw water to go through the CT tank. Used the virtual CT calculator to confirm. - Cleared alarms @08:00 - @08:15: Started well #2 in manual, left well #1 in man/off until water from well #2 has cleared the CT tank. - @08:32: Effluent is reading 1.72 mg/L - started well #1 in manual Spoke to Dave T (East ORO) discussed the adverse procedure with him, he advised to report to MOH and SAC Called York region public health @08:45 - Karen Padda @09:00 - Called Spills action center (SAC) - Spoke to Officer Haiden McDonald AWQI #170350 Provided written notice to MOH and SAC @10:10 Facility is back to normal operation, leaving wells running in manual, to ensure that this issue does not happen again. Will discuss with team on Tuesday | Stouffville Well 1 & 2 | 2025-10-13
EAST | October | Due to issues with CT not achieved on startup on the weekend - will only be running a single well for now. Enabled Effluent free chlorine low alarm - setpoint adjusted to 0.4 mg/L - @15:13 - manual stopped well #2, leaving well #1 running in D1 - Adjusted well #1 flow setpoint from 22 to 31 L/s - Adjusted well #2 flow setpoint from 20 to 30 L/s | Stouffville Well 1 & 2 | 2025-10-14
EAST | October | Switched hypo pump duty and silicate pump duty. | Stouffville Well 1 & 2 | 2025-10-07
EAST | October | Under direction of OIC Danielle Zhou. Contacted ROC to let them know about diesel LIT calibration. Worked with contractors to connect and calibrate diesel tank LIT. | Stouffville Well 1 & 2 | 2025-10-07
EAST | October | On site to pump out chambers and repair suction line on hypo pump 1 Pumped out Influent and effluent chambers Repaired suction line on hypo pump 1 and primed Station locked out on low Influent free Cl, 14:13 Initiated backflush with dechlorination pucks in the catch basin and cleaned turbidimeter cuvette Influent free Cl, 14:43 G: 0.38 mg/L A: 0.33 mg/L Adjusted analyzer to match average of grabs Effluent free Cl, 14:59 G: 0.65 mg/L A: 0.58 mg/L Adjusted analyzer to match average of grabs 17:03 completed backflush, tank turned over. And cleared the Influent Lo Lo alarm Found hypo pump 2 suction line crossthreaded Tyson Cornish on site | Stouffville Well 1 & 2 | 2025-10-02
EAST | October | On site to check station and equipment. Wells 1 and 2 are man/on. Station readings and chlorine grabs are in PWQ sheet. 09:08 Standardized both chlorine analyzers according to 3 grabs' average. Increased hypo pump 1 DF from 50% to 54%. It is running at 25%, discharge pressure = 80 psi. Silicate pump 1 is running at 89%, discharge pressure at 68 psi. Man/Stop well 1 & 2 in order to isolate the discharge valve in effluent chamb. Informed ROC. Tyson C replaced the cracked Parker fitting on hypo P2's suction line. Primed the line. Hypo pump 2 is back in auto duty 1. After Lee?s work, restored system back to normal. 11:25 grab influent free is 1.45 mg/l, analyzer = 1.44 mg/l. 11:28 grab effluent free is 0.69 mg/l, analyzer = mg/l. Man/start both wells, all chemical pumps are back in auto. Station is back to normal operation. Informed ROC. | Stouffville Well 1 & 2 | 2025-10-03
EAST | October | On site responding to effluent turbidity fault CMU5 #W11335682 Turbidity analyzer faulted due to flow fault. Flow is reading 0 ml/min to analyzer. Adjusted ball valve that controls flow to the analyzer, and throttled down the needle valve after the analyzer. Flow to analyzer is now reading 1.20 ml/min Started wells in manual at 15:37, faulted a few minutes later on turbidity fault again, unclear what caused it. Restarted wells again at 15:44, will monitor, informed ROC No further issues | Stouffville Well 1 & 2 | 2025-10-03
EAST | October | Under Direction of OIC ( Dan Zhou) On site to switch Silicate Pump and Hypo Pump duty to rest pumps. @ 14:28 hrs. Called ROC to switch pump duty. Hypo: Pump 2 Duty 1 ?-> Duty 2, Pump 1 Duty 2 ??> Duty 1 Silicate: Pump 2 Duty 1 ??> Duty 2, Pump 1 Duty 2 ??> Duty 1 | Stouffville Well 1 & 2 | 2025-10-09
EAST | October | Taking over for J Palmer. 17:04 Started well 1 in manual; monitored hypo pump on start up- influent quickly stabilized at target setpoint Closely monitored effluent residual to ensure CT is met. Will place well 2 in manual on once contact tank has turned over Found hypo pump 2 suction line losing prime; discovered broken line under compression fitting, connecting to suction check valve. Replaced line and tested pump manually to ensure prime was holding after shut down. Placed hypo pump 2 to duty 1. Discovered another leaking fitting on hypo pump 2 suction line; a cracked fast and tite, transition from PVC to parker line. Placed hypo pump 1 to duty 1 and isolated hypo pump 2 line and placed hypo pump 2 OOS. 18:00 Placed well 2 manual on | Stouffville Well 1 & 2 | 2025-10-02
EAST | October | Under direction of OIC (Dan Zhou) On-site for; - Station checks - Regulatory Sampling, Micro (W11298642) Data in PWQ excel Workbook Regulatory Samples taken @ 14:28 hrs Influent Water Grab @ 14:28 hrs. Grab FCl: 3.62 mg/L Analyzer FCl: 3.67 mg/L Treated Water (Effluent) Grabs @ 14:28 hrs. Grabs FCl: 2.32 mg/L TCl: 3.20 mg/L Analyzer FCl: 2.30 mg/L Switched hypo Pump Duty Pump 2 to Duty 2, Pump 1 to Duty 1 Switched Silicate Pump Duty Pump 1 to Duty 2, Pump 2 to Duty 1 Equipment OOS: None Facility Operating Nominally | Stouffville Well 1 & 2 | 2025-10-14
EAST | October | Under direction of OIC (Dan Zhou) On-site for; - Station checks Data in PWQ excel Workbook Influent Water Grab @ 10:56 hrs. Grab FCl: 3.62 mg/L Analyzer FCl: 3.56 mg/L Treated Water (Effluent) Grabs @ 09:09 hrs. Grabs FCl: 2.19 mg/L TCl: 2.92 mg/L Analyzer FCl: 2.22 mg/L Equipment OOS: None Facility and equipment operating nominally. | Stouffville Well 1 & 2 | 2025-10-06
EAST | October | On site to place well pumps back to auto and remove LOTO after construction on new valve is complete. Well pumps back to auto @ 16:25hrs. Ran well pump 2 in auto to ensure no issues with the system. No issues observed. | Ballantrae Well 1 & 2 | 2025-10-29
EAST | October | On site for station check. Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 1.92mg/l FCL Analyzer:1.98mg/l Effluent Free Cl2 grab residual: 1.68mg/l FCL Analyzer: 1.75mg/l Effluent Total Cl2 grab residual: 1.96mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Site currently undergoing Construction upgrades by Torbear. Equipment out of service: None. *Power outage on site @ 13:30hrs. Generator running, duty not active at time. No issues on site. | Ballantrae Well 1 & 2 | 2025-10-31
EAST | October | On site to calibrate Turbidimeter. No issues. | Ballantrae Well 1 & 2 | 2025-10-17
EAST | October | On site for station check and equipment verifications Duty is not active - wells are off Recorded station readings in PWQ sheets Verified analyzer readings with grab chlorine residuals - no adjustments needed Visual inspection of chemical systems Reviewed trends, Equipment OOS: None Station ok | Ballantrae Well 1 & 2 | 2025-10-24
EAST | October | On site for station check. Collected weekly micro samples (W11316252) and Quarterly Samples (W11247376). Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 1.98mg/l FCL Analyzer:1.98mg/l 12:20hrs: Effluent Free Cl2 grab residual: 1.76mg/l FCL Analyzer: 1.77mg/l Effluent Total Cl2 grab residual: 2.02mg/l 13:02hrs: Collected Well 1 raw samples. Switched Well Duties: W2 to D2, W1 to D1. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Site currently undergoing Construction upgrades by Torbear. Equipment out of service: None. | Ballantrae Well 1 & 2 | 2025-10-22
EAST | October | Under direction of OIC Dan Zhou On site for silicate delivery Start level 27.39 cm Stop level 41.55 cm | Ballantrae Well 1 & 2 | 2025-10-16
EAST | October | On site for station check. Also to open Well #2 backflushing valve for Backflow preventer certification/testing for future use for construction upgrades on site. Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 1.41mg/l FCL Analyzer:1.43mg/l Effluent Free Cl2 grab residual: 1.47mg/l FCL Analyzer: 1.43mg/l Effluent Total Cl2 grab residual: 1.70mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Site currently undergoing Construction upgrades by Torbear. Equipment out of service: None. | Ballantrae Well 1 & 2 | 2025-10-27
EAST | October | On site for station check. Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 1.63mg/l FCL Analyzer:1.61mg/l Effluent Free Cl2 grab residual: 1.60mg/l FCL Analyzer: 1.61mg/l Effluent Total Cl2 grab residual: 1.80mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Site currently undergoing Construction upgrades by Torbear. Equipment out of service: None. | Ballantrae Well 1 & 2 | 2025-10-17
EAST | October | On site for station check and equipment verifications Duty is not active - tower level -83% Recorded station readings in PWQ sheets Verified CL-17 analyzers with grab residuals Changed CL-17 reagents Topped up hypo day tank to 412 L Reviewed trends, equipment OOS: None Station ok | Ballantrae Well 1 & 2 | 2025-10-03
EAST | October | On site. To checked station and equipment. Well 1 is running in duty 1 upon arrival. 13:25 Collected well 1 raw. YD #W11298540. 13:29 effluent grab free = 1.78 mg/l, grab total = 2.05 mg/l. Effluent analyzer free = 1.77 mg/l. 13:29 Collected treated bac-T sample. 13:35 Switched well duty to place well 2 in duty 1. Switched hypo pump duty as well. Hypo pump 2 discharge pressure = 100 psi. It is running at 22%. Silicate pumps 2 is running at 45%, discharge pressure = 108 psi. 14:30 Collected well 2 raw bac-T sample. Other station readings and chlorine grabs are entered in PWQ sheet. Reviewed trends, no issues. | Ballantrae Well 1 & 2 | 2025-10-14
EAST | October | On site for station check and weekly micro sampling (W11256276) Contractors on site for BLW12 upgrades project Duty is active - BLETNL Level - 88% Well #1 running auto - 30 L/s, 666 kpa Recorded station readings in PWQ sheets Chemical systems inspections Hypo P2 dosing at 20%, 58.4 mL/min, DF = 51% Silicate P1 dosing at 43%, 76.3 mL/min Verified analyzer readings with grab chlorine residuals: Influent: @09:18 Grab free: 1.98 mg/L / Analyzer: 2.02 mg/L Effluent: @09:20 Grab free: 1.70 mg/L / Analyzer: 1.72 mg/L Grab total: 1.93 mg/L NTU: 0.042 Collected well #1 raw sample and 1/2 treated sample @09:25) @09:28 - manual started well #2 and once started, stopped well #1. Duty rotated wells - placed well #2 in duty 1 for the week. @10:00 - collected well #2 raw sample Reviewed trends, equipment OOS: Hypo P1 Station ok | Ballantrae Well 1 & 2 | 2025-10-01
EAST | October | Station Check (no issues found) Input data to PWQ 13:30 Verified CL17s (mg/L): Influent: Free: Grab 1.92, A 1.91 Treated: Free: Grab 1.56, A 1.65 (adjusted to match grabs) Total Grab 1.76 14:05 #11278483 Well 2 raw & treated samples 14:40 Well 1 raw sample Well 1 change to Duty 1 (Well 2 is Duty 2) | Ballantrae Well 1 & 2 | 2025-10-08
EAST | October | On site for station check and equipment verifications Duty is not active - BLETNL Level - 80% Recorded station readings in PWQ sheets Verified analyzer readings with grab chlorine residuals: @09:52 Adjusted effluent free analyzer from 1.39 to 1.50 mg/L Visual inspection of chemical systems - all ok Reviewed trends, equipment OOS: none Station ok | Ballantrae Well 1 & 2 | 2025-10-10
EAST | October | On site to complete station check. Time: 11:10 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.92 1.98 Time: 11:15 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.58 1.55 Total: 1.72 Verified analyzers with grabs. Checked station and trends. No OOS equipment. No outstanding alarms. | Ballantrae Well 1 & 2 | 2025-10-06
EAST | October | On site for station check. Collected weekly micro samples (W1330463). Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 2.16mg/l FCL Analyzer: 2.22mg/l 09:32hrs: Effluent Free Cl2 grab residual: 1.70mg/l FCL Analyzer: 1.74mg/l Effluent Total Cl2 grab residual: 2.15mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Ballantrae Well 3 | 2025-10-29
EAST | October | On site for station check. Collected weekly micro samples (W11316252) and Quarterly Samples (W11247376). Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 2.15mg/l FCL Analyzer:2.23mg/l 11:52hrs: Effluent Free Cl2 grab residual: 1.72mg/l FCL Analyzer: 1.63mg/l Effluent Total Cl2 grab residual: 2.11mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Ballantrae Well 3 | 2025-10-22
EAST | October | Under direction of OIC Dan Zhou On site for silicate delivery. Start level: 95 cm Stop level: 193 cm | Ballantrae Well 3 | 2025-10-16
EAST | October | On site to assist in construction upgrades by Torbear. The upgrades required the following: LOTO Well 3. Informed ROC.? Closed main isolation valve along HWY48, closed new BV in VC2, closed new mainline valve east of VC1.? Opened the drain valve in VC1 to drain CT1. Used 2 sump pumps to pump out the water. Placed dechlor pucks at the pump discharge. Made sure the water level is below the drain valve.? Powered off influent an effluent chlorine analyzers. 14:25hrs: Reopened main isolation valve on HWY48 to recharge pipe to VC2. No leaks or issues. Then opened new BV in VC2 and then cracked open mainline valve to refill CT1. Opened back flush valve in the station and placed sodium thiosulphate pucks at back flush manhole behind the station to dechlorinate. Back flushed well @ 8L/S starting at 15:10hrs after CT1 was refilled. 17:00hrs - stopped backflushing, turbidity levels within range. Called Electrical On call Dave Douherty to investigate VFD panel - noticed weird sound coming from VFD panel on Well 3 when turning breaker back on. Electrical mentioned that switch should remain in VFD mode and not in the off position, off position was causing loud banging noise. Manually started Well 3 @ 17:25hrs to monitor. No issues. Well back in auto. | Ballantrae Well 3 | 2025-10-21
EAST | October | On site for station check and equipment verifications Duty is not active - BLETNL level - 79% Recorded station readings in PWQ sheets Verified analyzer readings with grab chlorine residuals: Adjusted effluent free analyzer from 1.27 to 1.35 mg/L based on grabs Reviewed trends, equipment OOS: None Station ok | Ballantrae Well 3 | 2025-10-24
EAST | October | On site for station check. Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 1.83mg/l FCL Analyzer:1.87mg/l Effluent Free Cl2 grab residual: 1.67mg/l FCL Analyzer: 1.75mg/l Effluent Total Cl2 grab residual: 2.10mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Site currently undergoing Construction upgrades by Torbear. Equipment out of service: None. | Ballantrae Well 3 | 2025-10-17
EAST | October | On site for station check. Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 2.12mg/l FCL Analyzer: 2.14mg/l Effluent Free Cl2 grab residual: 1.71mg/l FCL Analyzer: 1.72mg/l Effluent Total Cl2 grab residual: 2.00mg/l Switched Chlorine Booster duties, placed Cl2 Booster P1 in Duty 1 and Chlorine Booster P2 will stay in D2, with auto duty rotate off. Noticed a small pinhole leak in the discharge PVC line on Cl2 Booster pump 2 near the pump itself. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Ballantrae Well 3 | 2025-10-31
EAST | October | On site for monthly WO?s. - Valve exercise, Silicate system inspection, well oil drip top up, emergency CL2 kit inspection. | Ballantrae Well 3 | 2025-10-28
EAST | October | On site for station check. Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 2.15mg//l FCL Analyzer: 2.22mg/l Effluent Free Cl2 grab residual: 1.62mg/l FCL Analyzer: 1.68mg/l Effluent Total Cl2 grab residual: 2.08mg/l Hot water through silicate board. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Site currently undergoing Construction upgrades by Torbear. Equipment out of service: None. | Ballantrae Well 3 | 2025-10-27
EAST | October | On site for station check. Collected in house operational iron samples. Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 2.14mg/l FCL Analyzer: 2.23mg/l Effluent Free Cl2 grab residual: 1.98mg/l FCL Analyzer: 1.93mg/l Effluent Total Cl2 grab residual: 2.54mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Site currently undergoing Construction upgrades by Torbear. Equipment out of service: None. | Ballantrae Well 3 | 2025-10-20
EAST | October | On site to open Contact Tank 2 by opening VC1 mainline valve in driveway. Conducted confined space entry on VC1 to open mainline valve. Permit completed. After valve was opened, flushed and took CL2 grab residual at PIT on inlet of CT2 to ensure chlorine residual was suitable before placing CT2 in operation. Cl2 grab residual taken at 0945hrs: 1.30mg/l free. 09:50hrs: Manually started BLW3. Bypass open and CT2 open. Closed bypass valve at hydrant after running well for 5 minutes. Will keep bypass closed at hydrant for 5 day run test. Gradually increased flow rate to gather data points for ETP pressure and flow. Placed Well 3 flow rate setting to 30L/S. Will leave at this flow rate for 5 day run test. | Ballantrae Well 3 | 2025-10-15
EAST | October | Onsite to repair chlorination #1. Green liquid in vacuum gauge line Informed ROC and operations. ROC place duty to manual off Purged chlorine system. Repaired the issue. Performed vacuum test. All ok Informed ROC and operations. Operation will inform ROC to place duty back to auto No other issues Left site Contractor busy in and around facility | Ballantrae Well 3 | 2025-10-09
EAST | October | On site for monthly maintenance: Informed ROC of work to be completed - JHSC health and safety inspection - Diesel generator test run and hours log (Started @13:10) Hours - 404:29, Fuel - 92.6/86.6 cm. Ran well #3 during test run, no issues during test run or transfer. (Stopped @14:29). See attached generator run sheet for full details) - Chlorine analyzer maintenance: Started @ and completed @13:36: Verified analyzers after maintenance completed. - Turbidity analyzer maintenance - Chlorine leak detector test @14:18 - Chlorine scrubber inspection and test - Low temperature alarm test Analyzer verifications - no adjustments needed Influent: @14:38 Grab free: 1.93 mg/L / Analyzer: 1.96 mg/L Effluent: @14:41 Grab free: 1.97 mg/L / Analyzer: 1.92 mg/L Equipment all back to auto Station ok | Ballantrae Well 3 | 2025-10-07
EAST | October | On site to relocate the silicate tank from silicate room to pump room and cleaned. | Ballantrae Well 3 | 2025-10-02
EAST | October | On site to flush the new CT tank and new piping. 08:56 started flushing through new fire hydrant. Flow rate is ~5 l/s. 09:17 grab free = 0.78 mg/l. Total = 0.91 mg/l. 10:00 started flushing the dead end of existing main (East portion) 10: 06 grab free = 1.25 mg/l. stopped flushing. 10:25 opened the east mainline valve (between the 2 blow offs) and flushing through the new fire hydrant. Flow rate is estimated to be around 40 l/s. Will return to site to take chlorine grabs. Well 3 is placed man/off. Informed ROC. 11:56 Back on site to check chlorine residual at the flushing port. Grab free = 1.30 mg/l, grab total = 1.51 mg/l. 12:00 Stopped flushing. Closed the secondary valve for the new fire hydrant. The new CT2 and piping remain isolated with VC1 isolation valve colsed. Informed ROC to placed Well 3 back to auto. Checked station and equipment. Chlorine booster pump 2 discharge pressure = 245 psi. Chlorination 2 is running at 41%, 22 ppd, DF = 75%. Silicate pumps 2 is running at 16%, discharge pressure = 82 psi. 12:56 effluent grab chlorine residual, FCL = 1.95 mg/l, TCL = 2.22 mg/l Effluent analyzer free = 1.87 mg/l. 12:56 collected treated and raw bac-T samples, YD #W11298540. Other station readings and chlorine grabs are entered in PWQ sheet. Reviewed trends, no issues. | Ballantrae Well 3 | 2025-10-14
EAST | October | On site to assist Torbear contractors and capital for connections of watermain around CCT#2 (New, and not in service yet) Contractors connected two new sections of water main near the New VC1 and VC2 chambers (Pre and post the new contact tank #2. No changes to current operation of system at BLW3 - water is still being directed to distribution through CCT #1 and the bypass through the hydrant as it has been for the last few months. Charged the new sections of water main to test for leaks, coming from a 2 inch hose from distribution water, with a backflow preventer attached. Will be returning to site tomorrow to continue with project. No changes to system operation at this time Completed the following PMs - Exhaust and supply fans checks - Well pump and motor grease (6m) - Chemical system inspection chlorine | Ballantrae Well 3 | 2025-10-08
EAST | October | Topped up silicate tank: 68 L?> 202 L | Ballantrae Well 3 | 2025-10-02
EAST | October | On site to complete station check. Time: 12:10 Influent Grab (mg/l) Analyzer (mg/l) Free: 2.07 2.08 Time: 12:13 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.69 1.70 Total: 2.02 Verified analyzers with grabs all ok. At 12:14 cleared comm alarm on OIT. Checked site and trends. No OOS equipment except for contact tank 2. At 12:20 changed out reagents for the influent CL-17 analyzer. | Ballantrae Well 3 | 2025-10-06
EAST | October | On site with Phil Degroot to flush the new CT tank 2 and piping. New CT tank 2 and new piping are isolated from the system. Used the existing fire hydrant with double back flow preventer to push distribution water through new section and out through new fire hydrant beside VC1. While attempting to flushing through the new fire hydrant beside CT1, a leak was discover from the new fire hydrant location. Contractor will address the leak. New CT 2 and piping remain isolated from the system. | Ballantrae Well 3 | 2025-10-09
EAST | October | On site for station check and weekly micro sampling (W11256276) Duty is not active - BLETNL Level - 92% Well #3 running in manual - 22 L/s, 701 kpa Chemical systems: Chlorinator #2 dosing at 43%, DF = 78%, 21.5 PPD Silicate P1 dosing at 20%, 20.3 mL/min Changed Right chlorine cylinder with Dan Zhou, tested for leaks, all ok Verified chlorine analyzers with grab residuals: Influent: @10:49 Grab free: 2.24 mg/L / Analyzer: 2.11 mg/L - Adjusted based on grabs Effluent: @10:52 Grab free: 1.90 mg/L / Analyzer: 1.87 mg/L Grab total: 2.38 mg/L NTU: 0.020 Collected well #3 raw and treated samples @10:55 Reviewed trends, equipment OOS: None Station ok | Ballantrae Well 3 | 2025-10-01
EAST | October | 11:07 took chlorine grab from existing fire hydrant, which is after CT2 and VC2. Free= 1.42 mg/l, total = 1.55 mg/l. | Ballantrae Well 3 | 2025-10-15
EAST | October | On site for station check and equipment verifications Duty is not active - BLETNL level - 78% Recorded station readings in PWQ sheets Verified chlorine analyzer readings with grab residuals - no adjustments needed Visual inspection of chemical systems - all ok Completed monthly cleaning work order Reviewed trends, equipment OOS: None Station ok | Ballantrae Well 3 | 2025-10-10
EAST | October | Station Check (no issues found) Input data to PWQ 12:45 Verified CL17s(mg/L) Influent: Free: Grab 2.10, A 2.14 Effluent: Free: Grab 1.88, A 1.85 Total Grab 2.10 12:05 #11278483 samples 13:10 placed well in Auto off | Ballantrae Well 3 | 2025-10-08
EAST | October | On site for Cl2 Cylinder change with Jack Palmer. No issues | Stouffville Reservoir and Wells 5 & 6 | 2025-10-17
EAST | October | Under direction of OIC (Dan Zhou) On-site for; - Station Checks - Regulatory Sampling, Q4 (W11247642), Micro (W11316346) Data in PWQ excel Workbook Regulatory Samples Taken @ 10:41 hrs. (Influent) Grab @ 10:41 hrs. FCl: 2.10 mg/L Analyzer FCl: 2.10 mg/L (Effluent) Treated Water Grabs @ 10:41 hrs. Grabs FCl: 1.88 mg/L TCl: 2.04 mg/L Analyzer FCl: 1.92 mg/L Equipment OOS: none Facility OK | Stouffville Reservoir and Wells 5 & 6 | 2025-10-22
EAST | October | Under direction of OIC (Stephen Baidy) On-site for; - Station Checks - Regulatory Sampling, Micro (W11330565) Regulatory Samples Taken @ 14:21 hrs. Data in PWQ excel Workbook (Influent) Grab @ 14:21 hrs. FCl: 1.94 mg/L Analyzer FCl: 1.96 mg/L (Effluent) Treated Water Grabs @ 14:21 hrs. Grabs FCl: 2.32 mg/L TCl: 2.40 mg/L Analyzer FCl: 2.36 mg/L Equipment OOS: none Facility OK | Stouffville Reservoir and Wells 5 & 6 | 2025-10-29
EAST | October | Under direction of OIC (Stephen Baidy) On-site for; - Station Checks Data in PWQ excel Workbook (Influent) Grab @ 09:02 hrs. FCl: 2.01 mg/L Analyzer FCl: 2.07 mg/L (Effluent) Treated Water Grabs @ 09:02 hrs. Grabs FCl: 1.90 mg/L TCl: 2.03 mg/L Analyzer FCl: 1.94 mg/L Changed High Lift Duty HLP1 Duty 1 to Duty 2, HLP2 Duty 2 to Duty 1 Equipment OOS: none Facility OK | Stouffville Reservoir and Wells 5 & 6 | 2025-10-24
EAST | October | Under direction of OIC (Dan Zhou) On-site for; - Station Checks - Switch Influent Sample Line and Corresponding Flow Path to Reservoir Data in PWQ excel Workbook (Influent) Grab @ 14:19 hrs. FCl: 2.11 mg/L Analyzer FCl: 2.14 mg/L (Effluent) Treated Water Grabs @ 14:29 hrs. Grabs FCl: 1.89 mg/L TCl: 2.11 mg/L Analyzer FCl: 1.93 mg/L @ 14:37 Switched Influent Sample Line and Corresponding Flow Path to Reservoir from West to East Equipment OOS: none Facility operating nominally | Stouffville Reservoir and Wells 5 & 6 | 2025-10-17
EAST | October | Under direction of OIC (Dan Zhou) On-site for; - Station Checks - Switch Influent Sample Line and Corresponding Flow Path to Reservoir Data in PWQ excel Workbook (Influent) Grab @ 12:02 hrs. FCl: 2.04 mg/L Analyzer FCl: 2.03 mg/L (Effluent) Treated Water Grabs @ 14:29 hrs. Grabs FCl: 1.88 mg/L TCl: 2.08 mg/L Analyzer FCl: 1.91 mg/L @ 12:04 hrs. Switched Influent Sample Line and Corresponding Flow Path to Reservoir from East to West @ 12:07 Changed High Lift Pump Duty from HLP2 duty 1 to duty 2 and HLP1 Duty 2 to duty 1 Received 12, 68 Kg Chlorine Cylinders with Dan Zhou and Jack Palmer. Returned 12 empty. Equipment OOS: none Facility operating nominally | Stouffville Reservoir and Wells 5 & 6 | 2025-10-20
EAST | October | Under direction of OIC (Dan Zhou) On-site for; - Station Checks Data in PWQ excel Workbook (Influent) Grab @ 12:237 hrs. FCl: 1.84 mg/L Analyzer FCl: 1.85 mg/L (Effluent) Treated Water Grabs @ 12:37 hrs. Grabs FCl: 2.28 mg/L TCl: 2.68 mg/L Analyzer FCl: 2.30 mg/L @ 11:30 hrs. Performed chlorine system inspection, Purged Chlorine system, changed chlorine cylinder 1 with Joe Mazza Equipment OOS: none Facility OK | Stouffville Reservoir and Wells 5 & 6 | 2025-10-31
EAST | October | On-site for station check Data in PWQ sheet Equipment OOS: none Station ok | Stouffville Reservoir and Wells 5 & 6 | 2025-10-03
EAST | October | On site to complete station check. Collecting weekly Bac-t Samples. W11298642 Weekly Bac-t Samples. Time: 12:20 Influent Grab (mg/l) Analyzer (mg/l) Free: 2.11 2.13 Time: 12:50 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.90 1.93 Total: 2.02 No outstanding alarms on site. Checked site and trends. No OOS equipment. Verified analyzers with grabs all ok. | Stouffville Reservoir and Wells 5 & 6 | 2025-10-14
EAST | October | Under direction of OIC (Dan Zhou) On-site for; - Station Checks - Switch High Lift Duty Data in PWQ excel Workbook (Influent) Grab @ 13:17 hrs. FCl: 2.00 mg/L Analyzer FCl: 2.00 mg/L (Effluent) Treated Water Grabs @ 13:17 hrs. Grabs FCl: 1.89 mg/L TCl: 2.02 mg/L Analyzer FCl: 1.90 mg/L @ 13:25 Called ROC to switch High lift Duty From HLP 2 Duty 1 to HLP 1 Duty 1, HLP1 Duty 2 and HLP2 Duty 1 Equipment OOS: none Facility operating nominally | Stouffville Reservoir and Wells 5 & 6 | 2025-10-10
EAST | October | Under direction of OIC (Dan Zhou) On-site for; - Station Checks - Switch Influent Sample Line and Corresponding Flow Path to Reservoir Data in PWQ excel Workbook (Influent) Grab @ 13:42 hrs. FCl: 1.92 mg/L Analyzer FCl: 1.94 mg/L (Effluent) Treated Water Grabs @ 13:27 hrs. Grabs FCl: 1.92 mg/L TCl: 2.11 mg/L Analyzer FCl: 1.93 mg/L Switch Influent Sample Line and Corresponding Flow Path to Reservoir from East to West Equipment OOS: none Facility operating nominally | Stouffville Reservoir and Wells 5 & 6 | 2025-10-06
EAST | October | Under direction of OIC (Dan Zhou) On-site for; - Station Checks - Regulatory Sampling, Micro (11256378) Regulatory Samples taken @ 13:24 Data in PWQ excel Workbook (Influent) Grab @ 13:24 hrs. FCl: 1.92 mg/L Analyzer FCl: 1.94 mg/L (Effluent) Treated Water Grabs @ 13:24 hrs. Grabs FCl: 1.88 mg/L TCl: 2.07 mg/L Analyzer FCl: 1.88 mg/L @ 14:44 Celled ROC to switch High Lift Pump 1 from duty 1 to duty 2 and High Lift Pump 2 from duty 2 to duty 1. Equipment OOS: none Facility operating nominally | Stouffville Reservoir and Wells 5 & 6 | 2025-10-01
EAST | October | Under direction of OIC (Dan Zhou) On-site for; - Station Checks - Regulatory Sampling: micro (W11278577) - Check OOS Sample Pump 1 Regulatory Samples taken @ 13:32 hrs. Data in PWQ excel Workbook (Influent) Grab @ 13:32 hrs. FCl: 2.06 mg/L Analyzer FCl: 2.10 mg/L (Effluent) Treated Water Grabs @ 13:27 hrs. Grabs FCl: 1.94 mg/L TCl: 2.11 mg/L Analyzer FCl: 1.91 mg/L Replaced tubing assembly in sample pump 1 @ 14:02 hrs. Called ROC to swap sample pump duty from SP2 Duty 1 to Duty 2 and SP1 Duty 2 to Duty 1 to verify function of SP1. SP1 is OK and back in service. Equipment OOS: none Facility operating nominally | Stouffville Reservoir and Wells 5 & 6 | 2025-10-08
EAST | October | On site to assist Travis W with chlorine leak detector test, and chlorine scrubber checks | Stouffville Reservoir and Wells 5 & 6 | 2025-10-07
EAST | October | On site for chlorine cylinder change with Dan Z Changed left side, tested vacuum switches and for leaks, no issues Station ok | Stouffville Reservoir and Wells 5 & 6 | 2025-10-10
EAST | October | Under direction of OIC (Dan Zhou) On-site for; - Preventative Maintenance; UV building Chlorine Analyzer Maintenance and Verification, High lift Building Chlorine Analyzer Maintenance and Verification, Turbidity Analyzer maintenance and verification - JHSC Health and Safety Checks - Monthly Generator Test Run - Chlorine Emergency Repair kit Inspection - Chlorine Scrubber Check - Chlorine Leak Detector Test UV Building Chlorine Analyzer Start Clean @ 11:10 hrs. Stop Clean @ 11:39 hrs. Influent Water Grab @ 12:26 hrs Grab FCl: 1.95 mg/L Analyzer FCl: 1.94 mg/L High Lift Building Chlorine Analyzer Clean Start @ 11:14 hrs. Clean Stop @ 11:43 hrs. Treated Water (Effluent) Grabs @ 12:40 AM Grabs FCl: 1.78 mg/L TCl: 1.95 mg/L Analyzer FCl: 1.79 mg/L Patrick Fobert on Site for; - Chlorine leak detector test - Chlorine Scrubber check Triggered Chlorine Leak @ 11:41 hrs. Scrubbers Operating Nominally Turbidity Analyzer Maintenance and calibration Start @ 12:31 hrs. Stop @ 12:42 hrs. Generator Test Run: @ 12:57 called ROC to place High lift Pump 1 in Manual OFF @ 12:59 started generator @ 13:13 called ROC to place High Lift Pump 2 in manual ON Start hours: 1114.6 Start time: 12:59 hrs. Stop Hours: 1115.6 Stop Time: 13:54 (excluding cool down time) Run Time hours: 1 hr Start Fuel: 83% Stop Fuel: 81 % Pre run checks; Battery Cell Levels: Ok Battery Terminals and Cables: Ok Oil Level: Ok Coolant Level: Ok Fluid Leaks: NO Coolant Recirculating pump: Ok Faulty Gauges: NO *under load* High lift pump 2 Operating Current: 45 Amps Operating Frequency: 61 Hz Operating Voltage: 580 Volts/ kilowatts Engine speed: 1750 RPM Water/coolant Temp: 170 f Oil Pressure: 50 psi Oil Temperature: 190 f Alarms; - STPS48 booster pump 2 uncomanded start alarm, interlocked into duty 3 - spoke with ROC and reset to auto duty rotate BP 1 in duty 1 BP2 in Duty 2 - High lift Pump 2 uncomanded stop - spoke with ROC and reset - HLP 2 in auto and Running Equipment OOS: none Well running nominally | Stouffville Reservoir and Wells 5 & 6 | 2025-10-07
EAST | October | Under direction of OIC (Dan Zhou) On Site for; - Facility station checks Data in PWQ Excel Workbook Grabs @ 13:35 hrs. FCl: 1.84 mg/L TCL: 1.98 mg/L Analyzer FCl: 1.81 mg/L Equipment out of Service: None Facility running nominally | Stouffville Highway 48 Booster Pumping Station | 2025-10-20
EAST | October | Under direction of OIC (Stephen Baidy) On Site for; - Station Checks Grabs @ 09:31 hrs. FCl: 2.00 mg/L TCl: 2.10 mg/L Analyzer: FCl: 1.98 mg/L Equipment out of Service: None Facility OK | Stouffville Highway 48 Booster Pumping Station | 2025-10-31
EAST | October | On site to complete station check. Time: 14:20 Grab (mg/l) Analyzer (mg/l) Free: 1.92 1.92 Total: 1.96 Verified analyzers with grabs. Checked station and trends. No OOS equipment. No outstanding alarms. | Stouffville Highway 48 Booster Pumping Station | 2025-10-27
EAST | October | Under direction of OIC (Stephen. Baidy) On Site for; - TSSA Upgrade Operator Support Grabs @ 09:31 hrs. FCl: 1.89 mg/L TCl: 2.03 mg/L Analyzer: FCl: 1.89 mg/L FCl: 0.99 mg/L Equipment out of Service: None Facility OK | Stouffville Highway 48 Booster Pumping Station | 2025-10-24
EAST | October | Under direction of OIC (Dan Zhou) On Site for; - Facility station checks Data in PWQ Excel Workbook Grabs @ 12:26 hrs. FCl: 1.77 mg/L TCL: 1.95 mg/L Analyzer FCl: 1.73 mg/L AIT Maintenance and Clean: Start @ 13:41 hrs. Stop @ 14:27 Changed Indicator and buffer reagents for AIT @ 14:36 hrs. ROC called about booster pump 2 VFD fault. -reset VFD, BP2 online *Turbidity Spike due to running air compressor for surge tanks. Equipment out of Service: None Facility running nominally | Stouffville Highway 48 Booster Pumping Station | 2025-10-10
EAST | October | Under Direction of OIC Dan Zhou On site for; Observe 48PS while Maintenance (electrical) run power outage test and portable generator test. To monitor pressure system and surge tank reserves. Pre testing procedure: - Flushed surge tanks and refilled - Took FCl residual from Surge tank Grab @12:56 1.36 mg/L - Called ROC to put both high lifts and both well pumps 5/6 in manual off Station power off @ 13:00 hrs. System Pressure (104 PSI) Volume of Surge Tanks (50%) 13:15 hrs. System pressure (85 PSI) Volume of Surge Tanks (35%) 13:29 hrs. System pressure (67 PSI) Volume of Surge tanks (20%) FCL: 0.42 mg/L @ 13:29 Power switched to portable generator Power off @ 13:36 hrs. Main power back on @ 14:15 hrs. @ 14:15 hrs. ROC placed well pumps and high lifts back in auto. As well as Turbidity meter in Cal mode on SCADA. @14:30 hrs. turb analyzer maintenance performed. @ 14:56 hrs. put turb analyzer out of cal mode. | Stouffville Highway 48 Booster Pumping Station | 2025-10-15
EAST | October | Under direction of OIC (Dan Zhou) On Site for; - Facility station checks Data in PWQ Excel Workbook Grabs @ 12:26 hrs. FCl: 1.77 mg/L TCL: 1.95 mg/L Analyzer FCl: 1.73 mg/L Equipment out of Service: None Facility running nominally | Stouffville Highway 48 Booster Pumping Station | 2025-10-06
EAST | October | On site to test temporary generator power for 48 booster pumps in preparation of new stationary generator planned power outage next week. Test complete and successful. Station and existing generator all good with no sanding alarms. | Stouffville Highway 48 Booster Pumping Station | 2025-10-15
EAST | October | Performed facility station check Data in PWQ sheet Grab @ 11:15 FCl = 1.78 mg/L TCl = 1.90 mg/L Analyzer FCl = 1.82 mg/L Equipment OOS: none Station ok | Stouffville Highway 48 Booster Pumping Station | 2025-10-03
EAST | October | On site to set up temp generator for the booster pumping station for next week. Got wiring prepped and ready to test for tomorrow. Under direction of oic. | Stouffville Highway 48 Booster Pumping Station | 2025-10-14
WEST | October | Onsite for station check No power site offline Site secure No issues observed | King City Wells 3 & 4 | 2025-10-24
WEST | October | Onsite for station check No power site offline Site secure No issues observed | King City Wells 3 & 4 | 2025-10-16
WEST | October | Logged in to wrong facility Supposed to be klieinburg 3 4 | King City Wells 3 & 4 | 2025-10-09
WEST | October | On site for station check No power to site doors locked site secure | King City Wells 3 & 4 | 2025-10-10
WEST | October | -on site to complete work orders -informed ROC of work -completed Diesel Generator Test Run: -start hours = 410.6 -stop hours = 411.8 -run time = 1.2 hours -start fuel = 1547 L -stop fuel = 1513 L -fuel used = 34 L 11:12 - transfer to generator power -ran KLPSWL pump 4 on generator power -completed Chlorine Leak Detector, Test 12:14 - transfer back to utility power -no issues with generator test run | Kleinburg Wells 3 and 4 | 2025-10-23
WEST | October | -on site to complete station check and collect samples -site offline and isolated from distribution system 10:39 - started well #3 in local running to waste at 25.4 l/s 10:39 - started well #4 in local running to waste at 25.8 l/s -checked equipment -reviewed trends -analyzer reagents ok -verified treated water chlorine analyzers: 10:47 - Analyzer readings: Free Chlorine = 0.02 mg/L Total Chlorine = 2.00 mg/L 10:47 - Grabs: Free Chlorine = 0.06 mg/L Total Chlorine = 2.11/2.14/2.14 mg/L 10:59 - adjusted treated water total chlorine analyzer to 2.13 mg/L based on average of 3 grabs -adjusted flow to treated water analyzers causing turbidity reading spikes 11:12 - collected weekly well #3 raw water micro. sample - W/O# W11330687 11:12 - collected weekly well #4 raw water micro. sample - W/O# W11330687 -collected quarter #4 samples - W/O # W11246941 -put both wells back into local off -no other issues found | Kleinburg Wells 3 and 4 | 2025-10-29
WEST | October | On-site for station check Checked residuals Total Analyzer 2.04mg/L Grab 2.08mg/L Free Analyzer 0.02mg/L Grab 0.05mg/L Reagents all okay No known issues | Kleinburg Wells 3 and 4 | 2025-10-10
WEST | October | -on site to complete station check -site offline and isolated from distribution system -checked equipment -reviewed trends -analyzer reagents ok -verified treated water chlorine analyzers: 10:37 - Analyzer readings: Free Chlorine = 0.06 mg/L Total Chlorine = 2.06 mg/L 10:37 - Grabs: Free Chlorine = 0.04 mg/L Total Chlorine = 2.07 mg/L -no issues found | Kleinburg Wells 3 and 4 | 2025-10-03
WEST | October | On site to complete station check and collect weekly bacti samples W11298764. -Ran wells 3&4 in local to waste to collect raw bacti samples. -Verified treated water analyzers: Free Chlorine @ 12:34 Grab: 0.06 mg/L Analyzer: 0.01 mg/L Total Chlorine @ 12:34 Grab: 2.06 mg/L Analyzer: 2.04 mg/L -Entered data into PD sheet | Kleinburg Wells 3 and 4 | 2025-10-14
WEST | October | -on site to complete station check and collect samples -site offline and isolated from distribution system 11:19 - started well #3 in local running to waste at 25.4 l/s 11:19 - started well #4 in local running to waste at 26.0 l/s -checked equipment -reviewed trends -analyzer reagents ok -verified treated water chlorine analyzers: 11:27 - Analyzer readings: Free Chlorine = 0.06 mg/L Total Chlorine = 2.01 mg/L 11:27 - Grabs: Free Chlorine = 0.07 mg/L Total Chlorine = 2.00 mg/L 11:54 - collected weekly well #3 raw water micro. sample - W/O# W11256500 11:54 - collected weekly well #4 raw water micro. sample - W/O# W11256500 -put both wells back into local off -no issues found | Kleinburg Wells 3 and 4 | 2025-10-01
WEST | October | Onsite for annual calibrations Informed ROC Used cal mode on scada during the work Instruments calibrated: FITs, LITs, PIT, chlorinators, chlorine gas sensors, WIT, NIT and AITs AITs reading the same as found. No adjustments made Cleared all associated alarms Informed ROC, armed building and left site | Kleinburg Wells 3 and 4 | 2025-10-06
WEST | October | -on site with power systems contractor for generator semi-annual maintenance -when attempting to transfer site to generator power generator breaker tripped twice. Ran generator in manual with no issues -informed CMS, will investigate transfer issue tomorrow. Generator can be manually transferred if needed. | Kleinburg Wells 3 and 4 | 2025-10-02
WEST | October | Install new lines on chlorine scrubber system | Kleinburg Wells 3 and 4 | 2025-10-09
WEST | October | -on site to troubleshoot generator. Called roc at 1300 to confirm I?ll be generating alarms with my testing on the generator. Placed system into manual off and did meggar test of the cables. Once completed i reinstalled everything and found no issues. Placed system into auto 1400 and called the roc to confirm cleared alarms. Under direction of oic | Kleinburg Wells 3 and 4 | 2025-10-06
WEST | October | Onsite for station check and to collect weekly micro sample W11278901 Ran wells 3&4 in local to waste Checked residuals mg/l @1240 Treated Total analyzer 2.03 grab 2.10 Free analyzer 0.02 grab 0.05 | Kleinburg Wells 3 and 4 | 2025-10-08
WEST | October | -on site to complete work orders -informed ROC of work -completed Ventilation System Inspection - Exhaust Fans -completed Pressure Relief Valve, Inspection -completed Deep Well Exhaust Valve, Maintenance -completed Chlorine Scrubber, Check -completed Chlorine Cylinder Emergency Repair Kit Inspection -completed Heating System, Inspection -completed JHSC Health and Safety Inspection -completed Chemical System Inspection - Silicate: -pump #1 OOS -ran pump #2 into calibration column, no issues -completed Ammonia System, Inspection: -ran both pumps into calibration column, no issues -completed Chemical System Inspection - Chlorine: -completed vacuum test on both chlorinators, no issues -returned all chemical systems to manual/ local off and isolated from system -completed Turbidimeter Maintenance: -verified and cleaned turbidimeter, no issues -completed Chlorine Analyzer, Maintenance: -verified analyzers after maintenance: 12:05 - influent analyzer = 0.05 mg/L Grab = 0.05 mg/L 12:06 - effluent analyzer = 0.09 mg/L Grab = 0.02/0.04/0.02 mg/L 12:08 - adjusted effluent analyzer to 0.03 mg/L based on average of 3 grabs 12:09 - Treated Analyzer readings: Free Chlorine = 0.06 mg/L Total Chlorine = 2.00 mg/L 12:09 - Treated Grabs: Free Chlorine = 0.03 mg/L Total Chlorine = 2.04 mg/L -site back to normal operation | Kleinburg Wells 3 and 4 | 2025-10-02
WEST | October | Station Check (no issues found) site off line input data to PWQ 12:00 Verified Depolox Treated (mg/l) Free: Grab 0.04, A 0.06 Total: Grab 2.00, A 2.06 | Kleinburg Wells 3 and 4 | 2025-10-06
WEST | October | on site for station check Check trends- All okay Topped up hypo tank- 63L/139L Verified analyzers Postinjection- Total CL2 Grab: 3.76 mg/L: Analyzer: 3.70 mg/L Common inlet/outlet- Total CL2 Grab: 3.40 mg/L: Analyzer: 3.41 mg/L Reagents All good in house lab Sample taken while tower draining entered values in PWQ sheet Equipment all okay | Schomberg Elevated Tank | 2025-10-17
WEST | October | On site for station check and weekly bacti sample W11316482 Check trends: all okay Tower filling 09:15- post injection analyzer Grab total Cl2- 3.88 mg/l Analyzer total Cl2- 3.77 mg/L deactivated HL duty- Tower Draining 09:55- common inlet/outlet analyzer Grab Free Cl2 - 0.02 mg/L Grab total Cl2- 3.40 mg/l Analyzer total Cl2- 3.47 mg/L Collected ATP and bacti sample while tower draining. Entered values in pwq sheet Equipment all okay | Schomberg Elevated Tank | 2025-10-22
WEST | October | 10:07- NDMA sample collected while tower draining | Schomberg Elevated Tank | 2025-10-28
WEST | October | -on site to complete station check and to collect sample for in house lab analysis - tower draining at 25.6 l/s, level = 33% - reviewed trends - CL17 reagents ok - checked equipment -recorded readings in PWQ sheet - no issues found -verified analyzers: 11:15 - common inlet/outlet TCL analyzer = 3.41 mg/L 11:15 - common inlet/ outlet grab: FCL = 0.00 mg/L TCL = 3.44 mg/L Mono = 3.19 mg/L 11:24 - post injection TCL analyzer = 4.66 mg/L 11:24 - post injection grab: TCL = 4.56 mg/L | Schomberg Elevated Tank | 2025-10-20
WEST | October | On site for station check and W11246969 Q4 Water Samples W11330635 Micro Sampling (without HPC) Check trends: all okay Tower draining (33%) 10:25- common inlet/outlet analyzer Grab Free Cl2 - 0.04 mg/L Grab total Cl2- 3.50 mg/l Analyzer total Cl2- 3.45 mg/L 10:35- post injection analyzer Grab total Cl2- 4.00 mg/l Analyzer total Cl2- 3.96 mg/L Collected samples while tower draining. Entered values in pwq sheet Equipment all okay | Schomberg Elevated Tank | 2025-10-29
WEST | October | on site for station check Check trends- All okay Topped up hypo tank- 73L/145L Verified analyzers Postinjection- Total CL2 Grab: 3.70 mg/L: Analyzer: 3.63 mg/L Common inlet/outlet- Total CL2 Grab: 3.40 mg/L: Analyzer: 3.42 mg/L Replaced Post injection Analyzer Reagents. in house lab Sample taken while tower draining entered values in PWQ sheet Equipment all okay | Schomberg Elevated Tank | 2025-10-24
WEST | October | on site for station check Check trends- All okay Tower draining (30%) Verified analyzers Postinjection- Total CL2 Grab: 4.01 mg/L: Analyzer: 4.06 mg/L Common inlet/outlet- Total CL2 Grab: 3.43 mg/L: Analyzer: 3.46 mg/L Replaced Post injection Analyzer Reagents. in house lab Sample taken entered values in PWQ sheet Equipment all okay | Schomberg Elevated Tank | 2025-10-27
WEST | October | on site for station check Check trends- All okay Topped up hypo tank- 80L/117.5L Verified analyzers Postinjection- Total CL2 Grab: 3.74 mg/L: Analyzer: 3.68 mg/L Common inlet/outlet- Total CL2 Grab: 3.34 mg/L: Analyzer: 3.40 mg/L in house lab Sample taken while tower draining entered values in PWQ sheet Equipment all okay | Schomberg Elevated Tank | 2025-10-31
WEST | October | On site for Station Check Check trends- All okay Verified analyzers Postinjection- Total CL2 Grab: 3.56 mg/L: Analyzer: 3.61 mg/L Common inlet/outlet- Total CL2 Grab: 3.45 mg/L: Analyzer: 3.50 mg/L Reagents All good Sample taken while tower draining entered values in PWQ sheet Equipment all okay | Schomberg Elevated Tank | 2025-10-03
WEST | October | Onsite for the following work order Informed ROC about the works being done W11301349 SHETCS,JHSC Health and Safety Inspection W11301477 SHETCS, Low Temperature Alarm, Test W11301767 SHETCS, Eye Wash, Cleaning & Solution Replacement W11301780 SHETCS, Inlet/Outlet Heat Trace System, Inspection W11301789 SHETCS, Outlet Heat Trace System, Inspection W11301924 SHETCS, Sodium Hypochlorite Pump, Maintenance W11301939 SHETCS, Sodium Hypochlorite Injection Points, Cleaning W11301313 SHETCS, Gasoline Generator, Test Run W11300963 SHETCS, CL-17sc Analyzer, Maintenance Verified Analyzers 12:25- Common inlet/outlet Total CL2- Grab:3.00 mg/L, Analyzer:2.94 mg/L 12:30- Post injection Analyzer Total CL2- Grab:3.80 mg/L, Analyzer:3.76 mg/L | Schomberg Elevated Tank | 2025-10-02
WEST | October | On site for station check and weekly bacti sample W11278729, NDMA W11247912 Check trends: all okay Tower draining 10:10- common inlet/outlet analyzer Grab Free Cl2 - 0.06 mg/L Grab total Cl2- 3.60 mg/l Analyzer total Cl2- 3.49 mg/L Collected ATP, NDMA and bacti sample while tower draining. Activated HL duty- Tower filling 10:40- post injection analyzer Grab total Cl2- 3.80 mg/l Analyzer total Cl2- 3.72 mg/L Entered values in pwq sheet Reagents all good. Equipment all okay. | Schomberg Elevated Tank | 2025-10-08
WEST | October | On site for station check and weekly bacti sample W11298712 Check trends: all okay Topped up Hypo Tank-54L/91L Tower filling 09:35- post injection analyzer Grab total Cl2- 3.72 mg/l Analyzer total Cl2- 3.70 mg/L deactivated HL duty- Tower Draining 10:00- common inlet/outlet analyzer Grab Free Cl2 - 0.02 mg/L Grab total Cl2- 3.52 mg/l Analyzer total Cl2- 3.50 mg/L Collected ATP and bacti sample while tower draining. Entered values in pwq sheet Changed common inlet/outlet analyzer Reagent bottles. Equipment all okay | Schomberg Elevated Tank | 2025-10-14
WEST | October | on site for station check Check trends- All okay Verified analyzers Postinjection- Total CL2 Grab: 3.80 mg/L: Analyzer: 3.73 mg/L Common inlet/outlet- Total CL2 Grab: 3.50 mg/L: Analyzer: 3.52 mg/L Reagents All good Sample taken while tower draining entered values in PWQ sheet Equipment all okay | Schomberg Elevated Tank | 2025-10-10
WEST | October | On site for station check and weekly bacti sample W11256448 Check trends: all okay Tower draining 10:50- pre injection analyzer Grab Free Cl2 - 0.04 mg/L Grab total Cl2- 3.50 mg/l Analyzer total Cl2- 3.41 mg/L Collected ATP and bacti sample while tower draining. Activated HL duty- Tower filling 11:10- post injection analyzer Grab total Cl2- 3.66 mg/l Analyzer total Cl2- 3.63 mg/L Entered values in pwq sheet Reagents all good. Equipment all okay. | Schomberg Elevated Tank | 2025-10-01
WEST | October | Onsite to check hypo pump 2 OOS. (no alarm came in, fault discovered during normal SCADA check) run pump 2 in local. Pump back in service. | Schomberg Elevated Tank | 2025-10-15
EAST | October | Reviewed the following on scada - To review trends and record trains MITs - To review trends and record filter daily performance, - To review permeate UV trends, no issues Operations and Adjustments: 0700hrs: ASI onsite for intake pipe inspection, LOTO the LL pumps, notified ROC and contractor on site Deactivated M-cleans on trains 5 - 8 Completed the follwing WOs: Turbidity Analyzer TU5300 Maintenance, Chemical System Inspection - Chlorine Wastewater Transfer Pump Maintenance and Duty Rotate, Sludge Transfer Pump Maintenance and Duty Rotate, UV System calibration Georgina WTP intake pipe (external) and outfall inspection Georgina Water Treatment Plant MIT and Daily Filter Performance Review and Log, 1600 hrs: returned all HL pumps and UV system to auto, cleared associated alarms, was active. 1600 hrs: Returned train 5 to 8 to M-clean schedule Initiated M-cleans on trains 5 - 8. Train 1 current 5 in M clean mode, rest are pending, will continue to monitor online. Low Lift Station: Chlorine analyzers: Both existing and newly installed chlorine analyzer and pH probes are running concurrently. LOTO all 4 LL pumps for intake inspection. Inspection crew added their locks in the LOTO process Equipment OOS: - Sludge pump3 emergency stop alarm - GAC3 FCV deviation Notified ROC that plant is back in full operation, no issues | Georgina Water Treatment Plant | 2025-10-28
EAST | October | Initiating MIT on train 3 to see if it passes or fails on the low pressure decay test. MIT failed again will look into it more thoroughly. | Georgina Water Treatment Plant | 2025-10-27
EAST | October | Reviewed the following on scada - To review trends and record trains MITs, all passed - To review trends and record filter daily performance, no issues observed - To review permeate UV trends, no issues - Wet well mussel plate inspection completed Operations and Adjustments: Plant running, mussel control chlorine system deactivated for raw water sample collection 0840 hrs: Collected Raw water bacT and other samples 0850 hrs: Collected treated bacT and other samples from Keswick header Keswick header chlorine residual: FCL = 1.95 mg/l. TCL = 2.26 my/l 1006 hrs: adjusted contact chamber tank 1 chlorine analyzer reading from 2.38 mg/l to 2.52 mg/l based on average of 3 grabs 1114 hrs: adjusted clearwel tank 11 chlorine analyzer reading from 1.92 to 2.18 mg/l based on average of grabs 1024 hrs: Adjusted Post clearwell chlorine analyzer free reading from 1.78 mg/l to 2.00 mg/l base on 2 grabs 1140 hrs: adjusted keswick free chlorine analyzer reading from 1.80 mg/l to 2.00 mg/l based on average of 3 grabs 1143 hrs: adjusted free chorine analyzer from 1.68 to 2,00 mg/l based on average of 3 grabs Low Lift Station: Chlorine analyzers: Both existing and newly installed chlorine analyzer and pH probes are running concurrently. Equipment OOS: - Sludge pump3 emergency stop alarm - GAC3 FCV deviation alarm - LL pump 3 | Georgina Water Treatment Plant | 2025-10-22
EAST | October | Reviewed the following on scada - To review trends and record trains MITs - To review trends and record filter daily performance, - To review permeate UV trends, no issues - Wet well mussel plate inspection completed - Shoreline Observation Completed and recorded in PWQ data sheet Operations and Adjustments: Collected both regulatory and in-house operational samples 13:35 hrs: Samples collected from the keswick header with the following Residual: Grab: FCL = 1.85 mg/l. Analyzer reading = 1.85 mg/l TCL = 2.48 mg/l. Analyzer reading = 2.50 mg/l Low Lift Station: Chlorine analyzers: Both existing and newly installed chlorine analyzer and pH probes are running concurrently. Cleaned and calibrated wet well and intake chlorine analyzers Equipment OOS: - Sludge pump3 emergency stop alarm - GAC3 FCV deviation | Georgina Water Treatment Plant | 2025-10-29
EAST | October | Reviewed the following on scada - To review trends and record trains MITs, all passed - To review trends and record filter daily performance, no issues observed - To review permeate UV trends, no issues - Wet well mussel plate inspection completed - Lake shoreline inspection, Operations and Adjustments: Switched UV duties, placed UV2 in lead duty ~ UV2 had critical fault at the start of the previous cycle. UV2 running with no issues. Received hypo top up Started M-clean on train 8 Low Lift Station: Chlorine analyzers: Both existing and newly installed chlorine analyzer and pH probes are running concurrently. Calibrated and adjusted intake chlorine analyzer reading, analyzer reading 0.00 mg/l upon arrival. Calibrated analyzer with portable water, returned to service and made adjustment =0.18 mg/l Equipment OOS: - Sludge pump3 emergency stop alarm - GAC3 FCV deviation alarm - LL pump 3 | Georgina Water Treatment Plant | 2025-10-17
EAST | October | Monitored M-cleans on trains 1-4, train3 pending. Also found train8 pending MIT in off position. Turned train8 on, train 8 started MIT. Passed MIT ( H = 1.60 kpa, L = 2.15 kpa) train8 back in production. Directed ROC to manually initiate M-clean on train3 after train4 is done cleaning. | Georgina Water Treatment Plant | 2025-10-18
EAST | October | Reviewed the following on scada - To review trends and record trains MITs, train 3 failed MIT on Low pressure side. - To review trends and record filter daily performance, - To review permeate UV trends, no issues - Wet well mussel plate inspection completed Operations and Adjustments: 0700hrs: ASI onsite for intake pipe inspection, LOTO the HL pumps, notified ROC Deactivated M-cleans on trains 1 - 4 MIN of Labour inspectors on site, inspected LOTO and LOTO procedures looked at scada to verify how other fail-safe measures. Cleaned and calibrated both east and west sed tanks chlorine analyzers. Cleaned and calibrated Outfall to the lake chlorine analyzer - 0.00 mg/l 1628 hrs: returned all HL pumps and UV system to auto, cleared associated alarms, was active. 1632hrs; initiated MIT on train3, train passed as follows: H = 5.37 kpa. L= 1.97 kpa 1700 hrs: Returned train 1 to 4 to M-clean schedule Initiated M-cleans on trains 1 - 4. Train 1 currently in McLean mode, rest are pending, will continue to monitor online. Low Lift Station: Chlorine analyzers: Both existing and newly installed chlorine analyzer and pH probes are running concurrently. LOTO all 4 LL pumps for intake inspection. Inspection crew added their locks in the LOTO proces. Equipment OOS: - Sludge pump3 emergency stop alarm - GAC3 FCV deviation alarm | Georgina Water Treatment Plant | 2025-10-27
EAST | October | Reviewed the following on scada - To review trends and record trains MITs, all passed - To review trends and record filter daily performance, no issues observed - To review permeate UV trends, no issues - Wet well mussel plate inspection completed Operations and Adjustments: Notified ROC before completing the following: Cleaned and calibrated clear well and contact tanks chlorine analyzers Cleaned and calibrated sedimentation tanks chlorine analyzers Initiated manual backwash on train8 after LL pump3 test Low Lift Station: Chlorine analyzers: Both existing and newly installed chlorine analyzer and pH probes are running concurrently. 0800 hrs: LL shut down to reconnect LL pump3 to power after new vfd installation as requested by contractor 1230 hrs Tested LL pump 3 in manual, ran pump3 through train 8 Equipment OOS: - Sludge pump3 emergency stop alarm - GAC3 FCV deviation alarm - LL pump 3 | Georgina Water Treatment Plant | 2025-10-20
EAST | October | Reviewed MIT and daily filter performance on all trains - all passed. Activated duty at 08:45. Turned off mussle control at 09:15. Accepted 3 chlorine cylinder toners at 11:00. Changed chlorine cylinder toner at 11:18. Start: 42.19/734kg Stop: 917/734kg Time: 13:35 Keswick Time: 13:35 Grab (mg/l) Analyzer (mg/l) Free: 1.85 1.85 Total: 2.48 2.50 Activated duty again at 13:20 due to duty shut off. | Georgina Water Treatment Plant | 2025-10-29
EAST | October | MIT pressure decay on low pressure on train 3 failed over night at 02:20. Initiated MIT at 09:53 to see if it passes. MIT failed at 10:25 out train 3 off at 10:30 will inform team on Monday. | Georgina Water Treatment Plant | 2025-10-25
EAST | October | Completing following work orders: W11288937 Air Dryer Check W11288948 Air Compressor Maintenance W11290594 Compressed Air System Inspection W11303621 Dehumidifier Element Change Out Reviewed MIT and daily filter performance on all trains - all passed. At 09:01 completed UV dehumidifier work orders which caused alarms cleared alarms at 10:40. No issues with work orders on site. Eric from instrumentation is on site working on back wash tank LIT. | Georgina Water Treatment Plant | 2025-10-16
EAST | October | To review trends and record trains MITs - To review trends and record filter daily performance, - To review permeate UV trends, no issues Operations and Adjustments: GAC2 turbidity fault, fault came in when duty started, changed vial and cleared turbidity fault alarm Troubleshoot with newly installed chlorine SV2 with Chris Scott tested on site auto no issues, placed in lead for the duty for further testing. Notified ROC. Low Lift Station: Chlorine analyzers: Both existing and newly installed chlorine analyzer and pH probes are running concurrently. Equipment OOS: - Sludge pump3 emergency stop alarm - GAC3 FCV deviation | Georgina Water Treatment Plant | 2025-10-30
EAST | October | On site to complete station check and lab analysis. Reviewed MIT and daily filter performance on all trains - all passed. Put inlet valve for UV2 back to auto at 08:50 after it had been left in local. Activating duty at 09:00 Took grabs Time: 10:45 Keswick Grab (mg/l) Analyzer (mg/l) Free: 1.63 1.68 Total: 2.05 2.11 Time: 10:48 Sutton Grab (mg/l) Analyzer (mg/l) Free: 1.63 1.65 Total: 2.12 2.10 After multiple grabs adjusted the hi lift or post clear well analyzer at 10:37 from a 1.45mg/l-1.70mg/l. | Georgina Water Treatment Plant | 2025-10-17
EAST | October | On site for facility station check, equipment verification and lab analysis Review MIT and daily filter performance on all membrane trains, all passed and no issues @11:10 - activated system duty - KSTKWP level - 69% Reviewed trending - no issues Completed PWQ sheets and lab data sheets Enabled Mussel control chlorination @12:50 Operational adjustments: Adjusted Keswick Header FCL from 1.47 to 1.65 mg/L Adjusted Keswick Header TCL from 2.00 to 1.90 mg/L Adjusted Sutton Header FCL from 1.51 to 1.63 mg/L Equipment OOS: Sludge P3 Station ok | Georgina Water Treatment Plant | 2025-10-31
EAST | October | Attending site to check fault on backwash holding tank LIT (W11369130). Transmitter electronics was found to be faulty and was replaced. SCADA alarms related to this device were cleared after replacement. ROC was notified before and after work was performed. | Georgina Water Treatment Plant | 2025-10-16
EAST | October | Entry made on 10/20/2025 was meant for Mount Albert Chlorine Cylinder change. | Georgina Water Treatment Plant | 2025-10-21
EAST | October | Attending site to check pH probe on WASH_AIT1 chlorine analyzer (W11399966). Replaced broken pH probe and calibrated using 7 & 10 buffers. Calibration mode was used during maintenance and associated SCADA alarms were cleared. ROC was notified before and after maintenance work was performed. | Georgina Water Treatment Plant | 2025-10-28
EAST | October | On site to complete the following: At 11:08 changed duty?s for low lift so that low lift pump 3 is in duty 1. Reviewed MIT and daily filter performance on all trains - all passed. At 11:25 started GAC2 backwash. Lowered filter to 3.00m, Backwashed on low, hi, and low wash from 11:52am-12:20pm. Filtered to waste for 22mins and during this time NTU is 0.163NTU at the start, at the end it is 0.132. Put GAC 2 back in service at 13:31. All alarms for GAC2 during this time are associated with GAC2 backwash including trends that are varying. | Georgina Water Treatment Plant | 2025-10-23
EAST | October | To review trends and record trains MITs, all passed - To review trends and record filter daily performance, no issues observed - To review permeate UV trends, no issues - Wet well mussel plate inspection completed - Did shoreline lake observation and recorded in pwq data sheet Operations and Adjustments: Received diesel fuel for plant generator. FMB FILT Train 1 failed to complete M clean, train went into pending mode when triggered for M clean. After a little troubleshoot remotely, tried FMB FILT train 2 by adjusting the start and stop times. Train2 went into M clean mode right away. Did the same for train 3, train also completed M clean with no issues. Train 1 completed M clean and returned to production after PCS disengaged MC pending alarm. Low Lift Station: Chlorine analyzers: Both existing and newly installed chlorine analyzer and pH probes are running concurrently. Drained wet well #2 for contractor to install LITs . Notified ROC, isolated wet well 2 and pumped down 16:14 hrs: returned wet well 2 to service. Notified ROC Equipment OOS: - Sludge pump3 emergency stop alarm - GAC3 FCV deviation alarm | Georgina Water Treatment Plant | 2025-10-09
WW-NORTH | October | On site to check odour control sump pit high level float. Float is working, intrinsically safe barrier that relays the input back to PAC is not working. Need to source a replacement and install. | Keswick Water Resource Recovery Facility | 2025-10-21
WW-NORTH | October | Onsite for daily operations Review scada/trends No decanting - low sludge level Collect in house lab samples Complete lab Enter data in sharepoint Collect weekly regulatory samples - raw only Divert filter feed to lagoon at 10:36hrs due to hi ammonia level (2.05mg/L) UV in local off Effluent pumps in local off Mechanical maintenance onsite for diffuser repairs in sbr1 Micheal B and Chris C stay after hours to assist maintenance with repairs | Sutton Water Resource Recovery Facility | 2025-10-21
WW-NORTH | October | Decanted and transferred STT 2 and 3 Switched WAS flow from STT 1 to STT 2 | Keswick Water Resource Recovery Facility | 2025-10-26
WW-NORTH | October | Performed facility station check Completed Lab analysis: Data in Sharepoint Decanted Sludge holding tanks: 1 & 2 Transferred Sludge holding tank: 1 Batch Wasted Recorded Odor Control Unit numbers Inspected headworks: leveled grit bin and raked bar screen Added 10 bags of soda ash Unclogged clarifier 3 scum trough | Keswick Water Resource Recovery Facility | 2025-10-27
WEST | October | -on site to complete station check -system duty active, pumps 2 and 3 running -checked equipment -reviewed trends -recorded readings in PWQ sheet -analyzer reagents ok -verified chlorine analyzers: 12:56 - Analyzer readings: Free Chlorine = 0.04 mg/L Total Chlorine = 2.15 mg/L 12:56 - Grabs: Free Chlorine = 0.04 mg/L Total Chlorine = 2.16 mg/L -no issues found | Kleinburg HWY 27 Booster Pumping Station | 2025-10-27
CENTRAL | October | On-site to top up NaSi day tanks. Filled tanks to fill line on tank 2, 589 to 1116L. NaSi tank OOR alarm triggered (123cm reading, span of 120). OOR alarm interlocked both NaSi pumps, but did not interlock Wells. Placed Wells man/off while so investigated. Disabled the OOR alarm as it appears the day tank LIT is still functioning normally, will re-enable once level below 120cm, interlock on NaSi pumps cleared, returned Wells to auto. Informed ROC. | Newmarket Well 1 & 2 | 2025-10-27
WW-NORTH | October | Inspected sludge transfer pumps. | Keswick Water Resource Recovery Facility | 2025-10-07
WEST | October | Station Check (no issues found) input data to PWQ 13:10 Verified Deplolox (mg/l): Free: Grab 0.03, A 0.05 Total: Grab 1.38, A 1.43 | Woodbridge East Booster Pumping Station | 2025-10-06
WW-WEST | October | In to Complete Reg. Sampling. Reviewed SCADA and Trends. No New Issues Found. | Nobleton Janet St. Sewage Pumping Station | 2025-10-07
WEST | October | Station Check (no issues found) input data to PWQ 14:30 Verified Depolox (mg/L): Treated: Free: Grab 1.43, A 1.41 Total: Grab 1.55 Reservoir Outlet: Free: Grab 1.69, A 1.77 | Ansnorveldt Wells 2, 3 & Reservoir | 2025-10-06
CENTRAL | October | Under direction of OIC, Ryan Bewley. Commissioned and calibrated diesel tank LIT with contractors. Connected generator modbus connection to SCADA system. | Newmarket Kirby Pumping Station | 2025-10-06
WEST | October | -on site for station check -pumps running/chamber dry | Nobleton Booster Pumping Station | 2025-10-06
CENTRAL | October | ROC called @ 6:55pm coz power blip, gas scrubber overload alarm & VFD fault came alarm came in ROC called, placed wells in manual and act reset scrubber alarm from building tab and started wells in auto as duty active. | Queensville Wells No. 1 and 2 | 2025-10-07
EAST | October | On site to check station and equipment. Pump 1 is man/on due to distribution valving arrangement. Station readings and chlorine grabs are in PWQ sheet. Reviewed trends, station is under normal operation. Generator warning alarm is outstanding to low fuel level. Fuel top up is in the que. | Richmond Hill Pugsley Pumping Station | 2025-10-06
WW-NORTH | October | Station checks completed Enter data into SharePoint | Holland Landing Sewage Pumping Station | 2025-10-23
WW-NORTH | October | Onsite to check station Review scada/trends Enter data in sharepoint | Sutton Woodriver Bend Sewage Pumping Station | 2025-10-23
WW-WEST | October | Completed station check. Reset earth leakage alarm on EF15 VFD. No other issues found. Raked bins. Entered data in spreadsheet. | Vaughan Humber Pumping Station | 2025-10-17
WW-WEST | October | - Inspected the generator and fuel level, all okay. Started the generator 1 at 9:26. Recorded readings on SharePoint after 30 minutes, no issues. Ran for approximately one hour. Runtime for generator 1 from 422.5 hrs to 423.5 hrs. Cleared alarms - Started generator 2 at 10:36. Recorded readings after 30 minutes. Run time for generator 2 from 398.4 hrs to 399.5 hrs. No issues with readings. Cleared alarms - Fuel level readings before: tank 1 at 0.93 m, tank 2 at 0.94 m, and gen 2 day tank at 1.05 m. Fuel readings after: tank 1 at 0.92 m, tank 2 at 0.94 m, and gen 2 day tank at 0.74 m - Added 8 bags of soda ash into the hopper - Inspected diversion tank blowers 1 and 2. Ran in manual, no issues. Filters are good. Belts are good. Oil level is good. Cleared diversion tank 1 and 2 uncommanded stop and general alarm once done - Inspected circular plant aeration blowers 1-4. Ran in manual with no issues. Oil replaced last month, all good. Belts are good. Cleared aeration blowers 1, 2 and 3 uncommanded stop alarm once done - Inspected aeration blowers 1 and 2. For aeration blower 1, found the filter cap on the floor and placed it back. Oil is all good. Belt is good. For aeration blower 2, filter is good, belt okay, and oil is good. No alarms created - Inspected raw sewage blower 1 and 2. Oil and filters are all good. Removed oil absorbent and cleaned up the area. Cleared alarms - Inspected sludge tank blowers 1 and 2. Cleared sludge tank blower 2 failed alarm. Filters might need cleaning soon. Oil is all good. Belts are good - Inspected vortex blowers 1 and 2. Filters are very good. Oil is good and belts are good. - Inspected WAS pumps 3-4. No issues. Couplings are good - Rotated RAS pump duties. Pump 2 from auto to manual off. Pump 1 to auto. Pump 3 from manual off to auto. Pump 4 from auto to manual off. - Enabled RAS batch wasting mode. Wasted 35 m^3 from train 1 and 25 m^3 from train 2 then reset RAS batch wasting mode once done | Kleinburg Water Resource Recovery Facility | 2025-10-09
ROC | October | LSSS - Ben from Property services off site. JDSS - Christian from Ferguson electric leaving site. | ROC General | 2025-10-10
CENTRAL | October | -Performed station check - logged station readings into PWQ sheet Grab: free=0.13mg/L total=3.02mg/L@12:35 influent free=2.60mg/L effluent free=2.44mg/L Analyzer: free=0.12mg/L total=3.06mg/L influent free=2.64mg/L effluent free=2.48mg/L -Collected weekly BacT sample YD #W11317110 -Changed effluent free reagents | Aurora Wells 1-4 Water Treatment Plant | 2025-10-22
WEST | October | Onsite for station check Duty not active Checked residuals mg/L @1038 Total analyzer 1.95 grab 1.85 Free grab 0.04 grab 0.02 reagents ok Exercised pumps 1&2 in local Historian heartbeat alarm came in, still trending right now | Kleinburg Whisper Lane Booster Pumping Station | 2025-10-16
WEST | October | Delivered rough estimate 750 L silicate to bulk tank. | Nobleton Wells 3 & 7 | 2025-10-10
EAST | October | On-site to change UPS batteries | Markham PD5 Reservoir | 2025-10-24
WW-NORTH | October | Station checks completed Enter data into SharePoint Check diesel containment | Holland Landing Sewage Pumping Station | 2025-10-09
WW-NORTH | October | Station checks completed Enter data into SharePoint Exercise force main valves turn pumps manual off while testing Change OCU grease screen Six month outfall check Beaverdam has been built and pond level is high, Work order has been made | Queensville West Sewage Pumping Station | 2025-10-09
WEST | October | Decreased both chlorinator dosage factors 160 to 157 % due to high effluent residual | Holland Landing Well No. 2 | 2025-10-09
CENTRAL | October | Informed ROC. Onsite to perform annual maintenance/calibrations. Put the devices in calibration mode. Devices were done as below. TWR_PIT, TWR_FIT, FREE and TOTAL AIT, TWR_LCV. Took a multiple grab samples and adjusted analyzer accordingly. AL TOTAL AIT - 2.91 mg/l, Grab Sample - 2.89 mg/l AL Free AIT - 0.03 mg/l, Grab Sample - 0.03 mg/l. All the related alarms were cleared and no issues. Informed ROC, armed the building and left the site. | Newmarket (Southeast) Ivsbridge Elevated Tank | 2025-10-09
WW-NORTH | October | On site with Aiden, Kyle J Rae and Satnam to trace heat trace bridge circuits found burn up wires in chamber in the yard repaired connections and verified 24 V at heat trace controllers had Yash invert alarm control signal key traces are functional no alarms currently present systems all back in auto | East Gwillimbury 2nd Concession Sewage Pumping Station | 2025-10-31
WW-NORTH | October | Attended for station check Recorded station readings in rounds sheet Checked dry well - p.2 running in duty Completed scheduled work orders Checked forcemain heat trace systems - no alarms showing in river bridge panel Inspected facility outfall Checked diesel containment pits Reviewed SCADA/trends. | East Gwillimbury 2nd Concession Sewage Pumping Station | 2025-10-14
WW-NORTH | October | On site for Generator load bank test with Total Power. Monitoring 1 hr generator station transfer test with operator. Generator station transfer completed. Total Power technician on site performing 2 hr load bank test. Generator controller in Local, circuit breaker to ATS opened. ROC notified. Generator not in auto, generator fault and generator warning alarms acknowledged. Generator load bank test complete. Generator controller returned to auto, all equipment returned to normal operation. ROC notified. | Queensville West Sewage Pumping Station | 2025-10-03
ROC | October | KSETDP- Kalid from IAM onsite. | ROC General | 2025-10-03
WW-NORTH | October | station checks lab and readings Bar screen auger hopper full, drained liquid. filters inspected, ok property maintenance on site checking emergency lighting in MCC and blower room. | Sutton Water Resource Recovery Facility | 2025-10-30
WW-NORTH | October | Onsite for daily operationa Review scada/trends Allow accuworx access to continue sbr1 maintenance Collect weekly regulatory samples Collect in house lab samples Complete lab Enter data in sharepoint Check station Decant stt plus transfer after load taken Reduce wasting in sbr2 from 350s down to 250s | Sutton Water Resource Recovery Facility | 2025-10-14
ROC | October | Carter Dunn Signing Out | ROC General | 2025-10-13
WEST | October | Reduced post injection target 3.50 to 3.15 mg/L | Holland Landing West Elevated Tank | 2025-10-14
WEST | October | Onsite for station check and to collect weekly micro sample W11298750 @1205 East cell Total grab 1.24 Free grab 0.01 Sl1000 Mcl 1.17 F nh3 0.12 T nh3 0.35 No2 0.000 West cell @1209 Total grab 1.20 Feee grab 0.04 Pumping station grab @1218 Total grab 1.55 Free grab 0.04 | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2025-10-14
EAST | October | On site for station check and sample collection. 9:45 collected samples from the North cell, station draining at the time of sampling Grabs, in mg/L, FCl 0.05, TCl 1.23 Analyzer TCl 1.24 Collected BacT sample YD W11298670 Unable to access the shared PWQ sheet so entering the North cell SL1000 data here, as follows, in mg/L Mono 1.12 FA 0.09 TA 0.31 Nitrite 0.00 pH 8.00 Replaced total chlorine analyzer reagents Check station and equipment, reviewed trends. No observed issues | Markham PD6 Reservoir | 2025-10-14
EAST | October | On site for station check and weekly micro sampling (W11299400) Tower level - 72% and draining at 32% Recorded station readings in PWQ sheets Verified analyzer readings with grab chlorine residuals from 08:32 to 08:44 Inlet: Free Grab: 1.86 mg/L / Analyzer: 1.70 mg/L (Adjusted analyzer based on grab) Total grab: 2.36 mg/L / Analyzer: 2.29 mg/L Outlet: Free grab: 1.50 mg/L / Analyzer: 1.39 mg/L (Adjusted analyzer based on grab) Total grab: 1.86 mg/L / Analyzer: 1.96 mg/L (Adjusted analyzer based on grab) Header: Free grab: 1.51 mg/L / Analyzer: 1.47 mg/L Total grab: 1.83 mg/L / Analyzer: 1.89 mg/L Collected micro sample @08:45 from header Reviewed trends, equipment OOS: None Station ok | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2025-10-14
WW-NORTH | October | On site to remove fixed ladder out of head works tower, where only able to get the bottom 10 feet of ladder due to access | Sutton Water Resource Recovery Facility | 2025-10-01
WW-WEST | October | Completed station check. No issues found. Added oil to screen drip oilers. Entered data in spreadsheet. Test ran standby generator. Start: 290.6 hrs. Stop: 291.6 hrs. Inspected heat exchanger radiator. Found fan 3 making unusual squeaking sounds. Created W11331647 work order to have problem investigated. Checked for, but did not find any, hazardous waste. Tested metro overflow float alarm. ROC received alarm. Tested hi/lo temperature alarm. ROC received alarm. Tested dry well flood float alarm. ROC received alarm. Inspected sump pit. Functioning satisfactorily. | Vaughan Humber Pumping Station | 2025-10-01
ROC | October | KSTP - Christian from Ferguson electric on site. | ROC General | 2025-10-01
CENTRAL | October | Station and equipment checked, no issues found Chemical levels and systems inspected, ok Weekly Bacti samples taken Topped up motor mineral oil Well 1 Verified analyzers, all grabs and readings emtered in to PWQ sheet influent F @ 0938 g:2.84 a:2.62 Effluent F @0943 g:2.56 a:2.43 Treated F @ 0945 g:0.18 a:0.14 Treated T @ 0949 g:2.90 a:2.92 temp 11.3 | Newmarket Well 1 & 2 | 2025-10-01
WW-NORTH | October | station checks sharepoint data entry | Sutton Woodriver Bend Sewage Pumping Station | 2025-10-30
CENTRAL | October | On-site to assist PCS/CMS electrical with metro valve troubleshooting. CMS replaced relays for solenoids on valve and I confirmed mechanical/electrical control of the valve via SCADA. Valve appears to have delay on receiving setpoint commands Chris Scott (PCS) determined that a PAC update is needed at a future date. Valve operating, will monitor. | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2025-10-30
CENTRAL | October | Onsite for station and equipment check, no issues found Changed outlet total reagents. Notified the ROC of testing tested and reset chlorine leak detection system. Worked well and reset on OIT panel. Chemical systems and levels inspected Verified analyzers, entered all readings and grabs into a PWQ sheet. | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2025-10-31
WEST | October | Onsite for station check Duty active Checked residuals mg/l Pre injection @1148 Total analyzer 1.07 grab 1.14 Free analyzer 0.06 grab 0.06 Sl1000 Mcl 0.20 F nh3 0.29 T nh3 0.33 Post injection @1211 Total analyzer 2.96 grab 2.96 Free analyzer 0.06 grab 0.03 Sl1000 Mcl 0.77 F nh3 0.28 T nh3 0.77 Tank @1202 Total grab 1.00 Free grab 0.07 Sl1000 Mcl 0.27 F nh3 0.35 T nh3 0.4 No2 0.004 Nitrate grab 0.048 Deactivated duty On last top up of ammonia may not have been mixed properly added more water | Holland Landing West Elevated Tank | 2025-10-31
EAST | October | On site for station check and equipment verifications - recorded station readings in PWQ sheets Tower level - 73% and draining at 23 L/s Verified analyzer readings - made the following adjustments between 09:50 and 10:03 Header free: 1.68 mg/L ??> 1.56 mg/L Inlet free: 1.75 mg/L ??> 1.64 mg/L Outlet free: 1.31 mg/L ??> 1.60 mg/L Reviewed trends, equipment OOS: None Station ok | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2025-10-31
WW-NORTH | October | station checks sharepoint data entry | Sutton High Street Sewage Pumping Station | 2025-10-20
CENTRAL | October | On-site for station and equipment check. No issues found. Verified analyzers, all measurements and grabs entered into PWQ sheet. Adjusted mono on post injection from 2.49 to 2.29. | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2025-10-20
WW-NORTH | October | On site to meet Bell technician to fix phone line. Phone line is restored. Confirmed auto dialer test alarm with ROC. | Sutton High Street Sewage Pumping Station | 2025-10-07
CENTRAL | October | -Performed station check - logged into PWQ sheet Grab: total=3.16mg/L free=0.02mg/L@9:35 Analyzer: total=3.08mg/L free=0.02mg/L -Collected weekly BacT sample YD W11279411 -Checked Depolox reagents - OK | Aurora Orchard Heights Pumping Station & Reservoir | 2025-10-08
CENTRAL | October | Diesel training Install new 4 inch pressure gauges on 1 5 and 6 | Newmarket Kirby Pumping Station | 2025-10-06
CENTRAL | October | Onsite to complete annual calibrations Informed ROC. ROC placed wells to manual off Used cal mode on scada during the work Instruments calibrated: Well FITs and LITs. Chemical LITs. Discharge PIT Cleared associated alarms Informed ROC. Asked to place duty back to auto. Armed building and left site No outstanding issues | Newmarket Well 1 & 2 | 2025-10-07
WW-NORTH | October | Performed station check Entered readings into SharePoint | Keswick Joe Dales Sewage Pumping Station | 2025-10-09
CENTRAL | October | On-site for station check. Site remains offline, no new issues found. | Newmarket (London) Yonge Street Elevated Tank | 2025-10-10
LINEAR | October | Air valve chamber at West Beaver Creek and HWY 7. Assisted with air valve replacement and check valve install. After replacement/install flushed the air valve and took a residual. Free-0.05 mg/l Total-1.37 mg/l | Linear Water System | 2025-10-08
CENTRAL | October | Onsite to complete station check and sampling. COC W11299501 and W11247926. 08:38 Reservoir level at 70% and draining at 54 l/s. 08:50. Verified analyzer (mg/l) and collected samples. Free chlorine: 1.30. Analyzer: 1.35 Total Chlorine grab: 1.61. Analyzer: 1.55 No new issues found. | Keswick West Park Reservoir | 2025-10-14
WEST | October | -on site to complete station check -activated system duty for station check, pump 2 running -checked equipment -reviewed trends -recorded readings in PWQ sheet -verified chlorine analyzers: 10:45 - Analyzer readings: Free Chlorine = 0.06 mg/L Total Chlorine = 1.62 mg/L 10:45 - Grabs: Free Chlorine = 0.04 mg/L Total Chlorine = 1.57 mg/L -no issues found | Woodbridge East Booster Pumping Station | 2025-10-27
WEST | October | Onsite for station check Pd8 duty active Checked residuals mg/l @1246 Total analyzer 1.85 grab 1.82 Free analyzer 0.00 grab 0.04 Reagents ok | East Vaughan Teston Pumping Station | 2025-10-27
WEST | October | -on site to complete station check -system duty active, pump 3 running -checked equipment -reviewed trends -recorded readings in PWQ sheet -verified chlorine analyzers: 09:22 - Analyzer readings: Free Chlorine = 0.07 mg/L Total Chlorine = 1.64 mg/L 09:22 - Grabs: Free Chlorine = 0.03 mg/L Total Chlorine = 1.53/1.53/1.57 mg/L 09:34 - adjusted total chlorine analyzer to 1.54 mg/L based on average of 3 grabs -no other issues found | Woodbridge East Booster Pumping Station | 2025-10-24
WW-CEAST | October | -station check of site -reviewed SCADA -inspected site -entered data into SharePoint -pump 2 remains OOS, pump out for repair -station okay | Newmarket Sewage Pumping Station & Equalization Tank | 2025-10-24
WW-CEAST | October | Took station readings and entered into SharePoint,, checked the dump pad all 3 lines available. Tried resetting the heat trace - it cleared on the panel but did not clear on SCADA, will try again Monday. Checked both compressors oil/belt - OK, also checked pump floor - all good. Switched out bin in the screening room and put the other bins back inside. Station running under normal ops - pump 3 still in Duty 7 due to flow meter. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-10-31
WW-CEAST | October | Got everything set up for Accuworx then completed station check and entered readings into SharePoint. Checked both compressors oil/ belt - OK. Chris had to clear 2 lines down at the dump pad as well. Cell 1 finished around lunch so we ( Chris and I ) opened the inlet gates for cell 1 and closed the gates for cell 2. I primed the 3 pumps 1,2 & 3 and put them in the respective duties. I switched the controlling LIT over to cell 1 - LIT 2. Chris turned bar screen 1 on and 2 off. Once cleaning was over Chris and I went and checked NMMS chamber - heater is on and chamber is dry - we also cleared the alarm in the cabinet. Station is running with cell 2 off line - ROC and Barry are informed about the station. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-10-22
WW-WEST | October | - Performed in-house lab and recorded readings on SharePoint - Checked station and recorded readings on SharePoint - Added 7 bags of soda ash - GFL onsite to take a load of sludge - Decanted the sludge thickening tank 1 then transferred sludge into the holding tank - Wessuc onsite to clean out aeration tank 1 - Cleaned DO probe on aeration tank 2 and removed rags - notified PCS of historian heartbeat alarm at 13:48 - pumped down scum tank in manual | Kleinburg Water Resource Recovery Facility | 2025-10-22
WEST | October | #11271953 Generator test Pre-check complete (oil, coolant, leaks) all ok 10:25 Start: 297:33 hours 11:30 Stop: 298:39 Run time : 66 minutes 10:55 30 minute readings: -oil press. 49psi, Coolant temp. 163F, 1804rpm -60Hz, 30/34 amps W/O # 11390698 created for louvre adjust & limit block re-installed (work completed by maintenance) #11272937 PRV #11272962 turbidity #1127298 hypo sys. #11272489 jhs #1123043 strainer #11273112 Depolox maint. 14:11 Verified (mg/l) Post Reservoir Free: Grab 1.89, A 1.83 Treated Free: Grab 1.78, A 1.71 | Ansnorveldt Wells 2, 3 & Reservoir | 2025-10-23
WW-CEAST | October | Got everything set up for Accuworx to finish cleaning the wet wells today,, went to the dump pad and cleared line 1 by back flushing and reset the valve. Took station readings and entered into SharePoint and also checked both compressors oil/belt - OK. Monitored cell 1 wet well levels in- there was no leakage into cell 2 last night. Cleaning finished at 10:30 ,, waited for Accuworx to get the hoses out of the wet wells today and opened the separation gate between the two cells and then opened the inlet gates as well as the middle channel gate,, ran down to the dry well side and primed pumps 4,5 and 6 and ran all 3 pumps at different times to ensure good flow. Put everything back into auto and set up pump duty rotation on all pumps except pump 3 due to flow meter being OOS. Station back to running under normal ops, pump 3 in Duty 7. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-10-24
WEST | October | Onsite for station check Pumping station Checked residuals mg/l @1430 Total grab 1.01 Free grab 0.04 | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2025-10-24
EAST | October | Under direction of OIC (Dan Zhou) On Site for; - TSSA Upgrade Operator Support Surge Tank Grabs @ 10:49 hrs. FCl: 0.99 mg/L @ 10:53 contacted ROC to let them know of temporary power outage at 48PS. Put Well pumps 5/6 in manual off and HLP 1/2 in manual off for duration of main power switch to portable generator power. Turbidity Spike due to surge tank start up. High turbidity due to air in line (can see air bubbles in turbidity meter discharge line and in bubble trap) @10:57 hrs. power off to station @ 11:23 hrs station powered by portable generator @ 11:49 hrs. turbidity spike caused by re-leveling surge tank volume using air compressor, bubble trap lost flow in process. Adjusted flow rate to resolve turbidity spike. @ 13:17 hrs. Power from portable generator to station off, turbidity spike due to flow change from main water supply to surge tanks @ 13:26 main power to facility returned, new generator hooked up @ 14:23 ATS switch turned to test to check new generator @ 14:30 placed High lift pumps 1 in auto on for load test, Well pumps 5/6, gas chlorinators and chlorine booster pumps currently off, and interlocked due to zero on Chlorine weigh scale. @ 12:19 Chlorine weigh scale LOLO alarm. Due to power on/off scale re tared with cylinders on scale, therefore reading zero Kg. @ 14:28 called P.Fobert and J.Palmer for assistance on chlorine weigh scale error. @ 14:45 P.Fobert and J.Palmer on site to reset chlorine weigh scale. *Note dosage records may be affected due to cylinder weight incorrectly represent by chlorine weigh scale. CT is trending and in range. All analyzers are on and functioning. @ 15:00 HLP placed in manual off and returned ATS to auto. @ 13:07 placed HLP?s 1 and 2 as well as Well pumps 5 and 6 back in Auto. Equipment out of Service: None Facility OK | Stouffville Highway 48 Booster Pumping Station | 2025-10-23
WW-CEAST | October | -went to open inlet gate 1 on bar screen 1 in wetwell, top floor of screen room had 20 H2S on gas monitor upon entering room, immediately left and made sure fans were running -all supply fans for screen room/wetwell were in auto, however none were running in auto -will return tomorrow to try and open inlet gate 1 | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-10-15
WW-CEAST | October | Completed station check, Reviewed SCADA and trending, Entered data into SharePoint. Station OK. | Newmarket Green Lane Pumping Station | 2025-10-31
WEST | October | -on site to complete station check -site out of service -site secure -no issues found -completed JHSC Health and Safety Inspection | King City Wells 3 & 4 | 2025-10-31
WW-CEAST | October | -station check of site -reviewed SCADA -reviewed trends -inspected site -station okay | Newmarket Green Lane Pumping Station | 2025-10-27
CENTRAL | October | Onsite to complete assigned work orders and troubleshooting- informed ROC: Received hypo delivery * Performed chemscan outlet/header hot water flush Adjusted inlet total analyzer (13:46) from a 1.68 to 1.35 based on multiple grabs (1.35, 1.33, 1.35)* At approx 14:13- chemscan header total analyzer spike to 5.00 mg/L (non reg). Header total CL17 reading 3.61 mg/L at this time. Header combined reading 3.53 mg/L at this time. Placed chemical systems in man/off, took grab to verify chemscan header analyzer: 1.40 mg/L. At approx 14:28- placed chemical system back into auto, will monitor while onsite * Verified analyzers Verified chemical systems proper dosing Will continue to monitor station via scada Station/equipment- Ok | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2025-10-28
WEST | October | In to complete station check. Enter data into PWQ. Analyzer reagent levels good. Cl2 BP pressure, vacuum good (1450kpa, -720mmhg) Influent analyzer error, analyzer dipped when taking sample flow for grab and then recovered. No other issues. W2 placed back to auto, run in manual to monitor dosing. Adjusted NaSi pump max flows from 100 to 95ml/min | Nobleton Well 2 | 2025-10-27
EAST | October | On site for station check Collected grabs, 13:05, in mg/L Free Cl 0.08 Total Cl 1.52 Inspected station equipment, reviewed station trends Recorded observations in the shared PWQ sheet Station and equipment okay | Richmond Hill Pugsley Pumping Station | 2025-10-27
WW-CEAST | October | Weather today Clear and 20 Celsius -On site to complete work orders W11268376, W11252833, W11254090, W11270662. -Completed station check. -Entered station readings into SharePoint. -Generator Test Run, notified ROC -JHSC Inspection -No Hazardous Waste to remove -Started generator at 09:30, transfer successful -Generator Start Hours: 612.5 hrs -Generator Stop Hours: 613.8 hrs -Run Time: 1.3 hrs -Fuel Start: 1017L -Fuel Stop: 1004L -generator stopped at 10:50, transfer successful, back on utility power -station okay | Mount Albert Pumping Station | 2025-10-06
WEST | October | On site for station check Rechlor Pre inj (mg/L) Fcl Analyzer: 0.03; Grab: 0.06 TCL Analyzer: 1.78; Grab: 1.69 Fa Analyzer: 0.11; Grab: 0.10 Ta Analyzer: 0.51; Grab: 0.44 Mcl Analyzer: 1.65; Grab: 1.68 Post inj Fcl Analyzer: 0.02; Grab: 0.04 TCL Analyzer: 1.76; Grab: 1.74 Fa Analyzer: 0.04; Grab: 0.07 Ta Analyzer: 0.43; Grab: 0.42 Mcl Analyzer: 1.90; Grab: 1.81 Changed out 10% sulphuric in chem scan Changed out left bank of chlorine cylinders with Jake muzzin. While trying to open cylinder 5 pig tail broke at the weld - isolate entire right side of the chlorine system informed TL will replace tomorrow. 29kg on left side should last through the night. | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2025-10-06
EAST | October | On site to complete station check. Time: 13:40 Influent Grab (mg/l) Analyzer (mg/l) Free: 2.04 1.96 Time: 13:45 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.50 1.48 Total: 1.74 Verified analyzers with grabs. At 13:46 cleared alarms on site. No OOS equipment except well 1 due to iron and manganese issues. Checked site and trends. Replaced influent free CL-17 analyzer reagents at 13:52. Cleaned site before leaving. | Mount Albert Wells 1 & 2 | 2025-10-06
EAST | October | On site for station check and equipment verifications Duty is active on arrival - Tower is filling at 10.5 L/s Recorded station readings in PWQ sheets Verified analyzer readings with grab chlorine residuals - no adjustments needed Reviewed trends, equipment OOS: none Station ok | Keswick Deer Park Elevated Tank | 2025-10-06
WW-CEAST | October | -station check of site -reviewed SCADA -inspected site -entered data into SharePoint -pump 2 remains OOS, pump missing -cleaned screen room, rotated bin -station okay | Newmarket Sewage Pumping Station & Equalization Tank | 2025-10-27
CENTRAL | October | On-site for a station and equipment check, no issues found Chemical levels and systems inspected Verified analyzers, all readings and grabs entered into PWQ sheet | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2025-10-27
WW-CEAST | October | Vibration data collection raw sewage pumps 1,3,4 Reset pump 4 discharge valves flooded pump fault (fail to close) valve was in fully closed position. Pump 3 packing adjusted excessive leak Pumps 1,3,4 available in auto | Newmarket Sewage Pumping Station & Equalization Tank | 2025-10-10
ROC | October | Angelica Chepiga signing in | ROC General | 2025-10-10
EAST | October | On site to check station and equipment. Pumps are man/off as normal operation. Chlorine grabs and station readings are entered in PWQ sheet. Exercised each pump for 15 minutes. Reviewed trends, station is under normal operation. Diesel tanks? LIT remain OOS. | Markham Pumping Station | 2025-10-10
WW-CEAST | October | Weather today Clear and 10 Celsius -On site to complete work orders W11349061, W11349658. -Investigate forcemain 1 fault alarm and pumped out chamber. -Chemical dosing line investigation. | Newmarket Sewage Pumping Station & Equalization Tank | 2025-10-09
WW-CEAST | October | Here for scum layer removal,,, opened everything up for Wessux to get into wet well and complete the work. Wet well walls were cleaned off as well as the layer of scum in the wet well. Job well done!!! | Newmarket Bogart Creek Sewage Pumping Station | 2025-10-08
WW-CEAST | October | Station check complete and the readings have been entered into the sharepoint. 45 day test with 50% H2O2 chemical in progress. Chemical pumps 1 and 2 manual off, pump 3 running in auto to dose into 13B only. | SEC Boxgove Corrosion Control Facility | 2025-10-14
WW-WEST | October | Onsite to work on the Air Compressor, tested the PIT as it was replaced and it?s working as expected. The LoLo and HiHi Pressure Switch?s are not functioning correctly, this mainly effects Local operations other than the HiHi Pressure Switch is an interlock to stop the compressors from running | Schomberg Water Resource Recovery Facility | 2025-10-14
EAST | October | On site for station check and weekly micro sampling (W11299400) Tower is on a drain cycle, outlet flow is 10.2 L/s Recorded station readings in PWQ sheets Verified analyzer readings from 09:24 to 09:32 - no adjustments needed Inlet: Grab free: 1.66 mg/L / Analyzer: 1.59 mg/L Grab total: 1.99 mg/L / Analyzer: 1.92 mg/L Outlet: Grab free: 1.68 mg/L / Analyzer: 1.72 mg/L Grab total: 1.96 mg/L / Analyzer: 2.02 mg/L Collected micro sample from outlet @09:33 Reviewed trends, equipment OOS: None Station ok | Keswick Deer Park Elevated Tank | 2025-10-14
WW-CEAST | October | Station check complete. Fan running as intended. No unusual odor detected on site during visit. Condensation draining via drain pipe Heater element - 96.4 Hydro - 260136 kwh | Bayview & Steeles Air Management Facility | 2025-10-27
WW-CEAST | October | On site for chamber inspections of 1050mm Forcemain for Newmarket PS. T18131-VC01 - water pumped out T18131-VC02 T18131-VC03 T18131-VC04 - water not pump out. Pump is not strong enough to push the water up the chamber. T18131-VC05 - water not pump out. Pump is not strong enough to push the water up the chamber. T18131-VC06 T18131-VC07 | Central-East Wastewater Linear System | 2025-10-28
WW-WEST | October | Set up pumps to pump aeration from tank 1 to tank 2. Picked up rags. | Kleinburg Water Resource Recovery Facility | 2025-10-28
WW-WEST | October | Completed station check. No issues found. | Vaughan Black Creek Pumping Station | 2025-10-20
WW-WEST | October | Collected weekly samples | Nobleton Janet St. Sewage Pumping Station | 2025-10-14
WW-WEST | October | Collect weekly samples for YDSS lab submission Complete in house lab analysis Decant sludge thickening tank and transfer thickened sludge to holding tank enter labs and data into ace spreadsheet. Reset RS composite for next Monday ydss sample. | Schomberg Water Resource Recovery Facility | 2025-10-14
CENTRAL | October | On-site for various WO's, - Chlorine leak detector test completed -ChemScan maintenance completed -Sump pit test and inspection completed -Dehumidifier inspected -Eyewash cleaning and fill in main building completed -valve exercised including both cell drains -Cleaned both deplox analyzers, verified after, PRE -AF 0.04 GF:0.04 AT:1.94 GT:1.94 POST-AF 0.02 GF:0.04 AT:1.91 GT: 1.83 -Chlorine system inspection completed | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-10-15
EAST | October | On site for station check Station is off for one week Langstaff trial isolation Verified analyzers, 14:20, in mg/L FCl G 0.06, A 0.00 adjusted analyzer to match average of grabs TCL G 1.46, A 1.55 adjusted analyzer to match average of grabs Completed PWQ sheet Station and equipment okay | Bayview Pumping Station | 2025-10-15
CENTRAL | October | On site with Divya to change chlorine bank B. Isolated cylinders. Upon taking the bank offline, discovered evidence of damage in the third pigtail from the center. Did not hook up new cylinders to bank B. Divya reset halogen system. Created W11356619 to replace pigtail. When the pigtail is replaced, new cylinders will be put online for bank B. Leaving site with bank B isolated. | Queensville Wells No. 3 and 4 | 2025-10-10
EAST | October | On site for station check and weekly micro sampling (W11299386) Tower level - 52% and draining at 45 L/S Recorded station readings in PWQ sheets Verified analyzer readings with grab chlorine residuals @10:49 Grab free: 1.25 mg/L / Analyzer: 1.28 mg/L Grab total: 1.51 mg/L Collected micro sample @10:52 Reviewed trends, equipment OOS: none Station ok | Sutton Elevated Tank | 2025-10-14
WW-WEST | October | Completed station check. No issues found. Entered numbers in spreadsheet. | Vaughan Pine Valley Pumping Station | 2025-10-01
ROC | October | Adam Button signing in 20C Clear | ROC General | 2025-10-01
ROC | October | AUSS- Terry R onsite running generator. | All Wastewater System ROC General | 2025-10-01
ROC | October | Angelica Chepiga signing out | All Wastewater System ROC General | 2025-10-01
WEST | October | On site to complete station check. Well is offline and isolated. Influent Free Chlorine @ 8:36 Grab: 0.35 mg/L Analyzer: 0.39 mg/L Effluent Free Chlorine @ 8:38 Grab: 0.11 mg/L Analyzer: 0.16 mg/L Treated Free Chlorine @ 8:40 Grab: 0.11 mg/L Analyzer: 0.06 mg/L Treated Total Chlorine @ 8:40 Grab: 2.20 mg/L Analyzer: 2.29 mg/L -Data entered into PD sheet | Holland Landing Well No. 1 | 2025-10-01
WEST | October | Onsite for station check and to collect weekly sample W11256486 North cell @1252 Total grab 1.87 Free grab 0.04 Sl1000 Mcl 1.72 F nh3 0.07 T nh3 0.41 No2 0.000 South cell @1300 Total grab 1.88 Free grab 0.05 West cell @1303 Total grab 1.89 Free grab 0.05 Rechlor Pre @1337 TCL analyzer 1.73 grab 1.71 Fcl analyzer 0.03 grab 0.01 Mcl analyzer 1.64 grab 1.63 F nh3 analyzer 0.09 grab 0.09 T nh3 analyzer 0.45 grab 0.41 Post @1347 TCL analyzer 1.88 grab 1.82 Fcl analyzer 0.02 grab 0.03 Mcl analyzer 1.95 grab 1.86 F nh3 analyzer 0.03 grab 0.05 T nh3 analyzer 0.47 grab 0.42 | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2025-10-01
WW-WEST | October | Completed daily lab and station check - entered data into SharePoint. UV bank A had a burnt out bulb - replaced. Short Power blip at 1:54pm. Checked plant - everything has been reset and placed back into duty. Rake drive reset and operating. | Schomberg Water Resource Recovery Facility | 2025-10-27
ROC | October | SEOC4 - Theodore finished at site | ROC General | 2025-10-27
CENTRAL | October | -Troubleshooting high treated free when ammonia pump #2 on duty 1. Release pressure on ammonia line 2 - pressure held and no water back-up - check valve was working 2. Started pump 2 to the set pressure - pressure held - check valve was working 3. Performed drawdown for ammonia pump 2 - 360mL/min - OK 4. Put ammonia pump 2 back to service 5. High treated free came in again 6. Backflushed contract tank until effluent free=0.24mg/L treated free=0.30mg/L 7. Checked ammonia injection point in the chamber - noticed low flow and low pressure at injection point 8. Checked PRV - noticed some tear on the diaphragm 9. We will rebuild the PRV - ammonia pump 2 will be offline tonight 10. Restarted Wells in auto | Aurora Wells 1-4 Water Treatment Plant | 2025-10-28
WW-WEST | October | Decanted sludge thickening tank and transferred remaining sludge to holding tank. Completed daily lab and station check - no new issues added data into SharePoint. Cleaned TSS probe | Schomberg Water Resource Recovery Facility | 2025-10-31
WW-WEST | October | Decanted sludge thickening tank and transferred remaining sludge to holding tank. Completed daily lab and station check - no new issues added data into SharePoint. Due to increasing MLSS numbers in lab, increased wasting from 1400to 2300 to 1400 to 2400 | Schomberg Water Resource Recovery Facility | 2025-10-23
ROC | October | KBSP, James from Wessuc is on site | ROC General | 2025-10-23
ROC | October | SEOC- Jeff from Keyshack is on site GRSSWA-Jeff from property services is on site | ROC General | 2025-10-23
WEST | October | #11295541 Ammonia Performed drawdown test (no changes made) Ammonia pump 2 place back in duty | Holland Landing Well No. 2 | 2025-10-23
WW-WEST | October | Completed station check - found filter 3 sand wash plugged, lanced and cleared the sand washer, it seems to be running normally now, will continue to monitor. Added data into SharePoint. Tested and confirmed sludge holding tank overflow alarm as well as exercised sludge holding tank overflow valve. Tested and confirmed sump pumps in process building and blower buildings, both sump puts operational and high level floats working, confirmed with ROC. Inspected scum pumps 1 and 2, greased nipples, ran both manually to confirm operation. Placed both pumps back in auto and in duty. | Schomberg Water Resource Recovery Facility | 2025-10-14
WEST | October | -on site to respond to low UVT alarm -reviewed trends, UVT dropped to 70% from 13:32 to 13:35. UVT drop was caused by filter turbidity spikes after filter #1 returned to service following a backwash -no low UV dose alarms occurred -checked UVT analyzer, no issues | Schomberg Water Treatment Plant & Wells 2-4 | 2025-10-14
WW-WEST | October | Onsite for station check - no new issues entered data into SharePoint. Ran generator for monthly test from 1:07pm to 2:17pm. Generator ran normally and transferred with no issues - entered data. Completed JHSC inspection. Checked building for Hazardous waste. Tested building high/low temperature alarms. | Schomberg Dr. Kay Pumping Station | 2025-10-01
ROC | October | NBET27 - Jeff (Keyshack) on site 14:26-14:38 | ROC General | 2025-10-24
ROC | October | JDSS - Drew from Ferguson electric off site. | ROC General | 2025-10-24
CENTRAL | October | Onsite for station check: Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok | Aurora Well 5 | 2025-10-24
WEST | October | On site to complete station check Verified analyzers @0900 Pre-injection Free chlorine Grab: 0.05mg/L Analyzer: 0.05mg/L Total chlorine Grab: 1.00mg/L Analyzer: 1.09mg/L SL1000 TCL 0.77mg/L Mono 0.28mg/L FA 0.31mg/L TA 0.37mg/L Post-Injection Free chlorine Grab: 0.06mg/L Analyzer: 0.08mg/L Total chlorine Grab: 3.02mg/L Analyzer 2.98mg/L SL1000 TCL 3.01mg/L Mono 2.46mg/L FA 0.10mg/L TA 0.59mg/L Tank TCL 0.86mg/L Mono 0.37mg/L Nitrite 0.005mg/L FA 0.32mg/L TA 0.39mg/L Reagents all ok Adjusted inlet free ammonia from 0.25-0.27mg/L as pre injection ammonia keeps fluctuating. Will continue to monitor on station checks. No issues on site | Holland Landing West Elevated Tank | 2025-10-24
WW-WEST | October | Reopened aer tank 1 inlet to put it back in service Reopened aer outlet valves and Ty closed the outlet channel interconnect Reopened RAS flow to aer tank 1 Placed tank 1 do probe back into tank Resumed alum flow to tank 1 | Nobleton Water Resource Recovery Facility | 2025-10-24
CENTRAL | October | Onsite to complete station check and sampling. 08:48 Reservoir level at 68% and draining at 50 l/s. 08:53. Verified analyzer (mg/l). Free chlorine: 1.39/1.42/142 Analyzer: 1.54. Adjusted analyzer to match grand. Analyzer menu buttons are not working well. Created work order for instrumentation to repair. Total Chlorine grab: 1.66. Analyzer: 1.71. No other new issues found. | Keswick West Park Reservoir | 2025-10-24
ROC | October | SEOC OCF - Ben Han from property services was on site to inspect a fan. Ben is finished his work and is off site. | ROC General | 2025-10-20
ROC | October | Adeela Khan signing out | ROC General | 2025-10-21
CENTRAL | October | Topped up silicate tank 317 L to 387 L. | Newmarket Well No. 15 | 2025-10-21
ROC | October | Pest Control visiting following sites; EGSSSC, QVSSSC, HLSSBS, HLPSYS, HLETYS, HLW2 | ROC General | 2025-10-28
ROC | October | QVETQS, Jeff from Key shack is on site | ROC General | 2025-10-21
EAST | October | On site to complete following work orders: W11293322 JHSC Inspection. W11300946 Chlorine Analyzer Maintenance. W11301756 Drain Valve Exercise. Taking grabs to verify analyzer after cleaning. Time: 14:20 Grab (mg/l) Analyzer (mg/l) Free: 1.27 1.28 No issues with grabs after analyzer cleaning. No issues with work orders. Any changes in trends are due to work orders being completed. | Musselman's Lake Elevated Tank | 2025-10-21
ROC | October | STRS48 - ETO engineering onsite for inspection for wells 5 & 6 | ROC General | 2025-10-29
ROC | October | Christian Van Beek signing out. | ROC General | 2025-10-23
ROC | October | LSSS - Ben from Property Services is finished on site | ROC General | 2025-10-20
EAST | October | On site for station check. Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 1.94mg/l FCL Analyzer:2.02mg/l Effluent Free Cl2 grab residual: 1.69mg/l FCL Analyzer: 1.78mg/l Effluent Total Cl2 grab residual: 1.95mg/l Adjusted SIlicate P2 MAX Flow from 170ml/min to 180ml/min based on cal column check.. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Site currently undergoing Construction upgrades by Torbear. Equipment out of service: None. | Ballantrae Well 1 & 2 | 2025-10-20
ROC | October | MAPS, Anil Magnum Fire is on site 11:46, Anil is finished on site | ROC General | 2025-10-24
EAST | October | On site to complete station check. Time: 08:45 Header Grab (mg/l) Analyzer (mg/l) Free: 1.50 1.45 Total: 1.96 2.03 Time: 08:47 Inlet Grab (mg/l) Analyzer (mg/l) Free: 1.75 1.79 Total: 2.11 2.11 Time: 08:50 Outlet Grab (mg/l) Analyzer (mg/l) Free: 1.56 1.46 Total: 1.92 1.98 Verified analyzers with grabs all ok. Checked station and trends. No outstanding alarms on site. No OOS equipment. | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2025-10-24
ROC | October | AUPSWS- Reza from IAM is on site | ROC General | 2025-10-08
ROC | October | RHAMF- Jeff from Keyshack is on site | ROC General | 2025-10-08
ROC | October | MAPS- Drew from Ferguson offsite. | ROC General | 2025-10-08
CENTRAL | October | On site to complete station check and collect weekly bacti sample (W11278525). Verified analyzers: Influent Free Chlorine @ 11:17 Grab: 2.72 mg/L Analyzer: 2.61 mg/L Effluent Free Chlorine @ 11:19 Grab: 2.56 mg/L Analyzer: 2.60 mg/L Treated Free Chlorine @ 11:07 Grab: 0.12 mg/L Analyzer: 0.16 mg/L Treated Total Chlorine @ 11:07 Grab: 3.10 mg/L Analyzer: 3.15 mg/L -Entered data into PD sheet -Checked trends -Took well 3 raw at 11:17, treated sample at 11:25 | Queensville Wells No. 3 and 4 | 2025-10-08
ROC | October | MTSP- Scott from IAM onsite for tour | ROC General | 2025-10-02
ROC | October | VNETAG - Jeff from keyshack finished on site and headed to VNETFD SUETDR - David Ip from ETO engineering on site. | ROC General | 2025-10-02
ROC | October | JDSS- Jeff from Keyshack is on site | ROC General | 2025-10-06
CENTRAL | October | Station and equipment checked, no issues found Received diesel fuel for generator Entered readings in to PWQ Sheet | Aurora (East) Wellington Pumping Station | 2025-10-06
ROC | October | AUW14- William from Chubb onsite. | ROC General | 2025-10-07
CENTRAL | October | On-site to complete the following work orders: -CL-17sc Analyzer maintenance, x 4 -CL17 Analyzer maintenance, x 4 -JHSC Inspection -Chemscan maintenance cleaned screens -Chemical storage tanks inspected -Comprehensive housekeeping -Visual injection point inspection -CL2 system inspection Monthly generator testing completed: -Pre-start inspection, ok -Hours start 232.04 Hours end 233.16 -Fuel start 2443.08 Fuel end 2421.02 -Run under load of pump 1 running for duration -RPM 1800 -Oil pressure 80 -Coolant temp 180 -Frequency 60.0 -Volts 600 -Amps 68 -Battery 27.7 Returned back to AUTO | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2025-10-07
ROC | October | YDOC- Phil from AB is on site to work on diesel tank | ROC General | 2025-10-07
ROC | October | JDSS- Garrick from Ferguson Electric | ROC General | 2025-10-07
ROC | October | KCETFS, Chris from PPT is finished on site | ROC General | 2025-10-06
ROC | October | KSTP, Christian from Ferguson Electric is on site | ROC General | 2025-10-14
ROC | October | KSSP, Ben from Property Services is on site, working on the HVAC system | ROC General | 2025-10-06
ROC | October | NMETYS - Kevin from Yorknet visiting site, will attend NMW15 next. 15:55 NMW15- Kevin off site. | ROC General | 2025-10-15
ROC | October | Christian Van Beek signing in. | All Wastewater System ROC General | 2025-10-01
CENTRAL | October | -Performed station check - logged station readings into PWQ sheet Grab: free=0.05mg/L total=2.54mg/L@8:35 Analyzer: free=0.04mg/L total=2.53mg/L -Checked Depolox reagents - OK -Collected weekly BacT sample YD #11317110 | Aurora (East) First Commerce Elevated Tank | 2025-10-22
WEST | October | Vibration testing | Jefferson Pumping Station & Reservoir | 2025-10-22
EAST | October | On site to complete station check. W11317191 Weekly Bac-t Sample. W11247404 Quarterly Sample. Time: 10:30 Inlet Grab (mg/l) Analyzer (mg/l) Free: 1.88 1.83 Total: 2.20 2.27 Time: 10:32 Outlet Grab (mg/l) Analyzer (mg/l) Free: 1.35 1.44 Total: 1.78 1.84 Verified analyzers with grabs all ok. Checked site and trends. | Keswick Deer Park Elevated Tank | 2025-10-22
CENTRAL | October | -Performed station check - logged station readings into PWQ sheet Grab: free=0.09mg/L total=2.84mg/L@10:20 Analyzer: free=0.04mg/L total=2.90mg/L -Checked Depolox reagents - OK -Collected weekly BacT sample YD #11317110 | Aurora (North) Orchard Heights Elevated Tank | 2025-10-22
WEST | October | On site to Complete Station Check. Residuals PD8 Total Grab: 2.12mg/L, Analyzer: 2.14mg/L PD8 Free Grab: 0.04mg/L, Analyzer: 0.02mg/L PD7 Total Grab: 2.22mg/L, Analyzer: 2.23mg/L PD7 Free Grab: 0.05mg/L, Analyzer: 0.06mg/L Freed sump discharge line to empty pd7 pit no issues on site | Maple Pumping Station | 2025-10-21
EAST | October | On site for station check. Collected weekly micro samples (W11316252) and Quarterly Samples (W11247376). Collected in house operational samples. Verification of HACH CL17 Chlorine Analyzer: 13:45hrs: Free CL2 grab residual: 1.06mg/l FCL Analyzer:1.06mg/l Total Cl2 grab residual: 1.23mg/l Checked station readings and verified Cl2 analyzer. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Musselman's Lake Elevated Tank | 2025-10-22
CENTRAL | October | -Performed station check - logged station readings into PWQ sheet Grab: treated total=2.86mg/L free=0.06mg/L@10:40 Analyzer: treated total=2.84mg/L free=0.05mg/L -Checked Depolox reagents - OK -Collected weekly BacT sample YD #W11331191 & in-house water quality samples | Aurora (North) Orchard Heights Elevated Tank | 2025-10-29
CENTRAL | October | On-site to collect scrubber media for testing. Unable to complete ammonia pump draw down due to high level in day tank 1. Will perform at a later date. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-10-21
EAST | October | On site for chlorine cylinder change with Danielle Zhou Replaced chlorine cylinder bank 2. Purged prior to change and informer RO Christian Van Beek of this work Bank 2 placed in standby. Station and equipment okay | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-10-20
CENTRAL | October | Station and equipment checked, no issues found. Chemical levels and systems inspected, ok Topped up ammonia day tank 1 Weekly bacti, operational and Q4?s samples taken. Verified analyzers and entered all readings and grabs into PWQ sheet | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-10-14
WEST | October | -On site to complete station check and collect weekly micro. samples -sample work order # W11298484 -well running in manual -cl2 booster pump # 1 running at 214 psi -chlorinator # 1 41% open dosing 22.5 ppd, vac = - 260 mbar, DF = 81.0% -silicate pump #1 running at 46%, 55.6 ml/min, 100 psi -checked equipment -reviewed trends -replaced influent CL17 reagents -silicate dosage below target, disabled silicate pump auto duty rotate to troubleshoot -verified chlorine analyzers: 11:05 - Influent Analyzer = 1.90 mg/L 11:05 - Influent grab: Free chlorine = 1.85 mg/L 11:06 - Effluent Analyzer = 1.64 mg/L 11:06 - Effluent grab: Free chlorine = 1.64 mg/L Total chlorine = 2.01 mg/L 11:10 - collected weekly treated water micro. sample 11:10 - collected weekly raw water micro. sample -recorded readings in PWQ sheet -no other issues found | Nobleton Well 2 | 2025-10-14
CENTRAL | October | Chlorine Cylinder change with RB (B side) | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-10-02
CENTRAL | October | -Performed station check - logged station readings into PWQ sheet Grab: treated total=2.94mg/L free=0.09mg/L@9:50 Analyzer: treated total=2.82mg/L free=0.03mg/L -Calibrated total analyzer based on 3 grab tests -Checked Depolox reagents - OK -Collected weekly BacT sample YD #W11331191 & in-house water quality samples | Aurora Orchard Heights Pumping Station & Reservoir | 2025-10-29
CENTRAL | October | -Performed station check - logged station readings into PWQ sheet Grab: free=0.08mg/L total=2.86mg/L@9:40 Analyzer: free=0.01mg/L total=2.87mg/L -Checked Depolox reagents - OK -Collected weekly BacT sample YD #11317110 | Aurora Orchard Heights Pumping Station & Reservoir | 2025-10-22
CENTRAL | October | -Topped up W3 & 4's drip oil reservoir -Performed station check - logged station readings into PWQ sheet -Changed treated total and free reagents -Received 16 chlorine cylinders | Aurora Wells 1-4 Water Treatment Plant | 2025-10-03
EAST | October | On site for station check and equipment verifications Duty is not active - BLETNL level - 80% Recorded station readings in PWQ sheets Verified analyzer readings with grab chlorine residuals Visual inspection of chemical systems - all ok Reviewed trends, equipment OOS: none Station ok | Ballantrae Well 3 | 2025-10-03
EAST | October | On site for station check and diesel generator test run. Working with Baseline contractor for generator inspection. Conducted generator pre inspection, including DEF fluid level - okay Engine hours Start 111.7 Stop 113.1 Total run time 1.4 hours Generator test run Start time 8:18 End time 9:50 (approx) Fuel levels Start 3192/ 3253 L Stop 3028/ 3095 L Pump 4 discharge valve failed to close - locally actuated 8% and reset alarm Pump 2 manual on at 8:26, pump 3 manual on at 8:30 Verified analyzers, 8:45, mg/L Free Cl G 0.01 A 0.02 Total Cl G 1.56 A 1.63 Generator run statistics, 8:57 4160 V voltage 166 A current 60 Hz frequency 1.09 MW power 85C coolant temp 460 kPa oil pressure 1800 RPM engine speed 27.6 V battery voltage 580 to 590C exhaust temp Checked pumps, valves, headers for condition and leakage. Inspected sump. Reviewed station trends. Inspected fuel fire suppression system. Inspected SARV panels Pump hours (at the VFD/ MCC) Pump 1 6597.19 Pump 2 6716.93 Pump 3 7802.49 Pump 4 7387.05 Pump 2 (running) - drawing 80 A, 527 kW Pump 3 (running) - drawing 81 A, 524 kW Suction pressure 35 kPa Discharge pressure 634 kPa Flow 1292 L/s Pump 2 discharge pressure 628 kPa Pump 3 discharge pressure 629 kPa Contractor repairing condensation leak in the exhaust manifold post SCR scrubber Identified SCR system fault - will create a work order for electrical maintenance to troubleshoot - W11335389 created for CMS Identified a deficiency in the coolant exhaust louver system - the left temperature sensor is below the air intake and so fails to achieve the desired temperature to close the coolant exhaust louvers - sent an email to the team to explain the issue. 9:32 shutting down the pumps and returning to auto Observed transfer back to utility did not have a 60 second timer, transfer was instant - inquired with PCS oncall Artour L to investigate where there is logic for a timer - Artour increased the timer to transfer back to utility from 10 mS to 60 seconds at my request - satisfied this has increased safety during load tests - will watch for the change on the next test run. Station back in service and on utility power - all okay | Bayview Pumping Station | 2025-10-03
WEST | October | On site for station check and jhsc inspection No power to site doors locked site secure | King City Wells 3 & 4 | 2025-10-03
EAST | October | On site to check station and equipment. Pump duty is not active upon arrival. P1 and P3 are in duty 1. Chlorine grabs and station readings are entered in PWQ sheet. Reviewed trends, station is under normal operation. | Bayview Pumping Station | 2025-10-10
WEST | October | On site to complete station check. Free chlorine Grab: 0.02mg/L Analyzer: 0.00mg/L Total chlorine Grab: 1.45mg/L Analyzer 1.51mg/L Reagents all ok | East Vaughan Teston Pumping Station | 2025-10-21
WEST | October | Onsite for station check Pd8 duty active Checks residuals mg/l Pd7 @1313 Total analyzer 1.81 grab 1.80 Free analyzer 0.02 grab 0.03 | East Vaughan Teston Pumping Station | 2025-10-14
WEST | October | -on site to complete station check -site offline and isolated from system -site secure -no issues | Holland Landing East Elevated Tank | 2025-10-06
CENTRAL | October | On-site for station check and Cl2 cylinder change. Changed Cl2 bank B with Alex Bell (OIT/under direction of OIC). Switched to run NaSi P1 to observe operation, appears to operate normally, place NaSi pumps in all stop duty rotation. Entered station readings into shared PD excel file. Replaced Effluent Free Cl CL17 analyzer reagents. Grab/analyzer results as follows (mg/L): Influent Free Cl (12:23): G: 2.66 A: 2.64 Effluent Free Cl (12:25): G: 2.60 A: 2.59 Treated Free Cl (12:26): G: 0.11 A: 0.15 Treated Total Cl (12:32): G: 2.96 A: 3.06 Checked station and equipment, Well pump house exhaust fan running but thermostat needs adjusting or replacing, WO already issued. No new issues found while on-site. | Newmarket Well No. 15 | 2025-10-06
WEST | October | On site to put well back online - distribution valve still closed Ran well to waste to ensure disinfection with chlorine strips. Adjusted well speed from 24L/s to 15L/s using the pilot since there?s no back pressure as we?re running to waste. Dechlor placed in chamber. Ensured zero total chlorine residual prior to sampling. Sampling wo W11405009 and W11405010. Please disregard all alarms as water is going to waste. | Holland Landing Well No. 1 | 2025-10-30
WEST | October | Station Check (no issues found) Input data to PWQ 12:50 Verified CL17s(mg/L) Influent: Free Grab 2.03, A 2.03 Effluent: Free Grab 1.61, Total: Grab 2.01 13:00 #11247726, #11330407 weekly and Q4 (raw/treated) samples Topped up Hypo day tanks | Nobleton Wells 3 & 7 | 2025-10-29
CENTRAL | October | Informed ROC. Performed annual calibration and put instruments in Cal mode while doing the tasks. Devices done were FITs, PIT, LIT, LCV and AITs. All alarms were cleared after the job. No other issues encountered. | Queensville Elevated Tank | 2025-10-30
EAST | October | Onsite for Effluent Free AIT A/D error Informed ROC Replaced colorimeter, took grabs and adjusted Gain. As left readings: A = 0.78mg/L G = 0.78mg/L Operations on site. Informed them of repair and grab results Informed ROC No other issues Left site | Stouffville Well 3 | 2025-10-29
WEST | October | Onsite for station check Well offline for rehab Checked residuals mg/l Influent free @0920 Analyzer 0.02 grab 0.07 Effluent free @0922 Analyzer 0.07 grab 0.03 Treated @0927 Total analyzer 1.85 grab 1.75 Free analyzer 0.03 grab 0.07 Changed reagents in influent free analyzer for | Holland Landing Well No. 1 | 2025-10-29
WEST | October | Onsite for station check and to collect weekly micro and Q4 sample Duty active to try and get grabs with fill cycle but inlet flow keep fluctuating Pre injection @1155 TCL analyzer 0.88 grab 0.90 Fcl analyzer 0.04 grab 0.06 Sl1000 Mcl grab 0.32 F nh3 grab 0.022 T nh3 grab 0.29 Post injection @1203 TCL analyzer 3.13 grab 3.06 Fcl analyzer 0.08 grab 0.10 Sl1000 Mcl grab 2.51 F nh3 grab 0.13 T nh3 grab 0.63 Tank @1212 TCL grab 0.90 Fcl grab 0.02 Sl1000 Mcl grab 0.36 F nh3 grab 0.38 T nh3 grab 0.45 No2 grab 0.005 Nitrate grab 0.034 Deactivated duty Collect treated samples @1252 Total grab 1.44 Free grab 0.03 | Holland Landing West Elevated Tank | 2025-10-29
WEST | October | On site for station check and to collect bacti sample wo#11278701 Residuals West Cell cell:@ 0830 Free: 0.05mg/L Total 1.75mg/L SL1000 readings Total Cl: 1.74mg/L Total NH3: 0.39mg/L Free NH3: 0.06mg/L NH2Cl: 1.65mg/L NO2: 0.000mg/L No issues on site | Jefferson Pumping Station & Reservoir | 2025-10-08
EAST | October | Adjusted P1 discharge valve actuator open limit switch . Tested. OK. | Markham Pumping Station | 2025-10-08
WEST | October | Attending site to check Free chlorine analyzer (W11387749). Analyzer has stabilized now to a reading of 0.05mg/L. There is no room to make any further downward adjustments but based on the reading, no further adjustment is required. Notified David Tarascio and he is satisfied with the current reading. | King City Dufferin Elevated Tank | 2025-10-30
WEST | October | -On-site to complete station check and collect samples -system duty not active, tower = 69 % -checked equipment -reviewed trends -CL17 reagents ok -verified chlorine analyzers: 09:44 - Analyzer readings: Free Chlorine = 0.15 mg/L Total Chlorine = 2.15 mg/L 09:44 - Grabs: Free Chlorine = 0.05/0.09/0.08 mg/L Total Chlorine = 2.08 mg/L MCL = 1.96 mg/L TNH3 = 0.49 mg/L FNH3 = 0.10 mg/L NO2 = 0.000 mg/L temp = 16.8 C 09:52 - collected weekly regulatory micro. sample - W/O # W11316440 -attempted to adjust free chlorine analyzer to 0.07 mg/L based on average of 3 grabs, however analyzer will not accept adjustment below 0.15 mg/L. Will create work order for instrumentation to calibrate -collected operational ATP sample -recorded readings in PWQ sheet -no other issues found | King City Dufferin Elevated Tank | 2025-10-22
WEST | October | -on site to complete station check -pump #4 running in schedule mode -checked equipment -reviewed trends -analyzer reagents ok -recorded readings in PWQ sheet -verified chlorine analyzers: 13:14 - Analyzer readings: Free Chlorine = 0.04 mg/L Total Chlorine = 2.04 mg/L 13:14 - Grabs: Free Chlorine = 0.00 mg/L Total Chlorine = 2.08 mg/L -no issues found | Kleinburg Whisper Lane Booster Pumping Station | 2025-10-31
CENTRAL | October | Onsite to complete station check. 08:00 Reservoir level at 75% and draining at 50 l/s. 08:34 Verified analyzer (mg/l). Free chlorine: 1.50 Analyzer: 1.46. Total Chlorine grab: 1.79. Analyzer: 1.81. No issues found. | Keswick West Park Reservoir | 2025-10-31
WEST | October | On site to complete station check. -No pumps running -Verified analyzers: Free Chlorine @ 13:47 Grab: 0.06 mg/L Analyzer: 0.04 mg/L Total Chlorine @ 13:47 Grab: 2.09 mg/L Analyzer: 2.07 mg/L -Checked trends -Entered data into PD sheet | Kleinburg Whisper Lane Booster Pumping Station | 2025-10-14
EAST | October | On site for monthly maintenance - informed ROC of work to be completed - Hach chlorine analyzer maintenance (Influent and effluent) Started @12:20, completed @12:50. Verified analyzer readings with grab residuals after maintenance Influent: @13:07 Grab free: 1.64 mg/L / Analyzer: 1.62 mg/L Effluent: @13:10 Grab free: 1.62 mg/L / Analyzer: 1.60 mg/L - Manual valves exercises - Check valve inspection - Exhaust and supply fans inspections Equipment back to auto, station ok | Mount Albert Well 3 | 2025-10-15
EAST | October | On site for station check and weekly micro sampling (W11298554) Tower level - 74% and draining at 10 L/s Recorded station readings in PWQ sheets Verified analyzer readings with grab chlorine residuals @14:12 - no adjustments needed Grab free: 1.31 mg/L / Analyzer: 1.25 mg/L Grab total: 1.48 mg/L Collected micro sample @14:15 from outlet Reviewed trends, equipment OOS: None Station ok | Mount Albert North Elevated Tank | 2025-10-14
EAST | October | On site for monthly maintenance: 10:45hrs: Cleaned Influent and Effluent HACH Cl17 Analyzers. Collected Cl2 grab residuals to verify Analyzers after cleaning: Influent Cl2 grab: 1.48mg/l Analyzer: 1.48mg/l Effluent Cl2 grab: 1.45mg/l Analyzer: 1.51mg/l Turbidimeter maintenance completed. Conducted Generator Test Run Diesel Generator Run Monthly Test @11:15 hrs Start Runtime: 11:15hrs, 999.4hrs, Fuel Start: 88.6cm/882L Stop Runtime: 12:25hrs, 1000.6hrs, Fuel Stop: 87.0cm/865L Generator Performance Data recorded below: Battery Cell Levels: OK Battery Terminals/Cables: Ok Oil and Coolant: Ok Amps: 75 Volts: 600 Hertz: 60 RPM: 1600 Oil Pressure: 55psi Oil Temp: 165F Water temp: 160F No issues during generator run test. Ran Well 2 during run test. JHSC Inspection. Conducted silicate and hypo injection point cleaning and pump inspection. No issues. | Ballantrae Well 1 & 2 | 2025-10-15
WEST | October | Onsite for station check and to collect weekly micro sample @1039 North cell Total grab 1.77 Free grab 0.07 Sl1000 Mcl 1.69 No2 0.001 F nh3 0.13 T nh3 0.46 @1040 Peel total analyzer 1.77 grab 1.83 @1042 Metro feed Total analyzer 1.76 grab 1.81 Free analyzer 0.04 grab 0.08 | Maple South Reservoir | 2025-10-14
CENTRAL | October | Onsite for station check/collect sample- WO# W11317124: Sample results (07:40): Free- 0.06, Total- 2.22 * Performed ?calibration zero? on free analyzer- adjusted free analyzer from 0.00 to 0.06 based on grabs (0.06, 0.06, 0.07) * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Newmarket (East) Harry Walker Elevated Tank | 2025-10-22
CENTRAL | October | Onsite for station check: Received hypo delivery * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Chemscan reagents- Ok Station/equipment- Ok | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2025-10-20
CENTRAL | October | On site to verify treated free Cl, noticed it was rising after doing troubleshooting of depolox in morning. Tower draining when arrived, Did zero cal on treated free Cl and adjusted analyzer based on avg grabs Treated free Cl @1:45pm G: 0.02, 0.02, 0.02mg/L A: 0.14mg/L - adjusted analyzer based on avg grabs to 0.02mg/L Treated total Cl @1:53pm G: 2.54mg/L A: 2.57mg/L | Newmarket (Southeast) Ivsbridge Elevated Tank | 2025-10-07
CENTRAL | October | Install pressure gauges on 2 3 and 4 | Newmarket Kirby Pumping Station | 2025-10-07
CENTRAL | October | Station and equipment check Receive 12 Full chlorine cylinders return 12 empty Change treated free reagent CL17 Took grabs @ 9:50 am Treated Total: 2.94 mg/l Treated Free: 0.12 mg/l *standardized treated total analyzer to match grabs All other readings on PD sheets Chemicals/reagents ok Ops normal | Newmarket Well 1 & 2 | 2025-10-17
CENTRAL | October | Topped up NaSi day tank 259 to 387L. | Newmarket Well No. 15 | 2025-10-27
CENTRAL | October | Topped up NaSi day tank from 105L to 360L. | Newmarket Well No. 15 | 2025-10-01
CENTRAL | October | Station and equipment checked, no issues found Chemical levels and systems inspected, ok Weekly Bacti samples taken Verified analyzers, all grabs and readings emtered in to PWQ sheet influent F @ 1113 g:2.68 a:2.63 Effluent F @1115 g:2.52 a:2.59 Treated F @ 1117 g:0.09 a:0.14 Treated T @ 1121 g:3.18 a:3.05 temp 11.2 | Newmarket Well No. 15 | 2025-10-01
CENTRAL | October | Station and equipment check Take operational samples and grabs @ 11:08 am Treated Total: 2.79 mg/l Treated Free: 0.12 mg/l Changed reagent Influent Free CL17 analyzer Chemicals/reagents ok Joe D deactivated Duty to complete work at Glenway OPs normal | Newmarket Wells 13-16 | 2025-10-20
EAST | October | On site to change cylinder Start: 0.0/63.8kg Stop: 68/63.8kg No issues | Georgina Water Treatment Plant | 2025-10-20
WEST | October | Station Check (no issues found) Input data to PWQ 9:10 Verified Depolox (mg/l) Free: Grab 1.17, A 1.17 Total: Grab 1.50, A 1.50 9:25 #11330407, #11247110 weekly and quarterly samples | Nobleton North Elevated Tank | 2025-10-29
WEST | October | Attending site to check chlorine analyzer after maintenance was performed earlier today. Free chlorine was found to be climbing due to addition of new cleaning grit earlier today. Verified and adjusted both Free and Total chlorine residual readings using portable DPD tester. Will monitor SCADA tomorrow to check for upward drift on the Free reading. | Nobleton North Elevated Tank | 2025-10-09
WEST | October | -On site to complete station check and collect weekly micro. samples -sample work order # W11298484 -well #5 running in manual -well #6 offline and isolated from distribution system -cl2 booster pump # 2 running at 180 psi -chlorinator # 2 85% open dosing 43.5 ppd, vac = - 80 mbar, DF = 183% -silicate pump #1 running at 64%, 12.7 rpm, 110 psi -checked equipment -reviewed trends -CL17 reagents ok -verified chlorine analyzers: 11:48 - Influent Analyzer = 2.66 mg/L 11:48 - Influent grab: Free chlorine = 2.88/2.94/2.94 mg/L 11:57 - adjusted influent analyzer to 2.92 mg/L based on average of 3 grabs 11:59 - Effluent Analyzer = 2.11 mg/L 11:59 - Effluent grab: Free chlorine = 2.28/2.32/2.30 mg/L Total chlorine = 2.80 mg/L 12:04 - adjusted effluent analyzer to 2.30 mg/L based on average of 3 grabs 12:07 - collected weekly treated water micro. sample 12:07 - collected weekly well #5 raw water micro. sample -recorded readings in PWQ sheet -no other issues found | Nobleton Wells 5 & 6 | 2025-10-14
CENTRAL | October | On site to complete Q4 NDMA resample (W11365164). Also topped up inlet analyzer acetate reagent and outlet analyzer potassium iodide reagent. | Queensville Elevated Tank | 2025-10-28
CENTRAL | October | On site to perform station check. Chris and his colleague on site to fix chlorine BP1 pressure gauge and valving. Currently running only W1 in Duty 1. Donald M and I changed chlorine cylinders. After looking at the valving and gauge it?s looks like the ejector needs to be replaced for CLBP1 line. Maintenance guys working on ejector repairing currently well site manual off and CLBP1/2 in local and lines purged chlorine cylinders closed for them to work. Once done will check the system. Took all dechlor measures before opening waste valve after purging lines. Informed ROC - Wells duty active on arrival - Entered readings into Process data sheet - Reagents all good - Trends all good - Equipment all okay - Dosage all good topped up silicate day tanks & NH3 TK2 - No new issues found Influent free Cl @ 10:01am G: 2.98mg/L A: 2.95mg/L Effluent free Cl @ 10:02am G: 2.68mg/L A: 2.75mg/L Treated free Cl @ 10:07am G: 0.24mg/L A: 0.21mg/L Treated total Cl @ 10:07am G: 3.10mg/L A: 3.15mg/L | Queensville Wells No. 1 and 2 | 2025-10-03
WEST | October | -on site to investigate generator breaker tripping issue. At 1210 had ROC place whisper lane pumps into manual and ran generator from ats for 10 minutes. Transferred it back to site power and confirmed breaker did not trip worked on the line filters for well 3 and did some investigation on the generator. When I completed 1420 had ROC place whisper lane pumps to auto. placed generator back to auto cleared faults and confirmed alarms had cleared on scada. Under direction of oic. | Kleinburg Wells 3 and 4 | 2025-10-03
CENTRAL | October | On-site responding to influent free lolo lockout. Issue with chlorine booster train 2. Backflushed well until influent high enough to start well again, dechlor in waste pit Leaving Chlorine booster train 2 local OOS | Queensville Wells No. 3 and 4 | 2025-10-30
WEST | October | Onsite for station check and to complete work orders Checked residuals mg/l @1130 Total grab 1.41 Free grab 0.05 Completed jhsc , no issues Exercise valves in reservoir and pumping station Ran pumps 1&2 Tested sumps | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2025-10-06
CENTRAL | October | On-site for a station and equipment check, no issues found. Bacti and operational samples taken on outlet flow Verified analyzers, all grabs and readings entered into PWQ sheet. | Richmond Hill Coon's Elevated Tank | 2025-10-29
CENTRAL | October | Station and equipment checked, no issues found Weekly bacti sample, Q4?s and operational samples taken. Verified analyzers and entered all readings and grabs into PWQ sheet. Inspection of cathodic protection system, as ROC email on the 13/10/2025 showing fault, system is green light status, ok | Richmond Hill Coon's Elevated Tank | 2025-10-14
WW-WEST | October | Collected the weekly samples | Nobleton Water Resource Recovery Facility | 2025-10-14
WEST | October | On site for station check Received (19) and returned (15) chlorine cylinders Rechlor Pre inj (mg/L) Fcl Analyzer: 0.01; Grab: 0.01 TCL Analyzer: 1.78; Grab: 1.72 Fa Analyzer: 0.10; Grab: 0.12 Ta Analyzer: 0.51; Grab: 0.44 Mcl Analyzer: 1.70; Grab: 1.72 Post inj Fcl Analyzer: 0.02; Grab: 0.01 TCL Analyzer: 1.91; Grab: 1.90 Fa Analyzer: 0.05; Grab: 0.08 Ta Analyzer: 0.47; Grab: 0.45 Mcl Analyzer: 2.04; Grab: 1.89 Topped up ammonia tank 1 from 15-76cm (4bags) Replaced grey reagent in chemscan | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2025-10-21
EAST | October | Georgina Plant Station checks Reviewed the following on scada - To review trends and record trains MITs, all passed - To review trends and record filter daily performance, no issues observed - To review permeate UV trends, no issues - Wet well mussel plate inspection completed Operations and Adjustments: Notified ROC before completing the following: 1000hrs: Did maintenance on both keswick and Sutton headers chlorine analyzers, zeroed analyzers after maintenance 1100hrs: Did residual grabs after cleaning and adjusted FCL readings on both headers and adjusted analyzer readings to 1.78 mg/l based on 2 grabs each Cleaned and calibrated both Keswick and Sutton turbidity analyzers 1230hrs: Permeate header analyzers maintenance~ Turbidity and chlorine analyzer maintenance Calibrated permeate header turbidity analyzer. Zeroed permeate header chlorine analyzer and verified, no adjustment required. Cleaned Fluoride probes on both headers. Placed GAC2 OOS for GAC manual backwash 1422 hrs:Completed backwash, allow GAC2 to rest for about 15 mins 1439 hrs: started filter waste (FTW). 1500 hrs; GAC2 FTW turbidity ~ 0.136 NTU Closed FTW valve 1503 hrs: Returned GAC2 to service, Low Lift Station: Chlorine analyzers: Both existing and newly installed chlorine analyzer and pH probes are running concurrently. Equipment OOS: - Sludge pump3 emergency stop alarm - GAC3 FCV deviation alarm - LL pump 3 | Georgina Water Treatment Plant | 2025-10-21
LINEAR | October | System back to normal operations from chamber number 3490133-11D to 3490133-11A and both the AVs were changed by north rock as planned. Total CL2 residual: 1.90 mg/L Free CL2 residual: 0.04 mg/L | Linear Water System | 2025-10-10
WW-WEST | October | Received call from ROC regarding low DO in aeration tank 2. Due to the issues the plant had over the weekend - responded to adjust air (W11393783). On arrival DO levels as follows, Tank 1: 6.11mg/L Tank 2: 1.05mg/L Adjust air valves and tank 2 began to climb again. Tank 2 DO has been trending down all day since this mornings adjustments. 23:13 Tank 1: 5.87mg/L Tank 2: 2.08mg/L Level continues to trend upwards. Unplugged submersible pumps as adequate mixed liquor and sludge should have been transferred to seed tank 1. RAS pump 1 showed no flow earlier in the evening (18:39), switched to pump 2 for tank 1 RAS. | Nobleton Water Resource Recovery Facility | 2025-10-26
WW-CEAST | October | -On site to complete work orders. -Wet well and bar screen cleaning and inspection completed. Inspected wet well, in good condition. Greased bar screens, including bottom sprocket in B2 of wet well. -Building automation system check completed. Acknowledged and reset old alarms. -Leslie SPS facility outfall inspection and cleaning work order completed earlier this month on Oct. 6 as part of Bayview Steeles OCF work orders. -Pumps 1 and 4 OOS. | Markham Leslie Pumping Station | 2025-10-22
WEST | October | -on site to complete station check and collect samples -sample work order # W11316705 -site offline and isolated from distribution system 13:27 - started well #3 in local running to waste at 25.6 l/s 13:27 - started well #4 in local running to waste at 26.6 l/s -checked equipment -reviewed trends -analyzer reagents ok -watermain currently isolated for new valve installation, no flow to analyzers 14:00 - collected weekly well #3 raw water micro. sample 14:00 - collected weekly well #4 raw water micro. sample -put both wells back into local off -no issues found | Kleinburg Wells 3 and 4 | 2025-10-22
EAST | October | Changed/replaced Surge Protector. Tested. Ok | Mount Albert North Elevated Tank | 2025-10-02
EAST | October | Under Direction of OIC (Dan Zhou) On site for; - Regulatory Sampling, micro (W11298642) - Station checks Regulatory samples taken @ 13:11 hrs. Data in PWQ Excel Workbook Grabs @ 13:11 hrs. FCl: 1.43 mg/L TCL: 1.62 mg/L Analyzer FCl: 1.42 mg/L Tower Duty ON (Filling) Equipment out of Service: None | Stouffville Zone 2 Elevated Tank | 2025-10-14
EAST | October | Activated duty at 13:27 to bring fresh water from zone 2 into zone 1 to bring up residuals in system and tower. | Stouffville Zone 1 Elevated Tank | 2025-10-27
EAST | October | Under Direction of OIC (Dan Zhou) On Site for monthly PM work orders; - JHSC Health and Safety Inspections - Inlet/Outlet Heat Trace System Inspection - Gasoline Portable Generator Test - Housekeeping - Semi annual Altitude Valve Inspection and Maintenance - Drain Valve exercise Analyzer Maintenance/Clean Start Clean @ 09:26 hrs. Stop Clean @ 10:05 hrs. Post maintenance/clean verification Grab @ 10:29 hrs. FCl:0.80 mg/L Grab @ 10:30 hrs. FCl: 0.80 mg/L Grab @ 10:31 FCl: 0.78 mg/L Analyzer: FCl: 0.76 mg/L Adjusted AIT to 3 grab average of 0.80 mg/L Tower Draining upon arrival, tower filling start @ 11:16 hrs. Changed Analyzer Reagent and buffer. Ran Generator for 10 minutes, functions well, oil is OK. Inlet/Outlet Heat Trace System functioning in good working order Performed maintenance on Altitude Valve and cleaned Y screen, with P. Fobert (OJT) Equipment OOS: None Facility OK | Stouffville Zone 1 Elevated Tank | 2025-10-15
EAST | October | On site for monthly maintenance - informed ROC - Level transmitter maintenance - Low temperature alarm - Heat trace system inspection - JHSC health and safety inspection - Portable gasoline generator test - Manual valves exercises - Housekeeping - Hach chlorine analyzer maintenance: Started @11:25 and completed @11:40. Verified analyzer readings with grab residuals Grab free: 1.19 mg/L / Analyzer: 1.18 Equipment back to auto, alarms cleared Station ok | Sutton Elevated Tank | 2025-10-16
EAST | October | Under direction of OIC (Dan Zhou) On-site for; - station checks Data in PWQ excel Workbook Influent Water Grab @ 09:07 hrs. Grab FCl: 2.00 mg/L Analyzer FCl: 2.03 mg/L Treated Water (Effluent) Grabs @ 09:07 hrs. Grabs FCl: 1.45 mg/L TCl: 1.63 mg/L Analyzer FCl: 1.41 mg/L Inspection of chemical room; revealed minor drip from ball valve connection (post chlorine booster pump) and T-joint between booster pump union joint. cannot swap ball valve and t joint until able to pressurize the system and test repair. Unable to pressurize system due to testing and sampling of Well 7. Well 3 is to remain off until confirmation and approval of well 7 sampling. - Informed team lead Dan Zhou Equipment OOS: None Facility and equipment off due to Well 7 testing and sampling. | Stouffville Well 3 | 2025-10-06
WEST | October | on site for station check Check trends- All okay Verified analyzers Postinjection- Total CL2 Grab: 3.74 mg/L: Analyzer: 3.70 mg/L Common inlet/outlet- Total CL2 Grab: 3.30 mg/L: Analyzer: 3.32 mg/L Reagents All good Sample taken while tower draining entered values in PWQ sheet Equipment all okay | Schomberg Elevated Tank | 2025-10-06
EAST | October | Under Direction of OIC (Dan Zhou) @ 12:52 hrs. On Site to receive Sodium Hypochlorite Delivery Volume before top up; Tank 1: 133.61 cm Tank 2: 132.81 cm After top up;; Tank 1: 204.8 cm Tank 2: 204.8 cm | Stouffville Well 1 & 2 | 2025-10-06
EAST | October | On site for station check. Collected weekly micro samples (11330463). Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 1.90mg/l FCL Analyzer:1.95mg/l 08:30hrs: Effluent Free Cl2 grab residual: 1.73mg/l FCL Analyzer: 1.78mg/l Effluent Total Cl2 grab residual: 1.88mg/l 0900hrs: Collected Well 2 raw samples Switched Well Duties: W2 to D1, W1 to D2. *After sample collection, manually stopped both wells. Locked out and tagged out both well VFD MCC?s to de-energize them for valve installation work to be completed today on the main line pipe post Contact Tanks completed by Torbear today. Work to be completed from 09:00hrs to 15:00hrs today. Informed ROC of Wells LOTO and that they will be offline for the day. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Site currently undergoing Construction upgrades by Torbear. Equipment out of service: None. | Ballantrae Well 1 & 2 | 2025-10-29
EAST | October | On site to complete station check. Switched reservoir intake valves opened east reservoir valve and closed west reservoir valve. No outstanding alarms on site. No OOS equipment. Time: 14:00 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.95 2.02 Time: 14:05 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.84 1.90 Total: 1.95 Verified analyzers with grabs all ok. Checked site and trends. | Stouffville Reservoir and Wells 5 & 6 | 2025-10-27
EAST | November | This is a contingency entry. Operator Chris Rodie was the OIC at time of work completed. He is no longer listed as OIC since he moved to another area. Below is transcript from paper log book. Nov, 15, 2023, time in 13:00 Onsite: Chris Rodie (OIC) Station check of site. AIT free: 1.83 mg/l Grab free: 1.78 mg/l, total: 1.89 mg/l. Flow: 0.28 L/s NTU: 0.024 Station all okay Time out: 13:07 | Stouffville Highway 48 Booster Pumping Station | 2023-11-15
EAST | October | Reviewed the following on scada - To review trends and record trains MITs, all passed - To review trends and record filter daily performance, no issues observed - To review permeate UV trends, no issues MAINT on site to replace triclamps on train 1. Train placed OOS service. Train 1 will remain OOS til next day because maintenance requires a couple of days. ROC notified. Low Lift Station: Chlorine analyzers: Both existing and newly installed chlorine analyzer and pH probes are running concurrently. LL pump2 hydraulic valve fail to open alarm keeps coming, notified PCS tech, Chris Scott did some troubleshooting remotely but could not find the problem, Chris will continue troubleshooting next day. LL pump2 will remain offline til next day. Notified ROC Before Diesel Generator Test Run Sheet running generator, the following were inspected: ? Battery cell levels ? Battery terminal and cables ? Oil level ? Coolant level ? Fluid leaks ? Coolant Recirculating pump ? Faulty gauges Diesel generator start time: 1317 hrs Diesel hours at start: 503.2 Fuel Level @ start: ? Tank #1 ~ 0.58m ? Tank #2 ~ Start time: After 30 min of running: ? Operating current = 250 A ? Operating frequency = 60 Hz ? Operating voltage = 600 V ? Engine speed = 2100 RPM ? Water temperature = 170 F ? Oil temperature = 195 F ? Oil pressure = 98 psi ? Fuel pressure. = ? ? Pyrometer/Exhaust = 684/706 F Stopped and transferred power to hydro @ 1450 hrs Diesel generator hours after shutdown: 504.7 hrs ? Tank #1 ~ 0.54m ? Tank #2 ~ Additional information/ Observations: Activated duty and conducted generator test under load, no issues Equipment OOS: - Sludge pump3 emergency stop alarm - GAC3 FCV deviation alarm - LL pump2 - FILT 1 tank | Georgina Water Treatment Plant | 2025-10-02
EAST | October | On site to provide OP support for LLP2 VFD commissioning. Tested it in remote manual and auto. Placed it auto duty 1. | Georgina Water Treatment Plant | 2025-10-01
EAST | October | Reviewed the following on scada - To review trends and record trains MITs, all passed - To review trends and record filter daily performance, no issues observed - To review permeate UV trends, no issues - Wet well mussel plate inspection completed Operations and Adjustments: Sodium Bisulphate tank top up ~ 0.22 m to 0.89 m (2,160 kg) 0900 hrs: Placed both UV systems inlet and outlet valves in manual and started draining Did maintenance on both UV systems Calibrated both UV systems and returned to service Activated duty with UV1 system in duty 1, no issues Low Lift Station: Chlorine analyzers: Both existing and newly installed chlorine analyzer and pH probes are running concurrently. Equipment OOS: - Sludge pump3 emergency stop alarm - GAC3 FCV deviation alarm - LL pump 3 - sodium hypo tank lo lo - Backwash tank 1 level loss of Echo alarm | Georgina Water Treatment Plant | 2025-10-15
EAST | October | Oversaw/assisted Total power technicians performed annual Diesel Generator load test. | Georgina Water Treatment Plant | 2025-10-07
EAST | October | On site responding to Total suspended solids hihi / fault and washwater pump lockout CMU5 #W11360943 ROC called about TSS high @09:53 - arrived on site @11:30 - Flushed lines to TSS analyzer and cleaned analyzer housing - TSS reading 0.6 mg/L after cleaning. Alarms cleared, and washwater pumps back to standby @11:50 - activated system duty while on site - KSTKWP level - 59% Reviewed MIT and daily filter performance on all trains - no issues and all passed - recorded readings in PWQ sheets @12:06 - train #4 shutdown on hihi turbdity on startup - reviewed trends, turbidity is coming down - placed train to M-clean as it is scheduled. If alarm comes in again, will leave train off until tomorrow No further issues on site | Georgina Water Treatment Plant | 2025-10-13
EAST | October | 09:15 Initiated MIT- Passed High pressure decay = 3.23 kPa Low pressure decay = 1.82 kPa 10:10 Placed train on | Georgina Water Treatment Plant | 2025-10-05
EAST | October | On site to respond to Boge air compressor fault. Manual indicated that the fault had something to do with either a faulty pressure sensor or an overcurrent event on the fan motor. Could not find any problems with those related components. Reset fault and tested for proper operation. Monitored proper operation for approximately an hour and a half. Left compressor running in lead duty. | Georgina Water Treatment Plant | 2025-10-06
EAST | October | Notified by ROC Train 1 performance yesterday lo/lolo 12:05 Instructed ROC to place train off | Georgina Water Treatment Plant | 2025-10-04
EAST | October | On site to conflict lab and station check. Completed grabs on Keswick and Sutton lines. Time: 11:55 Keswick Grab (mg/l) Analyzer (mg/l) Free: 1.72 1.74 Total: 2.05 2.08 Time: 11:58 Sutton Grab (mg/l) Analyzer (mg/l) Free: 1.76 1.73 Total: 1.99 2.06 Samples collected with out issue. All analyzers verified no changes needed to be made. | Georgina Water Treatment Plant | 2025-10-08
EAST | October | Reviewed the following on scada - To review trends and record trains MITs, all passed - To review trends and record filter daily performance, no issues observed - To review permeate UV trends, no issues - Wet well mussel plate inspection completed - Did shoreline lake observation and recorded in pwq data sheet Operations and Adjustments: MAINT on site to continue to work on train #1, (replacement of cam locks with triclamps). Took train 1 OOS and drained down for Maintenance. MAINT did a complete replacement on cassette D, tested MIT, train 1 passed (H = 3.0 kpa and L = 2.50 kpa) Backwashed train1 and placed back in service. Notified ROC Cleaned wash water to the lake chlorine analyzer, and verified by grab, = 0.01 no adjustment needed. Low Lift Station: Chlorine analyzers: Both existing and newly installed chlorine analyzer and pH probes are running concurrently. Equipment OOS: - Sludge pump3 emergency stop alarm - GAC3 FCV deviation alarm | Georgina Water Treatment Plant | 2025-10-08
EAST | October | Reviewed the following on scada - To review trends and record trains MITs, all passed - To review trends and record filter daily performance, no issues observed - To review permeate UV trends, no issues Operations and Adjustments: 1535 hrs: Initiated FMB train 1 backwash, and then initiated MIT with cassette C isolated, train passed MIT ( H = 3.32 kpa and L = 1.87 kpa). Directed ROC to return train 1 to service. Low Lift Station: Chlorine analyzers: Both existing and newly installed chlorine analyzer and pH probes are running concurrently. 1135 hrs: Together with PCS Tech (remote) continued with investigation of LL pump2 Hydraulic valve interlock alarm (valve failed to open, this alarm happens when comes to complete stop after production). PCS was able to fix valve issues Disabled LL pumps auto duty rotate, placed Pump2 as back up (second duty pump) to monitor valve operation into the weekend. Notified ROC and OIC on call. Equipment OOS: - Sludge pump3 emergency stop alarm - GAC3 FCV deviation alarm | Georgina Water Treatment Plant | 2025-10-03
EAST | October | On site to complete work orders: W11256056 Citric Acid Feed System Insp. W11308337 SO2 Leak Detector Test W11280746 CL2 Emergency Repair Kit Insp. W11267041 High Lift FCV Test W11291463 Aeration Blower Maint. W11269690 Hypo Pump Insp. W11269716 Caustic Soda Pump Insp. W11276116 SO2 Cylinder Emergency Repair Kit. W11269703 Sodium Bisulfite Pump Insp. W11273173 Mussel Plate Insp. No issues with work orders. Activated Sutton at 14:11. Switched fluoride pumps at 14:45 from pump 1 to pump 2. | Georgina Water Treatment Plant | 2025-10-07
EAST | October | Reassigned low lift pump duty so that LLP2 is in duty 1. Plant duty is not active. | Georgina Water Treatment Plant | 2025-10-07
EAST | October | On site to complete work order: W11305043 UV System Cleaning/Calibration Shut UV1 down and UV2 down and drained line at 10:12. Completed UV1 and UV2 calibration and cleaning from 10:12 to 15:30. Calibrations passed and have been entered into UV calibration folder. Put system back and activated duty at 14:50. No other work orders were able to be completed. No other issues. | Georgina Water Treatment Plant | 2025-10-15
EAST | October | Reviewed the following on scada - To review trends and record trains MITs, all passed - To review trends and record filter daily performance, no issues observed - To review permeate UV trends, no issues Operations and Adjustments: Total Power on site for 5 yr service/maintenance on diesen generator. Tech requested diesel generator to be placed in manual off during this 10:00 hrs: work on fluoride system, replaced fittings and conducted visual inspection. Did draw down test on fluoride chemical pumps through cal columns. Cleaned fluoride injectors and injection points. Activated duty, tested both pumps in during duty cycle. 1510 hrs: Verified fluoride reading by grabs 0.794 mg/l), when analyzer was at 0.79 mg/l. Notified ROC before and after completion. Low Lift Station: Chlorine analyzers: Both existing and newly installed chlorine analyzer and pH probes are running in parallel with old chlorine analyzers Equipment OOS: - Sludge pump3 emergency stop alarm - GAC3 FCV deviation alarm | Georgina Water Treatment Plant | 2025-10-07
EAST | October | Reviewed the following on scada - To review trends and record trains MITs, all passed - To review trends and record filter daily performance, no issues observed - To review permeate UV trends, no issues - Wet well mussel plate inspection completed Operations and Adjustments: 0900 hrs: Total power onsite to conduct a 5 yrs diesel generator service, Technician will place generator in manual during the period and return to auto when done. Notified ROC. 1330 hrs: Generator back in auto. No issues, ROC notified. Total Power on site for 5 yr service/maintenance on diesen generator. Tech requested diesel generator to be placed in manual off during this period. ROC and PS notified. 1030 hrs: Activated duty for station check. 1507 hrs: Adjusted HL header chlorine analyzer reading based on average of 3 grabs Maintenance (Electricians) on site to attend to air compressor - BOGE. Electricians were able to ack and reset alarm on air compressor and got it back up running. BOGE compressor will remain in service for performance monitoring. ROC and OIC on call notified Low Lift Station: Chlorine analyzers: Both existing and newly installed chlorine analyzer and pH probes are running concurrently. 1100 hrs: cleaned and calibrated LL chlorine analyzers ( both intake and wetwell). Did grabs on both and adjusted after cleaning and calibration. 1133 hrs: LL pump4 uncommanded stop. Ack and reset and return to service Equipment OOS: - Sludge pump3 emergency stop alarm - GAC3 FCV deviation alarm | Georgina Water Treatment Plant | 2025-10-06
EAST | October | Reviewed the following on scada - To review trends and record trains MITs, all passed - To review trends and record filter daily performance, no issues observed - To review permeate UV trends, no issues - Wet well mussel plate inspection completed Operations and Adjustments: 11:00 hrs: Adjusted contact chamber2 (1.63 mg/l to 1.74 mg/l) and clearwell 2 (1.1.46 to 1.58 mg/l)chlorine analyzers reading based average of 3 grabs. 1134 hrs: adjusted Post clearwell header chlorine analyzer reading from 1,34 to 1.55 based on 2 grabs Low Lift Station: Chlorine analyzers: Both existing and newly installed chlorine analyzer and pH probes are running concurrently. Equipment OOS: - Sludge pump3 emergency stop alarm - GAC3 FCV deviation alarm Notified ROC before leaving site | Georgina Water Treatment Plant | 2025-10-10
EAST | October | Reviewed the following on scada - To review trends and record trains MITs, all passed - To review trends and record filter daily performance, no issues observed - To review permeate UV trends, no issues - Wet well mussel plate inspection completed Operations and Adjustments: 0837 hrs: Shut down down LL pump3, placed on manual off, closed discharge valve and lock out and tag out. Notified ROC, contractor working on LL pump 3 Placed FMB train 1 in manual off, cleaned turbidity analyzer, and returned to standby. Placed mussel control chlorine system off Activated duty for sample collection Residuals - Keswick @ 135 hrs: FCL = 1.59 mg/L. Analyzer reading = 1.60 mg/l TCL = 1.95 mg/l Analyzer reading = 1.90 mg/l Collected raw water samples at 144 hrs. Returned mussel control chlorine system service after raw water sample collection Low Lift Station: Chlorine analyzers: Both existing and newly installed chlorine analyzer and pH probes are running concurrently. Equipment OOS: - Sludge pump3 emergency stop alarm - GAC3 FCV deviation alarm - LL pump 3 - sodium hypo tank lo lo | Georgina Water Treatment Plant | 2025-10-14
WW-CEAST | October | -station check of site -reviewed SCADA -inspected site -entered data into SharePoint -station okay | Aurora Henderson Sewage Pumping Station | 2025-10-24
WW-CEAST | October | Weather today A few clouds and 11 Celsius -On site to complete work order W11296149. -Operator assistance for wet well cleaning performed by Wessuc Inc. -Pump down wet well before they started cleaning. -Open bilco hatches and set up tripod and winch for access to wet well. -Off site early for work being performed this evening at Yonge & 19th Ave. | Aurora Henderson Sewage Pumping Station | 2025-10-29
WW-CEAST | October | Here to complete WO?s - checked odour control unit - all Ok and also cleaned the washroom and swept up the office area/ MCC room. Station running under normal ops - no issues observed. | Aurora Henderson Sewage Pumping Station | 2025-10-16
WW-CEAST | October | Here to set up wet well for cleaning,, flow was diverted to Aurora yesterday so we just pumped down the wet well and shut off the low level lock out. Wet well down to 0.63m and Wessex is now setting everything up. Truck air breaks broke so the north cell is empty and the south cell has a foot. Talked to Graham and all is good. Station is off line for the night. Informed ROC of the situation at the station. | Aurora Henderson Sewage Pumping Station | 2025-10-29
WW-CEAST | October | Here for the wet well inspection with CPD ,, warranty inspection completed ,, Dimitri and I went in to verify all gates are open and after getting out went to the valves on Henderson road and reinstated the flows back to the PS. Waited till wet well level was at 2.76m before getting pump 4 going with good flow (Duty 1 ) and also pump 2 (Duty 2) also good flow. Pump duty rotate has been shut off. Station is running as per normal,, I will reinstate pumps 1&3 tomorrow. | Aurora Henderson Sewage Pumping Station | 2025-10-30
WW-CEAST | October | Took station readings and entered into SharePoint,, reviewed trends - all looks good. Walked through the building - all is clean and everything looks good. Station running under normal ops - no issues found. | Aurora Henderson Sewage Pumping Station | 2025-10-27
WW-CEAST | October | Took station readings and entered into SharePoint,, reviewed trends - all pumps working as per normal/good flow rate and pressure. Station is back to all stop duty rotation and is operating as per normal. | Aurora Henderson Sewage Pumping Station | 2025-10-31
WW-CEAST | October | On site for station check (See details on SharePoint). All pumps available in all-stop auto duty rotation. Standby power generator available in auto. Found station with outstanding alarm regarding site hydro power failure alarm happened October 18, 2025, at 10:18pm. Generator is not running at time of arrival. Station is in local utility power. Cleared/reset alarm showing on the banner. Station operations normal. | Aurora Henderson Sewage Pumping Station | 2025-10-20
WW-CEAST | October | Completed the valve work @ Henderson drive to isolate Henderson SPS, send all flow to Aurora SPS in preparation for tomorrow wet well cleaning. | Aurora Henderson Sewage Pumping Station | 2025-10-28
WW-CEAST | October | Took station readings and entered into SharePoint,,, reviewed trends - all looks good. Station running under normal ops - no issues were found. | Aurora Henderson Sewage Pumping Station | 2025-10-06
WW-CEAST | October | On-site to complete PMs. W11283134, W11283121, W11283147, W11283432, W11283158 Completed above w.os. Pump test run: P4 pushed out 56.8 l/s @ 50% speed, Pump 3 pushed out 53.4 l/s @ 50% psd, Pump 2 pushed out 57 l/s @ 50% Spd, Pump 1 pushed out 57 l/s @ 50% spd. Noticed Some recirc valve do not open all the way due to short enable duration. Increased this set point from 1m to 2m | Aurora Henderson Sewage Pumping Station | 2025-10-08
WW-CEAST | October | Station check complete and the readings have been entered into the sharepoint Generator test run complete and the readings have been entered into the sharepoint. Tested valve room flood alarm, OK Tested building temp sensor for office/mech room, OK. There is about 8 minute delay before sending hihi alarm. | Aurora Henderson Sewage Pumping Station | 2025-10-03
WW-CEAST | October | -station check of site -reviewed SCADA -inspected site -entered data into SharePoint -SharePoint page needs updating as it?s copy pasted from another BIOREM facility, will work on this later today/week -shelved Exhaust Fan 1 Damper Fault Alarm, as Exhaust Fan 1 has been removed, and is out for bearing replacement, will restore these alarms when the fan is reinstalled -generator fault alarm was shelved until TSSA inspection is completed, temporary generator is hooked up and ready until passed TSSA inspection of generator -shelved alarms should be reinstated once all OOS equipment is put into operation -air handling system is working as intended, pH has partially dropped, in a few weeks hopefully the recirculated water will be between 1-3 pH -station is okay | Oak Ridges Air Management Facility | 2025-10-21
WW-CEAST | October | Unit 1 Recirc pump 1 overload alarm came in last night 22:30. NAC reset the alarm this morning and PCS placed Recirc P1 back in lead duty | Oak Ridges Air Management Facility | 2025-10-24
WW-CEAST | October | On site to accommodate bubble damper testing. Checked on site H2S sampler and it is out of calibration, asked AECOM to calibrate before the handover. | Oak Ridges Air Management Facility | 2025-10-17
WW-CEAST | October | Through confirmation w/ AECOM & BIOREM the Inlet Dampers are to be opened from 40% to 100% = fully open as per design. 2:55pm opened to 55%, 3:10pm opened to 70%, 3:25pm opened to 85%, 3:40pm opened to 100%. Outflow through system increased 75% from 4000 to 7000m3/h. Fan Speed automatically increased from apprx 48% +- to 54-56% on each Train. Further system adjustmensts will be made during testing and performance phases. | Oak Ridges Air Management Facility | 2025-10-28
WW-CEAST | October | -on site to start facility after media is inoculated with bacteria -met Mike from BIOREM and did a system walk through -met with Kyle Carlen from PCS to discuss system performance -fans were turned on at approximately 13:00 just before inoculating the media, to pull the wastewater through -opening top hatches for inoculating caused fans to ramp up due to suction pressure rise, put both fans manual speed 40% while bugs added -inoculation done, both fans back to auto speed -Kyle Carlen adjusted inlet pressure tolerance from 10% to 2% to keep the fan speed matching the -1.20 kPa suction pressure -fans are trying to maintain -1.20 kPa suction pressure -monitoring system -system is operating, fans are running in auto, auto speed, both trains are online -as H2S gas is pulled in, nutrient water in tanks will begin to lower in pH, goal is 1-3 pH, currently 7 pH approximately as it?s new water, will not waste any water until adequate pH levels achieved | Oak Ridges Air Management Facility | 2025-10-20
EAST | October | On site for MIT review, station check, lab analysis. Collected weekly micro samples (W11256420), Algae samples (W11256234), THM/VOC samples (W11256206). In house ATP samples collected and GLIP raw samples collected. Data recorded in PWQ sheet. Reviewed MIT and daily filter performance on all trains - all passed. Reviewed SCADA trends and UV trends. 09:35hrs: Conducted inspection on Clearwell, CT tanks and Post CLearwell Cl2 Analyzers. Verifications completed and put into PWQ sheet. 09:40hrs: Adjusted Post Clearwell CL2 Analyzer from 1.55mg/l to 1.70mg/l based on multiple Cl2 grab residuals. 10:00hrs: Performed lakeshore observation. No HAB observed. Recorded in PWQ sheet. 10:15hrs: Conducted testing on Low Lift P2. Required running low lift pump to Train 1 and Train #2. Informed ROC of associated work and alarms to disregard. 11:20hrs: Made adjustments to low lift CL2 Analyzers: Wetwell Analyzer from 0.03mg/l to 0.23mg/l, Raw water intake CL2 Analyzer from 0.09mg/l to 0.22mg/l based on multiple CL2 grab residuals 11:55hrs: Activated plant for sampling. 12:55hrs: Collected all raw water samples. 13:07hrs: Adjusted Sutton Line Fluoride Analyzer from 0.79mg/l to 0.66mg/l based on in house lab grabs. Collected Treated samples (Keswick Line) @ 13:10hrs. Cl2 grab residuals: FCL: 1.79mg/l TCL: 2.15mg/l Verification of CL2 Analyzers in PWQ sheet. There are new Raw Water and Wetwell Low lift AIT Analyzers installed in the low lift and they are working in parallel with the current Low lift analyzers on site to monitor the performance of the new CL2 Analyzers. We are still responding to alarms on current/older CL2 Analyzers until we fully switchover solely to the new CL2 Analyzers. Equipment out of service: Sludge P3 (leaking volute). Low Lift building equipment undergoing construction upgrades (Lexsan). Alarms to disregard (ROC notified through SCADA review PWQ sheet): Sludge P3 Emergency Stop Alarm, GAC 3 Flow Control Valve Deviation Alarm. | Georgina Water Treatment Plant | 2025-10-01