## Aurora SPS
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS | 1 | 1 | 1
12098721 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12098721 | 2 | 2025-10-17 13:24 | 2025-10-17 13:22 | Chris Rodie (WW-CEAST) @ Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility - AUSSMP Date Work Completed: 2025-10-17 13:22 ————————————————————— -station check of site -reviewed SCADA -inspected site -entered data into SharePoint -cleaned screen room, rotated bins as necessary -Pump 3 primed and put back to auto, testing pump by switching to duty 1 -Pump 3 flowmeter fault came back in, Pump 3 returned to duty 7/OOS, notified instrumentation Team Lead Eric -rotated duties for pumps -station okay ————————————————————— • Attachments: 0 | 0.99997 | 1 | 1
12125516 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12125516 | 1 | 2025-10-29 13:29 | 2025-10-29 13:27 | Chris Rodie (WW-CEAST) @ Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility - AUSSMP Date Work Completed: 2025-10-29 13:27 ————————————————————— -station check of site -reviewed SCADA -entered data into SharePoint -inspected site -cleaned screen room, put 3 bins out for pickup, 1 left 2/3 full in screen room -inspected air compressors -inspected suction valves, did not have time to exercise as line is clogged at dump pad requiring resolution -pump 3 remains OOS due to flowmeter fault, can be used in emergencies -station okay ————————————————————— • Attachments: 0 | 1 | 1 | 1
12122004 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12122004 | 1 | 2025-10-28 11:39 | 2025-10-28 11:33 | Chris Rodie (WW-CEAST) @ Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility - AUSSMP Date Work Completed: 2025-10-28 11:33 ————————————————————— -called to site to address clogged lines for dump pad -lines 1 and 2 were clogged and OOS, overtorque on plug valves -backflushed both lines, rags and diapers were stuck in the actuated plug valves, these plug valves are not the right valves for a system receiving diapers and rags, which is why these lines are frequently getting clogged and debris stuck in the plug valves -open all valves, valves back to remote -reset alarms on SCADA -all 3 lines are now available ————————————————————— • Worked With: Marcos Tungcol • Attachments: 0 | 1 | 1 | 1
12119177 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12119177 | 2 | 2025-10-27 09:57 | 2025-10-27 09:00 | Terry Reed (WW-CEAST) @ Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility - AUSSMP Date Work Completed: 2025-10-27 09:00 ————————————————————— Took station readings and entered into SharePoint,, checked the dump pad to ensure all 3 lines are available: yes they are. Checked both compressors oil/belt - OK. Checked pump floor - all looks good - no leaks and everything looks operational. Verified the sampling kit Ty-strap has not been tampered with and kit is -OK. Test ran each pump: P1- @ 23%=362.2 L/s, P2- @ 18%=305.2L/s, P3 is OOS due to flow meter and P4 - is 450L/s P5 - @42%=389.2L/s and P6 - @ 16%=310.9 L/s. Levelled out the bin in the screening room - went to top up bar screen oil but I’m gonna have to get a new bucket of oil,, I shut down the ventilation fans for the screening room as the weather is starting to change and it was pretty cool in there ( bar screens freezing up ). Went and checked the odour control for the EQ tank - greased the fan where required and it’s operating as it should. Station running as per normal, pump 3 in Duty 7 but can be ran - I will create a WO for LIT 4 EQ tank. ————————————————————— • Attachments: 0 | 0.99999 | 1 | 1
12098721 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12098721 | 2 | 2025-10-17 13:24 | 2025-10-17 13:22 | Chris Rodie (WW-CEAST) @ Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility - AUSSMP Date Work Completed: 2025-10-17 13:22 ————————————————————— -station check of site -reviewed SCADA -inspected site -entered data into SharePoint -cleaned screen room, rotated bins as necessary -Pump 3 primed and put back to auto, testing pump by switching to duty 1 -Pump 3 flowmeter fault came back in, Pump 3 returned to duty 7/OOS, notified instrumentation Team Lead Eric -rotated duties for pumps -station okay ————————————————————— • Attachments: 0 | 0.99999 | 1 | 1
12078354 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12078354 | 3 | 2025-10-10 12:11 | 2025-10-10 12:10 | Marcos Tungcol (WW-CEAST) @ Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility - AUSSMP Date Work Completed: 2025-10-10 12:10 ————————————————————— On site for station check (See details on SharePoint). All pumps available in timed auto duty rotation every 3 hours, except pump 3, which has an issue with flowmeter fault alarm. All standby power generator available in auto. Checked dry well. Checked bar screens. Bar screen 1 still out of service. Levelled rags from the rag bin. Cleaned bar screen room. Switched rag bin. Hauler’s dump pad is ok. All lines available. ————————————————————— • Attachments: 0 | 1 | 1 | 1
12087300 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12087300 | 1 | 2025-10-14 14:58 | 2025-10-14 14:56 | Christian Streef (WW-MAINT) @ Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility - AUSSMP Date Work Completed: 2025-10-14 14:56 ————————————————————— On site to fix barscreen #1. Chain off bottom sprocket. Fixed barscreen ran tested and put back in service. ————————————————————— • Worked With: Martin deVries • Attachments: 0 • [REMOTE ENTRY] | 0.000729 | 0 | 0
12057420 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12057420 | 1 | 2025-10-03 11:17 | 2025-10-03 11:16 | Barry Middleton (WW-CEAST) @ Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility - AUSSMP Date Work Completed: 2025-10-03 11:16 ————————————————————— Weather today Clear and 17 Celsius -On site responding to dump pad receiving line #1 valve over torque alarm. -manually opened valve back flushed line #1 and closed valve and cleared alarm. -Dump pad receiving line #1 back in service. -On site to complete work order W11264011. -On site to perform a station check. -Entered station readings into SharePoint. -Checked drywell and air compressors. -Checked screen room, raked rag bin, cleaned rags off conveyors, bar screen oil good. -Bar Screen Bin Removal and Replacement put rag bin back inside from pick up by Miller Waste. -Pump 3 OOS with Flowmeter fault issues. -pump 5 OOS with leakage alarm issues. ————————————————————— • Attachments: 0 | 1 | 1 | 1
12058004 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12058004 | 2 | 2025-10-05 15:32 | 2025-10-05 15:28 | Daniel Kim (WW-CEAST) @ Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility - AUSSMP Date Work Completed: 2025-10-05 15:28 ————————————————————— On site in response to Barscreen 1 not in auto alarm. Attempted to clear alarm and operate barscreen on hand, rake is stuck at the bottom not moving/causing overtorque alarm with a loud noise. Called ROC to dispatch Young J (WW) to assist in closing the barscreen 1 inlet valve to put the unit OOS. Cleared line 2 valve overtorque alarm. Flushed the line multiple times in the other direction with down stream valve closed. Young J on site, we closed barscreen 1 inlet gate valve. Went down to B2 to inspect the rake, confirmed one side chain has popped out of the sprocket. CMU3 created for CMS. ————————————————————— • Attachments: 0 | 1 | 1 | 1
12071199 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12071199 | 2 | 2025-10-08 11:34 | 2025-10-08 11:24 | Chris Rodie (WW-CEAST) @ Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility - AUSSMP Date Work Completed: 2025-10-08 11:24 ————————————————————— -station check of site and work orders completed -reviewed SCADA -inspected site -entered data into sharepoint -notified from ROC Adam Pump 2 MV2 fail to open -put pump 2 manual off to investigate forcemain discharge valve and pump discharge valve fail to open alarms, exercised both forcemain discharge valves for pump 2, put pump back to auto and duty 1, started pump 2 in auto, pump 2 ran and opened valves with no issues -will monitor pump 2 remotely and notify on call operator -pump 3 remains manual off due to flowmeter fault alarm, 5 pumps available -cleaned screen room, rotated bins as necessary -bar screen 1 remains OOS, and isolated -station okay ————————————————————— • Worked With: Jackie Saunders • Attachments: 0 | 1 | 1 | 1
12063113 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12063113 | 3 | 2025-10-06 10:45 | 2025-10-06 09:20 | Terry Reed (WW-CEAST) @ Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility - AUSSMP Date Work Completed: 2025-10-06 09:20 ————————————————————— Took station readings and entered into SharePoint,, checked both compressors oil/ belts and air- ok and also looked at air dryer and all looks good. Tested dry well flood alarm and confirmed by ROC. Completed H & S inspection - no issues and verified operation of all 3 cranes. Leveled out the bin in the screening room and cleaned out the auger and flushed out the drain as well as grease it. Pump 3 is in Duty 7 due to flow meter issue and pump 5 is in Duty 7 due to coolant leak,, inlet channel 1 is OOS due to chain off the bar screen. Rest of the station is running as per normal. Brought my chop saw in and made 4 hose stands for the dump pad. Glued saddle in today so they will be ready to go for tomorrow. ————————————————————— • Attachments: 0 | 1 | 1 | 1

## Leslie SPS
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS
12109765 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12109765 | 1900-01-01 | 2025-10-22 12:04 | 2025-10-22 12:03 | Philip Romito (WW-CEAST) @ Markham Leslie Pumping Station - LSSS Date Work Completed: 2025-10-22 12:03 ————————————————————— -On site to complete work orders. -Wet well and bar screen cleaning and inspection completed. Inspected wet well, in good condition. Greased bar screens, including bottom sprocket in B2 of wet well. -Building automation system check completed. Acknowledged and reset old alarms. -Leslie SPS facility outfall inspection and cleaning work order completed earlier this month on Oct. 6 as part of Bayview Steeles OCF work orders. -Pumps 1 and 4 OOS. ————————————————————— • Worked With: Jackie Saunders • Attachments: 0 | 1
12098756 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12098756 | 1900-01-02 | 2025-10-17 14:38 | 2025-10-17 14:38 | Philip Romito (WW-CEAST) @ Markham Leslie Pumping Station - LSSS Date Work Completed: 2025-10-17 14:38 ————————————————————— -Back on site to respond to Bar Screen 2 Fault Alarm reported by ROC. -Reset fault and ran Bar Screen 2 in hand. Rake is noticeably crooked and bearings are fairly noisy while bar screen is in operation. -Had D. Kim attend site and isolated inlet gate to Bar Screen 2. Placed bar screen 2 OOS and created work request for maintenance team to troubleshoot issue further. ————————————————————— • Worked With: Daniel Kim • Attachments: 0 | 1
12098129 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12098129 | 1900-01-02 | 2025-10-17 08:59 | 2025-10-17 08:59 | Philip Romito (WW-CEAST) @ Markham Leslie Pumping Station - LSSS Date Work Completed: 2025-10-17 08:59 ————————————————————— -On site to complete work orders. -Entered station readings into SharePoint. -Checked drywell. -Hoist inspection completed. -Drained condensate from air compressors. -Checked screen room, changed out rag bin, replaced bins following pick up, hosed down screw press drain lines, cleaned rags off bar screens. -Screw conveyor cleaning and lubrication completed. -Station check completed. -Forcemain header valve and actuator, exercise and inspection completed. Fully exercised South, North, and Header Tie Valves. South Forcemain Valve stuck at 98% open with an Overtorque Alarm. Unable to get valve to open further, will have to continue work. On valve at a later date. -RS pump inspection completed. Pumps 1 and 4 OOS. -Pump 2: 940L/s at 0%, 1420L/s at 50%, 1815L/s at 100%. -Pump 3: 1320L/s, -Pump 5: 940L/s at 0%, 1400L/s at 50%, 1765L/s at 100%. -Pump 6: 1135L/s. -Check valves inspection completed. -Air relief valves inspection completed. -Pumps 1 and 4 OOS. South Forcemain Overtorque Alarm outstanding at 98% open. ————————————————————— • Attachments: 0 | 1
12102496 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12102496 | 1900-01-03 | 2025-10-20 11:58 | 2025-10-20 11:58 | Philip Romito (WW-CEAST) @ Markham Leslie Pumping Station - LSSS Date Work Completed: 2025-10-20 11:58 ————————————————————— -On site to perform a station check. -Entered station readings into SharePoint. -Checked drywell, drained condensate from air compressor tanks. -Reset Earth Fault on AHU-1, unit now running in auto again. -Pumps 1-6 seal water strainer inspection completed. -Checked screen room, changed out rag bin, bar screen oil full, flushed screw press drain lines. -Pumps 1 and 4 remain OOS. -South Forcemain Valve Fault outstanding, Overtorque at 98% open. ————————————————————— • Attachments: 0 | 1
12071117 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12071117 | 1900-01-01 | 2025-10-08 10:18 | 2025-10-08 10:17 | Philip Romito (WW-CEAST) @ Markham Leslie Pumping Station - LSSS Date Work Completed: 2025-10-08 10:17 ————————————————————— -On site to perform a station check. -Entered station readings into SharePoint. -Checked drywell, drained condensate from air compressor tanks. -Rotated sump pump duties. -Checked screen room, changed out rag bin, placed bins out for pick up, flushed screw press drain lines, bar screen oil full. -Pump 1 and Generator 3 remain OOS. -Pumps 2-6 in auto and available. ————————————————————— • Worked With: Kevin Shaji • Attachments: 0
12091189 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12091189 | 1900-01-01 | 2025-10-15 12:14 | 2025-10-15 09:40 | Philip Romito (WW-CEAST) @ Markham Leslie Pumping Station - LSSS Date Work Completed: 2025-10-15 09:40 ————————————————————— -On site to complete work orders. -Station readings entered into SharePoint. -Checked drywell. -Air compressors inspection and cleaning completed. -Checked screen room, changed out rag bin, cleared out blockage in screw press drain lines. Topped up bar screen oil, swept floor. -Bar screen bin removal completed. -Station check completed. -BAS inspection completed. -Dry well sump put high level alarm test completed and confirmed by ROC. -Surge tank transmitter lines flushing completed, flushed air and sewage lines on both pressure and level sensors. -Reset all alarms caused from work on site. -Pumps 2-6 in auto and available. -Pump 1 remains OOS, Generator 3 remains OOS. ————————————————————— • Attachments: 0
12053288 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12053288 | 1900-01-05 | 2025-10-01 08:53 | 2025-10-01 08:53 | Philip Romito (WW-CEAST) @ Markham Leslie Pumping Station - LSSS Date Work Completed: 2025-10-01 08:53 ————————————————————— -On site to complete work orders. -Station check completed, readings entered into SharePoint. -Checked drywell. -Air compressors, inspection and cleaning completed. -Checked screen room, changed out rag bin, flushed screw press drain lines, topped up bar screen oil. -Bar screen removal completed for pick-up tomorrow. -Monthly diesel generator test run completed, readings entered into SharePoint. -Diesel generator 3 remains OOS, only generators 1 and 2 ran during the monthly test. -11:01 - Transferred site to generator power. -12:26 - Transferred site back to utility power. -Gen 1: Start time: 213:33, Stop time: 215:03, Run time: 1:30hrs. -Gen 2: Start time: 98:36, Stop time: 100:06, Run time: 1:30hrs. -Gen 3 hours remain at 88:09, generator OOS. -Monthly JHSC H&S inspection completed. -BAS check completed, acknowledged and reset old alarms, no active alarms. -Pump 1 OOS, Pumps 2-6 in auto and available. ————————————————————— • Attachments: 0 | 1
12053741 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12053741 | 1899-12-31 | 2025-10-01 19:15 | 2025-09-24 09:20 | Terry Reed (WW-CEAST) @ Markham Leslie Pumping Station - LSSS Date Work Completed: 2025-09-24 09:20 ————————————————————— Took station readings and entered into SharePoint,,, put bins out for pick up and washed out screens for Bayview again. Checked both compressors and also the BAS system - all good. Station running under normal ops - Pump 1 is OOS. ————————————————————— • Attachments: 0 | 1
WW-CEAST | Markham Leslie Pumping Station | 2025-10-10 | Took station readings and entered into SharePoint,, put bins back into the screening room and flushed out the bottom of the auger, also switched the bins out for the weekend. Checked both compressors oil/ belts - OK and drained the water from the holding tanks, exercised the drain valves on the surge tanks and also inspected both tanks - all looks good. Rolled up the hose that?s been on the floor and cleaned up the area a bit. Inspected the sump pit and activated pump - all good,, flushed the bubblers - no issues and checked the BAS system for the building. Checked the screens on the odour control unit - all good and set up a new sample line on pump 6 for the weekly samples. Station running under normal ops - pump 1 is still OOS waiting on parts. All alarms were cleared. | this one isnt on power Bi.. | 1 | 1
12057270 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12057270 | 1900-01-01 | 2025-10-03 09:01 | 2025-10-03 09:01 | Philip Romito (WW-CEAST) @ Markham Leslie Pumping Station - LSSS Date Work Completed: 2025-10-03 09:01 ————————————————————— -On site to perform a station check. -Entered station readings into SharePoint. -Checked drywell, drained condensate from air compressor tanks.. -Checked screen room, replaced rag bins following pick-up, changed out bin for the weekend, flushed screw press drain lines. -Generator 3 OOS, Pump 1 OOS. -Pumps 2-6 in auto and available. ————————————————————— • Attachments: 0
12063224 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12063224 | 1900-01-04 | 2025-10-06 12:54 | 2025-10-06 11:10 | Philip Romito (WW-CEAST) @ Markham Leslie Pumping Station - LSSS Date Work Completed: 2025-10-06 11:10 ————————————————————— -On site to complete work orders. -Hosed down dirty mist eliminator filters from Bayview Steeles OCF in screen room. -Checked screen room, changed out rag bins, flushed screw press drain lines, bar screen oil topped up. Cleaned rags off floor. -Station readings entered into SharePoint. -Checked drywell, drained condensate from air compressor tanks. -Seal water strainer inspection and cleaning completed. -Diesel generator 3 OOS. -Pumps 1 OOS. -Pumps 2-6 in auto and available. ————————————————————— • Attachments: 0 | 1
12109765 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12109765 | 1900-01-01 | 2025-10-22 12:04 | 2025-10-22 12:03 | Philip Romito (WW-CEAST) @ Markham Leslie Pumping Station - LSSS Date Work Completed: 2025-10-22 12:03 ————————————————————— -On site to complete work orders. -Wet well and bar screen cleaning and inspection completed. Inspected wet well, in good condition. Greased bar screens, including bottom sprocket in B2 of wet well. -Building automation system check completed. Acknowledged and reset old alarms. -Leslie SPS facility outfall inspection and cleaning work order completed earlier this month on Oct. 6 as part of Bayview Steeles OCF work orders. -Pumps 1 and 4 OOS. ————————————————————— • Worked With: Jackie Saunders • Attachments: 0 | 1

## Newmarket SPS
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS | 1
12115170 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12115170 | 1899-12-31 | 2025-10-24 11:55 | 2025-10-24 11:53 | Chris Rodie (WW-CEAST) @ Newmarket Sewage Pumping Station & Equalization Tank - NMSSBP Date Work Completed: 2025-10-24 11:53 ————————————————————— -station check of site -reviewed SCADA -inspected site -entered data into SharePoint -pump 2 remains OOS, pump out for repair -station okay ————————————————————— • Worked With: Jackie Saunders • Attachments: 0 | 1
12119297 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12119297 | 1899-12-31 | 2025-10-27 10:44 | 2025-10-27 10:42 | Chris Rodie (WW-CEAST) @ Newmarket Sewage Pumping Station & Equalization Tank - NMSSBP Date Work Completed: 2025-10-27 10:42 ————————————————————— -station check of site -reviewed SCADA -inspected site -entered data into SharePoint -pump 2 remains OOS, pump missing -cleaned screen room, rotated bin -station okay ————————————————————— • Attachments: 0

## Mt. Albert WRRF
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS
12099185 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12099185 | 1900-01-02 | 2025-10-19 10:04 | 2025-10-19 10:04 | Philip Romito (WW-CEAST) @ Mount Albert Water Resource Recovery Facility - MTSP Date Work Completed: 2025-10-19 10:04 ————————————————————— -On site to complete lab analysis and sludge handling work. -Decanted STT to headworks, then emptied tank into SHT. -Added two bags of soda ash to each aeration tank. -Completed lab analysis, entered results into SharePoint. -Found right side of cell 1 sand filter not draining and packed with sand. Cleared out under drain, removed built up sand. Pulled air lift, cleared out sand, and reset air lift. Air lift now working properly and draining. -Batch wasted 20m3, ran RAS pumps at 100% speed when returning to service. -Verified alum dosing and sand filter operation. -RAS pump 2 OOS, Aeration blower 3 OOS. ————————————————————— • Attachments: 0 | 1
12112560 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12112560 | 1900-01-03 | 2025-10-23 12:01 | 2025-10-23 12:00 | Chris Rodie (WW-CEAST) @ Mount Albert Water Resource Recovery Facility - MTSP Date Work Completed: 2025-10-23 12:00 ————————————————————— -station check and lab analysis of site -reviewed SCADA -inspected site -completed lab analysis, data entered into SharePoint -began diverting sand filter effluent to lagoon at 08:25, to prepare for UV maintenance by contractors, stopped diverting at 11:19, approximately 136 m3 of sand filter effluent was diverted to the lagoon -notified ROC of diversion and sending email to ENV Incident Notification -UV maintenance by contractors is complete -UV 1A is duty 1 and dosing 14 mw/cm2 -started decant pump, decanting sludge thickening tank back to influent -dumped thickened sludge to sludge holding tank -wasted 20 m3 from clarifier to sludge thickening tank, 10 m3 from each clarifier -clarifier 1 is OOS, RAS pumps 2 and 3 are off -added two bags of soda ash to each aeration tank, 4 bags total -cleaned RAS chamber -cleaned alum injection chamber -UV channel hose down -station okay ————————————————————— • Worked With: Jackie Saunders • Attachments: 0 | 1
12109807 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12109807 | 1899-12-31 | 2025-10-22 13:11 | 2025-10-22 13:10 | Barry Middleton (WW-CEAST) @ Mount Albert Water Resource Recovery Facility - MTSP Date Work Completed: 2025-10-22 13:10 ————————————————————— Weather today Light rain and 12 Celsius -On site to complete work orders W11309771, W11353484, W113373597, W11281061, W11281068, W11283051, W11316168. -Completed in-house lab analysis and station check. -Entered lab and station readings into SharePoint. -Grit Vortex 1 and 2 maintenance. -Oak ridges AMF - MUA training . -Isolated and drained down clarifier. -Daily SCADA review. -Doane Rd Effluent Discharge sewer inspection and cleaning. -Reset composite sampler for tomorrow. -Outfall inspection and cleaning. -Ran RAZ pumps #1 and #3 at 100% to clear them out for a bit - all back to auto as well as speed back to auto. -Added two bags of soda ash to each aeration tank. -Decanting STT into the Headworks. -Transferred the sludge and processing. -Aeration Blower back in service in auto duty rotation. -Clarifier 1 has been isolated, partially drained and put out of service to accommodate the works to be done by contractor. -RAS Pump 3 in manual off and out of service. -RAS pump 2 remains OOS. ————————————————————— • Worked With: Kevin Shaji, Marcos Tungcol • Attachments: 0 | 1
12115697 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12115697 | 1900-01-03 | 2025-10-26 12:34 | 2025-10-26 12:34 | Barry Middleton (WW-CEAST) @ Mount Albert Water Resource Recovery Facility - MTSP Date Work Completed: 2025-10-26 12:34 ————————————————————— Weather today a Few Clouds and 3 Celsius -On site to complete work order W11322495. -Completed in-house lab analysis and station check. -Entered lab and station readings into SharePoint. -Ran RAZ pumps #1 at 100% to clear it out for a bit - all back to auto as well as speed back to auto. -Batch wasted 7m3 from Clarifier #1. -Added two bags of soda ash to each aeration tank. -Decanting STT into the Headworks. -Transferred the sludge and processing. -Clarifier 1 has been isolated, partially drained and put out of service to accommodate the works to be done by contractor. -RAS Pump 3 in manual off and out of service. -RAS pump 2 remains OOS. ————————————————————— • Attachments: 0 | 1
12102638 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12102638 | 1900-01-01 | 2025-10-20 14:57 | 2025-10-20 14:57 | Barry Middleton (WW-CEAST) @ Mount Albert Water Resource Recovery Facility - MTSP Date Work Completed: 2025-10-20 14:57 ————————————————————— Weather today Partly Cloudy and 11 Celsius -On site to complete work orders W11309698, W11308482. -Completed in-house lab analysis and station check. -Entered lab and station readings into SharePoint. -Post aeration alum mixing chamber and Ras/Was inlet channel inspection and clean out. -Ran RAZ pumps #1 and #3 at 100% to clear them out for a bit - all back to auto as well as speed back to auto. -Added two bags of soda ash to each aeration tank. -Decanting STT into the Headworks. -Transferred the sludge and processing. -Aeration Blower #3 back in service in auto duty rotation. -RAS pump 2 remains OOS. ————————————————————— • Worked With: Kevin Shaji • Attachments: 0 | 1
12106162 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12106162 | 1899-12-31 | 2025-10-21 11:54 | 2025-10-21 11:53 | Barry Middleton (WW-CEAST) @ Mount Albert Water Resource Recovery Facility - MTSP Date Work Completed: 2025-10-21 11:53 ————————————————————— Weather today Light rain and 12 Celsius -On site to complete work orders W113312995, W11311919, W11311389, W11311206, W11313169, W11312023. -Completed in-house lab analysis and station check. -Entered lab and station readings into SharePoint. -2 tonne hoist system inspection. -Sand filter reject drain line flush. -Raw sewage sampler check. -Collected weekly raw sewage samples. -Reset composite sampler for tomorrow. -Post aeration alum mixing chamber and Ras/Was inlet channel inspection and clean out. -Ran RAZ pumps #1 and #3 at 100% to clear them out for a bit - all back to auto as well as speed back to auto. -Added two bags of soda ash to each aeration tank. -Decanting STT into the Headworks. -Transferred the sludge and processing. -Aeration Blower back in service in auto duty rotation. -RAS pump 2 remains OOS. ————————————————————— • Worked With: Kevin Shaji • Attachments: 0 | 1
12115258 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12115258 | 1899-12-31 | 2025-10-24 13:47 | 2025-10-24 13:46 | Kevin Shaji (WW-CEAST) @ Mount Albert Water Resource Recovery Facility - MTSP Date Work Completed: 2025-10-24 13:46 ————————————————————— -Reviewd scada, inspected site. -Completed in-house lab analysis and station check. -Entered lab and station readings into SharePoint. -Decanting STT into the Headworks. -Transferred the sludge and processing. -Batch wasted 5m3 from clarifier to sludge thickening tank. -Added two bags of soda ash to each aeration tank. -Clarifier 1 remain OOS, RAS pumps 2 and 3 are off. -WAS pump 2 switched to manually off due to clarifier 1 being OOS ————————————————————— • Attachments: 0 | 1
12122353 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12122353 | 1900-01-01 | 2025-10-28 13:51 | 2025-10-28 13:50 | Barry Middleton (WW-CEAST) @ Mount Albert Water Resource Recovery Facility - MTSP Date Work Completed: 2025-10-28 13:50 ————————————————————— Weather today a few clouds and 10 Celsius -On site to complete work orders W11325492, W11324828, W11327324, W11327651, W11327069, W11327069, W11327749, W11327305, W11334850. -Completed in-house lab analysis and station check. -Entered lab and station readings into SharePoint. -Collected weekly raw sewage samples. -Bar screen bin removal and replacement. -Sand filter reject drain line flush. -Daily SCADA review. -TNT Reagent Inventory Confirmation and Reordering. -Reset composite sampler for tomorrow. -Ran RAZ pumps #1 at 100% to clear them out for a bit - all back to auto as well as speed back to auto. -Added two bags of soda ash to each aeration tank. -Decanting STT into the Headworks. -Transferred the sludge and processing. -Clarifier 1 remains isolated, partially drained and put out of service to accommodate the works to be done by contractor. -RAS Pump 3 in manual off and out of service. -RAS pump 2 remains OOS. ————————————————————— • Worked With: Jackie Saunders • Attachments: 0 | 1
12066515 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12066515 | 1899-12-31 | 2025-10-07 13:19 | 2025-10-07 13:17 | Barry Middleton (WW-CEAST) @ Mount Albert Water Resource Recovery Facility - MTSP Date Work Completed: 2025-10-07 13:17 ————————————————————— Weather today Mostly cloudy and 19 Celsius -On site to complete work orders W11273459, W11273557, W11273543, W11273440, W11274063. -Completed station check. -Entered station readings into SharePoint. -Collected weekly raw sewage samples. -Ran RAZ pumps #1 and #3 at 100% to clear them out for a bit - all back to auto as well as speed back to auto. -Batch wasted 20m3 from aeration tank #1 and #2. -Added two bags of soda ash to each aeration tank. -Decanting STT into the Headworks. -Transferred the sludge and processing. -Aeration Blower 3 in manual off due to Failed to Start alarm that came in. -RAS pump 2 remains OOS. ————————————————————— • Worked With: Jackie Saunders • Attachments: 0 | 1
12075522 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12075522 | 1900-01-01 | 2025-10-09 11:15 | 2025-10-09 11:15 | Barry Middleton (WW-CEAST) @ Mount Albert Water Resource Recovery Facility - MTSP Date Work Completed: 2025-10-09 11:15 ————————————————————— Weather today Clear and 10 Celsius -On site to complete work orders W11270527, W11281483, W11283079, W11283066, W11280878, W11281027, W11283329. -Completed station check. -Entered station readings into SharePoint. -Post aeration alum mixing chamber and Ras/Was inlet channel inspection/cleanout. -Dissolved Oxygen meter verification. -Aeration tank blowers 1-2 inspection. -Ran RAZ pumps #1 and #3 at 100% to clear them out for a bit - all back to auto as well as speed back to auto. -Batch wasted 20m3 from aeration tank #1 and #2. -Added two bags of soda ash to each aeration tank. -Decanting STT into the Headworks. -Transferred the sludge and processing. -Aeration Blower 3 in manual off due to Failed to Start alarm that came in. -RAS pump 2 remains OOS. ————————————————————— • Worked With: Kevin Shaji • Attachments: 0 | 1
12078308 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12078308 | 1899-12-31 | 2025-10-10 11:48 | 2025-10-10 11:47 | Barry Middleton (WW-CEAST) @ Mount Albert Water Resource Recovery Facility - MTSP Date Work Completed: 2025-10-10 11:47 ————————————————————— Weather today Partly Cloudy and 14 Celsius -On site to complete work orders W11270527, W11344381, 11280494, 11281956, W11290635, W11286480. -Completed station check. -Entered station readings into SharePoint. -Oak Ridges AMF SCADA training. -Clarifier 1 and 2 maintenance. -Clarifier 1 and 2 condensation draining. -Bar screen bin removal and replacement. -Ran RAZ pumps #1 and #3 at 100% to clear them out for a bit - all back to auto as well as speed back to auto. -Added two bags of soda ash to each aeration tank. -Decanting STT into the Headworks. -Transferred the sludge and processing. -Aeration Blower 3 in manual off due to Failed to Start alarm that came in. -RAS pump 2 remains OOS. ————————————————————— • Attachments: 0 | 1
12071396 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12071396 | 1899-12-31 | 2025-10-08 12:49 | 2025-10-08 12:49 | Barry Middleton (WW-CEAST) @ Mount Albert Water Resource Recovery Facility - MTSP Date Work Completed: 2025-10-08 12:49 ————————————————————— Weather today Clear and 13 Celsius -On site to complete work orders W11349406, W11281161, W11281175, W11280483, W11270527. -SCADA Cybersecurity Training. -Scum Pumps 1-2 inspection. -Was pumps 1-2 inspection -Grit Dewatering Screw press maintenance. -Aeration Blower 3 in manual off due to Failed to Start alarm that came in. -RAS pump 2 remains OOS. ————————————————————— • Attachments: 0 | 1
12063223 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12063223 | 1899-12-31 | 2025-10-06 12:50 | 2025-10-06 12:49 | Barry Middleton (WW-CEAST) @ Mount Albert Water Resource Recovery Facility - MTSP Date Work Completed: 2025-10-06 12:49 ————————————————————— Weather today Clear and 21 Celsius -On site to complete work orders W11270527, W11268751, W11269459, W11270421. -Completed station check. -Entered station readings into SharePoint. -Bar screen bin removal and replacement. -Ran RAZ pumps #1 and #3 at 100% to clear them out for a bit - all back to auto as well as speed back to auto. -Batch wasted 20m3 from aeration tank #1 and #2. -Added two bags of soda ash to each aeration tank. -Decanting STT into the Headworks. -Transferred the sludge and processing. -Aeration Blower 3 in manual off due to Failed to Start alarm that came in. -RAS pump 2 remains OOS. ————————————————————— • Attachments: 0 | 1

## King City SPS
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS

## Schomberg WRRF
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS
12054925 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12054925 | 3 | 2025-10-02 10:51 | 2025-10-02 14:50 | Lauren Swanson (WW-WEST) @ Schomberg Water Resource Recovery Facility - SHSP Date Work Completed: 2025-10-02 14:50 ————————————————————— Decanted sludge thickening tank and transferred remaining sludge to holding tank Completed daily lab and station check - entered data into SharePoint Called ROC to inform of blower and RAS pump PMs being completed today, Inspected vortex blowers and grit blowers - all ok. Inspected aeration blowers 1-4, belts and filters good, oil levels on blowers 2 and 3 good. Changed oil on blowers 1 and 4. Was able to run blower 4 - still triggering a low pressure alarm, leaving in OOS Inspected RAS pumps 1-3. While changing oil on RAS pump 3 water leaking from oil line - created WO. Under direction changed alum dosing setpoints, changed finale pass to aeration alum dose from 95mg/L to 105mg/L Changed clarifier effluent alum dose from 25mg/L to 12mg/L ————————————————————— • Attachments: 0
12119178 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12119178 | 1 | 2025-10-27 09:53 | 2025-10-27 09:48 | Bill Van Bakel (WW-MAINT) @ Schomberg Water Resource Recovery Facility - SHSP Date Work Completed: 2025-10-27 09:48 ————————————————————— On site for aeration blower 1 oil leak. Found a fail input shaft oil seal. Tried tapping it in but very little movement. I topped up the oil and ordered a new seal ————————————————————— • Attachments: 0
12125618 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12125618 | 1 | 2025-10-29 14:59 | 2025-10-29 14:54 | Lauren Swanson (WW-WEST) @ Schomberg Water Resource Recovery Facility - SHSP Date Work Completed: 2025-10-29 14:54 ————————————————————— Decanted sludge thickening tank and transferred remaining sludge to holding tank. Completed daily lab and station check - no new issues. Added data into SharePoint. Made work order for vortex O2 sensor reading high at 23.2% handheld gas monitor reading 20.8. Checked outfall - no issues. Cleaned and verified DO probes. Worked on comprehensive cleaning of blower building. ————————————————————— • Attachments: 0
12127067 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12127067 | 5 | 2025-10-30 11:13 | 2025-10-30 15:10 | Lauren Swanson (WW-WEST) @ Schomberg Water Resource Recovery Facility - SHSP Date Work Completed: 2025-10-30 15:10 ————————————————————— Decanted sludge thickening tank and transferred remaining sludge to holding tank. Completed daily lab and station check - no new issues. - added data into SharePoint. Troubleshooting RAS pump 3 with electricians - placed RAS pump 3 into duty 1 and RAS pump 2 into duty 2 and back up to clarifier 2 to move the scada duty box. Placed RAS pump 1 into manual OOS. continuing it to monitor RAS pump 3 while in duty. Trouble shooting WAS pump 2 with electricians - turned WAS pump 1 into manual off and placed WAS pump 2 into manual on to run instead of pump 1 for wasting. WAS Pump 2 fully cycled with no issues. Placed WAS pump 2 back in Manual OOS and WAS pump 1 back in auto as main WAS pump. ————————————————————— • Attachments: 0

## Black Creek SPS
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS
12119468 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12119468 | 1 | 2025-10-27 13:20 | 2025-10-27 13:12 | Kyle Rae (W-MAINT) @ Vaughan Black Creek Pumping Station - BLSS Date Work Completed: 2025-10-27 13:12 ————————————————————— On site to investigate 120v receptacles on level B4. Receptacle, enclosure and wiring damaged by seepage through wall. B4 receptacle feeder isolated on B3. Receptacles on B4 de-energized until plan for replacements can be implemented. ————————————————————— • Attachments: 0

## Nobleton WRRF
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS
12078731 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12078731 | 1 | 2025-10-11 09:10 | 2025-10-11 08:01 | Daniel Hirstwood (LEADS) @ Nobleton Water Resource Recovery Facility - NBSP Date Work Completed: 2025-10-11 08:01 ————————————————————— Unplugged pumps pumping down aeration tank 2x only for them to plug again under. A minute each time. Level is approx 1ft5inches from bottom. Unplugged pumps. ————————————————————— • Attachments: 0
12115682 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12115682 | 3 | 2025-10-26 09:27 | 2025-10-26 09:24 | Daniel Hirstwood (LEADS) @ Nobleton Water Resource Recovery Facility - NBSP Date Work Completed: 2025-10-26 09:24 ————————————————————— Aeration basin 1 DO was found to be low (sub 0.20mg/L) since Friday Oct 24th at 5:30PM. Increased air flow to side 1 and decreased side 2. Have blowers 1 & 2 running in manual to establish DO. Will allow DO to reach homeostasis before making any more adjustments. Manual DO probe was reading approximately 0.5mg/L higher than online probe. DO currently at 1.72mg/L and climbing. Added 1 bag of soda ash to each aeration basin. ————————————————————— • Attachments: 0
12115694 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12115694 | 6 | 2025-10-26 11:42 | 2025-10-26 11:39 | Daniel Hirstwood (LEADS) @ Nobleton Water Resource Recovery Facility - NBSP Date Work Completed: 2025-10-26 11:39 ————————————————————— Complete small lab due to low do occurrence in aeration basin 1. Final pH: 7.19 @ 17.0 degrees Celsius Final ammonia is unmeasurable with low range kit (too elevated for range). Plant is not nitrifying. Test clarifier 2 for ammonia to determine if aeration tank 2 is nitrifying. Clarifier 2 ammonia is 0.025ppm. Set up 2 submersible pumps in aeration tank 2 to pump into aeration tank 1 to reseed the tank. Also valves RAS from clarifier 2 to aeration 1 (will do this for approx 2hrs). Submersible pumps can remain overnight. DO in tank 1: 2.43mg/L and tank 2: 6.64mg/L. Unsure if the do is balanced or not with valving because oxygen demand is quite high on tank 1 side. Lots of air flow. There could also be some solids imbalances with the aeration inlet gates recently adjusted which may be effecting the oxygen demand. Will reestablish notification before fine tuning solids and air. Notified management on call of issue as well as area supervisor. Also informed ROC to call for any low DO alarms. This is reflected in the SCADA review as well. ————————————————————— • Attachments: 0
12115701 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12115701 | 1 | 2025-10-26 14:54 | 2025-10-26 14:53 | Daniel Hirstwood (LEADS) @ Nobleton Water Resource Recovery Facility - NBSP Date Work Completed: 2025-10-26 14:53 ————————————————————— RAS pumps back into normal flows as of 2:35pm. Submersible pumps continue to run. DO in both basins approximately 2.4mg/L with 2 blowers in manual. ————————————————————— • Attachments: 0
12115738 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12115738 | 4 | 2025-10-26 23:11 | 2025-10-26 23:04 | Daniel Hirstwood (LEADS) @ Nobleton Water Resource Recovery Facility - NBSP Date Work Completed: 2025-10-26 23:04 ————————————————————— Received call from ROC regarding low DO in aeration tank 2. Due to the issues the plant had over the weekend - responded to adjust air (W11393783). On arrival DO levels as follows, Tank 1: 6.11mg/L Tank 2: 1.05mg/L Adjust air valves and tank 2 began to climb again. Tank 2 DO has been trending down all day since this mornings adjustments. 23:13 Tank 1: 5.87mg/L Tank 2: 2.08mg/L Level continues to trend upwards. Unplugged submersible pumps as adequate mixed liquor and sludge should have been transferred to seed tank 1. RAS pump 1 showed no flow earlier in the evening (18:39), switched to pump 2 for tank 1 RAS. ————————————————————— • Attachments: 0

## Kleinburg WRRF
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS
12053493 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12053493 | 1 | 2025-10-01 11:57 | 2025-10-01 11:57 | Young Jung (WW-WEST) @ Kleinburg Water Resource Recovery Facility - KBSPF Date Work Completed: 2025-10-01 11:57 ————————————————————— - Added 16 bags of soda ash into the hopper - Due to aeration tank 1 draining. Alarms were created such as aeration basin 1 solids fault. Shelved various alarms. Shelved two or more RAS pumps not available. Shelved two or more RAS pump not available. Shelved RAS pump 1 and pump 2 E-stop alarm. Aeration basin 1 front DO out of range alarm shelved - Due to dead filter 3 headloss transmitter (WO created) shelved various alarms until it can be resolved. Filter 3 headloss level out of range shelved. Filter 3 headloss level hihi alarm shelved. Filter 3 stage 2 head loss alarm shelved - Performed in-house labs and recorded readings on SharePoint. Numbers are elevated due to draining aeration tank 1 to tank 2. Draining will take couple more days - Checked station and recorded readings on SharePoint. No new additional issues - Enabled RAS batch wasting mode at 9:20. Wasted 20 m^3 from train 2 then reset RAS batch wasting mode once done - Notified ROC of the work being performed - Performed JHSC inspection. No issues. Tested eyewash. Admin bldg eye wash flow high alarm received ————————————————————— • Attachments: 0
12053738 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12053738 | 1 | 2025-10-01 19:05 | 2025-10-01 14:00 | Young Jung (WW-WEST) @ Kleinburg Water Resource Recovery Facility - KBSPF Date Work Completed: 2025-10-01 14:00 ————————————————————— - Finished cleaning generator room - Trojan UV contractor found hydraulic oil leak while performing inspection. Leak coming from hose on UV2 bank A 3rd cassette. Wiper will not function for the 3rd cassette due to hydraulic hose being unattached. Will order new parts - Unplugged filter 3 north side - Checked ordour control unit. No issues - Instrumentation fixed filter 3 headloss transmitter. Filter 3 headloss level out of range in shelved. Filter 3 headloss level hihi alarm unshelved. Filter 3 stage 2 head loss alarm unshelved ————————————————————— • Attachments: 0
12053742 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12053742 | 1 | 2025-10-01 20:01 | 2025-10-01 19:58 | Young Jung (WW-WEST) @ Kleinburg Water Resource Recovery Facility - KBSPF Date Work Completed: 2025-10-01 19:58 ————————————————————— - Test ran generator 1 and 2 starting from 16:26 to test UV function during generator test - Placed UV 1 and 2 into local on - Known issue but testing again to confirm. Testing revealed that after ATS power transfer for generator 1, generator 1 will shut off UV1 because generator 1 powers UV1. After ATS power transfer for generator 2, generator 2 will shut off UV2 because generator 2 powers UV2. - Due to this, during power transfers or monthly generator test, if testing generator 1, UV 2 should be running in duty to prevent UV1 from shutting off. The reverse for generator 2, for generator 2, UV1 should be running in duty to prevent UV2 from shutting off. This will ensure UV dosage is applied at all times. Notified team, supervisor and TL. - In addition, during power transfers UV channel 2 Bank A tends to fault due to power loss, causing "UV channel 2 Bank A power loss fault alarm". This tends to happen more frequently with generator 2 ATS. Will create a work order to address power loss fault for UV2 Bank A - Due to this work, multiple UV and process alarms were created. Such as, UV channel 2 bank 1a power loss fault, sec clarifier 1 and 2 overload alarm, soda ash conveyor e stop alarm, uv channel 2 bank 1a major alarm, uv channel 2 common major alarm, uv system 2 warning alarm, Site hydro power failure alarm, aut transfer switch e pow, mechanical screen lockout alarm, disel gen run alarm, mechanical screen gen alarm. Cleared all alarms and checked duties. - UV dosage was applied at all times and when testing suspected UV channel that was likely to shut off, adjusted the inlet sluice gate to close - Received call from ROC about influent channel 1 and 2 hitting hihi alarm. This is due to the higher flows coming in in addition to aeration tank 1 draining into aeration tank 2. Due to this, Placed filter 2 sluice gate to manual open and set filter 2 to run over night to prevent filters from opening and closing to catch up to higher influent channel level. - Will continue to monitor filter inlet channel and run more filters if it rises. ————————————————————— • Attachments: 0
12053740 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12053740 | 1 | 2025-10-01 19:19 | 2025-10-01 18:30 | Young Jung (WW-WEST) @ Kleinburg Water Resource Recovery Facility - KBSPF Date Work Completed: 2025-10-01 18:30 ————————————————————— Trojan contractor was servicing UV Channel 2 Bank A and B for semiannual maintenance, and replaced the low level probe. The new probe was placed in but it ended up causing low level fault and level signal fault on UV2. He determined that it was the relay not functioning properly and not sending the signal back to the HMI. He tested this theory by removing the probe and trying to trigger a low level fault, which did not show alarms on HMI. He went further later on and wanted to test UV2's relay by using UV1's relay. Contractor removed the relays from UV1 bank a and b while UV1 was active, in duty 1 and running. Hence, UV1 shut off immediately due to the relay being removed and triggered a low level fault on UV1 and no UV was dosed from 15:12 ~ 15:13 with average flow of 12.5 L/s. Roughly 0.75 m^3 of final effluent was bypassed. The bypass could not be contained due to the large volume moving through and no clean up was needed. Followed bypass/spill procedure and collected composite samples at 15:15 (W11331830) Notified supervisor, Tara Magee at 16:00. Sunny day with no rain. Visually checked final effluent channel and humber river and found no abnormalities. Took photos and sent it to supervisor. Notified SAC, Elaine gold; 1-PKUITJ at 18:00. Notified MOH, Mathilda Habib; 4237216 at 18:12. Notified lake simcoe conservation authority at 18:32 via email. ————————————————————— • Attachments: 0
12054957 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12054957 | 10 | 2025-10-02 11:38 | 2025-10-02 11:36 | Lance Johnson (LEADS) @ Kleinburg Water Resource Recovery Facility - KBSPF Date Work Completed: 2025-10-02 11:36 ————————————————————— De-ragged pumps in aeration tank 1, lowered and restarted pumping to tank 2. Collected samples for labs. Noted really low solids in aeration tank. Adjusted RAS/WAS valving so both RAS systems are discreet and functioning normally. Changed valving at head of aeration tanks so clarifier 1 RAS is deposited in the inlet channel, rather than into the aeration tank. Set all 4 RAS pumps to run to help transfer solids for approximately 20 minutes. Completed labs and entered numbers in spreadsheet. Numbers were a little unusual based on all of the above information. Closed air valves 3 and 4 on aeration tank 2 by two notches to direct more air to the tank inlet to better manage returning solids. Placed DO and SS probes from aeration tank 2 in buckets of water to keep moist and protect from direct sunlight. Wasted 40 m3 from clarifier 1. Lowered supernate valve on sludge tank 1 to return 10 m3 back to the process. Raised valve when complete. Set RAS pumps 2 and 4 in auto, auto speed, flow control, flow set at 15 l/sec. This is normal operation. All RAS/WAS basement valves in correct/normal positions. RAS P2 discharging into the inlet, which feeds tank 2. Hosed algae and 'crud' off of level floats in filters. This caused filter 2 airlift to stop lifting. Returned filter 2 to auto. Set filter 2 to duty 5 (out of service) as it requires some weir plates to function satisfactorily. Changed duty 2 filter stop flow from 18 l/sec to 10 l/sec to better reflect influent flow rates and filter needs. Should reduce unnecessary starting and stopping of duty 2. Added 15 bags soda ash to ash hopper. De-ragged pumps in aeration tank and lowered at end of day. ————————————————————— • Attachments: 0
12095484 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12095484 | 1 | 2025-10-16 11:50 | 2025-10-16 11:48 | Lance Johnson (LEADS) @ Kleinburg Water Resource Recovery Facility - KBSPF Date Work Completed: 2025-10-16 11:48 ————————————————————— Inspected tertiary building sump. ROC received high level alarm. Inspected headworks building PS. ROC received high level alarm. Inspected final effluent sampler. All okay. Inspected raw sewage sampler. All okay. Cleaned UV/FE channel. ————————————————————— • Attachments: 0
12095484 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12095484 | 1 | 2025-10-16 11:50 | 2025-10-16 11:48 | Lance Johnson (LEADS) @ Kleinburg Water Resource Recovery Facility - KBSPF Date Work Completed: 2025-10-16 11:48 ————————————————————— Inspected tertiary building sump. ROC received high level alarm. Inspected headworks building PS. ROC received high level alarm. Inspected final effluent sampler. All okay. Inspected raw sewage sampler. All okay. Cleaned UV/FE channel. ————————————————————— • Attachments: 0
12119308 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12119308 | 1 | 2025-10-27 10:57 | 2025-10-27 10:56 | Bill Van Bakel (WW-MAINT) @ Kleinburg Water Resource Recovery Facility - KBSPF Date Work Completed: 2025-10-27 10:56 ————————————————————— On site for sump pump 2 alarms. I will order a new pump and return with the small crane ————————————————————— • Attachments: 0

## Humber SPS
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS
12119919 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12119919 | 1 | 2025-10-27 21:33 | 2025-10-27 21:31 | Daniel Hirstwood (LEADS) @ Vaughan Humber Pumping Station - HMSS Date Work Completed: 2025-10-27 21:31 ————————————————————— Contacted by ROC for mechanical screen 2 fault. Arrived and found screen to faulted with an interlock as well. Motor overload indicator on. Visually inspected top sprockets and looked down at flight and chains - no obvious issues . Attempted to reset the screen and it immediately tripped again as soon as the motor engaged. Attempted to run in reverse with the same result. Create follow up cmu and notify maintenance team lead. ————————————————————— • Work Order(s): =12119872 • Attachments: 0
12122357 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12122357 | 1 | 2025-10-28 14:11 | 2025-10-28 14:06 | Christian Streef (WW-MAINT) @ Vaughan Humber Pumping Station - HMSS Date Work Completed: 2025-10-28 14:06 ————————————————————— On site for barscreen #2 OOS. Found barscreen jamming up. All chains sprockets and motor break in working order. Will need to pump down channel to see if any foreign objects are jammed into the rake at bottom of the barscreen. ————————————————————— • Worked With: Terry Cantwell • Attachments: 0
12125405 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12125405 | 3 | 2025-10-29 11:27 | 2025-10-29 11:14 | Lance Johnson (LEADS) @ Vaughan Humber Pumping Station - HMSS Date Work Completed: 2025-10-29 11:14 ————————————————————— On site to assist maintenance with barscreen 2 repair. Checked screen. Found no real issues. Closed wetwell interconnect valve. Set wetwell 2 out of service. Pumped wetwell 2 down below bar screen channel. Inspected actual screen down in the channel and found it full of wheels, concrete and asphalt. Removed 'junk' from in the screen in channel and the channel itself. Tested screen, which seemed to work successfully. Opened interconnect valve. Set wetwell 2 back in service on SCADA. Opened inlet valve for screen 2. Monitored screen. Worked well. All returned to normal. Put empty bins back inside. ————————————————————— • Attachments: 0
12125591 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12125591 | 1 | 2025-10-29 14:22 | 2025-10-29 14:20 | Christian Streef (WW-MAINT) @ Vaughan Humber Pumping Station - HMSS Date Work Completed: 2025-10-29 14:20 ————————————————————— On site for barscreen #2 jammed. Found barscreen jamming up with metal and asphalt. Cleared foreign materials, ran tested barscreen and put back into service. ————————————————————— • Worked With: Martin deVries • Attachments: 0

## Pine Valley
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS

## Joe Dales SPS
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS | 1

## Keswick WRRF
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS

## Sutton WRRF
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS
12063115 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12063115 | 1900-01-04 | 2025-10-06 10:46 | 2025-10-06 10:44 | Chris Colangelo (WW-NORTH) @ Sutton Water Resource Recovery Facility - SUSP Date Work Completed: 2025-10-06 10:44 ————————————————————— Onsite for daily operations Review scada/trends Gfl onsite to begin tank 1 maintenance Maintenance onsite to remove 6” pump and remove the generator. Remove hydraulic pumps from sbr1 Plug in 2 submersible pumps feeding eq tank to help lower sbr level. Turn on WAS pump in SBR 1 to help lower level - feeding SHT Place all four UV banks in local off causing major/critical alarms. EQ tank being diverted to lagoon Place SHT blowers in manual off to decant holding tank tomorrow Collect SBR2 decant sample during decant cycle Collect MLSS during first air cycle ————————————————————— • Attachments: 0 | 1
12102596 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12102596 | 1 | 2025-10-20 14:22 | 2025-10-20 07:45 | Darren Boddy (WW-NORTH) @ Sutton Water Resource Recovery Facility - SUSP Date Work Completed: 2025-10-20 07:45 ————————————————————— sludge handling. Load out station checks lab and reading stopped feeding lagoons after warming up UV's at 1040hrs. Plant now going through filters. Pulled and fixed air lift ( 1- f2 ) found 5 leaks on diffusers for SBR1. placed 2 submersibles in tank to pump down . hydraulic pump wouldn't start, maintenance replaced battery. screen brush put back in service. ————————————————————— • Attachments: 0