## Operational Issues
PERSONGROUP | LOGBOOK_MONTH | LDTEXT | DESCRIPTION | EVENTDATE
WW-NORTH | November | Decant sludge tanks 2&3 | Keswick Water Resource Recovery Facility | 2025-11-09
WW-NORTH | November | Continue decanting Transfer sludge tanks Add 10 bags of soda ash Review area SCADA Rake bar screen | Keswick Water Resource Recovery Facility | 2025-11-09
WW-NORTH | November | Open feed to WAS to sludge tank 1 Close feed to to 3 Review area SCADA Keswick sewage pumping station pump to low flow run a few times at 100% to try and clear low flow alarm | Keswick Water Resource Recovery Facility | 2025-11-08
WW-NORTH | November | Performed facility station check Completed Lab analysis: Data in Sharepoint Decanted Sludge holding tanks: 1, 2 & 3 Transferred Sludge holding tanks: 1 & 3 Inspected headworks: leveled grit bin and raked bar screen Added 10 bags of soda ash Completed monthly PM work orders: -Membrane Building, Containment Float Switches 1-6, Test -RAS/WAS Sump pumps inspection -WAS pumps 1-4 inspection Adjusted Alum pump 5 speed setpoint: 4 % -> 3% -RAS/WAS hoist inspection | Keswick Water Resource Recovery Facility | 2025-11-07
WW-NORTH | November | Performed station check Completed lab analysis and entered readings into SharePoint Decanted and transferred STT 1 Batch wasted 80m3 Checked head works - cleared bar screen and checked bin Received soda ash and hypo delivery Checked air compressors | Keswick Water Resource Recovery Facility | 2025-11-10
WW-NORTH | November | Performed facility station check Completed Lab analysis: Data in Sharepoint Decanted Sludge holding tanks: 1, 2 & 3 Transferred Sludge holding tanks: 1 & 3 Batch Wasted Inspected headworks: leveled grit bin and raked bar screen Added 10 bags of soda ash Recorded Odor Control Unit numbers Completed weekly PM Work order: -Membrane TSS probe maintenance Completed monthly PM work orders: -Membrane 2 tonne hoist inspection -Membrane 5 tonne hoist inspection | Keswick Water Resource Recovery Facility | 2025-11-06
WW-NORTH | November | ROC called for intensity alarm on UV channel 2 Rotated to channel 1 and will further look into the intensity readings | Keswick Water Resource Recovery Facility | 2025-11-10
WW-NORTH | November | Performed facility station check Completed Lab analysis: Data in Sharepoint Decanted Sludge holding tanks: 2 & 3 Transferred Sludge holding tank: 3 Batch Wasted into holding tank 1 Inspected headworks: leveled grit bin and raked bar screen Added 10 bags of soda ash Cleaned membrane turbidimeters: 1-5 Train 3 turbidimeter faulted last night on OOR again and began reading a negative value; within the hour the instrument began reading correctly. Replaced vial, also disconnected and reconnected data cable connection, suspecting a lose connection was causing the OOR alarm and reading a negative number. Will continue to monitor and continue troubleshooting if alarm comes in again. Completed weekly PM Work order: -Alum chemical panel valve exercise | Keswick Water Resource Recovery Facility | 2025-11-05
WW-NORTH | November | Started decanting STT 2 and 3 Switched WAS flow from STT 1 to STT 2 transferred STT 2 and 3 added 10 bags of soda ash | Keswick Water Resource Recovery Facility | 2025-11-02
WW-NORTH | November | On site to check on micro screen. Screen 1 running but inlet gate open and outlet gate close. Screen 2 both gates open but not running. Put outlet gate in hand and opened went to 99 %. Opened manually to open position and put in auto screen 2 gates closed all seems ok | Keswick Water Resource Recovery Facility | 2025-11-02
WW-NORTH | November | Performed facility station check Completed Lab analysis: Data in Sharepoint Decanted Sludge holding tanks: 1 & 2 Transferred Sludge holding tank: 1 Recorded Odor Control Unit numbers Inspected headworks: leveled grit bin and raked bar screen Added 10 bags of soda ash Received Alum delivery | Keswick Water Resource Recovery Facility | 2025-11-03
WW-NORTH | November | Performed facility station check Completed Lab analysis: Data in Sharepoint Collected Weekly Samples: Sewage (W11343583) Collected Monthly Samples: Alkalinity (W11343569) and Sludge (W11343194) Decanted Sludge holding tanks: 2 & 3 Transferred Sludge holding tank: 2 Inspected headworks: leveled grit bin and raked bar screen Added 10 bags of Soda Ash Rotated headworks screening channel duty Duty 1 = Channel 2 Duty 2 = Channel 1 Hot water tank OOS- Notified property services | Keswick Water Resource Recovery Facility | 2025-11-04
WW-NORTH | November | Performed station check Completed lab analysis and entered readings into SharePoint Decanted STT 2 and 3 Transferred STT 2 Batch wasted 90m3 Checked head works - cleared bar screen and checked bin Cleaned up rags around aeration pumps Programmed recovery clean on membrane train 3 Continued to pump down clarifier #2 | Keswick Water Resource Recovery Facility | 2025-11-20
WW-NORTH | November | On site to repair smoke alarm in generator building. Repaired. Tested. Ok. | Keswick Water Resource Recovery Facility | 2025-11-24
WW-NORTH | November | Plumbed seal water for Vortex 1 with solenoid valve. | Keswick Water Resource Recovery Facility | 2025-11-25
WW-NORTH | November | Onsite for sludge handling Begin Decanting stt 2 and 3 Out for sutton Back onsite Raise slip tubes to 100% Switch was feed to stt 3 | Keswick Water Resource Recovery Facility | 2025-11-30
WW-NORTH | November | Onsite to repair vortex seal water | Keswick Water Resource Recovery Facility | 2025-11-28
WW-NORTH | November | Performed station check Completed lab analysis and entered readings into SharePoint Decanted STT 2 and 3 Transferred STT 3 Programmed recovery clean on trains Received load of hypo Checked head works - cleared bar screen and checked bin | Keswick Water Resource Recovery Facility | 2025-11-21
WW-NORTH | November | Started decanting S.T.T's 2 and 3 Finished decanting and started transfers Switched WAS feed to S.T.T 3 | Keswick Water Resource Recovery Facility | 2025-11-23
WW-NORTH | November | Performed station check Completed lab analysis and entered readings into SharePoint Decanted and transferred STT 1 Checked head works - cleared bar screen and checked bin Recorded OCU readings Cleaned and flushed composite sampler lines Topped up temporary hypo tank | Keswick Water Resource Recovery Facility | 2025-11-24
WW-NORTH | November | sludge handling. Batch waste into STT1. Decanted and transferred STT3, now feeding WAS to STT3. lab and readings station checks sharepoint data entry | Keswick Water Resource Recovery Facility | 2025-11-27
WW-NORTH | November | Switch WAS feed from stt 2 to stt 1 | Keswick Water Resource Recovery Facility | 2025-11-29
WW-NORTH | November | Investigate hypo leak, tightened flange bolts leak tested with water. Flange still has leak. Drain water from tank and remove tank bulk head to investigate further. Removed bulk head new gasket and hardware required. Hypo tank OOS until repair is completed | Keswick Water Resource Recovery Facility | 2025-11-24
WW-NORTH | November | Performed station check Decanted and transferred STT 2 Completed lab analysis and entered readings into SharePoint Checked head works - cleared bar screen and levelled bin Topped up temporary hypo tank Programmed recovery clean on trains 2, 3, 4 | Keswick Water Resource Recovery Facility | 2025-11-28
WW-NORTH | November | Performed station check Completed lab analysis and entered readings into SharePoint Decanted STT 2 and 3 Transferred STT 3 Collected weekly samples (W11398856) Checked head works - cleared bar screen and levelled bin Drained and hosed membrane trains 1-4 | Keswick Water Resource Recovery Facility | 2025-11-25
WW-NORTH | November | Performed station check Completed lab analysis and entered readings into SharePoint Checked head works - cleared bar screen and levelled bin Decanted and transferred STT 2 Batch wasted in STT 3 Inspected and cleaned TSS probe | Keswick Water Resource Recovery Facility | 2025-11-26
WW-NORTH | November | Performed station check Decanted and transferred STT 1 and 3 Completed lab analysis and entered readings into SharePoint Checked headworks - cleared bar screen and check bin Programmed recovery clean on membrane train 5 Completed assigned EZMax work orders: - Tested gas detectors - Hypo metering pump inspection - Alum Chemical panel exercise - TSS probe inspection - UV unit rotation - Grit Vortex Dewatering Press inspection - Screening press 1, 2 inspections - Dewatering press 1, 2 inspection - Collection box blowers inspection - Travelling screen 1, 2 inspections - Headworks basement sump system inspection | Keswick Water Resource Recovery Facility | 2025-11-19
WW-NORTH | November | Performed station check Completed lab analysis and entered readings into SharePoint Decanted and transferred STT 1 and 2 Checked headworks - cleared bar screen and check bin Hypo Tank leaked into containment - Pumped Hypo tank into temporary tank - Installed temporary suction line on hypo pump 2 which feeds from temporary tank. | Keswick Water Resource Recovery Facility | 2025-11-11
WW-NORTH | November | On site to gather information for sodium hypo tank fitting. Found tank manufacturer and serial number for the tank. Contacted manufacturer and they will respond with availability of parts once I send follow-up photos of parts. | Keswick Water Resource Recovery Facility | 2025-11-27
WW-NORTH | November | Turned off master alarm switch for Odour control O2 alarms until unit is repaired | Keswick Water Resource Recovery Facility | 2025-11-13
WW-NORTH | November | in at 0750hrs. started sludge handling. out to sutton at 0810hrs back from sutton 0925hrs. decanted and transferred STT2, now feeding WAS to STT2. 10 bags of soda ash into Aeration channel. | Keswick Water Resource Recovery Facility | 2025-11-16
WW-NORTH | November | Onsite to spec out water solenoid for vortex seal water drain line. Parts to be ordered | Keswick Water Resource Recovery Facility | 2025-11-17
WW-NORTH | November | Began lab analysis, collected floc, final, and aeration samples to run relevant tests Completed lab analysis, Inputted lab results into SharePoint Switched sludge thickening tank 1 to local run then shut off when transfer/decant was complete Washed debris off membrane 3 Added soda ash bags in headworks | Keswick Water Resource Recovery Facility | 2025-11-13
WW-NORTH | November | Programmed heated hypo recovery cleans on Trains 1,2 and 4 Disabled Hi level alarm for scum tanks 1 and 2, left HiHi level alarm enabled | Keswick Water Resource Recovery Facility | 2025-11-14
WW-NORTH | November | Performed station check Decanted and transferred STT 1 and 3 Completed lab analysis and entered readings into SharePoint Added 10 bags of soda ash -set up 10 bags to be added on Sunday Checked headworks - cleared bar screen and checked bin Topped up caustic tank with 4 jugs Filled temporary hypo tank up to 1200L Completed assigned EZMax work orders: - Permeate Turbidimeter 1-5 maintenance - Back pulse pump inspections 1&2 - Effluent pump inspections 1&2 - CIP sump inspection - Membrane tanks 1-5 actuator blow down - Recirc pumps inspection 1&2 - Outfall gates inspections - UV gates inspections | Keswick Water Resource Recovery Facility | 2025-11-14
WW-NORTH | November | Performed station check Decanted/transferred sludge thickening tanks Fed tank 3 until full, then directed WAS to tank 2 Completed lab and entered readings into ACE sheet Collected weekly samples and delivered to Newmarket Completed scheduled work orders and notified ROC of work being completed Inspected sludge blowers Inspected channel aeration blowers Inspected sludge transfer pumps Inspected aeration blowers. | Keswick Water Resource Recovery Facility | 2025-11-18
WW-NORTH | November | Performed station check Completed lab analysis and entered readings into SharePoint Decanted and transferred STT 1 and 3 Batch wasted 80m3 Admin building and OCU sump inspections Supernate pump inspections | Keswick Water Resource Recovery Facility | 2025-11-17
WW-NORTH | November | Performed station check Completed lab analysis and entered readings into SharePoint Decanted and transferred STT 1 and 3 Batch wasted 80m3 Added 10 bags of soda ash in headworks Performed UV System and Hydraulic 1 and 2 maintenance Finished pumping hypo tank into temporary tank Pumped out hypo containment | Keswick Water Resource Recovery Facility | 2025-11-12
WW-NORTH | November | Onsite to measure lagoons Enter data in sharepoint | Holland Landing Lagoons | 2025-11-03
WW-NORTH | November | Attended for site check Recorded cell levels in rounds sheet. | Holland Landing Lagoons | 2025-11-24
WW-NORTH | November | Attended for site check Recorded cell levels in rounds sheet. | Holland Landing Lagoons | 2025-11-20
WW-NORTH | November | Checked lagoons Completed H+S inspection Entered levels in SharePoint | Holland Landing Lagoons | 2025-11-13
WW-NORTH | November | Onsite to check station Review scada/trends Enter data in sharepoint | Holland Landing Sewage Pumping Station | 2025-11-06
WW-NORTH | November | On site for check valve PMs. Found #3 to have low pressure. Topped it up to 110 psi. Grease all 3 and found no other issues | Holland Landing Sewage Pumping Station | 2025-11-07
WW-NORTH | November | Attended for station check Recorded station readings in rounds sheet Checked diesel containment pits Reviewed SCADA/trends Completed scheduled work orders and notified ROC of work being completed Performed standby generator test run and recorded readings in rounds sheet Start: 275.0 h Stop: 276.3 h Run time: 1.3 h Performed H&S inspection Inspected hoist Inspected OCU Performed dry well inspection Tested dry well flood alarm - in @ 9:38 Inspected sump pit and tested high level alarm - in @ 9:47 Inspected sewage pumps and ran @ 100% p.1: 81 L/s p.2: 78 L/s p.3: 71 L/s Inspected check valves - topped up p.3 check valve air pressure Inspected and exercised surge valves Tested dialer - received by ROC Tested diesel containment flood alarm for day tank - in @ 10:35 Checked for hazardous waste - none. | Holland Landing Sewage Pumping Station | 2025-11-10
WW-NORTH | November | Onsite to check station Review scada/trends Enter data in sharepoint Outstanding diesel containment flood from weekend. Vacuum out both diesel containments - one by bulk tanks was the issue Clear alarm | Holland Landing Sewage Pumping Station | 2025-11-03
WW-NORTH | November | Attended for station check Recorded station readings in rounds sheet Checked dry well - p.2 running in duty Reviewed SCADA/trends. | Holland Landing Sewage Pumping Station | 2025-11-20
WW-NORTH | November | On site for pump test with ASL Jeff Johnson Run pumped 1,2 and 3. Pumps starting at 100% 60 Hz then slows down to 85% 65.6 Hz Station back in auto | Holland Landing Sewage Pumping Station | 2025-11-26
WW-NORTH | November | Attended for station check Recorded station readings in rounds sheet Checked dry well - p.1 running in duty Dropped off inspected SRLs Reviewed SCADA/trends. | Holland Landing Sewage Pumping Station | 2025-11-27
WW-NORTH | November | Attended for station check Recorded station/monthly meter readings in rounds sheet Checked dry well - p.3 running in duty Checked diesel containment pits Picked up SRLs for inspection Reviewed SCADA/trends. | Holland Landing Sewage Pumping Station | 2025-11-24
WW-NORTH | November | On site for check valve 3 pressure leak. Found no external leaks so I will order a new cylinder | Holland Landing Sewage Pumping Station | 2025-11-21
WW-NORTH | November | Attended for station check Recorded station readings in rounds sheet Checked dry well - p.3 running in duty Checked diesel containment pits Cleaned washroom Reviewed SCADA/trends. | Holland Landing Sewage Pumping Station | 2025-11-17
WW-NORTH | November | Checked station Viewed HMI and trends Checked dry well area Ran all pumps @ 100% P1 - 80.5 L/s P2 - 79.6 L/s P3 - 71 L/s Recorded readings in SharePoint | Holland Landing Sewage Pumping Station | 2025-11-13
WW-NORTH | November | Onsite to check station Review scada/trends Enter data in sharepoint | East Gwillimbury 2nd Concession Sewage Pumping Station | 2025-11-06
WW-NORTH | November | Attended for station check Recorded station readings in rounds sheet Checked dry well - p.2 running in duty Checked diesel containment pits Reviewed SCADA/trends. | East Gwillimbury 2nd Concession Sewage Pumping Station | 2025-11-10
WW-NORTH | November | Onsite for wetwell clean with wessuc Alert roc Upon arrival duty active Throttle pump discharge valves to 70% Disable recirc loop - change normal mode pump speed from 60% to 100% Change controlling LIT from LIT 2 to 4 Enable low low level lockout for wetwell 1 Pump down wetwell 1 to .32m Wessuc complete wetwell 1 Enter wetwell and isolate wetwell 2 Bleed air on pump 2 - enable low low pevel lockout wetwell 1 Change controlling lit from 4 to 2 Pump down wetwell 2 to .80m Wessuc complete wetwell 2 Enter wetwell, open all gate valves Wetwells EQ?d, level at 2.67m Bleed air from pump 3 Discharge valves back to 100% open Re enable recirc loop and return station back to normal operation | East Gwillimbury 2nd Concession Sewage Pumping Station | 2025-11-04
WW-NORTH | November | Onsite to check station Review scada/trends Enter data in sharepoint Diesel containment | East Gwillimbury 2nd Concession Sewage Pumping Station | 2025-11-03
WW-NORTH | November | Took vibration readings on pump 2. | East Gwillimbury 2nd Concession Sewage Pumping Station | 2025-11-20
WW-NORTH | November | On site to replace diesel generator block heater. Replaced. Tested ok. Ran diesel generator in hand. Ok. Scad Alarms cleared and diesel back in Auto. | East Gwillimbury 2nd Concession Sewage Pumping Station | 2025-11-26
WW-NORTH | November | Attended for station check Recorded station readings in rounds sheet Checked dry well - p.2 running in duty Dropped off inspected SRLs Cleaned washroom and replaced emergency eyewash solution Building cannot be armed manually (does auto arm) Reviewed SCADA/trends. | East Gwillimbury 2nd Concession Sewage Pumping Station | 2025-11-27
WW-NORTH | November | Attended for station check Recorded station readings in rounds sheet Checked dry well - p.2 running in duty Reviewed SCADA/trends. | East Gwillimbury 2nd Concession Sewage Pumping Station | 2025-11-20
WW-NORTH | November | Checked station Viewed HMI and trends Checked dry well area Recorded readings in SharePoint | East Gwillimbury 2nd Concession Sewage Pumping Station | 2025-11-13
WW-NORTH | November | Attended for station check Recorded station/monthly meter readings in rounds sheet Checked dry well - p.2 running in duty Checked diesel containment pits Picked up SRL for inspection Took OCU grease filter to Newmarket for cleaning and returned to site Reviewed SCADA/trends. | East Gwillimbury 2nd Concession Sewage Pumping Station | 2025-11-24
WW-NORTH | November | Attended for scheduled work orders Notified ROC of work being completed Performed standby generator test run and recorded readings in rounds sheet Start: 237.2 h Stop: 238.3 h Run time: 1.1 h Generator coolant recirculation pump awaiting replacement Tested diesel containment flood alarm for day tank - in @ 9:48 Performed H&S inspection Inspected hoist - working Inspected OCU Inspected recirculation loop actuated valves Performed dry well inspection Tested dry well flood alarm - in @ 10:28 Inspected sump pit and tested high level alarm - in @ 10:40 Inspected sewage pumps Inspected check valves Exercised dry well surge valves Flushed air relief valve Tested dialer - received by ROC Checked for hazardous waste - none. | East Gwillimbury 2nd Concession Sewage Pumping Station | 2025-11-12
WW-NORTH | November | Attended for station check Recorded station readings in rounds sheet Checked dry well - p.3 running in duty Checked diesel containment pits - removed water from bulk tank sump pit Reviewed SCADA/trends. | East Gwillimbury 2nd Concession Sewage Pumping Station | 2025-11-17
WW-NORTH | November | On site for the sump pump hi alarm. Relocated the first float so it won?t hang up with the other floats found the second and third float are not floating. I will have a electrician replace them | Queensville West Sewage Pumping Station | 2025-11-07
WW-NORTH | November | Attended for station check Recorded station readings in rounds sheet Checked dry well - p.3 running in duty Checked diesel containment pits Reviewed SCADA/trends. | Queensville West Sewage Pumping Station | 2025-11-10
WW-NORTH | November | Onsite to clean wetwell with wessuc Alert roc Place both wetwells in pac mode Switch controlling lit from 3 to 1 Disable low low level lockout on wetwell 2 Enter wetwell and isolate wetwell 2 inlet gate and interconnect Place both sumps in local off Pump wetwell2 to .86m Check station review scada/trends Enter data in sharepoint Wessuc done wetwell2 Enter wetwell, open wetwell 2 and isolate wetwell 1 Pump down wetwell 1 to .88m, low low level lockout disabled ww1. Switch controlling lit back to lit3 Bleed p3 and ensure flow readings Wessuc complete wetwell1 Enter wetwell and open wetwell1 inlet gate and EQ valve Bleed air on p2 - ensure flow and normal operation. Sumps back in auto Alert roc work complete | Queensville West Sewage Pumping Station | 2025-11-06
WW-NORTH | November | Onsite to check station Review scada/trends Enter data in sharepoint Diesel containment | Queensville West Sewage Pumping Station | 2025-11-03
WW-NORTH | November | Attended for inlet level high switch alarm Tried to run grinder which had been off, but received overload alarm Grinder is off. | Queensville West Sewage Pumping Station | 2025-11-19
WW-NORTH | November | Attended for station check Recorded station readings in rounds sheet Checked dry well - p.2 running in duty Dropped off inspected SRLs? Cleaned washrooms Reviewed SCADA/trends - channel grinder OOS. | Queensville West Sewage Pumping Station | 2025-11-27
WW-NORTH | November | Attended for scheduled work orders Notified ROC of work being completed Performed H&S inspection Exercised forcemain 2 actuated valve Inspected OCU Inspected hoist Performed dry well inspection Tested dry well flood alarm - in @ 9:19 Inspected sump pit and tested flood alarm - in @ 9:31 Inspected sewage pumps and recorded flows @ 100% p.2: 72 L/s p.3: 65 L/s Inspected check valves Flushed air relief valve Exercised dry well valves Tested dialer - received by ROC Checked for hazardous waste - none. | Queensville West Sewage Pumping Station | 2025-11-11
WW-NORTH | November | Attended for station check Recorded station readings in rounds sheet Checked dry well - p.3 running in duty Channel grinder OOS Reviewed SCADA/trends. | Queensville West Sewage Pumping Station | 2025-11-20
WW-NORTH | November | Attended for station check Recorded station/monthly meter readings in rounds sheet Checked dry well - p.2 running in duty Checked diesel containment pits Picked up SRL for inspection Reviewed SCADA/trends - channel grinder OOS. | Queensville West Sewage Pumping Station | 2025-11-24
WW-NORTH | November | Attended for station check Recorded station readings in rounds sheet Checked dry well - p.2 running in duty Checked diesel containment pits Notified ROC of work being completed Performed standby generator test run and recorded readings in rounds sheet Start: 185.8 h Stop: 186.9 h Run time: 1.1 h Received channel grinder fault on high amperage - ran briefly in reverse and returned to auto but it faulted again, left grinder off on panel as there is a loud noise that can be heard upstairs when grinder runs Reviewed SCADA/trends. | Queensville West Sewage Pumping Station | 2025-11-17
WW-NORTH | November | Checked station Viewed HMI and trends Checked dry well area Recorded readings in SharePoint | Queensville West Sewage Pumping Station | 2025-11-13
WW-NORTH | November | station checks sharepoint data entry flushed blowdown | Morton Avenue Air Management Facility | 2025-11-06
WW-NORTH | November | Checked station Flushed blowdown Completed H+S inspection Checked fan room Recorded readings in SharePoint | Morton Avenue Air Management Facility | 2025-11-10
WW-NORTH | November | On site to troubleshoot Biofilter Exhaust fan #1. | Morton Avenue Air Management Facility | 2025-11-10
WW-NORTH | November | On site for blower 1 fault. Ran it for 20 m with no issues and then it fault on over current. We will order a replacement motor | Morton Avenue Air Management Facility | 2025-11-03
WW-NORTH | November | on site responding to Blower #1 tripping. Maintenance on site. Troubleshooting , found motor to be issue. Blower #2 left in duty 1. | Morton Avenue Air Management Facility | 2025-11-03
WW-NORTH | November | station checks sharepoint data entry blower #1 now duty 1 flushed blowdown. back at 1154hrs. Blower #1 tripped . Reset at Mcc and scada. checked blower operation, appears normal. | Morton Avenue Air Management Facility | 2025-11-03
WW-NORTH | November | Checked station Viewed HMI and trends Checked fan room Flushed blowdown Drained outside media tank | Morton Avenue Air Management Facility | 2025-11-20
WW-NORTH | November | Checked station Viewed HMI and trends Flushed blowdown Checked fan room | Morton Avenue Air Management Facility | 2025-11-24
WW-NORTH | November | station checks sharepoint data entry flushed blowdown | Morton Avenue Air Management Facility | 2025-11-13
WW-NORTH | November | Onsite to check station Review scada Enter data in sharepoint Flush blowdown | Morton Avenue Air Management Facility | 2025-11-17
WW-NORTH | November | Onsite for daily operations Review scada/trends Collect in house lab samples No decant due to low stt Complete lab Enter data in sharepoint Check station Filters ok. Run rag auger in manual - plugged. Pull apart rag press and clear blockage. Return to normal operations and running properly in auto Hose down barscreen area Increased Wasting on both SBR?s from 60s to 120s. | Sutton Water Resource Recovery Facility | 2025-11-07
WW-NORTH | November | Put WAS pumps one and two back in Auto WAS 1 500sec down to 60sec WAS 2 200sec down to 60sec UV channel 1A back in duty 1 | Sutton Water Resource Recovery Facility | 2025-11-06
WW-NORTH | November | Pump down and flush secondary EQ tank Plant checks completed Run rag auger in hand Lab completed and entered into SharePoint Rotate UV duties channel 2 B now duty 1 (Was channel 1A) having low intensity issues switched back to channel 1B | Sutton Water Resource Recovery Facility | 2025-11-06
WW-NORTH | November | Transfer sludge Plant walk through Check bar screen | Sutton Water Resource Recovery Facility | 2025-11-09
WW-NORTH | November | Plant checks completed Increase wasting on SBR 1&2 from 120sec to 240sec on both Fill lagoon chamber and back flush inlet due to low flows Disconnect sludge pad hose for haulers due to frozen lines Made W/O for sludge heat trace pad Decant and transfer sludge Complete lab and enter data into SharePoint Plug in heat lines on decant arms and air valves | Sutton Water Resource Recovery Facility | 2025-11-10
WW-NORTH | November | Removed rags and grit from bar screen to unclog it, increased air on two of the six sand filters | Sutton Water Resource Recovery Facility | 2025-11-05
WW-NORTH | November | clear EQ # 2 tank valve alarm test supernatant pump and put in auto - will monitor throughout day work on bar screen screw press clean vortex Y screens completed lab and enter data into SharePoint received alum delivery | Sutton Water Resource Recovery Facility | 2025-11-03
WW-NORTH | November | On site to check to see why supernate pump tripped on High temp. Looks like stop float is missing. Also water in thickening tank. Pump down supernate tank. Will monitor left supernate pump in manual off. Barscreen hopper full of rags and water. Put auger in hand forced rages down with bar rags and water going down. Left auger in hand. | Sutton Water Resource Recovery Facility | 2025-11-02
WW-NORTH | November | JH&S competed Plant checks Weekly MOE Lab samples taken to harry walker Complete lab and enter data into SharePoint Continue to work on bar screen hopper. Cleaned water line and ?Y? screen on the end of the auger Reset the septage system grinder after Sutton septic jammed it Emptied garage bins Dropped off toilet supplies | Sutton Water Resource Recovery Facility | 2025-11-05
WW-NORTH | November | Changed Lagoon pump run time from 0700-1900 to 0600-2400 | Sutton Water Resource Recovery Facility | 2025-11-04
WW-NORTH | November | Pump down and hose supernate tank Continue to work on bar screen auger | Sutton Water Resource Recovery Facility | 2025-11-03
WW-NORTH | November | Collect weekly YD samples | Sutton Water Resource Recovery Facility | 2025-11-25
WW-NORTH | November | Received ROC call for UV fault Switched UV duty 1 to channel 1A | Sutton Water Resource Recovery Facility | 2025-11-20
WW-NORTH | November | Performed facility station check Raked and levelled bar screen and grit bin Completed Lab analysis: Data in Sharepoint Adjusted ALUM dosage setpoint: 180 mg/L ?> 170 mg/L Tested UV level sensors by reengaging toggle switch - no faults were triggered, will continually monitor Pushed bins back inside headworks Contractors still on site for roof work | Sutton Water Resource Recovery Facility | 2025-11-19
WW-NORTH | November | Onsite to troubleshoot FIT to lagoon Informed ROC and operations Made adjustments to EPD parameters and tested Operations will monitor over the next few days Informed ROC armed buildings and left site | Sutton Water Resource Recovery Facility | 2025-11-27
WW-NORTH | November | Onsite for daily operations Review scada/trends Decant stt plus transfer after load taken Collect in house lab samples Check station Clear rags from barscreen area Filters ok Complete lab - data in sharepoint PCS and electrical onsite to continue UV investigation 12:20 Alert roc filter feed pumps off for duration of UV work | Sutton Water Resource Recovery Facility | 2025-11-26
WW-NORTH | November | Started decanting S.T.T Checked and leveled grit and rag bins Finished decanting and raised gate back to top position Started transfer to S.H.T | Sutton Water Resource Recovery Facility | 2025-11-23
WW-NORTH | November | Complete lab and enter data into SharePoint Plant checks completed Decant and transfer sludge after GFL remove load Pump out chambers Rotate septage duty pumps pump one now duty one UV rotation wiper back in Auto1-4 Found FIT 4 totalizer having a negative number after the flows stop Contractors on site working around hedge Road chamber | Sutton Water Resource Recovery Facility | 2025-11-24
WW-NORTH | November | Bar screen brush loud investigate. One segment of brush detached. Remounted guarding back in service | Sutton Water Resource Recovery Facility | 2025-11-24
WW-NORTH | November | Onsite as directed by MS (PCS Supervisor) to replace PLC responsible for UV. Onsite, setup PLC with program, IP, security and switched out processor, downtime approx 5min. Confirmed system connectivity and SCADA operation with Tyson. | Sutton Water Resource Recovery Facility | 2025-11-25
WW-NORTH | November | Alum delivery received Transfer sludge Shovel and hose bar screen Lab completed and entered into SharePoint Filter check | Sutton Water Resource Recovery Facility | 2025-11-28
WW-NORTH | November | Onsite for sludge handling Review scada/trends Decant stt plus transfer Clear rags and hose down barscreen area Check filters - ok | Sutton Water Resource Recovery Facility | 2025-11-30
WW-NORTH | November | Performed facility station check Completed Lab analysis: Data in Sharepoint Inspected headworks: leveled grit bin and raked bar screen Decanted sludge tank Continued troubleshooting UV:. -Wiper group reset to 1 again; investigated trends and involved PCS. Suspect a faulty connection. Work order created for further investigation on PCS end (W11461797) | Sutton Water Resource Recovery Facility | 2025-11-21
WW-NORTH | November | Performed facility station check Completed Lab analysis: Data in Sharepoint Inspected headworks: leveled grit bin and raked bar screen Decanted and transferred sludge Flushed and pumped down secondary EQ tank and raised pump Continued troubleshooting UV: -Awaiting Hach technician to service UVT analyzer; changed UVT to manual value of 65% on UV system controller. -Provided Trojan with wiper system information, which is resetting to 1 wiper group from 4; unable to determine the cause Increased lagoon pump speed setpoint to pump down the lagoon faster but the lagoon wetwell lo level switch interlocked the pumps. Placed back to auto speed control; no issues with wetwell level | Sutton Water Resource Recovery Facility | 2025-11-20
WW-NORTH | November | Under direction of OIC Chris Colangelo, Worked with Chris and Tyson Cornish to troubleshoot UV panel PLC controller. Replaced power supply and put the panel power on UPS to isolate transfer switch. | Sutton Water Resource Recovery Facility | 2025-11-26
WW-NORTH | November | Onsite for daily operations Review scada/trends Decant stt no transfer due to sht level Collect in house lab samples Complete lab Enter data in sharepoint Check station Clear rags from barscreen area Notice false flow being read on filter feed bypass to lagoon flowmeter. Call Instrumentation Rick L and Red B. 14:13hrs open up filter feed bypass to lagoon for troubleshooting purposes 14:21hrs close filter feed to lagoon bypass valve Monitoring flowmeter after investigation, no apparent issues. Flowmeter reading 0L/s Find filter 2C plugged. Pull filter and clear rag blockage. Filter back to normal operation Adjust WAS setpoint on sbr2 from 300s to 360s | Sutton Water Resource Recovery Facility | 2025-11-27
WW-NORTH | November | Performed facility station check Completed Lab analysis: Data in Sharepoint Decanted Sludge holding tanks Inspected headworks Trojan UV technician on site all day for UV maintenance Replaced wiper cylinder Replaced bulbs: 2A- module 2 lamp 3 2A- module 3 lamp 3 2B- module 1 lamp 1 Temporarily increased filter feed pump 1 speed setpoint to 100% which increased filter flow to 79 L/s | Sutton Water Resource Recovery Facility | 2025-11-13
WW-NORTH | November | called at 1743hrs by CPO Christian, High EQ level alarm. logged onto scada remotely . Found Filter feed pump running 15% set speed in manual control, switched to Auto speed control. Also changed Flow bias from 13 to 15 l/s. monitored until level stabilized. | Sutton Water Resource Recovery Facility | 2025-11-15
WW-NORTH | November | in at 0830hrs. sludge handling. Decanted and then topped up STT. checked building and equipment. out at 0905hrs. | Sutton Water Resource Recovery Facility | 2025-11-16
WW-NORTH | November | Plant checks completed Complete lab and put information in SharePoint Enable wiper system after power blip Decant sludge, and transfer after GFL remove load Rake bar screen and hose down Empty ADMIN building garbage | Sutton Water Resource Recovery Facility | 2025-11-17
WW-NORTH | November | Batch waste SBR tank 2 Increased wasting on tank 2 from 360sec to 420sec Decant and transfer sludge tank SBR 2 air valve local closed and in Maintenance mode for maintenance team to install blow off system aeration blowers 1-3 off as well Shelve division EQ valve fault and over torque alarms- faulty valve since the day it was installed and we do not use UV issues- looking into problems, UVT and dose showing 0 but the UV 1A and B are on with an intensity of 100 Clean UV transmittance probe under direction of Eric Simanovskis potential problem is UVT is not connecting to UV system Weekly samples taken and delivered to Harry Walker Parkway Manually Deacon SBR two well maintenance worked on new flow off-line | Sutton Water Resource Recovery Facility | 2025-11-18
WW-NORTH | November | Relocated drop leg and purge valve for North SBR. Picked up additional plumbing supplies and completed mechanical installation of purge valve. Electrical hookup currently being worked on | Sutton Water Resource Recovery Facility | 2025-11-18
WW-NORTH | November | Disabled pump rotation from all stop on septage receiving tank pumps. We are trying to find out if one pump is pumping more than the other | Sutton Water Resource Recovery Facility | 2025-11-17
WW-NORTH | November | Onsite to investigate purge valve installation | Sutton Water Resource Recovery Facility | 2025-11-17
WW-NORTH | November | Onsite for daily operations Review scada/trends Decant stt - no transfer Collect in house lab samples Collect weekly regulatory samples W11363705 Complete lab Enter data in sharepoint Check station Filters ok Clean rags from barscreen OCU filter inspection UV wipers back in service (1-4) Rotate UV duty from 1A to 2A. Compressor check Blower air reliefs Push out all 4 bins for miller waste - clean surrounding area and put all bins back in headworks | Sutton Water Resource Recovery Facility | 2025-11-11
WW-NORTH | November | Onsite for daily operations Review scada/trends No decant - stt ready for gfl load Check station Filters ok Electrical onsite to replace UV UPS batteries. 0938hrs turn off filter feed pumps 0941hrs verify UV effluent flow meter reads 0L/s CPD onsite to to investigate pressure switches on compressors 10:11hrs place filter feed pumps back in auto Clear UV alarms Collect in house lab samples Increase wasting on SBR1 from 240s to 300s Increase wasting on SBR2 from 240s to 360s | Sutton Water Resource Recovery Facility | 2025-11-14
WW-NORTH | November | responding to filter feed pump2 fault alarm from earlier power blip in area. Reset at mcc and on scada. all normal on leaving. cmu11446292 | Sutton Water Resource Recovery Facility | 2025-11-16
WW-NORTH | November | On site to replace Trojan UV Panel UPS batteries. | Sutton Water Resource Recovery Facility | 2025-11-14
WW-NORTH | November | Onsite for daily operations Review scada/trends Decant stt plus transfer after load Check station Filters ok - hose down plates and floats Collect in house lab samples Complete lab and enter data in sharepoint Remove rags from sbr inlet stems Clear rags from barscreen Barscreen maintenance Vortex oil changes UV inspection SBR decant arm maintenance EQ line flush Sump pump inspection Muffin monster maintenance Skimmed debris off sbr?s Screw press maintenance Grit press maintenance | Sutton Water Resource Recovery Facility | 2025-11-12
WW-NORTH | November | Pump 1 partially plugged ROC had low flow alarms and put OOS and in manual. Ran pump several times at 100% and also ran with Pump 2 at 100% cleared blockage running at 208 l/s back in auto and in rotation | Keswick Sewage Pumping Station | 2025-11-06
WW-NORTH | November | station checks sharepoint data entry | Keswick Sewage Pumping Station | 2025-11-06
WW-NORTH | November | Checked station Viewed HMI and trends Checked and completed consolidated dry well work order Ran all pumps 2 100% P1 - 207 L/s P2 - 215 L/s P3 - 210 L/s P4 - 211 L/s Cleared boiler fault | Keswick Sewage Pumping Station | 2025-11-10
WW-NORTH | November | station checks sharepoint data entry | Keswick Sewage Pumping Station | 2025-11-03
WW-NORTH | November | Onsite responding to CMU5 W11473371 boiler 1 fault alarm Receive call from ROC at 15:30hrs regarding boiler 1 fault Reset boiler fault and monitor function No apparent issues | Keswick Sewage Pumping Station | 2025-11-27
WW-NORTH | November | Checked station Viewed HMI and trends Checked dry well area Recorded readings in SharePoint | Keswick Sewage Pumping Station | 2025-11-20
WW-NORTH | November | Checked station Viewed HMI and trends Ran all pumps @ 100% P1 - 205.4 L/s P2 - 171.4 L/s P3 - 194.2 L/s P4 - 212.4 L/s Checked dry well area Recorded readings in SharePoint | Keswick Sewage Pumping Station | 2025-11-24
WW-NORTH | November | Attended for low flow alarms on pumps 1, 3, and 4 Backflushed each pump and ran at 100%, all flows above 200 L/s. | Keswick Sewage Pumping Station | 2025-11-19
WW-NORTH | November | Pump 1,3 and 4 low flows and partially plugged. run pumps several times at 100% in manual with no luck. will send operators to unplug all 3 pumps | Keswick Sewage Pumping Station | 2025-11-19
WW-NORTH | November | Checked station Viewed HMI and trends Ran pumps @ 100% P1 - 204.1 L/s P2 - 214.2 L/s P3 - 189.3 L/s P4 - 190.5 L/s Checked dry well area Recorded readings in SharePoint | Keswick Sewage Pumping Station | 2025-11-27
WW-NORTH | November | Recorded vibration readings for pumps. | Keswick Sewage Pumping Station | 2025-11-20
WW-NORTH | November | Attended for operational assistance for WESSUC wetwell clean Isolated wet well 2 and pumped down to 0.60 m Returned wet well 2 to service at 11:05 Isolated wet well 1 and pumped down to 0.85 m Returned wet well 1 to service at 13:30 Ran all pumps at 100% and returned all setpoints to their initial state. | Keswick Sewage Pumping Station | 2025-11-11
WW-NORTH | November | Onsite to reset outstanding boiler fault Fault message displayed ?loss of flame during operation? Clear/reset boiler system and alarms Alert TL of error message No apparent issues | Keswick Sewage Pumping Station | 2025-11-28
WW-NORTH | November | Ran pump 1 at 100% manual speed multiple time to increase flow and flush any debris out. | Keswick Sewage Pumping Station | 2025-11-18
WW-NORTH | November | Performed station check Entered readings into SharePoint Reset alarms on Boiler | Keswick Sewage Pumping Station | 2025-11-17
WW-NORTH | November | ROC emailed letting us know pump 2 had low flow. Ran pump 2 at 100% and also ran pump 3 with it. Ran several more times and managed to get a flow rate of 212 l/s | Keswick Sewage Pumping Station | 2025-11-14
WW-NORTH | November | Performed station check Entered readings into SharePoint Completed assigned EZMax work orders: - Diesel Generator test run - JHS Inspection - Hoist Inspection | Keswick Sewage Pumping Station | 2025-11-13
WW-NORTH | November | Onsite to check station review scada/trends Enter data in sharepoint Alert roc Transfer station to diesel power at 10:13hrs JHSC inspection Test wall fan and roof fan Transfer station back to hydro at 11:04hrs Enter diesel data in sharepoint Clear alarms | Sutton Woodriver Bend Sewage Pumping Station | 2025-11-10
WW-NORTH | November | ROC sent an email identifying Pump 4 had a low flow alarm, ran pump several times at 100% and cleared blockage ran at 209l/s | Keswick Sewage Pumping Station | 2025-11-12
WW-NORTH | November | Investigate order complaint no odours found complaint was probably from new asphalt being put down on roadway Station checks complete completed Diesel hut, OK Pump down wet well to 1 m Enter data into SharePoint | Sutton Woodriver Bend Sewage Pumping Station | 2025-11-06
WW-NORTH | November | Station checks completed Enter data into SharePoint Diesel hut ok | Sutton Woodriver Bend Sewage Pumping Station | 2025-11-04
WW-NORTH | November | Onsite to check station Review scada/trends No alarms Enter data in sharepoint Check diesel hut | Sutton Woodriver Bend Sewage Pumping Station | 2025-11-27
WW-NORTH | November | Vacuum and sweep control room Clean up leaves around wet well | Sutton Woodriver Bend Sewage Pumping Station | 2025-11-21
WW-NORTH | November | Onsite to check station Review scada/trends No alarms Reset dialer - going off on arrival Enter data in sharepoint | Sutton Woodriver Bend Sewage Pumping Station | 2025-11-20
WW-NORTH | November | Onsite to check station Review scada Clear info alarm Enter data in sharepoint Check Diesel hut | Sutton Woodriver Bend Sewage Pumping Station | 2025-11-24
WW-NORTH | November | station checks completed enter data into SharePoint diesel hut ok | Sutton Woodriver Bend Sewage Pumping Station | 2025-11-13
WW-NORTH | November | Station checks Hatch secure No odours | Sutton South River Sewage Pumping Station | 2025-11-06
WW-NORTH | November | Onsite to check station Review scada/trends Clear outstanding alarms from yesterdays power fail Reset dialer Enter data in sharepoint Diesel hut ok | Sutton Woodriver Bend Sewage Pumping Station | 2025-11-17
WW-NORTH | November | Onsite for annual calibrations Informed ROC Used cal mode on scada during the work Only LIT calibrated Informed ROC, armed panel and left site | Sutton South River Sewage Pumping Station | 2025-11-10
WW-NORTH | November | Onsite to check station Enter data in sharepoint JHSC Hatches secure | Sutton South River Sewage Pumping Station | 2025-11-10
WW-NORTH | November | Station checks completed Enter data into SharePoint Hatch secure | Sutton South River Sewage Pumping Station | 2025-11-03
WW-NORTH | November | Onsite to check station Enter data in sharepoint Hatches secure | Sutton South River Sewage Pumping Station | 2025-11-24
WW-NORTH | November | Onsite to check station Enter data in sharepoint Hatches secure | Sutton South River Sewage Pumping Station | 2025-11-27
WW-NORTH | November | Onsite to check station Enter data in sharepoint Hatches secure Minor housekeeping | Sutton South River Sewage Pumping Station | 2025-11-20
WW-NORTH | November | station checks completed enter data into SharePoint hatches secure | Sutton South River Sewage Pumping Station | 2025-11-13
WW-NORTH | November | responding to call from cpo Christian, resident can here alarm at station panel. reset dialer alarm, power blip in area earlier. cmu11446300 | Sutton South River Sewage Pumping Station | 2025-11-16
WW-NORTH | November | Onsite to check station Enter data in sharepoint Hatches secure | Sutton South River Sewage Pumping Station | 2025-11-17
WW-NORTH | November | Onsite to check station HMI has error and wont load scada. Phone oncall PCS A. litvinov to assist PCS reset HMI Review scada/trends Enter data in sharepoint Check pump house | Sutton High Street Sewage Pumping Station | 2025-11-10
WW-NORTH | November | Station checks completed Enter data into SharePoint Monthly diesel run Start 637.4hr Stop 638.7hr JH&S check Test high low temp | Sutton High Street Sewage Pumping Station | 2025-11-03
WW-NORTH | November | Station checks completed Enter data into SharePoint Diesel hut ok HMI screen not working | Sutton High Street Sewage Pumping Station | 2025-11-06
WW-NORTH | November | Onsite to check station Review scada/trends Enter data in sharepoint Check pump house | Sutton High Street Sewage Pumping Station | 2025-11-24
WW-NORTH | November | Onsite to check station Review scada/trends Enter data in sharepoint No alarms Check pump house | Sutton High Street Sewage Pumping Station | 2025-11-27
WW-NORTH | November | Yearly work order to operate incoming gate valve Closed and opened valve -operation ok Check incoming flow chambers -ok | Sutton High Street Sewage Pumping Station | 2025-11-19
WW-NORTH | November | Investigate vibration issue with pump 1 Found alignment issue with sheaves Went to adjust sheave on pump side and bushing is broken. Ordered and picked up new bushing for installation tomorrow. | Sutton High Street Sewage Pumping Station | 2025-11-11
WW-NORTH | November | Onsite to check station Review scada/trends Enter data in sharepoint Check pump house Monthly housekeeping | Sutton High Street Sewage Pumping Station | 2025-11-20
WW-NORTH | November | Onsite to check station Review scada/trends Clear outstanding alarms from yesterday's power fail Reset dialer Enter data in sharepoint Check pump house | Sutton High Street Sewage Pumping Station | 2025-11-17
WW-NORTH | November | Station checks completed Enter data into SharePoint Pump house ok Run pump 1 at 100% | Sutton High Street Sewage Pumping Station | 2025-11-13
WW-NORTH | November | Installed new lower bushing on pump 1 lower sheave. Aligned sheaves on pump 1 within spec Installed new belts on pump 1 Tested operation okay. Installed belts on pump 2 Took vibration readings on both pumps. Greased and inspected both pumps okay | Sutton High Street Sewage Pumping Station | 2025-11-12
WW-NORTH | November | On site to meet Wessuc for wetwell cleaning. Called ROC disabled low level lock out. Isolated and pumped down wetwell 1 closed off flow and interconnect gate. after clean was done primed pumps 1 and 2 and opened flow to wetwell 1 all good. Isolated wetwell 2 and pumped down. wetwell was cleaned opened interconnect gate and inlet gate to wetwell 2 and primed and ran pump 3 all ok. wetwell 1 station back in auto and enable low level lock out | Keswick Joe Dales Sewage Pumping Station | 2025-11-05
WW-NORTH | November | Checked station Reviewed trending No alarms Ran pumps yesterday at 100% after wetwell clean Entered data into sharepoint | Keswick Joe Dales Sewage Pumping Station | 2025-11-06
WW-NORTH | November | Checked station Viewed HMI and trends Checked dry well area Ran all pumps @ 100% P1 - 60.50 L/s P2 - 64.88 L/s P3 - 58.92 L/s Recorded readings in SharePoint | Keswick Joe Dales Sewage Pumping Station | 2025-11-10
WW-NORTH | November | Onsite to check station Review scada/trends Clear outstanding info alarm (intrusion) Enter data in sharepoint | Keswick Joe Dales Sewage Pumping Station | 2025-11-03
WW-NORTH | November | Checked station Viewed HMI and trends Ran all pumps @ 100% P1 - 55.16 L/s P2 - 59.50 L/s P3 - 53.74 L/s Checked dry well area Recorded readings in SharePoint | Keswick Joe Dales Sewage Pumping Station | 2025-11-24
WW-NORTH | November | Checked station Viewed HMI and trends Checked dry well area Recorded readings in SharePoint | Keswick Joe Dales Sewage Pumping Station | 2025-11-20
WW-NORTH | November | Checked station Viewed HMI and trends Checked dry well area Ran pumps @ 100% P1 - 53.84 L/s P2 - 57.78 L/s P3 - 52.93 L/s Recorded readings in SharePoint | Keswick Joe Dales Sewage Pumping Station | 2025-11-27
WW-NORTH | November | On site for temp gen removal. Reinstated station gen. All inputs tested. Station transfer test completed without issue. | Keswick Joe Dales Sewage Pumping Station | 2025-11-28
WW-NORTH | November | Checked station Viewed HMI and trends Ran all pumps @ 100% P1 - 58.90 L/s P2 - 62.80 L/s P3 - 56.46 L/s Checked dry well area Recorded readings in SharePoint | Keswick Joe Dales Sewage Pumping Station | 2025-11-13
WW-NORTH | November | Attended for station check Recorded station readings in rounds sheet Checked dry well - p.3 running in duty Checked temporary generator E-key lock missing from gate Reviewed SCADA/trends. | Keswick Joe Dales Sewage Pumping Station | 2025-11-17
WW-NORTH | November | In to complete monthly work orders Notified ROC of potential alarms Ran temporary diesel generator from 9:35am to 10:40am - no issue Completed H + S inspection Completed dry well consolidated work order | Keswick Joe Dales Sewage Pumping Station | 2025-11-12
WW-NORTH | November | Checked station Viewed HMI and trends Checked dry well area Ran all pumps @ 100% P1 - 100.3 L/s P2 - 103.1 L/s P3 - 104.3 L/s Checked and cleaned bar screen equipment | Georgina No. 4 Sewage Pumping Station | 2025-11-10
WW-NORTH | November | Checked station Reviewed trends No alarms Entered data into SharePoint Ran pumps at 100% P1 100 l/s P2 105 l/s P3 105 l/s | Georgina No. 4 Sewage Pumping Station | 2025-11-06
WW-NORTH | November | checked station reviewed trends entered data into sharepoint ran all pumps at 100% p1 99l/s p2 103l/s p3 107l/s no alarms | Georgina No. 4 Sewage Pumping Station | 2025-11-03
WW-NORTH | November | Checked station Viewed HMI and trends Notified ROC of diesel generator test run Ran diesel with no issues Checked dry well area Checked and cleaned of bar screen equipment Recorded readings in SharePoint Station back to normal power | Georgina No. 4 Sewage Pumping Station | 2025-11-24
WW-NORTH | November | Attended for bar screen and screw conveyer cleaning. | Georgina No. 4 Sewage Pumping Station | 2025-11-25
WW-NORTH | November | Checked station Viewed HMI and trends Checked dry well area Checked and cleaned bar screen equipment Recorded readings in SharePoint | Georgina No. 4 Sewage Pumping Station | 2025-11-20
WW-NORTH | November | Checked station Viewed HMI and trends Checked dry well area Cleaned bar screen equipment Recorded readings in SharePoint | Georgina No. 4 Sewage Pumping Station | 2025-11-27
WW-NORTH | November | Station checks completed Enter data into SharePoint Run bar screen in hand Run pumps 1&2 manual speed 100% | Georgina No. 4 Sewage Pumping Station | 2025-11-13
WW-NORTH | November | Onsite to check station Review scada/trends Clear outstanding alarms from yesterdays power fail. Reset dialer Clear rags on barscreen Enter data in sharepoint | Georgina No. 4 Sewage Pumping Station | 2025-11-17
WW-NORTH | November | In to complete monthly work orders Notified ROC of potential alarms Completed inspection of hoist Tested high / low temp. alarm Completed H + S inspection Completed sump system inspection | Georgina No. 4 Sewage Pumping Station | 2025-11-11
WEST | November | Onsite for station check Duty not active Checked residuals mg/l @1153 Total analyzer 1.62 grab 1.58 Free analyzer 0.07 grab 0.06 | Woodbridge East Booster Pumping Station | 2025-11-07
WEST | November | Onsite for station check Duty not active Checked residuals mg/l @1112 Total analyzer 1.63 grab 1.64 Free analyzer 0.06 grab 0.05 | Woodbridge East Booster Pumping Station | 2025-11-10
WEST | November | Onsite for station check Duty active Checked residuals mg/l @1147 Total analyzer 1.57 grab 1.56 Free analyzer 0.06 grab 0.04 | Woodbridge East Booster Pumping Station | 2025-11-03
WEST | November | Onsite for station check Duty not active Checked residuals mg/l @1141 Total analyzer 1.76 grab 1.74 Free analyzer 0.06 grab 0.05 | Woodbridge East Booster Pumping Station | 2025-11-21
WEST | November | Station Check (no issues found) Input data to PWQ 12:25 Verified Depolox (mg/l) Free: Grab 0.06, A 0.05 Total: Grab 1.47, A 1.53 | Woodbridge East Booster Pumping Station | 2025-11-27
WEST | November | Onsite for station check Duty active Checked residuals mg/L @1234 Total analyzer 1.74 grab 1.73 Free analyzer 0.06 grab 0.07 | Woodbridge East Booster Pumping Station | 2025-11-17
WEST | November | On site for Station Check Check Trends: All Okay Duty off 11:25- Verified Analyzers Grab Free Cl2-0.08 mg/L, Analyzer- 0.06 mg/L Grab Total Cl2- 1.52 mg/L, Analyzer- 1.57 mg/L Entered Values in PWQ Sheet Equipment okay. | Woodbridge East Booster Pumping Station | 2025-11-25
WEST | November | Onsite to complete work orders Completed jhsc with no with no issues Inspected sump pit and tested flood alarm Completed cl2 analyzer maintenance Electrolyte and grit ok Grabs Total analyzer 1.70 grab 1.69 Free analyzer 0.07 grab 0.07 | Woodbridge East Booster Pumping Station | 2025-11-18
WEST | November | Onsite for station check Duty not active Checked residuals mg/l @1130 Total analyzer 1.20 grab 1.16 Free analyzer 0.05 grab 0.07 | Woodbridge East Booster Pumping Station | 2025-11-14
WEST | November | On site for electrical and heat trace inspection. | Woodbridge East Elevated Tank | 2025-11-10
WEST | November | Onsite for station check and to collect weekly micro sample W11376158 Deactivated duty to get sample on drain cycle Checked residuals mg/l Total grab 1.85 Free grab 0.01 Sl1000 Mcl grab 1.48 No2 0.000 F nh3 0.14 T nh3 0.43 | Woodbridge East Elevated Tank | 2025-11-05
WEST | November | Onsite for station check and to collect weekly micro sample W11387525 Deactivated duty to get sample on down cycle Checked residuals mg/l @0944 Total grab 1.69 Free grab 0.05 Sl1000 Mcl grab 1.72 No2 grab 0.000 F nh3 0.08 T nh3 0.42 Reactivated duty afterwards | Woodbridge East Elevated Tank | 2025-11-19
WEST | November | Onsite to complete work orders Tested portable generator Completed jhsc with no issues Tested flood alarm | Woodbridge East Elevated Tank | 2025-11-18
WEST | November | Onsite to complete station check and to collect weekly micro sample W11403149 Deactivated duty yo get sample on down cycle Low level alarm came in Checled residuals mg/L @0943 Total grab 1.62 Free grab 0.05 SL1000 Mcl grab 1.60 No2 grab 0.004 F nh3 grab 0.11 T nh3 grab 0.43 Reactivated duty afterwards | Woodbridge East Elevated Tank | 2025-11-26
WEST | November | Onsite for station check and to collect weekly micro sample W11387539 Deactivated duty to get sample on down cycle Checked residuals mg/L @0944 Tcl grab 1.60 Fcl grab 0.04 Sl1000 Mcl grab 1.52 No2 0.000 F nh3 0.13 T nh3 0.46 | Woodbridge East Elevated Tank | 2025-11-12
WEST | November | Onsite to complete station check and to collect weekly micro sample W11403149 Remotely deactivated duty to collect sample on downcycle Checked residuals mg/L @1033 Total grab 1.41 Free grab 0.06 SL1000 Mcl grab 1.15 No2 0.05 F nh3 0.11 T nh3 0.34 | Woodbridge West Elevated Tank | 2025-11-26
WEST | November | Onsite for station check and to collect weekly micro sample W11376158 Checked residuals mg/L @1059 Total grab 1.37 Free grab 0.04 Sl1000 Mcl grab 1.36 No2 grab 0.000 F nh3 grab 0.08 T nh3 grab 0.35 No issues observed | Woodbridge West Elevated Tank | 2025-11-05
WEST | November | Onsite to complete work orders Did chamber entry to complete sump inspection Tested hi/lo level alarms Completed jhsc no issues Tested portable generator with no issues Exercised drain, actuated and manual valves | Woodbridge West Elevated Tank | 2025-11-20
WEST | November | Onsite for station check and to collect weekly sample W11387525 Tower draining Checked residuals mg/l @1044 Total grab 1.56 Free grab 0.04 Sl1000 Mcl grab 1.39 No2 0.003 F nh3 0.10 T nh3 0.38 | Woodbridge West Elevated Tank | 2025-11-19
WEST | November | Onsite for station check and to collect weekly micro sample W11387539 Deactivated duty to get sample on downcycle Checked residuals mg/L @1046 Tcl grab 1.49 Fcl grab 0.05 Sl1000 Mcl grab 1.38 No2 0.002 F nh3 0.15 T nh3 0.42 No issues observed | Woodbridge West Elevated Tank | 2025-11-12
WW-CEAST | November | On site to help Terry Reed clean up facility in preparation for the upcoming HR/PEC site visit. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-11-07
WW-CEAST | November | Took half of the station readings and entered into SharePoint , Marcos finished it off as my tablet was having a bad day. Cleaned up the area around the Diesels and the water meters - organized all of maintenance parts lying around and swept up the floor. Swept and mopped out the washroom,, I cleaned the toilet last week. Checked both compressors oil/belt - OK. Left at 12:30 to fill up Jerry cans with gas. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-11-07
WW-CEAST | November | On site to repair the air filter on the compressor. The compressor is back in duty | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-11-10
WW-CEAST | November | -On site to perform a station check. -Entered station readings into SharePoint. -Checked drywell and air compressors. -Found Air Compressor 1 with the air filter housing broken off of the unit. Placed the compressor to local off/OOS and created work request for maintenance team to repair issue. -Checked screen room, changed out rag bin, bar screen oil full. -Checked dump pad, found Line 3 with an outstanding Overtorque alarm from 14:35 on Nov. 7. Isolated and flushed line, cleared and reset fault. -Inspected heat trace at dump pad, all heat trace working properly. -Pump 3 remains OOS with Flowmeter fault, but can be run in an emergency. -Air Compressor 1 OOS. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-11-10
WW-CEAST | November | Attending site to check Radar LIT#4 (W11397846). Readings have been normal since the end of last week. Could not determine a cause of the erratic readings and there is no error in the device. Will need to wait for it to act up again. ROC was notified before and after maintenance work. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-11-05
WW-CEAST | November | Here to clear line 1 at the dump pad - backflushed line ,, a lot of rocks inside the line. Cleared obstruction and put line 1 back into service. CMU# W11425011. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-11-06
WW-CEAST | November | On site to troubleshoot dump pad drain issue. Upon arrival, found the drain below line 3 was clogged with full of material which caused the entire drain way to back up -> going to the catch basin at the back of the building. With the help from Ampot, we were able to unclog the problematic drain. Seems like finer grating is required as there were rocks/other types of solids in the drain. Cleaned catch basin at the back. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-11-06
WW-CEAST | November | -On site to assist maintenance team with repairs to wet well equalization valve pedestal. -Isolated Wet Well 1 and placed OOS to facilitate repairs to equalization valve. Monitored flows and levels throughout the day. -Responded to Line 1 Overtorque alarm this morning at the dump pad. Alarm came in at 05:25am. Isolated line and back flushed large amount of rags. Testes valve with no issues, cleared alarms, returned Line 1 to service. -Placed steel bin back outside of dump pad. Cleaned grating, drain channels, and walkways. Cleaned out drain pit behind building as well. -Maintenance has finished work on valve for today, but will need to return another day in the future. Equalization valve is now operational again and has been opened. Opened isolation gates back up and returned Wet Well 1 to service, along with pumps 1 and 2. -Pump 3 remains OOS due to Flowmeter fault, but can be used in an emergency. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-11-04
WW-CEAST | November | Interconnect valve pedestal replacement. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-11-04
WW-CEAST | November | -On site to perform a station check. -Entered station readings into SharePoint. -Checked drywell and air compressors. -Pump 1 placed OOS over the weekend due to MV2 valve faults. Tested Pump 1 MV2 valve locally with no issues. Test ran Pump 1 with no issues. Left Pump 1 in auto, duty 1. -Checked screen room, raked rag bin, topped up bar screen oil, cleaned rags off conveyors. -Test ran Pump 3 in manual for one duty cycle, Flowmeter still waiting on parts for replacements, no other issues noted with pump 3. Pummp 3 remains OOS, but can be run in an emergency. -All dump pad lines are in auto and available. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-11-03
WW-CEAST | November | -On site to complete work orders. -Station check completed, readings entered into SharePoint. -Checked drywell. -Air compressors, inspection and cleaning completed. -Air dryer, inspection and cleaning completed. -Checked screen room, raked rag bin, bar screen oil full. -Hazardous waste collection and removal completed, no items removed from site this month. -Monthly JHSC H&S inspection completed, no issues noted. -Monthly diesel generator test run completed. -0851 - Transferred site to generator power. -1027 - Transferred site back to utility power. -Generator run time: 1.7hrs. -All pumps and generators in auto. -Pump 3 in duty 7/OOS due to Flowmeter fault, but can be run in an emergency. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-11-05
WW-CEAST | November | Closed all valves for North side wetwell Removed pedestal for interconnect Fabricated new pedestal for interconnect Installed new pedestal Opened valves to put north wetwell back in service Complete | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-11-26
WW-CEAST | November | -On site to complete work orders. -Station check completed, entered readings into SharePoint. -Checked drywell. -Air compressors, inspection and cleaning completed. -Checked screen room, changed out rag bin, cleaned rags off conveyors. -Bar screen bin removal completed. -Assisted maintenance team with isolating Wet Well 1 and placing wet well OOS for wet well interconnect valve repair work. -Wet well interconnect valve repairs completed, reinstated wet well 1 and associated valves. Wet well 1 back in service. -Pump 3 remains OOS due to Flowmeter fault, but can be used in emergency. All other pumps in auto and available. -Checked dump pad, all three lines available. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-11-26
WW-CEAST | November | On site to troubleshoot line 1 overtorque alarm. Back flushed the line and cleared the alarm. Put line 1 back in service. A little bit of rags came out during the back flushing. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-11-27
WW-CEAST | November | On site to troubleshoot line 3 overtorque alarm. Back flushed the line and cleared the alarm. Put line 3 back in service. Not a lot of rags were observed during the back flushing. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-11-24
WW-CEAST | November | On site completed work orders. Station Check (See details on SharePoint) All pumps available in timed auto duty rotation every 3 hours, except, pump 3, which is in manual/duty 7, out of service. All standby power generators available in auto. Checked dry well. Checked bar screens. Levelled rags from the rag bin. Cleaned bar screens of rags on the floor and on the conveyor. Odour Control Scrubber System Inspection. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-11-24
WW-CEAST | November | -On site to complete work orders. -0557 this morning, Line 2 Overtorque Alarm came in at the dump pad. Isolated line, backflushed, removed ball of rags. Cleared alarm and placed Line 2 back in service. -Station check completed, readings entered into SharePoint. -Checked drywell and air compressors. -Checked screen room, raked rag bin. -Consolidated dry well valve exercises completed. -West Forcemain header valve fully exercised. East Forcemain header valve to be fully exercised on Dec. 10 as part of a CCTV inspection. -RSP discharge valve exercises conmpleted. -Suction valve exercises completed. -Pump 3 remains OOS with Flowmeter fault, but can be run in an emergency. Ran pump 3 while on site for one duty cycle. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-11-28
WW-CEAST | November | -On site to complete consolidated surge tank inspection work orders. -Surge tank and system inspection completed. -Surge tank valve and actuator, exercise and inspection completed. Exercised all valves, SURG_TK2_MV2 East valve kept getting Overtorque Alarms around 90% open. Issue had previously been noted and work request created, will follow-up on status of work request. -Surge tank drain line inspection completed. -Surge tank transmission line flushing completed. Flushed out both surge tank transmission lines. Cleared blockages in both transmission drain lines. Cleaned floors and reset alarms. -Checked dump pad while on site, no issues noted, all lines available. -Pump 3 remains OOS with Flowmeter fault, but can be used in an emergency. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-11-20
WW-CEAST | November | -On site to perform a station check. -Entered station readings into SharePoint. -Checked drywell and air compressors. -Checked screen room, changed out rag bin, cleaned rags off floor and conveyors, bar screen oil topped up. -Pump 3 OOS with Flowmeter fault, can be run in an emergency. -All lines available at dump pad. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-11-21
WW-CEAST | November | -On site to complete work orders. -Station check completed, readings entered into SharePoint. -Checked drywell. -Air compressors, inspection and cleaning completed. -Checked screen room, raked rag bin, cleaned conveyors, bar screen oil topped up. -Dump pad inspection and cleaning completed, cleaned grating and drain trough, cleaned walkways, cleaned out drain pit behind building. -Placed silver steel bin back down by dump pad. -Multiple haulers mentioned concerns regarding dump pad line valves closing too early before loads were fully emptied. Relayed concerns to CPD/PCS/by-law teams. -Ran Pump 3 for a couple duty cycles in manual. -Pump 3 remains OOS with Flowmeter fault, can be run in emergencies. -WW maintenance team on site to look at unit heaters 3 and 4 in screen room. Both unit heaters were placed OOS for motor overloading, due for replacement. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-11-19
WW-CEAST | November | -On site to investigate booster pump pressure issues at dump pad. Tested booster pump operation under various scenarios, but did not notice any obvious issues. Booster pumps working as intended, but take a very long time to pressurize tank. Booster pumps are reaching 690kpa stop setpoint, but no trucks on site this afternoon as well. Will relay findings to operations team and CPD. -Replaced rag bins following pick up, steel bin removed from screen room. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-11-13
WW-CEAST | November | -On site to perform a station check. -Entered station readings into SharePoint. -Checked drywell and air compressors. -Checked screen room, raked rag bin, cleaned conveyors, bar screen oil topped up. -All lines available at dump pad. -Heater trace controller 2 fault alarm outstanding. CPD looking into issue under warranty. -Pump 3 OOS with flowmeter fault, can be run in emergency though. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-11-17
WW-CEAST | November | -On site to perform a station check. -Entered station readings into SharePoint. -Checked drywell and air compressors. -Checked screen room, raked rag bin, cleaned conveyors, topped up bar screen oil. -Pump 3 remains OOS due to Flowmeter fault. -All three lines available at dump pad. -Reset Heat Controller 2 Fault alarm at dump pad. Issue relayed to CPD for investigation as it is still under warranty. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-11-14
WW-CEAST | November | -On site to respond to Line 1 Overtorque Alarm at the dump pad, CMU5 W11452656. -Alarm came in at approximately 12:15pm. -Isolated and flushed Line 1, removed ball of rags. Tested valve with no issues. -Cleaned rags and debris off ground and grating. Acknowledged and reset alarm. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-11-18
WW-CEAST | November | -On site to complete work orders. -Station check completed, readings entered into SharePoint. -Checked drywell. -Air compressors inspection and cleaning completed. -Checked screen room, all rag bins full, placed steel bin under press temporarily. Cleaned rags off floor and conveyors. Bar screen oil full. -Bar screen bin removal completed. -Consolidated monthly dry well pump floor inspection completed. -Autodialer test completed and confirmed by ROC. -High/low temp alarm test completed and confirmed by ROC. -Dry well flood alarm test completed and confirmed by ROC. -Sump pit inspection completed, tested pumps. -RS pump inspection completed: -Pump 1: 372L/s at 40%. -Pump 2: 372L/s at 40%. -Pump 3 OOS, no flow visible. -Pump 4: 427L/s. -Pump 5: 372L/s at 40%. -Pump 6: 376L/s at 40%. -Check valve inspections completed. -Checked dump pad, all lines available. Reset Heat trace controller 2 fault. -Ran Pump 3 in manual for one cycle during pump inspections. -Pump 3 remains OOS due to Flowmeter fault. Can be run in an emergency. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-11-12
WW-CEAST | November | On site for station check (See details on SharePoint) and wet well cleaning to be done by WESSUC. Both pumps available in all-stop auto duty rotation. SCADA trending. At around 8:00am, WESSUC on site and started setting up equipment in preparation for wet well cleaning. Wet well level lowered from time to time to or below 2.70m so that WESSUC can clean below the lower (2nd) grating level and the walls. After wet well cleaning, pumps put back in auto and available. Station back to normal operations after wet well cleaning. All alarms cleared/reset. No outstanding alarms. | Newmarket Green Lane Pumping Station | 2025-11-07
WW-CEAST | November | Took station readings and entered into SharePoint,, reviewed trends - all looks good. Station running under normal ops - no issues were found. | Newmarket Green Lane Pumping Station | 2025-11-10
WW-CEAST | November | Took station readings and entered into SharePoint,,, reviewed trends and also all stop Duty rotate. Also completed H&S inspection - no issues. Station running under normal ops - no issues. | Newmarket Green Lane Pumping Station | 2025-11-03
WW-CEAST | November | Took station readings and entered into SharePoint,, reviewed trends and pump flows - all good. Pumps in all stop duty rotate and no issues were found. | Newmarket Green Lane Pumping Station | 2025-11-24
WW-CEAST | November | On site completed Station Check (See details on SharePoint) Both pumps available in all-stop auto duty rotation. It was observed, pump 1 has more flows (Around 270L/s) compared to pump 2 (Around 150L/s), as per the 40% auto speed setpoint. Hence, pump 2 is incurring more time (more than double) to run than pump 1. Put pump 2 in 60% manual speed to compensate for the difference. Pump 2 is now getting more than 200L/s flows when running at 60% manual speed, and running less time for one cycle. SCADA is trending. | Newmarket Green Lane Pumping Station | 2025-11-21
WW-CEAST | November | On site to clear back up control mode for CMS while they are performing PM on pump 1. Ran pump 2 in local/100% to lower it down to back up mode stop setpoint. Cleared back up mode and placed pump 2 back in auto/D1 | Newmarket Green Lane Pumping Station | 2025-11-13
WW-CEAST | November | On site completed Station Check (See details on SharePoint) Both pumps available in all-stop auto duty rotation. Still, pump 1 has more flows and less running time against pump 2, although pump 2 speed increased to 60% manual speed. Station operations normal. SCADA is trending. | Newmarket Green Lane Pumping Station | 2025-11-28
WW-CEAST | November | Took station readings and entered into SharePoint,,, reviewed trends - Pump 2 is in Duty 1 with auto duty rotate off. Pump 1 is being worked on by maintenance. Pump flow is good on pump 2 and station is running under normal ops. | Newmarket Green Lane Pumping Station | 2025-11-14
WW-CEAST | November | Weather today Partly cloudy and 1 Celsius -On site to complete work orders W11340330, W11352649, W11352454, W11351269, W113352441, W11352428. -Completed in-house lab analysis and station check. -Entered lab and station readings into SharePoint. -Post filtration/UV channel hose down. -Post aeration alum mixing chamber clean out. -RAS/WAS inlet channel inspection and hose down. -Reset composite sampler for tomorrow. -Ran RAZ pumps #1 and #2 at 100% to clear them out for a bit - all back to auto as well as speed back to auto. -Added two bags of soda ash to each aeration tank. -Decanting STT into the Headworks. -Transferred the sludge and processing. -Batch wasted 10m3 from Clarifier #1 and #2. -Ras pump #3 in manual OOS. | Mount Albert Water Resource Recovery Facility | 2025-11-06
WW-CEAST | November | Took station readings and entered into SharePoint,, reviewed trends - all good and pump are back in all - stop Duty rotate. Reviewed trends - everything looks good. Station running under normal ops - no issues observed. | Newmarket Green Lane Pumping Station | 2025-11-17
WW-CEAST | November | Completed sludge processing as well as Lab work,, I had to go down and check the SEOC as per ROC instruction - all good. Wasted 16m3 and added 4 bags of soda ash. Station running under normal ops - no issues observed. RAZ pump 3 is OOS. | Mount Albert Water Resource Recovery Facility | 2025-11-09
WW-CEAST | November | On site completed work orders. -completed in-house lab Analysis (See details on SharePoint) -Station Check (See details on SharePoint). -Decanting STT into the Headworks. -Transferred the sludge and processing. -Batch wasted 20m3. -Added two bags each of Soda Ash into each Aeration Tanks -Removed rags from the sluice gates of Aeration Tanks -Checked DO Probes, removed rags from the probes. -RAS/WAS Inlet Channel Inspection and Cleaning -Post Aeration Alum Mixing Chamber Cleaning -Received 120 bags of soda ash delivery. | Mount Albert Water Resource Recovery Facility | 2025-11-10
WW-CEAST | November | Weather today Partly cloudy and 4 Celsius -On site to complete work orders W11340330, W11355798, W11355087. -Completed in-house lab analysis and station check. -Entered lab and station readings into SharePoint. -Reset composite sampler for weekend sampling. -Ran RAZ pumps #1 and #2 at 100% to clear them out for a bit - all back to auto as well as speed back to auto. -Added two bags of soda ash to each aeration tank. -Decanting STT into the Headworks. -Transferred the sludge and processing. -Batch wasted 10m3 from Clarifier #1 and #2. -Ras pump #3 in manual OOS. | Mount Albert Water Resource Recovery Facility | 2025-11-07
WW-CEAST | November | On site for filter 1 air regulator. I will order a replacement | Mount Albert Water Resource Recovery Facility | 2025-11-10
WW-CEAST | November | Attending site to check Inlet Chamber Level transmitter RSHW_LIT1 (W11416143). Found reading was frozen at level transmitter display. Readings returned to normal after cycling power to the device. SCADA calibration mode was used and ROC was notified before and after maintenance work. | Mount Albert Water Resource Recovery Facility | 2025-11-07
WW-CEAST | November | Received alum delivery 1.25m -> 3.74m. Checked inlet channel level flatline issue noted by ROC. Checked the inlet chamber and no obstruction/issues found which would have caused the flatlining issue. Created CMU2 for INST. RAS pump 3 will remain OOS overnight. RAS 1 and 2 back in service Put clarifier 1 back in service. Ras 2 dedicated to clarifier 1 and Ras 1 dedicated to clarifier 2 Approximately 86m3 of clarifier effluent diverted to lagoon between 2:00pm and 3:30pm for clarifier maintenance | Mount Albert Water Resource Recovery Facility | 2025-11-04
WW-CEAST | November | -on site to fix sand filter 1 module 2 which was not backwashing sand properly -this is in response to the high total phosphorus in the comp sample for the lab earlier today, which was 0.088, which is above the objective value of 0.070. -backwashing lance which cleans sand was clogged, pulled lance, cleared any bigger particles and reinstated lance, restored air flow and backwashing of sand looked normal, this was my response to being above the internal objective, sample was still below compliance objective of 0.1 mg/L TP -will return tomorrow for the Sunday lab, will check composite sample and see if Total phosphorus is trending downward -sand filter 1, module 1 seems to be backwashing but slightly underperforming as well, perhaps this week it can be investigated as well -currently both module 1 and 2 are backwashing -notified ROC of work, had CMU5 W11407901 for sand filter 1 maintenance which I returned to site for -W11407732 for Saturday Lab earlier in the day | Mount Albert Water Resource Recovery Facility | 2025-11-01
WW-CEAST | November | -On site for lab analysis and sludge handling. -Completed lab analysis and entered results into SharePoint. -Decanted STT to headworks, emptied tank into SHT. -Added one bag of soda ash to each aeration tank. -Batch wasted 8m3, ran RAS pump 1 at 100% speed when returning to service. -Found both modules in sand filter 1 clogged with sand piling up. Underdrain blocked around both air lifts. Cleared out excess sand, pulled air lifts, cleared out under drains. Both sand filter cells in operation and working normally now. -Final effluent total phosphorous value elevated at 0.091mg/L. Batch wasting completed today, sand filter blockages cleared out, alum dosing levels still elevated at 195mg/l in aeration and 15mg/l in filter. -Clarifier 1 OOS, WAS pump 2 OOS, RAS pumps 2 and 3 OOS. | Mount Albert Water Resource Recovery Facility | 2025-11-02
WW-CEAST | November | Weather today a few clouds and 10 Celsius -On site to complete work orders W11340330, W11338491, W11339147, W11335860, W11337560, W11340322. -Completed station check. -Completed standby generator test run. -Entered standby generator and station readings into SharePoint. -JHSC Health and Safety inspection. -Bar screen bin removal and replacement. -Sand filter #1 out of service and draining at 9:30 am. -Put Sand filter #2 in service at 9:30 am. -Hazardous waste collection and removal. -Reset composite sampler for tomorrow. -Ran RAZ pumps #1 at 100% to clear them out for a bit - all back to auto as well as speed back to auto. -Added two bags of soda ash to each aeration tank. -Decanting STT into the Headworks. -Transferred the sludge and processing. -Clarifier 1 remains isolated, refilling with effluent water, but still out of service to accommodate the works to be done by contractor. -RAS Pump 3 in manual off and out of service.? -RAS pump 2 remains OOS. | Mount Albert Water Resource Recovery Facility | 2025-11-03
WW-CEAST | November | Weather today Clear and 12 Celsius -On site to complete work orders W11340330, W11343271, W11343369, W11343355, W11343224, W11343828, W11400054, W11344015, W11342356. -Completed in-house lab analysis and station check. -Entered lab and station readings into SharePoint. -Collected weekly raw sewage samples. -At 9:10 am Alum delivery/receiving started at 1.25 m filled up to 3.72 m. -Sand filter reject drain line flush. -Reset composite sampler for tomorrow. -Ran RAZ pumps #1 at 100% to clear them out for a bit - all back to auto as well as speed back to auto. -Added two bags of soda ash to each aeration tank. -Decanting STT into the Headworks. -Transferred the sludge and processing. | Mount Albert Water Resource Recovery Facility | 2025-11-04
WW-CEAST | November | -on site for lab analysis and station check -lab complete, data entered into SharePoint -decanted sludge thickening tank -wasted remaining sludge from thickening tank to sludge holding tank -wasted 5 m3 from clarifier 2 to sludge thickening tank -added 1 soda ash bag per aeration tank -sand filter is still underperforming, will monitor -sand filter is the likely culprit of the slightly high TP at 0.088 | Mount Albert Water Resource Recovery Facility | 2025-11-01
WW-CEAST | November | On site completed work orders. -completed in-house lab Analysis (See details on SharePoint) -Decanting STT into the Headworks. -Transferred the sludge and processing. -Batch wasted 12m3. -Added two bags each of Soda Ash into each Aeration Tanks. -Alum dosage setpoints-post aeration changed from 195mg/L to 190mg/L. -Alum dosage setpoints-pre filter changed from 20mg/L to 15mg/L. -Odour control system is not running. Created CMU for CMS. | Mount Albert Water Resource Recovery Facility | 2025-11-05
WW-CEAST | November | On site completed work orders. -completed in-house lab Analysis (See details on SharePoint) -Decanting STT into the Headworks. -Transferred the sludge and processing. -Batch wasted 10m3 from clarifier #1. -Added two bags each of Soda Ash into each Aeration Tanks -Removed rags from the sluice gates of Aeration Tanks -Checked DO Probes, removed rags from the probes. -RAS/WAS Inlet Channel Inspection and Cleaning -Post Aeration Alum Mixing Chamber Cleaning | Mount Albert Water Resource Recovery Facility | 2025-11-03
WW-CEAST | November | -completed in-house lab Analysis (See details on SharePoint) -Decanting STT into the Headworks. -Transferred the sludge and processing. -Clarifier Scum System and Weir Cleaning - approximately 64m3 of flows have been diverted to the lagoon from 10.30am to 12.00pm for clarifier and weir inspection | Mount Albert Water Resource Recovery Facility | 2025-11-26
WW-CEAST | November | Weather today Overcast and 9 Celsius -On site to complete work orders W11340330, W11346796, W11348981, W11375991. -Completed station check. -Entered station readings into SharePoint. -Collected Clarifier scum system and weir cleaning. -Ran RAZ pumps #1 at 100% to clear them out for a bit - all back to auto as well as speed back to auto. -Added two bags of soda ash to each aeration tank. -Decanting STT into the, Headworks. -Transferred the sludge and processing. | Mount Albert Water Resource Recovery Facility | 2025-11-05
WW-CEAST | November | On site for water effluent pressure issue Opened valves to drain pressure. Pump is taking an excessive amount of time to come to full pressure. Pump 2 builds quickly to approximately 44 psi and then is slow to shutoff at approximately 68 psi Pump outlet is 1 1/4? feeding a 4? line. Larger second pump only works in local and will need to be looked at by electrical Unable to open check valves as contractors are using water. Isolated inlet and outlet valves on Pump 1 and no change in pump operation so no issues with check valve not holding. Will discuss with the team lead possible pump replacement or upgrade. | Mount Albert Water Resource Recovery Facility | 2025-11-27
WW-CEAST | November | -lab analysis and sludge handling -completed lab -entered data into SharePoint -reviewed SCADA -inspected site -decanted sludge thickening tank, wasted remaining sludge to holding tank -wasted 10 m3 from clarifier 1 -clarifier 2 remains offline -added 4 bags of soda ash total -station okay | Mount Albert Water Resource Recovery Facility | 2025-11-30
WW-CEAST | November | Weather today A few clouds and 4 Celsius -On site to complete work orders W11396438, W11395299, W11461901, W11461745, W11395756. -Completed station check. -Entered station readings into SharePoint. -Gather SRL/Winches for inspection. -Pump out WRRF Flowmeter chamber. -Bar screen bin Removal and replacement. | Mount Albert Water Resource Recovery Facility | 2025-11-24
WW-CEAST | November | -On site to perform a station check. -Entered readings into SharePoint. -Verified sand filter operation and alum dosing. -Added a second bag of soda ash to each aeration tank. -OCU OOS due to motor failure. | Mount Albert Water Resource Recovery Facility | 2025-11-25
WW-CEAST | November | Station check/lab complete and the readings have been entered into the sharepoint. Contractors completed installing davit base/winch for supernate pump in the headworks Batch wasted 10m3 in total. Dosed 4 bags of soda ash into aeration. Diverted secondary effluent to lagoon for clarifier maintenance. Approximately 77m3, 10:30 to 11:45am. | Mount Albert Water Resource Recovery Facility | 2025-11-21
WW-CEAST | November | -On site to collect weekly samples - W11398761. -Started decanting STT to headworks. -Added one bag of soda ash to each aeration tank. -Collect samples. | Mount Albert Water Resource Recovery Facility | 2025-11-25
WW-CEAST | November | Weather today Snow and 1 Celsius -On site to complete work orders W11396438, W11404719, W11404516, W11404529. -Completed in-house lab analysis. -Entered lab readings into SharePoint. -Batch wasted 23m3 from Clarifier #2. -Post aeration alum mixing chamber clean out. -Reset composite sampler for tomorrow. -Ran RAZ pumps #2 and #3 at 100% to clear them out for a bit - all back to auto as well as speed back to auto. -Added two bags of soda ash to each aeration tank. -Decanting STT into the Headworks. -Transferred the sludge and processing. -Clarifier 2 is now isolated, also partially drained and put out of service to accommodate the works to be done by contractor. -Odour control system OOS. -RAS Pump 1 and WAS Pump 1 in manual off and out of service.? | Mount Albert Water Resource Recovery Facility | 2025-11-27
WW-CEAST | November | Weather today A few clouds and 4 Celsius -On site to complete work orders W11396438, W11395299, W11461901, W11461745, W11395756. -Completed station check. -Entered station readings into SharePoint. -Gather SRL/Winches for inspection. -Pump out WRRF Flowmeter chamber. -Bar screen bin Removal and replacement. | Mount Albert Water Resource Recovery Facility | 2025-11-24
WW-CEAST | November | -On site for lab analysis and sludge handling. -Completed lab analysis, results entered into SharePoint. -Decanted STT to headworks, then emptied tank into SHT. -Batch wasted 10m3, ran RAS pumps at 100% speed when returning to service. -Added two bags of soda ash to each aeration tank. -Verified sand filter operation and alum dosing. | Mount Albert Water Resource Recovery Facility | 2025-11-23
WW-CEAST | November | Informed ROC. Onsite to perform annual calibration. Used the calibration mode during the work. Devices were done as below: all the LITs. Put everything back in service. All the related alarms cleared. No issues. Informed ROC and left the site. | Mount Albert Water Resource Recovery Facility | 2025-11-19
WW-CEAST | November | -on site for station check and work orders -assisted Terry Cantwell with effluent water pump investigation as to why they are not providing enough flow to effluent service water lines -station check completed -data entered into SharePoint -clean UV channel -inspect and clean air compressors -diversion of clarifier effluent to lagoon from 09:22 to 14:17, due to cleaning required of clarifier 2 before launder covers are installed, approximately 224 m3 of clarifier effluent was diverted -station okay | Mount Albert Water Resource Recovery Facility | 2025-11-27
WW-CEAST | November | -station check of site completed, data entered into SharePoint -lab analysis completed, data entered into SharePoint -decanted sludge thickening tank, wasted remaining sludge to holding tank -wasted 14 m3 from clarifiers to thickening tank -added 4 bags of soda ash total -Barry pumped out influent chamber where influent flowmeter is -cleaned RAS chamber, cleaned alum injection chamber -picked up SRL?s and davit arms for inspection at 380 Bayview -inspected aeration blowers -station okay | Mount Albert Water Resource Recovery Facility | 2025-11-24
WW-CEAST | November | -station check of site completed by Barry Middleton, data entered into SharePoint -lab analysis completed, data entered into SharePoint -added 1 bag of soda ash per aeration tank -reviewed SCADA -inspected site -decanted sludge thickening tank, wasted remaining sludge to holding tank -wasted 5 m3 of sludge from clarifier 1, clarifier 2 is OOS for launder cover install -sampling point on clarifiers blocked due to launder covers -ran RAS pumps at 100% speed to clear rags after wasting -snow has not been removed from site at 13:35 -station okay | Mount Albert Water Resource Recovery Facility | 2025-11-28
WW-CEAST | November | Weather today Clear and -1 Celsius -On site to complete work orders W11380029, W11390006, W89793, W11388963, W11389780, W11389767. -Completed in-house lab analysis and station check. -Entered lab and station readings into SharePoint. -Post filtration/UV channel hose down. -Post aeration alum mixing chamber clean out. -RAS/WAS inlet channel inspection and hose down. -Reset composite sampler for tomorrow. -Ran RAZ pumps #1 at 100% to clear them out for a bit - all back to auto as well as speed back to auto. -Added two bags of soda ash to each aeration tank. -Decanting STT into the Headworks. -Transferred the sludge and processing. -Odour control system Still OOS. | Mount Albert Water Resource Recovery Facility | 2025-11-20
WW-CEAST | November | -Completed in-house lab Analysis (See details on SharePoint) -Transferred the sludge and processing. -Batch wasted 16m3 -Flushed sand filter - reject drain line | Mount Albert Water Resource Recovery Facility | 2025-11-25
WW-CEAST | November | Weather today Overcast and 9 Celsius -On site to complete work orders W11396438, W11401734, W1145767, W11459168, W11361271, W11362295, W11361283, W11362692. -Completed station check. -Entered station readings into SharePoint. -Operator support for headworks building channel coating inspection. -Travelling screen maintenance. -Grit vortex 1 and 2 maintenance. -Screw Press maintenance. -Reset composite sampler for tomorrow. -Ran RAZ pumps #1 at 100% to clear them out for a bit - all back to auto as well as speed back to auto. -Added two bags of soda ash to each aeration tank. -Decanting STT into the Headworks. -Transferred the sludge and processing. -Clarifier 2 is now isolated, also partially drained and put out of service to accommodate the works to be done by contractor. -Odour control system OOS. -RAS Pump 1 and WAS Pump 1 in manual off and out of service.? | Mount Albert Water Resource Recovery Facility | 2025-11-26
WW-CEAST | November | -station check and lab analysis completed -lab data entered into SharePoint -reviewed SCADA -inspected site -started decant pump, drained sludge from thickening tank to sludge holding tank -added 4 bags of soda ash to aeration tanks -did not batch waste, trying to build up sludge and bugs to help total phosphorus in the effluent. Recommendation from Team Lead Daniel Kim -ran RAS pumps manual speed 100% after to clear rags, back to auto speeds -UV maintenance on UV reactor 1A, switched duty to UV reactor 1B, cleaning UV reactor 1A -adjusted requested volume to be wasted from 40 m3 to 35m3, to build up bugs, upon Team Lead Daniel Kim?s suggestion -put UV reactor 1A back to duty 1, no alarms, seems to be running no issues -contractors on site to switch crane/lifting base for decant pump in screen room -station okay | Mount Albert Water Resource Recovery Facility | 2025-11-19
WW-CEAST | November | On site completed work orders. -completed in-house lab Analysis (See details on SharePoint) -Decanting STT into the Headworks. -Transferred the sludge and processing. -Batch wasted 5m3. -DO meter verification work order completed. | Mount Albert Water Resource Recovery Facility | 2025-11-11
WW-CEAST | November | Onsite for annual calibrations Informed ROC Used cal mode on scada during the work Instruments calibrated: DO, pH, Air FIT?s and FITs Headworks FIT failed verification. Chamber is flooded. Will return to repair. FIT is working for now Cleared all associated alarms Informed ROC and left site | Mount Albert Water Resource Recovery Facility | 2025-11-20
WW-CEAST | November | Weather today Overcast and 5 Celsius -On site to complete work orders W11360441, W11372589, W11372373, W11372386. -Completed in-house lab analysis. -Entered lab readings into SharePoint. -Post aeration alum mixing chamber clean out. -RAS/WAS inlet channel inspection and hose down. -Reset composite sampler for tomorrow. -Ran RAZ pumps #1 and #3 at 100% to clear them out for a bit - all back to auto as well as speed back to auto. -Added two bags of soda ash to each aeration tank. -Decanting STT into the Headworks. -Transferred the sludge and processing. -Batch wasted 5m3 from Clarifier #1. -Ras pump #3 back in service. -Odour control system OOS. | Mount Albert Water Resource Recovery Facility | 2025-11-13
WW-CEAST | November | Completed station check/lab/sludge process. Batch wasted 20m3 in total and dosed total of 4 soda ash bags into the aeration. Noticed both sludge blowers in Local with Estop pressed in. Put both units back in service. Vortex blower 2 has been found Local as well, place the unit back in auto Changed auto wasting setpoint from 35m3 to 40m3 in response to increase in TSS/MLSS | Mount Albert Water Resource Recovery Facility | 2025-11-16
WW-CEAST | November | Weather today Overcast and 1 Celsius -On site to complete work orders W113380029, W11412261, W11378893, W11379692, W11379679, W11340365. -Completed in-house lab analysis. -Entered lab readings into SharePoint. -Post aeration alum mixing chamber clean out. -RAS/WAS inlet channel inspection and hose down. -Effluent Sewer chamber inspection and Sluice gate valve exercise. -Oak Ridges AMF Bubble Dampers Training. -Ran RAZ pumps #1 and #3 at 100% to clear them out for a bit - all back to auto as well as speed back to auto. -Added two bags of soda ash to each aeration tank. -Decanting STT into the Headworks. -Transferred the sludge and processing. -Batch wasted 20m3 from Clarifier 1 and 2 -Odour control system OOS. | Mount Albert Water Resource Recovery Facility | 2025-11-17
WW-CEAST | November | -station check of site -reviewed SCADA -inspected facility, completed plant rounds -added 4 bags of soda ash to aeration tanks -cleaning clarifier 2 -Matt Turner and Terry Cantwell replaced wire on decant pump hoist with new stainless steel wire -tested decant pump, working as intended -UV channel hose down -began diverting clarifier effluent to lagoon at 10:05 for clarifier 2 cleaning, initial influent totalizer for the day was 377 m3 -finished cleaning clarifier 2, have to wait an hour before cancelling diversion as algae can overflow to sand filters and clog sand filters, Barry will stop diversion and record influent totalizer after diversion is stopped -will notify ENV_Incident_notification once diversion is complete -off site at 11:05 -Barry stopped diverting clarifier effluent to lagoon at 12:05, diversion was from 10:05 to 12:05, and the approximate amount diverted was 93 m3 of clarifier effluent -Barry emailed ENV_Incident_Notification | Mount Albert Water Resource Recovery Facility | 2025-11-13
WW-CEAST | November | -station check of site and lab analysis completed -data entered into SharePoint -reviewed SCADA -started decant pump, decanted sludge thickening tank -sludge from thickening tank sent to sludge holding tank -decant pump off, wasted 20 m3 of sludge from clarifiers to thickening tank -added 4 bags of soda ash to aeration tanks -full oil change for clarifier 1 gear ring -Barry dropped off lab samples to 145 HWP for pickup -put bin out for pickup -station okay | Mount Albert Water Resource Recovery Facility | 2025-11-18
WW-CEAST | November | On site to replace the air regulator on filter #1. Air is on to the filter | Mount Albert Water Resource Recovery Facility | 2025-11-11
WW-CEAST | November | Weather today Snow and -3 Celsius -On site to complete work orders W11360441, W11363719, W11362736, W11364311, W11362238, W11362347, W113362320, W11361211. -Completed station check. -Entered station readings into SharePoint. -Collected weekly sewage samples at 8:40 am under W11363719. -Reset composite sampler for weekend sampling. -Ran RAZ pumps #1 and #2 at 100% to clear them out for a bit - all back to auto as well as speed back to auto. -Added two bags of soda ash to each aeration tank. -Sand filter filter-reject drain line flush. -Grit tank Blowers 1 and 2 inlet filter, pulleys, and oil check. -Sludge holding tank Blowers 1 and 2 inlet filter, pulleys, and oil check. -Sump Pumps maintenance. -Odour control system OOS. -Ras pump #3 in manual OOS. | Mount Albert Water Resource Recovery Facility | 2025-11-11
WW-CEAST | November | -completed in-house lab Analysis (See details on SharePoint) -Decanting STT into the Headworks. -Transferred the sludge and processing. -Added two bags each of Soda Ash into each Aeration Tanks -STT decanting pump snapped off the steel cable and fell into the tank. Created CMU for maintenance to re-attach it. | Mount Albert Water Resource Recovery Facility | 2025-11-12
WW-CEAST | November | Weather today Partly Cloudy and 0 Celsius -On site to complete work order W113380029, W11382186, W11382811, W11383366, W11362359, W11361279. -Completed station check. -Entered station readings into SharePoint. -Sand filter filter-reject drain line flush. -Scum pump 1 and 2 inspection. -Grit dewatering screw press maintenance. -Collected weekly raw sewage samples at 9:10 am under W11382811. -Ran RAZ pumps #1 and #3 at 100% to clear them out for a bit - all back to auto as well as speed back to auto. -Added two bags of soda ash to each aeration tank. -Decanting STT into the Headworks. -Transferred the sludge and processing. -Batch wasted 20m3 from Clarifier 1 and 2 -Odour control system OOS. | Mount Albert Water Resource Recovery Facility | 2025-11-18
WW-CEAST | November | Weather today Clear and 0 Celsius -On site to complete work orders W11360441, W11375811, W11262387, W11362373. -Completed in-house lab analysis. -Entered lab readings into SharePoint. -Post aeration alum mixing chamber clean out. -RAS Pump 1, 2, and 3 inspection. -WAS Pump 1 and 2 inspection. -Reset composite sampler for weekend. -Ran RAZ pumps #1 and #3 at 100% to clear them out for a bit - all back to auto as well as speed back to auto. -Added two bags of soda ash to each aeration tank. -Decanting STT into the Headworks. -Transferred the sludge and processing. -Batch wasted 20m3 from Clarifier #1. -Ras pump #3 back in service. -Odour control system OOS. | Mount Albert Water Resource Recovery Facility | 2025-11-14
WW-CEAST | November | -station check of site -reviewed SCADA -inspected site -entered data into SharePoint -added 4 bags of soda ash to aeration tanks total -tested air compressors for sand filters locally to test low and high pressure alarms, for Capital Delivery Team -air compressors failed to locally shutdown on high pressure switch -high pressure alarms for air compressors were due to the testing, reset all air compressor alarms, notified ROC | Mount Albert Water Resource Recovery Facility | 2025-11-14
WW-CEAST | November | -on site to complete lab analysis and sludge handling -added 4 bags of soda ash to aeration tanks -decanted sludge thickening tank, drained remaining sludge to holding tank, decant pump off -wasted 20 m3 of sludge from clarifier to thickening tank -ran RAS pumps at 100% manually to clear debris, RAS pumps back auto -uploaded lab data to SharePoint -inspected outfall chambers, beaver dams on both sides of roadway, notifying Supervisor Graham Beach -did a full oil change on clarifier 2 gear oil, to prevent arm from freezing in winter -station okay | Mount Albert Water Resource Recovery Facility | 2025-11-17
WW-CEAST | November | Onsite to get supernatent pump out of sludge tank. Operator had hooked pump Raised pump and removed from tank Removed rotted cable Sourced cable Will return to complete repair tomorrow. | Mount Albert Water Resource Recovery Facility | 2025-11-12
WW-CEAST | November | -station check of site -completed plant rounds -data entered into SharePoint -inspected blowers for sludge thickening tank -flushed sand filter reject drain -ensured clarifier gear box heaters were on and producing heat -inspected and tested scum pumps | Mount Albert Water Resource Recovery Facility | 2025-11-12
WW-CEAST | November | Replacing super Nate lifting cable with SS Reinstalled and tested. | Mount Albert Water Resource Recovery Facility | 2025-11-13
WW-CEAST | November | Weather today Light snow and -5 Celsius -On site to complete work order W11360441, W11359775, W11358830, W11335813, W11335837, W11340627, W11356020, W11354918, W11355195. -Completed station check. -Entered station readings into SharePoint. -Standby Power Generator Test Run. -JHSC Health and Safety Inspection. -Hazardous Waste Collection and Removal. -Bypass Sampling Kit, Check. -Hoist System, Inspection. - Check valve inspection. - Dry well flood alarm test. - Sump pit inspection. - RS pump motor / inspection. -Pump #1 speed 47% = 45.2 L/s. -Pump #2 speed 51% = 39.2 L/s. - RS pump grease / inspection. - Autodialer test.? -Checked dry well, ok. | Mount Albert Pumping Station | 2025-11-10
WW-CEAST | November | Weather today Partly cloudy and 4 Celsius -On site to complete work order W11354794. -Completed station check. -Entered station readings into SharePoint. -Checked dry well, ok | Mount Albert Pumping Station | 2025-11-07
WW-CEAST | November | Station Check (See details on SharePoint). Both pumps available in all-stop auto duty rotation. Standby power generator available in auto. Checked dry well, ok. | Mount Albert Pumping Station | 2025-11-03
WW-CEAST | November | Weather today Clear and 7 Celsius -On site collected weekly raw sewage samples at 10:55 am under W11343369, W11343355. -Rinsed composite sample container. -Reset composite sampler for next week raw sewage samples collection. | Mount Albert Pumping Station | 2025-11-04
WW-CEAST | November | -station check of site -reviewed SCADA -entered data into SharePoint -inspected site -activated duty and tested system, all okay -site okay | Mount Albert Pumping Station | 2025-11-20
WW-CEAST | November | -On site to collect weekly samples - W11398761. -Collected samples, flushed sample jug with hot water, reset composite sampler for 0700 December 1. | Mount Albert Pumping Station | 2025-11-25
WW-CEAST | November | Weather today A few clouds and 4 Celsius -On site to complete work orders W11356002, W11396368, W11394998. -Completed station check. -Entered station readings into SharePoint. -Consolidated wet well inspection. -Comprehensive housekeeping. -Both pumps available in all-stop auto duty rotation. -Standby power generator available in auto. -Checked dry well, ok. | Mount Albert Pumping Station | 2025-11-24
WW-CEAST | November | Weather today Snow and -1 Celsius -On site to complete work order W11406135. -Completed station check. -Entered station readings into SharePoint. -Both pumps available in all-stop auto duty rotation. -Standby power generator available in auto. | Mount Albert Pumping Station | 2025-11-28
WW-CEAST | November | Weather today Snow and -3 Celsius -On site collected weekly raw sewage samples at 9:20 am under W11363719. -Rinsed composite sample container. -Reset composite sampler for next week raw sewage samples collection. | Mount Albert Pumping Station | 2025-11-11
WW-CEAST | November | Weather today Ovaercast and -1 Celsius -On site to complete work orders W11378566, W11383554. -Completed station check. -Entered station readings into SharePoint. -2 tonne Hoist system inspection. -Both pumps available in all-stop auto duty rotation. -Standby power generator available in auto. -Checked dry well, ok. | Mount Albert Pumping Station | 2025-11-17
WW-CEAST | November | Weather today Partly Cloudy and 0 Celsius -On site collected weekly raw sewage samples at 10:00 am under W11382811. -Rinsed composite sample container. -Reset composite sampler for next week raw sewage samples collection. | Mount Albert Pumping Station | 2025-11-18
WW-CEAST | November | Weather today Clear and 0 Celsius -On site to complete work order W11374922. -Completed station check. -Entered station readings into SharePoint. -Both pumps available in all-stop auto duty rotation. -Standby power generator available in auto. -Checked dry well, ok. | Mount Albert Pumping Station | 2025-11-14
WW-CEAST | November | -On site to complete work orders. -Consolidated wet well work orders completed. -Bar screen cleaning and lubrication completed. -Screw conveyor cleaning and lubrication completed. -Sluice gate valve exercises completed, all valves fully exercised. -Wet well cleaning and inspection completed. -Wet well valve exercises completed. -Tipping bucket operational checks completed, tested each bucket multiple times, hosed down inside of north EQ to remove bugs and spider webs. -Consolidated surge tank inspection work orders completed: -Surge tank and system inspection completed. -Surge tank valve exercises and inspection completed. -Surge tank drain valve exercise and flush completed. -Surge tank transmission lines flushed. -Facility overflow inspection completed. -Wet well high level alarm test completed and confirmed by ROC. -Pump 2 remains OOS for repairs. | Newmarket Sewage Pumping Station & Equalization Tank | 2025-11-06
WW-CEAST | November | Took station readings and entered into SharePoint,, reviewed trends and checked both compressors oil/belts OK. Checked pump floor - all looks good - gonna grab a bucket from Bogey to carry up some rags on the floor. Levelled off the bin in the screening room and attached 2 - 25ft length of hose for wash down with a new nozzle as well. Station running under normal ops - pump 2 is still OOS. | Newmarket Sewage Pumping Station & Equalization Tank | 2025-11-10
WW-CEAST | November | NMEQBP Informed ROC. Onsite to perform annual calibrations. Used the calibration mode during the work. Devices were done as below : all gas detectors, Pump FITs, WPS_FIT. Put everything back in service. All the related alarms were cleared. No issues. Informed ROC, armed the building and left the site. | Newmarket Sewage Pumping Station & Equalization Tank | 2025-11-10
WW-CEAST | November | Helped Bill and Christian get bar screen 1 running again,, opened up channel gate for bar screen 1 after turning it back on (took LOTO off panel switch.) - Christian also greased all the sprockets on the bar screen, levelled off bin and pushed the empty one back into the screening room. Emptied garbage cans in the building into the rag bin. Took station readings and entered into SharePoint,, reviewed trends - all OK. | Newmarket Sewage Pumping Station & Equalization Tank | 2025-11-03
WW-CEAST | November | On site for bar screen 1oos found missing roller skates and one missing 2 bolts. Replaced the roller and put it back in auto. Also open the channel | Newmarket Sewage Pumping Station & Equalization Tank | 2025-11-03
WW-CEAST | November | Here to complete WO?s - Checked out Diesel - oil/coolant and batteries all OK - informed ROC then activated pumps at Second Con as well as Greenlane,, after they completed their cycle I shut down the pump at Newmarket and switched over to Diesel. Switch over went fine - all stations clear of alarms - put all 3 pumps at Newmarket back into auto. Completed station check and entered readings into SharePoint,, reviewed trends - emptied all the garbage and also emptied the top of the auger,, flushed out the rinse port and washed down the floor/ drain hose for auger and the stairs heading to the wet well. Bin is out for pick up and checked both compressors oil/belts OK. Verified operation of all cranes - no issues,, checked Second Con PS and put Greelane pumps into manual and switched back to main power - no issues with transfer back and I cleared alarms at all stations. Mopped out washroom and office and vacuumed main floor (full of bugs). No Hazardous waste to dispose of,, re- organized the shelving and also completed H&S check - all good. | Newmarket Sewage Pumping Station & Equalization Tank | 2025-11-05
WW-CEAST | November | Levelled out the bin in the screening room emptied the top of the auger as well then pushed bin out for pickup. Washed down the floor and flushed out the drain hose s well as the screen for the auger. Set up new bin and emptied garbage to the bin getting picked up. Had to leave for Bogey appt. Back and I took station readings and entered into SharePoint,,, reviewed trends - all pumps are good. Cleaned washroom and office. Checked both compressors oil/belts OK. Pump 2 is OOS | Newmarket Sewage Pumping Station & Equalization Tank | 2025-11-26
WW-CEAST | November | Took station readings and entered into SharePoint,, reviewed trends - pump flow - OK,, checked pump floor and cleaned up tools a bit. Levelled out bin in the screening room and cleaned out the top of the auger,, flushed out screen as well as the drain hose. Washed down floor and emptied garbage from the office. Swept out office and washroom. Station running under normal ops - pump 2 is OOS. | Newmarket Sewage Pumping Station & Equalization Tank | 2025-11-24
WW-CEAST | November | On site assisted Property Sevices for the audible testing of Fire Alarm System. Also, completed Station Check (See details on SharePoint) All pumps available in timed auto duty rotation every 3 hours, except, pump 2, which is still out of service for repair. Pump taken out of site. Standby power generator available in auto. Checked dry well. Checked bar screens. Ran dewatering pump at the EQ Tanks to lower the water/sewage level from 2.02m to 0.53m. | Newmarket Sewage Pumping Station & Equalization Tank | 2025-11-21
WW-CEAST | November | -On site to respond to Mechanical Screen 2 Fault Alarm reported by ROC. Cleared fault and ran bar screen 2 for multiple cycles in local and auto with no issues. | Newmarket Sewage Pumping Station & Equalization Tank | 2025-11-23
WW-CEAST | November | On site completed work orders. Station Check (See details on SharePoint) All pumps available in timed auto duty rotation every 3 hours, except, pump 2, which is still out of service for repair. Pump taken out of site. Standby power generator available in auto. Checked dry well, ok. Checked bar screens. Levelled out the bin in the screening room and emptied the top of the auger. Cleaned/hosed down the floor and flushed out the drain hose as well as the screen for the auger. Pushed rag bin back inside the screen room after picked up by Miller Waste yesterday. Consolidated Monthly Dry Well Pump Floor Inspection Dry Well Flood alarm Test - received and confirmed by ROC. Sump Pit Inspection Auto Dialer Alarm Test - 3 times tested but not received by ROC. Created work order (W11475581) to CMS to check the issue. Air Compressor Inspection High Low Temp Alarm Test - Station don?t have the capability to test the high low temperature alarm, however, it will alarm when the temperature is above or below temperature setpoints. RS Pump and Motor Inspection Pump 1 - @ 0% speed: 120 L/s, 139 kPa, 108 Amps, 617 V, 39 Hz; @35% speed: 230 L/s, 158 kPa, 153 Amps, 617 V, 46 Hz Pump 2 - Out of service. Pump 3 - @ 0% speed: 156 L/s, 135 kPa, 126 Amps, 371 V, 769 RPM, 39 Hz; @ 35% speed: 256 L/s, 150 kPa, 181 Amps, 445 V, 920 RPM, 46 Hz Pump 4 - @ 0% speed: 140 L/s, 125 kPa, 99 Amps, 615 V, 39 Hz; @ 35% speed: 239 L/s, 122 kPa, 155 Amps, 614 V, 46 Hz Check Valves Inspection | Newmarket Sewage Pumping Station & Equalization Tank | 2025-11-28
WW-CEAST | November | NMEQBP-Recalibrated the LEL sensor and all alarms were reset. | Newmarket Sewage Pumping Station & Equalization Tank | 2025-11-11
WW-CEAST | November | Took station readings and entered into SharePoint,, reviewed trends - all pump flows look good. Checked both compressors oil/belts and air filter - ok,, checked the sampling kit - seal not broken - all good. Levelled out the bin in the screening room and pushed it out for pick up,, set up a new bin. Emptied the top of the auger ,, cleared fault on conveyor 2 and cleaned up the mess - screen and floor still clean from Monday. Exercised all suction valves and discharge valves, greased the valves as well. Could not do pump 2 as it is isolated and drained. Checked the seal water system and the 3 running pumps are fine, could not fined a back up tank. All alarms cleared and station back to normal ops. | Newmarket Sewage Pumping Station & Equalization Tank | 2025-11-19
WW-CEAST | November | Here for pump 1 - no flow. Isolated pump and put it in Local,, drained pump and after morning meeting pulled a massive rag ball out of pump. Buttoned pump back up and opened the suction gate and discharge valve and primed the pump. Put pump 1 back into Duty 1 to see the flow,,, had to run the stairs 4 times and kept priming the pump before I finally got good flow. Left pump 1 in Duty 1 - @ 25% flow was 300L/s. | Newmarket Sewage Pumping Station & Equalization Tank | 2025-11-11
WW-CEAST | November | -On site to complete work orders. -Entered station readings into SharePoint. -Air compressors inspection and cleaning completed. -Checked drywell, removed piles of rags from pumps floor. -Checked screen room, changed out rag bin, cleaned floor and conveyor, bar screen oil full. -Bar screen bin removal completed. -Station check completed. -Pump 2 remains OOS. | Newmarket Sewage Pumping Station & Equalization Tank | 2025-11-12
WW-CEAST | November | Took station readings and entered into SharePoint,, reviewed trends and all is good. Checked both compressors and oil/belts - OK. Levelled the bin in the screening room and washed down floor and cleared the screen drain and the hose drain as well. Cleaned the back of the bar screens and squeegeed the floor. Oil for bar screen is OK. Pump 2 is OOS still but the rest of the station is running as per normal. | Newmarket Sewage Pumping Station & Equalization Tank | 2025-11-17
WW-CEAST | November | Took station readings and entered into SharePoint,, reviewed trends - all pumps working well ,, pump 2 is OOS due to maintenance rebuild. Checked both compressors oil/belts - all good. Levelled off bin in the screening room and emptied the top of the auger - flushed the drain screen as well as the drain line. Pushed bin back into the screening room and checked both bar screen oilers - all good. Took some of the rags from the pump clogs off the pump floor and put them in the bin. Emptied submersible pump from my truck as well as generator and hoses. Pump 2 is still OOS but station is running as per normal. | Newmarket Sewage Pumping Station & Equalization Tank | 2025-11-14
WW-CEAST | November | Station check complete and the readings have been entered into the sharepoint. Found generator room louver wide open and brining in cold air into the room. Closed the louver with using the thermostat. | Newmarket Bogart Creek Sewage Pumping Station | 2025-11-07
WW-CEAST | November | Took station readings and entered into SharePoint,, reviewed trends - all looks good. Verified wet well fans are off due to the cold air. Completed Diesel test run - no issues with transferring over and back and a pump (3) ran a couple of times - entered readings into SharePoint also H & S inspection- no issues found and no hazardous waste to dispose off. Verified operation of all 3 cranes, also station was pretty clean so I swept the MCC?s and walls cause of the cob webs. Station back to running on main power - all alarms cleared and informed ROC station is back to normal operation. | Newmarket Bogart Creek Sewage Pumping Station | 2025-11-03
WW-CEAST | November | Met with Town of Newmarket water to figure out the water meter,, they tried a few things but are going to half to re schedule to run a new line or replace meter | Newmarket Bogart Creek Sewage Pumping Station | 2025-11-26
WW-CEAST | November | On site completed Station Check (See details on SharePoint) All pumps available in timed auto duty rotation every 3 hours. Standby power generator available in auto. Ran pump 2 in local for a few minutes with a flow of 193.2 L/s at 110 kPa. Cleared building hi/lo temperature alarm. Diesel room is cold due to ventilation louver open. Turned up thermostat to 27 C, louver closed. Checked dry well, ok. Station operations normal. | Newmarket Bogart Creek Sewage Pumping Station | 2025-11-28
WW-CEAST | November | Took station readings and entered into SharePoint,,, reviewed trends - all good. Checked pump floor - no issues. Station running under normal ops - no issues found. | Newmarket Bogart Creek Sewage Pumping Station | 2025-11-24
WW-CEAST | November | Onsite for annual calibrations Informed ROC Used cal mode on scada during the work Instruments calibrated: FITs, LITs, PIT and gas detectors Cleared associated alarms Informed ROC Armed building and left site | Newmarket Bogart Creek Sewage Pumping Station | 2025-11-19
WW-CEAST | November | -On site to perform a station check. -Entered station readings into SharePoint. -Checked drywell. -Ran pump 2 in local for one duty cycle, flows normal at 190L/s. -Supply fan off for winter. | Newmarket Bogart Creek Sewage Pumping Station | 2025-11-21
WW-CEAST | November | -On site for air valve chamber inspection. -Significant amount of groundwater in chamber, Meter Chamber 2 Flood Alarm active on site. -Pumped out groundwater from chamber, sump pit connected to Meter Chamber 1. -Cleared debris away from storm water grates and surrounding area. -Completed chamber inspection, no other issues noted. -Reset and cleared chamber flood alarm on SCADA. | Newmarket Bogart Creek Sewage Pumping Station | 2025-11-13
WW-CEAST | November | Took station readings and entered into SharePoint,, reviewed trends - all pumps have good flow, check valves are all good - air valves are all good. Also checked the odour control unit - no issues found. Verified Dry well flood alarm,Building Hi/Low Temp alarm and dialer alarm - all confirmed by ROC. Flushed the sump pit out and ran 4 cycles with the sump pump with no issues. Cleared all alarms and station is back to normal operation. | Newmarket Bogart Creek Sewage Pumping Station | 2025-11-14
WW-CEAST | November | Took station readings and entered into SharePoint,, reviewed trends - all looks good. Checked pump floor - no issues found. Swept up the main floor and some of the walls due to spider webs. | Newmarket Bogart Creek Sewage Pumping Station | 2025-11-17
WW-CEAST | November | Took station readings and entered into SharePoint,, reviewed trends - all good. Exercised inlet valves (partial) except on the Duty 1 pump and exercised discharge valves - the ones that would work. Station running under normal ops - all alarms were cleared except Temp alarm. | Newmarket Bogart Creek Sewage Pumping Station | 2025-11-10
WW-CEAST | November | On site completed work orders. Station Check (See details on SharePoint) H2O2 Pump 3 has leak and fault alarms happened on Nov 3rd at 9:35am. Investigated today, was not able to clear the alarm as any touch on the screen buttons of the pump would not do anything but prompt a message "stop the pump first", although pump is NOT running. Due to this reason, was not able to use the flushing system to safely open up the tube housing, which has moisture inside the glass. Currently, it is confirmed, H2O2 Pump 2 is running in auto as duty 1 to Shaft 13B with a flow of 15.6 L/hr at 18% speed. H2O2 Pump 1 in manual/off. JHSC Health and Safety Inspection - eye wash alarm cleared/reset. Comprehensive Housekeeping - cannot completely do housekeeping due to so many contractor?s belongings on site. | SEC Boxgove Corrosion Control Facility | 2025-11-04
WW-CEAST | November | Station check complete and the readings have been entered into the sharepoint. H2O2 tank 2 low level alarm outstanding, chemical delivery scheduled for tomorrow to fill it back up. Reviewed set up/procedure for the scheduled delivery All dosing pumps are working as intended. Closed MV2 on shaft 13A for CD to take H2S sample @ shaft 13C | SEC Boxgove Corrosion Control Facility | 2025-11-25
WW-CEAST | November | -on site to receive hydrogen peroxide delivery -Tank 2 Start: 0.54m/4842L -Tank 2 Start: 1.22m/11027L -delivery was successful -flushed drain on fill line after delivery, reclosed flush valve -valve to top of tank closed -inspected site, all okay -have a few work orders to exercise sluice gates on site, will remain on site and restore valves to current positions after | SEC Boxgove Corrosion Control Facility | 2025-11-26
WW-CEAST | November | Station check complete and the readings have been entered into the SharePoint. Ventilation system inspection complete. Changed the filters. Chemical tank/pumps checked, all good. Pumps currently going though 45 day test | SEC Boxgove Corrosion Control Facility | 2025-11-18
WW-CEAST | November | Station check complete and the readings have been entered into the sharepoint. SPD on-site to troubleshoot H2O2 pump 3. We were able to flush pump 3 with temporary reset of leakage alarm. Replaced the hose/recalibrated the unit. | SEC Boxgove Corrosion Control Facility | 2025-11-11
WW-CEAST | November | On site completed work orders. Station Check (See details on SharePoint) Fans 2 and 3 currently running in auto as duty 2 and 1, respectively. Fan 3 in standby. Nutrient Tank Batch Mixing - all nutrient tanks have water. Odour Control Fans Impeller Bearing Lubrication Hoist System Inspection Blower Inspection JHSC Health and Safety Inspection - 11 lighting fixtures at the Carbon Unit Room and 3 lighting fixtures at the Fans Room, not working. These are previously reported last June 2025. Outstanding work orders request. Resubmitted request to CMS. Standby Power Generator Test Run - pre-test checked, ok. Generator started and stopped without a problem. Cleared/reset all alarms created by doing this work order. Generator back to auto and available. Station back to normal operations. | SEC Markham Odour Control Facility | 2025-11-04
WW-CEAST | November | On site completed work orders Station Check (See details on SharePoint) Fans 1 and 3 currently running in auto as duty 2 and 1, respectively. Fan 2 in auto, as standby. Standby power generator available in auto. Nutrient Tank Batch Mixing - filled up tank 2 with water. Tanks 1 and 3 full. Odour Control Fans Impeller Bearing Lubricated Damper and Knife Gate Set 3, Exercised and checked operational verification. Knife gate MV2 getting fault alarm but was able to cleared/reset. Comprehensive Housekeeping - vacuumed every rooms. Thoroughly cleaned washroom, sanitized/toilet bowl disinfected. Collected garbage. | SEC Markham Odour Control Facility | 2025-11-25
WW-CEAST | November | On site to check station and complete PMs Upon arrival, found Filter 1 recirc pump 1 and 2 had no flow but continuously running. No alarm outstanding on SCADA as alarm was found to be disabled. Found only Fan 2 running. Checked the duty screen and found only Fan 2 is active while other fans were not active. Activated all flow lolo/oor alarms for all the filter recirc pumps. Got both filter 1 recirc pumps amd filter 2 recirc pump 2 going. Placed filter 1 and 2 back in service. Also got Fan 3 going and placed it in D2. Both fans 2 and 3 running with 1% spd CMU2 created for non-working recirc pumps | SEC Markham Odour Control Facility | 2025-11-11
WW-CEAST | November | On site completed work orders Station Check (See details on SharePoint) Fans 2 and 3 currently running in auto as duty 1 and 2, respectively. Fan 1 in auto, as standby. Standby power generator available in auto. Nutrient Tank Batch Mixing - filled tanks with water. Added oil on water supply pumps. Odour Control Fans Impeller Bearing Lubricated Sump Pump Test/Maintenance Ventilation System Inspection Damper and Knife Gate Set 1, Exercised and Operational Verification Damper and Knife Gate Set 2, Exercised and Operational Verification Knife gates created alarms when exercised but was able to clear/reset all alarms. Checked Recirculation Pump 2 at Biofilter 1 for failure to start alarm as reported by ROC. Tried to run in auto/manual/local but to no avail. Totally no sound when commanded to run. Created work order no. W11452564 for CMS to check issue. Pump put in local mode/out of service. Found Recirculation Pump 1 at Biofilter 1 leaking badly at the base of the pump when running. Probably, due to rusts, which is visible all around the pump. Created work order no. W11452563 for CMS to check issue. Pump put in local mode/out of service. Also, gave access to ALECTRA staff to get the hydro meter reading at the hydro electrical cabinet. | SEC Markham Odour Control Facility | 2025-11-18
WW-CEAST | November | On site for station check (See details on SharePoint) Fan 1 currently running in auto as duty 1 with airflow of 16, 200 m3/hr. Fan 2 in auto and standby. Standby power generator available in auto. All gas monitors have normal readings. Found local SCADA OIT with blank monitor. Called ROC to call PCS/SCADA Oncall. Arthour Litvinov reset the OIT. Cannot clear/reset general HVAC alarm happened on Oct 23rd, 3:01pm. Still outstanding. | SEC Fairport Air Handling Facility (Shaft 4) | 2025-11-06
WW-CEAST | November | Test backflow preventers All 3 passed | SEC Fairport Air Handling Facility (Shaft 4) | 2025-11-03
WW-CEAST | November | On site completed work orders. Station Check (See details on SharePoint) Fan 2 currently running in auto as duty 1 with an airflow of 16,200 m3/hr at 0% speed. Fan 1 in auto as standby. Standby power generator available in auto All gas monitors have normal readings. Station operations normal. Comprehensive Housekeeping - sanitized/disinfected toilet. Collected garbage. Cleaned/vacuumed all rooms of the whole facility. | SEC Fairport Air Handling Facility (Shaft 4) | 2025-11-27
WW-CEAST | November | On site completed work orders. Station Check (See details on SharePoint) Fan 1 currently running in auto as duty 1 with an airflow of 16,200 m3/hr at 1% speed. Fan 2 in auto as standby. Standby power generator available in auto Cleared/reset O2 monitor alarm All gas monitors now have normal readings. Station operations normal. Knife Gate Valve Exercised Electric Valve Actuator Exercised and Inspected | SEC Fairport Air Handling Facility (Shaft 4) | 2025-11-20
WW-CEAST | November | On site to conduct fan pms vibration data collection | SEC Fairport Air Handling Facility (Shaft 4) | 2025-11-13
WW-CEAST | November | Weather: 3 C Cloudy Wind: 17 Kmh from WNW On site completed work orders. Station Check (See details on SharePoint) Fan 1 currently running in auto as duty 1 with an airflow of 16,200 m3/hr at 1% speed. Fan 2 in auto as standby. All gas monitors have normal readings. Heat Trace System Inspection JHSC Health and Safety Inspection - cleaned/hosed down fan room/ too much cobweb and bugs. Standby Power Generator Test Run - pre-test checked, ok. Generator started and stopped without problem. Cleared/reset all alarms. Generator back in auto and available. Station back to normal operations. HVAC alarm still outstanding. | SEC Fairport Air Handling Facility (Shaft 4) | 2025-11-13
WW-CEAST | November | On site completed work orders. Station Check (See details on SharePoint) Fan 1 currently running in auto as duty 1 with an airflow of 25,650 m3/hr at 0% speed. Fan 2 in auto as standby. Standby power generator available in auto All gas monitors have normal readings. Station operations normal. Comprehensive Housekeeping - sanitized/disinfected toilet. Collected garbage. Cleaned/swept/vacuumed all rooms of the whole facility. | SEC Altona Air Handling Facility (Shaft 6/7) | 2025-11-27
WW-CEAST | November | Weather: 6 C Mostly Sunny Wind: 15 Kmh from NW On site completed work orders. Station Check (See details on SharePoint) Fan 1 currently running in auto as duty 1 with airflow of 15, 675 m3/hr. Fan 2 in auto and standby. All gas monitors have normal readings. JHSC Health and Safety Inspection Standby Power Generator Test Run - pretest checked, ok. Generator started and stopped running without problem. Cleared/reset all alarms. Generator back in auto and available Station back to normal operations | SEC Altona Air Handling Facility (Shaft 6/7) | 2025-11-06
WW-CEAST | November | On site completed work orders. Station Check (See details on SharePoint) Fan 1 currently running in auto as duty 1 with airflow of 25,650 m3/hr. Fan 2 in auto and standby. All gas monitors have normal readings. Standby power generator available in auto. Heat Trace System Inspection Ventilation System Inspection - AHU filters dirty, replaced. Station operations normal. | SEC Altona Air Handling Facility (Shaft 6/7) | 2025-11-13
WW-CEAST | November | On site completed work orders. Station Check (See details on SharePoint) Fan 2 currently running in auto as duty 1 with an airflow of 25,650 m3/hr at 0% speed. Fan 1 in auto as standby. Standby power generator available in auto All gas monitors have normal readings. Station operations normal. Knife Gate Valve Exercised Electric Valve Actuator Exercised and Inspected | SEC Altona Air Handling Facility (Shaft 6/7) | 2025-11-20
WW-CEAST | November | On site to conduct Van PMs as well as collective vibration data | SEC Altona Air Handling Facility (Shaft 6/7) | 2025-11-13
WW-CEAST | November | -On site to perform a station check. -Heater element: 107.2F. -Hydro meter: 262676kWh. -Fan is running, condensate is draining. | Bayview & Steeles Air Management Facility | 2025-11-10
WW-CEAST | November | On site for station check. Heater Element Temp - 98.3 F Hydro Meter Reading - 261446 kWh Fan and motor running. No bad smell at time of visit. | Bayview & Steeles Air Management Facility | 2025-11-03
WW-CEAST | November | Weather: 10 C Rainy Wind: 17 Kmh from SW On site to investigate odour complaint. Case No. 4270959 Complainant: Sheida Rasi 416-995-3610 Resides at Fairfield Place North of the facility Investigated said odour complaint, walked throughout the surrounding facility, northwest and northeast of Bayview/Steeles, and at Fairfield Place, no bad odour detected. Facility operating normally. Fan and motor running. No bad odour detected inside the facility compound at time of investigation/visit. After 2 tries, was able to talked to the complainant, informing her of my findings. She said, when she opened her garage this morning, it is terribly bad odour, smells like sulphur. And also, there is smell in the street (Fairfield Place). She voiced her long frustrations. | Bayview & Steeles Air Management Facility | 2025-11-07
WW-CEAST | November | -On site to perform a station check. -Heater element: 102.0F. -Hydro meter: 265139kWh. -Station is operating normally. -Fan is running, condensate is draining, no odours detected on site. | Bayview & Steeles Air Management Facility | 2025-11-24
WW-CEAST | November | On site investigate access york OC case 4271429. Checked the equipment, all is running as intended. There is a very minor, almost unnoticeable smell where hydro meter is located. Other than that, all good. Sampled discharge stack air going out to the atmosphere with MSA gas monitor. Got result as follows: 4, 20.1, 1, 1(h2s). | Bayview & Steeles Air Management Facility | 2025-11-13
WW-CEAST | November | On site completed work orders. Station Check Heater Element Temp - 92.9 F Hydro Meter Reading - 263929 KWh Fan and motor running No bad odour detected at time of visit Station operation normal JHSC Health and Safety Inspection Odour Control Scrubber Inspection | Bayview & Steeles Air Management Facility | 2025-11-17
WW-CEAST | November | Test backflow preventers All 3 passed | SEC Pickering Odour Control Facility (York/Durham) | 2025-11-03
WW-CEAST | November | On site completed work orders. Station Check (See details on SharePoint) Nutrient tanks and pumps offline. Tanks full. Recirculation pump 1 at filter 2 running in auto. Fan 1 still OOS and in manual/off. Fan 2 running in auto. Bypass knife gate open. Standby power generator available in auto. JHSC Health and Safety Inspection | SEC Pickering Odour Control Facility (York/Durham) | 2025-11-06
WW-CEAST | November | On site completed work orders. Station Check (See details on SharePoint) Nutrient tanks batch mixing - pumps offline. Tanks full. Fan 1 running in auto. Fan 2 running in auto. Standby power generator available in auto. Completed housekeeping. | SEC Pickering Odour Control Facility (York/Durham) | 2025-11-20
WW-CEAST | November | On site completed work orders. Station Check (See details on SharePoint) Nutrient tanks batch mixing - pumps offline. Tanks full. Fan 1 running in auto. Fan 2 running in auto. Standby power generator available in auto. Blower Inspection Recirculation Pump and Strainer Inspection Booster Pump, Solenoid Valve and Media Spray Inspection | SEC Pickering Odour Control Facility (York/Durham) | 2025-11-27
WW-CEAST | November | On site to perform Van PMs, as well as recorded vibration data | SEC Pickering Odour Control Facility (York/Durham) | 2025-11-13
WW-CEAST | November | Weather: 6 C Cloudy Wind: 23 Kmh from WNW On site completed work orders. Station Check (See details on SharePoint) Fan 1 and 2 running in auto. Nutrient Tank Batch Mixing - nutrient pumps in manual/off. Nutrient tanks full of water. Standby Power Generator Test Run - pre-test checked, ok. Generator started and stopped without problem. Cleared/reset all alarms. Generator back in auto and available . Station back in normal operations. | SEC Pickering Odour Control Facility (York/Durham) | 2025-11-13
WW-CEAST | November | Loaded the truck up for the work tonight at 19th and Yonge,, arrived on site with Kevin and waited for traffic protection to set everything up. Worked on getting the valve box off and getting pieces of the insert out of the valve box then proceeded to opening the valve. Took a while to open as it?s been closed for 5 years. Took pictures and videos of the flow going across 19th ave as well as going down Yonge. Both valves are now fully opened as directed. | Central-East Wastewater Linear System | 2025-11-07
WW-CEAST | November | On site for passive odour control scrubber inspection and media replacement of Yonge St/Jefferson Forest Dr (SweetStreet). | Central-East Wastewater Linear System | 2025-11-26
WW-CEAST | November | -completed 5 vortex chamber inspections with Barry Middleton -W11392474, W11340774, W11379628, W11379530, W11379647 | Central-East Wastewater Linear System | 2025-11-25
WW-CEAST | November | On site for passive scrubbers inspection and media replacement for the following locations. Milne Lane Park Tuclor Lane/Hwy 48 | Central-East Wastewater Linear System | 2025-11-19
WW-CEAST | November | -On site for Aurora metering chamber inspection. Inspected chamber, reset chamber heater breaker which had tripped. Verified cabinet heater was working. | Central-East Wastewater Linear System | 2025-11-20
WW-CEAST | November | Weather today Mostly Cloudy and 4 Celsius On site completed inspection and media replacement of passive odour control scrubbers at the following locations: W11366145, W11366111, W11366094. -Leslie/Major Mackenzie. -Woodbine Ave/16th Ave VC. -Warden Ave/Enterprise Blvd. | Central-East Wastewater Linear System | 2025-11-12
WW-CEAST | November | -On site for chamber/sluice gate inspections/exercise. -Weather -5C and snowing. -Green Lane east gravity main, Chamber T1312-40A - unable to exercise sluice gate due to weather and location in middle of road. -Newmarket Hounds Trail meter chambers HND-136A and HND-138A inspections completed. -Newmarket SPS twin Forcemain chamber T18131-VC inspection completed. -Newmarket meter chamber 3393131-INLETN and chamber 3393131-02BN inspections completed. -Aurora-Henderson meter chamber T20264-01 inspections completed - sluice gates both fully exercised in past month during flow diversions for wet well cleaning at Henderson SPS. | Central-East Wastewater Linear System | 2025-11-11
WW-CEAST | November | -On site to complete valve exercise/inspection. -Hwy 404 trunk sewer valve chamber T9948-19 sluice gas valve exercise completed by operations several weeks ago during reinstating of 16th ave flows. -Aurora wastewater meter chamber 3393131-INLETA valve inspection completed. Replaced corroded lock on chamber hatch. | Central-East Wastewater Linear System | 2025-11-17
WW-CEAST | November | Investigated Access York OC case#4271429. Met with Tim V (Markham) @ condominium parking lot located NE corner of Bayview/Steeles intersection. Inspected 2 property MH connecting to Markham sewer. 0 H2S detected and did not observe any issues. Sewage flowing freely without obstruction. Inspected 3 YR MH (380600824, 380600825, 380600815). 0-1 PPM H2S detected. Did not observe any odor issues, sewage flowing freely about at least 20ft down. No positive pressure observed in the sewer headspace. Inspected Markham MH located along Whitelaw Ct/Fairfield Pl. O PPM H2S detected. Did not observe any issues. Inspected 1 Toronto MH west of Bayview/Steeles OCF. Plastic dish cover is installed in the MH, no odor present. Inspected 1 YR MH (380601447) with Markham. We found garbage bag in the sewer partially blocking the flow. Markham was able to use their tool to remove the garbage bag. No odor present, no other issue detected. | Central-East Wastewater Linear System | 2025-11-13
WW-CEAST | November | -On site to complete Bogart SPS Forcemain chamber inspection. | Central-East Wastewater Linear System | 2025-11-14
WW-CEAST | November | -Completed vortex chamber inspections for the following locations: -9th Line and Chruch Street -9th Line and 16th Ave -6200 16th Ave -16th Ave and Mingay Ave -16th Ave and William Berczy Blvd -16th Ave and Kennedy -Bathurst and Beverly Glen Blvd -19th Ave and Rochester Hill St -Leslie St and Performance Dr -Verified flow at all vortex chambers. Replaced multiple corroded locks and cleaned around hatches. | Central-East Wastewater Linear System | 2025-11-18
WW-WEST | November | Checked pump 4 for seal leak and no seal water. Seal area is dry Opened asco valve and checked flow okay. Checked line screens clear. Traced piping and no leaks found. Line pressure is low. Complete Checked pump 5 seal Cavity is full of sewage. Pump 5 will require a new seal. Complete. | Vaughan Black Creek Pumping Station | 2025-11-06
WW-WEST | November | Completed the station check Entered data into SharePoint Leveled the rag bin Test ran all pumps Inspected the pump seal water system Everything operating as intended | Vaughan Black Creek Pumping Station | 2025-11-07
WW-WEST | November | Raw sewage pump number three vibration data collection | Vaughan Black Creek Pumping Station | 2025-11-10
WW-WEST | November | Test ran both generators separately Put pumps in manual to pump down the wet well prior to each power transfer Completed the jhsc inspection Inspected and greased the ocu | Vaughan Black Creek Pumping Station | 2025-11-06
WW-WEST | November | Completed the station check Leveled the rag bin Turned on dry well ehus Entered data into SharePoint Everything operating as intended | Vaughan Black Creek Pumping Station | 2025-11-04
WW-WEST | November | Completed the station check Test ran each pump Entered data into SharePoint Everything operating as intended | Vaughan Black Creek Pumping Station | 2025-11-21
WW-WEST | November | - Checked station and recorded readings on SharePoint - Pushed bin out and cleaned area. Checked oil hopper, all okay | Vaughan Black Creek Pumping Station | 2025-11-25
WW-WEST | November | Called by ROC for Mechanical Screen not in auto. Arrived and found screen had a motor overload. Checked for any evidence of issues - none - reset the overload and put screen back into service. Monitored a couple cycles and noticed some hard chunks of fat in the bin. | Vaughan Black Creek Pumping Station | 2025-11-17
WW-WEST | November | - Worked with Gavin Walker - Notified ROC of the work being performed - Tested autodialer alarm. Alarm received - Tested hi and low temperature alarm. Alarm received - Exercised all wet well valves, cleaned the general area and hosed floors - Tested wet well and overflow level alarm. Alarm received - Bin has been picked up. Pushed bin back in and filled up oil hopper, all okay - Screen greased and inspected - Tested dry well flood alarm. Alarm received on SCADA and dialer - Exercised suction valve with no issues. Exercised other dry well valves - Flushed and tested air relief valves. No issues - Tested sump pit pumps by triggering floats. Turned on with no issues | Vaughan Black Creek Pumping Station | 2025-11-26
WW-WEST | November | Completed the station check Entered data into SharePoint Everything operating as intended | Vaughan Black Creek Pumping Station | 2025-11-18
WW-WEST | November | - Checked station and trends, and recorded readings on SharePoint. No new issues - Investigated building Lo temperature alarm. Unit heaters are all okay. Duct heater is turned on but the indicator light is not on. Seems like it duct heater is not getting power. Created a work order for property services Update: pushed bin out | Vaughan Black Creek Pumping Station | 2025-11-11
WW-WEST | November | - Checked station and recorded readings on SharePoint. No new issues - Levelled bin - Performed weekly pump test. Ran each pumps 1-5 manually, one at a time, and recorded readings. Check valve for pump 3 not closing. Work order already created Pump 1: 603 L/s, pressure 289 kPa Pump 2: 470 L/s at 100%, pressure 262 kPa Pump 3: 134 L/s at 100% speed, pressure 213 kPa Pump 4: 470 L/s at 100% speed, pressure 266 kPa Pump 5: 569 L/s at 100% speed, pressure 288 kPa | Vaughan Black Creek Pumping Station | 2025-11-14
WW-WEST | November | Completed the station check Entered data into SharePoint Everything operating as intended | Vaughan Humber Pumping Station | 2025-11-07
WW-WEST | November | Raked and repositioned bins. | Vaughan Humber Pumping Station | 2025-11-09
WW-WEST | November | - Assisted with Humber sample collection | Vaughan Humber Pumping Station | 2025-11-10
WW-WEST | November | Record vibration on pumps, driveshafts and motors. | Vaughan Humber Pumping Station | 2025-11-03
WW-WEST | November | Leveled the rag bins | Vaughan Humber Pumping Station | 2025-11-02
WW-WEST | November | Inspected the RS check valves Inspected the sump pit Inspected RS pumps P1: 601.4L/s P2: 618.4L/s P3: 620.9L/s P4: 626.1L/s P5: 623.9L/s Exercised fm, and suction valves Tested the dry well flood alarm, high low temp alarm and auto dialer, confirmed with ROC that these alarms were received | Vaughan Humber Pumping Station | 2025-11-03
WW-WEST | November | Collected weekly sewage sample | Vaughan Humber Pumping Station | 2025-11-04
WW-WEST | November | Inspected the ydss diversion chamber | Vaughan Humber Pumping Station | 2025-11-05
WW-WEST | November | Completed the station check Entered data into SharePoint Everything operating as intended Placed the film rag bins outside for pick up | Vaughan Humber Pumping Station | 2025-11-04
WW-WEST | November | Leveled the rag bins | Vaughan Humber Pumping Station | 2025-11-23
WW-WEST | November | - Checked station and recorded readings on SharePoint - Pushed bins out and cleaned area - Worked with Lance Johnson and maintenance to free up jammed bar screen 2. Isolated equipment, wet well 2, bar screen 2 and closed interconnect valve. Disabled low level lockout and pumped down wet well 2 to draw down channel. Once pumped down, placed pumps 3~5 into manual off, and placed wet well 2 out of service on setpoints - Removed large piece of wood. After work was finished, tested bar screen 2 after removing lock out with no issues. Placed wet well 2 back in service. Opened interconnect between wet well 1 and 2. Opened wet well 2 and bar screen isolation valve. Placed bar screen 2 back in auto. Placed pumps 3-5 in auto. Observed couple operation cycle with no issues | Vaughan Humber Pumping Station | 2025-11-25
WW-WEST | November | Bar screen 2 overtorqued Could not reset the bar screen Closed the screen inlet gate to isolate it | Vaughan Humber Pumping Station | 2025-11-24
WW-WEST | November | On site for bar screen 2 jam. With the operator?s help we drained the channel and removed a 4+4 40? long piece of wood. Test ran the screen and put it back in service | Vaughan Humber Pumping Station | 2025-11-25
WW-WEST | November | Informed ROC. Performed annual calibration and put instruments in Cal mode while doing the tasks. Devices done were PITs, FITs and LITs. All alarms were cleared after the job. No other issues encountered. | Vaughan Humber Pumping Station | 2025-11-24
WW-WEST | November | Completed the station check Entered data into SharePoint Pushed the empty rag bins back inside Leveled the rag bins Everything operating as intended | Vaughan Humber Pumping Station | 2025-11-21
WW-WEST | November | Worked (on site, not remotely) with team on bar screen . | Vaughan Humber Pumping Station | 2025-11-25
WW-WEST | November | - Worked with Gavin Walker - Notified ROC of the work being performed - Tested wet well overflow alarms. Wet well 1 and 2 hi level alarm received on dialer. Wet well 1 and 2 metro overflow alarm received on SCADA. Confirmed by ROC - Exercised all wet well valves and cleaned the general area - Bin has been picked up. Pushed bin back in and checked oil hopper, all okay. - Screen greased and inspected yesterday - Tested dry well flood alarm. Alarm received on SCADA. Tested dialer alarm. Both alarms received by ROC - Exercised all valves in dry well. Pump 3 inlet isolation is a bit stiff but rest are okay | Vaughan Humber Pumping Station | 2025-11-26
WW-WEST | November | Placed the empty rag bins back in the screen room, leveled the rag bins On site to assist with the semi annual diesel maintenance Placed the pumps in manual to pump down the wetwell prior to each power transfer After transfer, returned the pumps to auto Inspected the heat exchanger Completed the JHSC inspection Cleaned up around site | Vaughan Humber Pumping Station | 2025-11-13
WW-WEST | November | Unshelved Pump 3 VFD Not Ready Alarm. | Vaughan Humber Pumping Station | 2025-11-13
WW-WEST | November | On site for weekend scheduled work. Levelled bin | Vaughan Humber Pumping Station | 2025-11-15
WW-WEST | November | - Checked station and recorded readings on SharePoint. No new issues - Levelled bin | Vaughan Humber Pumping Station | 2025-11-14
WW-WEST | November | Completed the station check Entered data into SharePoint Placed the full rag bins outside for pickup Everything operating as intended | Vaughan Humber Pumping Station | 2025-11-18
WW-WEST | November | Collected the weekly samples | Vaughan Humber Pumping Station | 2025-11-18
WW-WEST | November | -Checked station and recorded trends. No new issues - Collected weekly regulatory samples - Pushed bins out | Vaughan Humber Pumping Station | 2025-11-11
WW-WEST | November | Completed daily lab and station check - no new issues. Added data into SharePoint. Added 7 bags of soda ash to hopper. Completed maintenance on clarifiers 1 and 2. Assisted young with air compressor maintenance. | Kleinburg Water Resource Recovery Facility | 2025-11-06
WW-WEST | November | Enabled 200 minute ras timer at 9:20. Set auto wasting for 20 m3 between 11:00 and 12:00 in 4 cycles. Set was pumps to auto. Added 5 bags soda ash to ash hopper. | Kleinburg Water Resource Recovery Facility | 2025-11-09
WW-WEST | November | On site for bar screen and press no power alarms. Found this to be the case. Called on-call electrician. Added 8 bags soda ash to hopper. Kyle Rae found heat trace for the screw was causing power fuses to blow in the screen and press control panel. Turned heat trace off. Will create work order to have heat trace repaired. (W11428320) | Kleinburg Water Resource Recovery Facility | 2025-11-08
WW-WEST | November | On site with operations to investigate loss of power to Mechanical Bar Screen panel. Found opened fuse feeding 120v control transformer. Further investigation found cause to be faulty heat trace. Heat trace currently inoperative and requires investigation and possible replacement. Mechanical Bar Screen panel reenergized and returned to normal operation. ROC notified. | Kleinburg Water Resource Recovery Facility | 2025-11-08
WW-WEST | November | - Inspected air compressor 1 and 2. Oil, filter and belt are all good. Tested drain, no issues | Kleinburg Water Resource Recovery Facility | 2025-11-06
WW-WEST | November | Completed daily lab and station check - no new issues. Added data into SharePoint. Stopped RAS pumps at 9:20am. Manually wasted 30m3 from WAS pump 2 (clarifier 2 ) from 10:20am to 12:15pm. No wasting from clarifier 1 to bring solids up. RAS resumed at 12:20 pm Added 9 bags of soda ash to hopper. Finished draining outside section of offline clarifier at 1:00 and started draining inner section of offline clarifier. | Kleinburg Water Resource Recovery Facility | 2025-11-07
WW-WEST | November | Reduced pause cycle timer to try and eliminate likelihood of press, freezing solid removed old heat trace as it has failed and has a short circuit reached out to suppliers to find replacement components will return at a later date to repair device | Kleinburg Water Resource Recovery Facility | 2025-11-10
WW-WEST | November | Started draining aeration tank 2 - opened tank interconnect to allow flow from aeration tank 1 to clarifier 2. Closed inlet gate to aeration tank 2. Closed RAS from clarifier 2 aeration tank 2 and opened RAS from clarifier 2 to aeration tank 1. Turned alum pump 4 into manual off and increased pump 3 dosage from 140mg/L to 280mg/L. Pulled DO and TSS probes from aeration tank 2 and placed in bucket of water. Placed 2 submersible pumps into aeration tank 2 to pump into aeration tank 1 Adjusting air butterfly valves to aeration tanks through out day to balance DO Decanted thickening tank and transferred remaining sludge to holding tank. Completed daily lab and station check - no new issues added data into SharePoint. Electricians onsite for heat trace on bar screen. Bled aeration condensation line. Added 7 bags of soda ash to hopper. Pulled rags from aeration outlet. | Kleinburg Water Resource Recovery Facility | 2025-11-10
WW-WEST | November | Completed daily lab and station check - no new issues. Added data into SharePoint. Due to low solids in tank 1 did not waste from tank 1. Manually wasted 25m3 from tank 2. Added 7 bags of soda ash to hopper. Cleaned and verified DO probes and exercised butterfly valves at aeration header. Exercised butterfly valves at distribution chamber. Alum delivery onsite at 1:10pm alum level at 0.90m. Signed paperwork and reviewed certificate of analysis. Alum tank full at 1:40pm alum level now at 3.38m | Kleinburg Water Resource Recovery Facility | 2025-11-05
WW-WEST | November | - Notified ROC of the work being performed - Inspected circular plant clarifier and drive. Oil is all good. Turned the breaker on, and ran it in manual with no issues. Turned breaker off once done - Inspected circular plant aeration blowers. Oil and belt are all good. Ran blowers 1~4 with no issues. Maintenance onsite to look at broken elbow on the air header. Maintenance also noticed a broken gearbox and will obtain parts to fix - Inspected circular plant aeration inlet filters on surface. All in good shape - Exercised scum tank 3 valve with no issues. Fully pumped down the circular plant scum chamber level in manual while the scum tank 3 was fully open. Pump put out good flow, roughly 30 L/s. Scum tank level from 1.9 m to 0.47 m - Shut off RAS 1-4, and WAS 1-2 on the breaker and hit Estop, and pumps in manual off. Triggered RAS pump e stop alarms, modbus comm alarm, and two or more RAS pumps not available. Maintenance working to replace coupling on RAS pump 4. Inspected RAS pumps 1-4 and WAS pump 1-2. Once done, placed everything back into service. RAS pump 1 and 3 in auto - Tested sump pump high level for the headworks sump and sludge blower room sump. Alarm received for AUXLSHH200 headworks sump. Audible alarm for sludge blower works and sludge building switch hi alarm received. Sludge blower sump pump 1 not putting out good flow compared to sump pump 2. Will continue to monitor - Tested RAS/WAS building sump. Float works and the pumps run on manual. The check valve for sump pump 2 does not work and allows flow to return back. Managed to clear the blockage by manually fully opening the check valve and running the pump. The check valve did not allow flow back. The isolation valve for pump 2 is very still and would not close. Created work order - Tertiary sump pump tested. Pumps run well in manual. Audible high alarm heard. Tertiary building sump hihi alarm received - Inspected heat trace. All okay. Turned on heat trace for vortex | Kleinburg Water Resource Recovery Facility | 2025-11-05
WW-WEST | November | - Notified ROC of the work being performed - Exercised WAS and RAS valves, and inspected check valve. No issues. Did not exercise some valves due to them being seized - Inspected sludge transfer pump 1 and 2. No issues. Oil and coupling is all good - Turned on filter building duct heater, filter room unit heater 1, filter unit heater 2, uv unit heater 3. Checked heating in filter building MCC room, all okay. Unit heater 1 for generator building on. Duct heater on. - Turned on hot water to the alum lines. Turned on unit heater 6, in alum room. 7B on - Blower room unit 1 on. Odour room and thickener room unit and duct heater on. - Continued pumping down offline circular clarifier | Kleinburg Water Resource Recovery Facility | 2025-11-06
WW-WEST | November | - Collected weekly regulatory samples - Performed part of the lab - Unclogged two submersible pumps. Placed one pump back in to continue pumping sludge - Decanted the sludge thickening tank 2 - Started draining offline circular plant clarifier for upcoming condition assessment - Notified ROC of the work being performed - Inspected the generator and fuel level, all okay. Started the generator at 10:20. Recorded readings on SharePoint after 30 minutes, no issues. Ran for approximately one hour. Runtime for generator 1 from 423.5 hrs to 424.4 hrs. - Started generator 2 at 10:33. Recorded readings after 30 minutes. Run time for generator 2 from 399.5 hrs to 400.6 hrs. No issues with readings. - Fuel level readings before: tank 1 at 0.92 m, tank 2 at 0.93 m, and gen 2 day tank at 1.11 m. Fuel readings after: tank 1 at 0.91 m, tank 2 at 0.93 m, and gen 2 day tank at 1.11 - Checked for hazardous waste. Tested eyewash. Admin building eyewash alarm received - Performed JHSC inspection. All okay. Received eyewash alarms - Inspected diversion tank blowers 1 and 2. Filters, belt and oil are all okay. Test ran both with no issues. Triggered diversion tank uncommanded stop and general alarm - Inspected aeration blower 1. Filters, belt and oil are all okay. Switched main duty to aeration 1 after to inspect blower 2 - Inspected aeration blower 2. Filters, belt and oil are all okay - Inspected vortex blowers. Filters, belt and oil are all okay. Checked bin for grit, no issues - Aeration tank 1 finished filling. Adjusted air valves. Will continue to monitor - unshelved KBSPR_AER_TK1_AIT2_LO aeration basin 1 back do Lo alarm. KBSPR_AER_TK1_AIT2_OOR aeration basin 1 back DO out of range. KBSPR_AER_TK1_AIT1_OOR aeration basin 1 front DO out of range. KBSPR_RAS_PMP0_OOS two or more RAS pumps unavailable. KBSPR_RAS_PMP1_MDBS_COMM RAS pump 1 comm. KBSPR_RAS_PMP2_MDBS_COMM RAS pump 2 comm. KBSPR_RAS_PMP1_ESTP RAS pump 1 estop. KBSPR_RAS_PMP2_ESTP RAS pump 2 estop. KBSP_AER_TK1_NIT1_FLT aeration basin 1 solids fault | Kleinburg Water Resource Recovery Facility | 2025-11-04
WW-WEST | November | Completed daily lab and station check - no new issues. Added data into SharePoint. Added 7 bags of soda ash to hopper. Inspected sludge tank blowers 1 and 2 - no issues, oil levels belts and filters good. Both operate normally. Inspected RSHW blowers 1 and 2 - no issues oil and filters good. Both operate normally | Kleinburg Water Resource Recovery Facility | 2025-11-04
WW-WEST | November | On site to replace the coupler on RAS pump4. Young will put it back in service. Also looked at the aeration leak in the clarifier with Terry C. To plan the repairs | Kleinburg Water Resource Recovery Facility | 2025-11-05
WW-WEST | November | Added 14 bags of soda ash to the hopper Batch wasted 20 m3 from each clarifier | Kleinburg Water Resource Recovery Facility | 2025-11-02
WW-WEST | November | - Cleaned scum tank - Removed LOTS of rags from aeration tank outlet and inlet - Checked DO probe and removed lots of rags on probe. Cleaned probe. No issues - Performed in-house lab and recorded readings on SharePoint - Checked station and recorded readings. No new issues - Added 7 bags of soda ash into the hopper - Started filling aeration tank 1 to put aeration tank 1 back in service. Opened aeration tank 1 inlet sluice gate. Revalved RAS flow back into aeration tank 1. Closed aeration tank outlet interconnect valve. Placed two submersible pump into aeration tank 2 to pump some solids into aeration tank 1. Opened aeration tank 1 air valves by one notch for all four butterfly valves. Reduced RAS flow from 20 L/s to 5 L.s. Placed alum pump 3 back into auto. Adjusted alum dosgae for pump 4 from 250 mg/L to 140 mg/L. Adjusted alum dosage for pump 3 from 128 mg/L to 140 mg/L - Unplugged RAS pump twice | Kleinburg Water Resource Recovery Facility | 2025-11-03
WW-WEST | November | Worked with Harie. Wessuc onsite for aeration tank 2 clean. Contractors onsite for sludge holding tank inspection and offline clarifier and aeration tank inspection -called ROC to notify of LOTO for inspections. LOTO on thickening tank transfer valves. Put THCK TK MV1 into local stop and locked out. Put THCK TK2 into local stop and locked out. Closed SCUM TK MV2 valve to holding tank and locked out. Put sump pump 1 and 2 into manual off as well as activating EStop for both pumps. Upon sludge holding tank inspection completion returned valves to remote and removed locks. Scum pumps back in auto. Increased soda ash runtime from 6.00seconds/h to 6.25seconds/h due to decreasing alkalinity in lab. Turned RAS pumps off at 11am. Started manually wasting at 12pm. Manually wasted 15m3 from clarifier 1 and wasted 5m3 from clarifier 2 due to sludge blanket difference. Clarifier 1 had a sludge blanket of 3ft Clarifier 2 had a sludge blanket of 1.5ft. Upon wasting completion returned RAS back to operation. Set sampler for 8am Sunday. At 2:11pm alum level sensor dropped to 0.00m before bouncing back to 1.58m and continues to drop to 0.00m and bounce back. Alum pumps continue to pump. Informed Dan Hirstwood who has contacted instrumentation. | Kleinburg Water Resource Recovery Facility | 2025-11-28
WW-WEST | November | - Increased soda ash runtime from 5.25 sec to 5.5 sec to increase alkalinity - Performed in-house lab and recorded readings on SharePoint. Sludge blanket for clarifier 1 was at 36 inches while clarifier 2 was at 4 inches. Imbalance is due to running on just aeration tank one and favouring clarifier 1 hydraulically. To try and correct the imbalance, raised outlet gate of aeration tank 2 and lowered outlet of aeration tank 1. Will monitor and make more adjustments next week - Enabled RAS batch wasting mode then wasted 25 m^3 from clarifier 1 and 5 m^3 from clarifier 2. Wasted more from clarifier 1 due to higher sludge blanket. Reset batch wasting mode once done - Cleaned admin building lab, washroom and floors - Performed station check and recorded readings on SharePoint - Repaired hose spray nozzle for aeration tank hydrant - Repaired leak on aeration tank hydrant by tightening the connection | Kleinburg Water Resource Recovery Facility | 2025-11-21
WW-WEST | November | Decanted sludge thickening tank and transferred remaining sludge. Collected regulatory weekly samples. Completed daily lab and station check - no new issues. Entered data into SharePoint. Turned RAS off at 9:40am. Manually wasted 15m3 from each clarifier from 10:40am to 11:50am. Turned RAS back on after wasting completed. Soda ash delivery onsite at 9:25am. Signed and reviewed papers. Added 8 bags of soda ash to hopper. Checked aeration outlet for rags. Inspected odour control unit and filled data sheet. Bled condensation from aeration condensation lines. | Kleinburg Water Resource Recovery Facility | 2025-11-24
WW-WEST | November | Harie Rajamithiran(OIT) working under the direction of Lauren Swanson(OIC). -Wessuc contractor on-site -Completed lab analysis -Cleared bar screen rags -Added 7 bags of Soda Ash -Drained groundwater out of influent flow meter chamber , inspected with no issues found -Completed station check | Kleinburg Water Resource Recovery Facility | 2025-11-28
WW-WEST | November | Onsite to complete aeration tank repair. Work completed. Allow parts to cure. Operations can then partially fill tank and inspect for any additional leaks. | Kleinburg Water Resource Recovery Facility | 2025-11-19
WW-WEST | November | - Inspected UV 1 and 2. UV 1 Bank B cassette 2 lower ballast fault still persists and troubleshooted the fault with David Dougherty from electrical. To troubleshoot, placed inlet sluice gate to UV channel 1 to local closed. Tried testing the rack, replaced ballast with new ones, and tried switching the cables and connection. The ballast fault still persists even though the all the bulbs turn on. David will speak to Trojan. Will discuss with TL and order a brand new cassette unit if needed. Once done, placed UV channel 1 back in service and in auto. left bank b cassette 2 disabled so that it does not trigger faults (all bulbs are still running and it will just not trigger alarms). | Kleinburg Water Resource Recovery Facility | 2025-11-27
WW-WEST | November | Completed daily lab and station check - no new issues. Added data into SharePoint. Enabled batch wasting at 9am and set WAS pumps to auto to waste 16m3 from 10am to 11am. Wasting completed at 11am. WAS pumps placed back into manual and RAS pumps placed back in operation. | Kleinburg Water Resource Recovery Facility | 2025-11-19
WW-WEST | November | Wessuc onsite at 8am for aeration tank 2 cleaning - decanting into diversion tank. Completed daily lab and station check all okay - added data into SharePoint. Increased soda ash runtime from 5.5 seconds/h to 5.75 seconds/h. Stopped RAS at 9:20am. Manually wasted 18m3 between 10:20am and 11:20am. Returned RAS to operation after wasting completed. Added 6 bags of soda ash to hopper. Verified and cleaned DO probes. Exercised clarifier sluice gates. Cleaned scum tank. | Kleinburg Water Resource Recovery Facility | 2025-11-26
WW-WEST | November | Completed daily lab and station check. No new issues added data into SharePoint. Turned RAS off at 10:30am. Manually wasted 16m3 from 11:30am to 12:30pm. RAS turned back on when wasting completed. Triggered filter bypass float to test alarm - called ROC to confirm. Added 5 bags of soda ash to hopper. | Kleinburg Water Resource Recovery Facility | 2025-11-25
WW-WEST | November | On site to replace the valves in the RAS/ WAS pump room sump pumps. Replaced the old ones with SS ball valves. Pumps are back in service | Kleinburg Water Resource Recovery Facility | 2025-11-24
WW-WEST | November | Remote batch wasted 15m3 per side and RAS is now back in auto. Added 7 x 25kg bags of soda ash to the dispensing hopper. | Kleinburg Water Resource Recovery Facility | 2025-11-30
WW-WEST | November | Added 9 bags of soda ash to the hopper Batch wasting 15m3 from each clarifier | Kleinburg Water Resource Recovery Facility | 2025-11-23
WW-WEST | November | Completed daily lab and station check. No new issues added data into SharePoint Enabled batch wasting at 9am and set WAS pumps to auto to waste 16m3 between 10am and 11am. Wasting completed at 11am and placed WAS pumps back into manual and RAS back into operation. | Kleinburg Water Resource Recovery Facility | 2025-11-20
WW-WEST | November | - Added 6 bags of soda ash into the hopper - Maintenance repaired the air header in the offline circular clarifier in the aeration cell - Performed annual filter maintenance. Cleaned sand lift filter for stage 2 filter 1 and 2. Partially drained filter 2 stage 1 and 2, and cleaned piping and coupling of scum. Checked for leaks while filling. No issues found | Kleinburg Water Resource Recovery Facility | 2025-11-19
WW-WEST | November | Entered sludge holding tank to remove concrete core. Disposed core in garbage bin. | Kleinburg Water Resource Recovery Facility | 2025-11-28
WW-WEST | November | Wessuc onsite for cleaning aeration tank 2. Electricians onsite to troubleshoot UV bank 1 B. Turned off RAS pumps at 11am. Manually wasted between 12pm to 1pm. Wasted 15m3 from clarifier 1 and manually wasted 5m3 from clarifier 2 due to a higher sludge blanket in clarifier 1. RAS pumps back in operation upon completion of wasting. Completed daily lab and station check - no new issues added data into SharePoint. Increased soda ash run time from 5.75seconds/h to 6.00seconds/h due to lower alkalinity in lab. Added 7 bags of soda ash to hopper. Continued hosing down sludge holding tank in preparation for inspection. | Kleinburg Water Resource Recovery Facility | 2025-11-27
WW-WEST | November | Investigate repair of circle plant aeration supply leak, removed broken section will return to complete repair weather permitting. | Kleinburg Water Resource Recovery Facility | 2025-11-14
WW-WEST | November | - Performed filter annual maintenance and monthly inspection on stage 2 filter 3 and 4. Cleaned sand lift air tube filters and hosed area - Previously adjusted filter start and stop due to frequently hitting filter hi inlet channel after going down to one aeration tank. Adjusted some settings back to where it was and to get higher filter reject flow rate for filters. Adjusted filter 2 start to 22 L/s from 20 L/s. Filter 3 start rate to 45 L/s from 40 L/s. Filter 4 start rate to 70 L/s from 65 L/s - Added 7 bags of soda ash into the hopper - Lowered alum from 280 mg/L to 275 mg/L due to good phosphorus numbers and settling | Kleinburg Water Resource Recovery Facility | 2025-11-20
WW-WEST | November | - Received a call about UV common major alarm and bank B module communication alarm - Came on site to investigate and found UV 1 Bank B module number 2 lost communication. This caused UV bank A to kick in as duty. No issues with the trend and UV continuous disinfection was applied at all times - Turned UV bank 1B locally off with no issues. Hit the breakers for bank 1B to kill power to bank 1B but this caused the UV channel 1 sluice gate to close followed by low level fault for channel 1. - To still allow backup UV channel 1 bank A to operate, turned breaker back on for UV 1 bank B but left it in locally off. - The system did not like UV 1 bank B being in local off and created not enough healthy banks available alarm and would go back to UV 2 - UV disinfection was applied at all times - Called an electrician to repair UV 1 Bank B module 2 Update: manually inputted duty 3 for UV 1 and hit apply. UV 2 in duty 1. Disabled duty rotation. Enabled RAS batch wasting mode. Wasted 20 m^3 and once done, reset RAS batch wasting mode. Added 9 bags of soda ash into the hopper | Kleinburg Water Resource Recovery Facility | 2025-11-15
WW-WEST | November | - Added 8 bags of soda ash into the hopper - Performed annual service on filter 2 and 4. Sand filter movement test result for filter 2: 12 inches, 12 inches, 7 inches, 1 inches. Filter 3: 24 inch, 6 inch, 3, inches, 16 inches, 3 inches. Filter 4: 12 inch ,14 inch, 12 inches, 12 inch. Cleaned sand lift filters - Filter 1 was partially drained to clean piping of scum and once finished, filter was allowed to fill. Noticed a water leak on inlet side coupling. Notified TL - Decanted the sludge thickening tank 2 then transferred sludge into the holding tank - GFL on site to take a load of sludge - TSSA upgrade resumed and contractors working in the generator room. Generator room high temperature triggered due to their work but all okay | Kleinburg Water Resource Recovery Facility | 2025-11-18
WW-WEST | November | Collected weekly regulatory samples. Completed daily lab and station check - no new issues. Added data into SharePoint. Batch wasting mode enabled at 8:55am and WAS pumps set to auto to waste 16m3 between 10am and 11am. Wasting completed at 11am and WAS pumps placed back in manual. RAS pumps back in operation. Worked with Young on annual inspection and cleaning on filters 2 and 4. | Kleinburg Water Resource Recovery Facility | 2025-11-18
WW-WEST | November | Attending site to check oxygen sensor issue (W11439944). Replaced sensor and calibrated. ROC was notified before and after maintenance work was performed. SCADA alarms were cleared. | Kleinburg Water Resource Recovery Facility | 2025-11-17
WW-WEST | November | Completed daily lab and station check - no new issues. Added data into SharePoint. Aeration tank 2 drained - fully closed butterfly valves for air to aeration tank 2. Enabled batch wasting at 10am and set wasting for 20m3 from 11am - 12pm. Wasting completed and WAS pumps placed back into manual and RAS pumps back in operation. Added 8 bags of soda ash to hopper | Kleinburg Water Resource Recovery Facility | 2025-11-13
WW-WEST | November | - Shelved KBSPR_AER_TK2_AIR2_OOR and KBSPR_AER_TK2_NIT_FLT due to aeration tank being OOS for ladder installation and maintenance work | Kleinburg Water Resource Recovery Facility | 2025-11-13
WW-WEST | November | The ballast fault alarm came in again and shows on local HMI as being out. I pulled it out and all ballasts are working and bulbs are on. Narrowed it down and it seems like the pin connector needs to be replaced as it is burnt. Something caused the fuse to blow, ballast to fault out and the wiring to get burnt. Electrical will need to investigate further on Monday. I've made UV 1 in duty 3. Disabled auto duty rotation. UV 2 will be the only one running in duty (it will rotate between UV2 bank A and B). I've disabled the 2nd cassette of UV1 bank B for now until it can be taken a look at. UV 1 bank A and B are both working and can be run in emergencies or during high flows. Notified supervisor and TL. Created work order for maintenance | Kleinburg Water Resource Recovery Facility | 2025-11-15
WW-WEST | November | Completed daily lab and station check - no new issues. Added data into SharePoint. Enabled batch wasting at 10am and put WAS pumps into auto and set to waste 16m3 between 11am and 12pm. Wasting complete at 12pm - WAS pumps placed back in manual and RAS placed back into operation. Worked with Young on filter maintenance, inspection and cleaning on filters 1 and 3. Added 9 bags of soda ash to hopper. Cleaned rags from aeration outlet. | Kleinburg Water Resource Recovery Facility | 2025-11-17
WW-WEST | November | Decanted sludge thickening tank and transferred remaining sludge to holding tank. Completed daily lab and station check - no new issues. Added data into SharePoint. Enabled batch wasting mode at 10am and set auto waste for 20m3 from 11am to 12pm. Auto waste complete and WAS pumps placed back into manual and RAS resumed. Maintenance onsite for work on circular clarifier diffuser. Notified ROC of work being done in the head works Inspected traveling bar screen - flushed and cleaned out screw, greased and checked oil levels. Inspected vortex 1 and 2 - cleared rags, greased and checked oil levels. Both operating normally Greased and inspected screenings compactor. Inspected grit dewatering screw oil level good, operating normally. CPD onsite for air compressor pressure switch testing. Ran both air compressors in local, both operated within pressure range. Placed air compressors back in remote and cleared alarms. | Kleinburg Water Resource Recovery Facility | 2025-11-14
WW-WEST | November | Continuing to drain aeration tank 2. Completed collecting weekly regulatory samples. Completed daily lab and station check - no new issues added data into SharePoint Enabled batch wasting at 10am and set WAS pumps to auto for wasting of 30m3 between 11am and 1pm. Wasting completed at 1pm - WAS pumps placed back into manual and RAS pumps back into operation. Added 6 bags of soda ash to hopper. Inspected odour control unit - no issues, data sheet filled out. Inspected both raw and final effluent composite samplers - both ok and working normally. | Kleinburg Water Resource Recovery Facility | 2025-11-11
WW-WEST | November | - pumped down scum tank manually with no issues - Checked for condensation in air lines - Performed annual service on filter 1 and 3. Pulled sand lift tube out and cleaned the filter. Performed sand filter movement test, result for filter 3: 16 inches, 6 inches, 10 inches, 7 inches. Piping, coupling all seem to be in good shape Update: as filter 1 was filing. Discovered leak coming through the inlet side coupling | Kleinburg Water Resource Recovery Facility | 2025-11-17
WW-WEST | November | Decanted sludge thickening tank and wasted remaining sludge to holding tank. Completed daily lab and station check - no new issues. Added data into SharePoint. Added 6 bags of soda ash to hopper. Continue to drain aeration tank 2. Cleaned and verified DO probes. | Kleinburg Water Resource Recovery Facility | 2025-11-12
WW-WEST | November | On site to set station up for wet-well cleaning. Isolated well 1. Valved pump 2 to well 2. Pumped well 1 down to 0.4 m. Set well 1 out of service. Set pumps 2 and 3 to duty 1 and 2. | King City Pumping Station | 2025-11-10
WW-WEST | November | Completed the station check Could not access the SharePoint excel sheet so the numbers will be added remotely Everything operating as intended | King City Pumping Station | 2025-11-07
WW-WEST | November | - Notified ROC of the work being performed - Wet well cleaning going on and wet well 1 is done cleaning - Opened inlet gate for wet well 1 and closed inlet gate for wet well 2. Interconnect still closed - Switched wet well 1 duty to 1 (WW1 LIT1 controlling) and put wet well 2 OOS. - Once wet well 1 was somewhat full. Bled air for pump 1 to remove air lock. Closed pump 2 inlet gate from wet well 2, and opened inlet gate from wet well 1. Pump 1 in duty 1 and pump 2 in duty 2. Pump 3 OOS - Pumped down wet well 2 to 0.4 m after disabling low level lockout. Wet well 1 low level lockout enabled - Tested pump 1 operation, all okay - Tested sump pit operation and manually lifted float. Sump pump turned on, no issues - Tested dry well flood alarm, alarm received. No issues - Tested diesel containment flood alarm. Alarm received - Performed JHSC inspection. All okay. Tested eyewash, no issues - Tested building Hi and Low temperature alarm. Alarm received - Checked for hazardous waste, none found - Inspected hoist system, all okay - Once wet well cleaning is done. Placed wet well 2 back in service. Opened interconnect valve. Opened inlet gate for wet well 2. Bled air from pump 3. Opened inlet gate from wet well 2 to pump 2. Enabled wet well 2 on setpoints. Enabled low level lockout on both wet wells - Tested and inspected pump, motor and check valves. All okay. Surge anticipator, all okay - Inspected the generator and fuel level, all okay. Started the generator at 13:00. Recorded readings on SharePoint after 30 minutes, no issues. Ran for approximately one hour. Runtime for generator 1 from 658.3 hrs to 659.3 hrs. Fuel level for tank 1 from 84.1 cm (826 L) to 83.4 cm (818 L). Fuel level for tank 2 from 83.6 cm (821 L) to 82.7 cm (811 L) | King City Pumping Station | 2025-11-10
WW-WEST | November | Completed the station check Entered data into SharePoint Everything operating as intended | King City Pumping Station | 2025-11-04
WW-WEST | November | - On site to push bin out | King City Pumping Station | 2025-11-27
WW-WEST | November | Completed the station check Entered data into SharePoint Everything operating as intended | King City Pumping Station | 2025-11-21
WW-WEST | November | In to Complete Scheduled WO. Removed and Replaced HWs Bin for Pick Up. Tidied and Inspected HWs. Topped Up Bar-screen Oil Hopper. No Issues Found. | King City Pumping Station | 2025-11-12
WW-WEST | November | Harie Rajamithiran(OIT) working under the direction of Gavin Walker(OIC) Completed housekeeping Completed station check | King City Pumping Station | 2025-11-25
WW-WEST | November | - Checked station and trends. Recorded readings on SharePoint - Notified ROC of the work being performed - Pushed bin back in. Cleaned screen and flushed drain line - Exercised valves that weren?t exercised during wet well cleaning. Shut off pump 1 and 3 then exercised valves. Once done, placed pump 1 and 3 back into service and back in duty rotation. Shut off pump 2 then exercised valves. Once done. Placed pump 2 back into service and duty rotation. Pump 1, 2, 3 fault alarm were created duty to this work. No issues | King City Pumping Station | 2025-11-14
WW-WEST | November | Completed the station check Entered data into SharePoint Inspected and tested the crane Everything operating as intended | King City Pumping Station | 2025-11-18
WW-WEST | November | - Upon arrival at the station, the gate was unlocked and the chain was missing. Notified TL and requested a replacement chain - Checked station and trends, and recorded readings on SharePoint | King City Pumping Station | 2025-11-11
WW-WEST | November | Completed station check. No issues found. Entered numbers in spreadsheet. Completed valve exercise work order. Completed consolidated dry-well work order: ROC received dialler test alarm, station flood alarm and hi/lo temp alarm. RSP test: P1 @ 100% - 61 l/sec. P2 @ 100% - 58 l/sec. P3 @ 100% - 64 l/sec. | Nobleton Janet St. Sewage Pumping Station | 2025-11-07
WW-WEST | November | Ross sewage pump vibration, data collection Turned on building heat that is available. Furnace not functioning turned off supply fan 501 blowing cold air only. Electric Heater on b1 not working | Nobleton Janet St. Sewage Pumping Station | 2025-11-10
WW-WEST | November | Test ran standby generator. Start hours: 450:24. Fuel: 88 cm / 1754 L. Stop hours: 451:30. Fuel: 88 cm / 1752 L. Worked on auto sampler to get correct sample volumes. Disabled liquid sensor and adjusted suction length to 37 ft. Sampler sampled correct volume. Set on schedule. | Nobleton Janet St. Sewage Pumping Station | 2025-11-05
WW-WEST | November | Completed station check. No issues found. Entered numbers in spreadsheet. Completed JHSC inspection with no findings. Inspected and calibrated raw sewage sampler. Looked for, but didn't find any, hazardous waste. | Nobleton Janet St. Sewage Pumping Station | 2025-11-04
WW-WEST | November | Collected monthly samples. | Nobleton Janet St. Sewage Pumping Station | 2025-11-04
WW-WEST | November | - collected weekly regulatory samples | Nobleton Janet St. Sewage Pumping Station | 2025-11-24
WW-WEST | November | Station checks, SharePoint readings and review of continuous monitoring data Comprehensive housekeeping | Nobleton Janet St. Sewage Pumping Station | 2025-11-21
WW-WEST | November | On site to assist contractor Total Power with Diesel generator PM and Load Test. Informed ROC of work to be done. Work completed. Generator back in auto and all alarms reset. | Nobleton Janet St. Sewage Pumping Station | 2025-11-19
WW-WEST | November | On site to complete station check. Diesel tank level reading incorrectly intermittently since Wednesday afternoon. Will create work order. Noted small crack forming on pressure gauge fitting on RSP 1. Removed heavy gauge assembly to reduce vibrations so pump can stay in service. Will create work order. | Nobleton Janet St. Sewage Pumping Station | 2025-11-28
WW-WEST | November | Informed ROC. Performed annual calibration and put instruments in Cal mode while doing the tasks. Devices done were FIT, LITs and gas sensors. All alarms were cleared after the job. No other issues encountered. | Nobleton Janet St. Sewage Pumping Station | 2025-11-27
WW-WEST | November | Completed station check and entered data in spreadsheet. No issues found. | Nobleton Janet St. Sewage Pumping Station | 2025-11-25
WW-WEST | November | Collected weekly compliance samples. Completed station check. No issues found. Entered data in spreadsheet. | Nobleton Janet St. Sewage Pumping Station | 2025-11-11
WW-WEST | November | Completed station check. No issues found. Entered data in spreadsheet. Inspected hoist. No issues found. | Nobleton Janet St. Sewage Pumping Station | 2025-11-14
WW-WEST | November | - Notified ROC of the work being performed - Wessuc onsite to clean wet well. Pumped down wet well for the contractors. No issues during work - Tested wet well overflow alarm. Received on dialer and scada | Nobleton Janet St. Sewage Pumping Station | 2025-11-12
WW-WEST | November | Collected weekly compliance samples. Completed station check. Entered data in spreadsheet. No issues found. | Nobleton Janet St. Sewage Pumping Station | 2025-11-18
WW-WEST | November | Completed the station check Entered data into SharePoint Everything operating as intended | Vaughan Pine Valley Pumping Station | 2025-11-07
WW-WEST | November | Completed the jhsc inspection | Vaughan Pine Valley Pumping Station | 2025-11-06
WW-WEST | November | Completed the station check Entered data into SharePoint Everything operating as intended | Vaughan Pine Valley Pumping Station | 2025-11-04
WW-WEST | November | Test ran the generator Greased the channel grinder Exercised the valves in the wet well Hosed down the wet well Tested the wet well high level alarm Tested the autodialer alarm Tested the dry well flood alarm Tested the building high low temp alarm Inspected the sump pit Inspected and tested RS pumps P1 ? 100% - 214.9L/s P2 ? 100% - 218L/s P3 ? 100% - 208.1L/s Inspected check valves Inspected the air relief valves Checked the site for hazardous waste Returned the station to normal operation | Vaughan Pine Valley Pumping Station | 2025-11-05
WW-WEST | November | Inspected the ocu and exercised the valves in the dry well | Vaughan Pine Valley Pumping Station | 2025-11-05
WW-WEST | November | Found Inlet Sewer Chamber T0514-08A, Sluice Gate valve. Attempted to exercise valve which is very stiff. Will report to team lead. | Vaughan Pine Valley Pumping Station | 2025-11-03
WW-WEST | November | Checked station and trends, and recorded readings on SharePoint. No new issues | Vaughan Pine Valley Pumping Station | 2025-11-25
WW-WEST | November | Completed the station check Entered data into SharePoint Briefly ran the generator to test an ongoing security system issue around power transfers Everything operating as intended | Vaughan Pine Valley Pumping Station | 2025-11-21
WW-WEST | November | - Checked station and trends. No new issues | Vaughan Pine Valley Pumping Station | 2025-11-11
WW-WEST | November | - Checked station and recorded readings on SharePoint. No new issues | Vaughan Pine Valley Pumping Station | 2025-11-14
WW-WEST | November | Remotely Placed Supernatant Drain Valve in Manual Open. Decant Complete. Remotely Closed Supernatant Valve in Manual. | Schomberg Water Resource Recovery Facility | 2025-11-06
WW-WEST | November | Completed the station check Entered data into SharePoint Everything operating as intended | Vaughan Pine Valley Pumping Station | 2025-11-18
WW-WEST | November | Remotely Placed Supernatant Drain Valve in Manual Open. | Schomberg Water Resource Recovery Facility | 2025-11-04
WW-WEST | November | Responding to RAS and WAS pump low flow alarms. Closed valve from clarifier 1 and opened valve between pumps to put pump 1 as duty 1 and pump 2 as duty 2. Pump 3 plugged and out of service for the weekend. | Schomberg Water Resource Recovery Facility | 2025-11-07
WW-WEST | November | In to Complete Scheduled WOs. Notified ROC. Completed Clarifiers #1 and 2 Inspections. Topped Up Oil Reservoirs and Greased Drive Chains. No Issues Found. Returned to Service. Cleared Associated Alarms. Completed Aer. DO Sensor Maintenance. Placed Probes in Calibration Mode. Cleaned and Inspected Units, No Issues Found. Returned to Service. Completed Grit Dewatering Screws #1 and 2 Inspections. No Issues Found. Returned to Service. | Schomberg Water Resource Recovery Facility | 2025-11-05
WW-WEST | November | In to Complete Scheduled WOs. Notified ROC. Lowered and Activated Decant Pump. CPD and Contractors On-site for Clarifier #2 Drive Rake Inspection and Modification. Activated Unit Several Cycles for Testing Purposes. Returned to OOS. Decant Complete, Raised and Deactivated Decant Pump. GFL On-site for Sludge Load. Sludge Transfer Valve Local Open, Transferred Thickened Sludge. Transfer Valve Returned to Manual Closed. Cleared Associated Alarm. | Schomberg Water Resource Recovery Facility | 2025-11-06
WW-WEST | November | In to Complete Scheduled WOs. Notified ROC. Lowered and Activated Decant Pump. Decant Complete, Raised and Deactivated Decant Pump. Sludge Transfer Valve Manual Open, Transferred Thickened Sludge. Transfer Valve Returned to Manual Closed. Completed WAS Pump #2 and RAS Pumps #2 and 3 Inspections. Removed Suction Lines and Check Valve Covers. Cleared Obstructions and Debris, Flushed Units. Inspected Drive Shaft Couplings, All OK. Returned to Service and Duty. Cleared Associated Alarms. | Schomberg Water Resource Recovery Facility | 2025-11-10
WW-WEST | November | In to Complete Scheduled WOs. Conducted Clarifier #1 Weir, Scum Trough and Launder Cleaning. Filter Inlet Valves Closed, Filter Diversion Valve to Lagoon Open @ 08:50. Lowered and Activated Decant Pump. Flushed and Recirculated Scum Tank. Placed Scum Valve in Manual Discharge and Activated Scum Pump #1 in Manual. Scum Tank Drawdown Complete. Returned All to Auto and Service. Cleaning Complete. Filter Inlet Valves Open, Filter Diversion Valve Closed @ 10:35. Diverted Approx. 65 m3 or 65 000 L to the Lagoon. Reported to York Incident Notification. Rotated Service Clarifier for Continued CPD and Contractor Work. Clarifier #2 Inlet Valve Manual Open, Aer. Tanks #1 and 2 Outlet Interconnect Gate Valve Manual Open, Clarifier #1 Inlet Valve Manual Closed. Placed RAS Pump #3 in Manual, Manual Speed @ 100% for Clarifier #1 Drawdown Process. RAS Pump #2 Manual Off. Decant Complete, Raised and Deactivated Decant Pump. Sludge Transfer Valve Manual Open, Transferred Thickened Sludge. Transfer Valve Returned to Manual Closed. Activated Aer. Tank and Clarifier Effluent Alum Line Hot Water Dosing Based on Seasonal Temperatures. Contractor On-site to Complete Clarifier #2 Drive Rake Modifications. Unit Deactivated for the Duration of Contractor Work. Dedicated RAS and WAS Pump #1 to Clarifier #1. Activated RAS Pump #1 in Manual, Manual Speed @ 100%, RAS Pump #3 Manual Off. Rotated WAS Pump Duties. Pump #1 Manual Off, Pump #2 in Auto. WAS Pump #2 and RAS Pumps #2 and 3 Dedicated to Clarifier #2. Completed Filter Inlet TSS Sensor Inspection. Placed Unit in Calibration Mode Locally, Cleaned Probe. No Issues Found. Returned to Service. WAS Pump #2 in Local On for Testing Purposes. Returned to Auto and Service. Placed RAS Pumps #2 and 3 in Duty and Auto, RAS Pump #3 Active in Duty #1. Clarifier #1 Drive Rake Over-torque Alarm Active, Notified by ROC. Cleared Alarm and Tested Unit with No Issues. Contractor Work Complete. Placed Clarifier #1 OOS and Clarifier #2 in Service. Cleared Associated Alarm. | Schomberg Water Resource Recovery Facility | 2025-11-07
WW-WEST | November | Remotely Responded to RAS to Aer. Tank No Flow Alarm Communicated by the ROC. RAS Pump #3 Producing No Flow @ 100% Speed. Rotated Duties, RAS Pump #2 in Duty #1 and Producing Flow. Alarm Cleared. Speed Deviation Alarm Outstanding. Notified ROC and On-Call Staff. | Schomberg Water Resource Recovery Facility | 2025-11-07
WW-WEST | November | Remotely Placed Supernatant Drain Valve in Manual Open. Decant Complete. Remotely Closed Supernatant Valve in Manual. | Schomberg Water Resource Recovery Facility | 2025-11-10
WW-WEST | November | Worked with Harie to train on Schomberg ops. Completed in house labs and input data into SharePoint. Decanted sludge thickening tank - did not transfer. | Schomberg Water Resource Recovery Facility | 2025-11-05
WW-WEST | November | Remotely Placed Supernatant Drain Valve in Manual Open. Decant Complete. Remotely Closed Supernatant Valve in Manual. | Schomberg Water Resource Recovery Facility | 2025-11-07
WW-WEST | November | On site due to equipment failure from a power blip Reset the clarifier and vortex blower 2 Everything back to normal operation | Schomberg Water Resource Recovery Facility | 2025-11-03
WW-WEST | November | Conducting Remote Testing of RAS and WAS System Post Inspection. Rotated RAS Pump Duties, RAS Pumps #2 and 3 Tested in Auto and Duty with No Issues. Activated WAS Pump #2 in Manual for Wasting and Testing Purposes with No Issues. Rotated WAS Pump Duties. Pump #1 Manual Off, Pump #2 in Auto. | Schomberg Water Resource Recovery Facility | 2025-11-10
WW-WEST | November | In to Complete Reg. Sampling and Scheduled WOs. Lowered and Activated Decant Pump. Returned Supernatant Drain Valve to Manual Closed. Investigated RAS Pump #2 Speed Deviation Alarms Communicated by the ROC. Inspection Found a Vibration While Running. Created Follow Up WO ?> W11415723. Notified On-Call Staff and ROC. Pump to Remain In Service. Decant Complete, Raised and Deactivated Decant Pump. Sludge Transfer Valve Local Open, Transferred Thickened Sludge. Transfer Valve Returned to Manual Closed. Reviewed SCADA and Trends. Returned Sludge Blower #1, Filter Reject Pump #1 and Aer. Blowers #3 and 4 to Duty Rotation and Service. | Schomberg Water Resource Recovery Facility | 2025-11-04
WW-WEST | November | In to Complete Scheduled WOs. Notified ROC. Reviewed SCADA and Trends. Returned Sludge Blower #2 and Aer. Blower #4 to Duty Rotation. RAS Pump #2 Issuing Speed Deviation Alarms. Placed RAS Pump #3 in Duty #1 Until Further Investigation. Alarm Cleared. Lowered and Activated Decant Pump. Decant Complete, Raised and Deactivated Decant Pump. Sludge Transfer Valve Local Open, Transferred Thickened Sludge. Visually Observed Transfer Process. Transfer Valve Returned to Manual Closed. Sludge Holding Tank Hi and HiHi Alarms to Remain Outstanding Until Sludge Load Removed. Transferred Station to Generator Power with No Issues. Acknowledged Associated Alarms. Transferred Station Back to Utility Power with No Issues. Cleared Associated Alarms. Completed JHSC Inspection. No Issues Found. Replaced Compressor Building Supply Fan Filter. | Schomberg Water Resource Recovery Facility | 2025-11-03
WW-WEST | November | Remotely Placed Supernatant Drain Valve in Manual Open. Decant Complete. Remotely Closed Supernatant Valve in Manual. | Schomberg Water Resource Recovery Facility | 2025-11-03
WW-WEST | November | On site due to a power blip around 9:00am, reset the clarifier, everything back to normal operation | Schomberg Water Resource Recovery Facility | 2025-11-01
WW-WEST | November | On site to replace the seal on blower 1 | Schomberg Water Resource Recovery Facility | 2025-11-05
WW-WEST | November | Attending site to check Vortex Oxygen sensor (W11403445). Sensor was replaced and calibrated. SCADA alarms were cleared after sensor replacement. | Schomberg Water Resource Recovery Facility | 2025-11-04
WW-WEST | November | Remotely Placed Supernatant Drain Valve in Manual Open. Decant Complete. Remotely Closed Supernatant Valve in Manual. | Schomberg Water Resource Recovery Facility | 2025-11-25
WW-WEST | November | Completed the station check and daily lab work Decanted then emptied the sludge thickening tank Entered data into SharePoint Removed floating debris from the aeration tank | Schomberg Water Resource Recovery Facility | 2025-11-27
WW-WEST | November | Remotely Placed Supernatant Drain Valve in Manual Open. Decant Complete. Remotely Closed Supernatant Valve in Manual. | Schomberg Water Resource Recovery Facility | 2025-11-19
WW-WEST | November | In to Complete Scheduled WOs. Notified ROC. Lowered and Activated Decant Pump. Decant Complete, Raised and Deactivated Decant Pump. Sludge Transfer Valve Manual Open, Transferred Thickened Sludge. Transfer Valve Returned to Manual Closed. Opened Clarifier #1 RAS/WAS Manual Suction Valve. Closed RAS/WAS Distribution Header Manual Interconnect Valve for Pump Dedication. RAS Pump #1 Manual On @ 100% Speed for Clarifier #1 Drawdown. RAS Pump #3 Manual On @ 45% Speed to Maintain Clarifier #2 RAS Service Flow. Created Follow Up WO to Address Aer. Blowers #2 and 3 Malfunctioning Vacuum Gauges ?> W11455733. Completed Debris Auger Service and Inspection. Drained and Replaced Oil. No Issues Found. Returned to Service. Cleared Associated Alarms. Completed WAS Pump #1 Inspection due to Previous WAS Lo/LoLo Flow Alarms. Removed Suction Line and Check Valve Cover. Cleared Obstructions and Debris, Flushed Units. Returned to Service and Tested in Manual with No Issues. Cleared Associated Alarms. Clarifier #1 Drawdown Process to be Continued. Returned RAS/WAS Suction Valves and Header to Service. RAS Pumps #1-2 in Auto and Duty, Pump #3 in Auto, OOS. Completed Aer. DO Sensor Maintenance. Placed Probes in Calibration Mode. Cleaned and Inspected Units, No Issues Found. Returned to Service. | Schomberg Water Resource Recovery Facility | 2025-11-19
WW-WEST | November | In to Complete Scheduled WOs. Notified ROC. Lowered and Activated Decant Pump. Decant Complete, Raised and Deactivated Decant Pump. Sludge Transfer Valve Manual Open, Transferred Thickened Sludge. Transfer Valve Returned to Manual Closed. Completed Filter Inlet TSS Sensor Inspection. Placed Unit in Calibration Mode Locally, Cleaned Probe. No Issues Found. Returned to Service. Completed UV System #1 and 2 Inspections. Found and Replaced Multiple Bulbs and O-Rings from Sleeves Containing Moisture from Rack #5 on UV #1 (A). Returned Rack to Service, However the Rack Did Not Re-Light, Possible Blown Fuse. Created Follow Up WO ?> W11475704. Returned Both UV Systems to Service. | Schomberg Water Resource Recovery Facility | 2025-11-28
WW-WEST | November | In to Complete Scheduled WOs. Notified ROC. Lowered and Activated Decant Pump. Decant Complete, Raised and Deactivated Decant Pump. Sludge Transfer Valve Local Open, Transferred Thickened Sludge. Transfer Valve Returned to Manual Closed. Completed Aer. Blowers #1-4 Oil Changes and Inspections. Air Filters and Belts OK. Returned to Service. Cleared Associated Alarms. | Schomberg Water Resource Recovery Facility | 2025-11-25
WW-WEST | November | In to Complete Reg. Sampling and Scheduled WOs. Investigated Recurring Alum Pumps #6 and 7 No Flow Alarms Communicated by the ROC. No Visible Leaks or Issues Found on Alum Board or Pumps. Cleared Associated Alarms and Returned Both Pumps to Duty and Service. Placed Alum Pumps #6 and 7 in Manual Off. Removed, Inspected and Cleaned Alum Dosage Line Flow Meter. Returned to Service. Flushed Alum Dosage Line with Hot Water, Returned to Normal Service Flow Rate. Returned Alum Pumps #6 and 7 to Auto and Duty. Will Continue to Monitor Pump Performance and Alarm Recurrence. | Schomberg Water Resource Recovery Facility | 2025-11-24
WW-WEST | November | In to Complete Scheduled WOs. Notified ROC. Opened Clarifier #1 RAS/WAS Manual Suction Valve. Closed RAS/WAS Suction Header Manual Interconnect Valve for Pump Dedication. RAS Pump #1 Manual On @ 100% Speed for Clarifier #1 Drawdown. RAS Pump #2 Manual On @ 7% Speed to Maintain Clarifier #2 RAS Service Flow. Lowered and Activated Decant Pump. Experienced Power Loss Event Whilst On-site, Generator Activated Automatically. Utility Power Restored and Transferred with No Issues. Reviewed SCADA, Restored Duties and Cleared Associated Alarms. Decant Complete, Raised and Deactivated Decant Pump. Clarifier #1 Drawdown Process Complete. Returned RAS/WAS Suction Valves and Header to Service. RAS Pumps #2-3 in Auto and Duty, Pump #3 in Auto, OOS. Completed Grit Dewatering Screws #1 and 2 Inspections and Service. Drained and Replaced Oil Reservoirs. Automatic Grease Applicators OK. Returned to Service. Completed Screenings Compactor Inspection and Service. Drained and Replaced Oil Reservoirs. Flushed Drainage Line. Returned to Service. Completed Aer. DO Sensor Maintenance. Placed Probes in Calibration Mode. Cleaned and Inspected Units, No Issues Found. Returned to Service. | Schomberg Water Resource Recovery Facility | 2025-11-26
WW-WEST | November | Remotely Re-Enabled RAS Pump Auto Duty Rotate, Pumps Rotated Automatically. Remotely Placed Supernatant Drain Valve in Manual Open. Remotely Responded to Alum Pumps #6 and 7 No Flow Alarms Communicated by the ROC. Returned Both Pumps to Duty, Alarms Cleared. Decant Complete. Remotely Closed Supernatant Valve in Manual. | Schomberg Water Resource Recovery Facility | 2025-11-21
WW-WEST | November | Remotely Placed Supernatant Drain Valve in Manual Open. Adjusted Auto Wasting Time Frame. WAS Pump Start: 15:00 ?> 16:00. Remotely Responded to Alum Pumps #6 and 7 No Flow Alarms. Acknowledged and Reset Alarms. Returned Both Pumps to Duty. Decant Complete. Remotely Closed Supernatant Valve in Manual. | Schomberg Water Resource Recovery Facility | 2025-11-28
WW-WEST | November | Harie Rajamithiran(OIT) working under the direction of Gavin Walker Cleaned in process building Cleaned washrooms Cleaned the UV FE channel Completed the 6 month sand filter maintenance | Schomberg Water Resource Recovery Facility | 2025-11-24
WW-WEST | November | In to Complete Scheduled WOs. Notified ROC. Lowered and Activated Decant Pump. Decant Complete, Raised and Deactivated Decant Pump. Opened Clarifier #1 RAS/WAS Manual Suction Valve. Closed RAS/WAS Suction Header Manual Interconnect Valve for Pump Dedication. RAS Pump #1 Manual On @ 100% Speed for Clarifier #1 Drawdown. RAS Pump #3 Manual On @ 40% Speed to Maintain Clarifier #2 RAS Service Flow. Adjusted Clarifier Eff. Alum Dosage Set-point Based On In-House and External Laboratory Results: 15 ?> 18 mg/L. GFL On-site for Sludge Load. Sludge Transfer Valve Local Open, Transferred Thickened Sludge. Transfer Valve Returned to Manual Closed. Cleared Associated Alarm. Completed Filter Inlet TSS Sensor Inspection. Placed Unit in Calibration Mode Locally, Cleaned Probe. No Issues Found. Returned to Service. Clarifier #1 Drawdown Process to be Continued. Returned RAS/WAS Suction Valves and Header to Service. RAS Pumps #1-2 in Auto and Duty, Pump #3 in Auto, OOS. | Schomberg Water Resource Recovery Facility | 2025-11-20
WW-WEST | November | Remotely Placed Supernatant Drain Valve in Manual Open. Remotely Rotated WAS Pump Duties. Pump #1 Manual Off, Pump #2 in Auto. Remotely Rotated RAS Pump Duties. Pump #3 in Duty #1, Pump #1 in Duty #3, OOS. Remotely Placed Scum Valve in Manual Discharge. Activated Scum Pump #2 in Manual. Scum Tank Drawdown Complete. Returned All to Auto and Service. Decant Complete. Remotely Closed Supernatant Valve in Manual. | Schomberg Water Resource Recovery Facility | 2025-11-24
WW-WEST | November | Remotely Placed Supernatant Drain Valve in Manual Open. Remotely Responded to Alum Pumps #6 and 7 No Flow Alarms Communicated by the ROC. Acknowledged and Reset Alarms. Returned Both Pumps to Duty. Decant Complete. Remotely Closed Supernatant Valve in Manual. | Schomberg Water Resource Recovery Facility | 2025-11-26
WW-WEST | November | Remotely Placed Supernatant Drain Valve in Manual Open. Decant Complete. Remotely Closed Supernatant Valve in Manual. | Schomberg Water Resource Recovery Facility | 2025-11-20
WW-WEST | November | Remotely Placed Supernatant Drain Valve in Manual Open. Decant Complete. Remotely Closed Supernatant Valve in Manual. | Schomberg Water Resource Recovery Facility | 2025-11-11
WW-WEST | November | Remotely Placed Sludge Transfer Valve in Manual Open, Transferred Thickened Sludge. Transfer Valve Returned to Manual Closed. | Schomberg Water Resource Recovery Facility | 2025-11-14
WW-WEST | November | In to Complete Reg. Sampling and Scheduled WOs. Notified ROC. Lowered and Activated Decant Pump. Decant Complete, Raised and Deactivated Decant Pump. Completed Grit Vortex #1 and 2 Inspections. Removed Rags and Debris from Impellers. Oil Levels OK. Greased Driveshaft Bearings. Returned to Service. | Schomberg Water Resource Recovery Facility | 2025-11-18
WW-WEST | November | Remotely Placed Supernatant Drain Valve in Manual Open. Re-Enabled RAS Pump Auto Duty Rotate, Pumps Rotated Automatically. Decant Complete. Remotely Closed Supernatant Valve in Manual. | Schomberg Water Resource Recovery Facility | 2025-11-12
WW-WEST | November | In to Complete Reg. Sampling and Scheduled WOs. Lowered and Activated Decant Pump. Decant Complete, Raised and Deactivated Decant Pump. Completed Filter Building and Blower Building Sump System Testing and Inspections. Tested HiHi Level Float Alarms, Confirmed Reception by the ROC. No Issues Found. Returned to Service. Cleared Associated Alarms. | Schomberg Water Resource Recovery Facility | 2025-11-11
WW-WEST | November | On site to assist contractor Total Power with Diesel PM and Load Test. Completed. Generator back in Auto and alarms reset. | Schomberg Water Resource Recovery Facility | 2025-11-17
WW-WEST | November | - Notified ROC of the work being performed - Inspected screenings compactor. All okay - Inspected travelling screen. All okay. Greased fittings - Inspected debris auger. All okay - Reduced wasting start window from 14 to 16 to reduce wasting - Performed in-house lab and recorded readings on SharePoint. No issues - Checked station and recorded readings. No new issues - Inspected vortex blowers 1 and 2. Belt, filter and oil are all good - Inspected sludge blowers 1 and 2. Belt and oil are good. Filters will need replacing soon. Placed order for more - Inspected aeration blowers 1-4. Oil and belt for blower 1-4 are all good. Filters were good for blower 1, 3, 4. Filter for blower 2 is satisfactory. Cleared aeration blowers uncommanded start and stop alarms. Placed all blowers back in duty rotation | Schomberg Water Resource Recovery Facility | 2025-11-13
WW-WEST | November | Install rubber repair kit backflow in chemical room and test Retested passed | Schomberg Water Resource Recovery Facility | 2025-11-13
WW-WEST | November | In to Complete Scheduled WOs. Lowered and Activated Decant Pump. Decant Complete, Raised and Deactivated Decant Pump. Adjusted Auto Wasting Time Frame. WAS Pump Start: 16:00 ?> 14:00. Completed Filter Inlet TSS Sensor Inspection. Placed Unit in Calibration Mode Locally, Cleaned Probe. No Issues Found. Returned to Service. | Schomberg Water Resource Recovery Facility | 2025-11-14
WW-WEST | November | Remotely Placed Supernatant Drain Valve in Manual Open. Remotely Placed Scum Valve in Manual Discharge. Activated Scum Pump #1 in Manual. Scum Tank Drawdown Complete. Returned All to Auto and Service. Decant Complete. Remotely Closed Supernatant Drain Valve in Manual. | Schomberg Water Resource Recovery Facility | 2025-11-18
WW-WEST | November | In to Complete Scheduled WOs. Notified ROC. Lowered and Activated Decant Pump. Decant Complete, Raised and Deactivated Decant Pump. Sludge Transfer Valve Manual Open, Transferred Thickened Sludge. Transfer Valve Returned to Manual Closed. Investigated UV Bank B Fault. Ran Unit in Local. Found and Replaced Burnt Out Bulb. Tested Unit, No Further Issues Found. Returned to Service. Cleared Local Alarm. Completed Aer. DO Sensor Maintenance. Placed Probes in Calibration Mode. Cleaned and Inspected Units, No Issues Found. Returned to Service. Completed Scum Pumps #1 and 2 Inspection. Couplings and Oil Levels OK. Test Ran Units in Local in Recirc. and Discharge Modes, No Issues Found. Returned Scum Pumps and Valve to Auto and Service. Completed RAS and WAS Pump #1 Inspections. Couplings and Oil Levels OK. No Issues Found. Returned to Service. Cleared Associated Alarms. Remaining RAS and WAS Pump Inspections Captured within WO #W11432144. | Schomberg Water Resource Recovery Facility | 2025-11-12
WW-WEST | November | Remotely Placed Supernatant Drain Valve in Manual Open. Decant Complete. Remotely Closed Supernatant Drain Valve in Manual. Remotely Placed Sludge Transfer Valve in Manual Open, Transferred Thickened Sludge. Transfer Valve Returned to Manual Closed. | Schomberg Water Resource Recovery Facility | 2025-11-17
WW-WEST | November | In to Complete Scheduled WOs. Notified ROC. Rotated WAS Pump Duties. Pump #2 Manual Off, Pump #1 in Auto. Rotated RAS Pump Duties. Pump #1 in Duty #1, Pump #3 in Duty #3, OOS. Adjusted Auto Wasting Time Frame. WAS Pump Start: 14:00 ?> 15:00. Completed Sludge Blower Building Room Supply Fan Filter Replacement with No Issues. Found UV Bank #1 (A) with Outstanding Local Alarm. Tested Unit in Manual. Rack #5 Showing No Power. Placed Bank in Manual Off. Notified On-site Maint. Electrician. Electrical Inspection of UV Bank #1 (A), Rack #5 Rendered a Blown Fuse. Fuse Replaced and Bank Tested in Manual with No Issues. Returned to Auto and Service. Cleared Associated Local Alarm. Completed Filter Reject Pumps #1 and 2 Inspections with No Issues. Tested Filter Reject Sump Hi Level Float, Confirmed Reception by the ROC. Returned All to Service and Cleared Associated Alarms. Completed Sludge Holding Tank Overflow Manual Valve Exercise with No Issues. Returned to Service. Completed Sludge Holding Tank Hi Float Alarm Test. Confirmed Reception by the ROC. Returned to Service. Cleared Associated Alarm. | Schomberg Water Resource Recovery Facility | 2025-11-17
WW-WEST | November | Remotely Placed Supernatant Drain Valve in Manual Open. Decant Complete. Remotely Closed Supernatant Valve in Manual. | Schomberg Water Resource Recovery Facility | 2025-11-14
WW-WEST | November | In to Complete Station Check. Cannot Review SCADA and Trends. OIT/HMI Error Message Remains Present. Notified TL. Will Review and Record Trends and Statistics Remotely. No other Issues Found. | Schomberg Dr. Kay Pumping Station | 2025-11-07
WW-WEST | November | P1 faulted due to a power blip Reset the vfd and everything is back to normal operation | Schomberg Dr. Kay Pumping Station | 2025-11-03
WW-WEST | November | There was a brief power blip around 9:00am causing p1 to fault. Reset the vfd and cleared the alarms. Everything back to normal operations | Schomberg Dr. Kay Pumping Station | 2025-11-01
WW-WEST | November | Remotely Placed Pump #1 in Manual Speed @ 100% for Pump Testing. Pump Testing Complete. Remotely Returned Pump #1 to Auto Speed. | Schomberg Dr. Kay Pumping Station | 2025-11-26
WW-WEST | November | In to Complete Station Check. Reviewed SCADA and Trends. Unable to Review Entirety of Station Pages due to PCS Issue. Created Follow Up WO ?> W11416182. No Other Issues Found. | Schomberg Dr. Kay Pumping Station | 2025-11-04
WW-WEST | November | In to Complete Station Check. Reviewed SCADA and Trends. No New Issues Found. | Schomberg Dr. Kay Pumping Station | 2025-11-28
WW-WEST | November | In to Complete Station Check. Reviewed SCADA and Trends. No New Issues Found. | Schomberg Dr. Kay Pumping Station | 2025-11-25
WW-WEST | November | Remotely Returned Pump #1 to Auto Speed. | Schomberg Dr. Kay Pumping Station | 2025-11-11
WW-WEST | November | In to Complete Station Check. Reviewed SCADA and Trends Remotely, Local HMI/OIT Issue Remains, Unable to Access or Login. No Other Issues Found. | Schomberg Dr. Kay Pumping Station | 2025-11-11
WW-WEST | November | Remotely Placed Pump #1 in Manual Speed @ 100% for Pump Testing. | Schomberg Dr. Kay Pumping Station | 2025-11-17
WW-WEST | November | In to Complete Scheduled WOs. Reviewed SCADA and Trends. No New Issues Found. | Schomberg Dr. Kay Pumping Station | 2025-11-18
WW-WEST | November | Completed Remote SCADA Trends Review. Pump #1 Run Times Appear Elongated. Placed Pump #1 in Manual Speed @ 100% for Flushing Purposes, Will Continue to Monitor. | Schomberg Dr. Kay Pumping Station | 2025-11-11
WW-WEST | November | - Notified ROC of the work being performed - Tested wet well high alarm. Alarm received - Tested pump and check valve, no issues - Tested air relief valve, no issues. Relieved air without problem - Wessuc onsite to clean wet well. Pumped down wet well for the contractors | Schomberg Dr. Kay Pumping Station | 2025-11-12
WW-WEST | November | In to Complete Scheduled WOs. Notified ROC. Contractor (Total Power) On-site for Semi-Annual Generator Testing and Inspection. Placed Pump #1 in Manual Speed @ 100% for Pump Testing. Manually Triggered Duty Rotation, Pump #1 in Duty #1. Reviewed SCADA and Trends. Pump Testing Complete with No Issues. Returned Pump #1 to Auto Speed. Transferred Station to Generator Power with No Issues. Acknowledged Associated Alarms. Completed JHSC and Hazardous Waste Removal Inspections with No Issues. Transferred Station Back to Utility Power with No Issues. Cleared Associated Alarms. Completed Building Hi/Lo Temperature Alarm Test. Confirmed Reception by the ROC. Returned to Service. Cleared Associated Alarms. | Schomberg Dr. Kay Pumping Station | 2025-11-14
WW-WEST | November | Pump Testing Complete. Remotely Returned Pump #1 to Auto Speed. | Schomberg Dr. Kay Pumping Station | 2025-11-18
WW-WEST | November | Informed ROC. Performed well LITs calibration and put instruments in Cal mode while doing the tasks. All alarms were cleared after the job. No other issues encountered | Schomberg Dr. Kay Pumping Station | 2025-11-17
ROC | November | Carter Dunn Signing In, 5D/Clear | ROC General | 2025-11-08
ROC | November | Angelica Chepiga signing out | ROC General | 2025-11-06
ROC | November | Connor Smith signing in -4C Snowy | ROC General | 2025-11-10
ROC | November | Connor Smith signing out | ROC General | 2025-11-05
ROC | November | Christian Van Beek signing out. | ROC General | 2025-11-09
ROC | November | STPSTL - Steven from ABPMC leaving site. | ROC General | 2025-11-05
ROC | November | Angelica Chepiga signing in, weather +6C | ROC General | 2025-11-05
ROC | November | Christian Van Beek signing in. | ROC General | 2025-11-06
ROC | November | KSSSQW - Joe Aloevera entering site 10:10 - finished at site | ROC General | 2025-11-07
ROC | November | STRS48 - Stephen and Phil from AB Project Management is on site to take out the old generator. | ROC General | 2025-11-07
ROC | November | MAPS- Courtney from Torbear onsite. | ROC General | 2025-11-06
ROC | November | KSTP - Drew from Ferguson Electric off site. | ROC General | 2025-11-06
ROC | November | AUETAD - Jason from Property Services is on site 10:15 - Jason is finished on site | ROC General | 2025-11-07
ROC | November | Adeela Khan signing in. Weather: 4C and cloudy | ROC General | 2025-11-07
ROC | November | JDSS - Theodore from AB finished at site | ROC General | 2025-11-07
ROC | November | Adam Button signing out | ROC General | 2025-11-08
ROC | November | Carter Dunn Signing Out | ROC General | 2025-11-08
ROC | November | Connor Smith signing in 2C Cloudy | ROC General | 2025-11-06
ROC | November | STPSTL- Steven from AB onsite. | ROC General | 2025-11-06
ROC | November | KSTP - Christian from Ferguson Electric on site to complete some drilling and pipe work. | ROC General | 2025-11-06
ROC | November | Town of Stouffville - Flushing for half the day | ROC General | 2025-11-07
ROC | November | KSSSQW - Joe O. is on site to fix a roof leak | ROC General | 2025-11-07
ROC | November | Angelica Chepiga signing in,weather +5C | ROC General | 2025-11-06
ROC | November | Adam Button signing in 3C Raining | ROC General | 2025-11-07
ROC | November | Adeela Khan signing in | ROC General | 2025-11-10
ROC | November | STPSMR - Steven from AB leaving site | ROC General | 2025-11-07
ROC | November | LSSS- Ben from Property Services onsite. | ROC General | 2025-11-10
ROC | November | STPSTL - Peter from ABPMC off site. | ROC General | 2025-11-06
ROC | November | Connor Smith signing out | ROC General | 2025-11-06
ROC | November | MAPS- Courtney from Torbear offsite. | ROC General | 2025-11-06
ROC | November | Adeela Khan signing out | ROC General | 2025-11-10
ROC | November | Ethan Ullalkar signing out. | ROC General | 2025-11-07
ROC | November | Christian Van Beek signing out. | ROC General | 2025-11-05
ROC | November | Christian Van Beek signing out. | ROC General | 2025-11-06
ROC | November | NBSP - Christine from security onsite for site visit | ROC General | 2025-11-07
ROC | November | Adeela Khan signing out | ROC General | 2025-11-07
ROC | November | Carter Dunn Signing Out | ROC General | 2025-11-09
ROC | November | AUETAD - Jason from PS finished at site | ROC General | 2025-11-07
ROC | November | Christian Van Beek signing in. Weather: 4C and clear. | ROC General | 2025-11-08
ROC | November | Carter Dunn Signing In, 0D/Snow | ROC General | 2025-11-09
ROC | November | KBSP- Terry Property Services offsite. | ROC General | 2025-11-06
ROC | November | Carter Dunn Signing In, -2D/Snow | ROC General | 2025-11-10
ROC | November | NMPSKC - Mike L. from IAM is on site 10:27 - Mike L. is finished on site | ROC General | 2025-11-07
ROC | November | Angelica Chepiga signing out | ROC General | 2025-11-07
ROC | November | Connor Smith signing out | ROC General | 2025-11-10
ROC | November | STPSTL - Drew from Ferguson Electric is on site 10:33- Ferguson Electric is finished on site | ROC General | 2025-11-10
ROC | November | AURSBS - Courtney finished at site | ROC General | 2025-11-07
ROC | November | KSTP- Gerrick from Ferguson onsite. | ROC General | 2025-11-06
ROC | November | KSTP - Garrick from Ferguson onsite for pipe runs for generator | ROC General | 2025-11-07
ROC | November | STPSTL- Hamid from ETO Engineering onsite. 17:14- Offsite. | ROC General | 2025-11-05
ROC | November | STPSTL- Theodore from AB leaving site and heading to STRS48 15:11- STRS48- Leaving site. | ROC General | 2025-11-05
ROC | November | MAPS- Courtney from Torbear offsite. | ROC General | 2025-11-05
ROC | November | STPSTL - Theodore from ABPMC on site for measurements. | ROC General | 2025-11-05
ROC | November | AUSS - Ben Han from property services leaving site. | ROC General | 2025-11-05
ROC | November | JDSS - Drew from Ferguson electric leaving site. | ROC General | 2025-11-03
ROC | November | JDSS- Drew from Ferguson onsite. | ROC General | 2025-11-04
ROC | November | Adeela Khan signing out | ROC General | 2025-11-01
ROC | November | AUPSWS- Phil from AB Construction onsite. Will be running generator. 11:50- Finished onsite. | ROC General | 2025-11-04
ROC | November | Adam Button signing in clear -1C | ROC General | 2025-11-02
ROC | November | MARS - Courtney from Torbear construction on site. | ROC General | 2025-11-03
ROC | November | Carter Dunn Signing Out | ROC General | 2025-11-03
ROC | November | Ethan U signing in | ROC General | 2025-11-03
ROC | November | Adam Button signing out | ROC General | 2025-11-01
ROC | November | Gluzen Ramos Ong signing in | ROC General | 2025-11-04
ROC | November | Wes from town of Stouffville flushing in Ballantrae | ROC General | 2025-11-04
ROC | November | Wes from town of Stouffville - Flushing in the afternoon | ROC General | 2025-11-04
ROC | November | LSSS- Ben from Property Services leaving site and heading to BVPS | ROC General | 2025-11-04
ROC | November | Angelica Chepiga signing out | ROC General | 2025-11-03
ROC | November | Adam Button singing in 4C Clear | ROC General | 2025-11-03
ROC | November | MAPS- Courtney from Torbear onsite. | ROC General | 2025-11-05
ROC | November | STETTL - Phil from ABPMC on site. | ROC General | 2025-11-05
ROC | November | MARS- Courtney from Torbear offsite. | ROC General | 2025-11-04
ROC | November | Adeela Khan signing in. Weather: 7C and partly cloudy | ROC General | 2025-11-04
ROC | November | Ethan Ullalkar signing out. | ROC General | 2025-11-03
ROC | November | Angelica Chepiga signing in, weather 7C | ROC General | 2025-11-03
ROC | November | Connor Smith signing out | ROC General | 2025-11-04
ROC | November | JDSS - Garrick from Ferguson electric on site. | ROC General | 2025-11-03
ROC | November | Adam Button signing out | ROC General | 2025-11-04
ROC | November | MAPS- Courtney from Torbear onsite. | ROC General | 2025-11-04
ROC | November | Connor Smith signing in 2 C Cloudy | ROC General | 2025-11-04
ROC | November | Adam Button signing in 2 Raining | ROC General | 2025-11-01
ROC | November | Adam Button signing out | ROC General | 2025-11-02
ROC | November | Ethan U signing in | ROC General | 2025-11-04
ROC | November | BVPS-Ben from Property Service finished onsite. | ROC General | 2025-11-04
ROC | November | Ethan Ullalkar signing out. | ROC General | 2025-11-04
ROC | November | GRSSWA - Kevin N from Yorknet on site. | ROC General | 2025-11-05
ROC | November | AUSS - Jeff from Keyshack on site. 16:10 Off site. | ROC General | 2025-11-03
ROC | November | Christian Van Beek signing in. | ROC General | 2025-11-05
ROC | November | BVPS - Ben from Property services onsite. 13:00 Ben from Property services offsite. | ROC General | 2025-11-03
ROC | November | KSSSP- Drew from Ferguson onsite. | ROC General | 2025-11-04
ROC | November | Adeela Khan signing in. Weather: 5C and Cloudy | ROC General | 2025-11-01
ROC | November | Adeela Khan signing out | ROC General | 2025-11-05
ROC | November | Connor Smith signing in 0C Snowy | ROC General | 2025-11-30
ROC | November | NMW15 - Kevin from Yorknet off site. Heading to NMETYS. | ROC General | 2025-11-26
ROC | November | QVW12- Thomas from IAM leaving site and heading to QVW34 | ROC General | 2025-11-20
ROC | November | STPSMR - Dominic from Honeywell on site. | ROC General | 2025-11-26
ROC | November | YDOC- John from property services is done on site and heading to SEOC QVW12- Garrick from Ferguson electric on site will be flipping off breaker to generator no impact on utility power expected KSSP- Theo from AB on site | ROC General | 2025-11-28
ROC | November | Connor Smith signing in | ROC General | 2025-11-19
ROC | November | STPSMR- Drew from Ferguson electric is on site | ROC General | 2025-11-19
ROC | November | Carter Dunn Signing In | ROC General | 2025-11-27
ROC | November | NBET27 - Jason from Palladin (647 210 3902) is on site to work on card reader trouble 11:49 - Jason is finished on site | ROC General | 2025-11-26
ROC | November | BLW3- Pete from Endeavor working for Torbear called and had triggered a generator fault alarm. Alarm cleared. | ROC General | 2025-11-19
ROC | November | NBSSJA- Ben from Property services is on site | ROC General | 2025-11-27
ROC | November | Connor Smith signing out | ROC General | 2025-11-29
ROC | November | Angelica Chepiga signing in, weather -2C | ROC General | 2025-11-28
ROC | November | AUW14- Dimitri from CPD onsite taking pictutres QVETQS- Thomas from IAM and Landmark finished onsite | ROC General | 2025-11-19
ROC | November | AUETFC, Terry G from property services is on site | ROC General | 2025-11-27
ROC | November | Carter Dunn Signing Out | ROC General | 2025-11-25
ROC | November | MARS- Courtney from Torbear is on site | ROC General | 2025-11-24
ROC | November | EGSSSC - Joe O from property services leaving site. Pesticon pest control visiting the following sites today: EGSSSC, QVSSSC, HLSSBS, HLETYS, HLETPR, HLW3, HLW1, ANW23 | ROC General | 2025-11-25
ROC | November | Carter D Signing In | ROC General | 2025-11-24
ROC | November | Christian an Beek signing in. Weather: 6C and clear. | ROC General | 2025-11-25
ROC | November | Adam Button signing in | ROC General | 2025-11-20
ROC | November | Ethan Ullalkar signing out. | ROC General | 2025-11-21
ROC | November | Christian Van Beek signing in. | ROC General | 2025-11-24
ROC | November | MKPSSA- Garrick from Ferguson Electric is offsite | ROC General | 2025-11-24
ROC | November | Pestacon attending MAPS, RHRSTR, VNRSKS | ROC General | 2025-11-19
ROC | November | STPSTL- Phil from Ab is done on site | ROC General | 2025-11-19
ROC | November | Ethan Ullalkar signing out. | ROC General | 2025-11-23
ROC | November | Connor Smith signing in -4 Clear | ROC General | 2025-11-29
ROC | November | STPSTL- Garrick from Ferguson Electric is on site | ROC General | 2025-11-25
ROC | November | QVW12/QVW34/QVETQS/MTSS/MTW12/MTETNL/MTW3/MTSP, PCO Operator on site | ROC General | 2025-11-28
ROC | November | NBSSJA - Ben from Property Services is on site to replace a VFD fan | ROC General | 2025-11-26
ROC | November | Carter Dunn Signing Out | ROC General | 2025-11-21
ROC | November | Adam Button signing in 1C Clear | ROC General | 2025-11-24
ROC | November | Stouffville Water System - Cody from OCWA will be flushing throughout Stouffville today. | ROC General | 2025-11-24
ROC | November | Pesticon Pest control operator visiting the following sites: MKRSMR, STW12, STRS48, STETBR, BLETNL, BLW3, STPSTL. | ROC General | 2025-11-24
ROC | November | Christian Van Beek signing out. | ROC General | 2025-11-25
ROC | November | MKPSSA- Drew from Ferguson Electric is on site 8:06- MKPSSA- Drew from Ferguson Electric is done on site | ROC General | 2025-11-20
ROC | November | Ethan Ullalkar signing out. | ROC General | 2025-11-22
ROC | November | Ethan U signing in Weather 4. | ROC General | 2025-11-23
ROC | November | STPSTL- drew from Ferguson Electric is on site KBSP- Stephen from AB is on site | ROC General | 2025-11-19
ROC | November | NMETYS- Melha from YRP is on site 10:45- NMETYS- Melha from YRP is done on site | ROC General | 2025-11-24
ROC | November | Adam Button signing in -2 Clear | ROC General | 2025-11-19
ROC | November | STPSMR- Dominic from Honeywell onsite. | ROC General | 2025-11-19
ROC | November | STPSTL - Drew from Ferguson Electric leaving site. | ROC General | 2025-11-25
ROC | November | JFPS - CPD with contractor on site. | ROC General | 2025-11-26
ROC | November | Angelica Chepiga signing out | ROC General | 2025-11-26
ROC | November | AUSS - Pat from Property Services is on site testing the fire alarm 08:46 - Pat is finished on site | ROC General | 2025-11-21
ROC | November | Connor Smith signing in 6C Clear | ROC General | 2025-11-21
ROC | November | STW12 - Garrick from Ferguson Electric on site for epoxy work. | ROC General | 2025-11-24
ROC | November | Adam Button signing out | ROC General | 2025-11-24
ROC | November | KSTP - Christian from Ferguson electric leaving site. | ROC General | 2025-11-26
ROC | November | Christian Van Beek signing out. | ROC General | 2025-11-24
ROC | November | Christian Van Beek signing out. | ROC General | 2025-11-19
ROC | November | Adam Button signing out | ROC General | 2025-11-25
ROC | November | STW12, Gerrick from Ferguson Electric is leaving site | ROC General | 2025-11-24
ROC | November | QVW12- Drew from Ferguson Electric is on site for temporary generator hook up KSTP- Andrew from Ferguson Electric is on site | ROC General | 2025-11-27
ROC | November | VNETFD- Meghal from YRP on site QVW34- Thomas from IAM is done on site | ROC General | 2025-11-20
ROC | November | MARS - Courtney (contractor) onsite for res restoration | ROC General | 2025-11-21
ROC | November | YDOC - Dimitry from CPD on site. 12:40 Off site. | ROC General | 2025-11-26
ROC | November | STPSMR- Dom from Honey well is done on site | ROC General | 2025-11-19
ROC | November | Pest control visiting sites: BLW12, NMETIB, NMETHW, NMW14, NMSSBP, NMEQ, NMSSHS, NMW12, NMW15, NMETYS, NMPSKC, NMW136, NMTKBS, ANW12. | ROC General | 2025-11-26
ROC | November | STPSTL- Drew from Ferguson Electric is on site SEOC4- Drew from Ferguson Electric is on site | ROC General | 2025-11-20
ROC | November | Ethan U signing in Weather 5. | ROC General | 2025-11-22
ROC | November | KSTP- Christian from Ferguson onsite. | ROC General | 2025-11-20
ROC | November | Adam Button signing out | ROC General | 2025-11-20
ROC | November | Connor Smith signing out | ROC General | 2025-11-26
ROC | November | Adeela Khan signing in | ROC General | 2025-11-26
ROC | November | Adeela Khan signing in. Weather: 4C and cloudy | ROC General | 2025-11-21
ROC | November | KSSP - Christian from Ferguson Electric is on site. | ROC General | 2025-11-21
ROC | November | SEOC67 - Theodore is finished on site | ROC General | 2025-11-21
ROC | November | MTSP - Terry G from property services on site to work on emergency lights. | ROC General | 2025-11-25
ROC | November | Connor Smith signing in 4C Clear | ROC General | 2025-11-22
ROC | November | MKPSSA- Garrick from Ferguson Electric is done on site | ROC General | 2025-11-24
ROC | November | KSTP, Christian from Ferguson Electric is leaving site | ROC General | 2025-11-24
ROC | November | Connor Smith signing out | ROC General | 2025-11-30
ROC | November | STPSTL - Drew from Ferguson Electric is finished on site | ROC General | 2025-11-21
ROC | November | STPSMR - Drew from Ferguson Electric is on site for a meeting | ROC General | 2025-11-26
ROC | November | STPSMR - Drew from Ferguson electric leaving site. | ROC General | 2025-11-26
ROC | November | Adeela Khan signing out | ROC General | 2025-11-26
ROC | November | Adam Button signing in -2 Clear | ROC General | 2025-11-27
ROC | November | MARS- Courtney from Torbear is on site | ROC General | 2025-11-27
ROC | November | STPSTL- Phil from AB onsite. | ROC General | 2025-11-19
ROC | November | STPSTL - Stephen from AB leaving site. | ROC General | 2025-11-26
ROC | November | MARS - Corey Ryan on site with a contractor. | ROC General | 2025-11-24
ROC | November | STPSTL- Stephen from AB on site | ROC General | 2025-11-28
ROC | November | Connor Smith signing in | ROC General | 2025-11-20
ROC | November | SEOC OCF- Drew from Ferguson heading to site. 15:25- Offsite. | ROC General | 2025-11-20
ROC | November | Adam Button signing in -3C Clear | ROC General | 2025-11-28
ROC | November | AUW14, Will from Chubb is on site | ROC General | 2025-11-19
ROC | November | SEOC13 - Johnathan (contractor) onsite for fire testing | ROC General | 2025-11-21
ROC | November | QVETQS- Thomas from IAM is on site | ROC General | 2025-11-20
ROC | November | BVPS - Owen from TQS on site to open some chamber lids for inspection. May see associated alarms. | ROC General | 2025-11-25
ROC | November | STPSTL- Drew from Ferguson Electric is done on site | ROC General | 2025-11-20
ROC | November | JDSS- Christian from Ferguson Electric is done on site | ROC General | 2025-11-27
ROC | November | QVW12 - Drew (Ferguson) finished on site | ROC General | 2025-11-27
ROC | November | Adam Button signing out | ROC General | 2025-11-19
ROC | November | MKPSSA - Drew onsite for epoxy work KBSP - Theodore from AB onsite | ROC General | 2025-11-21
ROC | November | Connor Smith signing out | ROC General | 2025-11-19
ROC | November | SEOC4 AHF - Johnathan from Property Services is on site for fire testing 13:06 - Johnathan is finished on site and is headed to SEOC 67 13:40 - Johnathan is finished on site at SEOC 67 | ROC General | 2025-11-21
ROC | November | QVETQS- Thomas from IAM is on site | ROC General | 2025-11-19
ROC | November | KSSP- Ben from Property services is done on site SEOC6- Drew from Ferguson Electric is on site | ROC General | 2025-11-20
ROC | November | QVETQS- Thomas from IAM is done site | ROC General | 2025-11-20
ROC | November | Carter Dunn Signing In, 4D/Clear | ROC General | 2025-11-20
ROC | November | MKETFA - Onat from ETO Engineering is finished on site | ROC General | 2025-11-26
ROC | November | Christian Van Beek signing in. Weather: -2C and clear. | ROC General | 2025-11-26
ROC | November | Domenic (Honeywell) - MTETNL - SUSP (dump pad only) | ROC General | 2025-11-27
ROC | November | Adeela Khan signing out | ROC General | 2025-11-21
ROC | November | NBW3 - Ken H from ITS onsite to complete work related to the corporate network system. | ROC General | 2025-11-25
ROC | November | STPSTL- Drew from Ferguson electric is done on site | ROC General | 2025-11-19
ROC | November | Christian Van Beek singing out. | ROC General | 2025-11-27
ROC | November | NMSSBP - Pat from Property Services is on site to test the fire alarm Pat is finished on site | ROC General | 2025-11-21
ROC | November | NMETHW - Thomas work on minor repoair | ROC General | 2025-11-21
ROC | November | KBSP - William from CHUBB on site. 18:00 Off site | ROC General | 2025-11-26
ROC | November | HLW2- Mike for CPD on site | ROC General | 2025-11-20
ROC | November | Adam Button signing out | ROC General | 2025-11-28
ROC | November | KBSP- Terry from Property Services leaving site. | ROC General | 2025-11-20
ROC | November | SEOC67- Drew from Ferguson leaving site. YDOC- Drew from Ferguson heading to site. | ROC General | 2025-11-20
ROC | November | MKETFA - Ahmad from YR police on site. 11:05 off site | ROC General | 2025-11-26
ROC | November | KSTP- Christian from Ferguson offsite. | ROC General | 2025-11-19
ROC | November | Connor Smith signing out | ROC General | 2025-11-23
ROC | November | KBSP-Theodore from AB is done on site | ROC General | 2025-11-19
ROC | November | HLSSBS- Ben from Property Service onsite for work on unit heater. | ROC General | 2025-11-19
ROC | November | KBSP- Theodore from AB offsite. | ROC General | 2025-11-20
ROC | November | Connor Smith signing out | ROC General | 2025-11-22
ROC | November | Carter Dunn Signing In | ROC General | 2025-11-28
ROC | November | JDSS, Drew from Ferguson electric is on site, they will be removing the temp generator | ROC General | 2025-11-28
ROC | November | HLW2 - Richard from International Water Supply is on site | ROC General | 2025-11-26
ROC | November | Angelica Chepiga signing out | ROC General | 2025-11-29
ROC | November | Carter Dunn Signing In, 1D/Clear | ROC General | 2025-11-19
ROC | November | Carter Dunn Signing In | ROC General | 2025-11-25
ROC | November | NMSSBP - Joe O on site for a quick visit and inspection. 15:41 - NMSSBP - Joe O leaving site. | ROC General | 2025-11-25
ROC | November | QVW12 - Christian from Ferguson Electric leaving site. Was on site briefly to collect equipment. | ROC General | 2025-11-24
ROC | November | STPSTL, Garrick from Ferguson Electric is on site | ROC General | 2025-11-25
ROC | November | BVPS - Owen from TQS leaving site. | ROC General | 2025-11-25
ROC | November | Adam Button signing in | ROC General | 2025-11-25
ROC | November | Ethan U signing in Weather 6. | ROC General | 2025-11-24
ROC | November | Gluzen Ramos Ong signing out | ROC General | 2025-11-27
ROC | November | Ethan U signing in | ROC General | 2025-11-21
ROC | November | Angelica Chepiga signing in, weather +8C | ROC General | 2025-11-26
ROC | November | STETTL - Dan (AB Const, 9054643613) | ROC General | 2025-11-27
ROC | November | Connor Smith signing in 6C Rain | ROC General | 2025-11-25
ROC | November | Adam Button signing out | ROC General | 2025-11-27
ROC | November | STPSTL, Theodor from AB is leaving site | ROC General | 2025-11-28
ROC | November | YDOC, Jonathon from Property services is on site, testing fire alarms | ROC General | 2025-11-28
ROC | November | Ethan Ullalkar signing out. | ROC General | 2025-11-13
ROC | November | STRS48 - Phil from AB offsite. | ROC General | 2025-11-11
ROC | November | KBSP - Ben from Property services on site. STRS48 - Phil from AB on site. | ROC General | 2025-11-11
ROC | November | Ethan Ullalkar signing out. | ROC General | 2025-11-12
ROC | November | Angelica Chepiga signing out | ROC General | 2025-11-11
ROC | November | MTSP - Terry G onsite for emergency lighting | ROC General | 2025-11-13
ROC | November | Pest Control attending following sites- VNETFD PVSS VNPSAP BLSS VNETAG | ROC General | 2025-11-11
ROC | November | SHTP - Vlad from Security Canada working onsite. | ROC General | 2025-11-11
ROC | November | STRS48 - Phil from AB working on site. | ROC General | 2025-11-12
ROC | November | STRS48 - Phil from AB leaving site. | ROC General | 2025-11-13
ROC | November | STRS48 - Phil from AB finished at site | ROC General | 2025-11-12
ROC | November | Carter Dunn Signing In, 0D/Clear | ROC General | 2025-11-14
ROC | November | Angelica Chepiga signing in | ROC General | 2025-11-11
ROC | November | Ethan U signing in | ROC General | 2025-11-13
ROC | November | Connor Smith signing out | ROC General | 2025-11-14
ROC | November | Christian Van Beek signing in. Weather: 2C and clear. | ROC General | 2025-11-16
ROC | November | STPSTL - Garrick from Ferguson electric on site, will run generator on load today for 4 hours. | ROC General | 2025-11-14
ROC | November | Carter Dunn Signing In | ROC General | 2025-11-17
ROC | November | Ethan Ullalkar signing out. | ROC General | 2025-11-15
ROC | November | Ethan Ullalkar signing out. | ROC General | 2025-11-17
ROC | November | KCETFS, Arhmed from PCP Telecomm is on site 09:17, Arhmed is finished on site | ROC General | 2025-11-14
ROC | November | Adeela Khan signing out | ROC General | 2025-11-17
ROC | November | Angelica Chepiga signing in | ROC General | 2025-11-12
ROC | November | Christian Van Beek signing out. | ROC General | 2025-11-16
ROC | November | Town of Stouffville - Andrew M from Ontario clean water agencies. Hydrant flushing and winterization, Zone 1 & 2 till 4pm C: 226-377-7178 15:41 - Andrew informed they are extending flushing to 5pm | ROC General | 2025-11-12
ROC | November | STRS48, Stephen from AB is on site | ROC General | 2025-11-17
ROC | November | Adam Button signing in -2 Clear | ROC General | 2025-11-18
ROC | November | Christian Van Beek signing out. | ROC General | 2025-11-18
ROC | November | MTSP, Terry from Property Services is on site | ROC General | 2025-11-18
ROC | November | KBSP - Terry G. from Property Services is on site working on the outside lights 13:47 - Terry is finished on site | ROC General | 2025-11-17
ROC | November | STPSTL, Drew from Ferguson Electric is on site | ROC General | 2025-11-18
ROC | November | STPSTL - Drew from Ferguson onsite for installation of temp generator | ROC General | 2025-11-13
ROC | November | Adam Button signing out | ROC General | 2025-11-13
ROC | November | KBSP- Phil from AB is offsite STPSMR- Franco from Property services is done on site | ROC General | 2025-11-18
ROC | November | QVETQS- Thomas from IAM is done on site | ROC General | 2025-11-18
ROC | November | GWTP, GWTP low - Kevin from Yorknet leaving site. | ROC General | 2025-11-12
ROC | November | Angelica Chepiga signing out | ROC General | 2025-11-12
ROC | November | BLSS- Chris from Property services is on site fore fire alarm testing | ROC General | 2025-11-11
ROC | November | Carter Dunn Signing In | ROC General | 2025-11-18
ROC | November | KBSP- Stephen from AB is on site | ROC General | 2025-11-18
ROC | November | MTSP - Terry G from Property services leaving site. | ROC General | 2025-11-13
ROC | November | PVSS - Vlad from Security Canada working on site. 16:45 Vlad off site. | ROC General | 2025-11-11
ROC | November | Angelica Chepiga signing out | ROC General | 2025-11-14
ROC | November | NMSSBP - Ben from Property services leaving site. | ROC General | 2025-11-11
ROC | November | Adam Button signing out | ROC General | 2025-11-18
ROC | November | Adam Button signing in 2C Raining | ROC General | 2025-11-12
ROC | November | Christian Van Beek signing in. Weather: 0C and clear. | ROC General | 2025-11-18
ROC | November | JDSS, Stephen from AB is on site | ROC General | 2025-11-14
ROC | November | KSTP, Drew from Ferguson Electric is leaving site | ROC General | 2025-11-14
ROC | November | Carter Dunn Signing Out | ROC General | 2025-11-12
ROC | November | Bayview Odor Control- Omar from IAM is on site | ROC General | 2025-11-18
ROC | November | KSTP - Drew from Ferguson electric leaving site. | ROC General | 2025-11-14
ROC | November | MTSP, Terry from property services is finished on site | ROC General | 2025-11-18
ROC | November | Carter Dunn Signing Out | ROC General | 2025-11-18
ROC | November | MAPS, Chris from Property Services is on site testing the fire alarm | ROC General | 2025-11-17
ROC | November | STPSTL - Drew from Ferguson leaving site | ROC General | 2025-11-13
ROC | November | KSSP/KSOCMA, Ranveer from PC Security is on site | ROC General | 2025-11-18
ROC | November | Connor Smith signing in 4C Cloudy | ROC General | 2025-11-13
ROC | November | Angelica Chepiga signing in | ROC General | 2025-11-14
ROC | November | STRS48, Franko from property services is on site | ROC General | 2025-11-18
ROC | November | QVW12 - Phil from AB Project Management and Construction is on site. 09:50 - Phil is finished on site | ROC General | 2025-11-17
ROC | November | Christian Van Beek signing in. Weather: 0C and clear. | ROC General | 2025-11-17
ROC | November | Adam Button signing in -3 Snowing | ROC General | 2025-11-11
ROC | November | Ethan U signing in Weather 2. | ROC General | 2025-11-12
ROC | November | Ethan U signing in Weather 2. | ROC General | 2025-11-16
ROC | November | Adam Button signing out | ROC General | 2025-11-11
ROC | November | Angelica Chepiga signing in, weather +4C | ROC General | 2025-11-13
ROC | November | Carter Dunn Signing In, 0D/Clear | ROC General | 2025-11-11
ROC | November | QVW12, Harry from Property services is on site | ROC General | 2025-11-14
ROC | November | Ethan Ullalkar signing out. | ROC General | 2025-11-16
ROC | November | Christian Van Beek signing in. Weather: 0C and clear. | ROC General | 2025-11-15
ROC | November | STRS48 - Phil from AB on site. | ROC General | 2025-11-13
ROC | November | Adeela Khan signing in. Weather: -1 and Snowing | ROC General | 2025-11-17
ROC | November | AUETFC - Terry G on site working on emergency lights 09:43 Terry G leaving site. | ROC General | 2025-11-13
ROC | November | STPSMR - Drew from Ferguson electric leaving site. | ROC General | 2025-11-12
ROC | November | YDOC - Ben from Property services on site. 14:05 Ben from Property services off site. | ROC General | 2025-11-12
ROC | November | KSTP - Drew from Ferguson electric on site. | ROC General | 2025-11-14
ROC | November | Ethan U signing in Weather 2. | ROC General | 2025-11-14
ROC | November | Ethan U signing in Weather 6. | ROC General | 2025-11-15
ROC | November | Christian Van Beek signing out. | ROC General | 2025-11-15
ROC | November | AUETAD - Can from ITS on site, checking corp. network. | ROC General | 2025-11-13
ROC | November | QVETQS, Junji from IAM is on site with Landmark | ROC General | 2025-11-18
ROC | November | KSTP- Khalid from Public works is on site | ROC General | 2025-11-18
ROC | November | STETBR - Historian heartbeat alarm. Checked site, operations normal and trends appear unaffected. Contacted Arthur L who will investigate. Created CMU5#W11428183 #Consult # CMU5 | All Water System ROC General | 2025-11-08
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-08
ROC | November | MARS - Cell 1 high level alarm. Deactivated duty 1 at RHRSTR to decrease flow from Richmond Hill to Vaughan. | All Water System ROC General | 2025-11-09
ROC | November | YWS+NYWS normal BVPS- Deactivated D1 RHMCMD- Placed valve in man/open | All Water System ROC General | 2025-11-08
ROC | November | MKRSEM- Reservoir 1 level hi alarm came in called Metro spoke with Zorhan to stop pumping to reservoir SHETCS- Post injection total high alarm came in interlocking hypo pumps. Cleared after 5 mins YWS+NYWS normal | All Water System ROC General | 2025-11-08
ROC | November | Christian Van Beek signing in. Weather: 4C and clear. | All Water System ROC General | 2025-11-08
ROC | November | Carter Dunn Signing Out | All Water System ROC General | 2025-11-08
ROC | November | GWTP - Multiple Train Permeate Turbidity Fault alarms came in. Checked site. Plant is not running. Called Stephen B, but no answer. Will try again 11:59 - Called Stephen B. who informed that the multiple train permeate turbidity fault alarms came in because of the UV maintenance that is being done. Stephen directed to disregard alarms until UV maintenance is finished. Stephen also informed that contractors are working to place pump 4 at the low lift station back online. Requested to disregard low lift power related alarms until work is complete | All Water System ROC General | 2025-11-07
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-09
ROC | November | AURSOH - activated Duty 1. VNRSKS - activated Duty 1 to help maintain MARS level. | All Water System ROC General | 2025-11-06
ROC | November | YWS + NYWS NORMAL | All Water System ROC General | 2025-11-06
ROC | November | YWS + NYWS NORMAL | All Water System ROC General | 2025-11-06
ROC | November | HLW1 - Treated Free chlorine residual HiHi, quick spike, value back to normal in 2 readings. Cleared alarm. - Station turbidity High alarm, will monitor. | All Water System ROC General | 2025-11-06
ROC | November | MKPSSA - Pump 2 man/stop. | All Water System ROC General | 2025-11-06
ROC | November | NMETHW, Activated D1 | All Water System ROC General | 2025-11-08
ROC | November | MKRSEM - Called Toronto Water and requested they stop flow to MKRSEM. | All Water System ROC General | 2025-11-09
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-09
ROC | November | STETBR - Patrick F deactivated duty remotely to help with STETTL fill cycle. He is monitoring and will activate Duty later today. # Consult | All Water System ROC General | 2025-11-05
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-09
ROC | November | Christian Van Beek signing out. | All Water System ROC General | 2025-11-09
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-09
ROC | November | MKRSEM- reservoir level lo alarm. Called Toronto water (Peter), requested to start two pumps to fill reservoir. | All Water System ROC General | 2025-11-06
ROC | November | MARS - High level, Deactivated RHRSTR Duty 1. | All Water System ROC General | 2025-11-07
ROC | November | Adeela Khan signing in. Weather: 4C and cloudy | All Water System ROC General | 2025-11-07
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-05
ROC | November | MKPSSA- Placed Pump 2 man/on to draw down MKREM | All Water System ROC General | 2025-11-05
ROC | November | KSTP - Conduit level sensor is now showing that the conduit channel is filling. Placed the KSTP high lift pumps in auto mode as per Patrick F direction. | All Water System ROC General | 2025-11-06
ROC | November | YWS + NYWS Normal Christian Van Beek signing out. | All Water System ROC General | 2025-11-06
ROC | November | YWS + NYWS Normal Connor Smith signing out | All Water System ROC General | 2025-11-05
ROC | November | AUPSRR - Post injection free chlorine hihi alarm. Checked site, reservoir recently started filling and the chlorination system activated. Trending shows a spike of the post injection free chlorine reading which returned to normal range after one reading. Reset alarm. | All Water System ROC General | 2025-11-08
ROC | November | ARPS- Total Ammonia Fault alarm. Duty 2 just deactivated. Able to reset alarm. | All Water System ROC General | 2025-11-05
ROC | November | KSETDP - Inlet total chlorine hihi alarm. Checked site, system duty recently deactivated. Trending shows a spike of the inlet total chlorine reading which dropped once inlet flow stopped. reset alarm. | All Water System ROC General | 2025-11-09
ROC | November | RHMCMD - Man/close to help with RHRSTR fill cycle. | All Water System ROC General | 2025-11-06
ROC | November | RHMCMD - back to auto, flow to RH | All Water System ROC General | 2025-11-06
ROC | November | RHMCMD - Opened valve. | All Water System ROC General | 2025-11-10
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-10
ROC | November | Connor Smith signing in -4C Snowy | All Water System ROC General | 2025-11-10
ROC | November | SHETCS - Post injection total chlorine hihi and hypo pumps 1 and 2 OOS alarms. Checked site, hypo pumps are manual off. Logbook shows Dave T logged into site, likely working on the system. | All Water System ROC General | 2025-11-05
ROC | November | YWS + NYWS Normal Connor Smith signing out | All Water System ROC General | 2025-11-06
ROC | November | NMW15 - Treated total chlorine High alarm, adjusted Chlorinator 2 dosage from 48 to 46%. | All Water System ROC General | 2025-11-06
ROC | November | RHMCMD - 100% open, flow to RH | All Water System ROC General | 2025-11-07
ROC | November | KLPSWL- Jacob M onsite for work orders including generator run, prv, flood alarm, and Cl leak alarm. | All Water System ROC General | 2025-11-06
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-08
ROC | November | STW12 - Deactivated STW2 and placed in auto mode. | All Water System ROC General | 2025-11-09
ROC | November | NMETIB, Activated D1 | All Water System ROC General | 2025-11-09
ROC | November | HLW1 - Cole W called and directed to place HLW1 in auto. Made necessary changes. | All Water System ROC General | 2025-11-05
ROC | November | KSTP - Ben H on site for the flocculation tank cleaning. KSTP will be offline for the duration of the work. | All Water System ROC General | 2025-11-06
ROC | November | SHTP- David T onsite for work orders including generator run, UVT analyzer maintenance, and health and safety. | All Water System ROC General | 2025-11-06
ROC | November | RHMCMD - Man/close to help with RHRSTR fill cycle. | All Water System ROC General | 2025-11-06
ROC | November | NMETHW - Deactivated Duty 1 to offset with NMETIB. | All Water System ROC General | 2025-11-06
ROC | November | SHTP - Filter 2 turbidity hi alarm after filter 1 backwash. Reset alarms as per shift report. | All Water System ROC General | 2025-11-06
ROC | November | AUW14- Treated free Cl2 hihi alarm , recovered after 3 mins. Cleared alarm | All Water System ROC General | 2025-11-06
ROC | November | NBW3 - Influent free chlorine lolo alarm. Checked site, well recently activated in schedule mode. Trending shows a sudden drop of the influent reading which recovered within one reading interval. Placed hypo pump 2 back into duty 1 and cleared alarms. Monitored well start. MKETFA - Mehdi from Toronto Water called to inform that they will be exercising valves and the tower outlet flow will be high during the exercise. Monitoring site. | All Water System ROC General | 2025-11-06
ROC | November | STETTL - Tower level lolo alarm. Checked site, tower duty 1 start setpoint is the same at the tower lolo level alarm. Tower is still being deep cycled by East Ops to help with seasonal chlorine residuals. | All Water System ROC General | 2025-11-06
ROC | November | AUETAD- Historian Heartbeat Alarm. Notified Artour L. He will look into it. | All Water System ROC General | 2025-11-06
ROC | November | STRS48 - Stephen and Phil from AB Project Management is on site to take out the old generator. | All Water System ROC General | 2025-11-07
ROC | November | STPSMR - Kyle R. called to inform that he is on site to troubleshoot pump 2 15:10 - Kyle called back to inform that he is finished on site and pump 2 is back to normal operations | All Water System ROC General | 2025-11-07
ROC | November | AUPSWS - Lee F called and requested that pump 4 be placed in duty 1 for inspection. Made necessary change. | All Water System ROC General | 2025-11-05
ROC | November | KLW34- Historian Heartbeat Alarm. Notified Artour L. He will look into it. 11:11- Artour L cleared alarm. | All Water System ROC General | 2025-11-06
ROC | November | NMVCBA - Placed 40 l/s man/open to extend NMETIB drain cycle. | All Water System ROC General | 2025-11-05
ROC | November | GWTP - Phil D and Stephen B on site to complete UV maintenance and test the generator and clean the clearwell analyzers. | All Water System ROC General | 2025-11-06
ROC | November | AUEQSJ- Eric S onsite working on LIT4 *Wrong Book | All Water System ROC General | 2025-11-05
ROC | November | Adeela Khan signing out | All Water System ROC General | 2025-11-07
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-09
ROC | November | NMW15, Treated Total Cl2 hi alarm, adjusted Cl2 dosing from 46% to 44%, will continue to monitor | All Water System ROC General | 2025-11-09
ROC | November | MKPSSA - Free chlorine residual hi alarm. Contacted Jack P who will attend site today to check the analyzer. Jack stated that if the alarm clears and returns it can be disregarded until 16:00 today. | All Water System ROC General | 2025-11-06
ROC | November | Stouffville Water System- Wes from Town of Stouffville flushing in Zone 2 | All Water System ROC General | 2025-11-06
ROC | November | STW12 - Deactivated STW2 and placed in auto mode. | All Water System ROC General | 2025-11-10
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-10
ROC | November | MTW12- Joe M onsite for work orders including generator run, injection points and analyzer maintenance. Disregard all alarms while onsite. | All Water System ROC General | 2025-11-06
ROC | November | GWTP- Low lift electrical room temp hihi alarm came in trends look sporatic. Will email East team about issue able to clear alarm | All Water System ROC General | 2025-11-07
ROC | November | QVW12- Combined Cl2 lo alarm came in. Well not active no water directed to users NMETIB- Activated D1 to offset from NMETHW as per shift report ARPS- Total ammonia fault alarm came in residual within range cleared alarm after 3mins YWS+NYWS normal | All Water System ROC General | 2025-11-07
ROC | November | STRS48- Eric S finished working on turbidimeter and leaving site. | All Water System ROC General | 2025-11-06
ROC | November | YWS + NYWS NORMAL | All Water System ROC General | 2025-11-05
ROC | November | SHTP - Filter 2 turbidity hi alarm after filter 1 backwash. Reset alarms as per shift report. | All Water System ROC General | 2025-11-05
ROC | November | NMTKKC - Header combined chlorine hihi alarm. Checked site, chemical system has interlocked on the hihi combined reading. Trending shows a sudden spike of the combined and total chlorine readings. Instrumentation team finished their annual calibrations minutes before the alarms triggered. Contacted Jason G to inform, while speaking with Jason G the analyzer readings returned to normal range and the alarms cleared. Will monitor site and call Jason G if issues arise. | All Water System ROC General | 2025-11-06
ROC | November | Stouffville Water System - Sean from Town of Stouffville called to inform he will be flushing in Zone 2. Called Travis W and informed of the flushing. Travis agreed that duty should be activated to offset the flushing operations while STRS48 high lifts are OOS. Activated system duty. | All Water System ROC General | 2025-11-06
ROC | November | STPSMR - lee F on site for vibration testing on the pumps. Lee requested that pump 2 be deactivated and pump 3 be activated. Made necessary duty changes. Noted that the pump duty priority system is preventing duty assignment changes during pump operation. Contacted Jack P who stated that the pumps can be manipulated in manual mode to achieve the desired duty assignments. Made necessary changes. | All Water System ROC General | 2025-11-06
ROC | November | NMVCBP, Placed valve man/open at 40L/sec | All Water System ROC General | 2025-11-09
ROC | November | GRTPLL - Low lift total chlorine res fault alarm. Disregard as per shift report. | All Water System ROC General | 2025-11-09
ROC | November | QVETQS- Inlet Total CL2 HiHi Switch. Alex B and Ryan B working on it. Can disregard. | All Water System ROC General | 2025-11-05
ROC | November | HLW1- Benson S onsite for work orders. Chlorine scrubber and leak detection test, Chlorine and turbidity analyzer maintenance, chemical system inspection. | All Water System ROC General | 2025-11-06
ROC | November | Connor Smith signing in 2C Cloudy | All Water System ROC General | 2025-11-06
ROC | November | KSETDP - Inlet total chlorine hihi alarm. Checked site, tower is filling. With KASTP offline GWTP is pushing limited flow to system. Chlorination system activating is causing spikes of the inlet chlorine which is a disregard scenario on the shift report. Will monitor. | All Water System ROC General | 2025-11-06
ROC | November | Ethan U signing in Weather 7. | All Water System ROC General | 2025-11-07
ROC | November | MKPSSA, Placed pump 3 man/on to help drawdown MKRSEM | All Water System ROC General | 2025-11-09
ROC | November | STRS48 - Travis W. and Jack P. is on site for a cylinder change | All Water System ROC General | 2025-11-07
ROC | November | KSTP - Donald M. is on site completing a Chlorine Leak Detection Test. | All Water System ROC General | 2025-11-07
ROC | November | MAPS - Jordan B. called to inform that he will be closing the PD8 suction valve in preparation for the trial | All Water System ROC General | 2025-11-07
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-07
ROC | November | MAPS PD7- P1 disch valve failed to open and P1 uncommanded stop alarm came in. Reset alarms will continue to monitor | All Water System ROC General | 2025-11-07
ROC | November | MKRSMR - Mehdi called to inform that he will be running pump 10 to make sure valve is working and the valve will open and close based on the pump. Mehdi will call back to inform when work is complete | All Water System ROC General | 2025-11-07
ROC | November | YWS + NYWS NORMAL | All Water System ROC General | 2025-11-06
ROC | November | QVW12- Treated Combined Chlorine Lo Alarm. Duty deactivated recently, wells not running. Values recovered. Cleared alarm. | All Water System ROC General | 2025-11-06
ROC | November | YWS+NYWS normal | All Water System ROC General | 2025-11-07
ROC | November | STW12- Placed both back wells in auto as STETBR D1 stop as per interim | All Water System ROC General | 2025-11-08
ROC | November | SHTP- Well 2 uncommanded stop alarm came in. Reset alarm wells not being called for | All Water System ROC General | 2025-11-08
ROC | November | NMW12- Treated total Cl2 lo and combined Cl2 lo alarms came in. Wells not active no water directed to users | All Water System ROC General | 2025-11-08
ROC | November | BLW12, Generator Running Status Alarm, Checked Hydro One outage map and noticed nothing was reported, talked with Hydro One operator Denis and reported the issue to him, he will get an advisor to give the ROC a follow up call to confirm that the issue is either on our end or their end. 09:46, Notified Joe M that the generator is running and passed on all the info that hydro one gave the ROC. If they do not call back in another 30 minutes or so, Joe M would like to be called consult | All Water System ROC General | 2025-11-08
ROC | November | MKMCLA - PAC communication failure alarm, cleared in 15 minutes. Trends restored. | All Water System ROC General | 2025-11-06
ROC | November | YWS + NYWS NORMAL | All Water System ROC General | 2025-11-07
ROC | November | YWS + NYWS Normal NMETIB, Activated D1 to keep towers offset | All Water System ROC General | 2025-11-08
ROC | November | HLW2, Deactivated D1 due to a high pressure downstream hihi alarm happening at HLW2 | All Water System ROC General | 2025-11-08
ROC | November | GWTP - Stephen B. is on site and will be working on UV reactor 2 and requested to disregard all alarms until work is complete Stephen also informed that capital is on site looking into the generator. Requested to disregard all alarms | All Water System ROC General | 2025-11-07
ROC | November | NBW2- Chlorine System Not in Auto Interlock, CL2 Gas Control 1,2 Failed to Close. Joe W onsite. Well man/off. Alarms cleared upon acknowledging | All Water System ROC General | 2025-11-06
ROC | November | STPSMR - Jack P. called back to inform that there is an issue with pump 2 and is triggering a VFD fault. Jack P. will call on call Electrician | All Water System ROC General | 2025-11-07
ROC | November | Initiating Maple to Jefferson feed | All Water System ROC General | 2025-11-09
ROC | November | MKRSEM - Request (Fashaed) to run 2 pumps | All Water System ROC General | 2025-11-07
ROC | November | KSTKWP- Free Cl2 and combined Cl2 trends are sporadically dropping out and recovering. Notified Patrick F. will take a look on SCADA #consult 7:29- KSTKWP- Patrick F heading to site. Created CMU5 W11427983 #CMU5 | All Water System ROC General | 2025-11-07
ROC | November | Wrong entry book | All Water System ROC General | 2025-11-07
ROC | November | GWTP- ZW2 recovery exceeded SP. alarm cleared upon acknowledgement. Will notify Patrick F when done at KSTKWP 21:39- GWTP- Patrick F done on site at KSTKWP. Able to fix analyzer and clear alarms. Notified of ZW2 recovery exceeded SP alarm directed to disregard disregard #consult | All Water System ROC General | 2025-11-07
ROC | November | YWS+ NYWS Normal | All Water System ROC General | 2025-11-08
ROC | November | Carter Dunn Signing Out | All Water System ROC General | 2025-11-09
ROC | November | STW12 - Back to auto. STETBR duty just deactivated. | All Water System ROC General | 2025-11-06
ROC | November | MKRSEM - Called Toronto water ( Peter), requested stop pumps. | All Water System ROC General | 2025-11-07
ROC | November | GWTP- Patrick F called. UV2 is OOS. KSTP- High Lifts are man/off. Can place back into auto once settled water conduit fills. | All Water System ROC General | 2025-11-06
ROC | November | YWS + NYWS NORMAL | All Water System ROC General | 2025-11-07
ROC | November | MAPS PD8 - Sanitary Sump 1 Level HiHi multiple alarms, looks like LIT instrument failed. Cole W will check SCADA. # Consult 01:05 As per Cole W - disregard alarm for now. Operations will attend first thing in the morning. | All Water System ROC General | 2025-11-07
ROC | November | STW12 - STW12 effluent free chlorine residual low alarm, duty not active, no water directed to users. | All Water System ROC General | 2025-11-07
ROC | November | STW12 - CT not achieved alarm/wells1 and 2 pumps interlocked. Notified Patrick F. He will check first thing in the morning. Requested to activate STETTL Duty 1. # Consult | All Water System ROC General | 2025-11-07
ROC | November | Christian Van Beek signing in. Weather: -2C and snow. | All Water System ROC General | 2025-11-09
ROC | November | Reverting Maple to Jefferson feed. | All Water System ROC General | 2025-11-09
ROC | November | YWS + NYWS NORMAL | All Water System ROC General | 2025-11-07
ROC | November | STETBR - Free chlorine Low alarm. Duty active, ET filling. STW12 - Placed Pumps 1 and 2 man/on for STETBR fill cycle. | All Water System ROC General | 2025-11-07
ROC | November | NMETIB - Deactivate duty 1 NMVCBA - Revert setpoint back to 40L/s NMVCIB - Revert setpoint back to 80L/s | All Water System ROC General | 2025-11-07
ROC | November | VNETFD- Deactivated D1 at 73 to help tower cycle better | All Water System ROC General | 2025-11-07
ROC | November | HLW1 - Station turbidity hi, rotated silicate pump 1 to duty 1 | All Water System ROC General | 2025-11-07
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-08
ROC | November | NMTKKC, Header Total Cl2 hi Alarm, Tank is currently draining, Spike occurred right after pumps shut down, will continue to monitor the residuals at site, if they continue to increase, will activate the duty on site so no water is being directed to customers and will contact operator | All Water System ROC General | 2025-11-08
ROC | November | Christian Van Beek signing out. | All Water System ROC General | 2025-11-10
ROC | November | NMW12 - Treated Chlorine and combined chlorine Lo alarms came in. Wells are not active and water is not being directed to users | All Water System ROC General | 2025-11-10
ROC | November | STW3 - Patrick F. called to inform that STW3 is back up and running and the well will be kept man/on for the weekend | All Water System ROC General | 2025-11-07
ROC | November | YWS + NYWS NORMAL | All Water System ROC General | 2025-11-07
ROC | November | NMW15 - Treated total chlorine hi. Jason G signed in on site. Called, no response | All Water System ROC General | 2025-11-07
ROC | November | NMTKKC- Header Combined Chlorine HiHi Alarm came in. Interlocked chemical pumps. Alarm reset. Notified Joe D. He will contact On call Operator. Requested to place chemical pumps in manual if it comes in again. 15:00- Joe D spoke with Jerry Z who is monitoring. | All Water System ROC General | 2025-11-10
ROC | November | Carter Dunn Signing In, -2D/Snow | All Water System ROC General | 2025-11-10
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-11
ROC | November | NMETIB- Activated duty | All Water System ROC General | 2025-11-06
ROC | November | KSTKWP - Donald M onsite for chlorine leak detection | All Water System ROC General | 2025-11-07
ROC | November | AUW14, Cl2 Cylinder Change over, Increased Cl2 dosing setpoint from 121 to 123% to help with the dosing | All Water System ROC General | 2025-11-08
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-08
ROC | November | STW12, Placed well 2 man/on to help fill STETBR | All Water System ROC General | 2025-11-08
ROC | November | RHMCMD - Placed valve in manual and closed. | All Water System ROC General | 2025-11-10
ROC | November | SHTP - FIlter 2 turbidity hi alarm. Checked site, filter 1 is going through a backwash. Turbidity for filter 2 has dropped. Reset alarm. | All Water System ROC General | 2025-11-10
ROC | November | NMVCBA - Palced valve in auto mode. | All Water System ROC General | 2025-11-09
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-10
ROC | November | SHETCS - Hypo pump 1 uncommanded stop alarm. Checked site, chlorination system is active. Duty rotated to pump 2 which is operating. Reset alarm. | All Water System ROC General | 2025-11-10
ROC | November | MARS - Cell 1 High level alarm. Activated VNRSKS to drawdown MARS. AURSOH - Activated duty 1. | All Water System ROC General | 2025-11-10
ROC | November | Angelica Chepiga signing out | All Water System ROC General | 2025-11-06
ROC | November | MARS - High level, placed RHMCMD man/open and deactivated RHRSTR Duty 1. | All Water System ROC General | 2025-11-06
ROC | November | HLETYS - PAC Communication failure alarm, cleared right away. | All Water System ROC General | 2025-11-06
ROC | November | YWS + NYWS NORMAL | All Water System ROC General | 2025-11-06
ROC | November | GWTP - ZW4 recovery exceeded recovery SP. Checked site, train has entered a backwash sequence. The alarm status value returned to normal immediately. Cleared alarm. | All Water System ROC General | 2025-11-09
ROC | November | MARS - Cell 1 level hihi. Deactivated RHRSTR duty 1. | All Water System ROC General | 2025-11-10
ROC | November | AUPSRR - Post injection combine and total chlorine residual LoLo alarms. Reservoir filling. Chlorine cylinder 2 in empty. Free ammonia normal. Notified Jerry Z. He will check SCADA. # Consult. 00:24 Jerry Z will attend site. # CMU 5 W11421197 | All Water System ROC General | 2025-11-06
ROC | November | AUW14 - Ernie H on site to complete a generator load test but will not be transferring station power. | All Water System ROC General | 2025-11-06
ROC | November | MKRSMR - Jack P on site to complete work orders including analyzer maintenance, flood alarm test, hi/low level alarm test and JHSC checks. | All Water System ROC General | 2025-11-06
ROC | November | STPSMR - Jack P. called to inform that he is on site with Travis W. and will be replacing the chlorine cylinder for bank 1. Will call back when cylinder change is complete | All Water System ROC General | 2025-11-07
ROC | November | MARS, Notified Toronto operator Andrew to go back to normal flow | All Water System ROC General | 2025-11-10
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-11
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-11
ROC | November | NMTKKC - Redempto B. and Ricardo are on site for annual calibrations 13:38 - Redempto called back to inform that he and Rick are finished on site | All Water System ROC General | 2025-11-07
ROC | November | Carter Dunn Signing In, 0D/Snow | All Water System ROC General | 2025-11-09
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-07
ROC | November | AUETAD - Activated duty 1 to fill tower in preparation for the Maple to Jefferson feed. | All Water System ROC General | 2025-11-09
ROC | November | NMETIB- Deactivated duty NMVCBA- Changed from 80L/s to 40L/s NMVCIB- Changed from 40L/s to 80L/s | All Water System ROC General | 2025-11-05
ROC | November | NMVCBA - back to auto. | All Water System ROC General | 2025-11-06
ROC | November | NMVCBA - Upstream pressure OOR alarms. Instrument issue. Will notify area. | All Water System ROC General | 2025-11-06
ROC | November | YWS + NYWS NORMAL | All Water System ROC General | 2025-11-06
ROC | November | ARPS- Total ammonia fault alarm. value back to normal, able to reset after 3 mins. | All Water System ROC General | 2025-11-06
ROC | November | STETTL- Tower level lo alarm came in. Tower deep cycling. Will clear during fill cycle | All Water System ROC General | 2025-11-08
ROC | November | RHRSTR, Deactivated D1 RHMCMD, Opened valve to 100% to have water flow from MARS to RHRSTR to keep ARPS pump running | All Water System ROC General | 2025-11-11
ROC | November | MKRSEM - Reservoir Level Lo alarm came in. Called Toronto Water (Mehdi) and requested two pumps on | All Water System ROC General | 2025-11-10
ROC | November | *WRONG BOOK ENTRY* | All Water System ROC General | 2025-11-10
ROC | November | RHMCMD, Placed valve man/closed | All Water System ROC General | 2025-11-10
ROC | November | YWS + NYWS Normal MKPSSA - Deactivated pump 3. | All Water System ROC General | 2025-11-09
ROC | November | YWS + NYWS NORMAL | All Water System ROC General | 2025-11-06
ROC | November | YWS + NYWS Normal GWTP, Clearwell 1 Cl2 hi Alarm, as per shift report, directed to disregard GWTP, Raw Water Total Cl2 Res hihi, As per shift report directed to disregard as a abnormal spike occurred. | All Water System ROC General | 2025-11-08
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-10
ROC | November | MKRSEM - Free chlorine residual fault alarm. Checked site, current reading and trending show no issues with the free chlorine. Contacted Jack P who is on site and triggered the alarm during the sample collection. Alarm cleared, jack stated the alarm can be disregarded until he is off site. | All Water System ROC General | 2025-11-05
ROC | November | MAPS PD8 - Sanitary Sump 1 Level HiHi alarm, will send email to Cole W. | All Water System ROC General | 2025-11-06
ROC | November | NMW136- Combine and Treated total chlorine residual Low alarms. Duty not active, quick dip, value recovered, cleared alarms. | All Water System ROC General | 2025-11-07
ROC | November | STETBR - Tower Level Lo alarm came in. Placed STW2 man/on as per interim | All Water System ROC General | 2025-11-10
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-09
ROC | November | STPSMR - Eric S. is on site completing a work order on AIT7. | All Water System ROC General | 2025-11-07
ROC | November | NMTKKS - Joe D onsite aware of header total chlorine. Monitoring combined chlorine as well | All Water System ROC General | 2025-11-07
ROC | November | HLETYS- Ammonia Pumps 1,2 Failed to Start. Notified Benson S. He will look into it. | All Water System ROC General | 2025-11-06
ROC | November | Gluzen Ramos Ong signing in BLW3 - Phil D. finished on site, in auto | All Water System ROC General | 2025-11-10
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-09
ROC | November | JFRS, Activated D2 as only 1 pump was pumping to the res, NRETCR just started filling which would cause JFRS to start to short cycle | All Water System ROC General | 2025-11-09
ROC | November | NMETIB, Deactivated D1 so towers can be offset | All Water System ROC General | 2025-11-09
ROC | November | SUETDR- Red B finished with LIT calibration. Placed PRV1 and PRV2 back into auto. | All Water System ROC General | 2025-11-10
ROC | November | Christian Van Beek signing in. | All Water System ROC General | 2025-11-06
ROC | November | BVPS - Lee F on site for vibration testing. Lee will be testing Pumps 1 and 3 and then pumps 2 and 4. Placed all pumps in manual mode, activated pump1 and then pump 3 after a delay to avoid pressure issues. Will complete the same strategy for pump 2 and 4 when needed. | All Water System ROC General | 2025-11-06
ROC | November | AUPSWS- Kyle R called. Taking pump 5 out of service for maintenance. Pump 4 running in duty 1. | All Water System ROC General | 2025-11-06
ROC | November | NMTKKC- Red B onsite troubleshooting Header Total Cl analyzer 14:50- Leaving site. | All Water System ROC General | 2025-11-06
ROC | November | STPS48- Travis W working on chlorine and turbidity analyzer. | All Water System ROC General | 2025-11-06
ROC | November | QVW34 - Lee F. on site working on chemical injection points, placed wells man/off. He informed spoke to Alex Bell (OIT) | All Water System ROC General | 2025-11-10
ROC | November | STW56 - Travis W on site to complete work orders including JHSC checks, generator test, analyzer maintenance and hi/low alarm tests. | All Water System ROC General | 2025-11-06
ROC | November | KSETWB - Patrick F on site to complete work orders including analyzer maintenance, JHSC checks, valve exercising and chlorine scrubber inspection. | All Water System ROC General | 2025-11-06
ROC | November | RHMCMD- Placed valve back into auto. | All Water System ROC General | 2025-11-06
ROC | November | YWS + NYWS Normal NMW12, Effluent Free Cl2 hi alarm, Adjusted Cl2 dosing factor from75% to 73%, will continue to monitor site | All Water System ROC General | 2025-11-09
ROC | November | QVW34 - Jason G, Alex B and Jason Moore on site to conduct a step test. Jason will be manipulating pumps throughout the test. | All Water System ROC General | 2025-11-06
ROC | November | AUPSWS - Kyle R finished working on pump 5 and leaving site. | All Water System ROC General | 2025-11-06
ROC | November | YWS + NYWS normal | All Water System ROC General | 2025-11-09
ROC | November | KSTP- Pre CL2 free residual hihi switch alarm came in. Checked trends once PACL pumps shutdown the free residual trend spiked up and flatlined but recovered after 5 mins. Will email east water team about outstanding alarm and continue to monitor. | All Water System ROC General | 2025-11-07
ROC | November | HLW2/HLETYS- PAC comm fails on site cleared upon acknowledgement. Trends okay YWS+NYWS normal | All Water System ROC General | 2025-11-08
ROC | November | YWS+NYWS normal | All Water System ROC General | 2025-11-08
ROC | November | MARS, Cell 1 North Lvl Lo alarm, 3 pumps running at ARPS/AURSBS is taking water from MARS, Res is flat lining, contacted Toronto operator Peter to increase the flow just to take a safety measure just incase starts to drop. Once AURSBS is done fill, will contact Peter to go back to normal flow | All Water System ROC General | 2025-11-08
ROC | November | NMVCBP - Ricardo L. and Redempto B. are on site replacing the pressure transmitter 10:28 - Redempto B. called to inform that he and Ricardo are finished on site | All Water System ROC General | 2025-11-07
ROC | November | Carter Dunn Signing In, 5D/Clear | All Water System ROC General | 2025-11-08
ROC | November | RHMCMD, Placed valve back to auto | All Water System ROC General | 2025-11-08
ROC | November | GWTP - Stephen B finished at site. UV2 off for the weekend KSETDP - Stephen B heading to site | All Water System ROC General | 2025-11-07
ROC | November | NMTKKC- Red B and Ric L onsite for annual calibrations. | All Water System ROC General | 2025-11-06
ROC | November | GWTP - Raw water total chlorine residual HiHi- quick spike, disregard as per SCADA review. | All Water System ROC General | 2025-11-06
ROC | November | NMTKKC- Red B onsite for calibrations. Placed Newmarket wells man/off for LIT calibration. 13:37- Red B finished. Placed wells back into auto. | All Water System ROC General | 2025-11-05
ROC | November | KLPSWL- Finished onsite. | All Water System ROC General | 2025-11-06
ROC | November | NMETIB- Activated duty. | All Water System ROC General | 2025-11-10
ROC | November | Angelica Chepiga signing in,weather +5C | All Water System ROC General | 2025-11-06
ROC | November | YWS + NYWS Normal MKRSEM, Notified Toronto operator peter to start filling the res | All Water System ROC General | 2025-11-08
ROC | November | NMVCBA - Upstream Pressure OOR and HiHi alarms came back in. Checked site and noticed that pressure levels have been spiking in the past day. Known issue and informed Eric S. who will take a look 11:22 - Eric called back to inform that he is on site 12:04 - Eric called back to inform that he is finished on site and was unable to diagnose an issue with the new PIT. Eric has opened a work order and will continue to monitor over the next couple of days | All Water System ROC General | 2025-11-10
ROC | November | NBW2 - Eric S. finished on site | All Water System ROC General | 2025-11-10
ROC | November | STETTL - Outlet free chlorine Low alarm, Duty is active, ET filling. | All Water System ROC General | 2025-11-07
ROC | November | AUPSRR - Chemscan OFFLINE Status alarm came in. Called Will M. but no answer. Will try again | All Water System ROC General | 2025-11-10
ROC | November | YWS + NYWS Normal Connor Smith signing out | All Water System ROC General | 2025-11-10
ROC | November | ARPS- Cristina S called and informed that valving is done and requested to call Peel to have them start up 1 transfer pump in pressure mode. Notified Peel. 11:42- Pump 5 started up in pressure mode. KLPS27- Enabled PD6 High Pressure Mode. Interim Procedure. | All Water System ROC General | 2025-11-10
ROC | November | NBW2 - Turbidity High High Switch alarm came in. Checked site. Well was running but interlocked on the high high turbidity. Called Cole W. who will take a look | All Water System ROC General | 2025-11-07
ROC | November | BVPS - Lee F finished his vibration testing on the pumps. Activated duty 1 and placed pumps in auto to maintain flow out of the pumping station. | All Water System ROC General | 2025-11-06
ROC | November | STW3 - Joe M & Travis W onsite to put well in production, running local to waste | All Water System ROC General | 2025-11-07
ROC | November | NBW37, Influent Free Cl2 lolo alarm, well locked out, once residual comes back up, will place well back online | All Water System ROC General | 2025-11-08
ROC | November | Angelica Chepiga signing out | All Water System ROC General | 2025-11-07
ROC | November | GWTP- Stephen B called to inform they will be testing Low Lift Pump 4. Disregard related alarms. | All Water System ROC General | 2025-11-10
ROC | November | GWTP - Chris S. called to inform that he will be commissioning low lift pump 4 | All Water System ROC General | 2025-11-10
ROC | November | STRS48 - Travis W called to inform the turbidity analyzer needs work from instrumentation and the high lift pumps will remain off until they complete their work. STETTL - Deactivated duty 1 after consulting with Travis W. STPSMR - Reverted pump changes made earlier for Lee F vibration testing. | All Water System ROC General | 2025-11-06
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-09
ROC | November | SHETCS - hypo pumps 1 and 2 failed to start. ET filling. Notified Dave T. and Cole W., Cole will attend CMU: W11432247 | All Water System ROC General | 2025-11-10
ROC | November | KSTP- Raw Water pH HiHi/OOR Alarms. Called Donald M. No answer. Called Patrick F. He will look into it. 15:40- Patrick F called. Can disregard this alarm for the night. | All Water System ROC General | 2025-11-10
ROC | November | GWTP - Stephen B. called back to inform that UV Reactor 2 will be off for the weekend due to a fault. Stephen informed that the UPS will be fixed on Monday | All Water System ROC General | 2025-11-07
ROC | November | Sharon Valve, distribution hihi pressure alarm, placed valve man/closed | All Water System ROC General | 2025-11-09
ROC | November | QVW34- Treated Total chlorine low alarm. Duty not active, no water directed to users. Value recovered, cleared alarm. | All Water System ROC General | 2025-11-06
ROC | November | SHTP - Reservoir Total Chlorine Lo alarm came in. Checked site. Noticed that the level dropped but is slowly rising. Will monitor | All Water System ROC General | 2025-11-10
ROC | November | MKRSEM - Historian Heartbeat alarm came in. Checked site. Called Artour L. who will take a look. CMU5 Created W11432273 #CONSULT #CMU5 | All Water System ROC General | 2025-11-10
ROC | November | GWTP- Raw Water Total Chlorine Res HiHi Alarm. Disregard as per SCADA Report. | All Water System ROC General | 2025-11-10
ROC | November | Adeela Khan signing out | All Water System ROC General | 2025-11-10
ROC | November | AURSBS - Activated duty 1 to help lower levels at MARS | All Water System ROC General | 2025-11-10
ROC | November | Gluzen Ramos Ong signing out | All Water System ROC General | 2025-11-10
ROC | November | KSTP - Security system intrusion alarm. FMC will notify corp. security. | All Water System ROC General | 2025-11-06
ROC | November | RHPSWA- Jordan B onsite testing flood alarm and running pumps. | All Water System ROC General | 2025-11-06
ROC | November | AUW14, Treated Free Cl2 hihi alarm, rotated Ammonia pumps so ammonia pump 1 is in D1. Will continue to monitor site till residual drops | All Water System ROC General | 2025-11-10
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-10
ROC | November | NMETIB, Activated D1 to offset towers | All Water System ROC General | 2025-11-10
ROC | November | Ethan Ullalkar signing out. | All Water System ROC General | 2025-11-07
ROC | November | AUPSRR- RSR Outlet Comb Chlorine Lo, RSR Outlet Tot Chlorine LoLo. Called William M. He is onsite working on it. | All Water System ROC General | 2025-11-10
ROC | November | KCETDS, Activated D1 | All Water System ROC General | 2025-11-11
ROC | November | GWTP- Artour L and Ian W onsite replacing UPS batteries. | All Water System ROC General | 2025-11-10
ROC | November | NMTKBS - Ryan B. is on site completing the hi/low tank alarms | All Water System ROC General | 2025-11-10
ROC | November | ARPS- Cristina S called. Requested to call Peel to have place all pumps man/off. Notified Bineesh from Peel and then informed Cristina S. Interim Procedure. | All Water System ROC General | 2025-11-10
ROC | November | AUPSRR- William M and Ben H working on Metro Valve. | All Water System ROC General | 2025-11-10
ROC | November | HLETYS- Ammonia Pump 1, 2 Failed to start Alarm. HLV2 is running in schedule mode and filling tower. Placed chemical pumps man off and will place back in auto when schedule mode ends. 17:47- Cleared alarms and placed chemical pumps back into auto. | All Water System ROC General | 2025-11-10
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-10
ROC | November | SHETCS - Cole W. called to inform that he is finished on site and directed to place the hypo pumps man/off if they continue to give issues through the night. 17:21 - Both hypo pumps had an uncommanded stop. Placed both pumps man/off as per Cole W. | All Water System ROC General | 2025-11-10
ROC | November | MARS - Called Toronto Water (Mehdi) and requested max flow in preparation for ARPS pressure loop scenario. | All Water System ROC General | 2025-11-10
ROC | November | STW12 - Generator Running Alarm came in. Checked site. Transfer switch is still connected to hydro power and generator is running in local. Called Travis W. who informed there were contractors on site for maintenance on the generator. Called Tyler Z. who informed Total Power are on site for fluid and oil change. Tyler will let Total Power know to place the generator back to auto once finished | All Water System ROC General | 2025-11-10
ROC | November | NBW2 - Eric S. working on effluent cl analyzer | All Water System ROC General | 2025-11-10
ROC | November | Adeela Khan signing in | All Water System ROC General | 2025-11-10
ROC | November | NBET- Joe M working in Nobleton today. Requested to activated duty. | All Water System ROC General | 2025-11-10
ROC | November | HLW2 VC - Downstream Pressure HiHi Alarm. Sharon Valve started up in schedule mode and interlocked valve. Will reset once schedule mode ends. 09:39- Reset alarm | All Water System ROC General | 2025-11-10
ROC | November | MARS- Lvl Lo Alarm RHRSTR- Activated duty. | All Water System ROC General | 2025-11-10
ROC | November | GWTP - Stephen B. is on site working on the UV System | All Water System ROC General | 2025-11-10
ROC | November | BLW3- Phil D onsite cleaning turbidity analyzer | All Water System ROC General | 2025-11-10
ROC | November | MKRSEM- Artour L cleared Historian Heartbeat Alarm. | All Water System ROC General | 2025-11-10
ROC | November | MKRSEM, Notified Toronto operator Andrew to stop pumping to the res | All Water System ROC General | 2025-11-11
ROC | November | SUETDR - Ricardo L. and Redempto B. are on site for annual calibrations 10:20 - Redempto B. called to inform that he wants to calibrate the LIT at SUETDR and wanted to know if it was a controlling tower. Spoke to Dan Z. who informed the discharge PRV's can be placed in manual for the calibrations. Placed both PRV's in manual until calibration is complete. | All Water System ROC General | 2025-11-10
ROC | November | QVW34- Lee F requested wells back into auto. He is leaving site. NMETIB- Deactivated duty. | All Water System ROC General | 2025-11-10
ROC | November | TMC317, Notified Peter from Toronto to go back to normal operation | All Water System ROC General | 2025-11-08
ROC | November | Adam Button signing in 3C Raining | All Water System ROC General | 2025-11-07
ROC | November | STW12/3, Placed wells 2/3 back to auto | All Water System ROC General | 2025-11-11
ROC | November | YWS+NYWS normal | All Water System ROC General | 2025-11-08
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-10
ROC | November | RHRSTR- Changed Duty 1 Start/Stop from 65/85% to 75/90%. Changed Duty 2 Stop from 55/75% to 65/75%. MARS- Attempted to change LoLo Level Alarm from 60 to 65% however unable due to this being a HMA. Interim Procedure | All Water System ROC General | 2025-11-10
ROC | November | NMVCBA - Upstream pressure OOR alarm, back to normal in one reading. Alarm cleared. | All Water System ROC General | 2025-11-06
ROC | November | HLW2 VC- Downstream Pressure HiHi Alarm. Sharon Valve opened in schedule mode and interlocked HLW2 VC. Will reset once schedule mode ends. 17:46-Cleared alarm | All Water System ROC General | 2025-11-05
ROC | November | STETTL - Activated Duty 1 | All Water System ROC General | 2025-11-06
ROC | November | NMTKKC- Red B finished onsite. | All Water System ROC General | 2025-11-05
ROC | November | STETBR - Free chlorine low alarm, quick drop, alarm cleared, will monitor. | All Water System ROC General | 2025-11-05
ROC | November | HLW1 to HLETYS Communication failure alarm/cleared right away. | All Water System ROC General | 2025-11-06
ROC | November | STETBR - Free chlorine residual low alarm, ET is filling, will monitor. | All Water System ROC General | 2025-11-06
ROC | November | QVW12- Joe D requested wells man/on (already running) and deactivated NMETHW duty for sampling. | All Water System ROC General | 2025-11-05
ROC | November | AUW14- Jerry Z onsite testing chlorine leak and cleaning chlorine analyzer | All Water System ROC General | 2025-11-05
ROC | November | Christian Van Beek signing out. | All Water System ROC General | 2025-11-05
ROC | November | Angelica Chepiga signing in, weather +6C | All Water System ROC General | 2025-11-05
ROC | November | NBET27- Joe W called. Tower is back online. He is also working on chlorine analyzer | All Water System ROC General | 2025-11-05
ROC | November | YWS + NYWS NORMAL | All Water System ROC General | 2025-11-05
ROC | November | AUW57- Influent Free Chlorine HiHi. Value recovered. Cleared alarm. | All Water System ROC General | 2025-11-05
ROC | November | STETBR - Free chlorine low alarm. Activated Duty 1. | All Water System ROC General | 2025-11-05
ROC | November | STETTL - Tower level Low alarm, area deep cycling ET to 45%. | All Water System ROC General | 2025-11-05
ROC | November | STETTL - Tower level LoLo alarm. Duty just activated. Will monitor. | All Water System ROC General | 2025-11-05
ROC | November | QVW12- Treated Total and Combined Chlorine Lo Alarms. Duty deactivated recently, wells not running. Values recovered. Cleared alarms. | All Water System ROC General | 2025-11-06
ROC | November | ANW23 - Benson& Jackie S onsite running generator, cleaning chlorine & turbidity analyzer as well as health and safety | All Water System ROC General | 2025-11-04
ROC | November | NMW136 - Combined Chlorine Lo alarm came in. Checked site. Well 16 is running and duty is almost at duty stop. Level took a dip but came back to optimal range within 5 mins and alarms cleared | All Water System ROC General | 2025-11-04
ROC | November | STETBR - Free Chlorine Lo alarm came in. Checked site. Noticed levels went back up. Alarms have been cleared and will continue to monitor | All Water System ROC General | 2025-11-04
ROC | November | AURSBS - Activated duty 1 | All Water System ROC General | 2025-11-05
ROC | November | QVW12- Influent free Cl2 hihi alarm came in recovered within 1 min of alarm coming in. Cleared alarm will continue to monitor | All Water System ROC General | 2025-11-02
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-02
ROC | November | YWS + NYWS normal | All Water System ROC General | 2025-11-02
ROC | November | MKPSSA, Placed pumps 2/3 man/off to help MKRSEM recover STRS48, Influent Free Cl2 hihi alarm, Pumps are pumping to drain atm, will continue to monitor, if residual doesn't drop on analyzer, will rotate pumps | All Water System ROC General | 2025-11-02
ROC | November | Carter Dunn Signing Out | All Water System ROC General | 2025-11-03
ROC | November | Ethan U signing in | All Water System ROC General | 2025-11-03
ROC | November | MKRSEM - Reservoir level lo, confirmed with East team as well as Stephen B that we can continue draining as MKPSSA with 2 pumps running. Okay going to 1.25m as per Stephen B | All Water System ROC General | 2025-11-03
ROC | November | STW12 - Stephen B requested Man/start well 1 pump to support STETTL fill cycle. | All Water System ROC General | 2025-11-03
ROC | November | STETBR- Free Cl2 res slowly dropping. Notified Stephen B. Directed to open FVC at STPSTL and place pumps in manual. STETTL- DeactivatedD1 STW12- Placed P2 in man/on (already running) made changes above to allow faster cycle of STETBR #consult | All Water System ROC General | 2025-11-02
ROC | November | QVW34- Influent free Cl2 hi alarm came in. Continued to monitor recovered after 3 mins alarm cleared | All Water System ROC General | 2025-11-02
ROC | November | MKRSEM - Called Toronto Water (Andrew) and requested two pumps on to help fill reservoir | All Water System ROC General | 2025-11-01
ROC | November | STW12 - Kingsley M restarting OIT, man/stop pumps 1 &2. Disregard Historian Heartbeat alarm. | All Water System ROC General | 2025-11-03
ROC | November | HLW2- Downstream Pressure HiHi Alarm. Sharon valve started in schedule mode / interlocked HLW2 VC. Will reset alarm once schedule mode is completed. | All Water System ROC General | 2025-11-03
ROC | November | AUW57 - Influent free chlorine lolo on startup, reading bounced back quickly and able to reset | All Water System ROC General | 2025-11-03
ROC | November | AUETAD- total and combined residuals much lower than expected with drastic drop around 08:30. Notified Joe D of issue and will check SCADA #consult | All Water System ROC General | 2025-11-03
ROC | November | SHTP- Power loss on site. KMNO P2 leakage and speed OOR, Raw water pumps OOS alarms came in. Generator did not start up but plant went back on utility. Notified Dave T will check SCADA SHETCS- Power loss on site. Able to clear alarms site okay HLW2- Downstream pressure hihi alarm came in as Sharon valve opened able to clear alarm as pressure stabilized 9:27-SHTP- Dave T will attend site for KMNO P2 alarms. Created CMU5 W11407709 #consult | All Water System ROC General | 2025-11-01
ROC | November | SHTP- Filter 1 Post rinse NIT hi alarm came in. Reset as per shift report 9:48- SHTP- Filter 2 Post rinse NIT hi alarm came in. Reset as per shift report | All Water System ROC General | 2025-11-01
ROC | November | GWTP - Stephen B called, disconnecting power for Low Lift work. | All Water System ROC General | 2025-11-03
ROC | November | HLETYS- Post injection total and combined CL2 lo alarms came in due to fluctuating flow going into tower. Will continue to monitor. AUETAD- Joe D notified ROC there is an issue with analyzer but unless the readings set off alarms Central water team will take a look and the analyzer is okay for the night | All Water System ROC General | 2025-11-03
ROC | November | STETBR- Deactivated D1 at 61% to help fill STETTL | All Water System ROC General | 2025-11-03
ROC | November | STETBR- Free CL2 lo alarm came in. Will continue to monitor. | All Water System ROC General | 2025-11-03
ROC | November | MARS- Called Metro and spoke with Peter to go back to normal flow | All Water System ROC General | 2025-11-03
ROC | November | MKRSEM- reservoir level lo alarm came in. Called Metro spoke with Brett to start two pumps to fill reservoir. SHTP- Filter 2/3 turbidity alarms came in as filter 1 came out of backwash. reset as per shift report | All Water System ROC General | 2025-11-02
ROC | November | MKETFA - Free chlorine hihi, informed Phil D of situation, will take a look. | All Water System ROC General | 2025-11-03
ROC | November | YWS + NYWS NORMAL | All Water System ROC General | 2025-11-03
ROC | November | VNRSKS- Activated D1 | All Water System ROC General | 2025-11-04
ROC | November | AURSBS - Post-inj free chlorine hi. Followed up with Joe D. Is monitoring and will attend site if next few readings don't drop | All Water System ROC General | 2025-11-04
ROC | November | NMVCBA- Placed back into atuo NMETHW- Deactivated duty. | All Water System ROC General | 2025-11-04
ROC | November | MARS- Called Metro spoke to Peter to increase flow to reservoir | All Water System ROC General | 2025-11-03
ROC | November | VNETFD- Deactivated D1 to help tower cycle better | All Water System ROC General | 2025-11-03
ROC | November | NMW15-Treated total Cl2 hi alarm came in. Checked trends well started up with elevated influent Cl2 residuals and has adjusted down accordingly. Will monitor for change both target influent and effluent are within range | All Water System ROC General | 2025-11-03
ROC | November | MAPS - Start Maple to JFRS feed as requested by Ben H | All Water System ROC General | 2025-11-04
ROC | November | MKPSMR - Dwayne L informed all valve work is complete and ready to revert system to have Toronto pumps back in auto. Informed TO (Zhoran) put pumps back in auto and changed duty start/stop to 2.5-4.5m RHPSPA - Man/stop pump 1. Deactivate duty 1. Place pumps 1-4 back in auto RHVCEM - Close from 50% back to 15% | All Water System ROC General | 2025-11-04
ROC | November | Nobleton Water System- Chris S doing some PCS Communication work. Requested wells off. Notified Joe W and deactivated duty. | All Water System ROC General | 2025-11-04
ROC | November | YWS + NYWS Normal Connor Smith signing out | All Water System ROC General | 2025-11-04
ROC | November | KSTP - Settled Water Turbidity Fault alarm came in. Checked site. Levels have gone back to optimal range within 2 mins and trending is okay. | All Water System ROC General | 2025-11-04
ROC | November | STW12 - Placed STW1 back to auto | All Water System ROC General | 2025-11-01
ROC | November | BVPS - Deactivated duty 1 RHMCMD - Placed valve man/closed | All Water System ROC General | 2025-11-05
ROC | November | NMW15 - Treated Total Chlorine Hi alarm came in. Checked site. Well has been running for more than an hour. Total chlorine level is just above the hi level. Will monitor 19:02 - After 10 mins, total chlorine levels have come back to optimal range and alarms have cleared 19:15 - Alarm came back in. Noticed influent levels were also higher than the target but not high enough to trigger an alarm. Placed the manual dosage setpoint from 49% to 44%. Will continue to monitor 19:25 - Treated chlorine levels were still elevated after 10 mins. Influent levels were also coming down. Called Joe D. who will take a look 19:33 - levels are back to optimal range and alarm has cleared 20:05 - Joe called back to inform that he has been monitoring levels, and everything seems to be back to optimal range. Joe requested a call back in case total chlorine levels rise again 21:19 - Treated free chlorine hi alarm came in again. Duty is no longer active and well is still running in schedule mode. Called Joe D. who directed to place well man/off for the night and will place it back to auto in the morning. Joe did inform that well can be utilized if needed through the night. Joe will address the issue to the team on Monday. #CONSULT | All Water System ROC General | 2025-11-01
ROC | November | SHTP - Filter 2 Turbidity Hi alarm came in. Checked site. Called Cole W. who directed to act/reset #CONSULT | All Water System ROC General | 2025-11-04
ROC | November | AURSBS- Eric S onsite calibrating Chlorine Leak Detection. | All Water System ROC General | 2025-11-04
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-05
ROC | November | MKVCSA - Chris S working on site. Will receive communication failure alarm. 14:06 Chris S finished on site. | All Water System ROC General | 2025-11-03
ROC | November | QVW12- Combined and treated free Cl2 hihi alarm came in. Wells not active no water directed to users will clear alarm when residuals recover | All Water System ROC General | 2025-11-03
ROC | November | MAPS PD7- Placed P2-4 in auto | All Water System ROC General | 2025-11-04
ROC | November | STRS48 - Influent Free Chlorine HiHi alarm came in. Checked site. Level came back down within 10 mins and alarms have cleared | All Water System ROC General | 2025-11-01
ROC | November | QVW12 - Joe D. called back to inform that he has placed chlorine booster pump back to auto and influent free chlorine levels have been steady. Joe directed to place wells man/off if influent free chlorine issues persist. Joe has placed QVW4 man/on and directed to place the well back to auto once duty deactivates. 04:00 - Duty deactivated and placed QVW4 back to auto | All Water System ROC General | 2025-11-02
ROC | November | NBET27 - Cole W called, area isolating ET today until tomorrow for underground valve installation. | All Water System ROC General | 2025-11-03
ROC | November | YWS + NYWS Normal Ethan Ullalkar signing out. | All Water System ROC General | 2025-11-04
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-04
ROC | November | MKMCLA - Chris S switching communication nod, will receive communication failure alarm, disregard for the duration of the work. | All Water System ROC General | 2025-11-03
ROC | November | NMW136- Treated total and combined Cl2 lo alarm came in. Quick dip in analyzer and recovered after 3 mins cleared alarm | All Water System ROC General | 2025-11-04
ROC | November | SHTP- Filter 1 Post rinse NIT hi alarm came in again. notified Dave T directed to start backwash on filter 1 RHMCMD- Placed in auto 10:15- SHTP- Filter 2 Post rinse NIT hi alarm came in. Notified Dave T will check on site | All Water System ROC General | 2025-11-01
ROC | November | YWS+NYWS normal Adam Button signing out | All Water System ROC General | 2025-11-01
ROC | November | KSTP - Stephen B. called to inform that he is finished on site and the fluoride analyzer is functioning. STW12 - Spoke to Stephen B. who directed to place both wells man/on while zone 2 duty is active. Once it deactivates, Stephen directed to place both wells back to auto. 01:42 - Duty has deactivated and placed both wells to auto as per Stephen b. STETTL - Tower Level Lo and LoLo alarms. Spoke to Stephen B. who informed these alarms are triggered due to deep cycle the tower. | All Water System ROC General | 2025-11-01
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-01
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-01
ROC | November | VNRSKS- Deactivated D1 at 81% | All Water System ROC General | 2025-11-02
ROC | November | ARPS- ROYKS- ROPKS comm failure alarm came in able to reset trends okay YWS+NYWS normal | All Water System ROC General | 2025-11-02
ROC | November | STRS48 - Influent Free chlorine HiHi alarm. Travis W on site, adjusted chlorine dosage. Alarm should clear soon. | All Water System ROC General | 2025-11-03
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-03
ROC | November | VNRSKS - Activated duty 1 | All Water System ROC General | 2025-11-05
ROC | November | STETBR - West from Town of Stouffville flushing in zone 1. Notified Travis W. | All Water System ROC General | 2025-11-03
ROC | November | NBW3- Station turbididty fault came in again well not active trends okay cleared alarm. Emailed West Water OPs about reoocuring alarms | All Water System ROC General | 2025-11-04
ROC | November | MMW1- Rick L and Red B working on well 9. | All Water System ROC General | 2025-11-03
ROC | November | MMW9 - Rick L & Red B finished at site | All Water System ROC General | 2025-11-03
ROC | November | MKMCEM - Gary P onsite, disregard flood alarm | All Water System ROC General | 2025-11-03
ROC | November | STETTL- Activated D1 MKPSSA- Activated D1 and placed P3 in auto | All Water System ROC General | 2025-11-04
ROC | November | AURSBS- Ammonia Containment Flood Alarm. Ben H and William M onsite for work orders including analyzer maintenance. | All Water System ROC General | 2025-11-04
ROC | November | STW3 - Red B finished on site. | All Water System ROC General | 2025-11-03
ROC | November | NMW15 - Jason G onsite testing chlorine leak | All Water System ROC General | 2025-11-04
ROC | November | NBW3- Station turbidity fault alarm came in. Trends look okay able to reset alarm | All Water System ROC General | 2025-11-02
ROC | November | KSTKWP- Donald M finished onsite. | All Water System ROC General | 2025-11-04
ROC | November | YWS+NYWS normal Adam Button signing out | All Water System ROC General | 2025-11-02
ROC | November | HLW1 - Red B & Rick L finished at site | All Water System ROC General | 2025-11-04
ROC | November | Adam Button signing in 2 Raining | All Water System ROC General | 2025-11-01
ROC | November | TPTH1 - Reverse flow OOR and Flowmeter fault alarm came in. Checked site. Noticed that levels were moving from York Region towards Toronto at a high flow rate. Called Toronto Water (Andrew) who informed he was trying to move water from district 5 towards bayview. Andrew informed levels are in good shape and will be closing the valve shortly 03:05 - Water is no longer flowing in reverse flow and alarms have cleared | All Water System ROC General | 2025-11-01
ROC | November | BVPS - Discharge Free Chlorine Hi alarm came in. Checked site. Pumps are running. Noticed free chlorine levels are high and rising. Will monitor 04:30 - Level has been consistent at the high level of 0.20 mg/L. Called Toronto Water (Andrew) who confirmed their total chlorine analyzer at their Bayview reservoir is within range of BVPS's Total Chlorine level. Will continue to monitor any changes | All Water System ROC General | 2025-11-01
ROC | November | Adeela Khan signing out | All Water System ROC General | 2025-11-01
ROC | November | BVPS- Stephen B done on site and heading to KSTP. Created CMU5 W11407892 #CMU5 | All Water System ROC General | 2025-11-01
ROC | November | KSTP, Filter 1 Backwash is OOS Alarm, Plant is currently offline, Backwash tank is currently filled with transfer pump 1 active, once backwash tank is drained, alarm will clear. Will continue to monitor site. | All Water System ROC General | 2025-11-03
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-01
ROC | November | VNRSKS- Activated D1 | All Water System ROC General | 2025-11-01
ROC | November | QVW34- Treated total Cl2 hi alarm cleared after 5 mins | All Water System ROC General | 2025-11-02
ROC | November | QVW12- Influent free Cl2 lo alarm came in. Looks like cylinders changing over as cylinder 2 is close to being empty was able to clear alarm as residual improved within 3 mins. Will continue to monitor | All Water System ROC General | 2025-11-01
ROC | November | STETTL- Tower level lo alarm came in. Tower deep cycling. D1 ill activated in 3 %. Will clear alarm when starts to fill | All Water System ROC General | 2025-11-01
ROC | November | STETBR, Deactivated D1, Stephen B called back saying to deactivate the duty to help zone 2 tower | All Water System ROC General | 2025-11-02
ROC | November | QVW12 - Influent Free Chlorine Lo alarm came in. Checked site. Wells have been running for over an hour. Prior issues with the influent levels today. Influent levels kept fluctuating NOW but did not hit the LoLo. Called Joe D. who will take a look #CONSULT | All Water System ROC General | 2025-11-02
ROC | November | SHTP - FILT 1 Turbidity Hi alarm came in. Checked site. Ack/reset as per shift report | All Water System ROC General | 2025-11-02
ROC | November | AURSBS - Activated duty to help lower levels at MARS | All Water System ROC General | 2025-11-02
ROC | November | QVW12, Treated Free Cl2 hihi/Combined Cl2 lo, Wells recently stopped. Trends shows that after wells turn off, the residual has a spike/dip. usually recovers within the hour from trending, will continue to monitor until the residuals recover | All Water System ROC General | 2025-11-02
ROC | November | HLETYS - Pre-Injection Combined Chlorine Lo alarm came in. Checked site. Tower is filling. Shift report directs to disregard alarm unless the LoLo alarm comes in | All Water System ROC General | 2025-11-01
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-01
ROC | November | STETTL, Activated D1, STW12 well was off when a low effluent free cl2 alarm came in, activated the duty to freshen up the line and to send water to the tower | All Water System ROC General | 2025-11-03
ROC | November | HLETYS- Pre injection combined Cl2 lo alarm came in. Disregard on shift report. Tower filling | All Water System ROC General | 2025-11-02
ROC | November | NMETHW - Free Chlorine Hi alarm came in. Checked site. Although duty had recently deactivated, tower is still filling through EGMCRW. Free chlorine levels may be higher due to QVW4 being run. Will continue to monitor. In case levels reach hihi or tower continues to fill for a longer period of time, will reach out to OIC. 04:42 - As NMETIB was activated, NMETHW was no longer back filling which allowed for the free chlorine levels to go back to optimal range and alarm has cleared. | All Water System ROC General | 2025-11-02
ROC | November | STRS48 - Activate duty 1, Kingsley M finished with work | All Water System ROC General | 2025-11-03
ROC | November | Adeela Khan signing out | All Water System ROC General | 2025-11-02
ROC | November | QVW12- Influent free Cl2 lolo alarm came in on well shutdown. Notified Joe D will take a look on SCADA Placed wells in man/off | All Water System ROC General | 2025-11-01
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-02
ROC | November | STRS48- Influent free Cl2 hihi alarm came in. Continued to monitor. was able to clear alarm after 5 mins | All Water System ROC General | 2025-11-02
ROC | November | STRS48 - Kingsley M working on OIT, deactivated wells while work in progress | All Water System ROC General | 2025-11-03
ROC | November | RHMCMD- Placed valve in auto STETBR- Deactivated D1 at 69% as STETTL struggling to fill STW12- Placed P2 in auto as per interim | All Water System ROC General | 2025-11-02
ROC | November | AUW14- Well 1 waste flow fault alarm. Well did not flow to waste on start up intermittent issue. Emailed Central water OPs and cleared alarm | All Water System ROC General | 2025-11-02
ROC | November | MKPSSA, Placed pumps 1/2 man/off as MKRSEM is failing to fill. Will continue to monitor, if MKRSMR starts to drop significantly, will place pump 2 back to auto so it can hold the res. | All Water System ROC General | 2025-11-02
ROC | November | Markham/Stouffville System, system is currently low across the board. Both Zone 1 and Zone 2 in Stouffville are trying to fill. Zone 2 is flatlining while zone 1 is slowly filling. Stouffville system is taking a lot from MKRSMR. MKRSMR is slowly draining since only having the 1 pump filling the res as ROC turned 1 pump off to help MKRSEM. MKRSEM is now slowly filling since only 1 is active at MKPSSA. System is currently in a stand still and just flat lining/draining. Contacted Stephen B to inform him of the situation as everything is low and nothing is wanting to recover. Call was made to make a strategy for the time being. Strategy for the night is to juggle MKRSMR and MKRSEM by having 1 pump run then switching to 2 pumps at MKPSSA so that flow can then help MKRSMR. Until Stouffville system is satisfied, juggling of both res's will be needed. consult | All Water System ROC General | 2025-11-02
ROC | November | MKETFA, Free Cl2 hi Alarm, As per shift report directed to disregard, if hihi comes in, will contact operator, as for now will send email to on call operator as per their shift report GWTP, Raw Water Total Cl2 Res hihi alarm, directed to disregard as long as the residual comes back down within 20 minutes of initial reading. will continue to monitor until the residual is back down to normal range | All Water System ROC General | 2025-11-02
ROC | November | HLW2- Placed Sharon valve back in auto | All Water System ROC General | 2025-11-02
ROC | November | YWS + NYWS Normal MKPSSA, placed PUMP 2 in auto | All Water System ROC General | 2025-11-02
ROC | November | JFRS - Kingsley M rebooting OIT, disregard heartbeat alarm MKRSEM - Request TO (Brent) to add 1 more pump for 3 pumps to run to assist with filling res as MKPSSA 2 pumps running still for trial isolation | All Water System ROC General | 2025-11-03
ROC | November | Made the following changes as per Dwayne L and Gluzen R : RHPSPA- deactivated D1, placed all pumps Man/off RHVCEM - man/open 50% VNPS PD7 switched from split to combine VNPS PD7 pumps 1 and 3 to auto. | All Water System ROC General | 2025-11-03
ROC | November | STW3 - Rick L & Red B onsite for chlorine analyzer | All Water System ROC General | 2025-11-03
ROC | November | STW3 - Kingsley M restarting OIT, disregard Historian Heartbeat alarm. | All Water System ROC General | 2025-11-03
ROC | November | SHTP- Filter 3 turbidity hi alarm after filter backwash. Reset as per shift report | All Water System ROC General | 2025-11-03
ROC | November | MKRSEM- Called Metro spoke with Brett to stop flow to reservoir STW12- Placed well 2 in manual as per interim to fill STETBR NMVCIB- Placed valve in manual 40L/s | All Water System ROC General | 2025-11-02
ROC | November | HLETYS- Post injection free CL2 lo alarm came. Checked trends looks like flow dropped below dosing setpoints and recovered quickly while chemical system turned off. Flow restored and chemical system operation and alarm cleared | All Water System ROC General | 2025-11-02
ROC | November | SHTP- Filter 3 turbididty hi alarm came in after filter backwash. Reset as per shift report STRS48- Influent free Cl2 hihi alarm came in as wells started up to fill res continue to monitor as residual recovered | All Water System ROC General | 2025-11-01
ROC | November | Adeela Khan signing in. Weather: 5C and Cloudy | All Water System ROC General | 2025-11-01
ROC | November | AUW14 - Influent Free Chlorine HiHi alarm came in. Wells have recently started up. After 4 mins, influent free chlorine levels went back to optimal range and alarm has been cleared | All Water System ROC General | 2025-11-02
ROC | November | NBW3- Station turbidity fault alarm came in able to rest well not active no water directed to users and trends okay QVETQS- Tower level hi deactivated D1 at 68% (NMETHW) | All Water System ROC General | 2025-11-03
ROC | November | SHTP- Filter Phase monitor fault alarm outstanding after power blip. Notified Cole W. Directed try and reset as well as to activate reservoir duty to ensure filters will run after power blip #consult | All Water System ROC General | 2025-11-03
ROC | November | NMETIB - Activated duty to help offset with NMETHW | All Water System ROC General | 2025-11-02
ROC | November | GWTP- Raw water total Cl2 res hihi alarm came in recovered quickly. Disregard and cleared as per shift report | All Water System ROC General | 2025-11-01
ROC | November | STETTL- Tower level lolo. Tower struggling to fill. Notified Stephen B. Directed to place STW1 in man/on to supplement flow | All Water System ROC General | 2025-11-02
ROC | November | RHMCMD, Placed valve man/open RHRSTR, Deactivated D1 so more flow can move from MARS to RHRSTR VNRSKS, Activated D1 | All Water System ROC General | 2025-11-03
ROC | November | NMW12 - Combined Chlorine Lo alarm came in. Wells are not running and water is not being directed to users | All Water System ROC General | 2025-11-02
ROC | November | STRS48- Influent free Cl2 hihi alarm came in. Cleared after 5 mins STETBR- Changed lo level alarm set point from 40 to 42 % | All Water System ROC General | 2025-11-02
ROC | November | YWS+NYWS normal QVW34- Placed Well 4 in man/on to push water south through EGMCRW | All Water System ROC General | 2025-11-02
ROC | November | YWS+NYWS normal | All Water System ROC General | 2025-11-02
ROC | November | PD6 - Zhoran from TO informed they are flushing 0022 discharge line from pumps 10-12 Informed Dwayne L and linear team will be reverting trial isolation changes from Markham starting from North end. | All Water System ROC General | 2025-11-04
ROC | November | HLW1 - Rick L & Red b onsite for annual calibrations | All Water System ROC General | 2025-11-04
ROC | November | Carter Dunn Signing In, 6D/Clear | All Water System ROC General | 2025-11-02
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-03
ROC | November | QVW4, Placed back to auto NMETIB, Activated D1 NMVCBP, Placed valve back to auto | All Water System ROC General | 2025-11-02
ROC | November | MKPSSA, Placed pumps back to auto. will continue to juggle the reservoirs till Stouffville is filled | All Water System ROC General | 2025-11-02
ROC | November | HLW2- Ammonia Pump 1 Fault, Treated Free Chlorine HiHi Alarm. Came in on startup. Cleared alarms. | All Water System ROC General | 2025-11-04
ROC | November | SHETCS - Deactivate tower duty as reservoir is at low level | All Water System ROC General | 2025-11-04
ROC | November | MAPS PD7- Placed P1 man/off MAPS PD8- Placed P2 in man/off and placed back in auto speed setpoint and returned P1-4 to auto | All Water System ROC General | 2025-11-04
ROC | November | YWS+NYWS normal | All Water System ROC General | 2025-11-03
ROC | November | MAPS PD8- Placed P2 in manual as D1 close to stop P1 started in its placed in auto. Placed P3/4 in manual and stopped P3 so 3 pumps would not run and Placed P2 speed set point at 0% P2 efficiency lo and wire to water lo alarm came in as a result. Cleared alarm once all other pumps stopped | All Water System ROC General | 2025-11-04
ROC | November | RHPSWA- Placed P1 in man/on STETBR- D1 active. Placed STW1 in man/on as per interim | All Water System ROC General | 2025-11-04
ROC | November | STPSMR - Kingsley M restarting OIT, disregard Historian heartbeat alarm. | All Water System ROC General | 2025-11-03
ROC | November | YWS+NYWS normal STPSTL- Placed FCV in man/0L/s and placed P1/2 in auto | All Water System ROC General | 2025-11-04
ROC | November | RHRSTR- Found D2 active Placed P2 in man/off and Placed P3 in man/off (already running) | All Water System ROC General | 2025-11-04
ROC | November | STPSMR- Dan B onsite for generator work. Disregard related alarms. | All Water System ROC General | 2025-11-04
ROC | November | Gluzen Ramos Ong signing in | All Water System ROC General | 2025-11-04
ROC | November | HLETYS- Ammonia Pump 1,2 Failed to Start. Reset alarms and both failed again. Placed both pumps and hypo pumps 1,2 in manual. Notified Cole W. He will take a look. W11420673 CMU5 | All Water System ROC General | 2025-11-05
ROC | November | STPSMR- Dan B finished onsite. | All Water System ROC General | 2025-11-04
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-03
ROC | November | QVETQS - Alex B. doing PMs including cleaning deplox cl analyzer, exercise tie valve, and JH&S | All Water System ROC General | 2025-11-04
ROC | November | EGMCRW- Ernie H onsite testing chamber flood alarm. | All Water System ROC General | 2025-11-04
ROC | November | MAPS- Ben H requested Pump 3 man/off JFRS- Ben H requested MV3 valve from 100 to 10% 12:30- Ben H placed MV4 and MV3 valves back into auto. Requested to place MAPSPD8 and VNPS PD8 back into auto | All Water System ROC General | 2025-11-04
ROC | November | NMETHW- Joe D onsite for deplox analyzer maintenance and health and safety work orders. | All Water System ROC General | 2025-11-04
ROC | November | RHMCH7- Chris S working on radio connection. will lose comms. | All Water System ROC General | 2025-11-04
ROC | November | HLW1- Cole W called. He is onsite placing well back online. Disregard alarms. | All Water System ROC General | 2025-11-05
ROC | November | STETTL - Outlet free chlorine low alarm. Checked site, duty is active and tower is filling. Trending shows a dip of the free chlorine reading which is recovering. Will monitor system. | All Water System ROC General | 2025-11-05
ROC | November | STETTL - Tower level lolo alarm. Checked site, system duty just activated, tower being deep cycled by East Water ops. | All Water System ROC General | 2025-11-05
ROC | November | STW12- Travis W onsite and requested to place well 1 and 2 in man/on. Well 2 already running in auto. | All Water System ROC General | 2025-11-05
ROC | November | NBW3 - Influent Free Chlorine HiHi alarm came in. Well just started up. Free chlorine levels came back down within 5 mins and alarms have cleared | All Water System ROC General | 2025-11-04
ROC | November | STW12 - Placed wells back to auto | All Water System ROC General | 2025-11-04
ROC | November | Angelica Chepiga signing out | All Water System ROC General | 2025-11-03
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-05
ROC | November | Connor Smith signing in | All Water System ROC General | 2025-11-05
ROC | November | QVW12- Influent free Cl2 lo alarm came in. trends look off. But recovered. Notified Joe D about potential issue with dosing. Joe D directed to rotate booster pump 2 to see if dosing improves. Will monitor for changes STETTL- Tower lolo came in as D1 started. Tower filling. Will clear alarm #consult | All Water System ROC General | 2025-11-01
ROC | November | QVW12- Combined CL2 lo alarm came in. Well not active no water directed to users Joe D called back Influent looks stable enough to run wiht booster pump 1 man/off. Will monitor next cycle | All Water System ROC General | 2025-11-01
ROC | November | Adam Button signing in clear -1C | All Water System ROC General | 2025-11-02
ROC | November | NMW15 - Jason G onsite cleaning chlorine & turbidity analyzer | All Water System ROC General | 2025-11-04
ROC | November | BVOPLAM - Kinsgley M working on OIT, disregard heartbeat alarm | All Water System ROC General | 2025-11-03
ROC | November | KCPSDS - Jacob M finished at site | All Water System ROC General | 2025-11-04
ROC | November | Adeela Khan signing in. Weather: 7C and partly cloudy | All Water System ROC General | 2025-11-04
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-04
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-05
ROC | November | Gluzen Ramos Ong signing out | All Water System ROC General | 2025-11-04
ROC | November | BVOPLAM - Kingsley M completed OIT work for the day. | All Water System ROC General | 2025-11-03
ROC | November | NBW3 - Joe W onsite running generator, turbidity, chlorine analyzer cleaning | All Water System ROC General | 2025-11-04
ROC | November | AURSBS- Ben H onsite with Tyler ZJ working on MV4 Valve. Lowered AUVCBS flow and placed AUW2 man/on. He will call when need to run Maple to Jefferson Feed to test MV4 valve. | All Water System ROC General | 2025-11-04
ROC | November | Adam Button signing in 4C Clear | All Water System ROC General | 2025-11-03
ROC | November | GRTPLL - Raw Water Total Chlorine HiHi alarm came in. Checked site. Shift report indicates that this can be disregarded as long as levels come down within 20 mins 19:15 - Levels came back to optimal range | All Water System ROC General | 2025-11-01
ROC | November | YWS + NYWS normal | All Water System ROC General | 2025-11-01
ROC | November | MKRSEM - Reservoir Level is low. Deactivated MKRSMR to allow MKRSEM time to fill | All Water System ROC General | 2025-11-02
ROC | November | KSTP - CO2 adjusted pH OOR/hihi, informed Donald M. Looking into issue RHPSPA - Tyler Z onsite running generator NMTKKC - Ammonia pump 1 failed to start. Able to clear and pump 1 able to run | All Water System ROC General | 2025-11-03
ROC | November | SHTP- Filter 2/3 turbidity hi alarm came in after filter 1 backwash. Reset alarms as per shift report | All Water System ROC General | 2025-11-03
ROC | November | AUW14- Treated free Cl2 hihi alarm came in recovered after 3 mins. Cleared alarm YWS+NYWS normal | All Water System ROC General | 2025-11-01
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-05
ROC | November | YWS+NYWS normal | All Water System ROC General | 2025-11-01
ROC | November | NBW3- Influent free Cl2 lolo switch alarm came in. Will try to restart well in 10 mins | All Water System ROC General | 2025-11-01
ROC | November | GWTP- Screen 2 diff level hihi alarm came in. Recovered within 5 mins cleared alarm | All Water System ROC General | 2025-11-01
ROC | November | SHTP- Filter 2 Turbidity OOR alarm came in Dave T on site working on turbidity meter | All Water System ROC General | 2025-11-01
ROC | November | KLPS27 - Historian Heartbeat alarm, notified Chris S. He will check. | All Water System ROC General | 2025-11-03
ROC | November | 07:33 RHMCMD - Placed back to auto. | All Water System ROC General | 2025-11-03
ROC | November | YWS + NYWS Normal Ethan Ullalkar signing out. | All Water System ROC General | 2025-11-03
ROC | November | KCETDS, Outlet Total Cl2 res lolo, abnormal dip occurred, will continue to monitor however if it doesn't recover after 3 readings, will contact operator | All Water System ROC General | 2025-11-03
ROC | November | Angelica Chepiga signing in, weather 7C | All Water System ROC General | 2025-11-03
ROC | November | HLW1 - Red B and Rick L on site for annual calibrations. | All Water System ROC General | 2025-11-03
ROC | November | STETBR- Free CL2 lo alarm still outstanding Notified Stephen B. Okay to deactivate at STETL and open FCV at STPSTL STPSTL- Placed P1/2 in manual and opened FCV at 40L/s STW12- Placed W1 in man/off | All Water System ROC General | 2025-11-03
ROC | November | MKRSEM- Called Metro spoke to Brett to stop pumping to reservoir | All Water System ROC General | 2025-11-01
ROC | November | MKPSSA- Placed P3 in man/on | All Water System ROC General | 2025-11-04
ROC | November | KSTP- Fin water Fluoride res lolo alarm came in. Notified Stephen B directed to rotate fluoride pumps to pump 1 to see if it recovers. Stephan B also directed to clear alarm If Residual recovers clear BVPS- Stephen B heading to site Free Cl2 analyzer issues from overnight. Created CMU5 W11407867 15:00- KSTP- Fin Water fluoride res not recovering. Notified Stephen B Directed to place high lifts in man/off until Stephen B can go to site and investigate High lift pump took 10 mins to shutdown. #CMU5 | All Water System ROC General | 2025-11-01
ROC | November | Initiating MAPS to JFRS feed run - Placed KCPSDS pumps man/off - Placed VNPS PD8 and MAPS PD8 pumps man/off - Placed VC MV3 into man - Placed AURSBS Res MV4 to man and close - Man/start pump 2 at MAPS 01:05 - Reverted all changes | All Water System ROC General | 2025-11-01
ROC | November | STW12 - Kingsley M completed OIT work. Placed STW12 pumps man/on. | All Water System ROC General | 2025-11-03
ROC | November | STPSTL- Changed FCV to 25L/s AURSBS -Ammonia tank level hi. LIT is reading okay reset alarm | All Water System ROC General | 2025-11-03
ROC | November | YWS+NYWS normal | All Water System ROC General | 2025-11-04
ROC | November | AURSBS- Activated D1 AURSOH- Activated D1 | All Water System ROC General | 2025-11-04
ROC | November | VNPS PD7- Placed P1 in man/off MARS PD7- Placed P1-3 in manual and started P1 JFRS- Deactivated D1 | All Water System ROC General | 2025-11-04
ROC | November | Connor Smith signing in 2 C Cloudy | All Water System ROC General | 2025-11-04
ROC | November | COTFA - PD6 Discharge Pressure HiHi MKPSSA - Discharge Pressure HiHi MKVCMM - Reverse Flow Hi Alarms came in upon MKRSMR duty activating. After checking site, all pressure and flow levels came back to optimal range within 5 mins | All Water System ROC General | 2025-11-04
ROC | November | NMETIB- Activated D1 at 67% as per shift report to offset from NMETHW | All Water System ROC General | 2025-11-04
ROC | November | KSETWP - Donald M onsite for chlorine analyzer maintenance. KSETWB - controlling tower while West park is isolated for valve work MKRSMR - TO (Zhoran) pump capacity back to normal. Ready to go back to normal operations GWTP - Stephen B onsite analyzer cleaning, chemical leak detector, contractor onsite working on low lift analyzer, testing probes | All Water System ROC General | 2025-11-04
ROC | November | NMW12- Combined/Treated CL2 lo alarm came in. Well not active will recover wen duty activates | All Water System ROC General | 2025-11-01
ROC | November | STETBR- Free Cl2 lo alarm came in. Will continue to monitor and contact OCO out if lolo comes in RHRSTR- Deactivated D1 RHMCMD- Placed Valve in manual | All Water System ROC General | 2025-11-01
ROC | November | RHMCMD- Placed valve in man/open KSETDP- Inlet total/free Cl2 hihi alarm disregard on shift report | All Water System ROC General | 2025-11-01
ROC | November | YWS+NYWS normal Adam Button signing out | All Water System ROC General | 2025-11-04
ROC | November | Ethan U signing in | All Water System ROC General | 2025-11-04
ROC | November | KSTP - Flouride lolo/fault. Monitored, next reading came back up. Alarm cleared | All Water System ROC General | 2025-11-04
ROC | November | KSTP - Fin water tot CL2/flouride res fault. Disregard as per shift report | All Water System ROC General | 2025-11-03
ROC | November | NBET- Nobleton Sys Fire Storage Cap. Low Alrm. NBET27 site is offline. | All Water System ROC General | 2025-11-04
ROC | November | NMVCBA - Upstream Pressure OOR Alarm came in. Checked site. Pressure was flashing OOR but came back within 5 mins. Alarms have cleared. Will continue to monitor 22:56 - Upstream Pressure OOR came back in along with Upstream Pressure HiHi alarm. High pressure stayed for about 4 mins. Called Rob P. who informed this may be an instrument issue #CONSULT | All Water System ROC General | 2025-11-04
ROC | November | QVW34- Treated total Cl2 lo alarm came in looks like analyzer dropped out recovered after 3 mins cleared alarm STPSTL- Placed FCV in man closed and placed P1/2 in auto as STETBR fill cycle begins | All Water System ROC General | 2025-11-02
ROC | November | YWS+NYWS normal | All Water System ROC General | 2025-11-02
ROC | November | HLW2- Down stream pressure hihi alarm came in reset alarm as pressure recovered. Came back in placed Sharon valve in man/closed reset alare will place back in auto once schedule mode ends ARPS- Total ammonia fault alarm came in. able to reset after 3 mins STETBR- Free Cl2 lo alarm came in able to reset | All Water System ROC General | 2025-11-02
ROC | November | STW12 - Place well 2 man/on position as Bethesda duty active | All Water System ROC General | 2025-11-03
ROC | November | BVPS- Placed P1/3 in auto | All Water System ROC General | 2025-11-04
ROC | November | RHPSPA - Kingsley M restarting OIT. | All Water System ROC General | 2025-11-03
ROC | November | HLW1 - Red B and Rick L finished on site. | All Water System ROC General | 2025-11-03
ROC | November | MKMCLA- Chris S finished on site. All back to normal. | All Water System ROC General | 2025-11-03
ROC | November | YWS+NYWS normal VNRSKS- Deactivated D1 AURSBS- Deactivated D1 | All Water System ROC General | 2025-11-01
ROC | November | AUPSRR- Chemscan OFFLINE Status. Called William M. No answer. | All Water System ROC General | 2025-11-05
ROC | November | Stouffville Water System- Peter from the Town will be flushing different areas for 10 minutes each throughout the day. | All Water System ROC General | 2025-11-05
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-01
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-01
ROC | November | YWS+NYWS normal | All Water System ROC General | 2025-11-01
ROC | November | Adeela Khan signing out | All Water System ROC General | 2025-11-05
ROC | November | Christian Van Beek signing in. | All Water System ROC General | 2025-11-05
ROC | November | BVPS - Tyler ZJ on site for a generator load test. Will see associated alarms. | All Water System ROC General | 2025-11-05
ROC | November | KCETDS- Activated D1 | All Water System ROC General | 2025-11-03
ROC | November | STW3 - Patrick F and Travis W on site to run the well to waste in preparation for bringing the well back in service. Patrick F is also deep cycling STETBR. | All Water System ROC General | 2025-11-05
ROC | November | VNPSCD - Jordan B onsite running generator and chlorine leak detector. BVPS - Deactivated duty 1 as requested | All Water System ROC General | 2025-11-04
ROC | November | EGMCRW - Ernie H. and Tyler S. cycling power | All Water System ROC General | 2025-11-04
ROC | November | VNPS PD7- Placed P2 in man/off | All Water System ROC General | 2025-11-04
ROC | November | YWS+NYWS normal | All Water System ROC General | 2025-11-04
ROC | November | SHTP- David T onsite for work orders. Working on Cl analyzers, Chlorine leak test, and KNMO System. | All Water System ROC General | 2025-11-04
ROC | November | STPSMR- Jack P onsite testing Cl Leak and Cl analyzer maintenance. | All Water System ROC General | 2025-11-05
ROC | November | HLETYS - Pre injection combined chlorine Low alarm, disregard by shift SCADA report. | All Water System ROC General | 2025-11-03
ROC | November | MARS- Toronto (Mehdi) called and will be running an extra Keele Street Pump for 30 minutes. | All Water System ROC General | 2025-11-05
ROC | November | BVPS- Tyler ZJ onsite and requested pumps man/off for generator run. | All Water System ROC General | 2025-11-05
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-04
ROC | November | HLETYS- Ammonia P1/2 failed to start alarms came in as Sharon valve runs in schedule mode. Was not able to reset alarms. Notified Dave T. 17:36- HLETYS- Dave T called back about Ammonia P 1/2 alarms should clear once the Sharon valve closes #consult | All Water System ROC General | 2025-11-01
ROC | November | NMW12 - Treated Total Chlorine Lo an combined chlorine lo alarms came in. Wells are not running and water is not being directed to users | All Water System ROC General | 2025-11-05
ROC | November | GWTP - GAC 4 Effluent Turbidity Fault alarm came in. Checked site. Trending is okay and turbidity levels are within range. Called Stephen B. who directed to disregard alarm for the night. Stephen B. requested a call back in case another GAC turbidity faults #CONSULT | All Water System ROC General | 2025-11-01
ROC | November | MARS - Cell 1 Level HiHi alarm came in. Activated VNRSKS and deactivated BVPS, to help lower levels at MARS | All Water System ROC General | 2025-11-02
ROC | November | HLW2- Downstream pressure hihi alarm came in as Sharon valve opened . Reset as pressure recovered | All Water System ROC General | 2025-11-02
ROC | November | YWS+NYWS normal | All Water System ROC General | 2025-11-02
ROC | November | MKRSEM - Request TO (Zhoran) to drop all pumps | All Water System ROC General | 2025-11-04
ROC | November | KCPSDS - Jacob M onsite hi/lo levels, cleaning chlorine analyzer, exercise valves QVW12 - Eric S attending site to work on flowmeter bypass, place well 1 & 2 man/off until work in complete QVW34 - Place well 4 currently running in man/on 10:26 - Eric S finished at site. place wells back in auto | All Water System ROC General | 2025-11-04
ROC | November | Kennedy Road- Rob P called to inform he is opening up valves to begin reverting trial isolation. | All Water System ROC General | 2025-11-04
ROC | November | AUETAD - Total and Comb Cl LoLo. Inquired with William M., on site with Ben H. troubleshooting analyzer | All Water System ROC General | 2025-11-04
ROC | November | HLETYS- Ammonia Pump 1,2 fail to start. Notified Cole W. Can disregard. Benson S heading to site for grabs | All Water System ROC General | 2025-11-05
ROC | November | VNPS - Lee F on site for vibration testing. Lee has requested to have all the pumps cycle on for vibration testing. Will be activating/deactivating pumps as needed by Lee F. Starting with pumps 1 and 2 at both PD8 and PD7 headers. | All Water System ROC General | 2025-11-05
ROC | November | VNPS- Lee F called and requested pumps 1,2 for PD7 and PD8 man/off. 11:09- Lee F requested pumps 3,4 man off | All Water System ROC General | 2025-11-05
ROC | November | SUETDR -Derek from Aquazition (705-500-0049) is on his way to Sutton for flushing. Emailed area. | All Water System ROC General | 2025-11-03
ROC | November | YWS + NYWS NORMAL | All Water System ROC General | 2025-11-26
ROC | November | NMETIB- Deactivated D1 at 74% to offset from NMETHW | All Water System ROC General | 2025-11-28
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-30
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-30
ROC | November | GWTP - UV reactor 1 & 2, warning, outside exp range, minor fault, transmittance lo. Informed Jack P. Will take a look Consult 21:21 - Directed to disregard for the night. Achieving adequate UV dosage. Alarms cleared | All Water System ROC General | 2025-11-24
ROC | November | NBW3- influent free hi alarm came in on well start up residual recovered after 3 mins alarm cleared | All Water System ROC General | 2025-11-27
ROC | November | ARPS- Jerry from Peel called back informing ROC normal operations have been resumed. | All Water System ROC General | 2025-11-27
ROC | November | QVW12, Alex B is finished on site and leaving | All Water System ROC General | 2025-11-27
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-25
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-24
ROC | November | ANW23 - King City operators will be flushing in Ansnorvedlt today. May see pressure alarms. Cole W will be monitoring SCADA during the initial flushing. | All Water System ROC General | 2025-11-24
ROC | November | GWTP- Chris S on site to for comms testing in preparation for tomorrows interim. Shouldn't expect any comms interruption but Chris S wants to be notified if any alarms come in | All Water System ROC General | 2025-11-24
ROC | November | BLW12 - Joe M called to inform that BLW12 will be OOS and local off for the duration of the day. | All Water System ROC General | 2025-11-25
ROC | November | HLETYS - Post injection combined chlorine low. Checked site, tower is filling with chemical system manual/off. Contacted Cole W who is completing some tests following the completion of the EG watermain installation and will return the system to normal operations once he is finished. | All Water System ROC General | 2025-11-25
ROC | November | KSTKWP, Free Cl2 lolo, Trending shows an abnormal dip that occurred, if analyzer reading doesn't recover after 2 readings, will contact on call operator 00:53, Residual has not come back up, notified Jack P, he will further look into the issue 01:38, Jack P activated the duty and the free came back to normal levels. Jack P directed to disregard the dip that occurred for the rest of the night. consult | All Water System ROC General | 2025-11-20
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-21
ROC | November | SHTP, Filt 1 Turbidity Hi alarm, a filter was back washing, directed to disregard as per shift report, if it comes in again, will notify operator | All Water System ROC General | 2025-11-21
ROC | November | Stouffville Water System- Peter from the Town will be flushing in Zone 2. | All Water System ROC General | 2025-11-19
ROC | November | Adam Button signing in -1 Clear | All Water System ROC General | 2025-11-20
ROC | November | Carter D signing out | All Water System ROC General | 2025-11-20
ROC | November | Christian Van Beek signing in. Weather: -2C and clear. | All Water System ROC General | 2025-11-26
ROC | November | NMW136 - Combined chlorine lolo and treated total chlorine lolo alarms. Checked site, well is off no water being directed to users. Trending shows a sudden dip of the readings which recovered within two reading intervals. Reset alarms. | All Water System ROC General | 2025-11-26
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-26
ROC | November | MKRSMR - Level hit duty stop. Called Toronto Water (Mehdi) and requested pump 10 be placed back to auto | All Water System ROC General | 2025-11-27
ROC | November | ARPS - Total and Free Ammonia Fault alarms came in. Checked site. Trends indicate a spike. Levels came back to optimal range within 5 mins and alarms have cleared | All Water System ROC General | 2025-11-27
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-30
ROC | November | Adeela Khan signing in. Weather: 0C and flurries | All Water System ROC General | 2025-11-30
ROC | November | Connor Smith signing in | All Water System ROC General | 2025-11-19
ROC | November | STETBR/RHRSWA- Talha H done OIT work historian heartbeat alarms cleared | All Water System ROC General | 2025-11-27
ROC | November | Initiating MAPS to JFRS feed run - Placed KCPSDS pumps man/off - Placed VNPS PD8 and MAPS PD8 pumps man/off - Placed VC MV3 into man - Placed AURSBS Res MV4 to man and close - Man/start pump 1 at MAPS 01:31 - Reverted all changes All as per procedure | All Water System ROC General | 2025-11-30
ROC | November | MARS - Hi level alarm came in. Placed RHMCMD in man/open Deactivated RHRSTR | All Water System ROC General | 2025-11-30
ROC | November | SHETCS - Hypo Pump 2 Failed to start alarm came in. Checked site. Tower is filling. Duty had already rotated hypo pumps so that hypo pump 1 is in duty 1 and is currently running. Ack/reset alarm | All Water System ROC General | 2025-11-28
ROC | November | Balantrae Water System- Received a call from Michael from Stouffville Firehall 52. They will be operating the hydrant outside the hall. BLW3- Placed man/off 14:27- Michael from Stouffville Fire called back. Finished operating hydrant. Placed BLW3 back into auto. | All Water System ROC General | 2025-11-29
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-29
ROC | November | JFRS - Only one pump running at VNPS PD7, activated Duty 2. | All Water System ROC General | 2025-11-26
ROC | November | MARS - level hihi alarm. Deactivated RHRSTR duty 1. | All Water System ROC General | 2025-11-27
ROC | November | NMTKKC - Ryan B. is on site with maintenance running pumps 10:50 - Ryan B. finished on site | All Water System ROC General | 2025-11-21
ROC | November | Ethan Ullalkar signing out. | All Water System ROC General | 2025-11-21
ROC | November | VNP8 - Jordan B. and Benson S. on site, confirmed they worked on surge tanks. Placed PD8 pumps back in auto. D1 and 2 active | All Water System ROC General | 2025-11-27
ROC | November | NBET27 - Parth P called and requested that the altitude valve be placed back in auto mode. | All Water System ROC General | 2025-11-25
ROC | November | GWTPLL - Artour L onsite for project for flow control valve commissioning | All Water System ROC General | 2025-11-21
ROC | November | MKRSEM- Called Toronto (Paul) and requested pumps off. | All Water System ROC General | 2025-11-19
ROC | November | NBW5- Eric S on site to work on silicate P2. HLW2- FCV2 Changed flow set point from 30L/s to 35L/s | All Water System ROC General | 2025-11-20
ROC | November | Adeela Khan signing in. Weather: 4C and cloudy | All Water System ROC General | 2025-11-21
ROC | November | HLW2- Benson S requested well back in auto | All Water System ROC General | 2025-11-19
ROC | November | QVW34 - Alex B. is on site flushing the silicate lines | All Water System ROC General | 2025-11-21
ROC | November | STETBR - Pumps in man/off, VC_FCV1 valve man/open at 28%. Low alarm 40%. Once low alarm triggered will close VC and valve pumps back in auto | All Water System ROC General | 2025-11-21
ROC | November | Carter Dunn Signing In | All Water System ROC General | 2025-11-27
ROC | November | STPSMR- Pump 3 VFD Fault Alarm. Came in on start up. Placed Pump 3 into manual and placed pump 1 into duty 1. Emailed East. | All Water System ROC General | 2025-11-29
ROC | November | Ethan U signing in Weather 0. | All Water System ROC General | 2025-11-22
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-22
ROC | November | SHETCS- Hypo pump 2 failed to start alarm came in. Reset alarm | All Water System ROC General | 2025-11-28
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-27
ROC | November | Stouffville Water System- Travis from the town called. They will be flushing in Zone 2. | All Water System ROC General | 2025-11-19
ROC | November | BVPS, Activated D1 to help water flow from RHRSTR to MARS ARPS, David from OCWA called, everything is back to normal operation | All Water System ROC General | 2025-11-28
ROC | November | Carter Dunn Signing out YWS + NYWS Normal | All Water System ROC General | 2025-11-27
ROC | November | QVW12 - Influent Free Chlorine Lo alarm came in. Checked site. Wells are running. Trends indicate a dip in influent free chlorine levels but has since recovered. Alarm has cleared 01:02 - Influent Free chlorine Lo alarm came in again. Increased Chlorine dosing factor by 3%. Will monitor. After a few minutes, levels continued to drop. Increased chlorine dosing factor by another 3% 01:20 - Influent levels continued to drop. Rotated chlorine pumps 01:25 - Influent Free Chlorine LoLo Switch alarm came in. This interlocked both wells. Called Joe D. who directed to wait 10 mins and reset. If the influent levels tank again, place both wells man/off and place QVW3 on. 01:30 - Influent levels are back to optimal range. 01:33 - Joe D. called back to inform that issue happened on a previous night and to only run 1 of the wells. Deactivated duty 2. Placed well 2 man/off and reset alarms 01:49 - Influent Free Chlorine HiHI alarm came in. After 2 mins, level came back down to optimal range. Will continue to monitor 02:51 - Placed QVW2 back to auto as duty 2 is no longer active #CONSULT | All Water System ROC General | 2025-11-30
ROC | November | Carter Dunn Signing Out | All Water System ROC General | 2025-11-25
ROC | November | HLW2- Combined Chlorine LoLo. Well is offline for rehab. | All Water System ROC General | 2025-11-25
ROC | November | HLETPR- Received a call from NAV Canada Flight Centre regarding Beacon Fault that had previously occurred. Was instructed by ROC during shift transfer to inform them that issue has been resolved. | All Water System ROC General | 2025-11-21
ROC | November | ANW23- Discharge pressure lolo discharge flow hihi alarms came in notified Cole W. Cole W will call King City OPs to adjust flushing 14:30- ANW23- Discharge pressure lolo discharge flow hihi alarms came in notified Cole W. Cole W will call King City OPs to adjust flushing | All Water System ROC General | 2025-11-24
ROC | November | STPSTL- Pump 1 Low Flow Alarm. Interlocked pump. Pump 2 switched into duty 1 and started up. STW12- Placed well 2 man/on for STETBR fill cycle STW3- Placed well man/on for STETBR fill cycle | All Water System ROC General | 2025-11-30
ROC | November | Adeela Khan signing in. Weather: 4C and cloudy | All Water System ROC General | 2025-11-23
ROC | November | GWTP- Low lift P4 hydraulic valve fail to open reset as per shift report 7:32- GWTP- Low lift P2 hydraulic valve fail to open reset as per shift report | All Water System ROC General | 2025-11-24
ROC | November | STRS48- Influent free lolo switch alarm came in. Dan Z will rotate sample pumps and investigate later today GWTP- LLP1/4 hydraulic valve failed to close and surge valve open alarms came in reset as per Dan Z | All Water System ROC General | 2025-11-25
ROC | November | NMW12- Ben H on site to test Well 2 forward flow lo and Influent free Cl2 lo alarms | All Water System ROC General | 2025-11-25
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-24
ROC | November | KSETDP- Inlet total Cl2 and free Cl2 hihi alarm came in. Residuals recovered after 3 mins alarms cleared | All Water System ROC General | 2025-11-24
ROC | November | MKRSEM- Dwayne L confirmed that the linear team has reverted all valving changes from this mornings trial. Notified Peter at Metro that operations can go back to normal once they have reverted their changes is on their side. | All Water System ROC General | 2025-11-25
ROC | November | STETBR - Tower Level Hi alarm came in. Placed STW2 and STW3 back to auto, as per interim | All Water System ROC General | 2025-11-29
ROC | November | GRTPLL - Low Lift Pump 1 Hydraulic Valve Uncommanded close alarm came in. Ack/reset as per shift report | All Water System ROC General | 2025-11-30
ROC | November | NBET27 - Joe W onsite for 0 cal on chlorine analyzer | All Water System ROC General | 2025-11-21
ROC | November | SUETDR - Activated duty 1 to fill the tower for the interim procedure. | All Water System ROC General | 2025-11-25
ROC | November | GWTP- ZW5 Channel 1,2 Part Counts Out of Range. Disregard as per SCADA Report | All Water System ROC General | 2025-11-22
ROC | November | ARPS- ROYKS to ROPYS comm faIl on site. Trends okay cleared alarm | All Water System ROC General | 2025-11-24
ROC | November | NMW136- Treated total Cl2 / combined Cl2 lo alarms came in. Looks like analyzer dropped out. Continued to monitor. Recovered after 6 mins alarms cleared | All Water System ROC General | 2025-11-24
ROC | November | STRS48- Travis W on site for Cl2 system inspection and Cl2 leak detection. Will have wells man/off for work. NMVCBA- Ben H and Ryan B on site | All Water System ROC General | 2025-11-20
ROC | November | STPSTL - Building security intrusion alarm, FMC called and will notify Corp security. | All Water System ROC General | 2025-11-27
ROC | November | AUETFC - Alex B on site to complete work orders including chlorine analyzer maintenance, valve exercising, low temperature alarm test and JHSC checks. | All Water System ROC General | 2025-11-25
ROC | November | AUW14 - Joe D on site to prepare the well system for ther step test tomorrow. Joe will be throttling the AUW1 valve down to reduce flow before shutting down well pump 1. Joe will keep AUW3 pump manual on until tomorrow with AUW1,2,4 manual/off. | All Water System ROC General | 2025-11-24
ROC | November | KSTP - Donald M. called to inform that he is headed to site. Directed to place High Lift pump 3 back to auto | All Water System ROC General | 2025-11-26
ROC | November | MAPS PD7, Placed pump 1 man/on for Dan B | All Water System ROC General | 2025-11-27
ROC | November | RHPSPA - Jack P and Travis W on site to complete work orders including pump testing, flood alarm test and a diesel generator test. | All Water System ROC General | 2025-11-25
ROC | November | QVW12 - Influent free chlorine hi alarm. Influent free chlorine reading is slowly increasing. Noticed that the actual chemical dosing setpoint is higher than the proposed setpoint. Applied the dosing setpoint again and monitored. | All Water System ROC General | 2025-11-27
ROC | November | ARPS, Airport Rd Free/Total Ammonia Fault Alarm, Pumps 1 and 2 have shut down, contacted Tegbeer from ARPS, he notified the ROC that electricians are on site doing work and accidentally knocked the pumps off. Notified Tegbeer to get those 2 pumps back into service as MARS needs to be filled at this current time. Pumps were then resorted. MARS, Notified Toronto operator Paul to increase the flow to MARS. Once the 3rd pump turns off at ARPS, ill get the flow reverted back to normal 20:23, MARS, Notified Toronto operator Paul to go back to normal flow | All Water System ROC General | 2025-11-20
ROC | November | YWS + NYWS Normal STW1/3, Placed wells 1/3 back to auto | All Water System ROC General | 2025-11-21
ROC | November | MAPS PD8 - PD8 P2 VFD Fault and Not Ready alarms came in. Checked site. This occurred as duty deactivated. Called Jacob M. who will take a look 20:09 - Jacob called back and directed to disregard alarms and place pump man/off for the night #CONSULT | All Water System ROC General | 2025-11-23
ROC | November | QVW12- Influent free Cl2 lo alarm came in. Checked trends looks like sudden drop in residual. Continued to monitor residuals dropped again after 3 mins. Started recover after 2 reading s alarms cleared but started to decline after 20 mins. Two wells running most of the day concern for lines freezing up. Notified Joe D. Directed to shut one well down and run one well at QVW34 if we start to lose at NMETHW. Deactivated D2 17:03- Cleared influent free Cl2 lo alarm #consult | All Water System ROC General | 2025-11-28
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-20
ROC | November | Stouffville Water System- Cody from OCWA called and will be flushing in Zone 1 and Zone 2. | All Water System ROC General | 2025-11-20
ROC | November | MKRSEM, Notified Toronto operator Paul to start filling the res | All Water System ROC General | 2025-11-20
ROC | November | STW12 + STW3 - Place wells in auto | All Water System ROC General | 2025-11-25
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-25
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-29
ROC | November | VNETAG - Tower level low alarm. Jacob M placed all pumps and MV1 valve man/off for sampling. | All Water System ROC General | 2025-11-26
ROC | November | MKRSEM - Called Toronto Water (Peter), requested stop pumps. | All Water System ROC General | 2025-11-29
ROC | November | STETBR- Tower lo level alarm came in STW12-Placed well 2 in man/on as per interim STW3- Placed well 3 in man/on as per interim | All Water System ROC General | 2025-11-27
ROC | November | MKRSMR - Paul (Toronto) informed shutting down PD6 pump briefly to switch PS back to utility power | All Water System ROC General | 2025-11-27
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-28
ROC | November | YWS + NYWS normal | All Water System ROC General | 2025-11-23
ROC | November | VNRSKS - Activated duty to help lower levels at MARS BVPS - Deactivated duty | All Water System ROC General | 2025-11-24
ROC | November | STETBR - Tower Level Hi alarm came in. Placed STW12 and STW3 back to auto | All Water System ROC General | 2025-11-24
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-24
ROC | November | Connor Smith signing in -4 Clear | All Water System ROC General | 2025-11-29
ROC | November | STW12- Placed well 2 in manual for STETBR fill cycle. STW3- Placed well 3 in manual for STETBR fill cycle. | All Water System ROC General | 2025-11-29
ROC | November | MAPS PD8 - Pump 2 VFD fault alarm at Duty stop. Notified Jordan B. | All Water System ROC General | 2025-11-26
ROC | November | HLVCMA- Rob P onsite performing work. Disregard alarms. | All Water System ROC General | 2025-11-19
ROC | November | BLETNL- Changed D1 start from 50 to 72 and activated D1 as per Dan Z STRS48- No recovery on influent free Cl2 analyzer. Travis W will attend site. NMW12- influent free Cl2 hi alarm came in on well start up recovered after 3 mins alarm cleared NMW15- influent free Cl2 lo alarm came in on well start up recovered after 3 mins alarm cleared GWTP- Phil D, Patrick F and Stephen B on site. Will be shutting down plant to work on low lift pump 1/2 as well as tying in hi lift pump 4. Plant will not be on utility power but PAC panels will be active so no comms issues expected. Phil D will call back when transferring back to utility power and directed to disregard alarms on site while they complete their work on site. | All Water System ROC General | 2025-11-25
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-25
ROC | November | STETBR- Tower level lo alarm came in STW12-Placed wells 1/2 in manual and started well 1 STW3- Started Well 3 in manual as per interim | All Water System ROC General | 2025-11-28
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-22
ROC | November | GWTP- Joe M called back and directed to disregard MUA unit 1 Diff Pressure alarm | All Water System ROC General | 2025-11-28
ROC | November | STETBR - Tower level low alarm. Placed STW12 well 2 pump and STW3 pump man/on for ET fill cycle. | All Water System ROC General | 2025-11-26
ROC | November | NMTKBS- Ian W working on OIT. Disregard Heartbeat Alarm. | All Water System ROC General | 2025-11-20
ROC | November | AUW57- Station turbidity hi alarm came in. Placed well in man off as only one silicate pump available. Emailed Central Water team | All Water System ROC General | 2025-11-19
ROC | November | aAUVCAD1/aNMMCBS1/aNMTKBS/aNRETCR1/aAUETFC - Kevin W. is rebooting each modem and PAC Communication alarms will come in. 11:41 - All PAC Communications alarms have been cleared | All Water System ROC General | 2025-11-26
ROC | November | RHPSPA - Rotate pump 3 to duty 1 and pump 4 duty 4 for instrumentation to work on pump 4. | All Water System ROC General | 2025-11-21
ROC | November | AUW57- Influent free Cl2 hi alarm on well start up trends recovered after 3 mins alarm cleared | All Water System ROC General | 2025-11-19
ROC | November | STRS48- Chlorine Gas Detector HiHi, Scrubber Running. Called Joe M. He is onsite with Jackie S working on it. | All Water System ROC General | 2025-11-19
ROC | November | SHTP - Filter 1 turbidity hi, back to normal range preparing for backwash | All Water System ROC General | 2025-11-22
ROC | November | GWTP- Raw Water Total Chlorine Res HiHi Alarm. Notified Stephen B. He will look into it. | All Water System ROC General | 2025-11-19
ROC | November | VNRSKS- Historian heartbeat alarm cleared | All Water System ROC General | 2025-11-19
ROC | November | QVW12- Alex B on site to troubleshoot chlorinator 2 and run generator | All Water System ROC General | 2025-11-20
ROC | November | NBW2 - Joe W on site to a chlorine gas leak alarm test. | All Water System ROC General | 2025-11-25
ROC | November | YWS+NYWs normal | All Water System ROC General | 2025-11-20
ROC | November | MKRSEM - Jack P requested disregard Free chlorine Residual fault alarm for 20 minutes. He is sampling. | All Water System ROC General | 2025-11-26
ROC | November | AUVCBS - PAC communication failure alarm, was able to clear alarm in a few minutes. | All Water System ROC General | 2025-11-26
ROC | November | NBET27 - Outlet Free CL2 Residual hi alarm came in. Checked site. System is filling. Called Joe W. who will investigate further and give the ROC a call back | All Water System ROC General | 2025-11-26
ROC | November | NMVCIB, Placed flow rate back to 80L/sec NMVCBA, Placed flow rate back to 40L/sec | All Water System ROC General | 2025-11-21
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-21
ROC | November | Ethan U signing in | All Water System ROC General | 2025-11-21
ROC | November | ARPS- Total ammonia lolo alarm came in. Called Peel spoke with David they have dispatched an operator to check site and verify residuals with grab samples | All Water System ROC General | 2025-11-20
ROC | November | NMTKKC - Chloramine analyzer offline alarm came in. Spoke to Joe D. who informed he triggered that alarm | All Water System ROC General | 2025-11-26
ROC | November | AUW57 - Divya informed that well 57 is still OOS due to the motor Adeela Khan signing out | All Water System ROC General | 2025-11-26
ROC | November | YWS + NYWS Normal Christian Van Beek singing out. | All Water System ROC General | 2025-11-27
ROC | November | BVPS - Discharge total and free cl LoLo, OOR. Jack P. informed tripped GRI breaker, troubleshooting on site. STRS48 - Lee F. changing wires affecting cl analyzers. Placed W56 and HLP man/off | All Water System ROC General | 2025-11-27
ROC | November | NBW5 - Kingsley M finished on site and requested that NBW5 be placed into auto mode. Made changes. | All Water System ROC General | 2025-11-24
ROC | November | GWTPLL - Low lift pump 2 disch failed to open. Plant is off. | All Water System ROC General | 2025-11-21
ROC | November | BLETNL- Jackie S onsite for chlorine analyzer maintenance, exercising valves and testing temperature alarms. | All Water System ROC General | 2025-11-20
ROC | November | STW3- Travis W. onsite for chlorine leak detection test. | All Water System ROC General | 2025-11-20
ROC | November | Connor Smith signing in 4C Clear | All Water System ROC General | 2025-11-22
ROC | November | NBET27 - OUtlet total Cl2 hihi. Followed up with Jacob M regarding CL2 total. Free took a bit more of a dip but withing range. Okay to disregard for the weekend as long as free remains withing range. Will continue to monitor | All Water System ROC General | 2025-11-22
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-22
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-22
ROC | November | NBW3 - Influent free hi, came up high on startup. Dropped to normal range | All Water System ROC General | 2025-11-23
ROC | November | NBW2- Kingsley M is resetting OIT. Placed well in man/off | All Water System ROC General | 2025-11-24
ROC | November | MAPS PD7- Kyle R req p2 to be placed in man/off in order to work on rotorque. Placed P2 in man/off and rotated duty 1 to pumps 3/4 | All Water System ROC General | 2025-11-25
ROC | November | GWTP- Stephen B. Finished onsite. Requested to deactivate duty. | All Water System ROC General | 2025-11-26
ROC | November | Adeela Khan signing in | All Water System ROC General | 2025-11-26
ROC | November | STERTL- Tower Lo level alarm came in. Jack P on site at STPSMR will be placing pumps back in auto BLW3- Joe M req well be placed in man/on. Placed P3 in man/on | All Water System ROC General | 2025-11-19
ROC | November | Carter Dunn Signing Out | All Water System ROC General | 2025-11-21
ROC | November | YWS + NYWS Normal NMETIB, Activated D1 to have towers offset | All Water System ROC General | 2025-11-20
ROC | November | NMW12 - Treated Total Chlorine Lo alarm came in. Checked site. Wells are not running, and water is not being directed to users | All Water System ROC General | 2025-11-21
ROC | November | NMW15 - Influent Free Chlorine Lo alarm came in. Checked site. Influent levels came back to optimal range and alarm has been cleared | All Water System ROC General | 2025-11-21
ROC | November | STETBR - Tower Level Lo alarm came in. Closed VC FCV1 and placed the STPSTL pumps back to auto | All Water System ROC General | 2025-11-21
ROC | November | VNETFD, Activated D1 | All Water System ROC General | 2025-11-19
ROC | November | Christian Van Beek signing out. | All Water System ROC General | 2025-11-24
ROC | November | Angelica Chepiga signing in, weather -2C | All Water System ROC General | 2025-11-28
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-21
ROC | November | STPSTL - No flow alarm on both pumps. Both pumps not available. Able to reset alarm and have pump 2 duty 1. QVW34 - Place well 3 back in auto | All Water System ROC General | 2025-11-23
ROC | November | STW12 - Place well 1 man/on STW3 - Place well man/on | All Water System ROC General | 2025-11-23
ROC | November | HLETYS- Activated duty Interim Procedure | All Water System ROC General | 2025-11-25
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-26
ROC | November | AUW57- Well did not pass contact tank before shutting down. Placed in man/on as per Ben H. Will placed in man/off when contact tank passes 17:03-AUW57- Turbidity issues resolved. Placed well back in auto | All Water System ROC General | 2025-11-19
ROC | November | GWTP, Make up air unit 1 Diff Pressure, Notified Joe M, he will look into it | All Water System ROC General | 2025-11-28
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-30
ROC | November | Connor Smith signing out | All Water System ROC General | 2025-11-22
ROC | November | STW12/SW3 - Place wells back in auto as Bethesda tower duty off | All Water System ROC General | 2025-11-23
ROC | November | GWTP- Eric S on site with Stephen B to work on raw total Cl2 analyzer 13:18- GWTP- Patrick F called and directed to disregard train 2 alarms for low lift testing | All Water System ROC General | 2025-11-19
ROC | November | NMW15- Jay G on site to test Cl2 leak test will Notify ROC when done on site | All Water System ROC General | 2025-11-20
ROC | November | Connor Smith signing out | All Water System ROC General | 2025-11-20
ROC | November | QVW12- Influent free Cl2 hihi alarm came in. Continued to monitor slowly coming down adjusting Chlorinator dosing factor from 115 to 112% to help recover | All Water System ROC General | 2025-11-28
ROC | November | AUETFC- Multi Function Analyzer Fault Alarm. Notified Jerry Z. He is onsite and will look into it. | All Water System ROC General | 2025-11-19
ROC | November | HLW2 - Place well man/off HLW2 VC - Place man/close for EG watermain replacement work on Yonge SHETCS - Activate duty 1 for interim | All Water System ROC General | 2025-11-25
ROC | November | YWS + NYWS Normal RHMCMD - Place man/close | All Water System ROC General | 2025-11-25
ROC | November | QVW12 - Donald M on site for station checks and activated QVW1 in manual mode. | All Water System ROC General | 2025-11-24
ROC | November | AUW5 - Divya P will attend site for station check. | All Water System ROC General | 2025-11-26
ROC | November | NMW15- influent free Cl2 lo alarm came in. Reset as trends recovered | All Water System ROC General | 2025-11-20
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-25
ROC | November | VNRSKS- Historian heartbeat alarm came in. Trends flatlined. Notified Kyle C will take a look on SCADA | All Water System ROC General | 2025-11-19
ROC | November | MARS- Jacob M and Joe W onsite for chamber inspections. Disregard temp, intrusion and flood alarms. | All Water System ROC General | 2025-11-20
ROC | November | Carter D Signing In | All Water System ROC General | 2025-11-24
ROC | November | Adeela Khan signing in. Weather: 0C and Flurries | All Water System ROC General | 2025-11-27
ROC | November | NBW3 - Influent free chlorine lolo upon start up. Reading came back. Able to clear AURSBS - Activate duty 1 | All Water System ROC General | 2025-11-25
ROC | November | AUPSWS- Will M on site to test hi lo temp alarm flood alarm and run generator MAPS PD7- Kyle R on site with Dan B to replace rotorque valve on P1. P1 is currently man/off BLW3- Jackie S and Joe M on site to test Cl2 leak alarm and run scrubber. Will be replacing a line later on which will require well to be man off. Notified Jackie S BLETNL is currently only at 59% with BLW12 OOS for contractors. 10:03- BLW12- Jackie S call back and will defer Cl2 leak test and any workorders requiring well shutdown until BLW12 is back online | All Water System ROC General | 2025-11-25
ROC | November | NMVCBA- Placed valve back into auto | All Water System ROC General | 2025-11-26
ROC | November | GRTPLL - Low Lift Discharge Total Chlorine HiHi alarm came in. Checked site. Shift report directs to monitor for 30 mins and levels should come back to optimal range. Will monitor 14:30 - Total Chlorine levels have come back down to optimal range | All Water System ROC General | 2025-11-26
ROC | November | YWS + NYWS NORMAL Angelica Chepiga signing out. | All Water System ROC General | 2025-11-26
ROC | November | Angelica Chepiga signing in | All Water System ROC General | 2025-11-27
ROC | November | SHTP/SHETCS - Site Hydro Power Fail alarms came in. Checked site. Called David T. who is on site and was able to clear alarms. UV's were not affected | All Water System ROC General | 2025-11-26
ROC | November | AUPSOH - Ricardo L. and Redempto L. are on site for annual calibrations | All Water System ROC General | 2025-11-26
ROC | November | GWTP - Stephen B requested Activate Duty 1, Disable Low lift chlorination for Mussel control, Chlorinator 6 dosage factor from 57 to 58%. | All Water System ROC General | 2025-11-26
ROC | November | NMETHW - Deactivated duty 1 | All Water System ROC General | 2025-11-27
ROC | November | MMW1 - Historian Heartbeat. Talah H. working on OIT | All Water System ROC General | 2025-11-27
ROC | November | GWTP - Patrick F onsite GAC1 backwashing tank, disregard GAC1 | All Water System ROC General | 2025-11-21
ROC | November | ARPS, Jerry from OCWA called, their work is now finished, they will be starting there pumps back up | All Water System ROC General | 2025-11-27
ROC | November | STETTL/STETBR- Andrew from OCWA flushing in zone 1/2 KSTP- Filter 1 Effl Fault alarm came in interlocking filter 1. Notified Joe M. directed to reset alarm. | All Water System ROC General | 2025-11-27
ROC | November | QVW12- Divya P req P1 be placed in man/off for utility transfer | All Water System ROC General | 2025-11-27
ROC | November | NBW37 - Jordan B on site to complete a diesel generator test and PRV flushing. | All Water System ROC General | 2025-11-25
ROC | November | NBW3- Placed back in auto NBW5- Kingsley M working on OIT. Placed well in man/off | All Water System ROC General | 2025-11-24
ROC | November | Ethan U signing in Weather 6. | All Water System ROC General | 2025-11-24
ROC | November | MKRSEM - Request TO (Zhoran) for 2 pumps | All Water System ROC General | 2025-11-24
ROC | November | HLW2 - VC - Downstream pressure hihi came in. Able to clear, will monitor | All Water System ROC General | 2025-11-25
ROC | November | YWS+NYWS Normal Adam Button signing out | All Water System ROC General | 2025-11-27
ROC | November | STETBR - Level Hi alarm, STW12, STW3 placed back to auto. | All Water System ROC General | 2025-11-28
ROC | November | YWS + NYWS NORMAL | All Water System ROC General | 2025-11-29
ROC | November | HLW2 - Combined Chlorine and Treated Total Chlorine Lo alarms came in. Well is local/off and water is not being directed to users | All Water System ROC General | 2025-11-29
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-29
ROC | November | NMW12 - Effluent Free Chlorine Fault alarm came in. Checked site. Wells were not active and water was not being directed to users. Alarm cleared within a few mins | All Water System ROC General | 2025-11-30
ROC | November | QVW12- Artour L on site for temporary generator tie in. Will need well man/off during testing later on today | All Water System ROC General | 2025-11-27
ROC | November | GWTP - Artour L finished at site | All Water System ROC General | 2025-11-21
ROC | November | Ethan Ullalkar signing out. | All Water System ROC General | 2025-11-22
ROC | November | Ethan U signing in Weather 4. | All Water System ROC General | 2025-11-23
ROC | November | GWTPLL - Low lift pump 2 hydraulic vlv fail to open. Duty 1 off. Known issue that persists. SHTP - Filter 2 turbidity hi, trends show spike in reading before coming within normal range again | All Water System ROC General | 2025-11-23
ROC | November | MKETFA - TO (Mehdi) informed they are exercising valve, may see hi flow leaving tower for a minute, pumps still in auto. | All Water System ROC General | 2025-11-23
ROC | November | GWTP, Stephen B/Phil D is finished on site | All Water System ROC General | 2025-11-24
ROC | November | NBET27, Parth P doing annual calibrations on site 14:35, Parth P called back, notified Cole W on the work he was doing, requested to place the altitude valve man/closed, Cole W said its good to go. Parth P called back to say West Team Lead agrees with the process. Placed Altitude valve man/closed. Will place it back to auto once Parth P is finished his work | All Water System ROC General | 2025-11-25
ROC | November | STRS48, Dan Z on site, running the Cl2 system in manual | All Water System ROC General | 2025-11-25
ROC | November | ARPS- Martin from Peel called. Will need to shut down pumps for 10-15 minutes due to backup power issue. 20:12- Martin called back and has started one pump back up. Back to normal operations. | All Water System ROC General | 2025-11-25
ROC | November | MTW12 - Joe M onsite for step test for well 1. While running may see chemical pumps OOS. Disregard alarm. Test will be until 13:00 | All Water System ROC General | 2025-11-21
ROC | November | NBW3 - Joe W. is on site and is aware of the influent Free Chlorine LoLo level lockout | All Water System ROC General | 2025-11-26
ROC | November | MKPSSA, Jack P on site, testing flood alarm and running gen | All Water System ROC General | 2025-11-28
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-30
ROC | November | NBW3 - Influent free chlorine HiHi alarm. Checked site, the well recently activated in schedule mode. Trending shows a spike of the influent free chlorine which returned to normal range within two reading intervals. Reset alarm. | All Water System ROC General | 2025-11-24
ROC | November | YWS + NYWS Normal Christian Van Beek signing out. | All Water System ROC General | 2025-11-19
ROC | November | Carter Dunn Signing In, 4D/Clear | All Water System ROC General | 2025-11-20
ROC | November | MAPS PD7, Deactivated D1 because MARS is continuing to drop. 3 pumps are running at ARPS and MAPS PD8 is currently deactivated, if level continues to drop, will take further action. Currently monitoring | All Water System ROC General | 2025-11-20
ROC | November | AUW57 - Combined Chlorine Lo alarm came in. Checked site. Well is not active and water is not being directed to users | All Water System ROC General | 2025-11-30
ROC | November | RHMCMD - Placed Valve back to auto | All Water System ROC General | 2025-11-30
ROC | November | STW3, Travis W on site, cleaning the turbidity analyzer | All Water System ROC General | 2025-11-28
ROC | November | Connor Smith signing out | All Water System ROC General | 2025-11-19
ROC | November | NMVCDD- Valve chamber flood alarm. Notified Dwayne L. Will check with linear team | All Water System ROC General | 2025-11-19
ROC | November | STETBR- Tower lo alarm came in. STW12- Placed well 1 in man/on STW3- Placed Well3 in man/on SHTP- Reservoir lo level alarm came in. Deactivated D1 at SHETCS | All Water System ROC General | 2025-11-24
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-27
ROC | November | NMW136, Combined Cl2 lolo//Treated Total Cl2 lolo, wells aren't running currently, trends show an abnormal spike that occurred, will monitor the site. If residuals don't recover, will place wells man/off for the night and send an email to the operator | All Water System ROC General | 2025-11-20
ROC | November | BLW12- Joe M working on turbidity meter | All Water System ROC General | 2025-11-19
ROC | November | RHPSPA - Red B, Parth P, Rick L onsite for annual calibrations | All Water System ROC General | 2025-11-21
ROC | November | MAPS PD7, Dan B on site, is currently working on pump 1, he will be turning pump 1 on/off to make sure everything is working properly. Placed pumps 2/3 man/off just to make sure they all dont start up QVW12, Artour L is leaving site | All Water System ROC General | 2025-11-27
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-19
ROC | November | RHRSWA, Historian Heartbeat Alarm, Trends are still available, notified Kyle C but no response, will call back in 10 minutes 20:29, Kyle C called back, he is looking into it CMU5: W11456171 | All Water System ROC General | 2025-11-19
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-19
ROC | November | STPSMR- Cl2 leak alarm came in and emergency system active. Joe M and Jackie P on site for maintenance. STETBR- Tower hi level alarm came in. Left STW12/3 in man on due to work going on at STPSMR as both STW12 are man/on with D1 active in zone 2 | All Water System ROC General | 2025-11-19
ROC | November | HLW2- FCV2 changed setpoints from 25L/s to 30L/s | All Water System ROC General | 2025-11-20
ROC | November | NMW15- Jason G finished onsite NMW12- Jason G heading to site for work on turbidimeter and testing Cl leak. | All Water System ROC General | 2025-11-20
ROC | November | YWS + NYWS Normal RHMCMD - Man/close | All Water System ROC General | 2025-11-23
ROC | November | AUW57- Influent Free Chlorine LoLo. Well is interlocked. Notified Jerry Z. He is onsite and aware. | All Water System ROC General | 2025-11-19
ROC | November | STETTL- Travis W onsite for workorders including analyzer maintenance, health and safety and altitude valve work. | All Water System ROC General | 2025-11-19
ROC | November | NBW3- Influent free Cl2 hi alarm on well start up recovered after 3 mins alarms cleared | All Water System ROC General | 2025-11-20
ROC | November | HLETYS- Post inj combined Cl2 hi alarm came in. Cleared upon acknowledgment | All Water System ROC General | 2025-11-20
ROC | November | STETBR//RHRSWA, Talha H resetting OITs | All Water System ROC General | 2025-11-27
ROC | November | GWTP- Sutton Header Fluoride Lo Alarm. Notified Patrick F. | All Water System ROC General | 2025-11-20
ROC | November | YWS + NYWS Normal QVW12, Adjusted Chlorinator 1 dosing factor from 115 to 111% | All Water System ROC General | 2025-11-20
ROC | November | RHMCMD - Man/close | All Water System ROC General | 2025-11-22
ROC | November | STW12/STW3 - Place wells back in auto as Bethesda tower duty off | All Water System ROC General | 2025-11-22
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-23
ROC | November | NMW12 - Effluent free chlorine fault alarm. Duty not active, no water directed to users. Alarm cleared in a few minutes. | All Water System ROC General | 2025-11-28
ROC | November | BVPS - Toronto Water (Mehdi) called about an outstanding UPS failure on his end from 12:15 today. Checked site. Nothing on York Region's side. Checked past logs which indicated there was a tripped breaker earlier in the day but was resolved within an hour. Mehdi informed that this does not affect operations and was just calling to confirm that everything was okay on YR's side | All Water System ROC General | 2025-11-27
ROC | November | STETBR - Tower Level Hi alarm came in. Placed STW1 and STW3 back to auto, as per interim | All Water System ROC General | 2025-11-27
ROC | November | Adeela Khan signing out | All Water System ROC General | 2025-11-28
ROC | November | NBW5 - Eric S. is finished on site and will leave silicate pump man/off as operations will need to take a look | All Water System ROC General | 2025-11-21
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-22
ROC | November | YWS+NYWS normal Adam Button signing out | All Water System ROC General | 2025-11-20
ROC | November | SHETCS- Hypo Pump 1,2 Failed to Start. Cleared alarms and hypo pump 1 started up in duty 1. | All Water System ROC General | 2025-11-23
ROC | November | AUPSRR - Post-inj free chlorine hihi, spike in trend dropped back to normal range | All Water System ROC General | 2025-11-23
ROC | November | SHTP- Well 2 Pump Uncomm Start Alarm. Wells 3,4 running in duty 1,2. Cleared alarm. | All Water System ROC General | 2025-11-22
ROC | November | NMETIB- Activated D1 at 60% to offset from NMETHW as per shift report | All Water System ROC General | 2025-11-24
ROC | November | YWS+ NYWS NORMAL | All Water System ROC General | 2025-11-28
ROC | November | YWS + NYWS NORMAL | All Water System ROC General | 2025-11-29
ROC | November | YWS + NYWS NORMAL | All Water System ROC General | 2025-11-29
ROC | November | SHETCS - Hypo Pump 1 Uncommanded stop alarm came in. Checked site. Noticed that Hypo pump 2 is man/off. Ack/reset alarm and hypo pump 1 is running again | All Water System ROC General | 2025-11-29
ROC | November | NMW15- Influent free Cl2 lo alarm came in on well start up. Trends recovered after 3 mins alarm cleared | All Water System ROC General | 2025-11-28
ROC | November | YWS + NYWS NORMAL | All Water System ROC General | 2025-11-29
ROC | November | MKRSEM - Level Lo alarm came in. Called Toronto Water (Peter) and requested 2 pumps on 04:31 - Called Toronto Water (Peter) and requested to stop pumping to reservoir | All Water System ROC General | 2025-11-30
ROC | November | NBET27- Total Cl2 lo alarm outstanding Notified Jake M. Directed to disregard but to call for free lo alarms | All Water System ROC General | 2025-11-24
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-23
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-23
ROC | November | NBET27 - Outlet Total CL2 Lo alarm came in. Checked site and noticed that the total chlorine dipped just below the lo level. Noticed duty is close to activating. Activated duty 1. Will continue to monitor site | All Water System ROC General | 2025-11-24
ROC | November | YWS + NYWS normal | All Water System ROC General | 2025-11-30
ROC | November | AURSBS - Activate duty 1 | All Water System ROC General | 2025-11-25
ROC | November | NBW5 - Eric S onsite working on silicate pump 2 | All Water System ROC General | 2025-11-21
ROC | November | Stouffiville Zone 2 - Rob P & Jon responded to watermain leak in area. CMU = 11461708 | All Water System ROC General | 2025-11-21
ROC | November | NMW136 - Combined Chlorine Lo alarm came in. Checked site. Well 16 is running. After 5 mins, combined chlorine came back to optimal range and alarm has cleared | All Water System ROC General | 2025-11-21
ROC | November | NMETIB- Activated D1 at 52% as per shift report to offset from NMETHW | All Water System ROC General | 2025-11-25
ROC | November | NMETIB - Deactivate duty 1 as Harry Walker is now active | All Water System ROC General | 2025-11-22
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-22
ROC | November | KBPS27- Cole W on site. Notified ROC card reader is not working and will have security arm site remotely | All Water System ROC General | 2025-11-28
ROC | November | GWTP- Make up air unit diff pressure alarm came in. Notified Patrick F will take a look on site SHTP- Cole W on site to work on Cl2 system Plant will be off for work | All Water System ROC General | 2025-11-28
ROC | November | GWTPP1, Kingsley M doing a server reset | All Water System ROC General | 2025-11-25
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-23
ROC | November | ARPS, David from OCWA called, pumps are back to normal operation | All Water System ROC General | 2025-11-28
ROC | November | KSTP- Fin Water Fluoride Res/Tot Cl2 Res Fault Alarms. Plant recently deactivated, disregard alarms as per SCADA review. | All Water System ROC General | 2025-11-28
ROC | November | Access York, Denise Di Luca from Access York called, said a customer is saying there was a main break happening at 3300 Rutherford Road, Vaughan, right at the Dollerama in the plaza. This is on private property and the leakage is going onto Rutherford. Notified Denise L to contact Vaughan as this would be there issue. Contacted Roads Department Mandy and asked for her to look into this, she notified the ROC that she doesn't see anything but will look around just to be sure. Contacted Dwayne L of the mainbreak, directed to disregard as we dont have anything in that plaza. Notified Vaughan Supervisor Nolan S of the situation, he will look into it further. Roads Dispatch = Mandy Access York = Denise Di Luca Vaughan = Nolan S | All Water System ROC General | 2025-11-24
ROC | November | STETTL - Outlet free chlorine. Joe M called to inform that the analyzer reading is accurate. Joe directed to disregard the outlet free chlorine hi alarm but call if the HiHi alarm triggers. | All Water System ROC General | 2025-11-26
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-27
ROC | November | MARS- Interconnect valve uncommanded close alarm came in. Notified Cole W. Reset alarm valve is normally manual open during cell 2 isolation | All Water System ROC General | 2025-11-27
ROC | November | NMETIB- Activated duty | All Water System ROC General | 2025-11-29
ROC | November | YWS + NYWS normal | All Water System ROC General | 2025-11-30
ROC | November | YWS + NYWS normal | All Water System ROC General | 2025-11-30
ROC | November | AUW14 - Divya called and directed to place the wells back to auto | All Water System ROC General | 2025-11-26
ROC | November | BLW12 - Joe M. called to inform that the wells will be offline until approximately 6PM | All Water System ROC General | 2025-11-26
ROC | November | AURSBS - Activated D1. | All Water System ROC General | 2025-11-26
ROC | November | MAPS PD7- Placed P1-3 back in auto and put P1 back in duty rotation | All Water System ROC General | 2025-11-27
ROC | November | AUW57- Influent free lolo/lolo switch alarm came in. Well man/off no water directed to users | All Water System ROC General | 2025-11-27
ROC | November | AUW57 - Combined Chlorine Lo alarm came in. Checked site. Well recently activated. Combined levels took a dip but starting to increase. Treated Total Chlorine levels are within range. Will continue to monitor site. 21:20 - Combined chlorine levels have come back to optimal range and alarm has been cleared | All Water System ROC General | 2025-11-27
ROC | November | NMW15- Influent free Cl2 lo alarm came in on well start up. Trends recovered after 3 mins alarm cleared NMW12- Influent free Cl2 hi alarm came in on well start up. Trends recovered after 6 mins alarms cleared | All Water System ROC General | 2025-11-19
ROC | November | Connor Smith signing in 0C Snowy | All Water System ROC General | 2025-11-30
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-30
ROC | November | GWTP- Stephen B placed UVs and high lifts in man/off to cut power to plant. Directed to disregard alarms from plant for duration of work and will call when done. Network will not be affected | All Water System ROC General | 2025-11-24
ROC | November | YWS + NYWS Normal Connor Smith signing out | All Water System ROC General | 2025-11-23
ROC | November | GWTP - ZW5 Channel 1 and 2 Parts Count OOR alarms came in. Checked shift report. Called Jack P. who will take a look on SCADA and will give a call back 18:39 - Jack called back to inform that these alarms can be disregarded for the night. Jack also directed to place train 5 off for the night once it finishes its backwash 18:43 - Backwash completed and placed train off, as per Jack P #CONSULT | All Water System ROC General | 2025-11-23
ROC | November | QVW12 - Divya P. informed contractors on site working on generators, he will man/stop wells for them and place back in auto when they're done | All Water System ROC General | 2025-11-27
ROC | November | QVW34 - CL2 Emergency Valve Closure Active, Chlorine Room Gas Leak, Chlorine Room Gas Level HiHi alarms came in. Checked site. Wells are interlocked. Wells were not running and water is not being directed to users. Called Jerry Z. who informed he will attend site but will need a second operator. Called Joe M. who will attend site also. CMU5 Created W11473466 09:00 - Alarms cleared #CONSULT #CMU5 | All Water System ROC General | 2025-11-27
ROC | November | Adam Button signing in -2 Clear | All Water System ROC General | 2025-11-27
ROC | November | MKETFA - Ahmad from YR police on site./ wrong book | All Water System ROC General | 2025-11-26
ROC | November | GWTP - Train 5 Backpulse Uncommanded open alarm came in. Stephen informed he is on site troubleshooting train 5 | All Water System ROC General | 2025-11-26
ROC | November | GWTP- Low lift 1/4 hydraulic valve fail to open. Notified Phil D will investigate AUW57- Tyler S on site to trouble shoot well motor issues. Req well 5 in man/off for work. Placed in man/off | All Water System ROC General | 2025-11-24
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-27
ROC | November | NMETIB - Deactivated Duty 1 to offset with NMETHW. | All Water System ROC General | 2025-11-28
ROC | November | RHMCMD- Placed valve back into auto | All Water System ROC General | 2025-11-20
ROC | November | ARPS- Jerry from Peel called to inform ROC they bare ready for the temporary shutdown. Notified Jerry MARS is at an okay level for temporary stoppage in pumping RHRSTR- Activated D1 VNRSKS- Deactivated D1 | All Water System ROC General | 2025-11-27
ROC | November | QVW34- Influent free Cl2 hi alarm. Recovered after 3 mins. Cleared alarm | All Water System ROC General | 2025-11-27
ROC | November | NMETIB- Activated D1 at 66% to offset from NMETHW as per shift report | All Water System ROC General | 2025-11-28
ROC | November | MKETFA, Rob P is leaving site, site is back to normal operation, Toronto valving is back to normal operation MARS, Notified Toronto operator Paul to go back to normal flow | All Water System ROC General | 2025-11-27
ROC | November | Adam Button signing in -3C Clear | All Water System ROC General | 2025-11-28
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-30
ROC | November | GWTP - Stephen B called to inform that they are de-activating the plant for scheduled work and to disregard all alarms from site. Hub 1 Server - Chris S is on site at GWTP with Stephen B and stated that communications issues may arise. Chris S will be monitoring from GWTP and has requested no calls for these communication failures. | All Water System ROC General | 2025-11-24
ROC | November | RHRSWA, Parth P is leaving site | All Water System ROC General | 2025-11-27
ROC | November | QVW12 - Chlorinator 2 dosing factor 107%, looks like influent chlorine residual stabilized after second duty pump stopped. All alarms cleared. Will monitor. | All Water System ROC General | 2025-11-28
ROC | November | MTW12- Influent Free Chlorine LoLo. Jackie S onsite troubleshooting. | All Water System ROC General | 2025-11-19
ROC | November | GWTP- Patrick F on site backwashing GAC 2 | All Water System ROC General | 2025-11-20
ROC | November | HLETYS - Cole W. called to inform that he deactivated duty | All Water System ROC General | 2025-11-26
ROC | November | Gluzen Ramos Ong signing out | All Water System ROC General | 2025-11-27
ROC | November | BVPS, Jack P on site, doing surge valve testing and flood alarm testing. Placed pumps 1/2/3/4 man/off so nothing triggers while Jack P is on site | All Water System ROC General | 2025-11-28
ROC | November | BLW3 - Joe M and Jackie S on site to complete some pipe work on the effluent side of the system. The well will be OOS until the end of the day. BLETNL is continuing its deep cycle until MTW12 and MTW3 are placed back in service. | All Water System ROC General | 2025-11-25
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-20
ROC | November | BLW3 - Jackie S called to inform they are now completing the chlorine leak detection test at BLW3 and the alarms can be disregarded. | All Water System ROC General | 2025-11-25
ROC | November | AUW57- Ryan B req CMU5 for outstanding turbidity issue overnight created CMU5 W11475625 #CMU5 | All Water System ROC General | 2025-11-28
ROC | November | NMETIB - Activate duty 1 to help offset with Harry Walker | All Water System ROC General | 2025-11-22
ROC | November | HLETYS - Post-inj combined chlorine hi, within normal range. Hi triggered upon startup, back within normal range next reading | All Water System ROC General | 2025-11-22
ROC | November | QVW12 - Effluent free chlorine Hi alarm, adjusted chlorine pump 2 dosage from 107 to 105%. | All Water System ROC General | 2025-11-28
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-29
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-29
ROC | November | MAPS PD7- Jake M done on site. P4 working okay. VNETFD- Joe W and Jake on site to perform JHS inspections, VC entries and will be testing temperature alarms | All Water System ROC General | 2025-11-20
ROC | November | STW12- Placed Well 1 in D1 placed in man/on STW3- Placed P3 in man/on as per interim | All Water System ROC General | 2025-11-20
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-21
ROC | November | MAPS/JFRS- Initiated Maple to Jefferson Feed. 01:59- Reverted Maple to Jefferson Feed | All Water System ROC General | 2025-11-23
ROC | November | NMETIB - Activate duty 1 | All Water System ROC General | 2025-11-23
ROC | November | AUW57- Dan B on site and has replaced motor on site and will be running well in manual to test it. Dan B will place well back in auto when done MKRSEM- Rob P called to inform ROC that they have isolate at 14 th avenue and contractors are working GWTP- Patrick F and Phil D are backwashing GAC 4 | All Water System ROC General | 2025-11-27
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-24
ROC | November | KSTP - Filter 1 Backwash is OOS alarm came in. Checked site. Plant is running. Filter 1 is interlocked due to backwash tank level hi. Called Jack P. who will take a look on SCADA 03:14 - Jack directed to place hi lift pumps man/off and to give him a call back if KSTKWP does not continue to fill #CONSULT | All Water System ROC General | 2025-11-24
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-24
ROC | November | ARPS- ROYKS to ROPKS comm fail alarm came in trends okay cleared alarm on site | All Water System ROC General | 2025-11-20
ROC | November | RHMCMD-Placed valve back into auto | All Water System ROC General | 2025-11-26
ROC | November | ARPS, Jerry from OCWA called, they are getting ready to turn off their pumps, gave him the confirmation that we are good on our end. Work should only take 20 minutes approx. MARS = 78%//5.4m AURSBS = 70%//4.21m VNRSKS = 69%//3.29m MARS, Notified Paul from Toronto to increase the flow to the res GWTP, Jeff from property services is on site testing fire alarms | All Water System ROC General | 2025-11-27
ROC | November | NMVCBA- Changed valve setpoints from 80L/s to 40L/s NMVCIB- Changed valve setpoints from 40L/s to 80L/s NMETIB- Deactivated D1 to offset from NMETHW as per shift report QVW34- Placed Well 3 in auto | All Water System ROC General | 2025-11-27
ROC | November | Adeela Khan signing in. Weather: -1C and Cloudy | All Water System ROC General | 2025-11-29
ROC | November | HLW1 - Combined Chlorine Lo alarm came in. Checked site. Well recently activated. Trends indicate a slight dip. After 3 mins, level came back to optimal range and alarm has cleared | All Water System ROC General | 2025-11-29
ROC | November | GWTP - Sutton Header Fluoride Lo alarm came in. Checked site. Noticed levels have come back to optimal range | All Water System ROC General | 2025-11-21
ROC | November | ARPS - David from OCWA called to inform that he will be switching the transformer which requires YR pumps be off for half an hour 11:57 - Called Toronto Water (Mehdi) to increase to max flow at MARS 12:17- David from OCWA called to inform that the transformer switch was successful and will be placing the ARPS back to auto shortly 13:59 - Called Toronto Water (Mehdi) and requested to go back down to normal flow | All Water System ROC General | 2025-11-21
ROC | November | SHETCS - Deactivate tower to help fill res. | All Water System ROC General | 2025-11-24
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-25
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-26
ROC | November | NMETHW- Activated D1 NMETIB- Deactivated D1 to offset from NMETHW | All Water System ROC General | 2025-11-19
ROC | November | NMVCDD- Dwyane L confirmed Linear team is on site for PMs KSTP- Yash S and Divya P on site to work on fluoride pumps high lifts are in man/off | All Water System ROC General | 2025-11-19
ROC | November | SHETCS - Hypo pump 1 uncommanded stop alarm. Was able to clear alarm, Hypo pump 1 restarted, will monitor. | All Water System ROC General | 2025-11-28
ROC | November | SHETCS - Hypo pump 1 uncommanded stop alarm. Cleared alarm, Hypo pump 1 restarted, will monitor. | All Water System ROC General | 2025-11-28
ROC | November | MKRSEM - Reservoir 1 Level Lo alarm came in. Called Toronto Water (Mehdi) and requested two pumps on to help fill reservoir | All Water System ROC General | 2025-11-21
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-21
ROC | November | Connor Smith signing in 6C Clear | All Water System ROC General | 2025-11-21
ROC | November | MARS- Cell1 (North) Lvl Hi Alarm. AURSBS- Activated duty | All Water System ROC General | 2025-11-22
ROC | November | QVW12 - Generator Fault alarm came in. Checked site. Generator is not running and site is connected to hydro power. Called Jerry Z. Jerry directed to leave the alarm outstanding for the night and he will inform the team tomorrow. #CONSULT | All Water System ROC General | 2025-11-27
ROC | November | KLET27, FMC called, notified them to call security | All Water System ROC General | 2025-11-27
ROC | November | NMVCBA- Changed valve setpoints from 40L/s to 80L/s NMVCIB- Changed valve setpoints from 80L/s to 40L/s | All Water System ROC General | 2025-11-27
ROC | November | AUW57, Influent Free Cl2 lolo, Abnormal dip occurred, will continue to monitor | All Water System ROC General | 2025-11-21
ROC | November | MARS- Cell1 (North) Lvl Hi Alarm RHMDMD- Placed in manual RHRSTR- Deactivated duty | All Water System ROC General | 2025-11-23
ROC | November | STW12 - Dan Z. called to inform that she is on site and will be cleaning the turbidity analyzers | All Water System ROC General | 2025-11-21
ROC | November | AUETFC, Parth P is leaving site, heading to AUETOH to work on flow meters 11:02, AUPSOH. Parth P/Rick L on site, working on flow meters | All Water System ROC General | 2025-11-28
ROC | November | NMETHW, Deactivated D3 | All Water System ROC General | 2025-11-19
ROC | November | NMVCBA- Placed valve manual 40L/s to help keep NMETIB and NMETHW offset. | All Water System ROC General | 2025-11-22
ROC | November | AUW57 - Station Turbidity Hi alarm came in. Checked site. Rotated silicate pump duty so pump 1 is in duty 1. Will monitor 22:05 - After 30 mins, turbidity levels have not gone back to optimal range. As this is a duty 2 well, placed well man/off. Will send an email to the central team | All Water System ROC General | 2025-11-27
ROC | November | YWS + NYWS Normal Carter D Signing Out | All Water System ROC General | 2025-11-28
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-23
ROC | November | SHTP- Changed reservoir start set point from 4.5m to 5.4m and stop setpoint from 5.0m to 5.7m. Changed SHETCS start D1 set point from 15% to 45% and stop set point from 45% to 80% as per interim | All Water System ROC General | 2025-11-24
ROC | November | Ethan Ullalkar signing out. | All Water System ROC General | 2025-11-25
ROC | November | Adam Button signing in | All Water System ROC General | 2025-11-25
ROC | November | MKRSEM- Free Chlorine Residual Fault Alarm. Disregard as per Jack P. | All Water System ROC General | 2025-11-19
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-28
ROC | November | VNPSCD - Post Injection Total and Combined Chlorine Hi alarms came in. Checked site. Levels came back to optimal range within 10 mins and alarms cleared 04:35 - Alarms came back in. Checked site. Nearing the hihi level. Called Jerry Z. who directed to shutdown the chemical system by placing the ammonia pumps in manual which interlocked the chlorine system and place 1 pump in manual at BVPS. This will help flush the lines. Jerry directed to do this for about 5 minutes until the post injection levels come back to normal range. 04:40 - Levels came back to optimal range and placed pump 2 at BVPS back to auto and alarms have cleared #CONSULT | All Water System ROC General | 2025-11-28
ROC | November | HLW2- Treated Free Chlorine HiHi Alarm. Value recovered. Cleared alarm. | All Water System ROC General | 2025-11-19
ROC | November | NBET27 - Parth P on site for annual calibrations. | All Water System ROC General | 2025-11-25
ROC | November | AUW14- Influent free Cl2 lo alarm came in didnt recover after 10 mins as Cl2 bank didnt switch over. Notified Jerry Z. Jerry Z will shutdown wells. Will be running generator on site STETBR- Tower level lo alarm came in. Placed STW12.STW3 in man/on as per interim | All Water System ROC General | 2025-11-25
ROC | November | AUPSWS, Will M is leaving site | All Water System ROC General | 2025-11-25
ROC | November | Toronto, Peter from Toronto called saying all their work is now finished, all valving has been reverted. MKPSSA, Placed pump 3 man/on to start drawing down MKRSEM | All Water System ROC General | 2025-11-25
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-25
ROC | November | GWTP- ZW5 Channel 1,2 Part Counts Out of Range. Notified Patrick F. Can disregard alarms SUETDR- Patrick F going to site for PMs including analyzer maintenance, temp alarms and health and safety. | All Water System ROC General | 2025-11-19
ROC | November | AUPSRR- Ben H notified ROC of town of aurora closed valve in system causing pressure issues AUPSRR. Valve was opened back up and issues have been resolved alarms cleared | All Water System ROC General | 2025-11-20
ROC | November | VNETFD- Jacob M and Joe W finished onsite NBW5- Eric S leaving site. Silicate Pump 2 will be OOS | All Water System ROC General | 2025-11-20
ROC | November | VNRSKS, Deactivated D1 to help allow MARS recover | All Water System ROC General | 2025-11-28
ROC | November | Adam Button signing in 1C Clear | All Water System ROC General | 2025-11-24
ROC | November | TPTH - Pressure HiHi and LoLo. Confirmed with Paul (Toronto), TO ops on site working on OIT and PITs RHRSWA - Parth P. finished working on cell 1 LIT, placed cell back to controlling | All Water System ROC General | 2025-11-27
ROC | November | Carter Dunn Signing In | All Water System ROC General | 2025-11-28
ROC | November | AUW57- Ryan B and Jay G on site AURSBS- Notified Jay G of D1 activation. Jay G not on site but will notified ops that are and gave the go ahead to start the duty early. | All Water System ROC General | 2025-11-25
ROC | November | Connor Smith signing in 6C Rain | All Water System ROC General | 2025-11-25
ROC | November | GWTP - Activated duty 1 to top up the towers for the interim procedure. | All Water System ROC General | 2025-11-25
ROC | November | YWS+NYWS normal | All Water System ROC General | 2025-11-19
ROC | November | NRETBR- Will M on site to test hi lo level alarms/ hi lo temp alarms as well as perform Cl2 analyzer maintenance | All Water System ROC General | 2025-11-20
ROC | November | GWTP- Sutton header fluoride lo alarm came in. No flow being directed to users as SUETDR D1 is not active Keswick line Fluoride is okay. Left alarm outstanding | All Water System ROC General | 2025-11-20
ROC | November | KCETDS- Outlet total Cl2 lolo alarm came in. Checked trends looks like the analyzer dropped out. Continued to monitor. Recovered after 3 mins. GWTP- LLP 1/2 hydraulic valve failed to open alarms came in. Cleared as per shift report | All Water System ROC General | 2025-11-25
ROC | November | Adeela Khan signing out | All Water System ROC General | 2025-11-24
ROC | November | AUPSWS, Building Flood Alarm, notified Will M, he is heading to site to fix the float | All Water System ROC General | 2025-11-25
ROC | November | KCPSDS - PAC control panel power failure. Able to clear, no outstanding issues on site KCETDS - Control panel power failure. Status went to normal as page opened. No outstanding issues with trends or site | All Water System ROC General | 2025-11-23
ROC | November | GWTP - Phil D & Patrick F troubleshooting low lift pmp 1 | All Water System ROC General | 2025-11-21
ROC | November | RHPSPA - Redempto called back to inform that he is finished his pressure tests and requested pumps 2 and 4 put back to duty 1 | All Water System ROC General | 2025-11-21
ROC | November | BLW12- Influent free hi alarm came in on well start up. Recovered after 3 mins cleared alarm | All Water System ROC General | 2025-11-25
ROC | November | GWTP- Stephen B cut flow to all analyzers to avoid flooding sumps during power transfer, Directed to disregard all analyzer alarms on site | All Water System ROC General | 2025-11-25
ROC | November | Adam Button signing out | All Water System ROC General | 2025-11-25
ROC | November | KSTP - Donald M. and Divya P. working on filter 1 effluent valve | All Water System ROC General | 2025-11-27
ROC | November | KSTP, Fin Water Fluoride Res/Tot Cl2 Res Fault Alarm, Plant is currently off. Nothing in the shift report to disregard, contacted Jack P, directed to disregard. consult | All Water System ROC General | 2025-11-20
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-20
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-20
ROC | November | GWTP, Clearwell 1 Cl2 lo alarm, Notified Jack P, Directed to turn on the recirc pump, placed Clearwell Pump 1 (Recirc Pump) man/on, will continue to monitor residual of clearwell. Once residual is back to normal, will send Jack P an email of when the pump was turned off. consult | All Water System ROC General | 2025-11-20
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-23
ROC | November | MAPS PD8 - Activated duty 1 | All Water System ROC General | 2025-11-30
ROC | November | GWTP- Stephen B called. He is still onsite troubleshooting train 5. Disregard related alarms. 21:50- Stephen B called and requested to place PV2 valve man open then man closed several times to see if it will take command. ZW8 Backpulse Inlet V Failed to Open. Stephen B requested place in manual and he will look into it. 22:15- Stephen B requested to initiate backwash. 22:13- ZW2 Backpulse Inlet V Failed to Open. Stephen B will look into it. 22:30- Stephen B. Requested to initiate backwash | All Water System ROC General | 2025-11-25
ROC | November | SHTP - Filter 3 Turbidity Hi alarm, Filter 1 just completed backwash. Disregard as per shift report. Cleared alarm. | All Water System ROC General | 2025-11-29
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-26
ROC | November | MARS- Cell1 (North) Lvl Hi Alarm RHMCMD- Placed in manual RHRSTR- Deactivated duty. | All Water System ROC General | 2025-11-26
ROC | November | AUW57 - Influent Free Chlorine Lo alarm came in. Well just started up. Will monitor 06:51 - Influent levels came back to optimal range and cleared alarm | All Water System ROC General | 2025-11-26
ROC | November | BLW12 - Joe M. called and directed to place well 1 man/on | All Water System ROC General | 2025-11-26
ROC | November | Christian Van Beek signing out. | All Water System ROC General | 2025-11-25
ROC | November | AUW57- Station Turbidity Hi Alarm. Rotated Silicate pump 2 into duty 1. Will monitor. | All Water System ROC General | 2025-11-25
ROC | November | Connor Smith signing in | All Water System ROC General | 2025-11-20
ROC | November | KSETDP - Altitude valve fail to close alarm. Checked site, operations appear normal. Altitude valve is manual/open. Able to reset alarm. | All Water System ROC General | 2025-11-27
ROC | November | MKRSEM - Called Toronto Water (Paul) and requested they deactivate the pumps pushing flow to MKRSEM. NMETHW - Activated duty 1. | All Water System ROC General | 2025-11-27
ROC | November | STPSMR- Ernie H on site to work on generator and will be running it later on KSETWB- Patrick F on site to test CL leak detection alarm | All Water System ROC General | 2025-11-27
ROC | November | MKRSEM - Called Toronto Water (Peter) and requested they deactivate the pumps pushing flow to MKRSEM. | All Water System ROC General | 2025-11-25
ROC | November | AUW57- Ryan B and Jay G done on site well running in man/on will place in auto later today | All Water System ROC General | 2025-11-25
ROC | November | SHETCS- Hypo Pump 1 Uncmd. Stop. Pump 2 is already man/off. Cleared alarm and pump started back up. 12:58- Hypo Pump 1 Uncmd. Stop. Cleared alarm. | All Water System ROC General | 2025-11-29
ROC | November | NMETIB- Deactivated duty. | All Water System ROC General | 2025-11-29
ROC | November | MKRSEM, Notified Toronto operator Paul to stop pumping to the res | All Water System ROC General | 2025-11-21
ROC | November | KSETDP- Inlet total Cl2 hihi alarm came in on Duty 1 activated on disregard as per shift report reset alarm as residual recovered | All Water System ROC General | 2025-11-27
ROC | November | QVW12- Influent free Cl2 hi alarm came in. Continued to monitor VNPS - Surge tank 1/2 lolo alarms came in. Benson S on site working BLW12- Joe M placed wells in man/off for contractors to complete work | All Water System ROC General | 2025-11-27
ROC | November | *WRONG BOOK* | All Water System ROC General | 2025-11-30
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-30
ROC | November | YWS + NYWS Normal Connor Smith signing out | All Water System ROC General | 2025-11-30
ROC | November | QVW12, Influent Free Cl2 lo alarm, Adjusted Chlorinator 1 dosing from 112% to 116%, will continue to monitor the influent, trending has shown a decrease in the influent. 01:30, Adjusted Chlorinator 1 dosing from 116% to 119% as the influent again started to drop again, will continue to monitor 01:36, Residual continues to rise and then drop, rotated chlorinators so chlorinator 2 is in D1 and chlorinator 2 is in D2. Will continue to monitor the site 01:41, Residual is climbing back to normal levels, will continue to monitor site till the site is back to normal residual levels, Chlorinator 1 may have issues, will send email out to operator | All Water System ROC General | 2025-11-20
ROC | November | STW2/3, Placed wells back to auto | All Water System ROC General | 2025-11-20
ROC | November | NMW12- Treated total/ combined Cl2 lo alarms came in. Wells not active no water directed to users | All Water System ROC General | 2025-11-20
ROC | November | KSETWB- Educator water/gas valve/cross chlor/tower chlor valves failed to open alarms came id due to decreased inlet flow. Reset alarm | All Water System ROC General | 2025-11-20
ROC | November | GWTP- Phil D onsite and will be locking out Low Lift Pump 1. | All Water System ROC General | 2025-11-20
ROC | November | NMTKKC - Joe D on site to complete a sump pump hi level alarm test, a hot flush of the chemical analyzer and has placed the chemical pumps offline for the duration of the analyzer work. Will see a chemscan offline alarm. | All Water System ROC General | 2025-11-25
ROC | November | MTW3 - Dan Z called and directed to place MTW3 into auto mode. Dan Z also informed that STRS48 is back to normal operations, and she is leaving site. | All Water System ROC General | 2025-11-25
ROC | November | Angelica Chepiga signing in, weather +8C | All Water System ROC General | 2025-11-26
ROC | November | NMETQS- Tower level High alarm. Deactivated Duty 1. | All Water System ROC General | 2025-11-26
ROC | November | STETTL - Outlet free chlorine hi alarm. Joe M heading to site to investigate. Created CMU5#W11471630 #CMU5 | All Water System ROC General | 2025-11-26
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-26
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-22
ROC | November | MKRSEM- Called Toronto (Paul) and requested two pumps on. | All Water System ROC General | 2025-11-22
ROC | November | STW12- Placed well 1 in manual for STETBR fill cycle STW3- Placed well in manual for STETBR fill cycle | All Water System ROC General | 2025-11-22
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-22
ROC | November | YWS + NYWS NORMAL | All Water System ROC General | 2025-11-28
ROC | November | NMVCBP, Placed flow setpoint from 40L/sec to 60L/sec to 80L/sec NMVCIB, Placed flow setpoint from 80L/sec to 60L/sec to 40L/sec | All Water System ROC General | 2025-11-20
ROC | November | NBET27- Outlet Total CL2 HiHi Alarm. Tower is filling. Free CL2, NBET and wells are reading normal. Will monitor. Emailed Jacob M. | All Water System ROC General | 2025-11-22
ROC | November | Adam Button signing in -2 Clear | All Water System ROC General | 2025-11-19
ROC | November | STW3 - Placed well in auto mode. STW12 - Placed STW2 in auto mode. | All Water System ROC General | 2025-11-27
ROC | November | QVW12 - Influent free chlorine hihi. Well recently activated. Influent free chlorine reading was abnormal before the well activated. Trending shows the influent free chlorine reading increased following well activation. While monitoring site the influent free chlorine reading returned to normal range. Monitored system to determine if the well will lockout on the effluent free chlorine spike. | All Water System ROC General | 2025-11-27
ROC | November | Angelica Chepiga signing out | All Water System ROC General | 2025-11-27
ROC | November | QVW34- Placed well 3 in man/on STPSMR- Historian heartbeat alarm came in. Trends look like they are flatlined then cut out and flatline again. Notified Ian W will check on SCADA. Created CMU5 W11472905 #CMU5 | All Water System ROC General | 2025-11-27
ROC | November | JFRS- Deactivated duty in preparation for Maple to Jefferson Feed. | All Water System ROC General | 2025-11-23
ROC | November | MKRSEM- Called Toronto (Paul) and requested pumps off. | All Water System ROC General | 2025-11-23
ROC | November | Christian Van Beek signing in. | All Water System ROC General | 2025-11-24
ROC | November | SHETCS- Hypo P2 failed to start alarm came in. Notified Cole W as this is the second time the pump has failed to start today. Directed to place in man/off for weekend. Will attend site if issues arise with P1 #consult | All Water System ROC General | 2025-11-28
ROC | November | YWS+NYWS normal Adam Button signing out | All Water System ROC General | 2025-11-28
ROC | November | NMW136- Influent free Cl2 lo alarm came in. on well start up. Trends recovered after 3 mins alarm cleared KSTP- Raw water turbidity fault, fluoride pumps not available, Fin water total Cl2 fluoride res fault alarms outstanding. Notified Jack P. Dire ted to reset and disregard Raw water turbidity fault alarm #consult | All Water System ROC General | 2025-11-19
ROC | November | NMVCBA- Placed valve in manual 50L/s 00:40- Placed back into auto | All Water System ROC General | 2025-11-21
ROC | November | RHMCMD- Placed valve in manual RHRSTR- Deactivated duty MKRSEM- Called Toronto (Paul) and requested pumps off. | All Water System ROC General | 2025-11-22
ROC | November | GWTP- Low Lift Pump 2 Hydraulic Vlv Fail to Open, Low lift Pump 4 Hydraulic Vlv Fail to Open. Cleared alarms as per SCADA report | All Water System ROC General | 2025-11-22
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-27
ROC | November | MARS - Level Hi alarm came in. Activated duty 1 at VNRSKS 03:52 - MARS - Level HiHI alarm came in. Everything topped up downstream. Deactivated duty 1 at BVPS | All Water System ROC General | 2025-11-28
ROC | November | ARPS, David from OCWA called, they are doing their pump PMs, their pumps will be off for roughly 15 to 30 minutes, will continue to monitor MARS levels | All Water System ROC General | 2025-11-28
ROC | November | QVW12- Alex B. onsite for health and safety work orders. Disregard eye wash alarms. | All Water System ROC General | 2025-11-20
ROC | November | HLW2- Placed well man/off and Placed FCV2 in auto changed flow setpoints from 20L/s to 25 L/s AUW57- Jerry Z on site to work on Cl2/ turbidity analyzers and test Cl2 leak detection alarm | All Water System ROC General | 2025-11-20
ROC | November | Carter Dunn Signing Out | All Water System ROC General | 2025-11-24
ROC | November | RHMCMD - back to auto. | All Water System ROC General | 2025-11-29
ROC | November | QVW34- Placed well back into auto. NMVCBA- Placed valve back into auto. | All Water System ROC General | 2025-11-22
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-23
ROC | November | AUPSOH- Rick L and Parth P on site for flowmeter calibration | All Water System ROC General | 2025-11-28
ROC | November | HLW1 - Combined Chlorine Lo alarm came in. Checked site. Duty recently activated. Combined levels took a dip but came back to optimal range within 2 mins. Alarm has cleared | All Water System ROC General | 2025-11-30
ROC | November | Carter Dunn Signing In, 1D/Clear | All Water System ROC General | 2025-11-19
ROC | November | QVW34, Influent Free CL2 hihi alarm came in, adjusted dosing from chlorinator 1 from 70% to 65%. NMETIB, Deactivated D1 to help allow NMETHW recover NMETHW, When receiving the the hihi influent, trends show an abnormal drop in the tower volume cubic meters trend, will continue to monitor and will send an email to the area at the end of the shift from my observations | All Water System ROC General | 2025-11-19
ROC | November | MKRSEM - Called Toronto water (Mehdi), requested start filling Res. | All Water System ROC General | 2025-11-26
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-21
ROC | November | AUPSRR- WPS Pressure Reducing Valve Uncommanded Open, Zurora Zone 3 Pressure Hi Alarm. Notified William M. He is just arriving to site and will take a look. | All Water System ROC General | 2025-11-20
ROC | November | HLW2- Sean P on site to disconnect well | All Water System ROC General | 2025-11-24
ROC | November | MKETFA - Jack P performing PMs including - testing temp alarms, Hi/low level alarms. Chlorine analyzers maintenance. | All Water System ROC General | 2025-11-26
ROC | November | GWTP - UV 2 dosage Hi alarm, duty just deactivated. Disregarded as per SCADA review. | All Water System ROC General | 2025-11-26
ROC | November | VNPSCD - Post Injection Combined CL2 HiHi alarm came in. After duty deactivated, alarm still outstanding. Called Ben H. who will take a look 04:47 - Ben called back to inform that this occurred as duty deactivated. Ben placed chlorine valves in manual and pushed fresh water in through BVPS. Ben will continue to monitor system #CONSULT | All Water System ROC General | 2025-11-24
ROC | November | RHRSWA- Parth P on site for annual calibrations. Req Cell 2 be placed as controlling tower. Change controlling tower from cell 1 to cell 2 | All Water System ROC General | 2025-11-27
ROC | November | MTW3- Generator running on site. Notified Joe M. On site for silicate run will investigate MAPS PD7- Kyle R on site to work on P1/2 actuator placed P2 in man/off | All Water System ROC General | 2025-11-27
ROC | November | BVPS- Jack P notified ROC Discharge Cl2 analyzers are back up and running. Jack P verified with Parth P that power interruption to analyzer wont be an issue. Cleared all alarms. No water directed to users during analyzer outage STRS48- Lee F done on site placed both wells and high lifts back in auto GWTP- Patrick F on site calibrating Keswick line pH probe STETBR/RHRSWA- Talha H working on OITs | All Water System ROC General | 2025-11-27
ROC | November | HLW2 - Combined chlorine lolo, treated chlorine lo. Duty not active, wells off. Dip in trend and came back to normal range next reading. | All Water System ROC General | 2025-11-22
ROC | November | QVW34 - Man/start well to help push water through Ringwell to Harry Walker | All Water System ROC General | 2025-11-22
ROC | November | RHMCMD - Man/open valve 100% | All Water System ROC General | 2025-11-22
ROC | November | STPSMR, Gas Detector hihi/Cl2 Emerg System Active Alarm, Jack P is safe, will be looking into the leak alarm | All Water System ROC General | 2025-11-27
ROC | November | RHPSPA - Rotate pump 1 into duty 1, and pump 2 which was running into duty 4 to keep it off. This is done for instrumentation Red B who is onsite | All Water System ROC General | 2025-11-21
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-23
ROC | November | NBET27 - Free chlorine residual back to normal, alarm cleared. Joe W leaving site. | All Water System ROC General | 2025-11-26
ROC | November | Gluzen Ramos Ong signing in | All Water System ROC General | 2025-11-27
ROC | November | TPH1- Pressure lolo alarm came in. Pressure recovered after 5 mins may be related to isolation work in PD5 | All Water System ROC General | 2025-11-27
ROC | November | KSTP- PACL P1 fault alarm came in. Notified Donald M. Will check on site | All Water System ROC General | 2025-11-28
ROC | November | KLET27/KLPSWL- Kevin W rebooting modems | All Water System ROC General | 2025-11-25
ROC | November | SHETCS- Post Injection Total CL2 HiHi. Value recovered. Cleared alarm. | All Water System ROC General | 2025-11-25
ROC | November | NMVCBA- Placed valve manual 40L/s to keep NMETIB and NMETHW offset. | All Water System ROC General | 2025-11-25
ROC | November | YDSS + YNSS Normal Connor Smith signing out | All Water System ROC General | 2025-11-26
ROC | November | HLETYS - Activate duty 1 for interim | All Water System ROC General | 2025-11-24
ROC | November | GWTP - Activate duty 1 for interim | All Water System ROC General | 2025-11-24
ROC | November | GWTP - Train 5 channel 1 & 2 parts count OOR during backwash of train 5. No further issues as train on standby and recovering 23:42 - Train 5 channel 1 & 2 parts count OOR came back. Informed Jack P. Okay to disregard for the night Consult | All Water System ROC General | 2025-11-24
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-28
ROC | November | Christian an Beek signing in. Weather: 6C and clear. | All Water System ROC General | 2025-11-25
ROC | November | HLW2 - combined chlorine lolo, treated total chlorine lolo. Well was off. Dip in trend but reading came back within normal range | All Water System ROC General | 2025-11-23
ROC | November | AUETFC - Parth P. is on site for annual calibrations 14:29 - Parth called back to inform he will be calibrating the tower LIT. Confirmed with Divya P. and placed pumps 4 and 5 into man/off. Parth will call once calibrations are complete 14:46 - Parth called back to inform that he is finished calibrating the LIT. Placed pumps back to auto | All Water System ROC General | 2025-11-26
ROC | November | STETTL - Outlet Free chlorine High alarm. Notified Joe M. He will check SCADA. # Consult. | All Water System ROC General | 2025-11-26
ROC | November | GRTPLL Low Lift Pump 4 and pump 1 Hydraulic Vlv uncommanded close alarms. Reset alarms as per SCADA shift report. | All Water System ROC General | 2025-11-29
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-29
ROC | November | NBW3- Influent Free Chlorine LoLo. Interlocked well which was starting up on schedule mode. Residual recovered. Waited 10 minutes and restarted well. | All Water System ROC General | 2025-11-30
ROC | November | NMETHW - Tower Level Lo alarm came in. Duty 2 just activated NMETIB - Deactivated duty1 | All Water System ROC General | 2025-11-30
ROC | November | STETBR - Tower Level Hi alarm came in. Placed STW2 and STW3 back to auto, as per interim | All Water System ROC General | 2025-11-30
ROC | November | QVW12 - Treated total chlorine Hi alarm. Will monitor. | All Water System ROC General | 2025-11-28
ROC | November | RHRSTR - Deactivated D1, RHMCMD man/open to maintain MARS level. | All Water System ROC General | 2025-11-29
ROC | November | NMW136 - Treated Total and Combine residual Low alarms. Duty not active. No water directed to users. Value recovered in 10 minutes. Cleared alarms. | All Water System ROC General | 2025-11-29
ROC | November | AUPSOH- Hydro Power Failure Alarm. Alarm cleared on its own. Site appears normal. | All Water System ROC General | 2025-11-30
ROC | November | GWTP- Jeff from Property Services Notified ROC that Stephen B contacted them to placed fire panel on test for duration of work today on site. Jeff req. to call security when work on site has been completed and fire panel can be placed back online | All Water System ROC General | 2025-11-25
ROC | November | AURSOH - Divya P called, instrumentation on site for annual calibration. | All Water System ROC General | 2025-11-26
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-22
ROC | November | NMETIB - Deactivate duty 1 QVW34 - Man/start well 3 | All Water System ROC General | 2025-11-23
ROC | November | Ethan Ullalkar signing out. | All Water System ROC General | 2025-11-23
ROC | November | GRTPLL - Low lift pump 3 Hydraulic vlv failed to open, Stephen B will check. | All Water System ROC General | 2025-11-26
ROC | November | MARS - Noted that Toronto Water was pushing more than normal flow through TMC 317 Keele St Transmission to MARS. Called Toronto Water (Mehdi) and requested they return to normal flow. | All Water System ROC General | 2025-11-27
ROC | November | NMVCBA- Ryan B and maintenance on site have valve in man/closed AUETFC- Parth P and Rick L on site for flow meter calibrations | All Water System ROC General | 2025-11-28
ROC | November | HLW1- Combined Cl2 lo alarm came in. Residual recovered after 3 mins alarm cleared | All Water System ROC General | 2025-11-28
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-24
ROC | November | NMW15 - Combined Chlorine Lo alarm came in. Well is running in schedule mode. Trends indicate the combined took a slight dip and recovered within 3 mins. Alarm has cleared | All Water System ROC General | 2025-11-30
ROC | November | NBW3 - Influent Free Chlorine HiHi alarm came in. Checked site. Well recently activated. Level came back to optimal range within 5 mins and alarm cleared | All Water System ROC General | 2025-11-30
ROC | November | NMETHW, Total/Combined Cl2 lo alarm, no flow leaving the tower, tower filling with no wells on currently, will continue to monitor 05:09, Tower is now draining, will monitor the tower until residuals are back to normal | All Water System ROC General | 2025-11-20
ROC | November | MKPSSA- Placed pump 3 man/off | All Water System ROC General | 2025-11-25
ROC | November | STW12- Placed well back into auto STW3- Placed well back into auto | All Water System ROC General | 2025-11-26
ROC | November | AUPSRR - William M testing chlorine leak alarm. | All Water System ROC General | 2025-11-26
ROC | November | MKRSEM, Notified Toronto operator Medhi to start filling the res | All Water System ROC General | 2025-11-19
ROC | November | HLETYS - Post-inj combined chlorine lo, slight dip in trends, readings came back within range. RHMCMD - Place back in auto | All Water System ROC General | 2025-11-23
ROC | November | NBW2 / NBW37 - Kingsley M called to inform he has completed his work at NBW2 and it can be placed into auto mode. Kingsley will be completing the same work at NBW37 and a historian heartbeat alarm is expected. Placed NBW37 in manual off and NBW2 in auto. | All Water System ROC General | 2025-11-24
ROC | November | AUW57, When doing SCADA check, noticed the contact tank had 8m3 in it. early in the night, the influent had a dip which shut off the well. Placed well man/off for operator to look at during the day. | All Water System ROC General | 2025-11-21
ROC | November | SHTP - Well 2 pump uncommanded start alarm. Ack/reset alarm as per David T. | All Water System ROC General | 2025-11-26
ROC | November | Town of Mount Albert - Informed they are repairing water service along 61 main street. Street isolated for work to repair. May experience lower flow than normal for a couple hours. Contact: 905-955-0613 | All Water System ROC General | 2025-11-21
ROC | November | YWS+NYWs normal Adam Button signing out | All Water System ROC General | 2025-11-19
ROC | November | RHMCMD, Placed valve man/open RHRSTR, Deactivated D1 so MARS can send more flow to RHRSTR | All Water System ROC General | 2025-11-20
ROC | November | NMW136 - Treated & combined chlorine lo. Sudden drop in reading. Analyzer came back within range next reading | All Water System ROC General | 2025-11-22
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-22
ROC | November | HLW2 - combined chlorine hihi. Interlocked well. Informed Benson B who is onsite. Disregard as he is watching over well GWTP - Patrick F onsite. Disregard train 2 alarms | All Water System ROC General | 2025-11-21
ROC | November | Adam Button signing out | All Water System ROC General | 2025-11-24
ROC | November | RHMCMD - Placed valve in auto. | All Water System ROC General | 2025-11-25
ROC | November | AUW57 - Dan B working on pump motor, will start and stop well 5 pump, Ben H is aware. | All Water System ROC General | 2025-11-26
ROC | November | Access York- Jen from Access York called about a property owner reporting a potential main break at 1853 HWY 7 in Vaughan. Property owner (Burrell Overhead Doors) had already spoken with City of Vaughan and they referred them to Access York. Checked all pipes confirmed not York infrastructure. No response from York Operators required | All Water System ROC General | 2025-11-24
ROC | November | VNETFD, Activated D1 | All Water System ROC General | 2025-11-20
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-28
ROC | November | RHMCMD - Place back in auto | All Water System ROC General | 2025-11-21
ROC | November | GWTP - Stephen B called to inform they completed their work but are investigating some alarms associated with ZW1. Stephen directed to disregard the not all devices in auto alarm and a reject pump alarm. | All Water System ROC General | 2025-11-24
ROC | November | BLW3 - Kyle C. is on site scoping out IO for future changes BLW3 - Gas Scrubber Fault alarm came in and cleared right away. Spoke to Kyle C. who informed he triggered the alarm and cleared it 11:45 - Kyle C. is finished on site | All Water System ROC General | 2025-11-21
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-24
ROC | November | MKRSEM- Reservoir level 1 lo alarm came in. called Metro spoke with Zorhan to start 2 pumps. STETTL- STETTL to STW12 comm alarm. Trends okay reset alarm | All Water System ROC General | 2025-11-28
ROC | November | Carter Dunn Signing In | All Water System ROC General | 2025-11-25
ROC | November | Adeela Khan signing out | All Water System ROC General | 2025-11-21
ROC | November | QVW12- Alex B was able to troubleshoot chlorinator 2 and will be working on silicate system for the remainder of the day KSTP- Donald M Divya P and Angelica C on site to work on analyzers. Plant is off | All Water System ROC General | 2025-11-20
ROC | November | MAPS - Kyle R and Dan are leaving site. They did not finish their work on PD& pump 1 but they informed that pump 2 can be placed back into auto and alarms cleared. Made the required changes. | All Water System ROC General | 2025-11-25
ROC | November | ARPS- Peter from OCWA called. Maintenance is completed on Ammonia analyzers. Trending is back to normal. | All Water System ROC General | 2025-11-20
ROC | November | SHTP- Noticed that Filter 1 NTU reading a negative value since this morning. Notified Jacob M. He will attend site. 21:03- Analyzer back to normal. Jacob M leaving site. W11461999 CMU5 | All Water System ROC General | 2025-11-21
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-22
ROC | November | ANW23 - Historian Heartbeat alarm came in. Well 2&3 pumps OOS alarm followed. Called Ian W. who will take a look | All Water System ROC General | 2025-11-26
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-21
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-22
ROC | November | STRS48 - Influent free chlorine lolo. Jack P is on site and informed that a water service line is leaking. jack has requested the assistance of the on call mechanical maintenance operator. Passed contact information to Jack P. | All Water System ROC General | 2025-11-25
ROC | November | GRTPLL Low Lift Pump 2 Hydraulic Vlv uncommanded close alarm. Reset alarm as per SCADA shift report. | All Water System ROC General | 2025-11-29
ROC | November | Angelica Chepiga signing out | All Water System ROC General | 2025-11-29
ROC | November | YWS + NYWS Normal Connor Smith signing out | All Water System ROC General | 2025-11-29
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-30
ROC | November | Adeela Khan signing out | All Water System ROC General | 2025-11-30
ROC | November | AUW57 - Station Turbidity Hi alarm came in. Checked site. Rotated silicate pump 2 into duty 1. Will monitor 07:18 - Placed Silicate pump 1 man/off as per Ben H. | All Water System ROC General | 2025-11-26
ROC | November | RHMCMD, Placed valve man/open RHRSTR, Deactivated D1 | All Water System ROC General | 2025-11-21
ROC | November | KSETWP- Divya P and Angelica C onsite for CL17 analyzer maintenance. | All Water System ROC General | 2025-11-20
ROC | November | GWTP - Stephen B and Joe M leaving site. All alarms cleared. | All Water System ROC General | 2025-11-26
ROC | November | NMW15- Station turbidity hi alarm came in. Rotated to silicate pump 1 will continue to monitor trends and place P2 if turbidity comes back to normal range MTW12- Jackie P Sampling well 1. Will activated D1 after completing sampling 12:01- NMW15- Jay G heading to site to trouble shoot turbidity issues. Well did not run long enough to determine silicate pump 2 is the issue | All Water System ROC General | 2025-11-19
ROC | November | AURSBS- Activated duty in preparation for Maple to Jefferson feed. | All Water System ROC General | 2025-11-22
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-23
ROC | November | NRETCR- Power Failure. Alarm cleared. AUMCBR- Control Panel Power Fail. Alarm cleared ABMC- Power Fail. Alarm cleared. | All Water System ROC General | 2025-11-23
ROC | November | NMW136- Combined / Treated total Cl2 lo alarm came in. Checked trends looks like analyzer dropped out. Residuals recovered after 3 mins alarms cleared | All Water System ROC General | 2025-11-27
ROC | November | GWTP,SUETDR - Dan Z called, PRV valves failing to open, Town of Georgina has been notified, and they will open zone valve. Dan Z requested to give her contact if they have any questions. | All Water System ROC General | 2025-11-13
ROC | November | HLW2 VC - Downstream Pressure HiHi Alarm. Sharon Valve started up in schedule mode and interlocked valve. Cleared alarm when schedule mode ended. | All Water System ROC General | 2025-11-13
ROC | November | HLW1 - Combined chlorine hi. Ongoing issue with site. Benson S is aware | All Water System ROC General | 2025-11-13
ROC | November | MKRSEM- Called Toronto (Peter) and requested two pumps on. | All Water System ROC General | 2025-11-13
ROC | November | RHVCEM - throttle down valve back to 15% RHRSTR - Activate duty 1 | All Water System ROC General | 2025-11-13
ROC | November | MARS - Request TO (Brent) for max flow | All Water System ROC General | 2025-11-13
ROC | November | AUW14 - Silicate room smoke detector. Informed Jerry Z, disregard as caused by silicate top up/delivery | All Water System ROC General | 2025-11-12
ROC | November | AUPSRR- Post Inj Free Chlorine HiHi Alarm. Value recovered, cleared alarm. | All Water System ROC General | 2025-11-13
ROC | November | RHMCMD- Placed valve in manual RHRSTR- Deactivated duty to try and move water out of MARS | All Water System ROC General | 2025-11-14
ROC | November | KLPS27 - Total chlorine residual High alarm. Jacob M on site, working on it. | All Water System ROC General | 2025-11-11
ROC | November | NMVCBA - Upstream pressure hihi/OOR, trend shows sudden spikes and drops in reading. Had occurred in previous weeks. Will monitor and relay information to Ben H & Ryan B on PIT1 issues | All Water System ROC General | 2025-11-12
ROC | November | AUETFC - Low level alarm, area deep cycling ET to 25%. 09:05 Jerry Z completed work onsite and returned Duty start point to 35 %. | All Water System ROC General | 2025-11-12
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-12
ROC | November | NMMCAD - Harsh P on site for inspection, disregard alarms for now. | All Water System ROC General | 2025-11-12
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-14
ROC | November | AUW57- Influent free Cl2 lo alarm came in on well start up. was able to clear alarm after 3mins | All Water System ROC General | 2025-11-11
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-17
ROC | November | HLW2 VC - downstream pressure hihi pressure, caused valve to close. Pressure came back down. Able to clear | All Water System ROC General | 2025-11-17
ROC | November | MKRSEM - Brett from Toronto water called, will work on Milliken PD5 pumps for 3 hours later today. Res. at 65%. Brett will call later with more information. | All Water System ROC General | 2025-11-12
ROC | November | GWTP - Artour L testing UPS on site. Plant is off. Disregard alarms for the duration of the test. | All Water System ROC General | 2025-11-11
ROC | November | Adam Button signing in 2C Raining | All Water System ROC General | 2025-11-12
ROC | November | MAPS PD7- Placed P2-4 in man/off (not running) | All Water System ROC General | 2025-11-12
ROC | November | VNPS PD7- Placed P1 in man/on NMVCIB- Changed flow set points from 80-40L/s NMVCBA- Changed flow set points from 40-80L/s | All Water System ROC General | 2025-11-12
ROC | November | MARS, Notified Toronto operator Andrew to increase the flow due to PD7/8 both active | All Water System ROC General | 2025-11-11
ROC | November | RHRSTR- Activated D1 RHMCMD- Placed Valve in auto | All Water System ROC General | 2025-11-11
ROC | November | MARS- Called Metro (Brett) requested to decrease flow to reservoir | All Water System ROC General | 2025-11-11
ROC | November | ANW34 - Wells 2&3 pumps OOS, RSV inlet free chlorine LoLo alarm, notified Benson S, He will check. | All Water System ROC General | 2025-11-11
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-12
ROC | November | Access York - Received call from Simon with a warm call from Town of King (David 416-559-5116). Informed of small water break @ Hambly Ave & 36 Norman Drive. Ownership is by town of King and they have a team onsite responding. | All Water System ROC General | 2025-11-12
ROC | November | ARPS- Discharge flow lolo alarm came in. Quick dip in trends was able to reset alarm | All Water System ROC General | 2025-11-12
ROC | November | KSTP- Filter 1 effl valve fault alarm came in. Notified Patrick F as filter 1 OOS. Patrick F will check SCADA MARS- Called Metro spoke with Andrew to increase flow to reservoir | All Water System ROC General | 2025-11-11
ROC | November | MAPS PD7, Placed pumps 3/4 back to auto | All Water System ROC General | 2025-11-11
ROC | November | AUVCBS - Communication failed alarm. Cleared alarm. | All Water System ROC General | 2025-11-11
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-11
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-11
ROC | November | MTW12 - Jackie S finished with well 1. Place all chemical pumps chlorine & silicate back in auto. Place well 1 back in auto. Activate duty 1 as requested by Jackie S | All Water System ROC General | 2025-11-12
ROC | November | STW3 - Travis W, on site for LIT maintenance, Silicate system flush, chlorine leak alarm test. | All Water System ROC General | 2025-11-13
ROC | November | AURSBS - Activate duty 1 | All Water System ROC General | 2025-11-13
ROC | November | AUPSRR - Spike in post-inj free chlorine hihi, dropped next reading to normal range, cleared alarm. Ammonia pump 2 uncmd stop. Able to clear, ammonia pump 1 running | All Water System ROC General | 2025-11-12
ROC | November | SHETCS - Deactivated Duty 1 to help SHTP Res level recover. As per interim memo. | All Water System ROC General | 2025-11-12
ROC | November | Ethan Ullalkar signing out. | All Water System ROC General | 2025-11-12
ROC | November | HLVCMA- PAC comm fail on site. Trends are spotty over the past 12 hours. Recovered after 5 mins. Will email West Water Ops | All Water System ROC General | 2025-11-12
ROC | November | YWS+NYWS normal | All Water System ROC General | 2025-11-12
ROC | November | RHMCMD - man/close to help maintain MARS level. | All Water System ROC General | 2025-11-11
ROC | November | MAPS PD7- Placed all pumps in man/off and stopped P2/3 VNPS PD7- Placed P1/3 in man/on | All Water System ROC General | 2025-11-11
ROC | November | KSTP - Donald M and Divya P running generator and troubleshooting fluoride pumps. | All Water System ROC General | 2025-11-13
ROC | November | MTW3- Joe M testing chlorine leak alarm. | All Water System ROC General | 2025-11-11
ROC | November | Christian Van Beek signing in. Weather: 2C and clear. | All Water System ROC General | 2025-11-16
ROC | November | AUPSOH- Jerry Z on site to run generator and test hi lo temp | All Water System ROC General | 2025-11-11
ROC | November | SHETCS- Hypo pumps 1/2 fail to start and post injection lo alarm came in. Tried to call Dave T 2 times no answer. cleared alarms to see if hypo pumps will run. Will continue to monitor SHTP- UV reactor 3 minor fault. alarm. Will follow up with Dave T when he calls back. Filter 2 hi turbidity as backwash sequence completed. reset alarm as per shift report STW12- Shaun P on site running generator with contractors on site 09:28- SHTP- Called Joe W on site with Dave Working on UV reactor 3 will be heading to SHETCS afterwards | All Water System ROC General | 2025-11-11
ROC | November | GWTP- Low lift P2 hydraulic vlv failed to open alarm came in. Reset as per shift report KSTKWP/SUETDR- Activated D1 as per interim | All Water System ROC General | 2025-11-13
ROC | November | YWS+NYWS normal | All Water System ROC General | 2025-11-13
ROC | November | AURSBS - Activate duty 1 RHMCMD - Man/close | All Water System ROC General | 2025-11-13
ROC | November | Ethan U signing in Weather 2. Snow | All Water System ROC General | 2025-11-16
ROC | November | SHTP - Noticed plant highlift running, called and confirmed with Cole W to revery highlift duty band back to normal to preserves reservoir for water resources/interim | All Water System ROC General | 2025-11-13
ROC | November | VNRSKS - Activate duty 1 as MARS reaching hi level | All Water System ROC General | 2025-11-17
ROC | November | YWS + NYWS Normal STW12/STW3 - Place wells in man/on | All Water System ROC General | 2025-11-16
ROC | November | STETTL - Historian heartbeat alarm, informed Yash S of outstanding alarm | All Water System ROC General | 2025-11-12
ROC | November | HLW2 VC - Downstream Pressure HiHi Alarm. Sharon Valve started up in schedule mode and interlocked valve. Will reset once schedule mode ends. | All Water System ROC General | 2025-11-11
ROC | November | MKRSEM, Notified Toronto operator Andrew to start filling the res | All Water System ROC General | 2025-11-11
ROC | November | AURSBS- Activated D1 | All Water System ROC General | 2025-11-12
ROC | November | NMETIB- Inlet flow hi alarm NMVCIB- Changed flow setpoints back to 80 L/s NMVCBA- Changed flow setpoints back to 40L/s NMETIB- Free Cl2 hi alarm came in after inlet flow increase. Slowly coming back down combined Cl2 residual okay able to reset after 5 mins | All Water System ROC General | 2025-11-13
ROC | November | MAPS PD7- Placed all pumps in man/off and started P4 | All Water System ROC General | 2025-11-13
ROC | November | SHETCS- Activated D1 as per interim | All Water System ROC General | 2025-11-13
ROC | November | MKRSEM - Jack P on site for chlorine analyzers maintenance, flood alarm and Hi/Low Res level alarms testing | All Water System ROC General | 2025-11-11
ROC | November | NMW15 - Chlorine weight scale 1 LoLo alarm. Placed well 15 pump man/off, Jason G will attend site later today. | All Water System ROC General | 2025-11-11
ROC | November | GWTP- Chris S on site to test low lift system. Will call when done 11:11-GWTP- Patrick F on site testing Cl2 leak alarm | All Water System ROC General | 2025-11-11
ROC | November | HLW1 - Combine chlorine Hi alarm, adjusted chlorinator 1 dosing factor from 113 to 110%. | All Water System ROC General | 2025-11-13
ROC | November | STW12 - Travis W completed work on site. Will start well 2 pump on manual mode and leaving site. | All Water System ROC General | 2025-11-11
ROC | November | MAPS - Yash S on site for Notwork Upgrades, David T on site assisting with work. | All Water System ROC General | 2025-11-13
ROC | November | SHETCS - Duty stop Set point from 45 to 80% and SHTP - Reservoir Stop level from 5,4 to 5,7 m. as per Interim Memo. | All Water System ROC General | 2025-11-12
ROC | November | AUPSRR - Checmscan offline alarm, followed up with Will M. Is working on chemscan for maintenance and chemical clean | All Water System ROC General | 2025-11-12
ROC | November | NMW136- Combine and Treated total chlorine residual Low alarms, quick dip, value recovered, cleared alarms. | All Water System ROC General | 2025-11-14
ROC | November | Carter Dunn Signing In, 0D/Clear | All Water System ROC General | 2025-11-14
ROC | November | NMETIB- Deactivated D1 to offset from NMETHW as per shift report | All Water System ROC General | 2025-11-11
ROC | November | RHMCMD- Placed valve in man/open 100% RHRSTR- Deactivated D1 | All Water System ROC General | 2025-11-13
ROC | November | GWTP- Stephen B called. Plant is back to normal operations. Sutton Header Fluoride Lo Alarm outstanding. Stephen B requested to clear alarm. He is leaving site shortly. | All Water System ROC General | 2025-11-13
ROC | November | RHMCMD- Placed valve in auto. | All Water System ROC General | 2025-11-13
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-13
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-14
ROC | November | NMTKKC - Header combined chlorine HiHi alarm, Joe D on site, monitoring. | All Water System ROC General | 2025-11-11
ROC | November | QVETQS - Eric S leaving site. | All Water System ROC General | 2025-11-11
ROC | November | GWTP- ZW1 and ZW8 Shutdown alarms, common perm turbidity Hi and HiHi alarms, Stephen B and Patrick F working on site. Called Stephen B, no response, will call later. | All Water System ROC General | 2025-11-11
ROC | November | QVW12 - Alex B onsite, dewatering eyewash. Requested disregard eyewash alarm for the duration of the work. | All Water System ROC General | 2025-11-14
ROC | November | Angelica Chepiga signing in | All Water System ROC General | 2025-11-11
ROC | November | NBET - Outlet free chlorine hi, informed Joe W. WIll head to site to check on possible analyzer issue with free. STRS48 - Rick L finished at stie. Placed high lift pumps 1 & 2 back in auto | All Water System ROC General | 2025-11-12
ROC | November | MKRSEM - Continuing to monitor levels, finding levels still climbing, to avoid hihi alarm informed Dan Z onf ongoing situation. Directed to continue to monitor and follow up if hihi alarm is triggered. MKPSSA - Run pump 3 man/on as well as per Dan Z. Toronto not pumping, requested Zhoran to place their pumps in man/off until notified. Will monitor Consult | All Water System ROC General | 2025-11-15
ROC | November | NMETIB- Free Chlorine Hi Alarm. Will email Central OPS 03:01- Free Chlorine HiHi Alarm. Will monitor and email Central OPS | All Water System ROC General | 2025-11-14
ROC | November | AUW14 - Well 4 uncmd stop. Able to reset but comes back in. Leaving well in man/off for the night. Infomred Ryan B of situation and rotated well 2 & 3 to duty 1, & well 1 to duty 3 Consult | All Water System ROC General | 2025-11-12
ROC | November | BLETNL-Tower fire storage lo alarm came in. East Ops deep cycling tower for the night to 55% | All Water System ROC General | 2025-11-12
ROC | November | MARS- Called Metro spoke with Peter to reduce flow to reservoir | All Water System ROC General | 2025-11-12
ROC | November | YWS+NYWS normal | All Water System ROC General | 2025-11-13
ROC | November | RHVCEM- Changed valve position from 15 to 25% RHVCEM- Changed valve position from 25 to 40% | All Water System ROC General | 2025-11-13
ROC | November | KSTP - Fin water total chlorine and fin water fluoride res fault alarms on HLP start after filter backwash. Disregard as per SCADA review. Fluoride pump 2 speed deviation , Fin water fluoride residual lowlow alarms. Duty 1 close to stop point. Emailed Dan Z. | All Water System ROC General | 2025-11-13
ROC | November | STETBR - Tower level Low alarm, man/start Well 2 pump | All Water System ROC General | 2025-11-13
ROC | November | MAPS - Yash S doing switch replacement. Deactivated Duty 1 for MAPS PD8 and MAPS PD7. Will receive communication failure alarms. 13:52 Yash S completed switch replacement. All communication alarms cleared. David T on site running both generators on load. | All Water System ROC General | 2025-11-13
ROC | November | NMTKBS - PAC Communication failure alarm, site offline- notified Yash S. He will check. 10:35 Yash S called, alarm cleared. Checked site. Duty is active, pumps not running. Deactivated duty and activated again. Pumps started. | All Water System ROC General | 2025-11-14
ROC | November | MAPS - Stop Maple to JFRS feed | All Water System ROC General | 2025-11-16
ROC | November | MARS, Cell 1 North Hi alarm, Activated both AURSBS and KCETDS to help with the drainage of MARS BVPS, Placed pumps 1/2/3 man/off TMC317/MARS, Notified Farshad to drop flow to low flow to MARS | All Water System ROC General | 2025-11-14
ROC | November | GWTP - Stephen B. is on site and will be testing the generator | All Water System ROC General | 2025-11-17
ROC | November | AUETAD- Evgeny S working on OIT, disregard Historian heartbeat alarm. | All Water System ROC General | 2025-11-14
ROC | November | QVW12, Lee F on site doing pump maint, | All Water System ROC General | 2025-11-14
ROC | November | QVW34 - place pump back in auto | All Water System ROC General | 2025-11-17
ROC | November | JFPS, Rotated pump duty so pumps 2/3 in D1 and pumps 1/4 in duty 2 and 3 10:11, all 4 pumps started to run, Duty didn't shut pumps off, Placed pumps 1/4 man/off to make sure they shut off properly 11:10, Ernie S/Sean P finished on site | All Water System ROC General | 2025-11-14
ROC | November | AUPSRR - Eric S on site, will work on post-injection total chlorine analyzer. Deactivated AU central Duty. AUPSRR pumps not running. William M is aware. | All Water System ROC General | 2025-11-14
ROC | November | AURSBS - Activated Duty 1 @ 48% to maintain MARS level. | All Water System ROC General | 2025-11-14
ROC | November | GWTP - Generator alarm and Generator fault alarms outstanding from the power fail scenario. Called Dan Z who will attend site to examine the generator. Created CMU5#W11446281 #CMU5 | All Water System ROC General | 2025-11-16
ROC | November | AUW57 - Influent free chlorine lolo alarm. Checked site, system duty 1 recently activated triggering the well to start. Following well start the influent free chlorine reading dropped triggering an interlock on lolo influent free chlorine reading. The influent free chlorine reading recovered within two reading intervals. Cleared alarms and monitored well activation. | All Water System ROC General | 2025-11-16
ROC | November | SHTP, Raw Water Tank Flow Hart Comm Alarm, David T called to get in contact with PCS so they can look into this alarm, notified Yash S, he is looking into it | All Water System ROC General | 2025-11-14
ROC | November | STETBR - Red B, Rick L, Parth P on site for annual calibration. | All Water System ROC General | 2025-11-14
ROC | November | AURSBS - Redempto B. and Ricardo L. are on site for annual calibrations | All Water System ROC General | 2025-11-17
ROC | November | QVW34 - Activated AVW3 to push water south across Ringwell Drive meter chamber in accordance with area best practices. | All Water System ROC General | 2025-11-16
ROC | November | HLW2 - Downstream pressure hihi alarm. Sharon valve has opened in schedule mode. Sharon valve will close in thirty minutes then the pressure will decrease, and alarms can be cleared and HLW2FCV will open. | All Water System ROC General | 2025-11-16
ROC | November | AUPSRR - Res Outlet free chlorine OOR alarm, notified William M. He will check and contact Eric S 12:32 Free chlorine analyzer value back to normal, alarm cleared. | All Water System ROC General | 2025-11-14
ROC | November | Angelica Chepiga signing out | All Water System ROC General | 2025-11-14
ROC | November | VNP7 - Place pump 1 & 3 back in man/off. MAP7 - Place pump 2 & 1 back in auto | All Water System ROC General | 2025-11-12
ROC | November | KSTP - Fin water flouride res fault/ tot CL2 fault. Reading okay, plant off | All Water System ROC General | 2025-11-17
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-17
ROC | November | NMW12 - Treated Chlorine Lo and Combined Chlorine Lo alarms came in. Checked site. Both wells are not running, and water is not being directed to users | All Water System ROC General | 2025-11-17
ROC | November | HLPSYS - PAC communication failure. Alarm cleared when acknowledged. Trending okay | All Water System ROC General | 2025-11-15
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-15
ROC | November | Ethan Ullalkar signing out. | All Water System ROC General | 2025-11-17
ROC | November | Ethan U signing in Weather 6. | All Water System ROC General | 2025-11-15
ROC | November | MAP7 - Pump 2 uncmd stop, valve failed to open. Rotated pump 3 duty 1 | All Water System ROC General | 2025-11-16
ROC | November | MARS - Begin maple to JFRS feed | All Water System ROC General | 2025-11-16
ROC | November | MKRSEM - Called Toronto Water (Mehdi) and requested they deactivate the pumps pushing flow to MKRSEM. | All Water System ROC General | 2025-11-18
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-17
ROC | November | KSETDP - inlet total chlorine hihi alarm. Checked site, system duty recently activated which started to fill the tower and activated the chlorination system. Values have stabilized, reset alarm. | All Water System ROC General | 2025-11-18
ROC | November | STRS48 - Rick L and Parth P on site for annual calibration. Worning on Well 5 and Well 6, chlorine room. | All Water System ROC General | 2025-11-13
ROC | November | MAP8 - Place pumps back min auto VNRSKS - Activate duty 1 | All Water System ROC General | 2025-11-13
ROC | November | QVW34 - Alex B running generator, turbidity meter maintenance. | All Water System ROC General | 2025-11-13
ROC | November | QVW34, Alex B working on the ammonia pumps and the fittings for the pumps | All Water System ROC General | 2025-11-17
ROC | November | Adeela Khan signing out | All Water System ROC General | 2025-11-17
ROC | November | STPSTL, Jack P on site, running the generator | All Water System ROC General | 2025-11-17
ROC | November | STPSTL - Kyle R on site with contractor working on temp generator will perform utility transfer later today. 08:45 Artour L on site with contractor and electrician testing temporary generator. | All Water System ROC General | 2025-11-13
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-13
ROC | November | JFPS, Sean P on site doing pump tests, Working on pumps 2/3 first then will rotate pumps for pumps 1/4 | All Water System ROC General | 2025-11-14
ROC | November | HLPSYS - Pac communication alarm. Cleared shortly after coming in. Trends appear fine | All Water System ROC General | 2025-11-12
ROC | November | RHMCMD - Back to auto/open to maintain MARS level. | All Water System ROC General | 2025-11-12
ROC | November | HLW1 - Eric S working on Treated free chlorine analyzer. Will check turbidity meter after. | All Water System ROC General | 2025-11-13
ROC | November | NBET - Outlet free Cl2 hi, known issue with analyzer. Called David T, will look into issue Consult | All Water System ROC General | 2025-11-13
ROC | November | NMTKKC - Ryan B. is on site and will be flushing the sample lines. Ryan will be turning the chemical system and analyzers off for approximately half an hour. Ryan directed to disregard alarms during this time | All Water System ROC General | 2025-11-17
ROC | November | HLETYS - Tower Level Hi alarm came in. Checked site and noticed that duty is not active and HLW2 is man/on. Called Benson S. who informed he is on site for a station check and will need the well on for another 15 mins | All Water System ROC General | 2025-11-17
ROC | November | YWS + NYWS Normal NMETIB - Activated duty 1 offset fill cycle from NMETHW. | All Water System ROC General | 2025-11-16
ROC | November | QVW34 - Treated Total Chlorine Lo alarm came in. Checked site. Well 3 is running in schedule mode. Seemed like as dip in trends but came back within 5 mins. Levels are back to optimal range and alarm has cleared | All Water System ROC General | 2025-11-17
ROC | November | YWS+NYWS normal | All Water System ROC General | 2025-11-13
ROC | November | Ethan U signing in | All Water System ROC General | 2025-11-13
ROC | November | SHETCS- Deactivated D1 as per interim AURSOH - Activated D1 NMTKBS- Activated D1 | All Water System ROC General | 2025-11-13
ROC | November | STETTL/STETBR- Andrew called from OCWA and will be flushing in Stouffville zone 1/2 today until the afternoon | All Water System ROC General | 2025-11-13
ROC | November | YWS + NYWS Normal Christian Van Beek signing out. | All Water System ROC General | 2025-11-18
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-16
ROC | November | SHTP- Dave T was able to resolve issues on site and is starting plant up. Will be testing hi/lo temp alarm while on site. | All Water System ROC General | 2025-11-18
ROC | November | NMW12, Jason G on site working on the Cl2 analyzers, directed to disregard alarms on site, Wells 1/2 man/off | All Water System ROC General | 2025-11-18
ROC | November | Carter Dunn Signing Out | All Water System ROC General | 2025-11-11
ROC | November | YWS+NYWS normal | All Water System ROC General | 2025-11-11
ROC | November | GWTP- Patrick F called , site back to normal operation. Disregard Low lift electrical room temp HiHi alarm. | All Water System ROC General | 2025-11-11
ROC | November | VNRSKS, Activated D1 | All Water System ROC General | 2025-11-11
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-12
ROC | November | Angelica Chepiga signing in, weather +4C | All Water System ROC General | 2025-11-13
ROC | November | NMETIB - Activated Duty 1 to offset with NMETHW | All Water System ROC General | 2025-11-13
ROC | November | RHRSTR - Deactivate duty 1 to pull more water from RHMCMD | All Water System ROC General | 2025-11-17
ROC | November | AUPSRR- Post inj total ammonia lo alarm came in. Checked trends sudden drop in free ammonia but spike in total ammonia. Site not dosing currently. Continued to monitor. Total and free ammonia as well as monochloramine trends are flatlined. Waited 10 mins to see if trends would return to normal range. 17:09- AUPSRR- Notified Divya P. Directed to wait another 20 mins for recovery 17:29-AUPSRR- Alarm cleared trends returned to normal range #consult | All Water System ROC General | 2025-11-18
ROC | November | HLW2- Downstream pressure hihi alarm came in as Sharon valve ran in schedule mode. Placed valve in man/close HLW2- Combined/total Cl2 lo alarms came in as a result of increase in pressure cleared alarms once pressure recovered | All Water System ROC General | 2025-11-18
ROC | November | Christian Van Beek signing in. Weather: 0C and clear. | All Water System ROC General | 2025-11-18
ROC | November | Adam Button signing in -3 Snowing | All Water System ROC General | 2025-11-11
ROC | November | NMETHW, Activated D1 to keep the towers offset | All Water System ROC General | 2025-11-12
ROC | November | Angelica Chepiga signing in | All Water System ROC General | 2025-11-12
ROC | November | RHMCMD - back to auto. RHRSTR duty just activated. | All Water System ROC General | 2025-11-12
ROC | November | AURSBS- Activated D1 | All Water System ROC General | 2025-11-13
ROC | November | JFRS- Jordan B on site for generator run HLETYS- Benson S on site testing hi lo temp and tower level alarms, Cleaning analyzers and inspecting chemical systems. Will be going to HLPSYS afterwards to run generator and health and safety inspections QVW34- Alex B on site to work on analyzers and a full chemical system inspection will have wells in local/off for duration of work | All Water System ROC General | 2025-11-11
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-14
ROC | November | ARPS - Pres fault alarm, pressure within range and no noticeable anomalies with pressure reading/trends. Able to clear | All Water System ROC General | 2025-11-14
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-15
ROC | November | MARS - Request (TO) Zhoran for min flow | All Water System ROC General | 2025-11-15
ROC | November | BVSPS - Deactivate duty 1 RHRSTR - Revert start/stop setpoints back to normal operations (65/85%) post Maple pressure mode event ended. | All Water System ROC General | 2025-11-15
ROC | November | STWS Zone 2- Shaun from town of Stouffville informed ROC of flushing in area | All Water System ROC General | 2025-11-11
ROC | November | YWS + NYWS Normal Carter Dunn Signing Out | All Water System ROC General | 2025-11-17
ROC | November | ANVC - Rick L on site for annual calibration. MTW12 - Historian Heartbeat alarm. Well interlocked. Notified Yash S, he will check SCADA. | All Water System ROC General | 2025-11-14
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-16
ROC | November | STPSMR - Tyler C on site for generator test. | All Water System ROC General | 2025-11-14
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-17
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-14
ROC | November | AURSBS - Activate duty 1 as MARS is getting hi | All Water System ROC General | 2025-11-15
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-15
ROC | November | HLETYS - Pac communication failure. Alarm cleared upon acknowledgement. Trends okay HLW2 - PAC communication failure. Alarm cleared upon acknowledgement. Trends okay | All Water System ROC General | 2025-11-15
ROC | November | KLPS27, Disabled PD6 High Pressure mode to place it back to normal operation | All Water System ROC General | 2025-11-17
ROC | November | BLETNL- Parth P on site for annual calibrations. Will call back when working on LIT as it is controlling tower | All Water System ROC General | 2025-11-18
ROC | November | RHMCMD, Placed Valve man/closed RHRSTR, Activated D1 | All Water System ROC General | 2025-11-12
ROC | November | GWTP, Patrick F working on the SO2 alarms, disregard vacuum alarms from site RHPSPA, Placed all pumps back to auto, Lee F is finished on site MKETFA, Parth P is finished on site | All Water System ROC General | 2025-11-18
ROC | November | AURSRR - Divya P called to inform that the residuals have recovered to normal range and requested that the ROC continue to monitor throughout the fill cycle. HLETYS - Ryan W from East Gwillimbury water called to inform that the watermain under repair in EG has been opened. Informed Ryan that the tower is currently draining despite duty 1 being active. Ryan W will contact the operator on site and determine if they are flushing post repair. Contacted Dave T to inform that the watermain has been repaired and valves opened as he requested on the shift report email. #consult | All Water System ROC General | 2025-11-18
ROC | November | HLW2 - Downstream pressure hihi alarm. Spoke with Ryan W from East Gwillimbury who stated that his operator reported that all three valves that were closed are now open and flushing has concluded. Contacted Dave T who is watching the system and is unsure why the pressure would spike to hihi levels and close the HLW2FCV. Dave T stated he will be watching the system and make changes as necessary. Ryan W will call back in one hour to determine if the system is back to normal operations. 19:09 - HLW2 - Dave T called to inform that he tried to slowly open the HLW2 FCV but the downstream pressure HiHi alarm triggered again. Dave T requested a call to Ryan W of East Gwillimbury for more information on any changes they may have made to valving in the system. Dave T stated that the towers would fill overnight but expressed concerns regarding fire flow capacity overnight. Conatcted Ryan W who stated that there was valving changes made in the system, in particular three valves that were previously open are now closed for their commissioning of new watermains and ongoing capital work. Informed Ryan W of Dave T's concerns regarding fire flow capacity. Ryan W requested a summary email of the sequence of events and Dave's concerns but seemed satisfied with the current system parameters. | All Water System ROC General | 2025-11-18
ROC | November | MKETFA - Outlet flow hihi alarm. Checked site, tower is draining at a rapid rate. Trending shows that outlet flow has been high since the duty deactivated earlier today. Outlet flow spiked above the hihi alarm setpoint but has returned to below the setpoint. Cleared alarm and will monitor system. | All Water System ROC General | 2025-11-18
ROC | November | GWTP- Raw water total Cl2 res hihi alarm came in. Disregard on shift report | All Water System ROC General | 2025-11-13
ROC | November | MAPS PD7 - Pumps 2/3 man/off VNPS PD7 - Pumps 1/3 to auto. | All Water System ROC General | 2025-11-13
ROC | November | YWS+NYWS normal Adam Button signing out | All Water System ROC General | 2025-11-18
ROC | November | HLW2- Downstream pressure hihi alarm came in valve is interlocked. Causing discharge pressure hihi at both HLW1/2. Notified Cole will take a look on SCADA and call back Well 2 locked out HLW1- influent free Cl2 lo alarm came in reset after 3 mins. Trends okay MTETNL- Jackie S on site to work Cl2 analyzers and test lo temp alarms 13:30-HLW2- Well interlocked again Cole W thinks a valve has been closed in HL system. Called Kristy B. (905-478-4283 *3850) Kristy B will call around to OPs to inquire about valve work in system. Cole W directed to place FCV2 in manual 25L/s when pressure issues have been resolved and to have OCO go to HLW2 later to reset outstanding alarms and backflush contact tank 13:44- HLW2- Kristy B called back contractor has isolated section of main to replace valve, cutting off the west side of the HL system. Ryan W is ORO for this project and should be contacted for any issues that continue to arise. Cole W has well 1 running to float tower during this work. 13:44- RHPSPA- Lee F on site for vibration testing. req P1/3 to be off and 2/4 to run. Placed P1/3 in man/off and P2/4 in man/on | All Water System ROC General | 2025-11-18
ROC | November | QVETQS- Eric S on site to work on outlet analyzer | All Water System ROC General | 2025-11-11
ROC | November | KSTP, Placed Fluoride pump 2 back to auto and placed the speed deviation back to on mode | All Water System ROC General | 2025-11-18
ROC | November | LSSS- David D on site to check 4160 Switch gear and will be placing P2 man/off for 15 mins **WRONG BOOK** | All Water System ROC General | 2025-11-11
ROC | November | NMVCBA - man/open 50l/s to extend NMETIB drain cycle. Offset with NMETHW. | All Water System ROC General | 2025-11-14
ROC | November | STW12 - Put wells back in auto as Zone 1 duty off STW3 - Place well back in auto | All Water System ROC General | 2025-11-12
ROC | November | MKRSEM, Notified Andrew from Toronto Water to turn off his pumps | All Water System ROC General | 2025-11-12
ROC | November | Angelica Chepiga signing out | All Water System ROC General | 2025-11-12
ROC | November | YWS+NYWS normal | All Water System ROC General | 2025-11-12
ROC | November | QVW34- Treated total Cl2 lo alarm. Wells not active no water directed to users slight dop in residual recovered withing 3 mins. Alarms cleared SHTP- Deactivated SHETCS duty to let reservoir recover as per interim | All Water System ROC General | 2025-11-12
ROC | November | MKRSEM - Brent from TO informed work ongoing and will leave pumps to PD5 off until work is complete | All Water System ROC General | 2025-11-12
ROC | November | KSTP- Raw water turbidity fault alarm came in. Notified Ben H will check site | All Water System ROC General | 2025-11-11
ROC | November | GWTP - ZW1 Permeate turbidity OOR alarm, UV reactor 1 Critical fault alarm. Notified Patrick F, he is working on it. | All Water System ROC General | 2025-11-11
ROC | November | STW12- Red B, Parth P and Rick L on site for annual calibrations will consult operators on site for well status | All Water System ROC General | 2025-11-11
ROC | November | JFPS - Pump 3 back to auto as per Jordan B. | All Water System ROC General | 2025-11-11
ROC | November | GWTP- highlifts Active with UV 1/2 bank alarms outatnding as well as train 1,4,8 alarms. Notified Patrick F. On site still tryting to get plant running and flow to filters cleared alarms on UV bank 2 as it is active. Will call when done on site with update | All Water System ROC General | 2025-11-11
ROC | November | ARPS - Airport Rd Pressure Fault alarm came in. Checked site. Alarm came in multiple times. Checked trends. Called OCWA (Martin) who will look into it 17:04 - Alarm came in again. Called OCWA (Binesh) for an update. Binesh informed that he will speak to his PCS team and give the ROC a call back 17:22 - Binesh called back to inform that due to the pressure interim last week, the pressure setpoints were never put back to the original setpoints. Binesh has changed the setpoints back and all alarms have cleared | All Water System ROC General | 2025-11-17
ROC | November | RHRSTR, Changed D2 start from 58% to 55% | All Water System ROC General | 2025-11-17
ROC | November | MKETFA, Parth P on site doing annual calibrations 11:15, Parth P ready to do the LIT calibrations, notified Toronto operator Andrew to places pumps man/off till the calibrations are complete | All Water System ROC General | 2025-11-17
ROC | November | AUPSRR - Eric S leaving site. All alarms cleared. | All Water System ROC General | 2025-11-14
ROC | November | GWTP - LL pump 3 & 4 hydraulic valv fail to open/uncmd close, surge relief valve open, total chlorine res fault. Informed Dan Z, will take a look | All Water System ROC General | 2025-11-12
ROC | November | GWTP - Stephen B working on Hypo pumps , disregard alarms. | All Water System ROC General | 2025-11-13
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-18
ROC | November | NMETIB - Deactivated duty 1 while NMETHW fills. NMVCBA - Reverted valve setpoint. NMVCIB - Reverted valve setpoint. | All Water System ROC General | 2025-11-18
ROC | November | QVW34 - Activated QVW3 in manual mode to promote water flow south across NCMCRW in accordance with area best practices. | All Water System ROC General | 2025-11-18
ROC | November | KSTP - Fin water total chlorine residual fault and fluoride residual fault alarms. Checked site, plant recently deactivated, no water bring directed to users. This alarm is common following plant shut down and was a long standing disregard on shift report. Will monitor site and clear alarms if possible. If issues persist will contact OCO. | All Water System ROC General | 2025-11-18
ROC | November | HLETYS - Post injection combined chlorine hi alarm. Alarm has triggered and cleared three times. Adjusted the hypo pump 2 max flow setpoint from 175ml/min to 180ml/min to reduce the residual reading. | All Water System ROC General | 2025-11-18
ROC | November | QVW12 - Alex B informed during the replacement injector for chlorine lines, parts were damaged. Wells in local until parts replaced to isolate chlorine gas. QVW34 - Alex B heading to site for PM, health & safety & eyewash alarm 11:00 - Alex B & Ryan B back onsite replace parts for well 1 & 2 | All Water System ROC General | 2025-11-13
ROC | November | VNRSKS - Deactivated D1 , placed VNPS PD7 pumps man/off, | All Water System ROC General | 2025-11-13
ROC | November | GWTP, Phil D on site, working on the turbidity analyzer ANVC, Redempto B is finished on site KSTP, Phil from Ferguson Electric is on site | All Water System ROC General | 2025-11-14
ROC | November | STPS48 - Red B on site for annual calibration. | All Water System ROC General | 2025-11-12
ROC | November | STW12- Travis W on site for analyzer maintenance, Silicate flushing, JHS inspections and will be working on generator with contractors later in the day | All Water System ROC General | 2025-11-11
ROC | November | GWTP - Stepen B called, contractors powering down Low lift, 1 drainage pump available, Stephen B requested disregard alarms for now. | All Water System ROC General | 2025-11-11
ROC | November | JFPS - Station back to normal power, cleared all alarms. Pump 1 failed to start. Notified Ernie H., he will check. 12:55 Ernie H reset alarms. Assigned Pump 1 to duty 1. Station back to normal, all alarms cleared. Ernie H leaving site. | All Water System ROC General | 2025-11-13
ROC | November | SHETCS- Post Injeection Total CL2 HiHi Alarm. Value recovered. Cleared alarm. | All Water System ROC General | 2025-11-13
ROC | November | VNPS PD7- Placed P3 speed setpoint in manual at 50% NBW3- Influent free Cl2 hi then lolo alarm came in. Reset as residual improved. Well started up okay. | All Water System ROC General | 2025-11-11
ROC | November | MTW3 - Joe W performing w/o including generator run and chlorine analyzers cleaning. | All Water System ROC General | 2025-11-11
ROC | November | NMTKKC- Changed D1 stop from 85% to 75% as Joe D done on site | All Water System ROC General | 2025-11-11
ROC | November | STRS48 - Rick L & Parth P onsite for annual calibrations. Confirmed with Travis W all okay to shut highlifts off in the meantime. Place both highlifts 1 & 2 man/off for duration of work NMETIB - Activate duty 1 to offset with Harrywalker | All Water System ROC General | 2025-11-12
ROC | November | NMW136- Jay G on site for Cl2 leak detection test and analyzer maintenance. Wells are man/off | All Water System ROC General | 2025-11-11
ROC | November | LSSS - Marcos T performing w/o on site including - headworks alarms, surge tanks alarms, High level alarms, dialer alarms. | All Water System ROC General | 2025-11-14
ROC | November | AUW14 - Tyler Z & Ernie H onsite working on well 3 wastevalve. Well is man/off | All Water System ROC General | 2025-11-12
ROC | November | HLW2 - Benson S testing chlorine gas alarm, cleaning chlorine analyzers and turbidity meter, chemical systems inspection, PRVs test. | All Water System ROC General | 2025-11-13
ROC | November | MAEP - Eyewash alarm, Followed up wit David T. Is onsite and testing alarm as well as diesel containment flood | All Water System ROC General | 2025-11-13
ROC | November | HLW1 - Combined chlorine hi alarm. Monitored and found reading remaining hi, dropped dosing from 112 to 110% | All Water System ROC General | 2025-11-12
ROC | November | GWTP - Low lift pump 2 hydraulic valve fail to open. Duty is off | All Water System ROC General | 2025-11-15
ROC | November | KCETFS- Joe W on site to test lo temp alarm, work on analyzers and run generator | All Water System ROC General | 2025-11-18
ROC | November | STETTL - West from Town of Stouffville flushing in Zone 2. | All Water System ROC General | 2025-11-14
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-18
ROC | November | Christian Van Beek signing in. Weather: 0C and clear. | All Water System ROC General | 2025-11-15
ROC | November | NMETIB - Activated duty 1 to offset fill cycle from NMETHW | All Water System ROC General | 2025-11-15
ROC | November | BLW12, Placed wells 1/2 man/off for Parth P who is doing tower calibration | All Water System ROC General | 2025-11-18
ROC | November | ARPS- discharge flow lolo alarm came in. Cleared right away MARS level getting hi and down stream storages are full will continue to monitor | All Water System ROC General | 2025-11-13
ROC | November | YWS + NYWS Normal Carter Dunn Signing Out | All Water System ROC General | 2025-11-18
ROC | November | KSETDP - Chlorine room gas detector fault alarm, Chlorine room gas leak alarm - Patrick F on site investigating. | All Water System ROC General | 2025-11-14
ROC | November | GWTP - Chris S completed work on Low lifts. Notified Stephen N. Constrictors still working onsite as per Stephen B. | All Water System ROC General | 2025-11-11
ROC | November | ARPS - Airport rd free and total ammonia fault alarms , back to normal in a few minutes. Cleared alarms. | All Water System ROC General | 2025-11-11
ROC | November | MKRSEM - Free chlorine residual Fault alarm, Jack P on site, requested to clear alarm. | All Water System ROC General | 2025-11-12
ROC | November | Angelica Chepiga signing in | All Water System ROC General | 2025-11-14
ROC | November | VNRSKS - VNPS PD7 pumps 1 and 3 man/stop, Duty just deactivated. 14:54 - MAPS PD7 pumps 1 and 2 to auto. | All Water System ROC General | 2025-11-11
ROC | November | Rutherford/ARPS/YPFM, Rob P called, they are reverting the isolation, notified ARPS operator Bineesh that they are reverting the isolation. Once Bineesh hears from the ROC a second time, he can make changes going back to normal operation 15:02, contacted Bineesh to turn off the pump at ARPS | All Water System ROC General | 2025-11-14
ROC | November | NMW12- Jay G done on site will be heading to NMTKKC NMW136- Eric S on site to work on total Cl2 analyzer | All Water System ROC General | 2025-11-18
ROC | November | YWS+NYWS normal Adam Button signing out | All Water System ROC General | 2025-11-11
ROC | November | AUW14, Eric S on site working on well 1 waste valve | All Water System ROC General | 2025-11-18
ROC | November | ANW23 - Res Inlet Free Chlorine Low alrm, wells 2&3 running. Benson S on his way to site, will check - as per Jacob M. | All Water System ROC General | 2025-11-12
ROC | November | QVW12 - Ryan B and Alex B finished on site. | All Water System ROC General | 2025-11-13
ROC | November | MKRSEM- Resevoir 1 level lo alarm came in. Called Metro spoke with Peter to start 2 pumps | All Water System ROC General | 2025-11-12
ROC | November | HLW2 - Influent free/combined lolo. Followed up with Benson S onsite and aware, is backflushing | All Water System ROC General | 2025-11-13
ROC | November | KSTP - Fin water flouride res lolo, checked site, reading came back to normal ranger BLW12 - Station turbidity fault. Nothing locked out, wells off. Informed Dan Z, disregard for the weekend as long as pumps are not interlocked. Informed of above higher than normal turbidity readings but within range. Silicate tank trend still going down when active Consult | All Water System ROC General | 2025-11-15
ROC | November | MKETFA - Free chlorine hi alarm. Checked site, trending shows a steady increase of the free chlorine reading. Sent email to area ops as directed by shift report. | All Water System ROC General | 2025-11-17
ROC | November | NMETIB, Jerry Z on site, testing eye wash alarm and testing flood alarm | All Water System ROC General | 2025-11-18
ROC | November | SHETCS - Hypo pump 2 failed to start alarm. Hypo pump 1 is running. Alarm cleared. | All Water System ROC General | 2025-11-12
ROC | November | HLW2 - Treated free chlorine hi alarm. Rotated ammonia pump duty. | All Water System ROC General | 2025-11-18
ROC | November | MARS - HiHi level alarm. Activated VNRSKS duty 1 to drawdown MARS level. | All Water System ROC General | 2025-11-19
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-19
ROC | November | MKRSEM - Low level alarm. Stopped the pumps at MKPSSA, reverted the valves at MKRSMR to auto mode. Called Toronto Water and requested they activate two pumps to fill MKRSEM and place the COTFA PD6 pumps into auto mode. | All Water System ROC General | 2025-11-15
ROC | November | KSTP - Filter 1 backwash OOS, appears filter 2 just went through a backwash causing clearwell to drop in level. OOS due to clearwell condition. Informed Dan Z. Disregard for now as we wait for clearwell to fill back up. Consult | All Water System ROC General | 2025-11-15
ROC | November | NMVCBA - Artour L finished at site with work on PIT | All Water System ROC General | 2025-11-13
ROC | November | GWTP- Raw Water Total Chlorine Res HiHi Alarm. Disregard as per SCADA Report. | All Water System ROC General | 2025-11-13
ROC | November | KSTP - Low lift pumps 2&3 speed OOR alarms. Notified Donald M. He is on site, Dan B and Tyler C working on Low lifts. | All Water System ROC General | 2025-11-14
ROC | November | STPSMR, Artour L is finished on site | All Water System ROC General | 2025-11-18
ROC | November | MTW12, Placed well 2 back to auto, Rick L is finished on site | All Water System ROC General | 2025-11-18
ROC | November | SHETCS - Hypo pump 1 fail to start alarm. Checked site, duty rotated to hypo pump 2. Operations are normal. Reset alarm. | All Water System ROC General | 2025-11-18
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-19
ROC | November | QVW34 - Deactivated QVW3 and placed it in auto mode. MKRSEM - Called Toronto Water (Mehdi) and requested they activate two pumps to push flow to MKRSEM. | All Water System ROC General | 2025-11-19
ROC | November | MARS- Cell1 (North) Lvl Lo Alarm. Called Toronto (Peter) and requested to increase flow. | All Water System ROC General | 2025-11-13
ROC | November | BVPS - Historian heartbeat alarm. Checked site, trending appears normal. Pumps are not active but duty 1 will activate soon. Unable to clear alarm, contacted Yash S who will check the system. Created CMU5#W11446320 #consult #CMU5 | All Water System ROC General | 2025-11-16
ROC | November | SHTP, Sean P on site doing a load test | All Water System ROC General | 2025-11-18
ROC | November | MTW3- Jackie S done on site will be activating D1 and placing well in auto 12:06- MTW3- Well didn't start up in duty. Jackie P left well off for now and will allow it to rest until duty starts 12:06-KSTP- Donald M on site for PACL line maintenance | All Water System ROC General | 2025-11-18
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-16
ROC | November | STW12/STW3 - Place well 2 & 3 back in auto QVW34 - Place well 3 back in auto | All Water System ROC General | 2025-11-16
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-16
ROC | November | MKRSEM - Brett from Toronto water notified about Milliken PD5 pumps isolation for 3 hours. Res @ 66%. | All Water System ROC General | 2025-11-13
ROC | November | AUPSRR - Post injection free chlorine hihi alarm. Checked site, trending shows a spike of the free chlorine reading which returned to normal range within one reading interval. Reset alarm. NRETCR - Outlet total chlorine low alarm. Checked site, tower is currently filling. Trending shows a small dip of the outlet total chlorine reading which recovered within two reading intervals. Reset alarm. | All Water System ROC General | 2025-11-15
ROC | November | MKRSEM - Request TO (Zhoran) to drop both pumps | All Water System ROC General | 2025-11-15
ROC | November | RHPSPA - Hydro power fail alarm and PD6 surge valve 1 open alarm. Checked site, duty just activated, one pump running. Generator did not activate and the ATS is pointing to town hydro indicating no power fail. Possible power blip. Surge valve ahs closed and second duty 1 pump is activating. Operations normal. Reset alarms. JFPS - VC UPS ATS source S2 alarm. Checked site, generator is not active, ATS pointing to town hydro. Pumps were not active when the alarm occurred. Operations normal. Reset alarm | All Water System ROC General | 2025-11-16
ROC | November | HLETPR - Obstruction beacon fault alarm. Contacted Nav Canada's London Flight Information Centre and spoke with David P. Provided David the necessary details of the tower. Requested a follow up call for November 21 at 07:30 at which point Nav Canada will confirm if the issue has been resolved. Created CMU5#W11453019 for the on call electrician as per the procedure. Sent email to Area Ops and CMS team lead as per the procedure. #CMU5 | All Water System ROC General | 2025-11-19
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-19
ROC | November | AUW14, Jerry Z on site starting the step test, directed to disregard hi flow alarms from wells | All Water System ROC General | 2025-11-18
ROC | November | Christian Van Beek signing out. | All Water System ROC General | 2025-11-16
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-17
ROC | November | MAPS PD7 - Lee F. is on site and will be working on pump 2. Duty is not active. Placed pump 2 man/off as Lee will be working on the discharge valve 11:17 - Lee F. is finished working on PD7 pump 2. Placed pump back to auto MAPS PD8 - Lee F. requested pump 4 be placed on for maintenance related work. Duty is active. Rotated pump duties so pump 4 is in duty 1 and pump 3 is now in duty 3 | All Water System ROC General | 2025-11-17
ROC | November | GWTP - Power fail alarm. Checked site, generator is running. Plant has interlocks across the system. Plant was not active at the time of the hydro fail, including UV system which was off. No water being directed to the distribution system. Contacted Dan Z to inform and allow her to double check the system parameters. KSTP - Power failure alarm. Checked site, most alarms cleared. Plant was not active during time of the hydro failure; no water being directed to distribution system. Two alarms outstanding, filter 1 and 2 influent valve uncommanded close. Informed Dan Z who will check the system. SUETDR - Hydro fail alarm. Checked site, no generator on site. No additional alarms present. Able to reset alarm indicating power has been restored. KSETDP - Site power fail alarm. Checked site, no generator on site. Both chlorinators have faulted and an altitude valve fail to close alarm occurred. Tower is draining to chlorinators not active. Altitude valve is manual open. Able to reset alarms, power appears restored. Informed Dan Z as this is a priority tower. Checked Hydro One power outage map and noted numerous power failures throughout the Keswick/Sutton/Georgina area. Crews are working in the area to restore power. #consult | All Water System ROC General | 2025-11-16
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-16
ROC | November | RHPSPA - Found pump 4 discharge valve 1 failing to close. Stuck partially open. Placed pump 4 man/off. Emailed team | All Water System ROC General | 2025-11-17
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-17
ROC | November | AURSBS - Activate duty 1 as MARS continues to climb with MARS - Called TO confirming already pushing min flow, able to throttle down slightly further for only 30min | All Water System ROC General | 2025-11-17
ROC | November | NMVCBA- Placed valve in manual 50L/s to slow NMETIB drain and keep offset with NMETHW | All Water System ROC General | 2025-11-13
ROC | November | VNPS- Placed PD8 Duty 1 pumps man/off MAPS- Placed pumps 1,2,3 back into auto | All Water System ROC General | 2025-11-13
ROC | November | AUPSRR - Historian heartbeat alarm. Checked site, operations appear normal but trending shows a gap. Trends have continued following the gap. Contacted Yash S and created CMU5#W11453030 #consult #CMU5 | All Water System ROC General | 2025-11-19
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-18
ROC | November | MARS - Cell 1 level hihi alarm. Activated VNRSKS duty 1 to drawdown MARS. 02:49 - MARS - Level still increasing with VNRSKS duty 1 active. Deactivated duty 1 at RHRSTR to prevent water pushing from Richmond Hill to Vaughan across the highway 7 meter chamber. | All Water System ROC General | 2025-11-18
ROC | November | SHTP - Reservoir total chlorine residual lolo alarm returned following the analyzer fault. Called Dave T who directed to deactivate the plant and deactivate the SHETCS duty so the high lift pumps shut down. Made necessary changes. Dave T will respond to site, created CMU5#W11450182. Original start setpoint was 4.50m and original stop setpoint was 5.40m. #consult #CMU5 | All Water System ROC General | 2025-11-18
ROC | November | MKETFA- Parth P on site to work on Cl2 analyzers | All Water System ROC General | 2025-11-18
ROC | November | STETBR, Travis W on site doing health and safety checks and also looking at the AITs on site | All Water System ROC General | 2025-11-18
ROC | November | NMW136- Treated total / combined Cl2 lo alarm came in. Wells not not active recovered after 3 mins alarm cleared | All Water System ROC General | 2025-11-18
ROC | November | HLETPR- Cole W and Joe W on site for PMs will be testing hi lo temp | All Water System ROC General | 2025-11-18
ROC | November | BLETNL, Parth P finished on site | All Water System ROC General | 2025-11-18
ROC | November | KSTP, Donald M has placed the low lift pumps Local/off, Plant will be off for the night and the raw water supply system will be off, directed to disregard alarms from site as it will be off however incase of emergency, notify on call operator | All Water System ROC General | 2025-11-17
ROC | November | Christian Van Beek signing in. Weather: 0C and clear. | All Water System ROC General | 2025-11-17
ROC | November | MKRSEM - Called Toronto Water (Mehdi) and requested they activate two pumps to push flow to MKRSEM. | All Water System ROC General | 2025-11-17
ROC | November | STETTL- STETTL to STRS48 comm alarm trends okay. STPSTL- STPSTL to STETBR comm alarm trends okay STRS48- STRS48 to STETTL comm alarm trends okay STETBR- STETBR to STPSTL comm alarm trends okay Cleared all alarms | All Water System ROC General | 2025-11-13
ROC | November | MAPS PD7- Placed all pumps in auto RHVCEM- placed valve back in man/open at 15% | All Water System ROC General | 2025-11-13
ROC | November | NMW12- Treated total and combined Cl2 lo alarm came in. Wells not active no water directed to users will clear when trends recover | All Water System ROC General | 2025-11-13
ROC | November | STPSMR- Artour L on site with contractors to work on generator connection points and test alarms MARS- Jordan B on site to test hi lo level alarm and to work on Cl2 analyzers | All Water System ROC General | 2025-11-18
ROC | November | NMVCBA Changed flow setpoints from 40L/s to 80L/s NMVCIB- Changed flow setpoints from 80L/s to 40L/s | All Water System ROC General | 2025-11-18
ROC | November | NMTKKC, Joe D turned off the generator on site | All Water System ROC General | 2025-11-14
ROC | November | MKRSEM - Request TO (Zhoron) to drop both pumps | All Water System ROC General | 2025-11-14
ROC | November | Carter Dunn Signing In | All Water System ROC General | 2025-11-17
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-17
ROC | November | STPSTL - Kyle R called, temporary generator test completed. Station back to normal power. Artour L finished on site. | All Water System ROC General | 2025-11-13
ROC | November | NMW15- Combined CL2 lo alarm came in, well not active no water directed to users. Residual should recover on D1 start. Will reset alarm RHPSPA- Discharge flow lolo alarm came in as D1 deactivated cleared alarm | All Water System ROC General | 2025-11-11
ROC | November | Ethan U signing in Weather 2. | All Water System ROC General | 2025-11-12
ROC | November | Carter Dunn Signing Out | All Water System ROC General | 2025-11-11
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-14
ROC | November | SUETDR - Aaron W called to request to inform Town of Georgina operator to also close the valve after duty 1 has been met due to ongoing issue with PRV valve not responding. Informed Will from town of Georgina on-call about action needed to first open valve who said will follow-up with his team lead Jeff. Dan Z, Aaron W, & Stephen B are aware of situation and that Will from town of Georgina has been notified. No ETA present from Town of Georgina, Dan Z had been given contact of Will and will also followup with their operator for any further questions. 17:37 - Christina L requested CMU5 for Bill V responding to broken valve in proximity to the front of GWTP. First chamber outside in front of plant. Confirmed with Cristina this is a separate matter from the PRV valve with Town of Georgina CMU = 11443695 | All Water System ROC General | 2025-11-13
ROC | November | MKPSSA - Finding res continuing to climb without pumps running MKPSSA - MV1 man/close & MV6 man/open 5:50 - MV1 man/open, MV6 man/close change made MKPSSA - Man/start pump 3 | All Water System ROC General | 2025-11-15
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-15
ROC | November | TMC317, Notified Toronto to push more flow to MARS VNRSKS, Deactivated D1, Placed pumps man/off VNPS PD7, Placed pumps 1/3 in auto | All Water System ROC General | 2025-11-14
ROC | November | NMTKKC, Joe D is heading to site to run the generator, will be on generator power for the next 8 hours. Joe D will be meeting a contractor on site | All Water System ROC General | 2025-11-14
ROC | November | MKETFA - Free chlorine hihi alarm. Checked site, trending is showing a steady increase of free chlorine residual. Disregard as per the shift report, sent email to OCO as per shift report. | All Water System ROC General | 2025-11-18
ROC | November | NMVCBA- Placed valve back into auto | All Water System ROC General | 2025-11-14
ROC | November | Adam Button signing out | All Water System ROC General | 2025-11-13
ROC | November | NMW12 - Treated total chlorine lolo and combined chlorine lolo alarms. Checked site, well is not running. No water being directed to users. Trending shows a sudden drop of the chlorine readings which are recovering. Will monitor values. KCETDS - Outlet total chlorine residual lolo alarm. Checked site, trending shows a sudden drop of the total chlorine residual reading. The value recovered within two reading intervals, reset alarm. | All Water System ROC General | 2025-11-15
ROC | November | HLW2 - PAC comm fail alarm has eliminated visibility of site on SCADA. Tower inlet flow has reduced and reversed indicating that the well has shut down. The HLW2FCV and the Sharon valve also are not showing on SCADA. Flow at HLETYS has reversed which is resulting in abnormally high combined and total chlorine readings on the pre-injection analyzer. Conatcted Dave T who will head to site to collect a grab sample. Dave T directed to deactivate the system duty until communications return. Created CMU5#W11446125 HLW2 - Dave T called back to inform that he has reported an adverse event related to the pre-injection combined chlorine readings and will complete the required paperwork. #consult #CMU5 | All Water System ROC General | 2025-11-15
ROC | November | GRTPLL - Raw water total chlorine hihi alarm. Checked site, treatment plant is active. Value returned to normal range within twenty minutes. Disregard a per the shift report. | All Water System ROC General | 2025-11-15
ROC | November | HLW1 - Combined chlorine hi again, dropped chlorinator 1 dossing from 113 to 110% | All Water System ROC General | 2025-11-12
ROC | November | ARPS- Discharge flow lo alarm came in. Slight dip in trends recovered right away alarm cleared VNPS PD7 - Placed P1 in man/off an MAPS PD7- Placed P2-4 in auto | All Water System ROC General | 2025-11-12
ROC | November | Carter Dunn Signing In, 0D/Clear | All Water System ROC General | 2025-11-11
ROC | November | MARS, Notified Toronto operator Andrew to bring flow back to normal levels | All Water System ROC General | 2025-11-11
ROC | November | GWTP - Low lift, Stephen B completed work on site, Low lifts back to auto operations, drainage pump 2 alarm outstanding/disregard. | All Water System ROC General | 2025-11-11
ROC | November | RHRSTR - Deactivated D1 at 89% and man/open RHMCMD to maintain MARS level. AURSBS - activated Duty 1. | All Water System ROC General | 2025-11-12
ROC | November | YWS + NYWS Normal BVPS, Placed pumps 1/2/3 back to auto | All Water System ROC General | 2025-11-14
ROC | November | STW12/STW3 - Man/start well 2 & 3 as Bethesda duty active | All Water System ROC General | 2025-11-15
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-15
ROC | November | GWTP - Dan Z called to inform that she has reset the Generator alarms and activated the system duty. The plant is operating as expected and she is leaving site. | All Water System ROC General | 2025-11-16
ROC | November | Adeela Khan signing in. Weather: -1 and Snowing | All Water System ROC General | 2025-11-17
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-15
ROC | November | RHMCMD - Placed valve in auto mode. | All Water System ROC General | 2025-11-15
ROC | November | MTETNL - Jackie S onsite running well 1 in local. Place chemical pumps both silicate and chlorine pumps man/off | All Water System ROC General | 2025-11-12
ROC | November | NMTKBS- Activated D1. | All Water System ROC General | 2025-11-11
ROC | November | AUETOH- Activated D1 NMETIB- Deactivated D1 to offset from NMETHW as per shift report | All Water System ROC General | 2025-11-13
ROC | November | GWTP- Low lift P3/4 hydraulic valve uncomm close alarm came in reset as per shift report P1 running with no issue | All Water System ROC General | 2025-11-13
ROC | November | MKRSEM- Called Metro spoke with Peter to stop pumping to reservoir. | All Water System ROC General | 2025-11-13
ROC | November | HLW1 - Silicate pump 1 fault on startup. Silicate pump 2 now duty 1. Able to clear alarm. Will monitor | All Water System ROC General | 2025-11-12
ROC | November | MARS, Notified Toronto operator Andrew to go back to normal flow | All Water System ROC General | 2025-11-11
ROC | November | RHMCMD, Placed valve man/open RHRSTR, Deactivated D1 | All Water System ROC General | 2025-11-12
ROC | November | ARPS- Total ammonia fault alarm came in. Continued to monitor cleared alarm after 5 mins as residual improved | All Water System ROC General | 2025-11-11
ROC | November | AUW14 - Effluent free chlorine lolo switch. Well running in man/on position. Informed Jerry Z of situation, will take a look. | All Water System ROC General | 2025-11-12
ROC | November | RHMCMD - man/close. | All Water System ROC General | 2025-11-12
ROC | November | GWTP - No sodium Hypochlorite pumps available, chlorine pump 1 and 2 not available. Called Dan Z, requested disregard, alarms will be outstanding until tomorrow. | All Water System ROC General | 2025-11-12
ROC | November | Ethan Ullalkar signing out. | All Water System ROC General | 2025-11-15
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-15
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-15
ROC | November | MAPS PD8 - Activated Duty 1 to maintain MARS level. | All Water System ROC General | 2025-11-11
ROC | November | AURSBS - Deactivated Duty 1 as per Interim memo to help with MARS level. | All Water System ROC General | 2025-11-13
ROC | November | HLW2- Downstream pressure hihi. Able to clear alarm | All Water System ROC General | 2025-11-11
ROC | November | MARS - Low level alarm, deactivated AURSBS duty 1. MARS - Called Toronto water (Zoran), requested to increase flow. | All Water System ROC General | 2025-11-12
ROC | November | NBET - Dave T called, requested disregard Outlet Free chlorine High alarm until tomorrow. | All Water System ROC General | 2025-11-13
ROC | November | NMTKKC - Joe D cleaning scam scan and chlorine analyzers. He placed all chem pumps man/off for the duration of work and requested to change duty 1 stop from 75 to 85%. Disregard chem scan offline alarm for now. | All Water System ROC General | 2025-11-11
ROC | November | ARPS - Dinesh from Peel called to inform they will be swapping from pump 5 to pump 3. They placed pump 5 man/on and pump 3 ran in auto until they could man/stop pump 3 | All Water System ROC General | 2025-11-12
ROC | November | NMTKBS - PAC Communication alarm, notified Yash S. He will check SCADA. | All Water System ROC General | 2025-11-14
ROC | November | QVW34 - Man/start well 3 as flow heading towards QVET via ringwell | All Water System ROC General | 2025-11-15
ROC | November | ARPS, Notified Jerry from OCWA to bring everything back to normal operation from pressure mode to level mode and pumps back to auto 16:26, GWTP, ZW7 Shutdown Alarm, notified Dan Z, She will look into it consult | All Water System ROC General | 2025-11-14
ROC | November | KSTP - Settled water turbidity hihi alarm. Checked site, treatment plant is offline for intake inspection tomorrow. Trending shows a sudden spike of the settled water turbidity value which is returning to normal range. Will clear alarms once possible. SHTP - Reservoir total chlorine residual fault alarm returned. Previous conversation with Dave T stated that this analyzer can alter dosing factors if reading incorrectly. Will monitor the value to determine if an additional call out is necessary. | All Water System ROC General | 2025-11-18
ROC | November | AUW14- Treated free Cl2 hihi alarm came in cleared after 6 mins | All Water System ROC General | 2025-11-11
ROC | November | GWTP - Low lift , Chemical room gas level HiHi alarm - Phil D working with Stephen B on site. Disregard alarm. | All Water System ROC General | 2025-11-11
ROC | November | MAP8 - Air handling unit general alarm. Confirmed with David T he is monitoring and will see if it can be reset by end of day | All Water System ROC General | 2025-11-13
ROC | November | VNRSKS - Placed MAPS PD7 pumps man/off, VNPS PD7 to spit mode/pumps 1 &3 to auto. | All Water System ROC General | 2025-11-12
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-12
ROC | November | MARS- Called Metro spoke with Brett to increase flow to reservoir AUPSRR- Will M on site to run generator and test Cl2 leak dtection system. Later today will be cleaning analyzers on site . | All Water System ROC General | 2025-11-11
ROC | November | NBW3 - Influent free chlorine lolo alarm. Checked site, well recently started in schedule mode. Trending shows a drop of the influent free chlorine reading shortly after well activation. The influent reading returned to normal range following the dip. Placed Hypo pump 2 back into duty 1, cleared alarm and monitored well activation. | All Water System ROC General | 2025-11-15
ROC | November | NBW5 - Joe W on site for generator test and chlorine analyzers /turbidity meter maintenance. | All Water System ROC General | 2025-11-13
ROC | November | STETBR - Red B completed work on site. | All Water System ROC General | 2025-11-14
ROC | November | KSETDP - Inlet Total chlorine HiHi alarm, disregard as per SCADA review. | All Water System ROC General | 2025-11-11
ROC | November | NMETHW, Deactivated D1 | All Water System ROC General | 2025-11-11
ROC | November | KCETDS, Activated D1 | All Water System ROC General | 2025-11-12
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-12
ROC | November | AURSOH, Deactivated D1 | All Water System ROC General | 2025-11-12
ROC | November | KCETDS, Deactivated D1 | All Water System ROC General | 2025-11-12
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-12
ROC | November | YWS + NYWS Normal Connor Smith signing out | All Water System ROC General | 2025-11-14
ROC | November | NMPSKC - Joe D called, contractor running generator on site until 15:00pm. | All Water System ROC General | 2025-11-14
ROC | November | GWTP - Stephen B requested disregard alarms from Air Blowers. Working on it. | All Water System ROC General | 2025-11-11
ROC | November | STW12 - Rick L completed work on site. | All Water System ROC General | 2025-11-11
ROC | November | Ethan Ullalkar signing out. | All Water System ROC General | 2025-11-13
ROC | November | Angelica Chepiga signing out | All Water System ROC General | 2025-11-13
ROC | November | ARPS- Airport Rd Discharge Flow LoLo Alarm. Alarm cleared. | All Water System ROC General | 2025-11-14
ROC | November | QVETQS - Inlet total chlorine HiHi switch alarm- Eric S working on it. | All Water System ROC General | 2025-11-11
ROC | November | RHMCMD - man/close to maintain MARS level. | All Water System ROC General | 2025-11-12
ROC | November | Angelica Chepiga signing out | All Water System ROC General | 2025-11-11
ROC | November | QVW34 - Kyle R. is on site and requested pump 4 man/off for about an hour as he is commissioning a VFD. Well has been placed man/off as Kyle needs to de energize. | All Water System ROC General | 2025-11-17
ROC | November | KLET27 - Historian heartbeat alarm. Checked site, trending is unaffected. Unable to clear alarm. Contacted Yas S and created CMU5#W11449964 #consult #CMU5 | All Water System ROC General | 2025-11-18
ROC | November | NMVCBA - Artour L working on PIT1 jumping values KCETFS - Evgeni S rebooting OIT STRS48 - Place wells 5 & 6 as well as highlifts back in auto as requested by Joe M. Path P & Rick L leaving site BLETNL - Revert duty 1 start from 55% back to 72% as requested by Joe M | All Water System ROC General | 2025-11-13
ROC | November | MARS - Low levels at reservoir. Called Toronto Water (Andrew) and requested to go back to normal flow | All Water System ROC General | 2025-11-17
ROC | November | QVW34 - Activated QVW3 to push flow south across the Ringwell Drive meter chamber. | All Water System ROC General | 2025-11-17
ROC | November | NBET, Joe W is on site, working on the Cl2 analyzers | All Water System ROC General | 2025-11-14
ROC | November | MKRSEM- Called Toronto (Peter) and requested pumps off. | All Water System ROC General | 2025-11-14
ROC | November | QVW34 - Deactivated QVW3 and placed in auto. | All Water System ROC General | 2025-11-18
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-18
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-18
ROC | November | AUPSRR - Will M onsite for analyzer maintenance on CL17 & may trigger Cl2 alarms | All Water System ROC General | 2025-11-13
ROC | November | NMETIB - Deactivated duty while NMETHW fills. | All Water System ROC General | 2025-11-15
ROC | November | BVPS - Duty just activated for RHRSTR and noted that BVPS had three pumps running. Duty 2 start setpoint is the same as the duty 1 start setpoint. Unsure what the original start setpoint was, changed duty 2 start setpoint to 60%. Sent email to area and Linear ops to investigate the original duty 2 start setpoint. Called Dan Z and Ryan B as central and east ORO to inform them of the situation as a third pump activation at BVPS requires ORO approval. #consult | All Water System ROC General | 2025-11-15
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-15
ROC | November | HLW2 - Downstream pressure hihi alarm. Checked site, the Sharon valve has opened in schedule mode which increased the pressure beyond the hihi alarm threshold and closed the duty 1 HLW2FCV. When the Sharon valve closes after thirty minutes the alarm can be cleared and the HLW2 FCV will open. | All Water System ROC General | 2025-11-15
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-15
ROC | November | NMETHW - Combined chlorine & total chlorine lo. No flow leaving tower. Will monitor 15:12 - Residual back no normal range as flow leaving tower | All Water System ROC General | 2025-11-17
ROC | November | VNPSAP - Site power failure and control panel power failure alarms. Checked site, pumps were active when alarms occurred. No generator on site. Tower is approximately halfway through fill cycle. Unable to clear alarms. Tower still filling because the supply valve is open in local mode. While monitoring the control panel power fail alarm cleared itself, all pumps cleared their interlock status and the supply valve returned to auto mode. Monitored system to ensure pumps and valves operated as expected. 15:22 - System not activating following power failure. Deactivated and then reactivated duty 1. Monitored pump start. | All Water System ROC General | 2025-11-16
ROC | November | GRTPLL - Raw water total chlorine residual hihi alarm. Checked site, trending shows a sudden spike of the total chlorine residual. Residual returned to normal range within twenty minutes. Disregard as per the shift report. | All Water System ROC General | 2025-11-16
ROC | November | GWTP - Low lift, Stephen B performing testing on site , running pumps in manual, requested disregard alarms for now. | All Water System ROC General | 2025-11-11
ROC | November | RHMCMD- Placed valve in manual closed | All Water System ROC General | 2025-11-13
ROC | November | RHMCMD - Man/close valve | All Water System ROC General | 2025-11-16
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-16
ROC | November | HLW1 - Eric S finished at site | All Water System ROC General | 2025-11-13
ROC | November | Christian Van Beek signing out. | All Water System ROC General | 2025-11-15
ROC | November | SHTP - Reservoir total chlorine fault alarm. Checked site, plant is currently off. Reservoir total chlorine trend appears normal. While monitoring the reservoir total chlorine reading showed an abnormal dip and triggered the low alarm and the low low alarm. Likely a false reading for the analyzer as this is abnormal behavior. Contacted Dave T who will check SCADA. 02:45 - SHTP - Reservoir total chlorine residual has returned to normal range. Able to reset all alarms. #consult | All Water System ROC General | 2025-11-18
ROC | November | Connor Smith signing in 4C Cloudy | All Water System ROC General | 2025-11-13
ROC | November | MAPS, Courtney from Tobare is on site | All Water System ROC General | 2025-11-12
ROC | November | YWS + NYWS NORMAL | All Water System ROC General | 2025-11-13
ROC | November | YWS + NYWS NORMAL | All Water System ROC General | 2025-11-13
ROC | November | MAPS- Placed PD8 pumps man/off VNPS- Placed PD7 duty 1 pumps into auto | All Water System ROC General | 2025-11-13
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-15
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-15
ROC | November | BLW12 - Station turbidity OOR, tower draining. Wells locked out. Informed Dan Z on issue. Will attend site tomorrow Consult | All Water System ROC General | 2025-11-16
ROC | November | Ethan Ullalkar signing out. | All Water System ROC General | 2025-11-16
ROC | November | NMW136- Influent free Cl2 lo alarm came in on well start up. Trends recovered and alarm cleared after 3 mins | All Water System ROC General | 2025-11-18
ROC | November | QVW34 - Alex B on site for chlorine analyzers maintenance. | All Water System ROC General | 2025-11-12
ROC | November | GWTP- Low Lift Surge Relief Valve Open Alarm. Alarm cleared. | All Water System ROC General | 2025-11-13
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-14
ROC | November | KSTP - Filter 1 backwash OOS alarm outstanding from last night. Filter has completed its backwash sequence, reset alarm as per Ethan U and Dan Z consultation. | All Water System ROC General | 2025-11-16
ROC | November | BLW12 - Dan Z called to inquire about the status if BLW12. Dan Z requested that the current alarms be cleared to determine if the interlock on the pumps will lift. All alarms cleared except for the station turbidity fault alarm. The interlock lifted. Dan Z directed to activate duty 1 and call her if the wells lock out again. | All Water System ROC General | 2025-11-16
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-16
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-16
ROC | November | AUPSOH - Discharge flow lolo alarm. Checked site, Flow is normal and pump speed is normal. Reset alarm. | All Water System ROC General | 2025-11-16
ROC | November | STW12/3- Placed P2/3 in man/on as per interim GWTP- Sutton header fluoride lo alarm came in. Fluoride pump speed dipped waited to see if residual recovered did not. Notified Stephen B will take a look on SCADA | All Water System ROC General | 2025-11-18
ROC | November | GWTP - Varius UV related alarms including faults. Dan Z on site activating plant following power failure and generator fault alarms. | All Water System ROC General | 2025-11-16
ROC | November | NMETIB - Deactivated duty 1 while NMETHW fills. | All Water System ROC General | 2025-11-16
ROC | November | YWS + NYWS Normal | All Water System ROC General | 2025-11-16
ROC | November | SHTP- Raw Water Tank Flow Hart Comm Alarm. Notified David T. Site operations look normal. Can disregard for the night. CONSULT | All Water System ROC General | 2025-11-13
ROC | November | MARS- Called Toronto (Peter) and requested back to normal flow. | All Water System ROC General | 2025-11-13
ROC | November | Carter Dunn Signing In | All Water System ROC General | 2025-11-18
ROC | November | Carter Dunn Signing Out | All Water System ROC General | 2025-11-12
ROC | November | SHTP - Drop filter start res level from 4.5 to 4.25m in order to deactivate duty 1 to stop low lifts and place low lift 2-4 man/off as per interim | All Water System ROC General | 2025-11-13
ROC | November | NBW3 - Influent free chlorine lolo switch. Joe W aware and heading to site. | All Water System ROC General | 2025-11-13
ROC | November | SHETCS - Hypo pump 1 uncommanded stop alarm, hypo pump 2 switched to Duty 1/not running. Notified David T, he will check SCADA. | All Water System ROC General | 2025-11-14
ROC | November | QVW12 - Lee F finished on site. 12:59 Placed Well 2 pump back to auto, ok with Alex B. | All Water System ROC General | 2025-11-14
ROC | November | KSETDP- Patrick F on site testing lo temp alarm, performing JHS checks and working on Cl2 analyzers | All Water System ROC General | 2025-11-18
ROC | November | NRETCR- Will M on site will be working on Cl2 analyzers and testing lo temp alarms | All Water System ROC General | 2025-11-18
ROC | November | BLW12 - Joe M onsite running generator cleaning chlorine and turbidimeter | All Water System ROC General | 2025-11-13
ROC | November | BVPS - Jack P on site for generator test. Requested man/stop all pumps. | All Water System ROC General | 2025-11-13
ROC | November | AUPSRR - Eric S testing chlorine leak alarm. | All Water System ROC General | 2025-11-14
ROC | November | STETTL- Dan Z informed ROC that town of Stouffville is flushing in zone 1/2 today | All Water System ROC General | 2025-11-18
ROC | November | QVW12, Alex B on site working on the Cl2 system/Gas Detection/Analyzer Maint/Ammonia System | All Water System ROC General | 2025-11-18
ROC | November | SHETCS- Dave T on site to test lo temp alar, Work on Cl2 analyzers and perform hypo system maintenance MTW3- Jackie S and Jack P on site to work on silicate system. Well in man/off | All Water System ROC General | 2025-11-18
ROC | November | BLW3, Joe M on site working on Cl2 analyzers/Temp Alarms/Chemical system/Generator running. Directed to disregard alarms from site till he leaves MTW12, Placed well 2 man/off for Rick L/Redempto B for annual calibrations | All Water System ROC General | 2025-11-18
ROC | November | MARS, Cell 1 Lo level alarm, Activated RHRSTR D1 and deactivated D1 at VNRSKS to help recover MARS. 3 pumps currently running at ARPS but still losing, will continue to monitor | All Water System ROC General | 2025-11-18
ROC | November | Adam Button signing in -2 Clear | All Water System ROC General | 2025-11-18
ROC | November | Ethan U signing in Weather 2. | All Water System ROC General | 2025-11-14
ROC | November | Carter Dunn Signing Out, Ethan U is on site | All Water System ROC General | 2025-11-14
ROC | November | KCETFS - Evgeny S working on OIT, disregard Historian Heartbeat alarm. | All Water System ROC General | 2025-11-13
ROC | November | JFPS - Ernie H on site for semiannual generator testing. | All Water System ROC General | 2025-11-13
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-08
ROC | November | YDSS + YNSS normal | All Wastewater System ROC General | 2025-11-08
ROC | November | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-11-06
ROC | November | SUSSWB - Satnam M on site to complete some maintenance on parts on the controlling panel. | All Wastewater System ROC General | 2025-11-06
ROC | November | NBSP- Aeration Basin 2 back DO lo alarm came in. Did not recover placed blower 1 in man/on as per interim YDSS+YNSS normal | All Wastewater System ROC General | 2025-11-08
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-09
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-09
ROC | November | NBSP - Aeration basin 2 DO level has recovered. Deactivated duty 2 blower and placed back in auto mode. | All Wastewater System ROC General | 2025-11-09
ROC | November | AURSBS - Activated duty 1 to prepare system for Maple to Jefferson feed NRETBR - Activated duty 1 to make room in JFRS for the Maple to Jefferson feed. VNPS PD8 - Placed pumps in manual off mode in preparation for the maple to jefferson feed | All Wastewater System ROC General | 2025-11-09
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-09
ROC | November | Christian Van Beek signing in. Weather: -2C and snow. | All Wastewater System ROC General | 2025-11-09
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-09
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-09
ROC | November | YDSS + YNSS Normal Christian Van Beek signing out. | All Wastewater System ROC General | 2025-11-06
ROC | November | QVSSSC - Chris C finished and leaving site. | All Wastewater System ROC General | 2025-11-06
ROC | November | AUSSSR- Line 1 Valve Overtorque Alarm, Failed to Close. Notified Dan K. Two lines are available. Requested to email On call operator. | All Wastewater System ROC General | 2025-11-06
ROC | November | AUSS- P3 in auto with flow meter faults active. Shift report logs it as in man/off. Placed back in man/off | All Wastewater System ROC General | 2025-11-07
ROC | November | SEOC - OCF Fan room GO2 low alarm and OCF damper station flood alarm. Both alarms are disregards on the shift report. | All Wastewater System ROC General | 2025-11-09
ROC | November | Christian Van Beek signing in. | All Wastewater System ROC General | 2025-11-06
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-10
ROC | November | KBSP- Young J onsite working on WAS pumps 3 and 4 , air compressors and sludge pumps | All Wastewater System ROC General | 2025-11-06
ROC | November | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-11-06
ROC | November | YDSS + YNSS Normal Connor Smith signing out | All Wastewater System ROC General | 2025-11-05
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-09
ROC | November | Christian Van Beek signing out. | All Wastewater System ROC General | 2025-11-09
ROC | November | Angelica Chepiga signing out | All Wastewater System ROC General | 2025-11-06
ROC | November | Angelica Chepiga signing in,weather +5C | All Wastewater System ROC General | 2025-11-06
ROC | November | NMVCBP - Pump 1 and 2 uncommanded stop alarms. Checked site, both pumps faulted. Reset alarm and monitored the pumps. Duty bounced back and forth between the pumps in an abnormal fashion and then both pumps faulted again. Called Terry R who directed to place the pumps manual/off until he gets to site for an inspection. | All Wastewater System ROC General | 2025-11-05
ROC | November | Bayview OCF - Marcos T. is on site responding to an odour complaint and requested a CMU5. CMU5 Created W11427894 | All Wastewater System ROC General | 2025-11-07
ROC | November | AUSSSR- Daniel K called and requested CMU5 for clogged drain W11424505 CMU5 | All Wastewater System ROC General | 2025-11-06
ROC | November | YDSS + YNSS Normal Connor Smith signing out | All Wastewater System ROC General | 2025-11-06
ROC | November | MTSP, Aeration Tank 2 DO lo, Placed Blower 1 back to manual/on 15:35, Placed back to auto | All Wastewater System ROC General | 2025-11-09
ROC | November | QVSSSC- Chris C onsite with Darren B for wetwell cleaning. | All Wastewater System ROC General | 2025-11-06
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-07
ROC | November | AUEQSJ- Eric S onsite working on LIT4 | All Wastewater System ROC General | 2025-11-05
ROC | November | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-11-06
ROC | November | KSSSQW - Pump 1 low flow alarm, reassigned D1 to pump 2. Placed P1 man/off. | All Wastewater System ROC General | 2025-11-06
ROC | November | YDOC - Eric S on site to calibrate the flow meters in a meter chamber with a contractor. | All Wastewater System ROC General | 2025-11-06
ROC | November | MTSP, Aeration Tank 2 DO lo alarm, Notified Terry R that ive been using blower 1 multiple times now, directed to keep using Blower 1 as needed. 16:17, Placed blower 1 back to man/on 16:40, Placed blower 1 man/off consult | All Wastewater System ROC General | 2025-11-09
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-09
ROC | November | MTSP - Aeration tank 1 DO lolo alarm. Activated blower 1 in manual mode as per the interim procedure. | All Wastewater System ROC General | 2025-11-09
ROC | November | MTSP - Deactivated blower 1 . | All Wastewater System ROC General | 2025-11-09
ROC | November | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-11-07
ROC | November | Carter Dunn Signing Out | All Wastewater System ROC General | 2025-11-09
ROC | November | Adeela Khan signing in. Weather: 4C and cloudy | All Wastewater System ROC General | 2025-11-07
ROC | November | BLSS - Gavin W on site for a generator test. | All Wastewater System ROC General | 2025-11-06
ROC | November | KBSP- Young J onsite working on clarifier. Disregard related alarms. | All Wastewater System ROC General | 2025-11-06
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-07
ROC | November | SHSP - Ras to Aer tank 2 no flow. Informed Lance J & Marcus R who is onsite. Will follow up with alarm 16:35 - RAS pump 3 unable to produce flow. Leaving RAS pump 2 in duty 1. Lance J will follow up later if any follow up needed. Disregard RAS pump 2 speed deviation alarm 17:22 - Lance J heading to site CMU = W11427948 | All Wastewater System ROC General | 2025-11-07
ROC | November | KCSSKR - Satnam M. is on site replacing the battery for the dialer | All Wastewater System ROC General | 2025-11-07
ROC | November | YDSS+YNSS normal KSSP Odour O2 sensor hihi and OOR alarms came in. Checked trends looks like erratic reading. Will email North waste water OPS of outstanding alarm | All Wastewater System ROC General | 2025-11-08
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-08
ROC | November | NBSP - Aeration Basin 2 Back DO low alarm. As per Interim memo rotated blowers. Aeration Blower 1 to Duty 1. Will monitor. DO value still dropping. Man/start Aeration Blower 1 as per Interim memo. | All Wastewater System ROC General | 2025-11-06
ROC | November | MTSP - Eric S. is on site to work on the inlet channel level transmitter 13:00 - Eric S. is finished on site | All Wastewater System ROC General | 2025-11-07
ROC | November | NBSP - Aeration basin 2 Low DO alarm cleared. Deactivated the duty 2 blower and placed it back in auto | All Wastewater System ROC General | 2025-11-08
ROC | November | SHSP - Clarifier 1 driver overtorque, cut out. Informed Marcus T. Disregard for now as in process of switch over | All Wastewater System ROC General | 2025-11-07
ROC | November | NBSP - RAS train 1 flow low alarm. Checked site, RAS 1 flow is sitting just below low alarm setpoint. RAS flow possible impacted by leaves clogging RAS pipes. Will monitor site and if the flow continues to decline will call OCO. | All Wastewater System ROC General | 2025-11-08
ROC | November | NBSP - Aeration basin 2 back DO lolo alarm. Checked site, only one aeration blower is running. Activated duty 2 blower in auto as per the interim procedure. | All Wastewater System ROC General | 2025-11-08
ROC | November | YDSS + YNSS Normal MTSP, Placed blower 1 back to auto | All Wastewater System ROC General | 2025-11-09
ROC | November | KSSSQW- PAC Minor Fault. Notified Artour L. He will look into it. | All Wastewater System ROC General | 2025-11-06
ROC | November | MTSP - Aeration tank 1 do low alarm. Activated blower 1 in manual as per the interim procedure. | All Wastewater System ROC General | 2025-11-09
ROC | November | NBSP- Aer Blower 2 back to auto. | All Wastewater System ROC General | 2025-11-07
ROC | November | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-11-07
ROC | November | Adeela Khan signing out | All Wastewater System ROC General | 2025-11-07
ROC | November | KSSSQW- P2 lo flow alarm came in. Sudden drop in flow but recovered quickly as speed went to 100%. Lo flo alarm came in again. rotated duty and placed P2 in man/off | All Wastewater System ROC General | 2025-11-07
ROC | November | Carter Dunn Signing In, 5D/Clear | All Wastewater System ROC General | 2025-11-08
ROC | November | YDSS+YNSS normal Adam Button signing out | All Wastewater System ROC General | 2025-11-08
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-08
ROC | November | Adeela Khan signing in | All Wastewater System ROC General | 2025-11-10
ROC | November | Ethan U signing in Weather 7. | All Wastewater System ROC General | 2025-11-07
ROC | November | Angelica Chepiga signing out | All Wastewater System ROC General | 2025-11-07
ROC | November | SHSP - Marcus R onsite. Rotating clarifiers, cleaning clarifier. Clarifier 2 will be in service and 1 will be offline and cleaned | All Wastewater System ROC General | 2025-11-07
ROC | November | SUSSWB- Chris C onsite running generator. | All Wastewater System ROC General | 2025-11-10
ROC | November | PVSS - Gavin W on site to complete work orders including a generator test, hi level alarm, autodialer alarm test, dry well flood alarm test and hi/low temperature test | All Wastewater System ROC General | 2025-11-05
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-05
ROC | November | Connor Smith signing in 2C Cloudy | All Wastewater System ROC General | 2025-11-06
ROC | November | SUSP - Lagoon Flow LoLo alarm came in. Checked site and called Chase J. who will take a look | All Wastewater System ROC General | 2025-11-10
ROC | November | MTSP - Aeration tank 1 struggling with extra aeration blower on. Noted that duty 2 blower deactivates when the third blower is activated because aeration tank 2 remains high enough to deactivate the duty 2 blower. Rotated controlling DO probe to aeration tank 1 as per the shift report. | All Wastewater System ROC General | 2025-11-09
ROC | November | NBSP - Vortex 2 water scour uncommanded close alarm. Reset alarm as per shift report. | All Wastewater System ROC General | 2025-11-10
ROC | November | MTSP - Deactivated aeration blower 1 and placed in auto mode. | All Wastewater System ROC General | 2025-11-09
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-10
ROC | November | Adeela Khan signing out | All Wastewater System ROC General | 2025-11-10
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-09
ROC | November | Connor Smith signing in -4C Snowy | All Wastewater System ROC General | 2025-11-10
ROC | November | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-11-05
ROC | November | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-11-05
ROC | November | BLSS - Historian heartbeat alarm. Checked site, trending is normal. Contacted Arthur L who will clear the alarm. | All Wastewater System ROC General | 2025-11-06
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-11
ROC | November | Carter Dunn Signing In, 0D/Snow | All Wastewater System ROC General | 2025-11-09
ROC | November | Ethan Ullalkar signing out. | All Wastewater System ROC General | 2025-11-07
ROC | November | RHAMF1- Unit 2 pH sensor lo alarm came in. Trending downward all week. Notified Marcos T. Will check SCADA but req to contact NAC about site access. Notified Jimmy Hulman (416-826-0586) Jimmy H Notified ROC that site access is permitted for any operational changes required. Notified Marcos T. Okay to disregard for the night #consult YDSS+YNSS normal | All Wastewater System ROC General | 2025-11-07
ROC | November | NBSP-Reset aeration basin 2 back DO lo alarm and placed aeration blower 1 in auto as per interim | All Wastewater System ROC General | 2025-11-08
ROC | November | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-11-06
ROC | November | KSSP, Hypo Containment Spill Alarm, Trends look like the tank is dropping, Notified Chase J, He will look into it 23:34, Chase J directed to disregard however if it goes below 1m, he would like a call consult | All Wastewater System ROC General | 2025-11-10
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-11
ROC | November | NBSP - Aeration basin 2 low DO alarm. Checked site, one blower currently active but combined tank DO reading is not low enough to trigger duty 2 blower. Activated duty 2 blower in manual mode as per the interim procedure. Will monitor to ensure the DO level recovers with two blowers on. | All Wastewater System ROC General | 2025-11-08
ROC | November | Carter Dunn Signing Out | All Wastewater System ROC General | 2025-11-08
ROC | November | Christian Van Beek signing out. | All Wastewater System ROC General | 2025-11-10
ROC | November | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-11-06
ROC | November | NBSP - Aeration Blower 1 back to auto. | All Wastewater System ROC General | 2025-11-06
ROC | November | KSSP - Tyson C onsite testing flood alarms for chemical storage | All Wastewater System ROC General | 2025-11-07
ROC | November | NBSP- Aeration basin 2 back DO lo alarm came in recovered quickly as second blower started up in D1. Reset alarm as per interim | All Wastewater System ROC General | 2025-11-07
ROC | November | SUSSSR- Chris C onsite testing hi level alarms. Ric L onsite for annual calibrations. | All Wastewater System ROC General | 2025-11-10
ROC | November | HLSSBS - Neil O. called to inform that he is on site for work orders. Will be completing a generator run, will be testing flood alarms and the Odour Control Unit | All Wastewater System ROC General | 2025-11-10
ROC | November | NBSSJA- Lance J onsite running diesel generator. | All Wastewater System ROC General | 2025-11-05
ROC | November | NMSSBP- Phil R onsite testing wet well hi level alarm. | All Wastewater System ROC General | 2025-11-06
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-09
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-09
ROC | November | YDSS + YNSS Normal MTSP, Aeration Tank 2 DO lo, Placed Blower 1 man/on to help increase the DO as per the shift report 14:50, Placed blower 1 back to auto | All Wastewater System ROC General | 2025-11-09
ROC | November | RHAMF- Kyle C working on OIT. Disregard Historian Heartbeat Alarm. | All Wastewater System ROC General | 2025-11-10
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-09
ROC | November | AUSS - Eric S finished and leaving site. | All Wastewater System ROC General | 2025-11-05
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-08
ROC | November | KBSP- Artour L was able to restore trends on SCADA. Data collecting on Local SCADA but not remote. Trends did not backfill and Artour L will follow up with Danielle M on Monday to backfill trends | All Wastewater System ROC General | 2025-11-07
ROC | November | SUSP- FMC called about intrusion alarm. No OPS on site Corp security is attending site | All Wastewater System ROC General | 2025-11-08
ROC | November | KBSP- Aer Basin 2 Back DO Out of Rng Alm. Disregard as per Lance J. Basin 2 is offline. Basin 1 back online. Call for any Aeration Basin 1 alarms. CONSULT | All Wastewater System ROC General | 2025-11-10
ROC | November | KSSP- Irrigation water flow fault alarm, disregard alarm as per SCADA review. | All Wastewater System ROC General | 2025-11-07
ROC | November | SEOC67- Marcos T onsite running generator. | All Wastewater System ROC General | 2025-11-06
ROC | November | NBSSJA - Lance J. is on site and will be testing the Hi/Lo temp alarm, station flood, and auto dialer alarms. | All Wastewater System ROC General | 2025-11-07
ROC | November | KBSP, Mechanical Screen Lockout/General Alarm. Notified Lance J, he will head to site 14:50, Lance J on site, When investigating the mechanical screen, he noticed there is no power to it, Lance requests electrician on call. Contacted Kyle R, he will get in contact with Lance 15:00, Kyle Rae is heading to site 17:44, Kyle/Lance are finished on site CMU5: W11428147 (Lance J) CMU5: W11428158 (Kyle R) | All Wastewater System ROC General | 2025-11-08
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-10
ROC | November | NBSP- Aeration basin 2 DO lo alarm came in. Placed Blower 1 in man/on as per interim 19:08- NBSP- Aeration basin 2 DO lo alarm cleared. Placed Blower 1 back in auto as per interim | All Wastewater System ROC General | 2025-11-07
ROC | November | YDSS + YNSS Normal Connor Smith signing out | All Wastewater System ROC General | 2025-11-10
ROC | November | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-11-07
ROC | November | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-11-07
ROC | November | YDSS+YNSS normal | All Wastewater System ROC General | 2025-11-07
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-08
ROC | November | KSSP - Scum Chamber 1 High Level alarm came in. Disregarded as per shift report | All Wastewater System ROC General | 2025-11-10
ROC | November | SHSP - Marcus R. called to inform that he is on site and will be working on RAS and WAS pumps. Marcus requested to disregard RAS/WAS pump alarms until work is complete | All Wastewater System ROC General | 2025-11-10
ROC | November | KCSSKR - Young J. called to inform that him and Lance are finished cleaning wet well 1 and are moving on to wet well 2. Young also informed that he will be completing a generator test, hi/lo temp alarm test, eyewash test, and diesel containment float test | All Wastewater System ROC General | 2025-11-10
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-08
ROC | November | SUSP, Historian Heartbeat, Notified Artour L, he will investigate CMU5: W11428310 | All Wastewater System ROC General | 2025-11-09
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-09
ROC | November | Gluzen Ramos Ong signing out | All Wastewater System ROC General | 2025-11-10
ROC | November | Christian Van Beek signing in. Weather: 4C and clear. | All Wastewater System ROC General | 2025-11-08
ROC | November | Carter Dunn Signing In, -2D/Snow | All Wastewater System ROC General | 2025-11-10
ROC | November | NBSP, Aer Basin 2 Back DO Lo alarm, as per interim procedure, placed blower 1 man/on to increase the DO, will continue to monitor the site. 18:49, Placed blower 1 back to auto, DOs are at a good spot | All Wastewater System ROC General | 2025-11-10
ROC | November | NBSP- Man/start Aeration blower 1. | All Wastewater System ROC General | 2025-11-07
ROC | November | RHAMF - Inlet Damper 2 OOR alarm came in and Odour Control System in Emergency Mode alarm. Called Terry R. who is unaware of any work being done and requested to call Kyle C. 09:57 - Called Kyle C. who informed that he is working with contractors to fix the issue 10:37 - Kyle C. informed that he and contractors are finished and site is back to normal operations | All Wastewater System ROC General | 2025-11-07
ROC | November | SHSP- Marcus R testing RAS and WAS pumps. Disregard alarms. | All Wastewater System ROC General | 2025-11-10
ROC | November | SUSP, UV Ch. 1 Bank 1A Low UV Intensity Fault, trends show it did drop a little, notified Chase J, he is looking into it but currently directed to disregard consult | All Wastewater System ROC General | 2025-11-10
ROC | November | NMSSBP, Discharge Flow lolo alarm, Duty 1 was active with pump 1 running, Trends show an abnormality of the pump trying to pump, Placed pump man/off for the time being however did call Terry R to inform him that the site has less then 60% pump availability for the site. Directed to disregard at this current time as he isn't to worried since YR has the EQ tank. He will head to site in the morning 04:51, Terry R is heading to site CMU5: W11432521 | All Wastewater System ROC General | 2025-11-10
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-11
ROC | November | YDSS+YNSS normal | All Wastewater System ROC General | 2025-11-08
ROC | November | MTSP - Aeration tank 2 DO low alarm. Changed controlling DO probe back to the original aeration tank 2. Monitored site. | All Wastewater System ROC General | 2025-11-10
ROC | November | Adam Button signing in 3C Raining | All Wastewater System ROC General | 2025-11-07
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-10
ROC | November | NBSP - RAS train 1 flow low alarm. Checked site, RAS flow dipped below alarm setpoint before returning to the normal range. Called Lance J who directed to reset the alarm if this pattern continues. Lance would like to be contacted if the RAS flow continues to decline below alarm threshold or if thew train 1 RAS flow is significantly different than the train 1 RAS flow. Also spoke with Lance regarding the potential for Aeration tank 2 low DO alarms which were triggered last night. Lance stated that the interim direction should be enough to handle the swings in DO readings. SHSP - Screen room O2 conc hi. Mentioned this alarm to Lance J who directed to disregard. | All Wastewater System ROC General | 2025-11-09
ROC | November | MTSS- Barry M onsite running generator, testing drywell flood and dialer. | All Wastewater System ROC General | 2025-11-10
ROC | November | KSSSQW- Cam B onsite testing drywell flood alarm. | All Wastewater System ROC General | 2025-11-10
ROC | November | KSOCMA - Exhaust Fan Low Pressure alarm came in. Disregarded as per shift report | All Wastewater System ROC General | 2025-11-10
ROC | November | Gluzen Ramos Ong signing in | All Wastewater System ROC General | 2025-11-10
ROC | November | NMEQBP- Parth P finished onsite. | All Wastewater System ROC General | 2025-11-10
ROC | November | KCSSKR - Lance J. is on site and will be cleaning both wet well. Currently starting with Wet Well 1. Lance informed that wet well related alarms can be disregarded for the day | All Wastewater System ROC General | 2025-11-10
ROC | November | NMEQBP - Parth P. is on site for annual calibrations | All Wastewater System ROC General | 2025-11-10
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-10
ROC | November | AUSSSR - Terry R called and directed to clear alarms on site. All alarms cleared. Terry stated that Line 1 is back in operation and requested a CMU5. Created CMU5#W11425011 #CMU5 | All Wastewater System ROC General | 2025-11-06
ROC | November | NMVCBP - Marcus T onsite fore wet well cleaning | All Wastewater System ROC General | 2025-11-07
ROC | November | KBSP- Laurnen S onsite draining Aeration Tank 1 and pulling DO probes. Disregard related alarms. | All Wastewater System ROC General | 2025-11-10
ROC | November | AUSSSR - Line 3 overtorque. Informed Terry R & Marcos T. Disregard for the night but will follow up if another line goes down | All Wastewater System ROC General | 2025-11-07
ROC | November | KBSP - Mechanical Screen General and lockout alarms came in. Checked site and noticed that the bar screen was in local. Called Lauren S. who informed that a work order had been made for the mechanical bar screen alarms. | All Wastewater System ROC General | 2025-11-10
ROC | November | SHSP- Lance J done on site. Was able to revalve RAS system to have another pump available but to call if any lo flows come back in. AUSSYS- Wetwell Ultrasonic hi alarm came in. LIT reading erratically but Hydrostatic LIT 2 is controlling. Will continue to monitor | All Wastewater System ROC General | 2025-11-07
ROC | November | KBSP- Found plant effluent flow flatlined. Notified Artour L. Will take a look on SCADA. Created CMU5 W11427998 #CMU5 | All Wastewater System ROC General | 2025-11-07
ROC | November | NBSP- Aeration basin2 back DO lo alarm came in recovered quickly as second blower started up in D1. Reset alarm as per interim | All Wastewater System ROC General | 2025-11-07
ROC | November | KSSSQW - Pump 1 low flow alarm on duty start. Alarm cleared. Pump 1 speed trend is very erratic. Will monitor. | All Wastewater System ROC General | 2025-11-05
ROC | November | JDSS - Channel grinder e stop alarm and fault alarm. Called Chase J to ask if he knows if Kevin K or Darren B are still on site. Chase is unsure, will contact Kevin K. #consult | All Wastewater System ROC General | 2025-11-05
ROC | November | Christian Van Beek signing out. | All Wastewater System ROC General | 2025-11-05
ROC | November | JDSS- Kevin K finished wet well cleaning and is offsite. | All Wastewater System ROC General | 2025-11-05
ROC | November | RHAMF - OCS in emergency mode alarm. Kyle C stated that contractors are on site working on the system and this alarm can be disregarded. | All Wastewater System ROC General | 2025-11-05
ROC | November | Angelica Chepiga signing in, weather +6C | All Wastewater System ROC General | 2025-11-05
ROC | November | SHSP - Marcus R on site to work on the clarifiers and in the headworks of the plant. | All Wastewater System ROC General | 2025-11-05
ROC | November | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-11-06
ROC | November | Gluzen Ramos Ong signing in | All Wastewater System ROC General | 2025-11-04
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-04
ROC | November | YDSS + YNSS normal | All Wastewater System ROC General | 2025-11-05
ROC | November | SUSP - Supernatant Pump uncommanded stop and Hi temp alarm came in. Checked site. Called Kevin K. who directed to disregard alarm #CONSULT | All Wastewater System ROC General | 2025-11-01
ROC | November | MTSP, Aeration Tank 1 DO lo alarm, Placed blower 3 man/on to help the DO as per interim 21:27, Placed blower 3 back to auto but then placed back to man/on as DO hasn't recovered | All Wastewater System ROC General | 2025-11-02
ROC | November | KSSP, Screen 1 Downstream V uncommanded close alarm, Alarm is continuously coming in, Clearing itself and then reactivating, notified Kevin K, he will look into it 22:02, Kevin K heading to site 23:01, Kevin K finished on site CMU5: W11408115 | All Wastewater System ROC General | 2025-11-02
ROC | November | NBSP - Laureen S onsite running generator | All Wastewater System ROC General | 2025-11-03
ROC | November | KBSP - Aeration Basin 1 Back DO Fault alarm came in. Checked site. Called Gavin W. who informed the aeration tank is offline and all alarms can be disregarded. NBSP - Spoke to Gavin about an update about the back DO LoLo issue. Gavin informed that he has placed aeration tank 2 as the controlling basin and cleared all alarms. Gavin also informed that if the Lo/LoLo alarm comes in through the night, to place an extra blower in manual #CONSULT | All Wastewater System ROC General | 2025-11-01
ROC | November | MTSP, Placed Blower 1 man/on as per interim procedure to bring the DO back up | All Wastewater System ROC General | 2025-11-02
ROC | November | KSSP, ZW3 Permeate Turbidity OOR alarm/Shutdown alarm, Notified Kevin K, directed to disregard consult | All Wastewater System ROC General | 2025-11-03
ROC | November | SHSP- Power loss on site, Generator running Sludge blower 2 uncomand start/stop, Aeration blower 4 uncommanded start/stop, Aeration tank mixer stop, Clarifier rack cut out, RAS pump 3 uncommanded start/stop. Notified Gavin W. Directed to reset alarms. All cleared but Clarifier rack. Gavin will attend site. Site back on utility SHSSDK- P1 VFD fault after Power blip generator off and back on utility Gavin W will attend site P2 running okay created CMU5 W11407716 #CMU5 | All Wastewater System ROC General | 2025-11-01
ROC | November | MTSP - Aeration tank 2 DO Low alarm, notified Barry M. Switched controlling tank from Tk1 to Tk2. | All Wastewater System ROC General | 2025-11-03
ROC | November | KBSP- RAS combined no flow alarm came in. Notified Gavin W. Directed to disregard #Consult | All Wastewater System ROC General | 2025-11-03
ROC | November | YDOC6- YDOC-YDOC6 Comm fail and Loss alarms came in. Power loss on site and UPS ran out. Notified Terry R directed to disregard | All Wastewater System ROC General | 2025-11-03
ROC | November | LSSS- LSS4-LSSSGM comm failure LSSS2- to LSSS4 comm failure alarms came in. Notified Chris S. Will take a look on SCADA created CMU5 W11412631 00:09- LSSS- Chris S called back UPS is dead on site. Chris S not sure but thinks it may have gone to UPS during transfer to utility and when the transfer failed it never went back to generator power. Notified Terry R of update and will be on site soon with Satnam M. Terry R directed to not make any changes during this time until they are on site. #CMU5 | All Wastewater System ROC General | 2025-11-03
ROC | November | AUSSYS - Phil R running generator, testing drywell flood, health and safety inspection. | All Wastewater System ROC General | 2025-11-03
ROC | November | SHSP- Power loss on site, Generator running Sludge blower 2 uncomand start/stop, Aeration blower 4 uncommanded start/stop, Aeration tank mixer stop, Clarifier rack cut out, RAS pump 3 uncommanded start/stop. Notified Gavin W. Directed to reset alarms. All cleared but Clarifier rack. Gavin will attend site. Site back on utility SHSSDK- P1 VFD fault after Power blip generator off and back on utility Gavin W will attend site P2 running okay created created CMU5 W11412575 #CMU5 | All Wastewater System ROC General | 2025-11-03
ROC | November | YDSS+YNSS normal | All Wastewater System ROC General | 2025-11-03
ROC | November | Adam Button signing in 2 Raining | All Wastewater System ROC General | 2025-11-01
ROC | November | AUSSSR- Line 1 valve failed to close and over torque alarm came in. Able to clear failed to clsoe alarm but over torque alarm would not clear. Left outstanding and emailed Central-east Wastewater team | All Wastewater System ROC General | 2025-11-04
ROC | November | NBSP- Marcus R requested to disregard Alum Tank Hi alarm | All Wastewater System ROC General | 2025-11-04
ROC | November | NMMC- PAC Communication Failure Alarm. Notified Chris S. He will look into it. | All Wastewater System ROC General | 2025-11-04
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-01
ROC | November | Adeela Khan signing out | All Wastewater System ROC General | 2025-11-01
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-05
ROC | November | KSSP - ZW3 Shutdown and Permeate Turbidity OOR alarms came in. Called Kevin K. who directed to disregard alarms for the night #CONSULT | All Wastewater System ROC General | 2025-11-04
ROC | November | YDSS+YNSS normal | All Wastewater System ROC General | 2025-11-03
ROC | November | YDSS+YNSS normal | All Wastewater System ROC General | 2025-11-04
ROC | November | SHSP- RAS P2 speed deviation alarm came in. RAS flow normal compared to past trends. Left alarm outstanding and emailed West waste water OPs 04:14- SHSP- Alarm cleared on its own | All Wastewater System ROC General | 2025-11-04
ROC | November | Adeela Khan signing out | All Wastewater System ROC General | 2025-11-02
ROC | November | YDSS+YNSS normal | All Wastewater System ROC General | 2025-11-02
ROC | November | SHSP - Marcus R onsite, directed sludge to holding tank. Disregard hihi level | All Wastewater System ROC General | 2025-11-03
ROC | November | LSSS- Comms restored to site. | All Wastewater System ROC General | 2025-11-04
ROC | November | YDSS+YNSS normal | All Wastewater System ROC General | 2025-11-01
ROC | November | NBSP- Aeration Basin 2 back DO lolo alarm cleared placed blower 2 in manual as per interim 16:42 NBSP- Aeration Basin 2 back DO recovered alarm cleared placed blower 2 in auto as per interim | All Wastewater System ROC General | 2025-11-01
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-01
ROC | November | NMSSHS - Terry R running generator. | All Wastewater System ROC General | 2025-11-03
ROC | November | MTSP - Barry M running generator. | All Wastewater System ROC General | 2025-11-03
ROC | November | MTSP, Changed Controlling DO tank from Tank 2 to Tank 1 as per shift report, DO Continued to drop in Tank 1 while Tank 2 remained high | All Wastewater System ROC General | 2025-11-02
ROC | November | KSSSQW, Pump 3 Lo Flow alarm, flow kept becoming irregular, rotated pump duty and placed pump 3 man/off. Will send email to operators | All Wastewater System ROC General | 2025-11-02
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-03
ROC | November | LSSS- Terry R leaving site. Site running okay all alarms cleared | All Wastewater System ROC General | 2025-11-04
ROC | November | HMSS - Gavin W testing Drywell flood , building temp alarms, dialer alarms. | All Wastewater System ROC General | 2025-11-03
ROC | November | Connor Smith signing in 2 C Cloudy | All Wastewater System ROC General | 2025-11-04
ROC | November | MTSP- Clarifier 1 No RAS Pump Running, RAS Pump 3 VFD Fault Alarm. Notified Dan K. Electrician Brent S onsite working on them. Disregard all RAS Pump alarms while work being performed. | All Wastewater System ROC General | 2025-11-04
ROC | November | AUSS- Phil R onsite with contractors for equalization valve repair. Wet well 1 will be OOS. | All Wastewater System ROC General | 2025-11-04
ROC | November | MTSP - Aeriation tank 1 DO lo, man/start blower 1 as per shift report | All Wastewater System ROC General | 2025-11-03
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-01
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-01
ROC | November | RHAMF1- Found site with comm fails but no alarms. Notified Chris S will take a look on SCADA. Created CMU5 W11408022 #CMU5 | All Wastewater System ROC General | 2025-11-02
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-02
ROC | November | YDSS+ YNSS Normal | All Wastewater System ROC General | 2025-11-03
ROC | November | YDSS+YNSS normal | All Wastewater System ROC General | 2025-11-01
ROC | November | YDSS+YNSS normal | All Wastewater System ROC General | 2025-11-02
ROC | November | NMSSBP- Diesel tank level hihi alarm came in. disregard on shift report NBSP- Aeration basin 1 back DO lolo not recovering much higher than lo alarm and back DO on aeration tank 2 exceeding hi alarm. Notified Gavin W. Will take a look on SCADA #consult | All Wastewater System ROC General | 2025-11-02
ROC | November | Adeela Khan signing in. Weather: 5C and Cloudy | All Wastewater System ROC General | 2025-11-01
ROC | November | KSSSQW- P2 uncommanded stop alarm came in. Checked trends Looks like duty rotated asp ump was shutting down. reset alarm YDSS+YNSS normal | All Wastewater System ROC General | 2025-11-02
ROC | November | Angelica Chepiga signing out | All Wastewater System ROC General | 2025-11-03
ROC | November | KSSP - ZW3 Permeate Turbidity OOR and Shutdown alarms came in. Checked site. Called Kevin K. who directed to disregard alarms for the night #CONSULT | All Wastewater System ROC General | 2025-11-01
ROC | November | LSSS- Followed up with Terry R about site visit for ongoing power outage. Terry R will not be attending site unless more issues arise on site. Contacted Alectra and confirmed the power restoration between 21:00 and 23:00. #consult | All Wastewater System ROC General | 2025-11-03
ROC | November | KSOCMA - Exhaust Fan 1 failed to start alarm, notified Darren B. He will check. | All Wastewater System ROC General | 2025-11-03
ROC | November | Adam Button signing out | All Wastewater System ROC General | 2025-11-01
ROC | November | RHAMF1- Chris S called back and Req call to Central East Wastewater OCO. Tara M called the ROC informing that Chris R has called in and replacement will be found. Tara M informed ROC that Phil R is covering. 8:45- Called Phil R informed ROC having comms restored is critical. Called Chris C back with Update. Called Jimmy H. from NAC (416-826-0586) to attend site. Jimmy H notified ROC that site is accessible with York regions swipe pass and ekey. Verified with Jimmy H that OPs are allowed to attend site and make changes without NAC present. Confirmed with Phil R. Chris S will attend site. Post injection free CL2 lo alarm came in flow into tower dropped below dosing setpoint recovered after flow returned to normal and cleared alarm. | All Wastewater System ROC General | 2025-11-02
ROC | November | RHAMF1- Chris S rebooted radio/cell comms returned trends look okay. Chris S leaving site | All Wastewater System ROC General | 2025-11-02
ROC | November | SUSSWB- Alarm panel battery lo alarm came in on dialer followed by alarm power panel restored alarm. Emailed North Wastewater OPs about reoccurring alarm trends and site okay NBSP- Aeration Basin 1 back DO lo alarm came in and lower than lolo alarm. Started blower 3 in manual as per shift report | All Wastewater System ROC General | 2025-11-02
ROC | November | LSSS - Marcos T running generator. SUSSHS - Chase J running generator. | All Wastewater System ROC General | 2025-11-03
ROC | November | SUSP- Lagoon flow lolo alarm slight dip in flow reset alarm | All Wastewater System ROC General | 2025-11-02
ROC | November | SEOC OCF- Marcos T onsite running generator. | All Wastewater System ROC General | 2025-11-04
ROC | November | MTSP- Chris R Finished on site unclogging filter 1 req CMU5 for work done. Created CMU5 W11407901 | All Wastewater System ROC General | 2025-11-01
ROC | November | NBSP- Aeration tank 2 back DO lolo alarm came in again placed blower 1 in man/on. Notified Gavin W of third occurrence to see if other changes need to be made. Will take a look on SCADA #consult | All Wastewater System ROC General | 2025-11-01
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-03
ROC | November | Angelica Chepiga signing in, weather 7C | All Wastewater System ROC General | 2025-11-03
ROC | November | Carter Dunn Signing Out | All Wastewater System ROC General | 2025-11-03
ROC | November | LSSS - Power outage, pump 2 & 5 VFD fault. CP2 panel power failure. Informed Terry R, will head to site shortly CMU = 11412540 | All Wastewater System ROC General | 2025-11-03
ROC | November | AUSS- P1 discharge valve MV2 failed to open again. Placed P1 in man/off and emailed Central-east wastewater team. | All Wastewater System ROC General | 2025-11-01
ROC | November | YDSS+YNSS normal | All Wastewater System ROC General | 2025-11-01
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-02
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-02
ROC | November | KSSP - Darren B onsite running generator | All Wastewater System ROC General | 2025-11-03
ROC | November | KSOCMA - Exhaust Fan 1 uncommanded stop alarm. Darren B will attend site. | All Wastewater System ROC General | 2025-11-03
ROC | November | SHSP - Marcus R running generator. Disregard sludge tank Hi and HiHi alarms. | All Wastewater System ROC General | 2025-11-03
ROC | November | KBSP - Wash pumps discharge pressure LoLo, UV channel 2 low flow alarm, notified Gavin W. Requested disregard alarms for now. Diverted flow to tank 1 from tank 2. Outlet closed with RAS pumps running. Gavin W requested to receive call when received effluent flow. | All Wastewater System ROC General | 2025-11-03
ROC | November | Adeela Khan signing out | All Wastewater System ROC General | 2025-11-05
ROC | November | KBSP - Young J. running generator and working on blowers | All Wastewater System ROC General | 2025-11-04
ROC | November | YDSS + YNSS Normal Ethan Ullalkar signing out. | All Wastewater System ROC General | 2025-11-04
ROC | November | SUSP- Chase J onsite for generator run. | All Wastewater System ROC General | 2025-11-05
ROC | November | Connor Smith signing in 9C Cloudy | All Wastewater System ROC General | 2025-11-05
ROC | November | AUSS- Phil R onsite for generator run and Health and Safety work orders. Disregard related alarms. | All Wastewater System ROC General | 2025-11-05
ROC | November | KBSP- Young J testing sump pump hi levels. | All Wastewater System ROC General | 2025-11-05
ROC | November | JDSS - Kevin K and Darren B on site to complete wet well cleaning. Kevin stated that they will be running pumps as needed and there may be associated high/low level alarms. | All Wastewater System ROC General | 2025-11-05
ROC | November | Adam Button signing in 4C Clear | All Wastewater System ROC General | 2025-11-03
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-04
ROC | November | AUSSSR - Line 1 overtorque alarm came in after hours, Phil R responded to alarm CMU: 11415788 | All Wastewater System ROC General | 2025-11-04
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-04
ROC | November | Gluzen Ramos Ong signing out | All Wastewater System ROC General | 2025-11-04
ROC | November | Carter Dunn Signing In, 6D/Clear | All Wastewater System ROC General | 2025-11-02
ROC | November | NBSP, Gavin W is finished on site, if DO drops again while 2 pumps are active, directed to give a call however system is back to normal operation | All Wastewater System ROC General | 2025-11-02
ROC | November | MTSP, Aeration Tank 1 DO lo Alarm, normally would turn on 3 blower as per interim procedure however on MTSP SCADA, Blower 3 is saying OOS. contacted Philip R for direction as DO is lowering and blower 3 is OOS. Philip R said blower should be back in service and directed to place it man/on to resolve the low do alarm. 20:11, Placed blower 3 back to auto consult | All Wastewater System ROC General | 2025-11-02
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-01
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-01
ROC | November | KSSSQW - Boiler 1 fault. Followed up with Kevin K. Okay to disregard for the night | All Wastewater System ROC General | 2025-11-04
ROC | November | Adeela Khan signing in. Weather: 7C and partly cloudy | All Wastewater System ROC General | 2025-11-04
ROC | November | NBSP- Aeration Basin 2 back DO lo alarm came in. Placed Blower 1 in man/on to bring up DO as per interim. Will continue to monitor 14:57-NBSP- Aeration Basin 2 back DO alarm cleared placed blower 2 in auto as per interim | All Wastewater System ROC General | 2025-11-01
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-01
ROC | November | YDSS+YNSS normal | All Wastewater System ROC General | 2025-11-01
ROC | November | SECC - Informed Dan K of hydrogen peroxide pump 3 fault | All Wastewater System ROC General | 2025-11-03
ROC | November | SECC - Marcos T onsite testing eyewash | All Wastewater System ROC General | 2025-11-04
ROC | November | YDSS+YNSS normal | All Wastewater System ROC General | 2025-11-01
ROC | November | LSSS - Terry R requested on 4160V page reset pump 2 and pump 5 alarms. Alarms cleared. 4 pumps available, generators running. | All Wastewater System ROC General | 2025-11-03
ROC | November | LSSS- 52-L1/L2 power available alarm came in continued to monitor. Did not transfer over with utility power available. Notified Terry R. Placed all pumps in manual and toggled L2 transfer to utility. Transfer failed. Notified Terry R. Terry R and Satnam M will attend site. Created CMU5 W11412621 #CMU5 | All Wastewater System ROC General | 2025-11-03
ROC | November | YDSS + YNSS Normal Ethan Ullalkar signing out. | All Wastewater System ROC General | 2025-11-03
ROC | November | KSSSQW- P1 lo flow alarm came in pump shutdown on D1 stop reset alarm | All Wastewater System ROC General | 2025-11-04
ROC | November | KBSP- UV channel 2 lo flow and common minor alarms came in. Disregard on shift report cleared upon acknowledgment YDSS+YNSS normal | All Wastewater System ROC General | 2025-11-04
ROC | November | YDSS + YNSS Normal Connor Smith signing out | All Wastewater System ROC General | 2025-11-04
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-05
ROC | November | YDSS+YNSS normal | All Wastewater System ROC General | 2025-11-04
ROC | November | Ethan U signing in | All Wastewater System ROC General | 2025-11-04
ROC | November | YDSS+YNSS normal Adam Button signing out | All Wastewater System ROC General | 2025-11-02
ROC | November | Adam Button signing out | All Wastewater System ROC General | 2025-11-04
ROC | November | KBSP- Sludge bld low O2 detected. Disregard on shift report | All Wastewater System ROC General | 2025-11-01
ROC | November | Adam Button signing in clear -1C | All Wastewater System ROC General | 2025-11-02
ROC | November | KBSP - Informed Gavin W that effluent flow came back as requested | All Wastewater System ROC General | 2025-11-03
ROC | November | YDSS+YNSS normal | All Wastewater System ROC General | 2025-11-04
ROC | November | YDSS+YNSS Normal MTSP- Aeration tank 2 DO lo alarm came in. Blowers started up and value recovered. Reset alarm as DO recovered instantly as per interim 13:12- MTSP- Aeration tank 2 DO lo alarm came in. Blowers started up and value recovered. Reset alarm as DO recovered instantly as per interim | All Wastewater System ROC General | 2025-11-02
ROC | November | YDSS+YNSS normal | All Wastewater System ROC General | 2025-11-02
ROC | November | YDSS+YNSS normal NBSP- Gavin W heading to site as tank DO is not balancing created CMU5 W11408083 #CMU5 | All Wastewater System ROC General | 2025-11-02
ROC | November | Ethan U signing in | All Wastewater System ROC General | 2025-11-03
ROC | November | SUSP- Bar Screen Fault, Dewatering Press Not Available. Chase J working on it. | All Wastewater System ROC General | 2025-11-05
ROC | November | RHAMF1 - Station power failure, generator running, inlet damper fault. Makeup air unit fail to start. Followed up with contractor on-call Jimmy, is onsite and aware. Doing power switch over to test run generator and get readings. | All Wastewater System ROC General | 2025-11-03
ROC | November | KSSSQW - Pump 1 Low flow alarm came in. Checked site. Flow was back to optimal range. Alarm has been reset. Will monitor | All Wastewater System ROC General | 2025-11-01
ROC | November | EGSSSC - Chris C onsite with Wesex for wetwell cleaning | All Wastewater System ROC General | 2025-11-04
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-03
ROC | November | MTSP- Chris R on site for Labs due to high total P. Created CMU5 W11407732 #CMU5 | All Wastewater System ROC General | 2025-11-01
ROC | November | Christian Van Beek signing in. | All Wastewater System ROC General | 2025-11-05
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-05
ROC | November | NLVC - Chris S onsite 11:53 - Leaving site | All Wastewater System ROC General | 2025-11-04
ROC | November | NMSSBP - Terry R on site for a diesel generator test run. | All Wastewater System ROC General | 2025-11-05
ROC | November | AUSS- P1 Discharge valve MV2 failed to open alarm came in P2 started up in D1 reset alarm | All Wastewater System ROC General | 2025-11-01
ROC | November | YDSS + YNSS normal | All Wastewater System ROC General | 2025-11-02
ROC | November | KBSP - Young J called to inform that Bill VB is on site to work on the RAS/WAS pumps. Young J will be working on clarifier 1 and the aeration blowers. | All Wastewater System ROC General | 2025-11-05
ROC | November | SHSP - Aeration blower 1 uncommanded start and stop alarms. Checked site, blower 3 is duty 1 and is operating. Trending shows that aeration blower 1 was not running when the alarm came in. Able to clear alarms. | All Wastewater System ROC General | 2025-11-05
ROC | November | LSSS - Amelia from Sewer by law on site for sampling pump 6. | All Wastewater System ROC General | 2025-11-26
ROC | November | Adam Button signing in -1 Clear | All Wastewater System ROC General | 2025-11-20
ROC | November | YDSS + YNSS normal | All Wastewater System ROC General | 2025-11-30
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-20
ROC | November | Connor Smith signing in | All Wastewater System ROC General | 2025-11-19
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-29
ROC | November | LSSS - Wet well 1 and 2 bubbler low air pressure alarms. Disregard as per the shift report. | All Wastewater System ROC General | 2025-11-19
ROC | November | AUSS- OC control panel power failure. H2S/ Combustible gas fault and OOR alarms came in. Notified Phil R. Electricians have cut power to room causing alarms. Directed to disregard until done on site | All Wastewater System ROC General | 2025-11-19
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-24
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-29
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-27
ROC | November | NBSSJA - Redempto B. doing annual calibrations | All Wastewater System ROC General | 2025-11-27
ROC | November | LSSS- Fai from EME is on site for sampling and req P6 to run P6 in D1. D1 will activate soon | All Wastewater System ROC General | 2025-11-19
ROC | November | Connor Smith signing out | All Wastewater System ROC General | 2025-11-20
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-21
ROC | November | AUSSMP - Phil R. called to inform that he is on site with maintenance to work on the interconnect valve and will have wet well 1 OOS for most of the day Channel 1 Stop Gate closed and Bar Screen 1 Not in Auto alarms came in. Spoke to Phil R. who informed that those alarms were triggered due to the work being done | All Wastewater System ROC General | 2025-11-26
ROC | November | Adam Button signing in -2 Clear | All Wastewater System ROC General | 2025-11-19
ROC | November | Adeela Khan signing in. Weather: 4C and cloudy | All Wastewater System ROC General | 2025-11-21
ROC | November | MTSP- Aeration Tank 2 DO LoLo Alarm. Changed DO Selection to tank 2 as per SCADA Report. Aeration Blower 2 started up in duty 2. Aeration Blower 3 Failed to start Alarm came in and cleared. 13:40- Aeration Blower 3 failed to start. Blowers 1,2 are running in duty. Alarm cleared. | All Wastewater System ROC General | 2025-11-29
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-22
ROC | November | Angelica Chepiga signing in, weather -2C | All Wastewater System ROC General | 2025-11-28
ROC | November | MTSP - Aeration blower 3 fail to start alarm. Checked site, duty has rotated and blower 1 and 2 are currently running. Reset alarm. | All Wastewater System ROC General | 2025-11-26
ROC | November | MTSP, Aeration Tank 2 DO lo, notified Chris R, he will look into it | All Wastewater System ROC General | 2025-11-27
ROC | November | Carter D Signing In | All Wastewater System ROC General | 2025-11-24
ROC | November | SHSP- Marcus R on site to work on UV system. No alarms expected but will call when done 13:33- SHSP- Screen room O2 hi alarm came in. Notified Marcus R | All Wastewater System ROC General | 2025-11-28
ROC | November | MTSP - Thickening Tank Level Fault alarm came in. Disregarded as per shift report | All Wastewater System ROC General | 2025-11-30
ROC | November | YDSS + YNSS Normal Connor Smith signing out | All Wastewater System ROC General | 2025-11-30
ROC | November | Ethan Ullalkar signing out. | All Wastewater System ROC General | 2025-11-23
ROC | November | Connor Smith signing in 6C Rain | All Wastewater System ROC General | 2025-11-25
ROC | November | YDSS+YNSS normal Adam Button signing out | All Wastewater System ROC General | 2025-11-28
ROC | November | LSSS- Amelia from EME is on site for sampling req P6 to run, Rotated P6 to D1. | All Wastewater System ROC General | 2025-11-24
ROC | November | LSSS - South discharge valve fault, north discharge valve fault and tie valve fault. Called Terry R who is on site completing work orders for these valves. | All Wastewater System ROC General | 2025-11-25
ROC | November | MTSP- Ric L onsite for annual calibrations. 14:32- Finished onsite. | All Wastewater System ROC General | 2025-11-20
ROC | November | YDSS + YNSS Normal Connor Smith signing out | All Wastewater System ROC General | 2025-11-29
ROC | November | SHSP- Marcus R working on compressors | All Wastewater System ROC General | 2025-11-20
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-25
ROC | November | Ethan Ullalkar signing out. | All Wastewater System ROC General | 2025-11-25
ROC | November | AUSSYS, Rick L/Parth P heading to site | All Wastewater System ROC General | 2025-11-28
ROC | November | SHSP/SHSSDK - Hydro power fail occurred on both sites. Power came back right away. Likely a power blip. Called Marcus R. who is aware and cleared alarms. | All Wastewater System ROC General | 2025-11-26
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-26
ROC | November | SHSP - Alum pump 6 and pump 7 no flow alarms. Called Gavin W who directed to try and reset the alarms and monitor to ensure the duty is assigned following the alarm clear. If duty is not automatically re-assigned, Gavin directed to apply it manually. | All Wastewater System ROC General | 2025-11-25
ROC | November | YDSS + YNSS Normal Christian Van Beek singing out. | All Wastewater System ROC General | 2025-11-27
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-20
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-21
ROC | November | LSSS- Bar Screen 2 Fault Alarm. Notified Chris R. He will attend site. 15:30- Finished onsite. Back to normal operations. W11476908 CMU5 | All Wastewater System ROC General | 2025-11-30
ROC | November | Carter Dunn Signing Out | All Wastewater System ROC General | 2025-11-24
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-29
ROC | November | LSSS- Marcos T on site having issues with local SCADA access. Notified Kyle C who will follow up with Marcos T. PAC camm fails on site no visual on site. Marcos will check wet well level and generator status 09:50- LSSS- Trends recovered and all alarms cleared. Generators shut down and back on utility 09:50- KSSP- Mike B on site to test gas monitors | All Wastewater System ROC General | 2025-11-19
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-22
ROC | November | Connor Smith signing in 4C Clear | All Wastewater System ROC General | 2025-11-22
ROC | November | AUSSSR- Line 2 valve over torque alarm came in. Emailed Central East Wastewater OPs about outstanding alarm | All Wastewater System ROC General | 2025-11-28
ROC | November | NBSSJA- David D called. Will be doing generator testing with Total Power. 13:28- Finished onsite. | All Wastewater System ROC General | 2025-11-19
ROC | November | SHSP - Alum pump 6 & 7 no flow. Came in twice with pump 6 shutting off. Informed Marcus R of ongoing issue, will look into it | All Wastewater System ROC General | 2025-11-21
ROC | November | AUSSYS - Redempto B finished on site and leaving. | All Wastewater System ROC General | 2025-11-25
ROC | November | SHSP - Marcus R on site to complete maintenance on all blowers on site. Marcus has directed to disregard alarms associated with the blowers and he will be starting with the aeration blowers. | All Wastewater System ROC General | 2025-11-25
ROC | November | RHAMF1, Historian heartbeat, Artour L is working on the OIT | All Wastewater System ROC General | 2025-11-28
ROC | November | AUSS- Generator 1-3 not in auto alarm came in. Alarms cleared upon acknowledgement | All Wastewater System ROC General | 2025-11-20
ROC | November | QVSSSC - Inelt Channel High High Switch alarm came in. Called Neil O. who directed to disregard alarms as the grinder has faulted and maintenance needs to attend site | All Wastewater System ROC General | 2025-11-21
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-23
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-23
ROC | November | Adam Button signing in 1C Clear | All Wastewater System ROC General | 2025-11-24
ROC | November | Christian Van Beek signing in. | All Wastewater System ROC General | 2025-11-24
ROC | November | HMSS - Young J on site to assist maintenance with work on barscreen 2. Wet well 2 has been drained and isolated for the duration of the work. | All Wastewater System ROC General | 2025-11-25
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-21
ROC | November | Carter Dunn Signing In | All Wastewater System ROC General | 2025-11-25
ROC | November | MTSS- Sewage Pump 1 on Hydrostatic Mode Alarm. Pumps pumped wetwell down to LoLo level and interlocked. Cleared alarm. NBSP- Filter Reject Sump Level LoLo Alarm. Cleared alarm | All Wastewater System ROC General | 2025-11-25
ROC | November | NMSSBP - Mech screen 2 fault. Informed Phil R, will head to site after. CMU = 11462206 | All Wastewater System ROC General | 2025-11-23
ROC | November | Adeela Khan signing in. Weather: 4C and cloudy | All Wastewater System ROC General | 2025-11-23
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-30
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-22
ROC | November | Ethan U signing in Weather 4. | All Wastewater System ROC General | 2025-11-23
ROC | November | MTSP - Thickening tank level fault. Disregard as per shift report | All Wastewater System ROC General | 2025-11-23
ROC | November | KSTP- Christian from Ferguson offsite Connor Smith signing out | All Wastewater System ROC General | 2025-11-20
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-23
ROC | November | NMSSHS- Ric L and Red B onsite for annual calibrations. 14:08- Finished onsite | All Wastewater System ROC General | 2025-11-19
ROC | November | YDSDS + YNSS Normal | All Wastewater System ROC General | 2025-11-25
ROC | November | QVSSSC- Inlet Channel High Switch Alarm. Channel Grinder is OOS. Cleared alarm | All Wastewater System ROC General | 2025-11-26
ROC | November | YDSS + YNSS Normal Connor Smith signing out | All Wastewater System ROC General | 2025-11-26
ROC | November | Adeela Khan signing in. Weather: 0C and Flurries | All Wastewater System ROC General | 2025-11-27
ROC | November | RHAMF, SEOC, YDOC - Evgeny S. rebooting OITs, informed not expected to lose visibility of sites | All Wastewater System ROC General | 2025-11-27
ROC | November | Angelica Chepiga signing in | All Wastewater System ROC General | 2025-11-27
ROC | November | SHSP - Marcus R performing inspection and changing oil , requested disregard grit dewatering and bar screen alarms. | All Wastewater System ROC General | 2025-11-26
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-19
ROC | November | Carter Dunn Signing In | All Wastewater System ROC General | 2025-11-27
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-24
ROC | November | AUSSYS- Red B on site for annual calibrations | All Wastewater System ROC General | 2025-11-25
ROC | November | KSSP, Cam B is on site washing the membrane tanks, disregard alarms from the membranes till he calls back | All Wastewater System ROC General | 2025-11-25
ROC | November | Carter D Signing Out YDSS+ YNSS Normal | All Wastewater System ROC General | 2025-11-27
ROC | November | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-11-29
ROC | November | NMEQBP/NMVCBP - Power Failure alarms came in. Seemed like a brief power blip. Trending is okay and operations was not affected | All Wastewater System ROC General | 2025-11-30
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-30
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-29
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-22
ROC | November | YWS + NYWS Normal | All Wastewater System ROC General | 2025-11-22
ROC | November | HMSS - Redempto B and Rick L on site for annual calibrations. | All Wastewater System ROC General | 2025-11-24
ROC | November | SUSP - Air compressors 1/2 Pressure LoLo alarms. Tyson C requested disregard, electrician working on site/ air compressors off. | All Wastewater System ROC General | 2025-11-26
ROC | November | SUSP, Rick L on site working on the outlet flow going to the lagoon | All Wastewater System ROC General | 2025-11-27
ROC | November | LSSS- Amelia from EME is on site req P6 to run. P3 running and recently started. Waited 10 mins and rotated P6 in duty 1 | All Wastewater System ROC General | 2025-11-28
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-29
ROC | November | MTSP- Inlet Chamber Level HiHi Alarm. Trends appear normal. Cleared alarm. | All Wastewater System ROC General | 2025-11-19
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-29
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-30
ROC | November | YDSS+YNSS normal Adam Button signing out | All Wastewater System ROC General | 2025-11-19
ROC | November | YDSS+YNSS normal | All Wastewater System ROC General | 2025-11-19
ROC | November | SUSP, UV Intensity Fault, shift report doesn't have this as a disregard, Trends show a gap for roughly 5 minutes, notified Cam B, directed to disregard, he will look into it though just to confirm the site is fine consult | All Wastewater System ROC General | 2025-11-20
ROC | November | Adeela Khan signing in | All Wastewater System ROC General | 2025-11-26
ROC | November | SHSP - Alum Pump 6 and 7 no flow alarms came in. Called Marcus R. who will take a look | All Wastewater System ROC General | 2025-11-26
ROC | November | QVSSSC- Inlet Channel High Switch Alarm. Notified Neil O. They will look into it today. | All Wastewater System ROC General | 2025-11-20
ROC | November | RHAMF1- Kyle C on site working with contractors to test emergency mode | All Wastewater System ROC General | 2025-11-20
ROC | November | Gluzen Ramos Ong signing out | All Wastewater System ROC General | 2025-11-27
ROC | November | QVSSSC - Inlet Channel Level OOR alarm came in. Checked site. Channel grinder is still OOS. Level is reading above the hihi range. Shift report directs to disregard both Hi and HiHi level alarms. | All Wastewater System ROC General | 2025-11-28
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-28
ROC | November | LSSS - Amelia G. from EME is on site to take a sample and requested pump 6 be run instead of pump 5. Rotated pump duty so that pump 6 is in duty 1 as per Gluzen R | All Wastewater System ROC General | 2025-11-21
ROC | November | Carter Dunn Signing In, 1D/Clear | All Wastewater System ROC General | 2025-11-19
ROC | November | Ethan U signing in Weather 0. | All Wastewater System ROC General | 2025-11-22
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-22
ROC | November | QVSSQS - Inlet channel loss of echo. Known issue with inlet channel. Caused by hihi inlet which is a disregard as per shift report | All Wastewater System ROC General | 2025-11-22
ROC | November | EGSSSC - Diesel failure alarm on the dialer. No alarms on SCADA, all trends ok. | All Wastewater System ROC General | 2025-11-29
ROC | November | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-11-29
ROC | November | KSSP - MUA2 Diff Pressure Sw High alarm came in. Checked site. Disregarded, as per shift report 01:28 - SF-4 Low Air flow Switch alarm 01:31 - Alum Chemical Room MUA-11 Diff pressure Switch hi alarm came in. Shift report indicates not to disregard chemical room MUA alarms. Called Chris C. who directed to disregard all MUA alarms, as long as the fans continue to run. Chris informed that he will take a look at these alarms later today #CONSULT | All Wastewater System ROC General | 2025-11-27
ROC | November | NMVCBP - Neil O. is on site and will be testing the sump hi level alarm | All Wastewater System ROC General | 2025-11-21
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-22
ROC | November | YDSS+ YNSS Normal | All Wastewater System ROC General | 2025-11-19
ROC | November | SUSP, UV System Major Fault/Transmittance lolo/Critical Failure alarm, Trends show a gap that lasted for 3 minutes, While this happened, all UVs were on with an intensity at 100%, Shift report doesn't show a disregard, contacted Cam B, he will look into the issue 03:25, UV system is failing to switch over, Cam B is heading to site 03:36, Cam B switched the UVs over again, if it reverts back to 1A, he would like a call CMU5: W11456455 | All Wastewater System ROC General | 2025-11-20
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-22
ROC | November | MTSS - Barry M on site to test the high level alarms. | All Wastewater System ROC General | 2025-11-24
ROC | November | AUSSSR- Line 1 valve failed to close/overtorque alarm came in. Notified Dan K. Will have Kevin J attend site later Created CMU5 W11472877 JDSS- Christian from Ferguson Electric is on site for Load bank test #CMU5 | All Wastewater System ROC General | 2025-11-27
ROC | November | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-11-29
ROC | November | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-11-28
ROC | November | KSSP - Brent St Croix on site. | All Wastewater System ROC General | 2025-11-24
ROC | November | RHAMF1- Jim G (416-826-0586) from North American Construction on site req filters to run. Notified Marcos T who will attend site | All Wastewater System ROC General | 2025-11-24
ROC | November | YDSS + YNSS normal | All Wastewater System ROC General | 2025-11-21
ROC | November | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-11-29
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-30
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-25
ROC | November | ABMC- Kevin W rebooting modem on site. Alarms cleared | All Wastewater System ROC General | 2025-11-25
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-22
ROC | November | MTSP - Aeriation tank 1 DO lo. Rotate tank 1 to controlling tank as per shift report | All Wastewater System ROC General | 2025-11-22
ROC | November | Ethan Ullalkar signing out. | All Wastewater System ROC General | 2025-11-22
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-23
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-27
ROC | November | KSSP, Alum Chem Rm MUA-11 Dif Press Sw Hi Alarm, Notified Chris C, directed to disregard at this time consult | All Wastewater System ROC General | 2025-11-28
ROC | November | NBSP- Scum Pump 2 uncommanded stop alarm came in. Notified Lance J. Will check pumps | All Wastewater System ROC General | 2025-11-27
ROC | November | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-11-28
ROC | November | AUSSR - Heat Tracing Controller 2 Fault alarm. Emailed Chris R about outstanding alarm. As per SCADA review alarm will be looked at by CD/Contractors. | All Wastewater System ROC General | 2025-11-28
ROC | November | Christian Van Beek signing in. Weather: -2C and clear. | All Wastewater System ROC General | 2025-11-26
ROC | November | KSSSQW, Boiler 1 Fault, notified Chris , he is heading to site CMU5: W11473371 | All Wastewater System ROC General | 2025-11-27
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-28
ROC | November | LSSS- Historian heartbeat alarm came in after power b lip. Trends flatlined. Notified Yash S. Created CMU5 W11455588 #CMU5 | All Wastewater System ROC General | 2025-11-19
ROC | November | Connor Smith signing in 0C Snowy | All Wastewater System ROC General | 2025-11-30
ROC | November | SEOC- OCF fan outlet O2 OOR alarm. Disregard on shift report | All Wastewater System ROC General | 2025-11-24
ROC | November | Connor Smith signing out | All Wastewater System ROC General | 2025-11-22
ROC | November | Christian an Beek signing in. Weather: 6C and clear. | All Wastewater System ROC General | 2025-11-25
ROC | November | LSSS- Kyle C leaving site. | All Wastewater System ROC General | 2025-11-19
ROC | November | KSSP- Alum storage eye wash activation alarm came in. Notified Mike B No one on site. Directed to try and clear alarm. | All Wastewater System ROC General | 2025-11-24
ROC | November | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-11-26
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-27
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-28
ROC | November | Adam Button signing in -2 Clear | All Wastewater System ROC General | 2025-11-27
ROC | November | SUSP- Lagoon P1 uncommanded stop and P2 failed to start alarms came in. Notified Tyson C will investigate | All Wastewater System ROC General | 2025-11-20
ROC | November | SUSP, Rick L is finished on site | All Wastewater System ROC General | 2025-11-27
ROC | November | QVSSSC- Inlet channel hihi/hihi switch alarm. disregard on shift report | All Wastewater System ROC General | 2025-11-27
ROC | November | Adam Button signing in -3C Clear | All Wastewater System ROC General | 2025-11-28
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-30
ROC | November | LSSS- Pac comm failure on site. Generator running and power transferred to generator.Notified Marcos T. Req PCD to take a look as it has reoccurred multiple times today and maybe due to a programming issue. Notified Kyle C. Kyle C is on his way to site already and will help Marcos T troubleshoot issue | All Wastewater System ROC General | 2025-11-19
ROC | November | SEOC, Evgeni S rebooting OIT. disregard historian | All Wastewater System ROC General | 2025-11-27
ROC | November | SUSP - Artour L. is on site to troubleshoot the UV PAC. May see communication issues but Artour directed to disregard alarms until work is complete 14:07 - Artour called back to inform that he is finished on site | All Wastewater System ROC General | 2025-11-26
ROC | November | YDSS+YNSS NORMAL Angelica Chepiga signing out | All Wastewater System ROC General | 2025-11-26
ROC | November | NMEQBP- Kingsley M rebooting server | All Wastewater System ROC General | 2025-11-27
ROC | November | Adeela Khan signing out | All Wastewater System ROC General | 2025-11-28
ROC | November | Carter Dunn Signing In | All Wastewater System ROC General | 2025-11-28
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-21
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-23
ROC | November | Connor Smith signing out | All Wastewater System ROC General | 2025-11-19
ROC | November | YDSS + YNSS normal | All Wastewater System ROC General | 2025-11-24
ROC | November | Connor Smith signing in -4 Clear | All Wastewater System ROC General | 2025-11-29
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-26
ROC | November | RHAMF1 - Kyle C working on site. Requested disregard alarms for the duration of the test. 15:36 Kyle C finished on site. | All Wastewater System ROC General | 2025-11-26
ROC | November | SHSP - Alum pump 6 and Pump 7 no flow alarms. Received a call from Marcus who will attend site to inspect the pumps. Marcus requested a CMU5. Created CMU5#W11465456 #CMU5 | All Wastewater System ROC General | 2025-11-24
ROC | November | MTSP - Milat from Corporate Security called to inform that there is a security intrusion alarm. Will dispatch mobile security | All Wastewater System ROC General | 2025-11-30
ROC | November | Adeela Khan signing out | All Wastewater System ROC General | 2025-11-30
ROC | November | KSSP - Alum Tank 1 Level OOR, LoLo and ROC Alarm came in. Checked site. Called Chris C. who directed to disregard for the night as this is most likely a sensor issue and will be addressed in the morning. #CONSULT | All Wastewater System ROC General | 2025-11-30
ROC | November | SHSSDK - Wet Well 1 Ultrasonic Level LoLo alarm came in. Checked site. Trends indiacate a LoLo level occurred but quickly recovered. Hydrostatic levels were optimal. Ultrasonic level came back to normal range within 5 mins and alarms have cleared. Will continue to monitor | All Wastewater System ROC General | 2025-11-30
ROC | November | LSSS- Talha H on site to look at server no service impact expected | All Wastewater System ROC General | 2025-11-20
ROC | November | MTSP- Parth P onsite for annual calibrations. | All Wastewater System ROC General | 2025-11-19
ROC | November | YDSS+YNSS normal Adam Button signing out | All Wastewater System ROC General | 2025-11-27
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-21
ROC | November | Ethan U signing in Weather 4. | All Wastewater System ROC General | 2025-11-21
ROC | November | KBSP, Lauren S on site, testing Estop alarms, directed to disregard Estop alarms till she calls back | All Wastewater System ROC General | 2025-11-28
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-20
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-30
ROC | November | YDSS+ YNSS Normal | All Wastewater System ROC General | 2025-11-20
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-21
ROC | November | YDSS + YNSS Normal Carter D Signing Out | All Wastewater System ROC General | 2025-11-28
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-23
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-23
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-23
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-28
ROC | November | KSSSQW - Boiler 1 Fault alarm came in. Checked site. Normal operations. Boiler 1 is showing local/off but both Hydroionic Pumps are running in local. As this is a low priority alarm, will send an email to the North Wastewater Team | All Wastewater System ROC General | 2025-11-27
ROC | November | QVSSSC- Inlet channel high switch alarm came in. Notified Neil O. Will attend site and see if channel grinder will run today | All Wastewater System ROC General | 2025-11-19
ROC | November | KSSSQW- Cam B on site to unplug P1/3/4 P2 running okay | All Wastewater System ROC General | 2025-11-19
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-26
ROC | November | AUSSSR- Line 3 Over torque and failed to close alarm came in. Notified Marcos T. Will attend site. Created CMU5 W11465484 #CMU5 | All Wastewater System ROC General | 2025-11-24
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-25
ROC | November | Adam Button signing in | All Wastewater System ROC General | 2025-11-25
ROC | November | LSSS- Power failure on site P2 VFD fault came in. Notified Phil R. Heading to site. Created CMU5 W11456137 #CMU5 | All Wastewater System ROC General | 2025-11-19
ROC | November | AUSSYS - Wetwell 1 Ultrasonic Level HiHi alarm came in. Checked site. Noticed a spike that quickly came down. Spike happened again. Alarm was able to clear. Will send an email to the central east team | All Wastewater System ROC General | 2025-11-24
ROC | November | KSSP - fuel storage smoke alarm and gen electrical room smoke alarm. Contacted operators on site, no answer. Operators are likely below ground working on plant systems. 12:37 - KSSP - Mike B called back and informed that these alarms can be disregarded until the end of the day. | All Wastewater System ROC General | 2025-11-24
ROC | November | HMSS- Intrusion alarm came in on dialer. Called Young J. Verified contractors on site and to disregard alarm | All Wastewater System ROC General | 2025-11-20
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-25
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-24
ROC | November | Adeela Khan signing out | All Wastewater System ROC General | 2025-11-26
ROC | November | NBSP - Vortex #2 Air Scour Uncommanded Close alarm came in. Ack/reset as per shift report | All Wastewater System ROC General | 2025-11-21
ROC | November | Adeela Khan signing out | All Wastewater System ROC General | 2025-11-21
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-22
ROC | November | SUSP, Tyson C on site working on the filter feed pumps and the UVs, directed to disregard alarms on site till he is finished | All Wastewater System ROC General | 2025-11-25
ROC | November | Angelica Chepiga signing out | All Wastewater System ROC General | 2025-11-27
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-23
ROC | November | SECC - Shaft 13A sluice gate OOR and fault alarm. Daniel K locked out the sluice gate while the contractors sample. | All Wastewater System ROC General | 2025-11-25
ROC | November | YDSS + YNSS Normal Christian Van Beek signing out. | All Wastewater System ROC General | 2025-11-19
ROC | November | Adam Button signing out | All Wastewater System ROC General | 2025-11-25
ROC | November | EGSSSC - Bill V. called to inform that he will be testing the generator | All Wastewater System ROC General | 2025-11-26
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-30
ROC | November | Adeela Khan signing in. Weather: 0C and flurries | All Wastewater System ROC General | 2025-11-30
ROC | November | Connor Smith signing in | All Wastewater System ROC General | 2025-11-20
ROC | November | NBSSJA - Diesel tank level HiHi alarm. Level suddenly increased. Will monitor and notify area if alarm doesn't clear. | All Wastewater System ROC General | 2025-11-26
ROC | November | GRSSWA - Generator running status alarm. Checked site, generator is active but ATS is pointing to town hydro indicating a short power blip. Operations appear normal will monitor site to ensure generator shuts down. | All Wastewater System ROC General | 2025-11-27
ROC | November | AUSSSR, Line 2 Valve Overtorque Alarm, Philip R heading to site CMU5: W11475522 | All Wastewater System ROC General | 2025-11-28
ROC | November | JDSS. Arthour L is on site, working with contractors on the removal of the temp generator. | All Wastewater System ROC General | 2025-11-28
ROC | November | Adeela Khan signing in. Weather: -1C and Cloudy | All Wastewater System ROC General | 2025-11-29
ROC | November | Carter Dunn Signing Out | All Wastewater System ROC General | 2025-11-21
ROC | November | KBSP- UV Ch 1 bank 1b major alarm/ UV 1 warning/ Critical/ warning alarms came in. Notified Lauren S. Young J and Lauren S working on UV bank 1 no alarms expected for bank 2 SHSP-Alum P6/7 no flow alarms came in ack reset as per shift report | All Wastewater System ROC General | 2025-11-27
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-30
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-30
ROC | November | HLSSBS - Chase J performing pump testing. Disregard alarms for the duration of the work. | All Wastewater System ROC General | 2025-11-26
ROC | November | SUSP - UV System Minor Fault alarm came in. Checked site. Called Chris C. who is aware and will clear alarm | All Wastewater System ROC General | 2025-11-26
ROC | November | YWS+NYWS normal Adam Button signing out | All Wastewater System ROC General | 2025-11-20
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-23
ROC | November | SHSP- Marcus R called. Can disregard sludge loading bad volume alarm when it comes in. | All Wastewater System ROC General | 2025-11-20
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-20
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-23
ROC | November | YDSS + YNSS normal | All Wastewater System ROC General | 2025-11-24
ROC | November | NBSP- Gavin W on site to change oil on compressors | All Wastewater System ROC General | 2025-11-24
ROC | November | NBSP- Gavin W working on filter air compressors on site | All Wastewater System ROC General | 2025-11-19
ROC | November | Adam Button signing out | All Wastewater System ROC General | 2025-11-24
ROC | November | LSSS- Comm Failure. All pumps not available. Called Marcos T. No answer. Called Daniel K. He will inform Marcos T who will be heading to site. W11455578 CMU5 | All Wastewater System ROC General | 2025-11-19
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-22
ROC | November | AUSS- Surge Tank 2 Level HiHi, OOR. Notified Phil R. He is working on it as well as surge tank 2. | All Wastewater System ROC General | 2025-11-20
ROC | November | SUSP - Filter Feed Pumps not available alarms, Tyson C called, Artour L working on UV and Filter feed pumps. Disregard alarms for the duration of the work. | All Wastewater System ROC General | 2025-11-26
ROC | November | YDSS+YNSS normal | All Wastewater System ROC General | 2025-11-20
ROC | November | HMSS, Gavin W is leaving site, Bar screen 2 will be oos for the night | All Wastewater System ROC General | 2025-11-24
ROC | November | KBSP- Sldg Thick'r Tnk 2 Lvl HiHi Alm. Disregard as per SCADA Report. | All Wastewater System ROC General | 2025-11-30
ROC | November | GRSSWA- Cam B on site to run generator | All Wastewater System ROC General | 2025-11-24
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-25
ROC | November | Christian Van Beek signing out. | All Wastewater System ROC General | 2025-11-25
ROC | November | Carter D signing out | All Wastewater System ROC General | 2025-11-20
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-22
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-25
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-22
ROC | November | JDSS, Kyle C resetting OIT, disregard historian heartbeat | All Wastewater System ROC General | 2025-11-28
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-26
ROC | November | SHSP- Alum pump 6/7 no flow alarm came in reset as per shift report | All Wastewater System ROC General | 2025-11-28
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-25
ROC | November | HMSS - Bill VB on site to complete work on barsceen 2. | All Wastewater System ROC General | 2025-11-25
ROC | November | SHSP- Marcus R onsite working on RAS and WAS Pumps as well as the shaftless conveyor. | All Wastewater System ROC General | 2025-11-19
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-26
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-27
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-21
ROC | November | KBSP- Sump P2 ovl /lockout/ general alarms came in. Disregard on shift report | All Wastewater System ROC General | 2025-11-19
ROC | November | SUSP - UV system minor fault. Nothing reported on shift report. Status reverted to normal on alarm. Checking trends there's a 1 minute gap, trends appear normal now. Informed Cam B regarding issue in relation to UV power disruptions. Okay to disregard, known issue with site and Trojan/PCs aware and working towards issue. Consult | All Wastewater System ROC General | 2025-11-24
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-24
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-23
ROC | November | NBSP - Filter Reject Sump Level LoLo alarm came in. Checked site. Noticed that the level went back to optimal range. Trends indicate that a dip occurred. | All Wastewater System ROC General | 2025-11-24
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-24
ROC | November | Adeela Khan signing out | All Wastewater System ROC General | 2025-11-24
ROC | November | HMSS, Redempto B is finished on site | All Wastewater System ROC General | 2025-11-24
ROC | November | Angelica Chepiga signing in, weather +8C | All Wastewater System ROC General | 2025-11-26
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-27
ROC | November | RHAMF - Marcos T called to inform he is leaving site. Marcos also confirmed that recirculation pump 2 on scrubber 2 has been locked out and tagged out and will be removed for repairs later today. | All Wastewater System ROC General | 2025-11-24
ROC | November | Ethan Ullalkar signing out. | All Wastewater System ROC General | 2025-11-21
ROC | November | KBSP - Lauren S on site to test the filter bypass alarm. | All Wastewater System ROC General | 2025-11-25
ROC | November | NMSSBP, Marcos T on site, testing dry well sump alarms and testing dialer alarms | All Wastewater System ROC General | 2025-11-28
ROC | November | YDOC- Fan 1 Fault/ Uncommanded stop alarm came in. Fan 1 outlet gate failed to close alarm came in. Reset alarm. | All Wastewater System ROC General | 2025-11-27
ROC | November | JDSS, Brent St Q on site doing a power transfer, he will be running the generator and then having a pump run when the generator is running. Placed pumps 2/3 man/off | All Wastewater System ROC General | 2025-11-28
ROC | November | Christian Van Beek signing out. | All Wastewater System ROC General | 2025-11-24
ROC | November | Gluzen Ramos Ong signing in | All Wastewater System ROC General | 2025-11-27
ROC | November | HMSS - Young J. is on site and will be testing the hi/low alarm, dry well flood and metro overflow alarms | All Wastewater System ROC General | 2025-11-26
ROC | November | RHAMF1- Marcos T on site with contractors and is shutting plant down for testing | All Wastewater System ROC General | 2025-11-24
ROC | November | STW3, Travis W on site, cleaning the turbidity analyzer | All Wastewater System ROC General | 2025-11-28
ROC | November | Carter Dunn Signing Out | All Wastewater System ROC General | 2025-11-25
ROC | November | NBSP- Scum pump 1 general alarm pump OOS. Gavin W directed to disregard HMSS- Bar screen 2 fault alarm came in. Notified Gavin W will attend site. Created CMU5 W11465773 #CMU5 | All Wastewater System ROC General | 2025-11-24
ROC | November | Connor Smith signing in 6C Clear | All Wastewater System ROC General | 2025-11-21
ROC | November | SEOC- Historian Heartbeat Alarm. Notified Kyle C. He will look into it. 2:09- Kyle C finished and cleared alarm. W11462015 CMU5 | All Wastewater System ROC General | 2025-11-22
ROC | November | Carter Dunn Signing In, 4D/Clear | All Wastewater System ROC General | 2025-11-20
ROC | November | Angelica Chepiga signing out | All Wastewater System ROC General | 2025-11-29
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-30
ROC | November | BLSS - Young J testing Drywell level, sump pit level, wet well flood alarms and auto dialer alarms. | All Wastewater System ROC General | 2025-11-26
ROC | November | SEOC- Evgeny S done rebooting OIT historian heartbeat alarm cleared | All Wastewater System ROC General | 2025-11-27
ROC | November | YDSS + YNSS Normal Connor Smith signing out | All Wastewater System ROC General | 2025-11-23
ROC | November | Ethan Ullalkar signing out. | All Wastewater System ROC General | 2025-11-13
ROC | November | SEOC4 - Shaft 4 O2 monitor. Disregard as per shift report | All Wastewater System ROC General | 2025-11-17
ROC | November | Adeela Khan signing in. Weather: -1 and Snowing | All Wastewater System ROC General | 2025-11-17
ROC | November | SHSP- Marcus R on site to test blower building/ process building sump level alarms | All Wastewater System ROC General | 2025-11-11
ROC | November | YDOC- F2 make up flow OOR alarm came in. Disregard on shift report | All Wastewater System ROC General | 2025-11-13
ROC | November | SHSP - Marcus R working on RAS pump 1 and 2 scum pumps. | All Wastewater System ROC General | 2025-11-12
ROC | November | KSSSQW- Pump 2 Flow Lo Alarm. Has come in several times. Rotated duties so pump 4 running in duty 1. | All Wastewater System ROC General | 2025-11-13
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-14
ROC | November | SUSP - Filter feed pump 2 VFD fault alarm and Div EQ tank 3 way valve overtorque and fault alarms. These alarms are outstanding from the power failure on site. Darren B will attend site to reset the VFD fault alarm and requested a CMU5. Created CMU5#W11446292 KSSP - Sludge transfer pump 2 uncommanded stop alarm and screen press 1 fault alarm. Alarms are upstanding from the power failure earlier. Darren B stated they can be disregarded for the rest of the day and over night until Monday at 09:00. #CMU5 | All Wastewater System ROC General | 2025-11-16
ROC | November | KCSSKR - Generator running status alarm. Checked site, generator running but ATS is pointing to town hydro. While on site the generator shut down. Cleared alarms. operations normal. | All Wastewater System ROC General | 2025-11-16
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-11
ROC | November | NBSSJA - Gavin W onsite for wet well cleaning, testing hi level, & turning off low level lockout | All Wastewater System ROC General | 2025-11-12
ROC | November | SHSP - Young J working on Blowers. | All Wastewater System ROC General | 2025-11-13
ROC | November | KSSSQW, Pump 4 lo flow alarm, Pump would ramp up and down consistently, Placed pump man/off and will send email to operator in morning about operational change | All Wastewater System ROC General | 2025-11-12
ROC | November | YDSS+ YNSS Normal | All Wastewater System ROC General | 2025-11-12
ROC | November | Carter Dunn Signing Out | All Wastewater System ROC General | 2025-11-12
ROC | November | Angelica Chepiga signing in | All Wastewater System ROC General | 2025-11-11
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-16
ROC | November | KSSP - SF-4 Low air flow switch alarm and MUA2 diff pressure switch high alarms. Shift report directs to disregard MUA alarms for anything except the chemical buildings. Able to reset the SF-4 air flow alarm. | All Wastewater System ROC General | 2025-11-16
ROC | November | NMSSHS, Meter Chamber 2 Flood Alarm, notified Terry R, directed to disregard for the night and to send an email to the team lead in the morning consult | All Wastewater System ROC General | 2025-11-11
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-12
ROC | November | KSSSQW- P3 lo flow alarm came in. Programing runs pump at 100% allowed pump to run for 10 mins at 100% to try and clear blockage. Will continue to monitor and clear alarm allowing pump to return to normal speed. Pump ran a 100% for 8 mins until D1 stopped. Cleared alarm. Will monitor next cycle | All Wastewater System ROC General | 2025-11-13
ROC | November | KSSSQW- P3 flow lo alarm came in again. Placed P3 in auto and rotated duty leaving only 2 pumps available. Will continue to monitor and contact OCO if any more issues arise on site. Will email North waste water OPs about outstanding issues | All Wastewater System ROC General | 2025-11-13
ROC | November | Connor Smith signing in 4C Cloudy | All Wastewater System ROC General | 2025-11-13
ROC | November | YDSS+YNSS normal KSSSQW- P1 lo flow alarm came in. Reset alarm and alarm came back in after returning to lower speed. Placed P1 in man off and rotated Duty | All Wastewater System ROC General | 2025-11-12
ROC | November | SHSP- Found clarifier 2 running when listed as OOS of SCADA Review. Notified Young J to clarify if this is intentional. Will check SCADA 21:00- SHSP- According to site eLog Clarify 2 was put into operation earlier in week. No issues found | All Wastewater System ROC General | 2025-11-12
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-12
ROC | November | Carter Dunn Signing In, 0D/Clear | All Wastewater System ROC General | 2025-11-14
ROC | November | EGSSSC- Diesel failure alarm came in on dialer came in. Disregard on shift report | All Wastewater System ROC General | 2025-11-13
ROC | November | SUSP - UV Channel 2 Bank 2A Lamp fail alarm, disregard as per SCADA review. | All Wastewater System ROC General | 2025-11-11
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-13
ROC | November | Adam Button signing in -3 Snowing | All Wastewater System ROC General | 2025-11-11
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-15
ROC | November | MTSP - Change aeriation tank 2 as controlling as tank 2 DO low | All Wastewater System ROC General | 2025-11-17
ROC | November | YDSS+YNSS normal | All Wastewater System ROC General | 2025-11-12
ROC | November | Angelica Chepiga signing out | All Wastewater System ROC General | 2025-11-12
ROC | November | LSSS - Amelia from By-law sampling pump 6, assigned pump 6 to duty 1. | All Wastewater System ROC General | 2025-11-12
ROC | November | KSSP - Screen press 1 fault alarm and sludge transfer pump 2 uncommanded stop alarms. Likely related to the power failure in the area. Darren B has been informed of the power failures and is on site at KSSP. Trending shows no indication of the UV system failing during the widespread power failure and the generator did not activate at KSSP. YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-16
ROC | November | KBSP - Lauren S called, contractors working on air compressors, disregard alarms for now. | All Wastewater System ROC General | 2025-11-14
ROC | November | Carter Dunn Signing In | All Wastewater System ROC General | 2025-11-17
ROC | November | SHSSDK - Redempto B. and Ricardo L. are on site for annual calibrations 11:07 - Red and Rick are finished on site | All Wastewater System ROC General | 2025-11-17
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-16
ROC | November | Ethan U signing in Weather 2. Snow | All Wastewater System ROC General | 2025-11-16
ROC | November | KSSP - SF-4 Low air flow switch alarm and MUA2 diff pressure switch high alarms. Both alarms are air supply systems for the raw sewage headworks building. Shift report directs to disregard MUA alarms for anything except the chemical buildings. Able to reset the SF-4 air flow alarm. | All Wastewater System ROC General | 2025-11-16
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-15
ROC | November | NBSP, Lance J on site, working on the air compressors, directed to disregard alarms from site. may also cause a sump flood alarm, directed to disregard. he will call the ROC to confirm alarms have come in | All Wastewater System ROC General | 2025-11-17
ROC | November | Ethan Ullalkar signing out. | All Wastewater System ROC General | 2025-11-15
ROC | November | YDSS + YNSS Normal AUSSYS - wet well 1 ultrasonic level hihi alarm. Checked site, this LIT is misreading. Station normal. | All Wastewater System ROC General | 2025-11-15
ROC | November | SHSP, David D from maint is on site, working with Total Power contractor, the will be running the generator and testing its load. | All Wastewater System ROC General | 2025-11-17
ROC | November | SHSP - Marcus R. is on site working on the generator 13:11 - Marcus R. called back to inform that he will be working on the reject sump pump and testing the hi/low float and may work on the compressors as well | All Wastewater System ROC General | 2025-11-17
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-17
ROC | November | SEBR - S1 humid chamber level low alarm. This alarm has been triggering often but quickly returns to normal alarm status and clears itself on acknowledgment. Sent email to area ops to have it investigated. | All Wastewater System ROC General | 2025-11-16
ROC | November | KSOCMA - Exhaust fan low pressure alarm. Disregard as per the shift report. | All Wastewater System ROC General | 2025-11-18
ROC | November | Adeela Khan signing out | All Wastewater System ROC General | 2025-11-17
ROC | November | YDSS+YNSS normal | All Wastewater System ROC General | 2025-11-13
ROC | November | Ethan U signing in | All Wastewater System ROC General | 2025-11-13
ROC | November | SUSP - UV system low dosage, UV system critical failure, UV system transmittance low low and major fault alarms. Checked site, UV system is active and showing all four banks as on. Trending appears normal except for a small gap of approximately one minute. The shift report details that the critical fault alarms comes in when the plant activates but the trending shows that flow to the UV system was consistent before the alarms occurred, indicating that the plant was online before the alarms triggered. Contacted Darren B to confirm this was not a failure of the UV system. While on the phone with Darren SCADA showed that all four UV banks activated again. Darren B will check SCADA. 00:05 - Darren B called back and stated he was unable to connect to SCADA. Darren inquired about the current status of the UV system and stated that the system appears to be operating normally based on the information given. Darren directed to disregard the outstanding alarms until 09:00 Tuesday morning. #consult | All Wastewater System ROC General | 2025-11-17
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-18
ROC | November | SEBR - F1 pump 2 fail to start alarm. Checked site, pump 1 is duty 1 and running. Able to clear alarm. | All Wastewater System ROC General | 2025-11-18
ROC | November | HMSS - Gavin W running generator. | All Wastewater System ROC General | 2025-11-13
ROC | November | LSSS, Wet Well 1 Bub Low Air Pressure, Dan K directed to disregard at this time | All Wastewater System ROC General | 2025-11-17
ROC | November | YDSS + YNSS Normal Carter Dunn Signing Out | All Wastewater System ROC General | 2025-11-17
ROC | November | Christian Van Beek signing out. | All Wastewater System ROC General | 2025-11-16
ROC | November | RHAMF1 - Kyle C. is working with the contractor and will be placing the system in emergency mode as they will be shutting down train 2. Train 1 will compensate for loss of air flow. Requested to disregard alarms for the time being 10:25 - Kyle C. is finished working on the system | All Wastewater System ROC General | 2025-11-17
ROC | November | SUSP - Eyewash alarm, followed up with Tyson C. Everything okay. Disregard AUSSYS - Evgeni S rebooting OIT | All Wastewater System ROC General | 2025-11-13
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-16
ROC | November | RHAMF1-Kyle C with contractors leaving shortly, site back to normal operation. | All Wastewater System ROC General | 2025-11-14
ROC | November | Adam Button signing in -2 Clear | All Wastewater System ROC General | 2025-11-18
ROC | November | BLSS- Young J on site working on Mech screen system | All Wastewater System ROC General | 2025-11-11
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-17
ROC | November | SEOC4 - Shaft 4 fan duty rotation imminent alarm. Disregard as per shift report. LSSS - Wet well 1 & 2 bub low air pressure. Disregard as known issue from this weekend | All Wastewater System ROC General | 2025-11-17
ROC | November | SEOC- F1 P2 failed to start. Reset alarm | All Wastewater System ROC General | 2025-11-13
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-17
ROC | November | Christian Van Beek signing in. Weather: 0C and clear. | All Wastewater System ROC General | 2025-11-18
ROC | November | LSSS - Wetwell 1 & 2 bub low air pressure. Informed Dan K, will take a look on SCADA 22:34 - Dan K will head to site to check for pressure leak CMU = 11446064 22:29 - Dan K finished at site. Ran compressor to top up pressure. Disregard for the night if alarms for bub low air pressure come back | All Wastewater System ROC General | 2025-11-14
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-18
ROC | November | YDSS + YNSS Normal Christian Van Beek signing out. | All Wastewater System ROC General | 2025-11-18
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-16
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-16
ROC | November | KSSSQW - Boiler 1 fault alarm. Checked site, operations are normal. Two previous times this alarm came it is was stated to be a disregard overnight. Low priority alarm. Leaving alarm outstanding and sending email to OCO. 18:14 - KSSSQW - Boiler 1 fault alarm was originally going to be a disregard. Review of the temperature trends shows the mechanical room and odour control room temperatures have been declining since. Called Darren B who directed to disregard for the night. #consult | All Wastewater System ROC General | 2025-11-16
ROC | November | KSSP - UV channel 2 bank 2 a lamp fail and adjacent lamp fail. Disregard alarms as per the shift report. | All Wastewater System ROC General | 2025-11-17
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-17
ROC | November | SUSSSR - Received a call from a citizen who stated that there is an audible alarm at SUSSSR. Contacted Darren B who will attend site to reset this audible alarm which was triggered by the power failure. Created a CMU5#W11446300 #consult #CMU5 | All Wastewater System ROC General | 2025-11-16
ROC | November | RHAMF - Odour control system in emergency mode alarm. Informed Daniel K, is onsite for testing and running only 1 fan. Disregard alarms until end of work day | All Wastewater System ROC General | 2025-11-12
ROC | November | KSSP, Chris C on site doing a chemical system drawdown | All Wastewater System ROC General | 2025-11-18
ROC | November | YDSS + YNSS Normal Carter Dunn Signing Out | All Wastewater System ROC General | 2025-11-18
ROC | November | YDSS+YNSS normal Adam Button signing out | All Wastewater System ROC General | 2025-11-18
ROC | November | SHSP, WAS Flow lolo, Notified Young J, he will contact Marcus R and they will figure it out | All Wastewater System ROC General | 2025-11-18
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-15
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-15
ROC | November | YDSS+YNSS normal | All Wastewater System ROC General | 2025-11-13
ROC | November | YDSS+YNSS NORMAL Angelica Chepiga signing out | All Wastewater System ROC General | 2025-11-14
ROC | November | GRSSWA - Cam B testing dry well flood and temp alarms. | All Wastewater System ROC General | 2025-11-11
ROC | November | JDSS - Cam B onsite testing diesel and monthly W/O | All Wastewater System ROC General | 2025-11-12
ROC | November | KSSP - UV Panel Major fault alarm, notified Mike B, he is on site, will check. | All Wastewater System ROC General | 2025-11-12
ROC | November | SECC - Hydrogen peroxide tank 2 level low switch alarm. Checked site, tank 2 level is low and pump 3 is active and drawing from the tank. Shift report does not indicate anything related to a disregard. Called Daniel K who stated that this site is completing a 45 day test and the plan is for this tank to be drained completely. Daniel K stated that the low and lowlow level alarms can be disregarded for hydrogen peroxide tank 2. Requested that Daniel K add these alarms to the shift report for future nights. #consult | All Wastewater System ROC General | 2025-11-17
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-17
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-18
ROC | November | YDSS+YNSS normal | All Wastewater System ROC General | 2025-11-11
ROC | November | QVSSSC- Neil O on site to test drywell flood. Sump Pit flood and eyewash alarms on site | All Wastewater System ROC General | 2025-11-11
ROC | November | SECC- H2O2 P2 failed to start alarm came in. Cleared after acknowledgement | All Wastewater System ROC General | 2025-11-11
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-12
ROC | November | Adam Button signing in 2C Raining | All Wastewater System ROC General | 2025-11-12
ROC | November | KSSSQW - Mike B onsite running diesel generator | All Wastewater System ROC General | 2025-11-13
ROC | November | SEOC - OCF O2 low alarm- disregard as per SCADA report. | All Wastewater System ROC General | 2025-11-12
ROC | November | Ethan Ullalkar signing out. | All Wastewater System ROC General | 2025-11-17
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-18
ROC | November | NBSP - Vortex 2 air scour uncommanded close alarm. Reset alarm as per shift report. | All Wastewater System ROC General | 2025-11-18
ROC | November | KSSP - ZW3 shutdown alarm due to permeate turbidity out of range. Checked site, two trains in production and two trains standing by. Most recent shift report states that train 3 turbidity shut down alarms can be disregarded. | All Wastewater System ROC General | 2025-11-18
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-15
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-15
ROC | November | KBSP - UV channel 1 major alarm. Young J called to inform he requires the assistance of the on-call electrician. Contacted Sean P who will respond. Created CMU5#W11446134 #consult #CMU5 | All Wastewater System ROC General | 2025-11-15
ROC | November | HMSS- Illegal entry alarm came in on dialer. Gavin W on site | All Wastewater System ROC General | 2025-11-18
ROC | November | KSSP- Neil O. on site to work sludge blowers and channel blowers | All Wastewater System ROC General | 2025-11-18
ROC | November | LSSS- David D on site to check 4160 Switch gear and will be placing P2 man/off for 15 mins | All Wastewater System ROC General | 2025-11-11
ROC | November | Carter Dunn Signing Out | All Wastewater System ROC General | 2025-11-11
ROC | November | AUSSSR- Line one valve failed to close alarm and over torque alarm came e in. Notified Phil r. Will attend site | All Wastewater System ROC General | 2025-11-18
ROC | November | SHSSDK- Young J cleaning wetwell and testing High level alarm. Disregard alarms for the duration of the work. Will attend NBSSJA after for wet well cleaning and High level alarm testing. | All Wastewater System ROC General | 2025-11-12
ROC | November | AUSSSR, Overtorque Valve line alarm, CMU5 made for Philip R CMU5: W11452656 | All Wastewater System ROC General | 2025-11-18
ROC | November | Ethan U signing in Weather 2. | All Wastewater System ROC General | 2025-11-12
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-14
ROC | November | NMSSHS - Terry R finished on site, | All Wastewater System ROC General | 2025-11-14
ROC | November | Christian Van Beek signing in. Weather: 2C and clear. | All Wastewater System ROC General | 2025-11-16
ROC | November | YDSS + YNSS Normal KBSP - UV channel 1 common major alarm. Checked site, trending shows no indication of a power failure at the plant. Contacted Young J who will investigate the issue. 12:10 - KBSP - Young J attending site to investigate further. Created CMU5#W11446116 #consult | All Wastewater System ROC General | 2025-11-15
ROC | November | Ethan U signing in Weather 6. | All Wastewater System ROC General | 2025-11-15
ROC | November | Carter Dunn Signing Out, Ethan U is on site | All Wastewater System ROC General | 2025-11-14
ROC | November | SHSP- Marcus R on site to work on vortex's and conveyors | All Wastewater System ROC General | 2025-11-18
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-19
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-16
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-19
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-14
ROC | November | VNRSKS - Activate duty 1 AURSBR - Activate duty 1 as MARS is hi level | All Wastewater System ROC General | 2025-11-16
ROC | November | SUSP - Equalization tank hi alarm. Checked site, tank is reading hi and the filter pump is on. Called Darren B who will check the system #consult | All Wastewater System ROC General | 2025-11-15
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-15
ROC | November | SHSP - WAS pump 2 uncmd stop. Ras pumps active. Trends show pump was not running when alarm came in. | All Wastewater System ROC General | 2025-11-15
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-19
ROC | November | NMVCBP - Wet well 1 ultrasonic mode, pump 2 interlocked. Cleared hi temp and uncmd alarm but pumps remains interlocked since maintenance pulled pump 1. Followed up with Marin T. Martin T will reach back with Dan K regarding pump issues and hi alarm MTSP - Chris R diverting, disregard effluent lolo | All Wastewater System ROC General | 2025-11-13
ROC | November | AUSSYS - Evgeny S completed work. | All Wastewater System ROC General | 2025-11-13
ROC | November | SUSP - Tyson C called, work on UVs completed. Alarms cleared. Tyson C leaving site. | All Wastewater System ROC General | 2025-11-13
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-13
ROC | November | YDOC - Fan 1 uncmd stop. Fan 1 outlet gate fault. Placed fan 1 in man/off. Informed dan K of knife gate fault. Disregard for the night and will address tomorrow Consult | All Wastewater System ROC General | 2025-11-13
ROC | November | SUSP - Hydro power not available alarm and associated alarms for large scale power failure. Checked site, generator is running. UV system did drop during the initial power transfer to generator power. Contacted Darren B who is currently at KSTP and will check site. SUSSWB - Hydro power fail alarm. Checked site, generator is running. A high wet well level alarm came in but they cleared. Operations appear normal. SUSSHS - Generator running alarm. Checked site, generator is off and ATS is pointing to town hydro. Cleared alarm. SUSSSR - Hydro power fail alarm. Checked site, operations appear normal. Town hydro available alarm is present. Able to clear alarms. GRSSWA - Hydro power fail alarm. Checked site, generator is running but the ATS is pointing to town hydro indicating that normal power has been restored. Operations appear normal, no additional alarms. Hydro One Power outage map shows numerous power failure sites in the Georgina/Keswick/Sutton area. Crews working to restore various small outages. #consult | All Wastewater System ROC General | 2025-11-16
ROC | November | MTSP - Aeriation tank 1 still reading li, Man/start blower 3 | All Wastewater System ROC General | 2025-11-16
ROC | November | NBSP- Brent St. C. on site for generator load test. Lance J on site as well | All Wastewater System ROC General | 2025-11-18
ROC | November | SUSP, UV System Major Fault, notified Chase J, he is looking into it | All Wastewater System ROC General | 2025-11-18
ROC | November | KCSSKR, Young J on site, pumps will be off as needed | All Wastewater System ROC General | 2025-11-14
ROC | November | SUSP - No Air compressors available, UV system UPS fault alarms - Notified Chris C. As per Chris C. CPD working on compressors, electrician working on UV system UPS. Chris C on site, disregard alarms until further notice. | All Wastewater System ROC General | 2025-11-14
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-14
ROC | November | BLSS - Mechanical Screen System Not On and Screen 1 Fault alarms came in. Called Young J. who informed that no one is on site and will head to site to check this out 10:45 - Dan H. is headed to site. CMU5 Created W11449605 #CMU5 | All Wastewater System ROC General | 2025-11-17
ROC | November | SEOC67 - Terry C requested switch Fans, Assigned Fan 2 to Duty 1, Fan 1 to Duty 2. | All Wastewater System ROC General | 2025-11-13
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-15
ROC | November | YDSS + YNSS Normal MTSP - Place blower 3 back in auto | All Wastewater System ROC General | 2025-11-16
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-17
ROC | November | SEBR - F1 pump 2 fail to start alarm. Checked site, pump 1 is duty 1 auto and running. Shift report states that filter 1 pump 2 is OOS but it is currently in auto mode. Able to clear alarm but will monitor site through the night. | All Wastewater System ROC General | 2025-11-17
ROC | November | YDSS+YNSS normal | All Wastewater System ROC General | 2025-11-13
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-14
ROC | November | Angelica Chepiga signing in, weather +4C | All Wastewater System ROC General | 2025-11-13
ROC | November | Adam Button signing out | All Wastewater System ROC General | 2025-11-13
ROC | November | NMVCBP - Martin D working on pumps. Will start/stop. Disregard alarms. | All Wastewater System ROC General | 2025-11-13
ROC | November | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-11-13
ROC | November | Angelica Chepiga signing in | All Wastewater System ROC General | 2025-11-14
ROC | November | EGSSSC- Diesel containment flood alarm came in. Diesel LIT trends holding. Notified Darren B of issue. Directed to disregard. #consult | All Wastewater System ROC General | 2025-11-12
ROC | November | KSSP- Hypo tank lo alarm outstanding Chase J on site emptying tank in to secondary containment not on SCADA SUSSHS- P1 OOS for night | All Wastewater System ROC General | 2025-11-11
ROC | November | Carter Dunn Signing In, 0D/Clear | All Wastewater System ROC General | 2025-11-11
ROC | November | YDOC - Man/start fan 1 and stop fan 2 for maintenance check as requested by Terry C | All Wastewater System ROC General | 2025-11-13
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-12
ROC | November | Christian Van Beek signing in. Weather: 0C and clear. | All Wastewater System ROC General | 2025-11-15
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-16
ROC | November | Christian Van Beek signing in. Weather: 0C and clear. | All Wastewater System ROC General | 2025-11-17
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-11
ROC | November | SUSSHS - Matt T working on Pump 1. | All Wastewater System ROC General | 2025-11-11
ROC | November | Ethan Ullalkar signing out. | All Wastewater System ROC General | 2025-11-12
ROC | November | Angelica Chepiga signing out | All Wastewater System ROC General | 2025-11-11
ROC | November | EGSSSC - Neil O running generator, testing flood alarm and dialer alarm, testing eyewash alarm. | All Wastewater System ROC General | 2025-11-12
ROC | November | AUSSYS - Wet well 1&2 No discharge path alarms. Phil R on site. | All Wastewater System ROC General | 2025-11-14
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-18
ROC | November | QVSSSC - Channel Grinder E stop came in. As this is a critical alarm, called Neil O. who confirmed there is a jam in the channel grinder and is currently trying to fix the jam. | All Wastewater System ROC General | 2025-11-17
ROC | November | SUSP - Tyson C called, contractor working on UVs, disregard UV alarms for the duration of the work. | All Wastewater System ROC General | 2025-11-13
ROC | November | KSSSQW - Neil O and Cam B on site for wetwell cleaning. Disregard alarms for the duration of the work. | All Wastewater System ROC General | 2025-11-11
ROC | November | SHSP - Marcus R working on UV system, disregard alarms for the duration of the work. | All Wastewater System ROC General | 2025-11-12
ROC | November | YDSS + YNSS Normasl Connor Smith signing out | All Wastewater System ROC General | 2025-11-14
ROC | November | SUSP - UV Channel 1 UV intensity fault alarm. Chris C working on it. | All Wastewater System ROC General | 2025-11-11
ROC | November | SEOC4 - Marcus T onsite running generator | All Wastewater System ROC General | 2025-11-13
ROC | November | LSSS, Yash S is heading to site to reset the OIT as per Marcos T | All Wastewater System ROC General | 2025-11-17
ROC | November | KBSP, Lauren S on site working in the headworks building, directed to disregard alarms on site | All Wastewater System ROC General | 2025-11-14
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-11
ROC | November | RHAMF1, Kyle C on site with contractors, station will be running in emergency mode, directed to disregard alarms on site as Kyle will be working with contractors | All Wastewater System ROC General | 2025-11-14
ROC | November | YDSS+YNSS normal Adam Button signing out | All Wastewater System ROC General | 2025-11-11
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-12
ROC | November | SUSP - Compressor 1 excessive run time alarm. Informed Tyson C, will look into issue | All Wastewater System ROC General | 2025-11-13
ROC | November | NMSSHS, Terry R on site, testing wet well alarms and testing dialer alarms | All Wastewater System ROC General | 2025-11-14
ROC | November | SHSSDK - Contractors running semi-annual generator test, Marcus R on site monitoring. | All Wastewater System ROC General | 2025-11-14
ROC | November | QVSSSC - Neil O. is headed to site to run the generator | All Wastewater System ROC General | 2025-11-17
ROC | November | SEBR - S1 humid chamber low level switch alarm. Disregard as per Dan K email. | All Wastewater System ROC General | 2025-11-17
ROC | November | AUSS - Phil R testing High wet well level, Dry well flood, dialer alarms. | All Wastewater System ROC General | 2025-11-12
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-15
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-17
ROC | November | YDSS+YNSS normal | All Wastewater System ROC General | 2025-11-13
ROC | November | MTSP - Aeriation tank 2 DO lolo, change controlling tank to tank 2 | All Wastewater System ROC General | 2025-11-16
ROC | November | EGSSSC - Diesel containment flood. Disregard as per Darren B | All Wastewater System ROC General | 2025-11-13
ROC | November | NBSP - Scum pump 1 general alarm. Called Lance J, disregard for the night | All Wastewater System ROC General | 2025-11-13
ROC | November | Christian Van Beek signing out. | All Wastewater System ROC General | 2025-11-15
ROC | November | MTSP - Aeration tank 1 DO lo, rotated tank 1 to controlling as per shit report | All Wastewater System ROC General | 2025-11-15
ROC | November | NMSSBP - Screen 1 differential fault. Disregard as per shift report | All Wastewater System ROC General | 2025-11-15
ROC | November | SEOC4 - Terry C requested to switch Fans, assigned Fan 1 to Duty 1, Fan 2 to Duty2. | All Wastewater System ROC General | 2025-11-13
ROC | November | SUSP, Chase J on site, Working on the blowers and the valving on site, directed to disregard alarms on site till he leaves | All Wastewater System ROC General | 2025-11-18
ROC | November | Angelica Chepiga signing out | All Wastewater System ROC General | 2025-11-13
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-13
ROC | November | KBSP - Young J finished at site. UV 1 will remain OOS for the weekend with UV2 in duty | All Wastewater System ROC General | 2025-11-15
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-16
ROC | November | Ethan Ullalkar signing out. | All Wastewater System ROC General | 2025-11-16
ROC | November | Angelica Chepiga signing in | All Wastewater System ROC General | 2025-11-12
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-14
ROC | November | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-11-16
ROC | November | MTSP - Aeriation tank 1 DO lo. Swap to tank 1 controlling tank as per shift report | All Wastewater System ROC General | 2025-11-16
ROC | November | KSSSQW- P4 lo flo alarm came in was able to clear | All Wastewater System ROC General | 2025-11-18
ROC | November | MTSP, No air compressor available alarm, contacted Barry M but no response, left voice message, will call back in 10 minutes 11:01, Chris R called saying him and reliance were working on the air compressors, directed to disregard | All Wastewater System ROC General | 2025-11-14
ROC | November | Carter Dunn Signing In | All Wastewater System ROC General | 2025-11-18
ROC | November | AUSS- P1 disc MV2 failed to open alarm came in able to reset | All Wastewater System ROC General | 2025-11-18
ROC | November | Ethan U signing in Weather 2. | All Wastewater System ROC General | 2025-11-14
ROC | November | KBSP - Eric S. is on site and will be working on the gas analyzers 13:20 - Eric called back to inform that he is finished on site and has cleared all outstanding alarms | All Wastewater System ROC General | 2025-11-17
WEST | November | Onsite for station check Well duty not active Checked residuals mg/l @1351 Post reservoir Free analyzer 1.90 grab 1.64 Adjusted analyzer @1356 Treated Free analyzer 1.77 grab 1.68 Total grab 1.96 Noticed air in lines, primed both hypo pumps | Ansnorveldt Wells 2, 3 & Reservoir | 2025-11-07
ROC | November | MARS - Courtney from Torbear on site. | ROC General | 2025-11-10
ROC | November | Christian Van Beek signing out. | ROC General | 2025-11-10
ROC | November | Ethan U signing in Weather 7. | ROC General | 2025-11-07
ROC | November | YDOC - Drew from Ferguson Electric is on site 07:23 - Drew is finished on site | ROC General | 2025-11-10
ROC | November | JFPS - Houman from CPD with contractors on site. | ROC General | 2025-11-03
ROC | November | MTW3 - Jerry from AB on site. | ROC General | 2025-11-03
ROC | November | STPSMR- Garrick from Ferguson Electric is on site | ROC General | 2025-11-24
ROC | November | MARS - Courtney from Torbear Contracting is on site | ROC General | 2025-11-17
ROC | November | Town of Stouffville - Andrew from OWCA flushing zone 1 & 2 until 13:00 | ROC General | 2025-11-17
ROC | November | KSETWB - Contractor onsite for fibre optic cable JFPS - Frank from PS onsite for maintenance and filter change | ROC General | 2025-11-12
ROC | November | GRSSWA- Kevin from York net leaving site, heading to GWTP and GWTP Low lift. | ROC General | 2025-11-12
ROC | November | VNRSKS - Francesco from PR onsite for sprinkler test | ROC General | 2025-11-13
ROC | November | Angelica Chepiga signing out | ROC General | 2025-11-13
WEST | November | On site for station check Well duty not active Checked residuals mg/l Treated hl @1417 Free analyzer 1.76 grab 1.75 Total grab 1.92 Post res @1420 Free analyzer 1.63 grab 1.79 Adjusted analyzer | Ansnorveldt Wells 2, 3 & Reservoir | 2025-11-10
WEST | November | On site for Scheduled PM's. Informed ROC about the Works being done. W11342270 ANW23 JHSC Health and Safety Inspection (1M) W11341780 ANW23, Generator Test Run (1M) Pre check Battery okay- 13.3 V Coolant- Okay Oil - Okay Before Start Start time- 09:53 Run time- 298:39 hr Ran Pump 3&4 in Auto when reservoir on 75% After Stop Stop time- 10:57 Run time- 299:48 hr W11342451 ANW23, Eye Wash, Cleaning & Solution Replacement W11342737 ANW23, Pressure Regulating Valve Maintenance (1M) W11342812 ANW23, Valve Exercise (3M) W11342834 ANW23, Ansnorveldt Wells 2/3, Air Release Valve Inspection (3M) W11342903 ANW23, Ansnorveldt Wells 2/3 , Siemens Depolox 5/Micro 2000 Chlorine Analyzer (1M) 13:20-Verified post res Analyzer free CL2 grab-1.95 mg/L, Analyzer 2.00 mg/L 13:30-Verified pre res Analyzer free CL2 grab-3.40 mg/L, Analyzer 3.38 mg/L 13:35-Verified post res(treated) Analyzer free CL2 grab-2.00 mg/L, Analyzer 2.10 mg/L | Ansnorveldt Wells 2, 3 & Reservoir | 2025-11-04
WEST | November | Onsite for station check Duty not active Verified Analyzers 09:35-Post res Free analyzer 2.07 mg/L, grab 2.06 mg/L 09:38-Treated HL Free analyzer 2.13 mg/L, grab 2.09 mg/L Total grab- 2.15 | Ansnorveldt Wells 2, 3 & Reservoir | 2025-11-03
WEST | November | On site for station check, weekly micro sampling, and a Q4 re-sample. Activated well duty on arrival. Checked SCADA and trending. Entered station data into PWQ sheet. Verified chlorine analyzers: Reservoir inlet free chlorine @ 10:14 Grab: 3.04 mg/L Analyzer: 3:11 mg/L Reservoir Outlet free chlorine @ 10:06 Grab: 1.97 mg/L Analyzer: 1.97 mg/L Treated Water Free Grab @ 10:20 - 1.98 mg/L Analyzer 2.05 mg/L Total grab @ 10:18 - 2.05 mg/L Adjusted analyzer at 11:06 after three grab samples to 1.89 mg/L. Station OK. | Ansnorveldt Wells 2, 3 & Reservoir | 2025-11-05
WEST | November | On site for station check Check Trends: All okay Well off Verified Analyzers 13:50-Post Reservoir Free Grab: 1.44 mg/L, Analyzer 1.37 mg/L 13:54-Post Reservoir (treated) Free- grab 1.48mg/L, Analyzer 1.38mg/L Entered Values in PWQ sheet. Equipment okay. | Ansnorveldt Wells 2, 3 & Reservoir | 2025-11-28
WEST | November | Onsite for station check Well duty active CHecked residuals mg/L Reservoir inlet @1401 Free analyzer 3.04 grab 2.76 Adjusted based on average of multiple grabs Pre inj @1405 Free analyzer 1.50 grab 1.44 Treated HL @1408 Free analyzer 1.43 grab 1.45 Total grab 1.66 Topped up hypo tank | Ansnorveldt Wells 2, 3 & Reservoir | 2025-11-24
WEST | November | On site for station check Check Trends: All okay Well off Verified Analyzers 08:45-Post Reservoir Free Grab: 1.42mg/L, Analyzer 1.48mg/L 08:50-Post Reservoir (treated) Free- grab 1.38mg/L, Analyzer 1.38mg/L Entered Values in PWQ sheet. Equipment okay. | Ansnorveldt Wells 2, 3 & Reservoir | 2025-11-21
WEST | November | on site to Complete Station Check and to collect bacti sample W11402444 Check Trends: All okay. Well running Historian heartbeat alarm interlocked the well, PCS fixed it, started the well again. Verified Analyzers 09:45-Pre Reservoir Free Grab: 3.50mg/L, Analyzer 3.43mg/L 09:48-Post Reservoir Free Grab: 1.50mg/L, Analyzer 1.40mg/L 09:20-Post Reservoir (treated) Free- grab 1.47mg/L, Analyzer 1.37mg/L Total grab- 1.55 mg/L. Samples Collected Entered Values in PWQ sheet. Equipment okay. | Ansnorveldt Wells 2, 3 & Reservoir | 2025-11-26
WEST | November | on site to Complete Station Check and to collect bacti sample W11386650 Check Trends: All okay. Well running Verified Analyzers 09:05-Post Reservoir Free Grab: 1.40mg/L, Analyzer 1.44mg/L 09:00-Pre Reservoir Free Grab: 3.30mg/L, Analyzer 3.20mg/L 09:20-Post Reservoir (treated) Free- grab 1.44mg/L, Analyzer 1.44mg/L Total grab- 1.50 mg/L. Samples Collected Entered Values in PWQ sheet. Equipment okay. | Ansnorveldt Wells 2, 3 & Reservoir | 2025-11-19
WEST | November | On site for station check Well off Verified Analyzers 14:25-Post Reservoir Free Grab: 1.35mg/L, Analyzer 1.45mg/L 14:30-Post Reservoir (treated) Free- grab 1.51mg/L, Analyzer 1.50mg/L W11342762-Turbidity analyzer maintenance and calibration vial cleaned and verified analyzer Entered Values in PWQ sheet. Equipment okay. | Ansnorveldt Wells 2, 3 & Reservoir | 2025-11-17
WEST | November | On site for station check Well running Troubleshoot inlet free cl2 low. Found leak in the discharge and suction side lines of hypo pump 2, changed all lines suction & discharge, replaced tube. primed the line. put the pump back to duty. Verified Analyzers 10:25-Post Reservoir Free Grab: 1.17mg/L, Analyzer 1.26mg/L 10:30-Pre Reservoir Free Grab: 2.82, Analyzer 2.82mg/L 10:00-Post Reservoir (treated) Free- grab 1.42mg/L, Analyzer 1.38mg/L Total grab- 1.54 mg/L. Entered Values in PWQ sheet. Equipment okay. No other issues on site. | Ansnorveldt Wells 2, 3 & Reservoir | 2025-11-14
WEST | November | on site to Complete Station Check and to collect bacti sample W11368100 Gate hinge bracket seen bent, informed Team lead. Well running increased hypo Pump 1,2 dosage factor by 2% Verified Analyzers 09:10-Post Reservoir Free Grab: 1.60mg/L, Analyzer 1.50mg/L 09:30-Pre Reservoir Free Grab: 2.60mg/L (2.56.2.58,2.64), Analyzer 1.80mg/L Adjusted Analyzer up to 2.50 mg/L Samples Collected 10:00-Post Reservoir (treated) Free- grab 1.40mg/L, Analyzer 1.45mg/L Total grab- 1.56 mg/L. Entered Values in PWQ sheet. Equipment okay. Topped up Hypo tank- 27cm,26cm/47cm,46cm No other issues on site. | Ansnorveldt Wells 2, 3 & Reservoir | 2025-11-12
CENTRAL | November | -Performed station check - logged station readings into PWQ sheet Grab: total=2.62mg/L free=0.06mg/L@8:55 Analyzer total=2.51mg/L free=0.01mg/L -Topped up Depolox's buffer solution -Calibrated total analyzer based on 3 grab tests -Collected weekly BacT sample YD #W11348542 & monthly sample YD #W11348512 | Aurora (East) First Commerce Elevated Tank | 2025-11-05
CENTRAL | November | Informed ROC. Onsite to perform annual calibration/maintenance. Used calibration mode during the work. Devices were done as below. TWR_LIT, TWR_PIT, TWR_LCV, Free and Total chlorine analyzer. Informed ROC before and after calibration of TWR_LIT. Took a multiple grab samples and adjusted analyzer accordingly. Free Grab - 0.04 mg/l, Free AIT - 0.04 mg/l Total Grab - 2.64 mg/l , Total AIT - 2.70 mg/l. Put everything back in service. All the related alarms were cleared. No issues. Informed ROC, armed the building and left the site. | Aurora (East) First Commerce Elevated Tank | 2025-11-26
CENTRAL | November | On site to complete PMs. Notified the ROC of relevant alarms. -Completed Depolox analyzer maintenance: -Topped up KI reagent -Verified analyzer with following grabs: Outlet Free chlorine @ 11:03 G: 0.03 mg/L A: 0.05 mg/L Outlet Total Chlorine @ 11:08 G: 2.58 mg/L A: 2.73 mg/L Adjusted analyzer based on average of grabs. Analyzer read 2.59 mg/L afterwards. -Completed portable generator test -Inspected altitude valve -Flushed and inspected air valves -Inspected inlet/outlet hear trace system: no apparent issues -Exercised drain valve -Tested low temp alarms -Completed JHSC inspection -Inspected dehumidifier -Inspected ventilation system -Exercised all manual valves | Aurora (East) First Commerce Elevated Tank | 2025-11-25
CENTRAL | November | Informed ROC Onsite to perform annual calibrations. Used calibration mode during the work. - inlet and outlet FIT. Added grit for total chlorine analyzer. Put everything back in service. All the related alarms were cleared. No issues. Informed ROC, armed the building and left the site. | Aurora (East) First Commerce Elevated Tank | 2025-11-28
CENTRAL | November | -Performed station check - logged station readings into PWQ sheet Grab: free=0.05mg/L total=2.68mg/L@9:05 Analyzer: free=0.00mg/L total=2.63mg/L -Checked Depolox reagents - OK -Collected weekly BacT sample YD #W11387379 & DWSP samples -Calibrated and zeroed free analyzer | Aurora (East) First Commerce Elevated Tank | 2025-11-19
CENTRAL | November | On site to perform station check and to collect weekly bacti sample WO#11403047, & to collect operational samples - Tower draining when arrived - Entered readings to Process Data sheets and collected samples - Check trends all okay - Checked reagents - Equipment all okay - No new issues found Free Cl grab @ 2:56pm G: 0.04mg/L A: 0.04mg/L Treated Total Cl grab @ 2:56pm G: 2.66mg/L A: 2.71mg/L | Aurora (East) First Commerce Elevated Tank | 2025-11-26
CENTRAL | November | -Performed station check - logged station readings into PWQ sheet Grab: total=2.72mg/L free=0.07mg/L@8:50 Analyzer: total=2.69mg/L free=0.02mg/L -Checked Depolox reagents - OK -Collected weekly BacT sample YD #W11368818 & in-house water quality samples | Aurora (East) First Commerce Elevated Tank | 2025-11-12
CENTRAL | November | On site to top up gas in portable generator. No issues found | Aurora (East) First Commerce Elevated Tank | 2025-11-28
CENTRAL | November | Test pump 4 vibration | Aurora (East) Wellington Pumping Station | 2025-11-05
CENTRAL | November | On site with mechanics to replace pump #5 motor. ROC notified. Pump 5 speed OOR alarm acknowledged. Building temperature alarm acknowledged. Unit heaters #5 and 6 in generator rm energized. Pump 5 motor installation complete, correct rotation verified in hand. Returned to auto. All equipment in normal operation. ROC notified. | Aurora (East) Wellington Pumping Station | 2025-11-06
CENTRAL | November | On-site for station checks. Adjusted temperature alarm set point and building temperature alarm cleared, building temp ok. Noticed that reverse flow has been registered on the flow meter over the past week, but trending does not show reverse flow, WO for PCS to add reverse flow trending will be made for further investigation, will monitor. No other new issues found while on-site. | Aurora (East) Wellington Pumping Station | 2025-11-07
CENTRAL | November | On-site for a station and equipment check, no issues found Hands All readings entered in PWQ sheet | Aurora (East) Wellington Pumping Station | 2025-11-10
CENTRAL | November | On-site for a station and equipment check, no issues found All readings and measurements entered into PWQ sheet | Aurora (East) Wellington Pumping Station | 2025-11-03
CENTRAL | November | Wrong location entered by mistake. | Aurora (East) Wellington Pumping Station | 2025-11-04
CENTRAL | November | On-site for a station and equipment check, no issues found Entered all readings into PWQ sheet | Aurora (East) Wellington Pumping Station | 2025-11-21
CENTRAL | November | on-site for various WO's Sump pit inspection and pump tested Exercised suction and discharge valves Pump and motor inspections while running Flood test alarm completed JHSC inspection completed Visual inspection of check valves and PRV/surge valve Visual inspection of ventilation system Station and equipment checked, no issues found All readings and measurements entered into PWQ sheet Comprehensive house keeping Generator testing under load of pump 4 -began at 1036 completed at 1142 -fuel start 1995, finish 1959L -Hours start 366.0 finish 367.1 -oil pressure 50psi -water temp 170'F -battery 32 -oil temp140'f -600 V 347V 60.0 Hz -Fuel containment alarm tested | Aurora (East) Wellington Pumping Station | 2025-11-25
CENTRAL | November | On-site to complete station check. - Entered data into PD sheets. - Tower Duty inactive on arrival. - Checked trends - all okay. - Pump 1/2/3 manual off &P4/5 in auto. - No new issues found. Suction pressure: 347 kPa Discharge pressure: 594 kPa Discharge flow: 0 L/s | Aurora (East) Wellington Pumping Station | 2025-11-28
CENTRAL | November | On-site for a station and equipment check No issues found All readings and measurements entered into PWQ sheet | Aurora (East) Wellington Pumping Station | 2025-11-14
CENTRAL | November | Pump 5 baseline vibration testing | Aurora (East) Wellington Pumping Station | 2025-11-17
CENTRAL | November | On-site for a station and equipment check, no issues found All readings and measurements entered into PWQ sheet | Aurora (East) Wellington Pumping Station | 2025-11-17
CENTRAL | November | -Performed station check - logged station readings into PWQ sheet Grab: total=2.84mg/L free=0.06mg/L@12:15 Analyzer total=2.95mg/L free=0.03mg/L -Topped up Depolox's KI solution -Collected weekly BacT sample YD #W11348542 & monthly sample YD #W11348512 | Aurora (North) Orchard Heights Elevated Tank | 2025-11-05
CENTRAL | November | On site to complete station check and to collect weekly bacti samples WO#11403047 & to collect operational samples. - Tower draining when arrived @51% - Entered data into PD & collected samples - Check trends all okay - Checked reagents - Equipment all okay - No issues found Treated Free Cl grab @ 12:52pm A: 0.07mg/L G: 0.06mg/L Treated Total Cl grab @ 12:52pm A: 2.86mg/L G: 2.92mg/L | Aurora (North) Orchard Heights Elevated Tank | 2025-11-26
CENTRAL | November | -Performed station check - logged station readings into PWQ sheet Grab: free=0.06mg/L total=3.02mg/L@15:15 Analyzer: free=0.06mg/L total=2.88mg/L -Topped up Depolox buffer solution -Collected weekly BacT sample YD #W11387379 | Aurora (North) Orchard Heights Elevated Tank | 2025-11-19
CENTRAL | November | -Finished the following work orders *Performed H&S inspection *Depolox analyzer maintenance *Valve exercises | Aurora (North) Orchard Heights Elevated Tank | 2025-11-13
CENTRAL | November | -Performed station check - logged station readings into PWQ sheet Grab: total=2.90mg/L free=0.06mg/L@13:10 Analyzer: total=3.00mg/L free=0.06mg/L -Checked Depolox reagents - OK -Collected weekly BacT sample YD #W11368818 & in-house water quality samples | Aurora (North) Orchard Heights Elevated Tank | 2025-11-12
CENTRAL | November | On-site for a station and equipment check, no issues found Hands Chemical levels and systems ok Topped up ammonia day tank 2 Adjusted Chemscan total ammonia post injection value to 0.54 from 0.33 SL1000 grab was 0.47 Verified analyzers, all readings and grabs entered into PWQ sheet | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-11-10
CENTRAL | November | Station and equipment checked, no issues found. Changed tube in ammonia pump 2. Primed and performed drawdown test. Changed dosage in SCADA max to 1600ml/m from 1450ml/m. Auto rotate on duty. Notified oncall operator about changes to monitor Topped up ammonia day tank 1. Verified analyzers and entered all measurements and grabs into PWQ sheet | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-11-05
CENTRAL | November | On-site for station check. Grab/analyzer results as follows (mg/L): Post-Injection: Free Cl (09:58): G: 0.10 A: 0.08 Total Cl (10:02): G: 3.28 A: 3.23 Pre-Injection: Free Cl (10:10): G: 0.05 A: 0.09 Total Cl (10:14): G: 1.93 A: 1.92 Switched to run ammonia P2 to observe operation. No new issues found while on-site. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-11-07
CENTRAL | November | On-site to perform various work orders Chemscan maintenance completed Changed Yellow reagent and topped up green reagent Both duplex analyzer maintenance completed Cylinder bank 2 change with B Hess Hoist testing and inspection, ok Sump pump inspection and test, ok Troubleshoot ammonia drawdown testing with B Hess, flood alarm test completed | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-11-04
CENTRAL | November | On-site for a station and equipment check, no issues found. Received 16 cylinders of CL2, returned the the same Chemical systems and levels ok Verified analyzers, all readings and grabs entered into PWQ sheet. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-11-03
CENTRAL | November | On site with Ben H to troubleshoot the mv 4 passing while closed. Ben placed maple pumps in manual. We then closed the valve manually and adjusted stops on the actuator to be more closed. We then tested to confirm we shouldn't get an over torque when operating valve. With mv4 closed we then tested running maple to Jefferson to confirm that this valve doesn't pass. After one hour of running no change in Aurora res volume was confirmed. Placed valve back to auto and valve was opened. Under direction of oic. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-11-04
CENTRAL | November | Worked with Tyler ZJ on reservoir MV4. Adjusted closed limit and tested to see if valve is holding by running a Maple PD8 to JFRS feed. Successful test. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-11-04
CENTRAL | November | Attending site to check chlorine gas detectors (scrubber and chlorine storage rooms (W11415795). Both sensors are displaying 'Cal Required' message. Calibrated both sensors without errors. Facility was off-line during maintenance work. ROC was notified before and after maintenance. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-11-04
CENTRAL | November | on-site for a station and equipment check, no issues found Chemical levels and systems ok Topped up ammonia day tank 1 Verified analyzers, entered all readings and grabs into PWQ sheet chemscan free ammonia pre injection changed to 0.07 from 0.03 and post injection total ammonia to 0.57 from 0.66, as per grabs on SL1000 Cylinder change with J Garnett, bank 2 | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-11-21
CENTRAL | November | Station and equipment check Took grabs from post @ 2:20 pm Total: 3.15 mg/l Free: 0.05 mg/l Chemicals/reagents ok SL1000 readings to be taken Wednesday sample day Ops normal | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-11-24
CENTRAL | November | On-site for a station and equipment check, no issues found Verified analyzers and entered all readings and grabs into PWQ sheet Adjust pre free ammonia on Chemscan to 0.05 from 0.09 based on SL 1000 grabs Weekly bacti sample taken Outlet totalizer reset, noted on PWQ sheet | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-11-19
CENTRAL | November | On-site for a station and equipment check, no issues found Verified analyzers and entered all readings and grabs into PWQ sheet Topped up ammonia day tank 2 Took bacti samples while draining Operational samples taken | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-11-26
CENTRAL | November | On-site to complete station check - Res filling/draining when arrived - Entered data into PD sheets. - Trends all good. - Equipment all good. - Dosages all good - topped up tank NH3 TK1 - Reagents all good. - topped up acetate buffer @ post injection depolox - No new issues found. Pre-Injection Free Cl grab @ 11:20am G: 0.06mg/L A: 0.06mg/L Total Cl grab @ 11:20am G: 2.01mg/L A: 2.00mg/L Post-Injection Free Cl grab @ 11:23am G: 0.07mg/L A: 0.05mg/L Total Cl grab @ 11:23am G: 3.16mg/L A: 3.11mg/L | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-11-28
CENTRAL | November | AURSBS Station and equipment check, no issues found Verified analyzers Chemical levels and systems ok Verified analyzers and entered all readings and grabs into PWQ sheet Changed pre-mono to 1.58 from 1.75mg/L and post-mono to 2.83 from 3.08 mg/L on chemscan unit Weekly bacti and operational samples taken. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-11-12
CENTRAL | November | Station and equipment checked, no issues found Chemical systems and levels ok, topped up ammonia day tank 2 Cylinder change with J Zhang on bank 1 Verified analyzers, all readings and grabs entered into PWQ sheet | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-11-17
CENTRAL | November | Informed ROC. Performed annual calibration and put instruments in Cal mode while doing the tasks. Devices done were AITs Chemscan and ammonia LITs. All alarms were cleared after the job. No other issues encountered. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-11-17
CENTRAL | November | On-site for a station and equipment check, no issues found. Topped up ammonia day tank 1 Chemical levels and systems ok Verified analyzers, entered all readings and grabs into PWQ sheet | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-11-14
CENTRAL | November | Station and equipment checked, no issues found bacti sample and blended fluoride sample taken Verified analyzer, entered all measurements and grabs into PWQ sheet | Aurora (Southwest) Allenvale Elevated Tank | 2025-11-05
CENTRAL | November | Onsite for various work orders; JHSC inspection completed, Building low temp alarm test, Analyzer maintenance and refill of reagents General housekeeping portable generator test ,ok heat trace continuity ok Manual valves exercised | Aurora (Southwest) Allenvale Elevated Tank | 2025-11-06
CENTRAL | November | On-site with B Hess to troubleshoot total analyzer readings. Initial grabs were 2.03 1.97 and 2.05mg/L Flushed all lines, checked electrolyte, and pulled reagent lines to clear any potential air. Grabs after analyzer settling @1033 2.07, 2.10 and 2.12mg/L Analyzer set to 2.09mg/L | Aurora (Southwest) Allenvale Elevated Tank | 2025-11-04
CENTRAL | November | Station and equipment checked, no issues found Verified analyzer and entered all readings and grabs into PWQ sheet Bacti sample taken while draining Operational sample taken as well. | Aurora (Southwest) Allenvale Elevated Tank | 2025-11-26
CENTRAL | November | On-site for a station and equipment check, no issues found Took weekly bacti sample while draining Verified analyzer and entered all readings and grabs into PWQ sheet | Aurora (Southwest) Allenvale Elevated Tank | 2025-11-19
CENTRAL | November | On-site for a station and equipment check, no issues found Verified analyzer, entered all readings and grabs into PWQ sheet Weekly bacti and operational samples taken | Aurora (Southwest) Allenvale Elevated Tank | 2025-11-12
CENTRAL | November | -Performed station check - logged station readings into PWQ sheet -Checked ChemScan reagents - OK | Aurora Orchard Heights Pumping Station & Reservoir | 2025-11-07
CENTRAL | November | -Performed station check - logged station readings into PWQ sheet | Aurora Orchard Heights Pumping Station & Reservoir | 2025-11-10
CENTRAL | November | On-site for pumping station check. Entered site readings into into shared PD excel file. No new issues found while on-site. | Aurora Orchard Heights Pumping Station & Reservoir | 2025-11-03
CENTRAL | November | -Performed station check - logged station readings into PWQ sheet Grab: total=3.16mg/L free=0.07mg/L@11:45 Analyzer total=3.18mg/L free=0.03mg/L -Topped up Depolox's KI solution -Collected weekly BacT sample YD #W11348542 & monthly sample YD #W11348512 | Aurora Orchard Heights Pumping Station & Reservoir | 2025-11-05
CENTRAL | November | On-site for station check. Entered station readings into shared PD excel file. No new issues found while on-site. | Aurora Orchard Heights Pumping Station & Reservoir | 2025-11-28
CENTRAL | November | On site to complete station check and to collect weekly bacti samples W11403047 and operational samples - Reservoir draining - Entered data into Process Data sheets & samples - Equipment all good - Trends all good - Reagents all good - No other issues Treated free Cl @ 1:18pm G: 0.04mg/L A: 0.01mg/L Treated total Cl @ 1:18pm G: 2.86mg/L A: 2.91mg/L | Aurora Orchard Heights Pumping Station & Reservoir | 2025-11-26
CENTRAL | November | Onsite to wrap up annual calibrations Informed ROC Placed devices in cal mode on scada Instruments calibrated: FITs Cleared associated alarms Informed ROC and left site Operations onsite | Aurora Orchard Heights Pumping Station & Reservoir | 2025-11-28
CENTRAL | November | -Performed station check -Checked Depolox reagents - Ok | Aurora Orchard Heights Pumping Station & Reservoir | 2025-11-24
CENTRAL | November | On site to complete station check with Ryan B - Reservoir draining - Entered data into Process Data sheets - Equipment all good - Trends all good - Reagents all good - No other issues Treated free Cl @ 11:11am G: 0.01mg/L A: 0.02mg/L Treated total Cl @ 11:11am G: 3.06mg/L A: 3.06mg/L | Aurora Orchard Heights Pumping Station & Reservoir | 2025-11-21
CENTRAL | November | -Performed station check - logged station readings into PWQ sheet Grab: free=0.06mg/L total=2.88mg/L@14:45 Analyzer: free=0.03mg/L total=2.98mg/L -Checked Depolox reagents - OK -Collected weekly BacT sample YD #W11387379 | Aurora Orchard Heights Pumping Station & Reservoir | 2025-11-19
CENTRAL | November | Onsite for annual calibrations Informed ROC Used cal mode on scada during the work Instruments calibrated: AITs, PIT and LITs No adjustments made to AITs Free G = 0.04mg/l A = 0.01mg/l Total G = 2.89mg/l A = 2.91mg/l Cleared all associated alarms Informed ROC, armed building and left site | Aurora Orchard Heights Pumping Station & Reservoir | 2025-11-26
CENTRAL | November | On-site for pumping station check. Entered station readings into shared PD excel file, no new issues found. | Aurora Orchard Heights Pumping Station & Reservoir | 2025-11-14
CENTRAL | November | -Performed station check - logged station readings into PWQ sheet Grab: total=2.90mg/L free=0.09mg/L@10:40 Analyzer: total=2.98mg/L free=0.03mg/L -Checked Depolox reagents - OK -Collected weekly BacT sample YD #W11368818 & in-house water quality samples | Aurora Orchard Heights Pumping Station & Reservoir | 2025-11-12
CENTRAL | November | -Finished the following work orders *H&S inspection *Valve exercises *Pump & motor inspection *Depolox analyzer maintenance *Dehumidifier maintenance *Vent inspection *PRV inspection *Tested Hi/Lo temp alarm *Diesel generator test run Pre-run inspection - OK Hours Start=199.7 Finish 200.9 Fuel Start=2632L Finish 2620L Tested generator while under load (P3 and P4): RPM- 1800 Volts- 600 Amperes- 75 Hertz- 60 Coolant temp 87oC Oil temp 94oC Fuel temp- 87 C | Aurora Orchard Heights Pumping Station & Reservoir | 2025-11-11
CENTRAL | November | -Performed station check - logged station readings into PWQ sheet | Aurora Orchard Heights Pumping Station & Reservoir | 2025-11-17
CENTRAL | November | Attending site to check Post Inj. Total chlorine analyzer AIT15. Could not find anything out of the ordinary. Suspect the issue was low reagents as the situation was corrected by replacing the reagents and priming the analyzer. All good now. | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2025-11-07
CENTRAL | November | On-site for a station and equipment check, no issues found Hands on training with Ben Hess on metro FCV. Chemical levels and systems operating normally Analyzers verified, all readings and grabs entered into PWQ sheet Adjusted mono offset pre injection on chemical from 1.64 to 1.50 on a grab of 1.48 | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2025-11-10
CENTRAL | November | -Responded LoLo post-inj total 1. Upon arrival, post-inj total analyzer reading=0.00mg/L - post-inj total analyzer is not a reportable analyzer 2. Noticed analyzer was running out of reagetns 3. Changed reagents & primed it 4. Verified analyzer: grab=2.14mg/L analyzer=2.22mg/L | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2025-11-06
CENTRAL | November | On-site for pumping station/rechlor station check and Cl2 cylinder change. Changed Cl2 bank B with Jerry Zhang. Replaced yellow chemscan analyzer reagent and adjusted offsets for Pre/Post FA/TA/Mono/Total Cl to better represent grab samples. Grab/CL17 analyzer results as follows (mg/L): Pre-Injection: Free Cl (12:53): G: 0.07 A: 0.07 Total Cl (12:54): G: 2.32 A: 2.26 Post-Injection: Free Cl (13:03): G: 0.06 A: 0.06 Total Cl (13:05): G: 2.36 A: 2.29 Z3: Free Cl (13:07): G: 0.06 A: 0.05 Total Cl (13:10): G: 2.30 A: 2.22 Checked station and equipment, no new issues found, monitored chemscan analyzer following reagent/offset change, appears to be operating normally, post FA grab at 14:30 0.5mg/L. | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2025-11-07
CENTRAL | November | Station and equipment checked, no issues found Changed pre injection analyzer reagents Chemical systems and levels inspected Verified analyzers, all readings and grabs entered into PWQ sheet | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2025-11-03
CENTRAL | November | Onsite for a station and equipment check, no issues found Topped up ammonia tank 1 Verified all analyzers, all readings and grabs entered into PWQ sheet. Took weekly bacti sample along with fluoride testing (WO#11347952) | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2025-11-05
CENTRAL | November | On-site to adjust metro flow control valve pilots. Backed them out 6 full turns and set lock nuts. Will monitor if further adjustment required | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2025-11-20
CENTRAL | November | Onsite for station check: Replaced outlet free CL17 reagents * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Chemscan reagents- Ok Station/equipment- Ok | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2025-11-24
CENTRAL | November | On-site for a station and equipment check, no issues found Changed both reagents in both the free and total Zone 3 analyzers Changed Potassium iodide (grey) in Chemscan unit Verified analyzers, entere all readings and grabs into PWQ sheet Weekly bacti sample taken. | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2025-11-19
CENTRAL | November | On-site for a station and equipment check, no issues found Weekly bacti sample taken while draining Operational sample taken Verified analyzers, adjusted pre free ammonia to 0.09 from 0.04 based on a sl1000 grab of 0.07mg/L Entered all readings and grabs into PWQ sheet | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2025-11-26
CENTRAL | November | On site to complete station check. - Entered data into PD Sheet - Trends all good - Equipment all good - Dosages all good - Reagents all good - No new issues found Pre- Injection Free Cl grab @ 9:28am G: 0.08mg/L A: 0.04mg/L Total Cl grab @ 9:28am G: 1.65mg/L A: 1.68mg/L Post Injection Free Cl grab @ 9:30am G: 0.09mg/L A: 0.07mg/L Total Cl grab @ 9:30am G: 2.72mg/L A: 2.71mg/L Zone 3 Free Cl grab @ 9:35am G: 0.04mg/L A: 0.04mg/L Total Cl grab @ 9:35am G: 2.22mg/L A: 2.23mg/L Res Outlet Free Cl grab @ 9:38am G: 0.04mg/L A: 0.04mg/L Total Cl grab @ 9:38am G: 2.20mg/L A: 2.23mg/L | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2025-11-28
CENTRAL | November | on-site for a station and equipment check, no issues found Chemical levels and systems ok Changed reagets in both post free and pre total analyzers Verified analyzers, entered all readings and grabs into PWQ sheet general house keeping | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2025-11-21
CENTRAL | November | On-site for various WO?s., notified ROC All cl17-sc analyers cleaned and put back online Unable to trigger CL2 alarm using two different methods. WO created Chemical injection visual inspections completed. JHSC inspection completed | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2025-11-13
CENTRAL | November | On-site for various work orders. General housekeeping completed Generator run under load from 1044 to 1142 Fuel start 2360.91. End 2351.92 Battery @ 28 Volts @345 Hertz @60.0 Oil pressure @ 82psi Temp @ 180 Chemscan maintenance completed CL 17 analyzer maintenance completed with the exception of Res Outlet free as unable to scroll through menu options. Work order created Ammonia system inspection completed including spill containment alarm test. Tried to complete cl2 leak test. Unable to trigger Will try a different puffer tomorrow | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2025-11-11
CENTRAL | November | On-site for a station and equipment check, no issues found C Smith, ROC, caught post total flatlined on SCADA at 2.64mg/L. I put the unit into cleaning mode, cleaned unit and then exited the mode. Unit began to trend thereafter. Verified analyzers, all readings and grabs were entered into PWQ sheet Chemical levels and systems ok. | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2025-11-14
CENTRAL | November | Attending site for 2 issues - AUPSRR_RES_RSR1_AIT1 chlorine analyzer has non-functioning menu push-buttons (W11436029) and chlorine room gas leak detector failed monthly bump test (W11443557). Replaced all push-button in chlorine analyzer. Also, replaced non-responsive chlorine leak detector and calibrated. SCADA Calibration mode was used for both devices to reduce the number of alarms. ROC was notified before and after maintenance work. | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2025-11-14
CENTRAL | November | Station and equipment check, no issues found Verified analyzers Chemical levels and systems ok Verified analyzers and entered all readings and grabs into PWQ sheet Chemically cleaned chemscan unit JHSC inspection completed Weekly bacti and operational samples taken. | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2025-11-12
CENTRAL | November | On-site for station and equipment check, no issues found. Topped ammonia tank day tank 2 Toopwd up DI and muiratic acid mix on Chemscan unit. Chemical level and systems ok Verified analyzers, entered all readings and grabs into PWQ sheet | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2025-11-17
CENTRAL | November | -Performed station check - logged station readings into PWQ sheet -Checked CL17 reagents - OK -Collected iron sample | Aurora Well 5 | 2025-11-07
CENTRAL | November | -Performed station check - logged station readings into PWQ sheet -Checked CL17 reagents - OK -Performed silicate pump 2 drawdown -Decreased Cl:N ratio from 4.0 to 3.9 due to low FA -Collected in-house water quality samples | Aurora Well 5 | 2025-11-10
CENTRAL | November | -Changed chlorine cylinder -Performed statin check - logged station readings into PWQ sheet Grab: treated total=2.74mg/L free=0.18mg/L influent free=2.60mg/L effluent free=2.44mg/L Analyzer: treated total=2.82mg/L free=0.13mg/L influent free=2.70mg/L effluent free=2.35mg/L -Changed effluent free reagents -Collected weekly BacT samples YD #W11348542 -Collected in-house iron sample | Aurora Well 5 | 2025-11-05
CENTRAL | November | On-site for station check, in-house operational sampling and quarterly raw water pH monitoring. Raw water pH grab 8.11. Entered station readings into shared PD excel file. Collected in-house operational sample. Grab/analyzer readings as follows (mg/L): Influent Free Cl (08:48): G: 2.60 A: 2.66 Effluent Free Cl (08:50): G: 2.30 A: 2.32 Treated Free Cl (08:52): G: 0.10 A: 0.12 Treated Total Cl (08:53): G: 2.86 A: 2.78 No new issues found while on-site. | Aurora Well 5 | 2025-11-03
CENTRAL | November | Change motor | Aurora Well 5 | 2025-11-20
CENTRAL | November | Install new motor, check rotation and run Shut off and adjust top nut run for thirty minutes Minor noise in motor | Aurora Well 5 | 2025-11-27
CENTRAL | November | Run well 5 with motor uncoupled from well Slight shimmy in the top bearing and wining noise. Reconnect motor had Ben Hess run well in manual. Whining noise increased a little and shimmy still present, recommend replacing motor in the near future | Aurora Well 5 | 2025-11-24
CENTRAL | November | Returned W5 to auto as turbidity has returned to normal operating range. Informed ROC. | Aurora Well 5 | 2025-11-28
CENTRAL | November | Returned W5 to auto, shutdown as duty not called for, trends ok. | Aurora Well 5 | 2025-11-21
CENTRAL | November | On-site with Jason Garnett for Cl2 system overhaul WO. Isolated Cl2 cylinders and purged chlorine system (Well 5 local/off). Isolated site from distribution and pulled NaSi injection points to replace grip rings, re-installed injection points. Replaced chlorine lines, regulators and ejectors. Tested system and checked for leaks. Backflushed main with dechlorination measures in place following overhaul. Returned site to normal operation. Started W5 in remote/man to observe operation of cl2 train 1. W5 locked out on lolo Influent Free Cl at 12:28 (analyzer read 0.43mg/L for one reading and then returned to normal operating range), took grab as follows: 12:32 Influent Free Cl G: 2.50 A: 2.58 Analyzer received incorrect reading, train 1 ok. Reset lolo Influent lock out and started W5 in remote/man again to observe train 2. Site appears to be running normally, will return W5 to remote/auto later today remotely. Informed ROC. | Aurora Well 5 | 2025-11-25
CENTRAL | November | On site with Dan Boate, Tyler Smith and Chris Iliohan to replace Well #5 pump motor. Well motor locked out. Operations notified. Replacement motor frame incompatible. Well motor remains locked out. | Aurora Well 5 | 2025-11-26
CENTRAL | November | -Performed station check - logged station readings into PWQ sheet -Collected in-house water quality sample -Changed treated free reagents -Cleaned silicate injection point #1 | Aurora Well 5 | 2025-11-27
CENTRAL | November | -Put injector 2 back -Changed chlorine cylinder -Finished the following work orders *CL17 analyzer maintenance *Turbidimeter maintenance *Chlorine leak test *Chemical system inspection *Exhaust fan/ damp check *Deep well exhaust valve inspection *H&S inspection | Aurora Well 5 | 2025-11-20
CENTRAL | November | Returned W5 to remote/auto, duty 2 active, trends appear normal. | Aurora Well 5 | 2025-11-25
CENTRAL | November | On-site for a station and equipment check Found CL2 injector leaking at compression nut. Created WO W11465712 To address Chemical levels and systems ok Verified analyzers and entered into PWQ sheet | Aurora Well 5 | 2025-11-24
CENTRAL | November | On-site for station check and CMU5 W11475625 AUW57 Turbidity issues. Found NaSi pumps air locked. Primed pumps and checked max flow/PSV/PRV settings. Backflushed main with dechlorination measures in place to remove excess NaSi from main. Grab/analyzer results as follows (mg/L): Influent Free Cl (09:59): G: 2.17 A: 2.10 Effluent Free Cl (10:00): G: 0.09 A: 0.10 Treated Free Cl (10:02): G: 0.04 A: 0.06 Treated Total Cl (10:03): G: 2.56 A: 2.52 Topped up oil pot for W5 and started W5 in remote/man to observe operation. Turbidity increase to high level alarm from previous run cycle, but is returning to normal operating range. Will continue to monitor remotely and return W5 to auto remotely once turbidity high alarm is cleared. Observed minor noise from W5 as noted in previous elog entry by Lee F following motor swap, will continue to monitor. No other new issues found while on-site. | Aurora Well 5 | 2025-11-28
CENTRAL | November | Reviewed trends from lolo Influent lock out at 00:30 last night, residuals rebounded shortly after Well shutdown. Rotated back to cl2 booster pump 2 and started W5 in remote/man and am remotely monitoring status. | Aurora Well 5 | 2025-11-21
CENTRAL | November | Placed W5 man/off after consulting with team lead about high pitched noise noted earlier. Created WO for CMS to investigate next week. | Aurora Well 5 | 2025-11-21
CENTRAL | November | On site to complete station check to collect weekly bacti samples W11403047. Electricians and mechanical on site to fix noise with the well. - Well duty inactive on arrival - Entered data into Process data sheet & collected samples - Dosage all good - Reagents all ok - Trends all good - Equipments all ok - NaSi P1 OOS - No new issues found Influent free Cl @ 9:41am G: 2.62mg/L A: 2.65mg/L Effluent free Cl @ 9:40am G: 2.20mg/L A: 2.26mg/L Treated free Cl @ 9:38am G: 0.16mg/L A: 0.12mg/L Treated total Cl@ 9:38am G: 2.68mg/L A: 2.71mg/L | Aurora Well 5 | 2025-11-26
CENTRAL | November | -Performed station check - logged station readings into PWQ sheet Grab: treated total=2.78mg/L free=0.19mg/L@10:00 Influent free=2.68mg/L effluent free=2.44mg/L Analzyer: treated total=2.76mg/L free=0.12mg/L Influent free=2.73mg/L effluent free=2.34mg/L -Checked CL17 reagents - OK -Collected weekly BacT sample YD #W11387379 and in-house iron samples -Cleaned silicate injection points due to low dosage - when put silicate injector back, one of the fitting cross-threaded - put silicate pump 2 OOS, I will change the fitting tomorrow | Aurora Well 5 | 2025-11-19
CENTRAL | November | On-site for station check with Divya Patel. Entered station readings into shared PD excel file. Grab/analyzer results as follows (mg/L): Influent Free Cl (13:46): G: 2.72 A: 2.72 Effluent Free Cl (13:47): G: 2.42 A: 2.33 Treated Free Cl (13:49): G: 0.09 A: 0.12 Treated Total Cl (13:50): G: 2.70 A: 2.75 Turned on unit heater in NaSi/Cl2 room. Noticed that W5 seems to be making high pitched noise while running, unsure if normal, took video and will consult team lead and will create follow up WO for CMS to investigate if necessary. No other new issues found while on-site, site in auto. | Aurora Well 5 | 2025-11-21
CENTRAL | November | -Collected iron samples | Aurora Well 5 | 2025-11-13
CENTRAL | November | -Performed station check - logged station readings into PWQ sheet Grab: treated total=2.74mg/L free=0.20mh/L@12:45 influent free=2.68mg/L effluent free=2.36mh/L Analyzer: treated total=2.84mg/L free=0.13mg/L influent free=2.70mg/L effluent free=2.37mg/L -Checked CL17 reagents - OK -Collected weekly BacT sample YD #W11368818 & in-house water quality samples | Aurora Well 5 | 2025-11-12
CENTRAL | November | -Performed station check - logged station readings into PWQ sheet -Checked CL17 reagents - OK -Collected in-house water quality samples | Aurora Well 5 | 2025-11-17
CENTRAL | November | On-site for station check. Replaced Influent Free Cl CL17 analyzer reagents. Entered station readings into shared PD excel file. Grab/analyzer results as follows (mg/L): Influent Free Cl (09:34): G: 2.32 A: 2.23 Effluent Free Cl (09:40): G: 0.06 A: 0.10 Treated Free Cl (09:41): G: 0.05 A: 0.06 Treated Total Cl (09:42): G: 2.48 A: 2.45 No new issues found while on-site. | Aurora Well 5 | 2025-11-14
CENTRAL | November | -Performed station check | Aurora Well 6 | 2025-11-10
CENTRAL | November | On-site for station check, JHSC inspection and general housekeeping work orders. No new issues found while on-site. Site remains offline. | Aurora Well 6 | 2025-11-03
CENTRAL | November | Site offline. Perimeter and facility checked. No issues found | Aurora Well 6 | 2025-11-24
CENTRAL | November | -Performed station check | Aurora Well 6 | 2025-11-17
CENTRAL | November | -Reset hi/lo temp alarm - wrong settings | Aurora Well 6 | 2025-11-13
CENTRAL | November | -Performed statin check - logged station readings into PWQ sheet Grab: treated total=3.02mg/L free=0.17mg/L influent free=2.62mg/L effluent free=2.52mg/L Analyzer: treated total=3.02mg/L free=0.13mg/L influent free=2.52mg/L effluent free=2.50mg/L -Changed effluent free reagents -Collected weekly BacT samples YD #W11348542 -Collected in-house iron sample -Finished the following work orders *Tested Chlorine leak alarm *Performed CL17 analyzer maintenance | Aurora Wells 1-4 Water Treatment Plant | 2025-11-05
CENTRAL | November | -Performed station check - logged station readings into PWQ sheet -Changed treated free reagents - OK -Collected in-house iron sample | Aurora Wells 1-4 Water Treatment Plant | 2025-11-07
CENTRAL | November | Oversaw/assisted Total Power technician performed Annual Generator Load Test and PM. | Aurora Wells 1-4 Water Treatment Plant | 2025-11-06
CENTRAL | November | In to transfer silicate load to truck. No issues. Used transfer P2, isolation valve and camlock cover returned to closed. Silicate hose emptied into tank, camlock soaking in water bin. | Aurora Wells 1-4 Water Treatment Plant | 2025-11-07
CENTRAL | November | Fill up silicate truck. Discharge line isolation to fill port, si transfer p2 returned to normal position (closed, off). Flushed si hose with warm water. | Aurora Wells 1-4 Water Treatment Plant | 2025-11-10
CENTRAL | November | -Performed station check - logged station readings into PWQ sheet -Checked CL17 reagents - OK -Decreased Cl:N ratio from 3.9 to 3.8 due to low FA -Collected in-house water quality samples | Aurora Wells 1-4 Water Treatment Plant | 2025-11-10
CENTRAL | November | -Finished the following work orders *Air valve inspection *Chemical system inspection | Aurora Wells 1-4 Water Treatment Plant | 2025-11-04
CENTRAL | November | On-site for station check, in-house operational sampling and quarterly raw water pH monitoring. Changed Cl2 bank A with Will Mather. Batched ammonia tank 1 and topped up NaSi day tanks. Ran Wells 2/3 in remote/man and switched to run W1/4 in remote/man for raw water pH grabs. Raw water pH grabs as follows: W1: 8.11 W2: 8.10 W3: 8.06 W4: 8.09 Activated duty 1 and returned Wells to auto, W1 shutdown and then restarted, received waste flow fault alarm when restarted, will monitor. Entered station readings into shared PD excel file. Collected in-house operational sample. Grab/analyzer readings as follows (mg/L): Influent Free Cl (11:07): G: 2.66 A: 2.59 Effluent Free Cl (11:08): G: 2.46 A: 2.48 Treated Free Cl (11:10): G: 0.08 A: 0.12 Treated Total Cl (11:10): G: 2.94 A: 3.00 Found W3 waste motorized valve passing slightly, will follow up with CMS as valve was replaced earlier this year. No other new issues found while on-site. | Aurora Wells 1-4 Water Treatment Plant | 2025-11-03
CENTRAL | November | Adjusted silicate dose from 18 mg/L to 17 mg/L, this is to bring closer to our bench testing in 2016/2017 We will do dissolved iron samples to monitor the change | Aurora Wells 1-4 Water Treatment Plant | 2025-11-03
CENTRAL | November | -Performed station check - logged station readings into PWQ sheet -Checked CL17 reagents - OK | Aurora Wells 1-4 Water Treatment Plant | 2025-11-24
CENTRAL | November | Onsite to throttle down Aurora Well #1 discharge valve until flow at 15 L/s in preparation for tomorrow?s step test- Once 15 L/s flow reached, placed well #1 in man/off (09:20). Informed ROC | Aurora Wells 1-4 Water Treatment Plant | 2025-11-24
CENTRAL | November | On site to top up silicate truck for NM well 13/16. No issues found | Aurora Wells 1-4 Water Treatment Plant | 2025-11-25
CENTRAL | November | On site to top up silicate truck for nobleton sites. 09:26- Before:1.06cm/1.07cm,After:1.01cm/1.03cm 12:17- Before:1.01cm/1.03cm,After:0.97cm/0.99cm | Aurora Wells 1-4 Water Treatment Plant | 2025-11-20
CENTRAL | November | -Performed station check - logged station readings into PWQ sheet Grab: treated total=3.10mg/L free=0.18mg/L@12:50 Influent free=2.62mg/L effluent free=2.54mg/L Analzyer: treated total=3.06mg/L free=0.12mg/L Influent free=2.58mg/L effluent free=2.58mg/L -Checked CL17 reagents - OK -Collected weekly BacT sample YD #W11387379, DWSP samples, and in-house iron samples | Aurora Wells 1-4 Water Treatment Plant | 2025-11-19
CENTRAL | November | On site to complete station check & to collect weekly bacti samples W11403047 - Entered data into Process Data Sheet & collected samples - Reagents all good - Trends all good - Equipment all okay - Dosage all good - No new issues found Influent free Cl @ 10:28am G: 2.68mg/L A: 2.60mg/L Effluent free Cl @ 10:31am G: 2.56mg/L A: 2.56mg/L Treated free Cl @ 10:33am G: 0.12mg/L A: 0.13mg/L Treated total Cl@ 10:33am G: 3.02mg/L A: 3.07mg/L | Aurora Wells 1-4 Water Treatment Plant | 2025-11-26
CENTRAL | November | -Performed step test for W1 -Finished the following work orders *Performed H&S inspection *Diesel gen set test run Pre-run inspection - good Hour Start 87.00 Stop 87.00 Fuel Start 7218L Stop 7284L Generator operating stats while under load (P1 and P4): RPM- 1800 Oil pressure-78 Oil temp- 189 F Coolant temp- 179 F Fuel pressure- 102psi Fuel temp- 89F Frequency- 60 Hz Voltage- 603 V Amperage- 165A Once test run completed, placed generator back into auto as per normal operations- informed ROC * -Changed chlorine cylinders | Aurora Wells 1-4 Water Treatment Plant | 2025-11-25
CENTRAL | November | On site to complete cylinder change with Donald M. No issues found | Aurora Wells 1-4 Water Treatment Plant | 2025-11-27
CENTRAL | November | On-site with Divya Patel for station check. Divya batched ammonia tank 1 and completed raw building station check. Topped up NaSi day tanks and entered station readings into shared PD excel file. Grab/analyzer results as follows (mg/L): Influent Free Cl (12:33): G: 2.60 A: 2.66 Effluent Free Cl (12:35): G: 2.58 A: 2.51 Treated Free Cl (12:36): G: 0.10 A: 0.13 Treated Total Cl (12:42): G: 3.04 A: 3.09 Adjusted Cl:AMM ratio from 3.8 to 3.7 based on Treated water FA grab of 0.01mg/L, new FA grab 0.02mg/L, will monitor. Adjusted unit heater up in Cl2 booster room. No new issues found. | Aurora Wells 1-4 Water Treatment Plant | 2025-11-21
CENTRAL | November | Topped up silicate day tanks and place wells 1/4 manual on as INST working on OHRES LIT annual calibration. No other issues found | Aurora Wells 1-4 Water Treatment Plant | 2025-11-26
CENTRAL | November | -Performed station check - logged station readings into PWQ sheet -Changed effluent free reagents -Collected in-house water quality sample | Aurora Wells 1-4 Water Treatment Plant | 2025-11-27
CENTRAL | November | On-site for station check. Entered station readings into shared PD excel file. Topped up NaSi day tanks. Grab/analyzer results as follows (mg/L): Influent Free Cl (08:08): G: 2.54 A: 2.47 Effluent Free Cl (08:09): G: 1.52 A: 1.47 Treated Free Cl (08:10): G: 0.07 A: 0.07 Treated Total Cl (08:11): G: 2.62 A: 2.63 Checked station and equipment, topped up W3 oil pot. No new issues found while on-site. | Aurora Wells 1-4 Water Treatment Plant | 2025-11-28
CENTRAL | November | On site to top up silicate truck for NM wells | Aurora Wells 1-4 Water Treatment Plant | 2025-11-25
CENTRAL | November | On site to top up silicate truck for MA wells1/2 | Aurora Wells 1-4 Water Treatment Plant | 2025-11-25
CENTRAL | November | -Performed station check - logged station readings into PWQ sheet Grab: treated total=2.98mg/L free=0.16mg/L@12:15 influent free=2.54mg/L effluent free=2.42mg/L Analyzer: treated total=3.03mg/L free=0.13mg/L influent free=2.56mg/L effluent free=2.48mg/L -Checked CL17 reagents - OK -Collected weekly BacT sample YD #W11368818 & in-house water quality samples | Aurora Wells 1-4 Water Treatment Plant | 2025-11-12
CENTRAL | November | On site to take silicate for delivery. While completing job flange busted, had to isolate silicate pump 2. Informed Central team lead of issue and also issued a work order for it to be repaired. | Aurora Wells 1-4 Water Treatment Plant | 2025-11-13
CENTRAL | November | -Changed chlorine cylinders | Aurora Wells 1-4 Water Treatment Plant | 2025-11-11
CENTRAL | November | -Finished the following work orders *Rotork inspection *Pump & motor inspection *Turbidimeter maintenance -Collected iron sample | Aurora Wells 1-4 Water Treatment Plant | 2025-11-13
CENTRAL | November | -Performed station check - logged station readings into PWQ sheet -Changed influent free reagents | Aurora Wells 1-4 Water Treatment Plant | 2025-11-17
CENTRAL | November | On-site for station check. Entered station readings into shared PD excel file. Grab/analyzer results as follows (mg/L): Influent Free Cl (10:38): G: 2.70 A: 2.62 Effluent Free Cl (11:01): G: 2.58 A: 2.50 (adjusted to 2.58 based on average of 3 grabs) Treated Free Cl (10:45): G: 0.10 A: 0.12 Treated Total Cl (10:45): G: 2.92 A: 3.01 Adjusted Cl:AMM ratio from 3.9 to 3.8 based on FA grab of 0.01mg/L, new FA grab of 0.03mg/L, will monitor. Created follow up WO to investigate/service waste valve for W1 for intermittent waste flow fault issues. No other new issues found while on-site. | Aurora Wells 1-4 Water Treatment Plant | 2025-11-14
CENTRAL | November | Attending site to check well 1 waste flowmeter (W11445935). Flowmeter was not showing flow during flow condition. Re-programmed empty pipe detection parameter. Flowmeter appears to be functioning correctly now. Will monitor for several days before closing work order. ROC was notified before and after maintenance work was performed. | Aurora Wells 1-4 Water Treatment Plant | 2025-11-18
CENTRAL | November | On site to top up silicate truck for new market wells. 09:11AM- before- 1.18 m, after 1.14 m 11:05 AM- before- 1.14 m, after 1.08 m 13:12 AM - before- 1.08 m , after 1.07 m | Aurora Wells 1-4 Water Treatment Plant | 2025-11-18
CENTRAL | November | -Performed step test for W3 with L. Paterson & J. Moore - 20L/s, 40L/s, and 60L/s -Troubleshooting W1 waste flow fault alarm with E. Simanovskis - changed setting on flow meter | Aurora Wells 1-4 Water Treatment Plant | 2025-11-18
CENTRAL | November | Cylinder change with J Zhang | Aurora Wells 1-4 Water Treatment Plant | 2025-11-17
EAST | November | Vibration testing | Bayview Pumping Station | 2025-11-06
EAST | November | On site for station check Verified chlorine analyzers, 14:50, in mg/L Free Cl - G 0.11; A 0.04 Total Cl - G 1.57; A 1.63 Recorded observations in the shared PWQ sheet Reverse flow totalizer reading incorrectly with a false 10,000,000 M3 output. Will liaise with the Instrumentation team to investigate - informed Danielle Mollicone and ORO. Station and equipment okay. | Bayview Pumping Station | 2025-11-10
EAST | November | Attended site for station check. Station and equipment okay | Bayview Pumping Station | 2025-11-07
EAST | November | Onsite to respond to FCL hi alarm. Arrived site, cleaned analyzer sample bowl and probe. Did zero calculation on analyzer, and returned to service. Analyzer reading TCL = 1.73 mg/l, FCL = 0.08 mg/l. 1610 hrs: Did grabs: TCL = 1.71 mg/l FCL = 0.03 mg/l. Notified ROC before leaving site. | Bayview Pumping Station | 2025-11-01
EAST | November | On site to complete station check. No outstanding alarms on site. No OOS equipment. Switched pump duties pump 2 and 4 are duty 1 and pumps 1 and 3 are duties 2 and 3 respectively. Time: 12:50 Grab (mg/l) Analyzer (mg/l) Free: 0.07 0.02 Total: 1.59 1.65 Verified analyzer with grabs. Checked site and trends. | Bayview Pumping Station | 2025-11-03
EAST | November | On site for electrical team training of generator load bank transfer scheme. Also performed short generator station transfer test. | Bayview Pumping Station | 2025-11-05
EAST | November | On site for station check Completed Surge valve exercise and inspection Flood alarm test Informed RO Carter Dunn of the work performed Verified chlorine analyzers, 9:15, in mg/L Free Cl - G 0.04; A 0.04 Total Cl - G 1.39; A 1.44 Recorded observations in the shared PWQ sheet Station and equipment okay | Bayview Pumping Station | 2025-11-28
EAST | November | On site for deep cleaning Free and total chlorine analyzer powered off due to a power interruption of the GFI receptacle. Station was off at the time, was not directing flow to users. Verified free and total chlorine analyzers Grabs @ 13:04 hrs. FCl: 0.04 mg/L TCl: 1.37 mg/L Analyzer: FCl: 0.04 mg/L TCl: 1.41 mg/L | Bayview Pumping Station | 2025-11-27
EAST | November | On site for station check Verified chlorine analyzers, 10:00, in mg/L Free Cl - G 0.06; A 0.03 Total Cl - G 1.53; A 1.53 Inspected equipment, reviewed trends Station and equipment okay | Bayview Pumping Station | 2025-11-21
EAST | November | On site for station check Recorded observations in the shared PWQ sheet Station and equipment okay | Bayview Pumping Station | 2025-11-17
EAST | November | On site for station check. Reviewed scada, duty not active. Cell level @ 71 and 70% Visual inspection in and around station Verification of equipment and instrumentation. Outstanding alarm: None Verified chlorine analyzers readings. Chlorine residual @ 13:25 hrs Grab: FCL= 0.08 mg/L TCL = 1.62 mg/L Analyzer: FCL 0.03 mg/L TCL= 1.60 mg/L Station OK, Recorded station readings into PWQ data sheet | Bayview Pumping Station | 2025-11-14
EAST | November | On site for preventative maintenance work orders Completed Dehumidifier cleaning and inspection Ventilation system inspection Centrifugal pump 1 inspection Centrifugal pump 2 inspection Centrifugal pump 3 inspection Centrifugal pump 4 inspection Chlorine analyzer maintenance Sump pump maintenance JHSC inspection Diesel generator test run Completed diesel generator pre inspection prior to test - all okay Diesel generator hours Start 113.3 Stop 114.5 Diesel fuel Start 3029/3074 L Stop 2888/2951 L Performed diesel generator test on load, pumps 2 and 3 Generator run statistics, loaded: Coolant temperature 86C Oil pressure 460 kPa Engine speed 1802 RPM Battery voltage 27.6V Oil temperature 97C Pyrometer (exhaust) temperature 588C Fuel pressure 500 kPa SCR system fault alarm latched during generator test run - ongoing, known, deficiency Dmitri (Capital) attended site to inspect generator exhaust leak - noted contractor repair insufficient and remains a deficiency Station back in auto - station and equipment okay | Bayview Pumping Station | 2025-11-13
WEST | November | On site to complete station check. Free chlorine Grab: 0.02mg/L Analyzer: 0.00mg/L Total chlorine Grab: 1.92mg/L Analyzer 1.95mg/L Reagents - all ok | East Vaughan Teston Pumping Station | 2025-11-07
WEST | November | On site to complete station check. Free chlorine Grab: 0.02mg/L Analyzer: 0.00mg/L Total chlorine Grab: 1.95mg/L Analyzer 1.96mg/L Reagents - all ok | East Vaughan Teston Pumping Station | 2025-11-10
WEST | November | On site to complete station check. Free chlorine Grab: 0.02mg/L Analyzer: 0.00mg/L Total chlorine Grab: 1.80mg/L Analyzer 1.86mg/L Reagents - topped up acetate | East Vaughan Teston Pumping Station | 2025-11-03
WEST | November | Vibration testing Tested all 8 pumps | East Vaughan Teston Pumping Station | 2025-11-05
WEST | November | On site to complete station check. Free chlorine Grab: 0.04mg/L Analyzer: 0.00mg/L Total chlorine Grab: 1.89mg/L Analyzer 1.95mg/L Reagents - all ok Flushed sanitary pit | East Vaughan Teston Pumping Station | 2025-11-20
WEST | November | On site to complete station check. Free chlorine Grab: 0.02mg/L Analyzer: 0.00mg/L Total chlorine Grab: 1.90mg/L Analyzer 1.96mg/L Reagents - all ok | East Vaughan Teston Pumping Station | 2025-11-28
WEST | November | On site for the following VNPS, 00082017) Charlatte Surge Tanks, East Vaughan Pumping Station (3M) VNPS, Eye Wash Cleaning & Solution Replacement - East Vaughan PS (6M) VNPSCD, Chlorine Scrubber Maintenance / Media Sampling, East Vaughan Disinfection Building (6M)) VNPS, Comprehensive Housekeeping MAIN FLOOR - WEST (1M) VNPSCD Comprehensive Housekeeping CHEMICAL DISINFECTION BLDG - WEST (1M) VNPS, Comprehensive Housekeeping LOWER LEVEL - WEST (1M) No issues on site | East Vaughan Teston Pumping Station | 2025-11-27
WEST | November | Remote response to post injection Hihi combined chlorine. Chlorine readings went Hihi on post injection analyzers after the reservoir stopped filling and the chlorine system was shutting itself down. There was no flow at the time of the Hihi alarm. The alarm is non-reportable as the post injection is going into the reservoir and not directed to users. There is another analyzer at the end of the reservoirs that would be reportable. To clear the alarms I put the chemical system in manual then started a pump at Bayview PS to start filling the reservoir. Alarms all clear, chemical system back to auto. | East Vaughan Teston Pumping Station | 2025-11-24
WEST | November | On site to complete station check. Free chlorine Grab: 0.04mg/L Analyzer: 0.00mg/L Total chlorine Grab: 1.89mg/L Analyzer 1.92mg/L Reagents - all ok | East Vaughan Teston Pumping Station | 2025-11-24
WEST | November | On site to complete station check. Free chlorine Grab: 0.04mg/L Analyzer: 0.00mg/L Total chlorine Grab: 1.88mg/L Analyzer 1.89mg/L Reagents - all ok | East Vaughan Teston Pumping Station | 2025-11-17
WEST | November | On site to complete station check. Free chlorine Grab: 0.02mg/L Analyzer: 0.00mg/L Total chlorine Grab: 1.91mg/L Analyzer 1.94mg/L Reagents - all ok | East Vaughan Teston Pumping Station | 2025-11-14
WEST | November | Onsite to complete station check Site remains off line. | Holland Landing East Elevated Tank | 2025-11-10
WEST | November | In to complete PMs. Notified ROC of related alarms (site power failure, low temp, flood alarm). Completed chamber inspection with Joe Williams. Completed generator test run, confirmed site power failure alarm triggered and generated cleared alarm. Completed JHSC, low temp alarm PMs. No issues. | Holland Landing East Elevated Tank | 2025-11-18
WEST | November | On site for station check. 12:40-Took grab samples: Free: 0.04 mg/L Total: 1.08 mg/L Entered values in PWQ sheet Equipment okay | Holland Landing Sherwood Pumping Station | 2025-11-07
WEST | November | On site for station check. 11:21-Took grab samples: Free: 0.03 mg/L Total: 0.80 mg/L Entered values in PWQ sheet Equipment okay | Holland Landing Sherwood Pumping Station | 2025-11-10
WEST | November | On site for station check. Took grab samples: Free: 0.03 mg/L Total: 1.01 mg/L No issues. | Holland Landing Sherwood Pumping Station | 2025-11-03
WEST | November | Onsite for station check Checked residuals mg/L @1345 Total grab 1.00 Free grab 0.03 | Holland Landing Sherwood Pumping Station | 2025-11-24
WEST | November | On site for station check. Check trends: All okay. 09:57-Took grab Free: 0.02 mg/L Total: 1.46 mg/L Entered values in PWQ sheet Equipment okay | Holland Landing Sherwood Pumping Station | 2025-11-21
WEST | November | On site for station check. Check trends: All okay. 12:00-Took grab Free: 0.04 mg/L Total: 1.25 mg/L Entered values in PWQ sheet Equipment okay | Holland Landing Sherwood Pumping Station | 2025-11-28
WEST | November | Onsite for Scheduled PM workorders. Informed ROC about the works being done. W11388793 HLPSYS, JHSC Health and Safety Inspection W11389111 HLPSYS, Low Temperature Alarm, Test W11389323 HLPSYS, Header Discharge Valve, Exercise W11389389 HLPSYS, Header Suction Valve, Exercise W11388384 HLPSYS, Diesel Generator Test Run Pre check Battery okay- 13 V Coolant- Okay Oil - Okay Before Start Start time- 10:34 Run time- 1426.5 hr Fuel level-696L/85.6cm Pumps 1,2,3 running auto according to duty. After Stop Stop time- 11:35 Run time- 1427.6 hr Fuel level-690L/85 cm Generator exhaust leaking, which makes the room foggy. CMU created W11435877 | Holland Landing Sherwood Pumping Station | 2025-11-11
WEST | November | On site for station check. Check trends: All okay. 12:55-Took grab Free: 0.08 mg/L Total: 1.92 mg/L Entered values in PWQ sheet Equipment okay | Holland Landing Sherwood Pumping Station | 2025-11-14
WEST | November | On site for station check. Check trends: All okay. Contractors on site for roof work Entered values in PWQ sheet | Holland Landing Sherwood Pumping Station | 2025-11-17
WEST | November | On site for station check. Verified Analyzers 12:20-Treated Free Grab- 0.13mg/L, Analyzer -0.19 mg/L 12:20-Treated Total Grab- 3.60 mg/L (3.64,3,60,3.57), Analyzer -3.33 mg/L Adjusted analyzer up to 3.50 12:40-Influent Free Grab- 3.24 mg/L, Analyzer -3.16 mg/L 12:45-effluent Free Grab- 2.74mg/L, Analyzer -2.57 mg/L Couldn't effluent free analyzer adjust because arrow key not working. Changed Silicate pump 1,2 max flow from 0.7 to 0.8 mL/min based on Dosing. entered values in pwq sheet. Equipment okay | Holland Landing Well No. 1 | 2025-11-10
WEST | November | Top up silicate tanks. | Holland Landing Well No. 1 | 2025-11-10
WEST | November | Onsite for scheduled PM work orders. Informed ROC about the works being done. Topped up Ammonia Tank 1- 26.42 cm/89.6 cm Completed the following work orders W11350518 HLW1, Chlorine Gas Detector, Test W11352036 HLW1, Turbidity Analyzer TU5300, Maintenance and Calibration W11352772 HLW1, Chemical System Inspection - Chlorine W11353378 HLW1, Chemical System Inspection - Ammonia W11352877 HLW1, Chemical System Inspection - Silicate W11351016 HLW1, JHSC Health and Safety Inspection W11350378 HLW1, Chlorine Scrubber, Check W11351016 HLW1, JHSC Health and Safety Inspection 11352937 HLW1, Cl2 Emergency Repair Kit Inspection W11350661 HLW1, Chlorine Analyzer, Maintenance Verified Analyzers Treated Free Grab- 0.26mg/L, Analyzer -0.19 mg/L Treated Total Grab- 3.40 mg/L, Analyzer -3.32 mg/L Influent Free Grab- 3.10mg/L, Analyzer -3.20 mg/L effluent Free Grab- 2.70mg/L, Analyzer -2.50 mg/L Couldn't adjust because arrow key not working | Holland Landing Well No. 1 | 2025-11-06
WEST | November | On site for station check. Verified Analyzers 13:30-Treated Free Grab- 0.23mg/L, Analyzer -0.20 mg/L 13:30-Treated Total Grab- 3.46 mg/L, Analyzer -3.38 mg/L 13:43-Influent Free Grab- 3.22mg/L, Analyzer -3.27 mg/L 13:45-effluent Free Grab- 2.88mg/L, Analyzer -2.67 mg/L Couldn't effluent free analyzer adjust because arrow key not working. Created CMU workorder for Effluent free CL17 Cl2 analyzer-W11427794 Changed Treated free and total reagents. Switched ammonia pump duty from tank 2 to tank 1. entered values in pwq sheet. Equipment okay | Holland Landing Well No. 1 | 2025-11-07
WEST | November | Informed ROC. Performed annual calibration and put instruments in Cal mode while doing the tasks. Devices done were AITs, NIT, WIT, chlorinators and gas sensors. -Replaced the right side chlorine gas cylinder with a full one. -Changed the electronic board of treated free chlorine analyzer because buttons were not responding. All alarms were cleared after the job. No other issues encountered. | Holland Landing Well No. 1 | 2025-11-04
WEST | November | Informed ROC. Performed annual calibration and put instruments in Cal mode while doing the tasks. Devices done were LITs and PIT. All alarms were cleared after the job. No other issues encountered. | Holland Landing Well No. 1 | 2025-11-03
WEST | November | Onsite for station check Check trends : all okay Well off line 10:45-Verified Analyzers Treated Free Grab- 0.02 mg/L, Analyzer -0.03 mg/L Treated Total Grab- 1.96 mg/L, Analyzer - 1.96 mg/L entered values in PWQ sheet. | Holland Landing Well No. 1 | 2025-11-03
WEST | November | Onsite to change cl2 cylinder Cl2 weight to 53.6 to 119.8 kg | Holland Landing Well No. 1 | 2025-11-28
WEST | November | In to place W1 back in service following passing sample results post rehab and disinfection (W11405010, WW11405009). Primed Cl2 system by running BP1, then BP2 with chlorinators open for short time. Used Backwash Reset button for CT to clear Low influent alarms. Confirmed influent sample water is distribution water: Influent mg/L 0910 A: FCl 0.02 G: FCl 0.10 TCl 1.31 Span calibrate influent Cl17 from 3.42 to 3.30mg/L based on grab. W1 locked out on Turbidimeter fault before CT timer cleared. Tried to reset CT timer but was unable. Restart W1 with CT slider at 39/57m3, W1 may interlock on effluent Lo/Lolo or CT not achieved if distribution sample water is not turned over in time from effluent Cl17 sample line. NTU spike appears to be caused by turning over water in CT tank that has not moved in several weeks (other than draining back to analyzer sample lines). Residuals (mg/L) Effluent 0958 G: FCl 1.64 TCL 2.48 Treated 1110 G: FCl 0.6 TCL 3.38 A; FCl 0.22 tcl 3.20 Unable to adjust effluent Cl17, will issue CMU to INST to replace Cl17 board (enter key not working). Unable to adjust Treated Cl17 FCl lower, at limit of span range. NaSi pump max flow SPs lowered from 80 to 70ml/min until treated NTU is back to normal range. Multiple issues with ammonia dosing: -NH3 p1 max flow matches SP of 105ml/min. -pumps able to maintain treated free residual when run at higher speeds. -swapped to nh3 tank 2 and dosing improved significantly, will have tank 1 pumped out and refilled. -adjust nh3 p2 max flow from 130 to 110ml/min based on fnh3 grabs. Adjust Cl2 nh3 ratio from 4.2 to 4.10 (0.00 nh3 at 4.2, 0.11 nh3 at 4.00). FCV was adjusted from 15 to 24L/s. Initially adjusted during post rehab flushing and sampling, higher flows without system backpressure. Collected weekly BacT and Q4 samples (w11347868, w11247026). Analyzer reagent levels good. Enter data into PWQ. | Holland Landing Well No. 1 | 2025-11-05
WEST | November | HLW1 On site for station check and weekly Bacti Samples W11402705 Check trends: All okay Well running Verified Analyzers 13:00-Treated Free Grab- 0.09mg/L, Analyzer -0.17 mg/L 13:00-Treated Total Grab- 3.30 mg/L, Analyzer -3.34 mg/L Samples Taken. 13:13-Influent Free Grab- 3.10 mg/L, Analyzer -3.07 mg/L 13:07-effluent Free Grab- 2.64 mg/L, Analyzer -2.59 mg/L Reagents all okay entered values in pwq sheet. Equipment okay | Holland Landing Well No. 1 | 2025-11-26
WEST | November | on site for station check. check trends: all okay Well running Topped up Ammonia tank 2- 16.72cm/79.91cm Verified Analyzers 11:33- Influent Free Grab: 2.90mg/L, Analyzer: 2.98mg/L 11:35- Effluent Free Grab: 2.58mg/L, Analyzer: 2.51mg/L 11:20- Treated Free Grab: 0.09mg/L, Analyzer: 0.09mg/L 11:20- Treated Total Grab: 3.26mg/L Analyzer: 3.34mg/L Replaced Effluent free reagents entered values in PWQ sheet. Put well manual off and completed W11390037-silicate chemical system line and injection point flush and then put well back to auto. equipment okay. | Holland Landing Well No. 1 | 2025-11-21
WEST | November | on site for station check. Topped up Silicate Tank check trends: all okay Well running Verified Analyzers 11:20- Influent Free Grab: 2.92mg/L, Analyzer: 2.94mg/L 11:15- Effluent Free Grab: 2.64mg/L, Analyzer: 2.53mg/L 11:10- Treated Free Grab: 0.10mg/L, Analyzer: 0.17mg/L 11:10- Treated Total Grab: 3.28mg/L Analyzer: 3.29mg/L Reagents all good. entered values in PWQ sheet. equipment okay. | Holland Landing Well No. 1 | 2025-11-28
WEST | November | HLW1 On site for station check and weekly Bacti Samples W11386800 Check trends: All okay Well running Verified Analyzers 12:55-Treated Free Grab- 0.15mg/L, Analyzer -0.17 mg/L 12:55-Treated Total Grab- 3.38 mg/L, Analyzer -3.30 mg/L Samples Taken. 13:05-Influent Free Grab- 3.02 mg/L, Analyzer -2.96 mg/L 13:10-effluent Free Grab- 2.60 mg/L (avg 2.62,2.58,2.64), Analyzer -2.36 mg/L adjust effluent free analyzer to 2.50 mg/L. Reagents all okay entered values in pwq sheet. Equipment okay | Holland Landing Well No. 1 | 2025-11-19
WEST | November | Onsite for station check Well running in order to collect operational sample Checked residuals mg/L Influent @1118 Free analyzer 2.95 grab 2.96 Effluent @1119 Free analyzer 2.53 grab 2.50 Treated Total analyzer 3.29 grab 3.28 Free analyzer 0.17 grab 0.11 SL1000 mcl grab 2.65 F nh3 0.07 t nh3 0.65 Received cl2 cylinder delivery 12 received 12 taken | Holland Landing Well No. 1 | 2025-11-24
WEST | November | Attending site for Effluent chlorine analyzer issue (W11427794). Some push buttons were not functioning - replaced all switches. Also noticed that the turbidimeter was reading high. Replaced sample vial basket and calibrated. Reading dropped back to normal. Well was off during maintenance work. ROC was notified before and after maintenance work. | Holland Landing Well No. 1 | 2025-11-13
WEST | November | Decreased influent residual target 3.20 to 3.00 mg/L due to high combined alarm | Holland Landing Well No. 1 | 2025-11-13
WEST | November | Chlorine cylinder change with CW (A side) | Holland Landing Well No. 1 | 2025-11-18
WEST | November | On site for station check Well off Check trends: all okay. Verified Analyzers 11:50-Treated Free Grab- 0.09mg/L, Analyzer -0.06 mg/L 11:50-Treated Total Grab- 2.40 mg/L, Analyzer -2.43 mg/L 12:00-Influent Free Grab- 2.40 mg/L, Analyzer -2.30 mg/L 11:57-effluent Free Grab- 0.12 mg/L, Analyzer -0.08 mg/L entered values in pwq sheet. Equipment okay | Holland Landing Well No. 1 | 2025-11-14
WEST | November | on site for station check. check trends all okay Well running Verified Analyzers 12:35- Influent Free Grab: 2.90mg/L, Analyzer: 3.00mg/L 12:30- Effluent Free Grab: 2.48mg/L, Analyzer: 2.42mg/L 12:10- Treated Free Grab: 0.12mg/L, Analyzer: 0.17mg/L 12:10- Treated Total Grab: 3.36mg/L Analyzer: 3.36mg/L entered values in pwq sheet. equipment okay. | Holland Landing Well No. 1 | 2025-11-17
WEST | November | On site for station check and weekly Bacti Samples W11368382 Well running Verified Analyzers 13:50-Treated Free Grab- 0.15mg/L, Analyzer -0.18 mg/L 13:50-Treated Total Grab- 3.60 mg/L, Analyzer -3.62 mg/L Samples Taken after Cleaned the Raw water sample tap with 12% Sodium Hypochlorite. 14:05-Influent Free Grab- 3.23 mg/L, Analyzer -3.30 mg/L 14:08-effluent Free Grab- 3.00 mg/L, Analyzer -2.61 mg/L Couldn't adjust effluent free analyzer because arrow key not working. entered values in pwq sheet. Equipment okay | Holland Landing Well No. 1 | 2025-11-12
WEST | November | W11424524- Changed Cl2 Cylinder with J. Muzzin | Holland Landing Well No. 2 | 2025-11-06
WEST | November | on site for station check. check trends all okay Well running Verified Analyzers 14:30- Influent Free Grab: 3.10mg/L, Analyzer: 3.15mg/L 14:37- Effluent Free Grab: 2.78mg/L, Analyzer: 2.79mg/L 14:25- Treated Free Grab: 0.13mg/L, Analyzer: 0.18mg/L 14:25- Treated Total Grab: 3.10mg/L Analyzer: 3.18mg/L Sharon Valve grab Total Chlorine 2.09mg/L Changed effluent free reagent. entered values in pwq sheet. Made CMU W11427885 for heater unit. equipment okay. | Holland Landing Well No. 2 | 2025-11-07
WEST | November | on site for station check. check trends all okay Well running Verified Analyzers 13:55- Influent Free Grab: 3.02mg/L, Analyzer: 3.11mg/L 12:01- Effluent Free Grab: 2.88mg/L, Analyzer: 2.85mg/L 13:40- Treated Free Grab: 0.13mg/L, Analyzer: 0.18mg/L 13:40- Treated Total Grab: 3.28mg/L Analyzer: 3.21mg/L Sharon Valve grab Total Chlorine 2.44mg/L Changed treated total reagent. entered values in pwq sheet. equipment okay. | Holland Landing Well No. 2 | 2025-11-10
WEST | November | Top up silicate tanks. | Holland Landing Well No. 2 | 2025-11-10
WEST | November | on site for station check and Weekly Bacti Samples W11347868 check trends all okay Well running Verified Analyzers 09:27- Influent Free Grab: 3.20mg/L, Analyzer: 3.19mg/L 09:33- Effluent Free Grab: 2.78mg/L, Analyzer: 2.83mg/L 09:45- Treated Free Grab: 0.12mg/L, Analyzer: 0.18mg/L 09:45- Treated Total Grab: 3.20mg/L Analyzer: 3.23mg/L 09:45- Performed advanced monitoring (SL1000) MonoChloramine- 2.83mg/L Free Ammonia- 0.13mg/L Total Ammonia- 0.68mg/L Nitrite-0.004 Sharon Valve grab Total Chlorine 2.30mg/L Topped up Ammonia Tank 1- 17.72cm/80.10cm Ammonia Pump 1 Max flow set point changed from 95mg/L to 100 mg/L to lower Free ammoina value. entered values in PWQ sheet equipment okay | Holland Landing Well No. 2 | 2025-11-05
WEST | November | on site for station check check trends all okay Well running Residuals Treated Total Grab: 3.40mg/L Analyzer: 3.32mg/L Treated Free Grab: 0.21mg/L, Analyzer: 0.19mg/L Effluent Free Grabs: 2.82mg/L, Analyzer: 2.87mg/L Influent Free Grabs: 3.30mg/L, Analyzer: 3.25mg/L Performed advanced monitoring (SL1000) Mono 2.65mg/L FA 0.05mg/L TA 0.57mg/L Sharon Valve grab Total Chlorine 2.13mg/L entered values in PWQ sheet equipment okay | Holland Landing Well No. 2 | 2025-11-03
WEST | November | Onsite for station check Well isolated and offline for rehab Checked residuals mg/L Effluent free @1429 Analyzer 0.14 grab 0.09 Treated @1433 Total analyzer 1.68 grab 1.87 Free analyzer 0.05 grab 0.09 Adjusted total analyzer based on average of multiple grabs Sharon feed @1443 Total grab 1.90 Reagents ok | Holland Landing Well No. 2 | 2025-11-28
WEST | November | Onsite for station check Well in manual off in preparation for rehab Checked residuals mg/l @0909 Influent free Analyzer 2.57 grab 2.48 @0917 Effluent free Analyzer 0.43 grab 0.50 @0919 Treated Total analyzer 1.00 grab 0.95 Free analyzer 0.04 grab 0.09 Sharon feed @0924 Total grab 0.88 Isolated station distribution valve and locked it out, isolated contact tank inlet valve This caused loss of flow to influent analyzer so powered it off Placed well in local off Well was put in offline mode | Holland Landing Well No. 2 | 2025-11-24
WEST | November | HLW2 On site for station check and weekly Bacti Samples W11386800 Check trends: All okay Well running Verified Analyzers 14:00-Treated Free Grab- 0.20mg/L, Analyzer -0.30 mg/L 14:00-Treated Total Grab- 3.20 mg/L, Analyzer -3.16 mg/L Samples Taken. 14:10-Influent Free Grab- 3.22 mg/L, Analyzer -3.16 mg/L 14:12-effluent Free Grab- 2.76 mg/L, Analyzer -2.85 mg/L Free NH3 read 0mg/Land Treated free cl2 reads 30 mg/L, So Lowered Ammonia pump 1 & 2 max flow by 10 . (now,SL1000 Free NH3- 10 mg/L ) increasing by 5ml/min after the reading. (now, ammonia pump 1 & 2 maxflow setpoints -95 mL/min, 93 mL/min) Reagents all okay entered values in pwq sheet. Equipment okay | Holland Landing Well No. 2 | 2025-11-19
WEST | November | Onsite to investigate hi combined alarm interlocking well Influent free @1514 Free analyzer 2.61 Grab 2.50 Treated total @1526 Total analyzer 2.17 grab 2.11 Started well @1534 Influent free @ 1556 Analyzer 3.17 grab 3.21 Effluent @1558 Free analyzer 2.66 grab 2.66 Treated @1600 Free analyzer 0.20 grab 0.14 Total analyzer 3.16 grab 3.12 It appears to at earlier adjustment to increase tested total cl2 analyzer was based on faulty grabs and operator error. This is because since it was brought down grabs are within range of analyzer. Also based on the trends both the influential and effluent analyzers match grabs and neither of those values were high. In addition to that the chlorination is in manual and the chlorination position has not changed significantly within the last week | Holland Landing Well No. 2 | 2025-11-21
WEST | November | on site for station check. check trends all okay Site offline for rehab Verified Analyzers 14:35- Treated Free Grab: 0.03mg/L, Analyzer: 0.06mg/L 14:35- Treated Total Grab: 1.73mg/L Analyzer: 1.67mg/L Sharon Valve grab Total Chlorine 1.85 mg/L entered values in pwq sheet. equipment okay. | Holland Landing Well No. 2 | 2025-11-26
WEST | November | On site to investigate malfunctioning heater. Found heater contactor and thermostat to be defective. New heater installed. | Holland Landing Well No. 2 | 2025-11-20
WEST | November | -monitored well start up, no residual issues -FCV2 still experiencing high downstream pressure -FCV2 to remain closed for the night, no further pressure issues at HLW2 | Holland Landing Well No. 2 | 2025-11-18
WEST | November | On site for station check Topped up ammonia tank 1- 17.25cm/80cm Check trends: All okay Well running Verified Analyzers 13:45-Treated Free Grab- 0.18mg/L, Analyzer -0.22 mg/L 14:00-Treated Total Grab- Sl1000-3.75mg/L), Analyzer -3.33 mg/L adjusted analyzer to 3.90 mg/L based on multiple grabs, well interlocked. Adjusted the analyzer back to 3.34 mg/L. 15:15- J.Muzzin on site | Holland Landing Well No. 2 | 2025-11-21
WEST | November | Onsite for Scheduled PM workorders. Informed ROC about the works being done. Topped up Ammonia Tank 2- 18.16cm/82.26 cm Completed the following work orders W11363528 HLW2, JHSC Health and Safety Inspection W11361874 HLW2, Chlorine Gas Detector, Test W11364247 HLW2, Chemical System Inspection - Chlorine W11362706 HLW2, Pressure Relief Valve, Maintenance W11361553 HLW2, Chlorine Scrubber, Check W11363446 HLW2, Low/High Temperature Alarm, Test W11363606 HLW2, Turbidimeter, Maintenance W11364560 HLW2, Chemical System Inspection - Ammonia maxflow set point matched drawdown test value W11364263 HLW2, HLW2 Chemical System Inspection - Silicate, maxflow set point matched drawdown test value W11362250 HLW2, Pressure Relief Valve, Maintenance W11399121 HLW2, Holland Landing Well 2, Chemical System Line and Injection Point Flush - Silicate W11362072 HLW2, Chlorine Analyzer Maintenance, Holland Landing Verified Analyzers 15:00- Treated Free Cl2 Grab:0.06 mg/L, Analyzer:0.08mg/L 15:00- Treated Total Cl2 Grab:1.70 mg/L, Analyzer:1.60mg/L 15:05- Influent Free Cl2 Grab:2.90 mg/L, Analyzer:2.97mg/L 15:20- Effluent Free Cl2 Grab:1.94 mg/L, Analyzer:1.91mg/L | Holland Landing Well No. 2 | 2025-11-13
WEST | November | Replace Cl2 right cylinder and tare scale, with C Warnica. No issues | Holland Landing Well No. 2 | 2025-11-18
WEST | November | on site for station check. check trends all okay Well running Verified Analyzers 14:42- Influent Free Grab: 3.22mg/L, Analyzer: 3.21mg/L 14:40- Effluent Free Grab: 2.80mg/L, Analyzer: 2.82mg/L 14:20- Treated Free Grab: 0.15mg/L, Analyzer: 0.16mg/L 14:50- Treated Total Grab: 3.20mg/L Analyzer: 3.22mg/L Sharon Valve grab Total Chlorine 2.6 mg/L entered values in pwq sheet. equipment okay. | Holland Landing Well No. 2 | 2025-11-14
WEST | November | -on site to respond to well lockout due to high discharge pressure -well locked out before completing 15 minutes PTTW volume 14:01 - collected effluent grab: FCL = 0.07 mg/L TCL = 1.73 mg/L indicating treated distribution water -used back flush completed button to reset start up regulatory relief volume, will monitor well start up remotely -leaving well manual off due to pressure issues in distribution system | Holland Landing Well No. 2 | 2025-11-18
WEST | November | On site to top up silicate day tank. | Holland Landing Well No. 2 | 2025-11-18
WEST | November | on site for station check. check trends all okay Well running Verified Analyzers 13:20- Influent Free Grab: 3.04mg/L, Analyzer: 3.13mg/L 13:25- Effluent Free Grab: 2.80mg/L, Analyzer: 2.85mg/L 13:05- Treated Free Grab: 0.15mg/L, Analyzer: 0.18mg/L 13:05- Treated Total Grab: 3.42mg/L Analyzer: 3.36mg/L Changed treated free reagents Sharon Valve grab Total Chlorine 2.62 mg/L entered values in pwq sheet. equipment okay. | Holland Landing Well No. 2 | 2025-11-17
WEST | November | on site for station check. check trends all okay Well running Verified Analyzers 15:10- Influent Free Grab: 2.82mg/L, Analyzer: 2.88mg/L 15:15- Effluent Free Grab: 2.50mg/L, Analyzer: 2.59mg/L 14:50- Treated Free Grab: 0.09mg/L, Analyzer: 0.17mg/L 14:50- Treated Total Grab: 3.20mg/L Analyzer: 3.26mg/L collected samples. Sharon Valve grab Total Chlorine 2.34 mg/L entered values in pwq sheet. equipment okay. | Holland Landing Well No. 2 | 2025-11-12
WEST | November | On site for station check and Weekly bacti samples W11347868 12:29-Pre injection FCL- Grab- 0.01 mg/L; Analyzer - 0.03 mg/L TCL- Grab-0.89 mg/L; Analyzer - 0.77 mg/L Adjusted TCL to 0.89 mg/L Mono- 0.24 mg/L FA - 0.35 mg/L TA- 0.39 mg/L 13:30-Post injection FCL- Grab- 0.03 mg/L; Analyzer - 0.07 mg/L TCL- Grab-3.24 mg/L; Analyzer - 3.2 mg/L Mono- 0.243 mg/L FA - 0.10 mg/L TA- 0.58 mg/L Changed pre injection free ammonia value from 0.41 mg/l to 0.37 mg/L based on grabs. 12:10-Tank FCL- Grab- 0.06 mg/L TCL- Grab-1.16 mg/L Mono- 0.26 mg/L FA - 0.41 mg/L TA- 0.46 mg/L Nitrite- 0.005 mg/L Nitrate- 0.044 mg/L Sample taken entered values in PWQ sheet Equipment okay. | Holland Landing West Elevated Tank | 2025-11-05
WEST | November | On site for station check Tower draining 54% Verified Analyzers 09:35-Pre injection FCL- Grab- 0.09 mg/L; Analyzer - 0.11 mg/L TCL- Grab-1.90 mg/L; Analyzer - 2.16 mg/L Adjusted Analyzer 1.90 based on grabs (1.88,1.92,1.95) 09:55-Post injection FCL- Grab- 0.06 mg/L; Analyzer - 0.08 mg/L TCL- Grab-1.92 mg/L; Analyzer - 1.68 mg/L Adjusted Analyzer 1.92 based on grabs (1.90,1.92,1.95) Activated Duty. Tower filling SL100 readings 10:50-Pre injection FCL- Grab- 0.04 mg/L; Analyzer - 0.08 mg/L TCL- Grab-1.45 mg/L; Analyzer - 1.50 mg/L Mono- 0.33 mg/L FA - 0.21 mg/L TA- 0.27 mg/L 11:09-Post injection FCL- Grab- 0.37 mg/L TCL- Grab-3.18 mg/L Mono- 2.40 mg/L FA - 0.00 mg/L TA- 0.44 mg/L Changed inlet free ammonia SP from 0.35 to 0.25 based on grabs and chemical dosing. Changed hypo pump 1,2 max flow SPs from 155mL/min to 170 mL/min based on grabs and chemical dosing. 11:45-Post injection FCL- Grab- 0.08 mg/L; Analyzer - 0.07 mg/L TCL- Grab-3.50 mg/L; Analyzer - 3.40 mg/L Mono- 2.84 mg/L FA - 0.08 mg/L TA- 0.64 mg/L 10:25-Tank FCL- Grab- 0.04 mg/L TCL- Grab-1.16 mg/L Mono- 0.26 mg/L FA - 0.32 mg/L TA- 0.37 mg/L Nitrite- 0.005 mg/L Nitrate- 0.073 mg/L entered values in PWQ sheet Equipment okay. | Holland Landing West Elevated Tank | 2025-11-07
WEST | November | On site for station check Activated duty.Tower filling 52% Verified Analyzers 09:30-Pre injection FCL- Grab- 0.03 mg/L; Analyzer - 0.05 mg/L TCL- Grab-0.98mg/L; Analyzer - 0.94 mg/L SL100 readings Mono- 0.26 mg/L FA - 0.25 mg/L TA- 0.30 mg/L 10:00-Post injection FCL- Grab- 0.09 mg/L; Analyzer - 0.07 mg/L TCL- Grab-3.56mg/L; Analyzer - 3.51 mg/L Mono- 2.77 mg/L FA - 0.18 mg/L TA- 0.73 mg/L Increased Chlorine: Ammonia ratio from 4.2 to 4.6 based on grabs and chemical dosing. Changed hypo pump 1,2 max flow SPs from 170mL/min to 175 mL/min based on grabs and chemical dosing. 10:27-Post injection Mono- 2.91 mg/L FA - 0.09 mg/L TA- 0.67 mg/L 10:40-Tank FCL- Grab- 0.01 mg/L TCL- Grab-0.93 mg/L Mono- 0.29 mg/L FA - 0.28 mg/L TA- 0.34 mg/L Nitrite- 0.006 mg/L Nitrate- 0.111 mg/L entered values in PWQ sheet Equipment okay. | Holland Landing West Elevated Tank | 2025-11-10
WEST | November | Received Hypo delivery: Start level 32.17 cm Stop level 95.88 cm | Holland Landing West Elevated Tank | 2025-11-04
WEST | November | Responding to nh3 pumps fail to start alarms, notified by ROC. Pumps interlocking due to very low ammonia dose requirement; inlet SP is 0.44 due to increased system nh3 after poor dosing and performance since last week. Increased post-inj combined cl2 target SP from 3.15 to 3.30mg/L to increase ammonia dose and help prevent pump alarms (nh3 pumps now running at 4% up from 0-1%). Will request operators continue monitoring inlet and post-inj ammonia, adjust inlet SP accordingly to maintain good ammonia dosing and improve WQ in ET and system. | Holland Landing West Elevated Tank | 2025-11-05
WEST | November | On site for station check Duty active Checked residuals (mg/l) and entered data into PWQ sheet. Topped up Potassium Iodide solution for both Pre-injection and post injection analyzers. Pre injection @13:27 Total analyzer 0.70 grab 0.72 Free analyzer 0.03 grab 0.04 Sl1000 Mono 0.14 FA 0.34 TA 0.37 Post injection @13:33 Total analyzer 3.01 grab 2.98 Free analyzer 0.06 grab 0.08 Sl1000 Mono 2.65 FA 0.26 TA 0.79 Tank @13:30 Total grab 0.62 Free grab 0.02 Sl1000 Mono 0.16 FA 0.39 TA 0.42 Nitrite 0.006 Nitrate grab 0.016 | Holland Landing West Elevated Tank | 2025-11-03
WEST | November | On site for station check to monitor Free ammonia and total ammonia, and Cole W. adjusted ammonia dosing setpoints. Entered station check data to PWQ Sheet. Free and Total Ammonia monitoring: Grab @ 13:44 Post injection Mono 2.82 FA 0.24 TA 0.80 Grab @ 14:11 Post Injection FA 0.00 TA 0.57 Grab @ 14:28 Post Injection Mono 2.98 FA 0.00 TA 0.57 Grab @ 14:42 Post Injection Mono 2.99 FA 0.05 TA 0.64 | Holland Landing West Elevated Tank | 2025-11-04
WEST | November | -on site to troubleshoot high post injection free ammonia readings Pre injection readings: MCL = 0.19 TNH3 = 0.27 FNH3 = 0.24 Post injection readings: MCL = 2.70 TNH3 = 0.70 FNH3 = 0.16 -completed drawdowns on ammonia pumps: Pump 2 max flow = 118 ml/min scada setpoint = 120 ml/min Pump 1 max flow = 102 ml/min scada setpoint = 110 ml/min -suspect ammonia tank concentration is high -increased ammonia pump #1 max flow setpoint 110 to 160 ml/min and pump #2 max flow setpoint 120 to 180 ml/min -post injection grab with pump 2 running: MCL = 3.21 TNH3 = 0.65 FNH3 = 0.02 -decreased ammonia pump 2 max flow setpoint 180 to 170 ml/min -post injection grab with pump 1 running: MCL = 2.86 TNH3 = 0.67 FNH3 = 0.11 -increased ammonia pump 1 max flow setpoint 160 to 165 ml/min | Holland Landing West Elevated Tank | 2025-11-28
WEST | November | On site for station check and Weekly bacti samples W11402705 Check Trends: All okay Tower draining (81%) 10:50- Sample taken Grab Free CL2-0.09 mg/L Grab Total CL2-1.90 mg/L Activated duty Verified Analyzers 11:15-Pre injection FCL- Grab- 0.04 mg/L; Analyzer - 0.12 mg/L TCL- Grab-1.72 mg/L; Analyzer - 1.78 mg/L 11:50-Post injection FCL- Grab- 0.04 mg/L; Analyzer - 0.08 mg/L TCL- Grab-3.20 mg/L; Analyzer - 3.22 mg/L Reagents okay entered values in PWQ sheet Equipment okay. | Holland Landing West Elevated Tank | 2025-11-26
WEST | November | On site for station check. Tower filling (46%) Check trends:all okay. Verified Analyzers 10:20-Pre injection FCL- Grab- 0.03 mg/L; Analyzer - 0.09 mg/L TCL- Grab-1.32 mg/L; Analyzer - 1.31 mg/L 10:35-Post injection FCL- Grab- 0.07 mg/L; Analyzer - 0.07 mg/L TCL- Grab-3.40 mg/L; Analyzer - 3.43 mg/L Topped up acetate buffer reagent for both analyzers. entered values in PWQ sheet Equipment okay. | Holland Landing West Elevated Tank | 2025-11-21
WEST | November | -Upon further investigation suspect ammonia dosing issues may be due to poor mixing at lower flows. Returned ammonia pump max flow setpoints to original setpoints and increased flow from FCV2 -post injection grab: MCL = 3.05 TNH3 = 0.67 FNH3 = 0.07 | Holland Landing West Elevated Tank | 2025-11-28
WEST | November | nsite for station check Duty active Checked residuals mg/l Pre injection @1258 Total analyzer 0.90 grab 1.07 Free analyzer 0.06 grab 0.06 Sl1000 Mcl 0.19 F nh3 0.33 T nh3 0.35 Post injection @1307 Total analyzer 3.50 grab 3.6 Free analyzer 0.07 grab 0.09 Sl1000 Mcl 2.88 F nh3 0.13 T nh3 0.69 Tank @1318 Total grab 1.10 Free grab 0.03 Sl1000 Mcl 0.25 F nh3 0.37 T nh3 0.42 No2 0.07 Nitrate grab 0.055 Took second grab of post injection sl1000 @1326 F nh3 0.03 T nh3 0.56 Mcl 2.72 All reagents ok Deactivated duty afterwards | Holland Landing West Elevated Tank | 2025-11-24
WEST | November | On site for station check and Weekly bacti samples W11386800 Check Trends: All okay Tower draining (68%) 10:25- Sample taken Grab Free CL2-0.05 mg/L Grab Total CL2-2.20 mg/L Activated duty Verified Analyzers 11:40-Pre injection FCL- Grab- 0.10 mg/L; Analyzer - 0.13 mg/L TCL- Grab-1.95 mg/L; Analyzer - 1.98 mg/L 11:55-Post injection FCL- Grab- 0.10 mg/L; Analyzer - 0.09 mg/L TCL- Grab-3.10 mg/L; Analyzer - 3.10 mg/L Reagents okay entered values in PWQ sheet Equipment okay. | Holland Landing West Elevated Tank | 2025-11-19
WEST | November | On site for station check Tower filling (60%) Check trends:all okay. Verified Analyzers 13:15-Pre injection FCL- Grab- 0.06 mg/L; Analyzer - 0.09 mg/L TCL- Grab-1.30 mg/L; Analyzer - 1.34 mg/L 13:25-Post injection FCL- Grab- 0.11 mg/L; Analyzer - 0.07 mg/L TCL- Grab-3.30 mg/L; Analyzer - 3.28 mg/L Reagents all okay. entered values in PWQ sheet Equipment okay. | Holland Landing West Elevated Tank | 2025-11-14
WEST | November | On site for station check and Weekly bacti samples W11368382 Tower draining (50%) 11:40- Sample taken Grab Free CL2-0.09 mg/L Grab Total CL2-2.06 mg/L Activated duty Verified Analyzers 12:20-Pre injection FCL- Grab- 0.11 mg/L; Analyzer - 0.12 mg/L TCL- Grab-1.70 mg/L; Analyzer - 0.62 mg/L 12:30-Post injection FCL- Grab- 0.11 mg/L; Analyzer - 0.08 mg/L TCL- Grab-3.40 mg/L; Analyzer - 3.33 mg/L entered values in PWQ sheet Equipment okay. | Holland Landing West Elevated Tank | 2025-11-12
WEST | November | -on site to respond to pre injection combined chlorine hihi alarm -at 12:48 a PAC communication failure caused HLW2 and FCV2 to shutdown while rechlorination system was active. The sudden drop in flow caused the tower to start draining and a combined chlorine reading above 4.0 mg/L was registered on the regulatory pre-injection chlorine analyzers while directing flow to users 12:53 - 12:56 - combined chlorine residual above 4.0 mg/L reaching a maximum of 4.43 mg/L with an outlet flow reaching a maximum of 10.5 l/s -remotely put HLW1 into manual on and opened tower waste valve from 13:00 - 13:07 to direct flow to waste 13:05 - PAC communication failure cleared at HLW2 and FCV2, activated system duty to push water back into the tower and away from users -increased minimum dosing flow from 8 l/s to 20 l/s to reduce potential for chemical overdosing in low flow events in case of further communication fails -arrived on site and collected pre injection grab sample: 14:07 -Pre injection Analyzer readings: Free Chlorine = 0.04 mg/L Total Chlorine = 0.64 mg/L 14:07 -Pre injection Grabs: Free Chlorine = 0.04 mg/L Total Chlorine = 0.66 mg/L -site back to normal operation -filed AWQI # 170756, no further instruction required by public health or SAC | Holland Landing West Elevated Tank | 2025-11-15
WEST | November | Receive hypo delivery. | Holland Landing West Elevated Tank | 2025-11-18
WEST | November | On site for station check. Topped up Ammonia Tank - 13.16cm/79.5 cm Activated duty. Tower filling (65%) Ammonia pumps failed to start alarm came, changed inlet Free ammonia set point from 0.25 mg/L to 0.24 mg/L. Check trends:all okay. Verified Analyzers 10:40-Pre injection FCL- Grab- 0.08 mg/L; Analyzer - 0.13 mg/L TCL- Grab-1.97 mg/L; Analyzer - 2.00 mg/L 10:55-Post injection FCL- Grab- 0.12 mg/L; Analyzer - 0.10 mg/L TCL- Grab-3.12 mg/L; Analyzer - 3.20 mg/L Reagents all okay. entered values in PWQ sheet Equipment okay. | Holland Landing West Elevated Tank | 2025-11-17
WEST | November | On sit for the following Scheduled PM Work orders. Informed ROC about the works being done. W11381926 HLETYS, High & Low Water Level Alarm, Test W11382356 HLETYS, Sensing Line Heat Trace System, Maintenance W11382378 HLETYS, Low Temperature Alarm, Test W11383792 HLETYS, Ammonia System Inspection Drawdown test matched Pump maxflow setpoints W11383805 HLETYS, Sodium Hypochlorite System Inspection Drawdown test matched Pump maxflow setpoints W11398342 HLETYS, Sump Pit System Inspection W11398317 HLETYS, Siemens Depolox 5/Micro 2000, Chlorine Analyzer, Maintenance Verified Analyzers pre injection free Cl2 Grab- 0.05 mg/L; Analyzer-0.08 mg/L pre injection total Cl2 Grab- 1.20 mg/L; Analyzer-1.18 mg/L post injection free Cl2 Grab- 0.01 mg/L; Analyzer-0.07 mg/L post injection total Cl2 Grab- 3.50 mg/L; Analyzer-3.40 mg/L | Holland Landing West Elevated Tank | 2025-11-11
WEST | November | On site to complete station check. Free Chlorine Grab: 0.05mg/L Total Chlorine Grab: 1.58mg/L No issues on site | Jefferson Pumping Station & Reservoir | 2025-11-10
WEST | November | On site to complete station check. Free Chlorine Grab: 0.05mg/L Total Chlorine Grab: 1.72mg/L No issues on site | Jefferson Pumping Station & Reservoir | 2025-11-03
WEST | November | Restarted the Operator Interface Terminal due to Windows Updates. Notified the Remote Opertions Center and OIC. | Jefferson Pumping Station & Reservoir | 2025-11-03
WEST | November | On site for station check and to collect bacti sample wo#11347854 Residuals West Cell cell:@ 0835 Free: 0.05mg/L Total 2.07mg/L SL1000 readings Total Cl: 2.07mg/L Total NH3: 0.43mg/L Free NH3: 0.09mg/L NH2Cl: 1.74mg/L No issues on site | Jefferson Pumping Station & Reservoir | 2025-11-05
WEST | November | On site to complete station check. Free Chlorine Grab: 0.05mg/L Total Chlorine Grab: 1.66mg/L No issues on site | Jefferson Pumping Station & Reservoir | 2025-11-20
WEST | November | On site to complete station check. Free Chlorine Grab: 0.05mg/L Total Chlorine Grab: 1.75mg/L No issues on site | Jefferson Pumping Station & Reservoir | 2025-11-24
WEST | November | On site for station check and to collect weekly sample W11402580 East cell @12:55 Chlorine Free grab 0.05mg/L Total grab 1.73mg/L No issues on site | Jefferson Pumping Station & Reservoir | 2025-11-26
WEST | November | On site to complete station check. Free Chlorine Grab: 0.05mg/L Total Chlorine Grab: 1.82mg/L No issues on site | Jefferson Pumping Station & Reservoir | 2025-11-28
WEST | November | Oversaw/assisted Total Power technician performed Semi Annual Diesel Generator PM. | Jefferson Pumping Station & Reservoir | 2025-11-13
WEST | November | On site for station check and to collect bacti sample wo#11386786 Residuals West Cell cell:@ 13:55 Free: 0.05mg/L Total 1.93mg/L SL1000 readings Total Cl: 1.98mg/L Total NH3: 0.41mg/L Free NH3: 0.07mg/L NH2Cl: 1.60mg/L No issues on site | Jefferson Pumping Station & Reservoir | 2025-11-19
WEST | November | On site to complete station check. Free Chlorine Grab: 0.05mg/L Total Chlorine Grab: 1.75mg/L No issues on site | Jefferson Pumping Station & Reservoir | 2025-11-14
WEST | November | Performed Annual electrical pm and motor pm. | Jefferson Pumping Station & Reservoir | 2025-11-14
WEST | November | On site for station check and to collect bacti sample wo#11368236 Residuals East Cell cell:@ 12:45 Free: 0.05mg/L Total 1.91mg/L SL1000 readings Total Cl: 1.90mg/L Total NH3: 0.43mg/L Free NH3: 0.14mg/L NH2Cl: 1.49mg/L Nitrite 0.000mg/L No issues on site | Jefferson Pumping Station & Reservoir | 2025-11-12
WEST | November | On site for the following JFRS, JHSC Health and Safety Inspection, Jefferson RES and BPS (1M) JFRS, Drain Valve Exercise, Jefferson RES (6M) JFRS, Actuated Valve Exercise & Inspection, Jefferson RES (3M) JFPS, Standby Power Generator Test Run and Run Hours log, Jefferson WPS (1M) Run hours start 647.6hrs stop 648.8hrs Fuel start 6615L stop 6571L JFRS, Sump Pit System Inspection, Jefferson RES (1M) JFRS, Air Valve Flush & Inspection, Jefferson RES (3M) JFPS, Sump Pit System Inspection, Jefferson WPS (1M) JFPS, Actuated Valves Exercise & Inspection, Jefferson WPS (1M) JFPS, Pump & Motor Inspection, Jefferson WPS (1M) JFRS, Ventilation System Inspection, Jefferson Valve House (1M) JFPS, Low Temperature Alarm Test, Jefferson WPS (1M) JFPS, Ventilation System Inspection, Jefferson WPS (1M) JFRS, Sump Pit System Inspection, Jefferson Valve House (1M) JFPS, Dehumidifier Inspection & Cleaning, Jefferson WPS (1M) JFRS, Air Valves Flush & Inspection Jefferson, Valve House (??) JFRS, Flood Alarm Test Jefferson Valve House (1M) JFRS, Dehumidifier Inspection & Cleaning, Jefferson, Valve House (1M) JFRS, Dehumidifier Inspection & Cleaning, Jefferson, RES (1M) JFRS, External Venting Screens Inspection, Jefferson RES (1M) No issues on site | Jefferson Pumping Station & Reservoir | 2025-11-11
WEST | November | On site to complete station check. Free Chlorine Grab: 0.05mg/L Total Chlorine Grab: 1.83mg/L No issues on site | Jefferson Pumping Station & Reservoir | 2025-11-17
WEST | November | Onsite for station check Duty active Checked residuals mg/l @1052 Total grab 1.89 Free grab 0.04 | King City Dufferin Booster Pumping Station | 2025-11-07
WEST | November | Onsite for station check Duty not active Checked residuals mg/l @1000 Total grab 1.92 Free grab 0.02 | King City Dufferin Booster Pumping Station | 2025-11-10
WEST | November | Onsite for station check Duty not active Checked residuals mg/l @1437 Total grab 1.96 Feee grab 0.02 | King City Dufferin Booster Pumping Station | 2025-11-03
WEST | November | Onsite to complete work orders Exercised valves Exercised surge tank prv Completed jhsc , no issues | King City Dufferin Booster Pumping Station | 2025-11-04
WEST | November | Station Check (no issued found) Input data to PWQ 13:50 CL2 grab residuals (mg/l) Free: 0.08 Total: 1.76 | King City Dufferin Booster Pumping Station | 2025-11-27
WEST | November | Onsite for station check Duty not active Checked residuals mg/l @1404 Total grab 1.99 Free grab 0.03 | King City Dufferin Booster Pumping Station | 2025-11-21
WEST | November | On site for station check Check Trends: All okay. Station duty not active 09:50- Grab samples taken Free Cl2 Grab-0.03 mg/L Total Cl2 Grab- 1.90 mg/L entered values in PWQ sheet equipment okay. | King City Dufferin Booster Pumping Station | 2025-11-25
WEST | November | Onsite for station check Duty not active Checked residuals mg/l @1036 Total grab 1.59 Free grab 0.05 | King City Dufferin Booster Pumping Station | 2025-11-14
WEST | November | On site for station check Grabs Free 0.05mg/L Total 1.70mg/L No other issues on site | King City Dufferin Booster Pumping Station | 2025-11-17
WEST | November | Onsite for station check and to collect weekly micro sample W11347840 Tower draining CHecked residuals mg/L @1440 Total analyzer 2.00 grab 2.00 Free analyzer 0.06 grab 0.08 Sl1000 MCl grab 1.99 No2 grab 0.005 F nh3 0.10 T nh3 0.50 | King City Dufferin Elevated Tank | 2025-11-05
WEST | November | Onsite to complete work orders Placed pumping station pumps in manual Exercised actuated valve Exercised air relief valves Exercised drain valves Cleaned cl17 Grabs before Total analyzer 2.09 grab 1.91 Free analyzer 0.05 grab 0.04 Grabs after Total analyzer 2.20 grab 1.99 Free analyzer 0.06 grab 0.06 Adjusted total analyzer based on average of multiple grabs to 1.98 Completed just no issues observed | King City Dufferin Elevated Tank | 2025-11-04
WEST | November | Onsite for station check and to collect weekly micro samples W11402458 Tower draining Checked residuals mg/l @1424 Total analyzer 1.71 grab 1.72 Free analyzer 0.03 grab 0.02 Sl1000 Mcl grab 1.61 No2 grab 0.004 Changed reagents in free analyzer | King City Dufferin Elevated Tank | 2025-11-26
WEST | November | Changed Total Analyzer reagents | King City Dufferin Elevated Tank | 2025-11-25
WEST | November | Onsite for station check and to collect weekly micro sample Tower draining Checked residuals mg/l @1442 Total analyzer 1.71 grab 1.67 Free analyzer 0.04 grab 0.08 Sl1000 Mcl grab 1.65 No2 0.006 F nh3 0.12 T nh3 0.45 Reagents ok | King City Dufferin Elevated Tank | 2025-11-12
WEST | November | Only wife station check and to collect weekly micro sample W11386772 Tower draining Checked residuals mg/l @1433 Total analyzer 1.86 grab 1.85 Free analyzer 0.04 grab 0.05 Sl1000 Mcl grab 1.72 No2 0.003 F nh3 0.14 T nh3 0.48 | King City Dufferin Elevated Tank | 2025-11-19
WEST | November | On site for electrical and heat trace inspection. | King City Fisher Elevated Tank | 2025-11-10
WEST | November | Onsite for station check and to collect weekly micro sample W11347840 Checked resoiduals mg/L @1410 Total grab 1.99 grab 1.86 Free grab 0.05 grab 0.05 Adjusted total analyzer based on average of multiple grabs Sl1000 @1420 Mcl grab 1.71 F nh3 grab 0.12 T nh3 grab 0.46 @1410 No2 grab 0.002 | King City Fisher Elevated Tank | 2025-11-05
WEST | November | Onsite for station check and to collect weekly micro sample w11386772 Tower draining Checked residuals mg/l @1355 Total analyzer 1.77 grab 1.67 Free analyzer 0.04 grab 0.06 Sl1000 Mcl grab 1.70 No2 0.005 F nh3 0.12 T nh3 0.45 | King City Fisher Elevated Tank | 2025-11-19
WEST | November | Onsite for station check and to collect weekly micro sample W11402458 Tower draining Checked residuals mg/l @1349 Total analyzer 2.00 grab 1.86 Free analyzer 0.04 grab 0.04 Adjusted total analyzer based on average of multiple grabs Sl1000 Mcl 1.82 No2 0.002 F nh3 0.10 T nh3 0.45 | King City Fisher Elevated Tank | 2025-11-26
WEST | November | Onsite for station check and to collect weekly micro sample Checked residuals mg/L @1413 Total analyzer 1.84 grab 1.77 Free analyzer 0.04 grab 0.03 Sl1000 Mcl grab 1.99 No2 0.000 F nh3 0.13 T nh3 0.53 | King City Fisher Elevated Tank | 2025-11-12
WEST | November | Workorders: #11368659 Depolox maint. 12:45 Verified (mg/L) Free: Grab 0.04, A 0.04 Total: Grab 1.63, A 1.73 (adjusted to match grabs) #11398238 PRV #11398267 Heat tr. #11398303 manual V. #11398396 jhs #11398595 low temp #11398638 Heat tr. #11398732 Port. Gen | King City Fisher Elevated Tank | 2025-11-18
WEST | November | Onsite for station check and to collect weekly micro sample W11376158 Checked residuals mg/L @1146 Total grab 2.04 Free grab 0.01 Sl1000 Mcl grab 2.12 F nh3 0.14 T nh3 0.56 No2 0.000 | Kleinburg Elevated Tank | 2025-11-05
WEST | November | On site for electrical and heat trace inspection. | Kleinburg Elevated Tank | 2025-11-10
WEST | November | Onsite for station check and to collect weekly micro sample W11402594 Tower draining Checked residuals mg/l @1148 Total grab 2.19 Free grab 0.05 Sl1000 Mcl grab 1.98 No2 grab 0.005 F nh3 grab 0.10 T nh3 grab 0.49 | Kleinburg Elevated Tank | 2025-11-26
WEST | November | Onsite for station check and to collect weekly micro sample Tower draining Checked residuals mg/l @1119 Total grab 2.02 Free grab 0.06 Sl1000 Mcl grab 1.97 No2 0.000 F nh3 0.10 T nh 0.49 | Kleinburg Elevated Tank | 2025-11-19
WEST | November | Onsite to complete work orders Exercised manual and drain valves Tried to run generator , did not start properly will make work order | Kleinburg Elevated Tank | 2025-11-11
WEST | November | Onsite for station check and to collect weekly micro sample W11368250 Checked residuals mg/l @1300 Tcl grab 1.98 Fcl grab 0.04 Sl1000 Mcl grab 1.88 No2 0.000 F nh3 0.18 T nh3 0.55 C | Kleinburg Elevated Tank | 2025-11-12
WEST | November | Onsite for station check Duty active Checked residuals mg/l @1242 Total analyzer 2.05 grab 1.96 Free analyzer 0.03 grab 0.02 | Kleinburg HWY 27 Booster Pumping Station | 2025-11-10
WEST | November | Onsite for station check Duty not active Checked residuals mg/l @1309 Total analyzer 2.04 grab 2.05 Free analyzer 0.03 grab 0.06 | Kleinburg HWY 27 Booster Pumping Station | 2025-11-07
WEST | November | Onsite for station check Duty active Checked residuals mg/l @1340 Total analyzer 2.12 grab 2.07 Free analyzer 0.03 grab 0.03 Reagents ok No issues observed | Kleinburg HWY 27 Booster Pumping Station | 2025-11-03
WEST | November | Station Check (no issues found) Input data to PWQ 10:10 Verified Depolox (mg/l) Free: Grab 0.06, A 0.04 Total: Grab 2.10, A 2.17 (Topped up both Ki/dist. & Acetate reagents) | Kleinburg HWY 27 Booster Pumping Station | 2025-11-27
WEST | November | On site for station check Check trends: All okay duty off. 13:45- Verified Analyzers Grab free Cl2- 0.04 mg/L, Analyzer- 0.03 mg/L. Grab Total Cl2- 2.10 mg/L, Analyzer- 2.18 mg/L. Reagents Okay. entered values in PWQ sheet. Equipment Okay. | Kleinburg HWY 27 Booster Pumping Station | 2025-11-25
WEST | November | Onsite for station check Duty active Checked residuals mg/l @1055 Total analyzer 2.25 grab 2.20 Free analyzer 0.03 grab 0.01 Reagents ok | Kleinburg HWY 27 Booster Pumping Station | 2025-11-21
WEST | November | Onsite for station check Duty not active checked residuals mg/l @1400 Total analyzer 2.12 grab 2.05 Free analyzer 0.03 grab 0.04 | Kleinburg HWY 27 Booster Pumping Station | 2025-11-17
WEST | November | Onsite to complete work orders Tested flood alarm Did monthly check on Cl2 analyzer Reagents and electrolyte ok Grabs Total analyzer 1.26 grab 2.05 Free analyzer 0.01 grab 0.01 Adjusted total analyzer Afterwards Hi cl2 alarm came in Total analyzer 2.74 grab 1.90 Adjusted analyzer | Kleinburg HWY 27 Booster Pumping Station | 2025-11-11
WEST | November | Onsite for station check Duty active Checked residuals mg/L Total analyzer 2.12 grab 2,10 Free analyzer 0.02 grab 0.02 Completed JHSC no issues | Kleinburg HWY 27 Booster Pumping Station | 2025-11-14
WEST | November | Onsite to complete work orders Tested flood alarm, no issues Tested prv Did cl2 monthly maintenance Added grit to free cl2 reservoir Grabs Total analyzer 2.08 grab 2.09 Free analyzer 0.05 grab 0.05 Did pump & motors inspection no issues observed | Kleinburg Whisper Lane Booster Pumping Station | 2025-11-06
WEST | November | Onsite for station check Duty not active Checked residuals mg/l @1250 Total analyzer 1.98 grab 1.99 Free analyzer 0.04 grab 0.06 | Kleinburg Whisper Lane Booster Pumping Station | 2025-11-07
WEST | November | Onsite for station check Schedule mode duty active Checked residuals mg/l @1314 Total analyzer 2.02 grab 2.08 Free analyzer 0.05 grab 0.04 | Kleinburg Whisper Lane Booster Pumping Station | 2025-11-10
WEST | November | Onsite for station check Duty not active Checked residuals mg/l @1227 Total analyzer 1.93 grab 1.96 Free analyzer 0.04 grab 0.05 Reagents ok | Kleinburg Whisper Lane Booster Pumping Station | 2025-11-03
WEST | November | Delivered fuel cube to site, added 880 Litres of fuel to back up generator. It?s currently sitting at 65% full. Will need to bring an additional fuel cube. | Kleinburg Whisper Lane Booster Pumping Station | 2025-11-25
WEST | November | On site for station check Check trends: All okay Station duty Active 12:25- Verified Analyzers Grab Free Cl2- 0.05 mg/L, Analyzer - 0.02 mg/L Grab Total CL2- 2.02 mg/L, Analyzer - 2.01 mg/L Reagents All good entered values in PWQ sheet Equipment okay. | Kleinburg Whisper Lane Booster Pumping Station | 2025-11-25
WEST | November | On site for a station check Duty not active Checked residuals mg/l @1001 Total analyzer 2.00 grab 1.96 Free analyzer 0.02 grab 0.05 Reagents ok Exercised pumps 1&2 in local | Kleinburg Whisper Lane Booster Pumping Station | 2025-11-21
WEST | November | Station Check (no issues found) Input data to PWQ 11:15 Verified Depolox (no is issues found) Free: Grab 0.04, A 0.02 Total: Grab 1.91, A 1.95 (topped up reagents) | Kleinburg Whisper Lane Booster Pumping Station | 2025-11-27
WEST | November | Onsite for station check Schedule mode duty active Checked residuals mg/l @1259 Total analyzer 2.11 grab 2.15 Free analyzer 0.02 grab 0.02 | Kleinburg Whisper Lane Booster Pumping Station | 2025-11-14
WEST | November | Onsite for station check Duty not active Checked residuals mg/l @1423 Total analyzer 2.04 grab 2.12 Free analyzer 0.02 grab 0.02 | Kleinburg Whisper Lane Booster Pumping Station | 2025-11-17
LINEAR | November | Onsite to replace and setup MWEL-LT9. Informed ROC Replaced probe and configured. Verified scada reading. Water resources verified reading. All good Informed ROC, armed building and left site | Major MacKenzie and Newkirk Road Dewatering Wells | 2025-11-03
LINEAR | November | Totalizer: 478518 m3 Discharge pressure: 30.18 Kpa Flow Rate: 11.4 l/s Monitoring well: 219.1 Well 8 RPM: 2448 AMP: 5.5 %: 42 Level:208.1 masl Well 13 RPM: 2113 AMP: 4.9 %: 21 Level: 205.8 masl | Major MacKenzie and Newkirk Road Dewatering Wells | 2025-11-04
LINEAR | November | Totalizer: 480876 m3 Discharge pressure: 30.81 Kpa Flow Rate: 11.3 l/s Monitoring well: 219.2 Well 8 RPM: 2450 AMP: 5.5 %: 42 Level:208.0 masl Well 13 RPM: 2112 AMP: 4.9 %: 21 Level: 205.8 masl | Major MacKenzie and Newkirk Road Dewatering Wells | 2025-11-28
WEST | November | On site for station check and to collect bacti sample wo# w11347854 Residuals @ 11:25 colorimeter *west Cell* Total Grab: 1.98mg/L Free Grab: 0.05mg/L Operational Sampling (SL1000) Total Cl: 2.00mg/L Total NH3: 0.4mg/L Free NH3: 0.09mg/L NH2CL: 1.77mg/L No issues on site | Maple North Reservoir | 2025-11-05
WEST | November | On site for station check and to collect bacti sample wo# w11386786 Residuals @ 09:55 colorimeter *West Cell* Total Grab: 1.88mg/L Free Grab: 0.07mg/L Operational Sampling (SL1000) Total Cl: 1.85mg/L Total NH3: 0.42mg/L Free NH3: 0.10mg/L NH2CL: 1.63mg/L Nitrite 0.001mg/L No issues on site | Maple North Reservoir | 2025-11-19
WEST | November | On site for station check and to collect bacti sample wo# w11402580 Residuals @ 10:15colorimeter *East Cell* Total Grab: 1.98mg/L Free Grab: 0.05mg/L Operational Sampling (SL1000) Total Cl: 1.95mg/L Total NH3: 0.44mg/L Free NH3: 0.10mg/L NH2CL: 1.71mg/L No issues on site | Maple North Reservoir | 2025-11-26
WEST | November | On site for station check and to collect bacti sample wo# w11368236 Residuals @ 09:30 colorimeter *East Cell* Total Grab: 1.85mg/L Free Grab: 0.05mg/L Operational Sampling (SL1000) Total Cl: 1.82mg/L Total NH3: 0.40mg/L Free NH3: 0.09mg/L NH2CL: 1.54mg/L Nitrite 0.000mg/L No issues on site | Maple North Reservoir | 2025-11-12
WEST | November | On site for VNRSKS, JHSC Health and Safety Inspection, North Maple RES (1M) VNRSKS, Sump Pump, Inside Inspection & Maintenance, North Maple RES (1M) No issues on site | Maple North Reservoir | 2025-11-18
WEST | November | On site to Complete Station Check. Residuals PD8 Total Grab: 2.09mg/L, Analyzer: 2.10mg/L PD8 Free Grab: 0.04mg/L, Analyzer: 0.02mg/L PD7 Total Grab: 1.85mg/L, Analyzer: 1.88mg/L PD7 Free Grab: 0.05mg/L, Analyzer: 0.05mg/L Closed pd8 header and ensured splitter was open. Placed both valves in local. Sanitary pumps not working - contacted electrician to come to site | Maple Pumping Station | 2025-11-07
WEST | November | On site to repair basement sump pump/sanitary pump system malfunctioning float switches. Tested for proper operation. | Maple Pumping Station | 2025-11-07
WEST | November | On site to Complete Station Check. Residuals PD8 Total Grab: 2.02mg/L, Analyzer: 2.08mg/L PD8 Free Grab: 0.05mg/L, Analyzer: 0.02mg/L PD7 Total Grab: 1.95mg/L, Analyzer: 1.95mg/L PD7 Free Grab: 0.05mg/L, Analyzer: 0.05mg/L | Maple Pumping Station | 2025-11-10
WEST | November | On site to Complete Station Check. Residuals PD8 Total Grab: 2.16mg/L, Analyzer: 2.18mg/L PD8 Free Grab: 0.04mg/L, Analyzer: 0.02mg/L PD7 Total Grab: 1.92mg/L, Analyzer: 1.89mg/L PD7 Free Grab: 0.05mg/L, Analyzer: 0.05mg/L | Maple Pumping Station | 2025-11-03
WEST | November | On site with Dan Boate and Tyler Smith to install replacement Rotork actuator on PD7 Pump #1. Pump #1 starter, Pump #1 actuator and Pump#2 actuator de-energized and locked out to perform replacement. ROC notified. New actuator installation incomplete, requires programming and testing. Pump# 1 starter and actuator remain de-energized and locked out. Pump #2 actuator reenergized. Cole Warnica and ROC notified. | Maple Pumping Station | 2025-11-25
WEST | November | On site to Complete Station Check. Residuals PD8 Total Grab: 1.98mg/L, Analyzer: 1.94mg/L PD8 Free Grab: 0.05mg/L, Analyzer: 0.02mg/L PD7 Total Grab: 1.95mg/L, Analyzer: 1.94mg/L PD7 Free Grab: 0.05mg/L, Analyzer: 0.04mg/L Pd8 p2 vfd vault came in again - contacted elec asked to leave it outstanding to see fault codes. No issues on site | Maple Pumping Station | 2025-11-28
WEST | November | On site to Complete Station Check. Residuals PD8 Total Grab: 1.99mg/L, Analyzer: 2.09mg/L PD8 Free Grab: 0.04mg/L, Analyzer: 0.02mg/L PD7 Total Grab: 1.91mg/L, Analyzer: 1.95mg/L PD7 Free Grab: 0.05mg/L, Analyzer: 0.04mg/L No issues on site | Maple Pumping Station | 2025-11-24
WEST | November | Onsite to complete work orders Completed station check Checked residuals mg/l Pd7 Duty not active @1100 Total analyzer 1.98 grab 1.97 Free analyzer 0.05 grab 0.06 Pd Duty active @1105 Total analyzer 2.13 grab 2.08 Free analyzer 0.02 grab 0.04 Pd7 pump 4 interlocked due to hi pressure switch Tried to start in manual and in shut down causing discharge header lolo flow alarm Tried to exercise valve and pump started , closed and stopped pump. Decided to open valve to open completely and ran pump. Cleared lolo flow interlock. Stopped pump Tried running pump in manual and was successful Placed back to auto will continue to monitor Completed chamber inspection of reservoir metering chamber With J. Williams | Maple Pumping Station | 2025-11-20
WEST | November | On site with Dan Boate to program and test actuator on PD7 pump #1. ROC notified. PD7 pump #1 and actuator programming/testing completed, returned to normal operation. ROC and Cole Warnica. | Maple Pumping Station | 2025-11-27
WEST | November | On site to Complete Station Check. Residuals PD8 Total Grab: 1.82mg/L, Analyzer: 1.89mg/L PD8 Free Grab: 0.04mg/L, Analyzer: 0.02mg/L PD7 Total Grab: 1.71mg/L, Analyzer: 1.73mg/L PD7 Free Grab: 0.05mg/L, Analyzer: 0.06mg/L No issues on site | Maple Pumping Station | 2025-11-14
WEST | November | PD7 pump 2, check grease pump 4 PD 8 Sump pumps | Maple Pumping Station | 2025-11-17
WEST | November | Onsite for station check Checked residuals mg/l Pd7 Duty not active @1106 Total analyzer 1.91 grab 1.90 Free analyzer 0.05 grab 0.03 Pd8 Duty active @1120 Total analyzer 2.12 grab 2.06 Free analyzer 0.02 grab 0.05 | Maple Pumping Station | 2025-11-17
WEST | November | -on site to complete work orders -informed ROC of work -completed Screen Inspection -completed Air Handling Units, Inspection & Maintenance -completed Ventilation Systems, Inspection, Maple WPS Generator Building -completed Flood Alarm, Test, Maple WPS Generator Building -completed Fuel Transfer Pump Control Panel, Test -completed JHSC Health and Safety Inspection, Maple WPS and South Res -completed Siemens Depolox 5 Maintenance -verified analyzers after maintenance: 10:23 - PD7 Analyzer readings: Free Chlorine = 0.05 mg/L Total Chlorine = 1.72 mg/L 10:23 - PD7 Grabs: Free Chlorine = 0.04 mg/L Total Chlorine = 1.74 mg/L 10:27 - PD8 Analyzer readings: Free Chlorine = 0.02 mg/L Total Chlorine = 1.81 mg/L 10:27 - PD8 Grabs: Free Chlorine = 0.04 mg/L Total Chlorine = 1.79 mg/L -completed 10 Tonne Hoist System, Inspection -completed Sump Pump, Inspection & Maintenance -completed AC Units 1-4 (Backup) Test Run -power systems contractor on site for generator semi-annual maintenance 13:48 - transfer to generator power -activated PD7 and PD8 duties 14:50 - transfer back to utility power -no issues with generator test run -completed Diesel Generator 1 Test Run Start hours = 468.8 Stop hours = 470.0 Run time = 1.2 hours -completed Diesel Generator 2 Test Run Start hours = 482.6 Stop hours = 483.8 Run time = 1.2 hours Fuel Start = day tank 1: 596 L day tank 2: 722 L Bulk tank: 31128 L Fuel Stop = day tank 1: 481 L day tank 2: 642 L Bulk tank: 31121 L Fuel Used = 195 L -site back to normal operation -leaving PD7 pump 1 OOS due to discharge valve failing to open / close | Maple Pumping Station | 2025-11-13
WEST | November | On site for station check and to collect bacti sample wo#w11347854 Peel Total Grab: 1.90mg/L, Analyzer: 1.90mg/L Metro Total Grab: 1.85mg/L, Analyzer: 1.96mg/L Metro Free Grab: 0.04mg/L, Analyzer: 0.01mg/L Residuals North cell:@ 12:00 Free: 0.05mg/L Total 2.06mg/L SL1000 readings Total Cl: 2.03mg/L Total NH3: 0.44mg/L Free NH3: 0.08mg/L NH2Cl: 1.84mg/L Reagents - all okay No issues on site | Maple South Reservoir | 2025-11-05
WEST | November | On site for station check and to collect bacti sample wo#w11386786 Peel Total Grab: 1.90mg/L, Analyzer: 1.87mg/L Metro Total Grab: 2.02mg/L, Analyzer: 2.05mg/L Metro Free Grab: 0.04mg/L, Analyzer: 0.01mg/L Residuals North cell:@ 0900 Free: 0.05mg/L Total 2.05mg/L SL1000 readings Total Cl: 2.08mg/L Total NH3: 0.45mg/L Free NH3: 0.09mg/L NH2Cl: 1.82mg/L Nitrite 0.000mg/L Reagents - all okay No issues on site | Maple South Reservoir | 2025-11-19
WEST | November | On site for station check and to collect bacti sample wo#w11402580 Peel Total Grab: 1.80mg/L, Analyzer: 1.84mg/L Metro Total Grab: 2.07mg/L, Analyzer: 2.08mg/L Metro Free Grab: 0.05mg/L, Analyzer: 0.01mg/L Residuals North cell:@ 0915 Free: 0.05mg/L Total 2.06mg/L SL1000 readings Total Cl: 2.06mg/L Total NH3: 0.45mg/L Free NH3: 0.09mg/L NH2Cl: 1.80mg/L Reagents - all okay No issues on site Reset VFD and placed pump2 pd8 back in auto | Maple South Reservoir | 2025-11-26
WEST | November | On site for station check and to collect bacti sample wo#w11368236 Peel Total Grab: 1.82mg/L, Analyzer: 1.74mg/L Metro Total Grab: 1.91mg/L, Analyzer: 1.90mg/L Metro Free Grab: 0.04mg/L, Analyzer: 0.01mg/L Residuals North cell:@ 0845 Free: 0.05mg/L Total 2.02mg/L SL1000 readings Total Cl: 1.96mg/L Total NH3: 0.41mg/L Free NH3: 0.08mg/L NH2Cl: 1.69mg/L Nitrite 0.000mg/L Reagents - all okay No issues on site | Maple South Reservoir | 2025-11-12
WEST | November | On site for the following MARS, Ventilation & Dehumidifier, Maintenance, South Maple RES (1M) MARS, High & Low Water Level Alarm, Test, South Maple RES (2M) MARS, Siemens Depolox 5 Maintenance, South Maple RES (1M) MARS, 3 Tonne Hoist, Inspection, South Maple RES (3M) MARS, Sump Pump South Maple RES (1M) MARS, Isolating Valve Box Cover, Inspection, South Maple RES (1M) MARS, CL17 Chlorine Analyzer Maintenance, South Maple RES (5W) No issues - contractors on site | Maple South Reservoir | 2025-11-18
CENTRAL | November | Onsite for station check/collect samples- WO# W11348556 & W11347966: Sample results (14:20): Free- 0.01, Total- 2.38 * Adjusted total analyzer from 2.50 to 2.40 based on multiple grabs (2.38, 2.40, 2.38) * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Newmarket (East) Harry Walker Elevated Tank | 2025-11-05
CENTRAL | November | Onsite to complete assigned work orders- informed ROC: H/S inspection Heat trace inspection Depolox analyzer maintenance Manual valve exercise/inspection Actuated valve inspection Performed station housekeeping Station/equipment- Ok | Newmarket (East) Harry Walker Elevated Tank | 2025-11-04
CENTRAL | November | Onsite for station check/collect sample- WO# W11402398: Sample results (09:42): Free- 0.00, Total- 2.32 * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Newmarket (East) Harry Walker Elevated Tank | 2025-11-26
CENTRAL | November | Onsite for station check/collect weekly sample- WO# W11387393: Sample results (08:30): Free- 0.01, Total- 2.26 * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Newmarket (East) Harry Walker Elevated Tank | 2025-11-19
CENTRAL | November | On-site for station check, in house operational sampling and weekly micro sampling (W11368054) work orders. Grab/analyzer results as follows (mg/L): Free Cl (09:03): G: 0.02 A: 0.10 (adjusted to 0.02 based on average of 3 grabs) Total Cl (09:11): G: 2.03 A: 2.18 (adjusted to 2.03 based on average of 3 grabs) Collected samples and entered station data into shared PD excel file. Will monitor FA residuals, grab of 0.14mg/L, ET draining. No new issues found while on-site. | Newmarket (East) Harry Walker Elevated Tank | 2025-11-12
CENTRAL | November | Informed ROC. Performed annual calibration and put instruments in Cal mode while doing the tasks. Devices done were PIT, LITs and LCV. All alarms were cleared after the job. No other issues encountered. | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2025-11-05
CENTRAL | November | Informed ROC. Returned back to check again the header total chlorine analyzer. Operator Joe shut off the chemical system and calibrated again the analyzer. AIT=1.7 mg/l Grab=1.69 mg/l Observed for a while and looked stable. Operator Joe run again the chemical system and observed for a while. Analyzer reading was stable around 3.6 mg/l. Everything looked good. All alarms were cleared after the job. No other issues encountered. | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2025-11-06
CENTRAL | November | Onsite for station check: Instrumentation onsite for annual calibrations * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Chemscan reagents- Ok Station/equipment- Ok | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2025-11-07
CENTRAL | November | Onsite for station check/collect samples- WO# W11348556 & W11347966: Sample results (12:20): Free- 0.02, Total- 1.44 * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Chemscan reagents- Ok Station/equipment- Ok | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2025-11-05
CENTRAL | November | Informed ROC. Performed annual calibration and put instruments in Cal mode while doing the tasks. Devices done were AITs and FIT. All alarms were cleared after the job. No other issues encountered. | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2025-11-06
CENTRAL | November | Onsite for station check: Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Chemscan reagents- Ok Station/equipment- Ok | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2025-11-10
CENTRAL | November | Onsite for station check: Replaced header free CL17 reagents * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Chemscan reagents- Ok Station/equipment- Ok | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2025-11-03
CENTRAL | November | Onsite to receive hypo delivery * | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2025-11-04
CENTRAL | November | Onsite for station check/collect sample- WO # W11402398: Sample results (14:05): Free- 0.02, Total- 1.64 * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Chemscan reagents- Ok Station/equipment- Ok | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2025-11-26
CENTRAL | November | Onsite to complete assigned work orders- informed ROC: Chemscan outlet/header hot water flush Sump system high level test Ammonia pump inspections Performed hypo pump #4 injection point cleaning- placed hypo pump #4 back into auto duty once completed Received hypo delivery | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2025-11-25
CENTRAL | November | Onsite for station check: Replaced inlet total CL17 reagents * Replaced header total CL17 reagents * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Chemscan reagents- Ok Station/equipment- Ok | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2025-11-28
CENTRAL | November | Onsite for station check: Placed hypo p#4 in man/off- not dosing correctly- likely due to clogged injection point, will return to site to perform injection point maintenance * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Chemscan reagents- Ok Station/equipment- Ok | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2025-11-24
CENTRAL | November | On site for station check with Ryan B - Res filling 56% @ 108L/s - Entered data into PD Sheet - Check trends all okay - Checked reagents - Equipment all okay - Dosage all good - topped up ammonia tank 2 & hypo tank 1&2 - No issues found Outlet Total Cl grab @ 10:08am G: 1.33mg/L Free Cl grab @ 10:08am G: 0.04mg/L Inlet (Post-injection) Total Cl grab @ 10:02am G: 1.18mg/L A: 1.21mg/L Free Cl grab @ 10:02am G: 0.03mg/L A: 0.02mg/L Header (Pre-injection) Total Cl grab @ 10:00am G: 1.27mg/L A: 1.31mg/L Free Cl grab @ 10:00am G: 0.04mg/L A: 0.02mg/L | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2025-11-21
CENTRAL | November | Onsite for station check/collect weekly sample- WO# W11387393: Sample results (13:45): Free- 0.00, Total- 1.66 * Due to high header FA while draining, adjusted CL/AMM ratio from 3.90 to 4.00- will continue to monitor * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Chemscan reagents- Ok Station/equipment- Ok | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2025-11-19
CENTRAL | November | On-site for station check, in house operational sampling and weekly micro sampling (W11368054) work orders. Batched ammonia tank 2. Grab/analyzer results as follows (mg/L): Pre-Injection (Inlet): Free Cl (13:04): G: 0.03 A: 0.02 Total Cl (13:09): G: 1.54 A: 1.48 Post-Injection (Header): Free Cl (13:19): G: 0.09 A: 0.06 Total Cl (13:20): G: 3.52 A: 3.46 Collected samples. Entered station readings into shared PD excel file and adjusted boost Cl:AMM ratio from 3.7 to 3.8 based on Header FA grab of 0.09mg/L while draining, will monitor. No new issues found while on-site. | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2025-11-12
CENTRAL | November | Onsite to complete assigned work orders- informed ROC: Received hypo delivery * H/S inspection Hi/Lo temp test Ventilation inspection CL17 analyzer maintenance Chemscan analyzer maintenance Chemscan outlet/header hot water flush Chemical tank inspections Hypo pump inspections Performed station housekeeping 12:15: took grabs to verify header CL17 analyzers (res draining): Grabs: Free- 0.08, Total- 3.58 Analyzers: Free- 0.07, Total- 3.70 Adjusted total analyzer from 3.70 to 3.58 based on grabs (3.58, 3.58, 3.50) * Hypo pump inspections: Adjusted hypo pump #3 max flow rate from 460 to 480 (multiple drawdowns attempted) Station/equipment- Ok | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2025-11-11
CENTRAL | November | Onsite for station check: Adjusted outlet (boost) CL/AMM ratio from 3.80 to 3.90 due to high FA while res draining- will continue to monitor change * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Chemscan reagents- Ok Station/equipment- Ok | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2025-11-14
CENTRAL | November | Received hypo aprox. 710 L Ops normal | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2025-11-18
CENTRAL | November | On-site for station check and sample line flushing PMs. Informed ROC, placed chemical system man/off and placed header CL17s and chemscan analyzer in maintenance mode to flush sample lines. Flushed sample lines and returned site to normal operation. Grab/analyzer results as follows (mg/L): Pre-Injection (Header): Free Cl (09:05): G: 0.05 A: 0.03 Total Cl (09:05): G: 2.32 A: 2.24 Post-Injection (Inlet): Free Cl (09:14): G: 0.09 A: 0.06 Total Cl (09:24): G: 2.72 A: 2.46 (adjusted slope to better reflect average of 3 grabs, new Total Cl grab vs analyzer at 10:03 of: G: 2.60 A: 2.61) Checked station and equipment, no new issues found. Adjusted unit heater in hypo room. | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2025-11-17
CENTRAL | November | On site to do pms and install fiber box. We confirmed electrical on site was in good operation and box got installed. Under direction of oic | Newmarket (London) Yonge Street Elevated Tank | 2025-11-10
CENTRAL | November | Station and equipment check ET OFFLINE as per normal ops | Newmarket (London) Yonge Street Elevated Tank | 2025-11-10
CENTRAL | November | Station and equipment check ET OFFLINE as per normal ops Removed debris from yard | Newmarket (London) Yonge Street Elevated Tank | 2025-11-04
CENTRAL | November | Station and equipment check all ok Complete workorders ET remains OFFLINE as per normal ops | Newmarket (London) Yonge Street Elevated Tank | 2025-11-25
CENTRAL | November | Station and equipment check ET offline as per norm Ops ok | Newmarket (London) Yonge Street Elevated Tank | 2025-11-20
CENTRAL | November | Station and equipment check OFFLINE Re-installed insulation in exhaust fan port Admin duties Ops normal | Newmarket (Northeast) Davis Drive Elevated Tank | 2025-11-10
CENTRAL | November | Onsite for station check: Station offline * Station/equipment- Ok | Newmarket (Northeast) Davis Drive Elevated Tank | 2025-11-04
CENTRAL | November | On site to complete station check. Site secure and offline. All equipment - ok. No issues found for tower or well14. | Newmarket (Northeast) Davis Drive Elevated Tank | 2025-11-28
CENTRAL | November | Onsite for station check/collect samples- WO# W11348556 & W11347966: Sample results (09:05): Free- 0.05, Total- 2.42 * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Newmarket (Southeast) Ivsbridge Elevated Tank | 2025-11-05
CENTRAL | November | Onsite for station check/collect weekly sample- WO# W11387393: Sample results (11:10): Free- 0.08, Total- 2.64 * Adjusted total analyzer from 3.17 to 2.64 based on multiple grabs (2.64, 2.62, 2.64) * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Newmarket (Southeast) Ivsbridge Elevated Tank | 2025-11-19
CENTRAL | November | Onsite for station check/collect sample- WO# W11402398: Sample results (11:25): Free- 0.03, Total- 2.80 * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Newmarket (Southeast) Ivsbridge Elevated Tank | 2025-11-26
CENTRAL | November | -Finished the following work orders *Tested flood alarm *Exercised valves *Performed H&S inspection *Performed heat trace inspection *Performed Depolox analyzer maintenance *Tested portable generator | Newmarket (Southeast) Ivsbridge Elevated Tank | 2025-11-18
CENTRAL | November | On site to troubleshoot hihi free Cl reading Did zero cal for free chlorine and adjusted depolox analyzer to match avg grabs Free Cl Grabs @ 7:55am G:- 0.05mg/L A:- 0.17mg/L adjusted to match grabs avg to 0.05mg/L Total Cl grabs @ 8:00am G:- 2.58mg/L A:- 2.65mg/L No other issues found. | Newmarket (Southeast) Ivsbridge Elevated Tank | 2025-11-14
CENTRAL | November | On-site for station check, in house operational sampling and weekly micro sampling (W11368054) work orders. Replaced potassium iodide solution for depolox analyzer. Grab/analyzer results as follows (mg/L): Free Cl (08:28): G: 0.05 A: 0 (adjusted to 0.05 based on average of 3 grabs) Total Cl (08:29): G: 2.80 A: 2.86 Collected samples and entered station data into shared PD excel file. No new issues found while on-site. | Newmarket (Southeast) Ivsbridge Elevated Tank | 2025-11-12
CENTRAL | November | 12:06 deactivated duty 1 as per Ryan Bewley request. | Newmarket (Southeast) Ivsbridge Elevated Tank | 2025-11-13
CENTRAL | November | On-site for assigned work orders, informed ROC. Completed JHSC inspection, Tank high/low water level alarm test, dechlorination puck dispenser cleaning, general housekeeping and drain valve exercise. 300mm drain valve appears to remain seized, operated drain valve off of recirc line with dechlorination measures in place, Team Lead/Supervisor aware and will arrange future replacement of valve when tank offline. Completed depolox analyzer maintenance and verified analyzer as follows (mg/L): Free Cl (12:15): G: 0.05 A: 0.14 (adjusted to 0.05mg/L based on average of 3 grabs) Total Cl (12:23): G: 2.90 A: 2.91 No new issues found while on-site. | Newmarket (West) Bathurst Tank | 2025-11-10
CENTRAL | November | Onsite for station check/collect samples- WO# W11348556 & W11347966: Sample results (11:20): Free- 0.03, Total- 2.58 * Adjusted inlet total analyzer from 2.66 to 3.02 based on multiple grabs (3.00, 3.02, 3.02) * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Newmarket (West) Bathurst Tank | 2025-11-05
CENTRAL | November | Onsite for station check/collect weekly sample- WO# W11387393: Sample results (12:32): Free- 0.05, Total- 2.66 * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Newmarket (West) Bathurst Tank | 2025-11-19
CENTRAL | November | Onsite for station check/collect sample- WO# W11402398: Sample results (12:40): Free- 0.09, Total- 2.72 * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Newmarket (West) Bathurst Tank | 2025-11-26
CENTRAL | November | Onsite for station check: SCADA OIT screen not working- informed PCS * Station/equipment- Ok | Newmarket Kirby Pumping Station | 2025-11-10
CENTRAL | November | Onsite for station check: Station/equipment- Ok | Newmarket Kirby Pumping Station | 2025-11-07
CENTRAL | November | Informed ROC. Performed annual calibration and put instruments in Cal mode while doing the tasks. Devices done were FIT, PITs, LIT and LCV. All alarms were cleared after the job. No other issues encountered. | Newmarket Kirby Pumping Station | 2025-11-05
CENTRAL | November | Onsite for station check: Station/equipment- Ok | Newmarket Kirby Pumping Station | 2025-11-03
CENTRAL | November | Flow testing on pumps Manually open flow valve to try and increase flow, 3l/s improvement | Newmarket Kirby Pumping Station | 2025-11-21
CENTRAL | November | On-site for station check, pump inspections and to assist CMS with fire pump tests. Placed FCV1 in D2 to close valve. Placed chemical system man/off at NMTKKC to avoid chemical dosing issues during pump tests. Placed AUPSOH pumps 3/4 man/off and ran/inspected NMPSKC Pumps 1/2. Ran P5/P6 for CMS Lee Ferguson and Tyler Zimmerman-Jones to observe flow rates/system conditions. Ran/inspected Pumps 3/4 and returned site to normal operation. Returned AUPSOH P3/4 to auto. Returned NMTKKC to normal operation. Entered station readings into shared PD excel file. Checked station and equipment, no new issues found. Informed ROC. | Newmarket Kirby Pumping Station | 2025-11-21
CENTRAL | November | Onsite for station check: Station/equipment- Ok | Newmarket Kirby Pumping Station | 2025-11-24
CENTRAL | November | Onsite to complete assigned work orders and monitor generator performance during planned outage- informed ROC: Generator test run (generator running all day for planned outage): Start time- 08:20 Stop time- 15:20 Start hours- 22.65 Stop hours- 29.55 Start fuel- 948 L (94.8 cm) Stop fuel- 899 L (90.2 cm) Generator operating stats: Speed- 1800 rpm Volts- 601 Hertz- 60 Oil pressure- 37 psi Coolant temp- 170 F H/S inspection High/Low temp test Ventilation inspection PRV inspection Flow control valve inspection Performed station housekeeping At 15:10- notified by NT Power that the work has been completed- good to transfer station back to hydro power At 15:12- transferred station back to hydro power as per normal operations- informed ROC At 15:20- generator shutdown- generator back in auto as per normal operations- no issues during generator run Station/equipment- Ok | Newmarket Kirby Pumping Station | 2025-11-14
CENTRAL | November | Onsite for station check: Onsite to assist CPD and NT Power with planned station power outage- informed ROC: At 08:20- transferred station to generator power to assist with project. Generator pre test inspection completed prior to transfer- no issues. Generator start hours: 22.65 Generator start fuel: 948 L (94.8 cm) Once planned outage work completed- will return station to hydro power- informed ROC Station check completed Station/equipment- Ok | Newmarket Kirby Pumping Station | 2025-11-14
CENTRAL | November | On-site for station check. Entered station data into shared PD excel file. Adjusted unit heaters. Checked station and equipment, no new issues found. | Newmarket Kirby Pumping Station | 2025-11-17
CENTRAL | November | Station and equipment check Took grabs and in-house iron sample @ 10:10 am Treated Total: 2.92 mg/l Treated Free: 0.13 mg/l No adjustments required, all other readings entered in PD sheets shared online folder Changed CL2 cylinders with Joe D, right bank Chemicals/reagents ok Ops normal | Newmarket Well 1 & 2 | 2025-11-10
CENTRAL | November | Station and equipment check Took grabs @ 9:30 am Treated Total: 2.90 mg/l Treated Free: 0.10 mg/l Analyzer Total: 3.01 mg/l Analyzer Free: 0.14 mg/l *standardized Total analyzer to match grabs Chemicals/reagents ok All other readings entered into PD sheets Ops normal | Newmarket Well 1 & 2 | 2025-11-07
CENTRAL | November | Station and equipment check Take weekly BacT samples W11347680 and grabs @ 9:15 am (running) Treated Total: 2.87 mg/l Treated Free: 0.12 mg/l No adjustments needed Chemicals/reagents ok Ops normal | Newmarket Well 1 & 2 | 2025-11-05
CENTRAL | November | Station and equipment check Took grabs and in-house operational samples at 10:15 am Treated Total: 2.95 mg/l Treated Free: 0.13 mg/l pH: 8.08 All other readings entered into PD sheets shared online folder Topped up Ammonia Tank 1 Chemicals/reagents ok Ops normal | Newmarket Well 1 & 2 | 2025-11-03
CENTRAL | November | Topped up NaSi day tanks 698 to 992L. | Newmarket Well 1 & 2 | 2025-11-04
CENTRAL | November | On site to top up silicate Before 723.78L After 1085L No issues found | Newmarket Well 1 & 2 | 2025-11-25
CENTRAL | November | Station and equipment check Take weekly BacT sample W 11403061 and grabs @ 9:50 am Treated Total: 2.81 mg/l Treated Free: 0.13 mg/l All other readings on PD sheets shared online folder Top up ammonia tank 2 Ops normal | Newmarket Well 1 & 2 | 2025-11-26
CENTRAL | November | Station and equipment check Take weekly BacT sample and grabs @ 9:50 am Treated Total: 2.90 mg/l Treated Free: 0.14 mg/l Chemicals/reagents ok Ops normal | Newmarket Well 1 & 2 | 2025-11-19
CENTRAL | November | Onsite to complete Maximo workorders Informed ROC (Connor) of ongoings Placed wells manual OFF Completed w/o?s with no issues Placed wells back to Auto, duty not active Ops normal | Newmarket Well 1 & 2 | 2025-11-20
CENTRAL | November | Station and equipment check Took grabs and in-house iron sample @ 8:55 am Treated Total: 3.00 mg/l Treated Free: 0.14 mg/l No adjustments required Chemicals/reagents ok Ops normal | Newmarket Well 1 & 2 | 2025-11-24
CENTRAL | November | Station and equipment check Took grabs @ 8:45 am Treated Total: 2.99 mg/l Treated Free: 0.12 mg/l No adjustments required All other readings on PD sheets Chemicals/reagents ok Ops normal | Newmarket Well 1 & 2 | 2025-11-21
CENTRAL | November | On site to change chlorine cylinders with Donald M. No issues found | Newmarket Well 1 & 2 | 2025-11-27
CENTRAL | November | On site to complete station check with Ryan B. - Wells duty inactive on arrival - Entered data into PD sheet - Reagents all good - changed treated total CL17 reagents - Trends all good - Equipment all okay - Dosage all good - No issues found Influent free Cl @ 1:42pm G: 2.42mg/L A: 2.45mg/L Effluent free Cl @ 1:42pm G: 0.10mg/L A: 0.08mg/L Treated free Cl @ 1:43pm G: 0.08mg/L A: 0.08mg/L Treated total Cl@ 1:43pm G: 2.56mg/L A: 2.48mg/L Changed silicate pump max flow based on draw down P1- 215 to 200ml/min | Newmarket Well 1 & 2 | 2025-11-28
CENTRAL | November | Station and equipment check Take weekly BacT samples W11368832 and grabs @ 9:10 am Treated Total: 2.91 mg/l Treated Free: 0.10 mg/l Analyzer Total: 2.86 mg/l Analyzer Free: 0.14 mg/l Topped up Ammonia tank 2 Chemicals/reagents ok Changed CL2:ammonia ratio from 3.90 - 3.85 will monitor Ops normal | Newmarket Well 1 & 2 | 2025-11-12
CENTRAL | November | On site to top up silicate with Benson S under training. No issues found | Newmarket Well 1 & 2 | 2025-11-18
CENTRAL | November | On site to complete station check. - Wells duty active on arrival - Entered data into PD sheet - Reagents all good - Trends all good - Equipment all okay - Dosage all good - No issues found Influent free Cl @ 9:57am G: 2.50mg/L A: 2.56mg/L Effluent free Cl @ 9:58am G: 2.42mg/L A: 2.47mg/L Treated free Cl @ 10:00am G: 0.13mg/L A: 0.14mg/L Treated total Cl@ 10:00am G: 2.82mg/L A: 2.85mg/L | Newmarket Well 1 & 2 | 2025-11-14
CENTRAL | November | Station and equipment check Take in-house iron sample and grabs @ 10:20 am (running) Treated Total: 2.90 mg/l Treated Free: 0.10 mg/l Analyzer Total: 2.81 mg/l Analyzer Free: 0.12 mg/l *standardized Total analyzer to match grabs Changed CL17 reagents ?effluent free? Topped up ammonia tank 1 Chemicals/reagents ok Ops normal | Newmarket Well 1 & 2 | 2025-11-17
CENTRAL | November | Onsite to complete monthly maximo workorders Informed ROC (Carter D) of ongoings Cleaned all CL17 analyzers Changed reagents "treated free" analyzer Hot water flush both Silicate lines (Full) Ammonia drawdown complete, accurate on scada Chlorine system inspection visual ok Empty garbages Top up Well oil reservoir Ops normal | Newmarket Well 1 & 2 | 2025-11-18
CENTRAL | November | On site to top up silicate with Benson S under training. Jason G on site, no other issues found. | Newmarket Well 1 & 2 | 2025-11-18
CENTRAL | November | drop off 9 bags of ammonia admin duties Station ops normal | Newmarket Well 1 & 2 | 2025-11-12
CENTRAL | November | Onsite for station check: Station offline * Station/equipment- Ok | Newmarket Well 14 | 2025-11-04
CENTRAL | November | On-site for flushing of main. Flushed approximately 122m3 with dechlorination measures, Total Cl grab at 10:50 1.75mg/L. Adjusted heater in NMETDD hut, temp alarm cleared. | Newmarket Well 14 | 2025-11-20
CENTRAL | November | Flushed main total of 92m3 with dechlorination, total Cl grab at 14:30 1.53mg/L. | Newmarket Well 14 | 2025-11-13
CENTRAL | November | On-site to investigate Cl2 room low temperature alarm. Adjusted unit heater and cleared alarm, no new issues. | Newmarket Well 14 | 2025-11-12
CENTRAL | November | On-site for station check and housekeeping work orders of NMETDD and NMW14. Sites remain offline. | Newmarket Well 14 | 2025-11-17
CENTRAL | November | Station and equipment check Took grabs and in-house iron sample @ 8:40 am Treated Total: 3.23 mg/l Treated Free: 0.12 mg/l Chemicals/reagents ok Installed insulation on exhaust fan access port in chlorine room (exhaust fan removed) All other readings entered into PD sheets online Ops normal | Newmarket Well No. 15 | 2025-11-07
CENTRAL | November | Station and equipment check Take grabs and in-house iron sample @ 8:25 am (running) Treated Total: 3.20 mg/l Treated Free: 0.10 mg/l Analyzer Total: 3.29 mg/l Analyzer Free: 0.14 mg/l *standardized analyzer to match grabs on Total CL17 Changed chlorine cylinder w/ Joe D Chemicals/reagents ok Ops normal | Newmarket Well No. 15 | 2025-11-10
CENTRAL | November | Adjusted silicate dose from 12 mg/L to 11 mg/L, this is to bring closer to our bench testing in 2016/2017 We will do dissolved iron samples to monitor the change | Newmarket Well No. 15 | 2025-11-03
CENTRAL | November | Onsite to complete Maximo workorders Informed ROC (Ethan U) of ongoings Completed ammonia pump drawdown and changed rates to the following P1= 98 ml/min P2= 100 ml/min JHSC inspection completed no issues Exhaust valve maintenance complete Cleaned ALL CL17s and Turbidimeter cleaned all site tubes and "y" screens CL2 Leak detector test/halogen - all ok Chemical system inspection All complete Ops normal | Newmarket Well No. 15 | 2025-11-04
CENTRAL | November | Station and equipment check Take weekly BacT sample W11347680 grabs and in-house iron sample @ 8:20 am Treated Total: 3.34 mg/l Treated Free: 0.14 mg/l CL2:Ammonia ratio changed from 4.00 - 3.90 All other readings entered in PD sheets shared online folder Chemicals/reagents ok Ops normal | Newmarket Well No. 15 | 2025-11-05
CENTRAL | November | Station and equipment check Took grabs @ 9:35 am and in-house operational samples Treated Total: 3.25 mg/l Treated Free: 0.13 mg/l All other readings entered into PD sheets shared online folder Topped up ammonia tank #2 Chemicals/reagents ok Ops normal | Newmarket Well No. 15 | 2025-11-03
CENTRAL | November | Station and equipment check Take weekly BacT sample W11403061 and grabs @ 9:10 am Treated Total: 3.44 mg/l Treated Free: 0.15 mg/l All other readings on PD sheets Chemical/reagents ok Ops normal | Newmarket Well No. 15 | 2025-11-26
CENTRAL | November | Assisted Jason Garnett with station check. Adjusted NaSi P1 max flow from 270 to 280mL/min, target NaSi dose 10mg/L and calculated dose 12mg/L since last station check, will monitor. | Newmarket Well No. 15 | 2025-11-25
CENTRAL | November | Onsite to receive chlorine delivery Change chlorine cylinder w/ Ben H (Left side) Started well in manual, will return for station check | Newmarket Well No. 15 | 2025-11-24
CENTRAL | November | Station and equipment check Take weekly BacT sample and grabs @ 8:45 am Treated Total: 3.10 mg/l Treated Free: 0.13 mg/l Also collected in-house iron sample Chemicals/reagents ok Ops normal | Newmarket Well No. 15 | 2025-11-19
CENTRAL | November | Back onsite to investigate high turbidity Both silicate pumps are plumbed to one injection point, flushed lines with hot water and pulled injection point 2 and cleaned Also pulled and cleaned foot valves P1 should be ok, if high turbidity comes in with p2 possible roller replacement needed or tube Both in auto | Newmarket Well No. 15 | 2025-11-19
CENTRAL | November | Onsite with Ryan B for Station and equipment check Took grabs and in-house iron sample @ 9:10 am Treated Total: 3.30 mg/l Treated Free: 0.14 mg/l All other readings on PD sheets shared online folder Chemicals/reagents ok Ops normal | Newmarket Well No. 15 | 2025-11-25
CENTRAL | November | On site to top up silicate Before 241L After 380L No issues found | Newmarket Well No. 15 | 2025-11-25
CENTRAL | November | On site to complete station check. Verified analyzers: Influent Free Chlorine @ 9:29 Grab: 2.84 mg/L Analyzer: 2.85 mg/L Effluent Free Chlorine @ 9:20 Grab: 2.98 mg/L Analyzer: 2.92 mg/L Treated Free Chlorine @ 9:15 Grab: 0.15 mg/L Analyzer: 0.15 mg/L Treated Total Chlorine @ 9:15 Grab: 3.44 mg/L Analyzer: 3.39 mg/L -Entered data into PD sheet -Checked trends -Topped up mineral oil for well 15 | Newmarket Well No. 15 | 2025-11-28
CENTRAL | November | On site to install conduit into SCADA panel for Yorknet project. | Newmarket Well No. 15 | 2025-11-20
CENTRAL | November | Donald M & I changed chlorine cylinder. No issues found | Newmarket Well No. 15 | 2025-11-27
CENTRAL | November | Station and equipment check Took grabs @ 8:15 am (running) Treated Total: 3.18 mg/l Treated Free: 0.14 mg/l Influent Free: 2.82 mg/l *standardized influent analyzer to match grabs, Chemicals/reagents ok, placed well manual off to save on CL2 delivery expected Monday Station ops normal | Newmarket Well No. 15 | 2025-11-21
CENTRAL | November | Onsite to take another in-house iron sample Test chlorine leak alarm - no issues Informed ROC (Adam B) Ops normal | Newmarket Well No. 15 | 2025-11-20
CENTRAL | November | On site to complete station check. Got hi FNH3 so did the DD for ammonia pumps but they are working fine, increase Cl:NH3 ratio from 3.90 to 4.10mg/L - will monitor - Well duty active on arrival - Entered readings into Process data Sheet - Reagents all good - Trends all good - Dosage all okay - Equipment all okay - No new issues found Influent free Cl @ 9:09am G: 2.80mg/L A: 2.89mg/L Effluent free Cl @ 9:12am G: 2.76mg/L A: 2.76mg/L Treated free Cl @ 9:14am G: 0.12mg/L A: 0.15mg/L Treated total Cl@ 9:14am G: 3.20mg/L A: 3.26mg/L | Newmarket Well No. 15 | 2025-11-14
CENTRAL | November | Station and equipment check Took grabs and in-house iron sample @ 8:35 am (running) Treated Total: 3.00 mg/l Treated Free: 0.10 mg/l Analyzer Total: 3.11 mg/l Analyzer Free: 0.14 mg/l *standaedized Total analyzer to match grabs Adjusted flow on influent analyzer Topped up ammonia tank 1 Chemicals/reagents ok Ops normal | Newmarket Well No. 15 | 2025-11-17
CENTRAL | November | Onsite to troubleshoot chlorine weigh scales reading zero Upon arrival scales had already reset themselves Manually Tare left side to approximately 32 kg, last known reading. Right side has a full cylinder at 68 kg CL2 calculated dose might be inaccurate at tomorrow station check. Replenished CL17 reagents on both treated analyzers (free/total) Well back in auto Ops normal | Newmarket Well No. 15 | 2025-11-11
CENTRAL | November | Station check Take weekly BacT sample W11368832, in-house iron sample and grabs @ 8:25 am (running) Treated Total: 3.11 mg/l Treated Free: 0.12 mg/l Analyzer Total: 3.08 mg/l Analyzer Free: 0.14 mg/l No adjustments required Chemicals/reagents ok Ops normal | Newmarket Well No. 15 | 2025-11-12
CENTRAL | November | On site to top up silicate with Benson S under training. No issues found | Newmarket Well No. 15 | 2025-11-18
CENTRAL | November | Station and equipment check Took grabs and in-house iron sample @ 11:20 am Treated Total: 2.69 mg/l Treated Free: 0.12 mg/l No adjustments required Changed CL17 reagent ?Effluent free? Chemicals/reagents ok *Joe D deactivated duty via scada at approximately 11:24 am Ops normal | Newmarket Wells 13-16 | 2025-11-10
CENTRAL | November | Station and equipment check Took grabs and in-house iron sample @ 10:25 am Treated Total: 2.70 mg/l Treated Free: 0.10 mg/l Analyzer Total: 2.82 mg/l Analyzer Free: 0.13 mg/l *standardized Total analyzer to match grabs Chemicals/reagents ok All other readings entered in PD sheets Ops normal | Newmarket Wells 13-16 | 2025-11-07
CENTRAL | November | Station and equipment check Took grabs and operational samples at 2:45 pm (Ran in manual for 1 hour) Treated Total: 2.83 mg/l Treated Free: 0.13 mg/l Adjusted CL2/Ammonia ratio to 4.3 (will monitor at next station check with wells running longer) All other readings entered on PD sheets shared folder Chemicals/reagents ok | Newmarket Wells 13-16 | 2025-11-03
CENTRAL | November | Adjusted silicate dose from 16 mg/L to 15 mg/L, this is to bring closer to our bench testing in 2016/2017 We will do dissolved iron samples to monitor the change | Newmarket Wells 13-16 | 2025-11-03
CENTRAL | November | Station and equipment check Take weekly BacT samples W11347680, grabs and in-house iron sample @ 10:05 am (running) Treated Total: 2.73 mg/l Treated Free: 0.13 mg/l No adjustments needed All other readings entered into PD sheets shared online folder Chemicals/reagents ok Ops normal | Newmarket Wells 13-16 | 2025-11-05
CENTRAL | November | Station and equipment check Take weekly BacT sample W11403061 and grabs @ 10:30 am Treated Total: 2,77 mg/l Treated Free: 0.10 mg/l All other readings on PD sheets shared online folder Chemicals/reagents ok | Newmarket Wells 13-16 | 2025-11-26
CENTRAL | November | On site to top up silicate. No issues found Before 2941.30L After 3709.54L | Newmarket Wells 13-16 | 2025-11-25
CENTRAL | November | Station and equipment check Take grabs and in-house iron sample @ 10:15 am Treated Total: 2.90 mg/l Treated Free: 0.10 mg/l All other readings on PD sheets Changed reagents CL17 ?influent free? Topped up ammonia tank 2 Ops normal | Newmarket Wells 13-16 | 2025-11-24
CENTRAL | November | Station and equipment check Take weekly BacT sample and grabs @ 10:30 am Treated Total: 2.80 mg/l Treated Free: 0.12 mg/l Changed reagent CL17 treated free analyzer Chemicals ok Ops normal | Newmarket Wells 13-16 | 2025-11-19
CENTRAL | November | Station and equipment check Took grabs @ 10:30 am (running) Treated Total: 2.75 mg/l Treated Free: 0.12 mg/l Chemicals/reagents ok All other readings on PD sheets Ops normal | Newmarket Wells 13-16 | 2025-11-21
CENTRAL | November | On site to complete station check with Ryan B - Wells duty inactive when arrived - Entered readings into PD sheets - Changed Treated Total Cl CL17 analyzer reagents - Trends all good - Equipment all okay - No issues found Influent free Cl @ 1:04pm G: 2.42mg/L A: 2.42mg/L Effluent free Cl @ 1:04pm G: 0.08mg/L A: 0.10mg/L Treated free Cl @ 1:05pm G: 0.07mg/L A: 0.08mg/L Treated total Cl @ 1:05pm G: 1.84mg/L A: 1.83mg/L Adjusted NaSi P1 max flow from 255 to 250mL/min and NaSi P2 max flow from 290 to 280mL/min based on pump drawdowns. | Newmarket Wells 13-16 | 2025-11-28
CENTRAL | November | Onsite to complete Maximo workorders Informed ROC (Adam B) of ongoings No issues during work Ops normal | Newmarket Wells 13-16 | 2025-11-11
CENTRAL | November | Station and equipment check Take weekly BacT samples W11368832, in-house iron sample and grabs @ 10:30 am (well 16 running) Treated Total: 2.74 mg/l Treated Free: 0.13 mg/l Chemicals/reagents ok Ran well 13 in manual to get raw sample and rotated duties, 13 now duty 1 placed back to auto Ops normal | Newmarket Wells 13-16 | 2025-11-12
CENTRAL | November | On site to top up silicate with Benson S under training, no issues found. | Newmarket Wells 13-16 | 2025-11-18
CENTRAL | November | On site to complete station check - Well 13 running when arrived - Entered readings into PD sheets - Reagents all good - Trends all good - Equipment all okay - Dosage all good - Topped up NH3 TK1 - No issues found Influent free Cl @ 1:13pm G: 2.64mg/L A: 2.70mg/L Effluent free Cl @ 1:14pm G: 2.40mg/L A: 2.34mg/L Treated free Cl @ 1:16pm G: 0.16mg/L A: 0.13mg/L Treated total Cl @ 1:16pm G: 2.68mg/L A: 2.64mg/L | Newmarket Wells 13-16 | 2025-11-14
CENTRAL | November | Attending site to check Total chlorine analyzer (W11449637). Analyzer has 1 low reading every day or so. Could not find any obvious issues with device. Lubricated peristaltic pump parts and cleaned out colorimeter reagent/buffer injection port. Will monitor SCADA trends to determine if further action is required. ROC was notified before and after maintenance work. Associated alarms were cleared. | Newmarket Wells 13-16 | 2025-11-18
CENTRAL | November | Station and equipment check Took grabs and in-house iron sample @ 11:25 am (running) Treated Total: 2.77 mg/l Treated Free: 0.14 mg/l Analyzer Total: 2.66 mg/l Analyzer Free: 0.14 mg/l *standardized Total analyzer to match grabs Chemicals/reagents ok Changed chlorine cylinders w/ Divya P (left bank) Ops normal | Newmarket Wells 13-16 | 2025-11-17
CENTRAL | November | Onsite to complete Maximo workorders No changes to operations needed Station ops normal | Newmarket Wells 13-16 | 2025-11-13
WEST | November | **disregard entry was meant for woodland acres** On site for the following RHPSWA, JHSC Health and Safety Inspection, Woodland Acres Reservoir and WPS (1M) RHPSWA, Hoist System Inspection, Woodland Acres WPS (3M) KCETDS, King City Dufferin St Elevated Tank, Station Check, (1W) RHPSWA, Ventilation System Inspection, Woodland Acres WPS (1M) RHPSWA, PRV Valve Inspection, Woodland Acres, WPS(1M) RHPSWA, Pump & Motor Inspection, Woodland Acres WPS RHPSWA, Check Valve Service & Inspection, Woodland Acres WPS (3M) RHPSWA, Flood Alarm Test, Woodland Acres WPS (1M) RHPSWA, Discharge Valve & Actuator Exercise & Inspection, Woodland Acres WPS (1M) RHRSWA, Sump Pit System Inspection, Woodland Acres RES (1M) RHRSWA, Flood Alarm Test, Woodland Acres RES (1M) RHRSWA, High/Low Temperature Alarm Test, Woodland Acres RES (1M) RHRSWA, Dehumidifier Inspection & Cleaning, Woodland Acres RES (1M) RHRSWA, Manual Valve Exercise, Woodland Acres RES (?M) RHRSWA, Actuated Valve Exercise & Inspection, Woodland Acres RES (1M) RHRSWA, External Venting Screens Inspection, Woodland Acres RES (1M) RHRSWA, Air Valve Flush, Woodland Acres RES (3M) No issues | Nobleton Booster Pumping Station | 2025-11-06
WEST | November | Complete station check. No issues, pump running. | Nobleton Booster Pumping Station | 2025-11-10
WEST | November | Complete station check. No issues, pump running. | Nobleton Booster Pumping Station | 2025-11-03
WEST | November | Station Check (no issues found) Pump running | Nobleton Booster Pumping Station | 2025-11-28
WEST | November | Station check (no issues) | Nobleton Booster Pumping Station | 2025-11-21
WEST | November | Conducted station check. No issues. | Nobleton Booster Pumping Station | 2025-11-17
WEST | November | Station check and JHS inspection no issues | Nobleton Booster Pumping Station | 2025-11-14
WEST | November | Depolox -sample flow had slowed over the night, adjusted flow and normal readings returned -topped up both reagents 11:00 Verified (mg/L) Free: Grab 1.05, A 1.01 Total: Grab 1.33, 1.35 | Nobleton North Elevated Tank | 2025-11-06
WEST | November | Tower placed back in service Opened both manual valves in valve house Altitude valve (opened both 3/8" ball valve on bonnet, closed solenoid bypass 3/8" ball valve, opened 3/8" ball valve to surge springs) 14:30 Verified Depolox (mg/L) Free: Grab 1.40, A 1.43 Total: Grab 1.98, A 2.80 (adjusted to match grabs) | Nobleton North Elevated Tank | 2025-11-05
WEST | November | On site to isolate NBET27 from system using valves in pipe gallery. A new isolation valve will be tied into WM outside of NBET27 on November 4th. Notified ROC of NBET27 isolation from system and associated alarms etc. Isolated NBET27 inlet / outlet BFVs. Isolated LCV1 piloting valves to Bonnet, to hold position. LCV1 piloting appears to be setup to only be used as check valve, will inspect after WM valve work is completed. Residuals: mg/L 1010 A: FCl 0.81 tcl 1.47 G: FCl 1.24 tcl 1.31 Unable to span calibrate cl2 analyzer due to isolation of system analyzer (sample line pulls from isolated inlet/outlet section of piping). Analyzer can be calibrated after WM work is completed. NBET27 placed in ?offline? mode on SCADA. | Nobleton North Elevated Tank | 2025-11-03
WEST | November | Station Check (ET isolated to allow a connection to be installed) Data input to PWQ 8:50 Chlorine Grab Residuals (mg/l) Free: 1.21 Total: 1.32 8:55 #11347732 weekly sample taken from Outlet tap | Nobleton North Elevated Tank | 2025-11-05
WEST | November | 12:20 Responding to a high free residual. Zero cal. performed Free: Grab 1.54mg/l, A 1.70 (adjusted to match grabs) Total: Grab 1.80mg/l, A 1.81mg/l | Nobleton North Elevated Tank | 2025-11-21
WEST | November | Total chlorine analyzer-Put grit on the analyzer. | Nobleton North Elevated Tank | 2025-11-27
WEST | November | Informed ROC. Onsite to perform annual calibration/maintenance. Used the calibration mode during the work. Devices were done as below: Free and Total AIT, TWR_PIT, TWR_LIT, inlet and outlet FIT, TWR_LCV. Informed ROC before and after calibration of PIT, took a permission to close TWR_LCV from Cole. ROC closed and opened LCV and put it back to auto after calibration. Informed Cole about valve closing issue. Took a multiple grab samples and adjusted analyzers accordingly. Free grab - 1.87mg/l, AL Free AIT - 1.86 mg/l Total grab - 2.15 mg/l , AL Total AIT - 2.15 mg/l Put everything back in service. All the related alarms were cleared. No issues. Informed ROC, armed the building and left the site. | Nobleton North Elevated Tank | 2025-11-25
WEST | November | Work completed November 26th Responded to High Free Residual readings on Depolox Performed zero cal 15:30 Free Grab 1.65 (adjusted to match) Total grab 2.00, A 2.13 (adjusted to match) | Nobleton North Elevated Tank | 2025-11-28
WEST | November | 14:20 Responding to Depolox (free higher than total) Zero Cal Free Grab: 1.57mg/l Total Grab 1.84, A 1.78mg/l | Nobleton North Elevated Tank | 2025-11-28
WEST | November | Station Check (no issues found) Input data to PWQ 10:05 Verified Depolox (mg/l) Free: Grab 1.55, A 1.26 (adjusted to match grabs) Total: Grab 1.82, A 1.90 10:15 #11402314 weekly sample | Nobleton North Elevated Tank | 2025-11-26
WEST | November | Station Check (no issues found) Input data to PWQ 12:40 Verified Depolox (mg/l) Free: Grab 1.56, A 1.94(adjusted to match grabs) Total: Grab 1.71, A 1.74 (re-attached small tubing on 4way valve (that blew off)) 1:35 #11386664 bact. and operational samples | Nobleton North Elevated Tank | 2025-11-19
WEST | November | Onsite to complete work orders Tested portable generator with no issues Did monthly maintenance on cl2 analyzer Electrolyte and grit ok Grabs Total analyzer 1.60 grab 1.54 Free analyzer 1.61 grab 1.47 Adjusted free analyzer Free cl2 value climbed and adjusted again | Nobleton North Elevated Tank | 2025-11-13
WEST | November | Station Check (no issues found) Input data to PWQ 9:50 Verified Depolox (mg/L) Free: Grab 1.43, A 0.79 (adjusted to match grabs) Total: Grab 1.66, A 1.27 (adjusted to match grabs) adjusted analyzer flow 10:05 #11367970 bact. sample | Nobleton North Elevated Tank | 2025-11-12
WEST | November | Station Check (no issues found) Input data to PWQ 12:25 Verified Depolox (mg/L) Free: Grab 1.55, A 1.25 (adjusted to match grabs) Total: Grab 1.70, A 1.51 (adjusted to match grabs) 12:45 #11347732 weekly samples | Nobleton South Elevated Tank | 2025-11-05
WEST | November | Station Check (no issues found) Input data to PWQ 9:25 Verified Depolox (mg/l) Free: Grab 1.60, A 1.13 (adjusted to match grabs) Total: Grab 1.90, A 2.00 (adjusted to match grabs) 9:35 #11402314 weekly bact. sample | Nobleton South Elevated Tank | 2025-11-26
WEST | November | Station Check (no issues found) Input data to PWQ 12:10 Verified Depolox (mg/l) Free: Grab 1.14, A 1.16 Total: Grab 1.89, A 1.98 12:20 #11386664 Bact. and operational samples | Nobleton South Elevated Tank | 2025-11-19
WEST | November | Onsite to complete work orders Exercised manual valves Completed jhsc with no issues Tested portable generator with no issues Completed cl2 analyzer Electrolyte and grit ok Reagents ok Grabs Free analyzer 0.71 grab 1.46 Total analyzer 1.78 grab 1.79 Adjusted free analyzer | Nobleton South Elevated Tank | 2025-11-13
WEST | November | Station Check (no issues found) Input data to PWQ 9:10 Verified Depolox (mg/l) Free: Grab 1.27, A 0.99 (adjusted to match grabs) Total: Grab 1.72, A 1.78 (topped up distilled/KI & Acetate reagents) 9:20 #11367970 bact. sample 14:40 Depolox Free spike Free: Grab 1,76, A 3.5 (adjusted to match grabs) Total: Grab 2.20, A 2.20 (no change) | Nobleton South Elevated Tank | 2025-11-12
WEST | November | Depolox 9:15 Zero Cal Free 4.10 mg/l after zeroing Standard calibrated to 1.12mg/l to match grabs (will monitor) Sump pump float failed (maint. responding with new) 12:00 new sump installed | Nobleton South Elevated Tank | 2025-11-14
WEST | November | In to complete station check and top up silicate tank. Enter data into PWQ. Span calibrate influent analyzer from 1.89 to 1.83mg/L based on grabs. Replace Influent/effluent cl17 reagents. Topped up silicate tank from 46 to 67cm. NTU spiked interlocking well, may have been related to filling Si tank. NTU value returned to normal after spike, reset w2 and monitor startup. Influent cl17 residual appeared to spike before restarting well 2 (close to reagent replacement). Reading was unrealistically high for too long without increased dosing to match; - default calibrate Influent cl17, bringing gain to 1.0 and take grab. Influent cl17: mg/L G: FCl 2.26 A: FCl 2.28 | Nobleton Well 2 | 2025-11-07
WEST | November | On site for station check. Collected in house iron samples. Collected Raw PH @10:40hrs: 7.79 Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 1.79mg/l FCL Analyzer: 1.82mg/l Effluent Free Cl2 grab residual: 1.77mg/l FCL Analyzer: 1.78mg/l Effluent Total Cl2 grab residual: 2.11mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Nobleton Well 2 | 2025-11-10
WEST | November | Attending site to replaced faulty push buttons on Effluent chlorine analyzer (W11424717). Buttons were replaced and analyzer calibration was verified using DPD colorimeter. Calibration mode was used and associated alarms were cleared once work was completed. ROC was notified before and after maintenance work. | Nobleton Well 2 | 2025-11-10
WEST | November | #11341898 Turb #11341739 Press. relief #11344132 deep well #11342169 JHS #11343951 Silicate sys. #11243999 chlorine sys #11364205 dechlor. #11383202 flush #11342097 CL17 maint. 12:30 Verified CL17s (mg/L) Influent: Free Grab 1.68, A 1.73 Effluent: Free Grab 1.40, A 1.48 Total Grab 1.69 Effluent CL17 analyzer keypad not working (generated w/o #11424717) | Nobleton Well 2 | 2025-11-06
WEST | November | In to complete station check. Enter data into PWQ. Analyzer reagent levels good. No issues. | Nobleton Well 2 | 2025-11-03
WEST | November | Station Check (no issues found) Input data to PWQ 11:25 Verified CL17s (mg/l) Influent: Free Grab 1.80, A 1.85 Effluent: Free Grab 1.71, A 1.76 Total Grab: 2.07 11:20 #11347732 weekly samples | Nobleton Well 2 | 2025-11-05
WEST | November | Restarted the Operator Interface Terminal due to Windows Updates. Notified the Remote Operations Center. Well was off during the restart process. | Nobleton Well 2 | 2025-11-24
WEST | November | Station Check (no issues found) Input data to PWQ 11:05 Verified CL17s (mg/l) Influent: Grab 1.95, A 1.96 Effluent: Grab 1.86, A 1.92 Total: Grab 2.50 11:15 #11386664 bact. samples | Nobleton Well 2 | 2025-11-19
WEST | November | Station Check (no issues found) Input data to PWQ 11:20 Verified CL17 (mg/L) Influent: Free Grab 1.80, A 1.84 Effluent: Free Grab 1.63, A 1.68 Total Grab 1.92 | Nobleton Well 2 | 2025-11-21
WEST | November | Station Check (no issues found) Input data to PWQ 13:06 Verified CL17s (mg/l) Influent: Free Grab 2.05, A 1.98 Effluent: Free Grab 1.74, A 1.74 Total Grab 2.07 | Nobleton Well 2 | 2025-11-28
WEST | November | Station Check (no issues found) Input data to PWQ 10:30 Verified CL17s (mg/L) Influent: Free Grab 1.86, A 1.85 Effluent: Free Grab 1.78, A 1.81 Total Grab 2.52 #11341855 CL2 leak | Nobleton Well 2 | 2025-11-25
WEST | November | Entry made in error (correction added to Nobleton North Tower) Responding to high free residual readings on Depolox performed a Zero Cal 15:30 Free Grab 1.65 (adjusted to match) Total Grab 2.00, A 2.13 (adjusted to match) | Nobleton Well 2 | 2025-11-26
WEST | November | Station Check (no issues found) Input data to PWQ 1:30 Verified CL17s(mg/l) Influent: Free Grab 1.98, A 1.92 Effluent: Free Grab 1.80, A 1.86 Total Grab 2.52 1:40 #11402314 weekly samples | Nobleton Well 2 | 2025-11-26
WEST | November | Chlorine cylinder change with Jacob (B side) | Nobleton Well 2 | 2025-11-13
WEST | November | On site for station check. Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 1.82mg/l FCL Analyzer: 1.78mg/l Effluent Free Cl2 grab residual: 1.83mg/l FCL Analyzer: 1.80mg/l Effluent Total Cl2 grab residual: 2.16mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Nobleton Well 2 | 2025-11-17
WEST | November | Station Check (no issues found) Input data to PWQ 14:05 Verified CL17s (mg/L) Influent: Free Grab 1.95, A 1.99 Effluent: Free Grab 1.76, A 1.71 Total Grab 2.06 | Nobleton Well 2 | 2025-11-14
WEST | November | Station Check (no issues found) input data to PWQ 13:35 Verified CL17s (mg/L) Influent: Free Grab 1,74, A 1.83 (adjusted to match grabs) Effluent: Free Grab 1.72, A 1.80 (adjusted to match grabs) Total: Grab 2.12 14:00 #11367970 bact. samples | Nobleton Well 2 | 2025-11-12
WEST | November | On site for station check. Collected in house iron samples. Collected Raw PH for Well #7 @10:10hrs: PH: 7.70 Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 1.91mg/l FCL Analyzer: 1.89mg/l Effluent Free Cl2 grab residual: 1.43mg/l FCL Analyzer: 1.30mg/l Effluent Total Cl2 grab residual: 1.70mg/l Topped up Hypo Day tanks Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: Well 3 offline. | Nobleton Wells 3 & 7 | 2025-11-10
WEST | November | In to complete station check. Enter data into PWQ. Analyzer reagent levels good. Took hypo inventory for estimating delivery volume on 11th. No issues. | Nobleton Wells 3 & 7 | 2025-11-07
WEST | November | Responded to well uncommanded stop Influent CL17 sensor alarm cleared Cleared all alarms, well started auto in duty | Nobleton Wells 3 & 7 | 2025-11-04
WEST | November | In to complete station check. Enter data into PWQ. W7 interlock on low influent after startup with Hypo P2. Reset interlocks and monitored startup with hypo P1, no issues. Trends appear to show Hypo P2 is not always priming (not running at 100% speed at startup). Will investigate with PCS, pump speed is in auto. Analyzer reagent levels good. No other issues. | Nobleton Wells 3 & 7 | 2025-11-03
WEST | November | #11352055 Turb. #11350054 deep well ex. #11350063 Hypo #11352741 Hypo #11350736 CL17 #11351915 HI/LO temp #11351961 vent #113552021jhs #11390024 chem. sys. #11352853 silicate 10:00 Verified CL17s (mg/L) Influent: Free Grab 1.59, A 1.55 Effluent: Free Grab 1.59, A 1.63 Total Grab: 1.82 Hypo day tank top up (data input to PWQ) | Nobleton Wells 3 & 7 | 2025-11-04
WEST | November | Station Check (no issues found) Input data to PWQ 9:35 Verified CL17s (mg/L) Influent: Free Grab 2.04, A 2.08 Effluent: Free Grab 1.56. A 1.58 Total Grab: 1.90 9:45 #11347732 Weekly samples | Nobleton Wells 3 & 7 | 2025-11-05
WEST | November | Restarted the Operator Interface Terminal due to Windows Updates from 1000 Hrs to 1006 Hrs. Notified the Remote Operations Center. Wells were off during the restart process. | Nobleton Wells 3 & 7 | 2025-11-24
WEST | November | -on site to receive hypo delivery -filled tanks 67.3 / 66.6 cm to 97.4 cm | Nobleton Wells 3 & 7 | 2025-11-24
WEST | November | Station Check (no issues found) Input data to PWQ 10:35 Verified CL17 (mg/L) Influent: Free Grab 1.23. A 1.28 Effluent: Free Grab 1.43, A 1.40 Total: Grab 1.60 Cl17 (new reagents for influent & effluent) Topped up hypo day tanks | Nobleton Wells 3 & 7 | 2025-11-21
WEST | November | On site to top up silicate tank | Nobleton Wells 3 & 7 | 2025-11-20
WEST | November | In to Complete Station Check Residuals Effluent free Grab: 1.69mg/L, Analyzer: 1.61mg/L Influent free Grab: 1.58mg/L, Analyzer: 1.52mg/L Reagents - all okay Performed diesel generator test run Start hours 367.3 stop hours 368.5 Start fuel 877.73L stop fuel 875.18L Test prv - all ok No other issues on site | Nobleton Wells 3 & 7 | 2025-11-25
WEST | November | Station Check (no issues found) Input data to PWQ 11:10 Verified CL17s (mg/L) Influent: Free Grab 1.44, A 1.42 Effluent: Free Grab 1.56, A 1.58 Total Grab 1.75 Hypo day tanks top up | Nobleton Wells 3 & 7 | 2025-11-28
WEST | November | Station Check (no issues found) Input data to PWQ 9:00 Verified CL17s (mg/l) Influent: Free Grab 2.05, A 1.99 Effluent: Free Grab 1.56, A 1.61 Total Grab 1.85 9:15 #11386664 bact. samples | Nobleton Wells 3 & 7 | 2025-11-19
WEST | November | Station Check 11:30 well 7 interlocked on Low Influent upon start up (due to suspected air in hypo line, momentary dip, reset and started remotely) Input data to PWQ 12:05 Verified CL17s (mg/l) Influent: Free Grab 1.92, A 1.98 Effluent: Free Grab 1.65, A 1.71 (adjusted to match grabs) Total: Grab 1.91 12:15 #11402314 weekly samples | Nobleton Wells 3 & 7 | 2025-11-26
WEST | November | On site for station check. Collected in house iron samples. Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 1.54mg/l FCL Analyzer: 1.44mg/l Effluent Free Cl2 grab residual: 1.74mg/l FCL Analyzer: 1.80mg/l Effluent Total Cl2 grab residual: 2.01mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Nobleton Wells 3 & 7 | 2025-11-17
WEST | November | Station Check (no issues found) Input data to PWQ 13:25 Verified CL17s (mg/L) Influent: Free Grab 1.81, A 1.85 Effluent: Free Grab 1.61, A 1.85 (adjusted to match grabs) Total Grab 1.85 Silicate Pump 2 (small leak that has stopped) will monitor Silicate pumps 1&2 (Decreased max. flow setpoint (down) from 135ml/min. to 130ml/min. (as per lab results) | Nobleton Wells 3 & 7 | 2025-11-14
WEST | November | Hypo delivery (input chemical date to PWQ) | Nobleton Wells 3 & 7 | 2025-11-11
WEST | November | Station Check (no issues found) input data to PWQ Verified CL17s (mg/L) 10:40 Influent: Free Grab 2.05, A 2.00 11:25 Effluent: Free Grab 1.90, A 1.95 (adjusted to match grabs) Total Grab 2.12 11:20 #11367970 bact. sample | Nobleton Wells 3 & 7 | 2025-11-12
WEST | November | Chlorine cylinder change (A side) with Dave T | Nobleton Wells 5 & 6 | 2025-11-06
WEST | November | On site for station check. Collected in house iron samples. Collected Raw PH for Well #5 @11:45hrs: PH: 7.79 Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 2.64mg/l FCL Analyzer: 2.60mg/l Effluent Free Cl2 grab residual: 2.34mg/l FCL Analyzer: 2.25mg/l Effluent Total Cl2 grab residual: 2.60mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: Silicate P2. | Nobleton Wells 5 & 6 | 2025-11-10
WEST | November | In to complete station check and silicate tank top up. Enter data into PWQ. Top up silicate tank to approx 50 cm from 40cm (see PWQ). Analyzer reagent levels good. No issues. | Nobleton Wells 5 & 6 | 2025-11-07
WEST | November | In to complete station check. Enter data into PWQ. Created CMU W11412339 to troubleshoot NaSi LIT. Readings have been erratic for past few days, unable to get accurate dose calculations. Analyzer reagent levels good. Span calibrate based on grabs: Influent cl17 to 2.34 from 2.55mg/L Effluent cl17 to 1.78 from 1.90mg/L No other issues. | Nobleton Wells 5 & 6 | 2025-11-03
WEST | November | Station Check (no issues found) Input data to PWQ 10:35 Verified CL17s (mg/L) Influent: Free Grab 2.50, A 2.57 Effluent: Free Grab 2.19, A 2.19 Total Grab: 2.96 10:40 #11347732 weekly samples | Nobleton Wells 5 & 6 | 2025-11-05
WEST | November | Check for hot water flush line for silicate | Nobleton Wells 5 & 6 | 2025-11-21
WEST | November | Station Check (no issues found) Input data to PWEQ 10:00 Verified CL17s (mg/l) Influent: Free Grab 1.96, A 2.00 Effluent: Free Grab 2.09, A2.11 Total Grab 2.72 CL17 Effluent (new reagents) | Nobleton Wells 5 & 6 | 2025-11-28
WEST | November | Station Check (no issues found) Input data to PWQ 9:50 Verified CL17s (mg/l) Influent: Grab 2.66, A 2.66 Effluent: Grab 2.26, A 2.34 Total Grab 3.20 10:05 #11386664 Bact. samples | Nobleton Wells 5 & 6 | 2025-11-19
WEST | November | On site to top up silicate tank | Nobleton Wells 5 & 6 | 2025-11-20
WEST | November | Station Check (no issues found) Input data to PWQ 11:30 Verified CL17s (mg/l) Influent: Free Grab 2.66, A 2.63 Effluent: Free: Grab 2.20, A 2.21 Total Grab 2.90 11:40 #11402314 weekly samples | Nobleton Wells 5 & 6 | 2025-11-26
WEST | November | Restarted the Operator Interface Terminal due to Windows Updates. Restarted from 1012 Hrs to 1019 Hrs. Notified the Remote Operations Center. Wells were off during the restart process. | Nobleton Wells 5 & 6 | 2025-11-24
WEST | November | Station Check (no issues found) Input data to PWQ 11:30 Verified CL17s(mg/l) Influent: Free Grab 2.62, A 2.64 Effluent: Free Grab 2.40, A 2.32 Total: Grab 3.40 Worked on silicate lines with JB | Nobleton Wells 5 & 6 | 2025-11-25
WEST | November | Station Check (no issues found) Input data to PWQ 9:30 Verified CL17s (mg/L) Influent: Grab 1.96, A 1.97 Effluent: Grab 2.15, A 2.13 Total Grab 2.98 Chlorine cylinder change with JM (Bside) | Nobleton Wells 5 & 6 | 2025-11-21
WEST | November | Attending site to check silicate pump#2 (W11443611). Removed incorrect roller and installed correct roller and new tube, as the existing tube has been completely flattened out. Found foot valve on pump#2 was completely plugged up. Foot valve was removed, disassembled and cleaned out. Pump#2 in now outputting about 40% more than pump#1. I will submit a work order to West Water to rebuild silicate pump#1 with the correct parts. Also, attending site to check silicate level transmitter (W11412339). Found transducer face was coated in silicate. Cleaned transducer and put back into service. ROC was notified before and after maintenance work. All associated alarms were cleared. | Nobleton Wells 5 & 6 | 2025-11-21
WEST | November | Attending site to check silicate pump#2. Found pump has incorrect roller. Pump failure caused by using incompatible parts from different manufacturer. Will return to attempt repairs. ROC notified before and after maintenance work. | Nobleton Wells 5 & 6 | 2025-11-20
WEST | November | On site for station check. Collected in house operational iron samples @11:20hrs. Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 1.95mg/l FCL Analyzer: 1.88mg/l Effluent Free Cl2 grab residual: 2.09mg/l FCL Analyzer: 2.04mg/l Effluent Total Cl2 grab residual: 2.52mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Nobleton Wells 5 & 6 | 2025-11-17
WEST | November | Station Check (no issues found) input data to PWQ 11:30Verified CL17s (mg/L Influent: Free Grab 1.80, A 1.85 Effluent: Free Grab 1.67, A 1.71 Total Grab 2.14 | Nobleton Wells 5 & 6 | 2025-11-14
WEST | November | #11362899 CL17 maintenance: 9:55 Verified (mg/L) Influent: Free: Grab 1.82, A 1.83 Effluent: Free: Grab 1.65, A 1.67 #11362972 Diesel run: 10:30 pre-check complete & ok 10:36 Start test: Fuel (94.2cm/982L, 91.8cm/956L), Hours: 255:18 11:05 Thirty min. check: 600volts,, 60hz, 50amps, oil press. 57psi, coolant temp. 178F, 1804rpm 11:42 End test, Hours: 256:22 #11362899 Cl2 kit (sealed) #11362939 Cl2 leak #11362959 prv #11293805 scrubber sample #11363038 manual valve #11363061 scrubber #11363139 air valve #11364347 chem. insp. #11363264 jhs #11363421 dehum #11363435 hi/lo temp #11399134 silicate inj. #11363488 diesel spill #11363622 turb. #11363488 silicate | Nobleton Wells 5 & 6 | 2025-11-13
WEST | November | Station Check (no issues found) Input data to PWQ 12:10 Verified CL17s (mg/l) Influent: Free Grab 2.62, A 2.60 Effluent: Free Grab 2.20, A 2.25 Total: Grab 2.90 12:15 #11367970 bact. samples | Nobleton Wells 5 & 6 | 2025-11-12
CENTRAL | November | Adjusted flow to outlet analyzer slightly. | Queensville Elevated Tank | 2025-11-10
CENTRAL | November | On-site with Alex Bell (OIT/under direction of OIC) for station check and weekly micro sampling (W11347694). Outlet grab/analyzer results as follows (mg/L): Free Cl (13:24): G: 0.07 A: 0.05 Total Cl (13:24): G: 2.40 A: 2.47 Collected micro sample. Alex noted that the flow to the inlet analyzer was difficult to adjust (trends show some fuzziness to readings), placed analyzer in calibration mode and removed PSV to clean, cracked PVC line to total Cl analyzer by accident, replumbed around cracked PVC for time being and verified analyzer once flow/readings returned to normal operating range, as follows (mg/L): Inlet Free Cl (14:26): G: 0.06 A: 0.04 Total Cl (14:23): G: 2.92 A: 2.64 (adjusted to 2.92mg/L based on average of 3 grabs) Monitored analyzer and cleared alarms, returned site to normal operation. Will create WO to have inlet analyzer PVC repaired. Will monitor Inlet Free Ammonia, adjustments made to Cl:AMM ratio earlier today at QVW12 to increase ammonia dosage. Entered station readings in shared PD excel file. No other new issues found while on-site. | Queensville Elevated Tank | 2025-11-05
CENTRAL | November | Adjusted flow to outlet analyzer slightly to try and reduce noise in trend. | Queensville Elevated Tank | 2025-11-07
CENTRAL | November | Adjusted flow to outlet and inlet analyzers in response to fuzzy trends. | Queensville Elevated Tank | 2025-11-03
CENTRAL | November | On site to complete PMs. Notified ROC of relevant alarms. -Exercised and inspected actuated valves: all good -Inspected inlet/outlet heat trace systems: all good -Inspected and flushed air valve: all good -Completed JHSC inspection. All good -Completed portable generator test. All good -Performed maintenance on Depolox chlorine analyzers. Cleaned y-screens and flushed sample lines ? due to cutting off sample flow, outlet analyzer readings can be disregarded for 12:38 to 12:58, inlet analyzer readings between 12:52 to 13:10. Verified analyzers after cleaning: Inlet Free chlorine @ 13:18 Grab: 0.03 mg/L Analyzer: 0.02 mg/L Total chlorine @ 13:18 Grab: 2.58 mg/L Analyzer: 2.60 mg/L Outlet Free chlorine @ 13:26 Grab: 0.03 mg/L Analyzer: 0.04 mg/L Total chlorine @ 13:26 Grab: 2.34 mg/L Analyzer: 2.40 mg/L Topped up KI reagent for inlet chlorine analyzer. | Queensville Elevated Tank | 2025-11-04
CENTRAL | November | On site to complete station check, collect weekly bacti sample (W11386626). Verified analyzers: Inlet Free chlorine @ 9:43 Grab: 0.02 mg/L Analyzer: 0.02 mg/L Total chlorine @ 9:43 Grab: 2.60 mg/L Analyzer: 2.66 mg/L Outlet Free chlorine @ 9:29 Grab: 0.05 mg/L Analyzer: 0.05 mg/L Total chlorine @ 9:29 Grab: 2.16 mg/L Analyzer: 2.18 mg/L -Entered data into PD sheet -Checked trends | Queensville Elevated Tank | 2025-11-19
CENTRAL | November | On site to complete station check, collect weekly bacti sample (W11402412), and collect operational samples (W11402633). Verified analyzers: Inlet Free chlorine @ 9:41 Grab: 0.06 mg/L Analyzer: 0.02 mg/L Total chlorine @ 9:41 Grab: 2.70 mg/L Analyzer: 2.68 mg/L Outlet Free chlorine @ 9:29 Grab: 0.02 mg/L Analyzer: 0.05 mg/L Total chlorine @ 9:29 Grab: 2.24 mg/L Analyzer: 2.17 mg/L -Entered data into PD sheet -Checked trends -Topped up acetate reagents for both inlet and outlet analyzers | Queensville Elevated Tank | 2025-11-26
CENTRAL | November | On site to complete station check, collect weekly bacti sample (W11368068), and collect operational samples (W11368310). Verified analyzers: Inlet Free chlorine @ 10:30 Grab: 0.05 mg/L Analyzer: 0.02 mg/L Total chlorine @ 10:30 Grab: 3.22 mg/L Analyzer: 3.24 mg/L Outlet Free chlorine @ 10:16 Grab: 0.06 mg/L Analyzer: 0.05 mg/L Total chlorine @ 10:16 Grab: 2.54 mg/L Analyzer: 2.52 mg/L -Entered data into PD sheet -Checked trends | Queensville Elevated Tank | 2025-11-12
CENTRAL | November | Attending site to check Outlet Total chlorine analyzer due to noisy readings (W11435847). Could not find anything obviously wrong with the analyzer. Replaced electrolyte in both the Inlet and Outlet Total chlorine probes to see if the readings stabilize. Will check trends tomorrow. Calibration mode was used to reduce the number of alarms. ROC was notified before and after maintenance work. Related alarms were cleared after work was completed. | Queensville Elevated Tank | 2025-11-11
CENTRAL | November | Onsite with Alex B for chlorine cylinder change Left bank Topped up ammonia tank 2 Electrical onsite for heater repair, will return with new unit Ops normal | Queensville Wells No. 1 and 2 | 2025-11-06
CENTRAL | November | On site to complete the station check. -Topped up silicate day tanks 484L -> 791L Verified analyzers: Influent Free Chlorine @ 12:58 Grab: 2.78 mg/L Analyzer: 2.80 mg/L Effluent Free Chlorine @ 12:54 Grab: 2.98 mg/L Analyzer: 2.86 mg/L Treated Free Chlorine @ 12:41 Grab: 0.24 mg/L Analyzer: 0.23 mg/L Treated Total Chlorine @ 12:48 Grab: 3.48 mg/L Analyzer: 3.42 mg/L -Entered data into PD sheet -Checked trends Low influent chlorine free alarm came in after an hour of running chlorine booster pump 2. Switched chlorine booster pumps. Took a grab at 13:38, result was 2.04 mg/L (analyzer was 1.99mg/L). At 13:44, grab was 2.90 mg/L while analyzer was 2.92 mg/L. Continued to monitor well until effluent free and treated total analyzer readings showed recovery towards usual operational ranges. No low effluent free chlorine or low combined treated chlorine alarms triggered. | Queensville Wells No. 1 and 2 | 2025-11-07
CENTRAL | November | On site to remove and replace unit heaters in the chlorine room and the ammonia room. | Queensville Wells No. 1 and 2 | 2025-11-07
CENTRAL | November | Changed reagents for influent free chlorine analyzer. | Queensville Wells No. 1 and 2 | 2025-11-10
CENTRAL | November | On site to complete the station check and collect operational samples. -Changed chlorine cylinder bank B with Ryan -Started wells manually -Topped up silicate day tanks 474L -> 811L -Topped up ammonia tank 1 Verified analyzers: Influent Free Chlorine @ 9:52 Grab: 2.96 mg/L Analyzer: 2.87 mg/L Effluent Free Chlorine @ 9:57 Grab: 2.76 mg/L Analyzer: 2.72 mg/L Treated Free Chlorine @ 9:59 Grab: 0.20 mg/L Analyzer: 0.23 mg/L Treated Total Chlorine @ 9:59 Grab: 3.36 mg/L Analyzer: 3.31 mg/L -Entered data into PD sheet -Checked trends | Queensville Wells No. 1 and 2 | 2025-11-10
CENTRAL | November | Attending site with Hach service technicians to update chlorine analyzer firmware and to bypass internal flowmeter due to flow restriction. Well was shut off during work via ROC. Turbidimeter spikes were due to flow adjustments made to chlorine analyzers. Also replaced desiccant in turbidimeter (W11412180). ROC was notified before and after maintenance work was performed. | Queensville Wells No. 1 and 2 | 2025-11-04
CENTRAL | November | On site to complete the station check and collect operational samples. -Under direction of Ben Hess, adjusted flow setpoint for well 1 from 70.0L/s to 47.0L/s. -Changed chlorine cylinder bank B with Joe D. -Topped up silicate day tanks 514L -> 808L -Topped up ammonia tank 1 Verified analyzers: Influent Free Chlorine @ 10:28 Grab: 2.80 mg/L Analyzer: 2.87 mg/L Effluent Free Chlorine @ 10:37 Grab: 2.60 mg/L Analyzer: 2.68 mg/L Treated Free Chlorine @ 10:12 Grab: 0.22 mg/L Analyzer: 0.21 mg/L Treated Total Chlorine @ 10:14 Grab: 3.26 mg/L Analyzer: 3.17 mg/L -Entered data into PD sheet -Checked trends -Placed well 4 in manual-on | Queensville Wells No. 1 and 2 | 2025-11-03
CENTRAL | November | On-site for station check, in-house operational sampling, weekly micro sampling (W11347694). Collected raw/treated samples, grab/analyzer results as follows (mg/L): Influent Free Cl (10:19): G: 2.80 A: 3.00 (adjusted slope of analyzer to better reflect average grab sample, next reading of analyzer 2.84mg/L, will monitor) Effluent Free Cl (10:25): G: 2.66 A: 2.67 Treated Free Cl (10:27): G: 0.21 A: 0.22 Treated Total Cl (10:29): G: 3.30 A: 3.21 Switched to run ammonia pump 1 as FA grab 0mg/L, new grab also 0mg/L FA, adjusted Cl:AMM ratio from 4.3 to 4.0, final FA grab of 0.04mg/L. Will continue to monitor ammonia dosage. Topped up NaSi day tanks. No other new issues found. | Queensville Wells No. 1 and 2 | 2025-11-05
CENTRAL | November | Under direction of OIC Divya Patel. Worked with contractors and operations to connect and test temporary generator. This is so that station generator can undergo TSSA upgrades. ROC notified of the testing. | Queensville Wells No. 1 and 2 | 2025-11-27
CENTRAL | November | On site to complete the station check. -Completed chlorine cylinder change with Ben H. on bank B -Topped up silicate day tanks 420L -> 794L Verified analyzers: Influent Free Chlorine @ 11:53 Grab: 3.10 mg/L Analyzer: 2.98 mg/L Effluent Free Chlorine @ 12:10 Grab: 2.80 mg/L Analyzer: 2.69 mg/L Treated Free Chlorine @ 13:19 Grab: 0.20 mg/L Analyzer: 0.24 mg/L Treated Total Chlorine @ 11:58 Grab: 3.12 mg/L Analyzer: 3.11 mg/L -Entered data into PD sheet -Checked trends | Queensville Wells No. 1 and 2 | 2025-11-21
CENTRAL | November | On site to complete station check. Verified analyzers: Influent Free Chlorine @ 12:22 Grab: 2.98 mg/L Analyzer: 2.97 mg/L Effluent Free Chlorine @ 12:20 Grab: 2.80 mg/L Analyzer: 2.89 mg/L Treated Free Chlorine @ 12:07 Grab: 0.17 mg/L Analyzer: 0.23 mg/L Treated Total Chlorine @ 12:07 Grab: 3.40 mg/L Analyzer: 3.38 mg/L -Entered data into PD sheet -Checked trends -Topped up silicate day tanks 390L -> 810L -Portable generator contractor on site | Queensville Wells No. 1 and 2 | 2025-11-28
CENTRAL | November | Confirmed well electrical back to normal with electrician and PCS, returned wells to auto. | Queensville Wells No. 1 and 2 | 2025-11-27
CENTRAL | November | On site to complete station check and collect weekly bacti samples (W11402412). Verified analyzers: Influent Free Chlorine @ 13:05 Grab: 2.96 mg/L Analyzer: 2.85 mg/L Effluent Free Chlorine @ 13:09 Grab: 2.66 mg/L Analyzer: 2.62 mg/L Treated Free Chlorine @ 13:00 Grab: 0.17 mg/L Analyzer: 0.21 mg/L Treated Total Chlorine @ 13:07 Grab: 3.14 mg/L Analyzer: 3.03 mg/L -Entered data into PD sheet -Checked trends -Topped up ammonia tank 1 | Queensville Wells No. 1 and 2 | 2025-11-26
CENTRAL | November | 13:00 Remotely activated well 1 in manual 13:29 hrs. On-site for station check. Well 1 running at 70 l/s. Topped up silicate day tanks. 13:40 Verified analyzers(mg/l): Influent free grab: 2.98. CL17: 2.95. Effluent free grab: 2.56. CL17: 2.60. Treated free grab: 0.19. CL17: 0.21. Treated total grab: 3.16. CL17: 3.11. Monochloramine: 2.61. Free ammonia: 0.06. Total ammonia: 0.57. 13:58. Activated nm east duty 1. Remotely deactivated nm central east duty. Placed well 1 back into auto. No issues found on site. | Queensville Wells No. 1 and 2 | 2025-11-24
CENTRAL | November | On site to complete PMs. Notified ROC of relevant alarms. -Inspected chlorinator 1 after influent dosing issues last night. Put dechlor in waste chamber and slightly opened waste valve during testing process. Determined cause to be freezing of cylinders when running both wells. Closed waste valve. Room heater adjusted. -Completed monthly generator run test: Fuel before test: 81.3cm ¦ 1381L Hours before test: 616.6 hrs Test start: 9:56 On load @ 9:58 Test end: 11:05 Cooldown end: 11:08 Fuel after test: 78.3cm ¦ 1328L Hours after test: 617.8 hrs -Added more dechlor and reopened waste valve slightly while flushing silicate lines with hot water. -Isolated contact chamber and depressurized raw main to clean silicate injection points. Isolation of contact tank caused low flow to influent chlorine analyzer. This resulted in false low and lolo influent free chlorine alarms. Upon reopening valve once work was completed, the analyzer resumed reading what it had prior to losing flow. Verified analyzer: Influent Free Chlorine @ 14:15 Grab: 2.63 mg/L Analyzer: 2.74 mg/L -Performed turbidimeter maintenance: verified calibration, cleaned instrument. All good -Completed JHSC inspection -Activated duty 1 to run wells and monitor silicate dosing | Queensville Wells No. 1 and 2 | 2025-11-20
CENTRAL | November | On site to do cylinder change with Donald M and helped PCS & electrician run portable generator on load by running well 1 in manual. Will Operate virtually | Queensville Wells No. 1 and 2 | 2025-11-27
CENTRAL | November | On-site for chlorine cylinder delivery 12 full and 12 empties to take away | Queensville Wells No. 1 and 2 | 2025-11-24
CENTRAL | November | On site to complete the station check and collect weekly bacti samples (W11386626). Verified analyzers: Influent Free Chlorine @ 11:36 Grab: 2.88 mg/L Analyzer: 2.89 mg/L Effluent Free Chlorine @ 11:32 Grab: 2.70 mg/L Analyzer: 2.66 mg/L Treated Free Chlorine @ 11:24 Grab: 0.26 mg/L Analyzer: 0.22 mg/L Treated Total Chlorine @ 11:25 Grab: 3.00 mg/L Analyzer: 3.12 mg/L -Entered data into PD sheet -Checked trends | Queensville Wells No. 1 and 2 | 2025-11-19
CENTRAL | November | On-site with Alex Bell (OIT/under direction of OIC) to replace chlorine gas ejector #2 and return train 2 to service. Purged Cl2 system. Replaced ejector with rebuilt ejector, and will store old ejector in inventory once rebuilt. Checked for leaks/vacuum, and introduced Cl2 back into system. Checked for Cl2 leaks. Backflushed main with dechlorination measures in place. Returned system to normal operation and ran W1 in remote/man to observe operation. Adjusted chlorine dosage factor as high Influent alarm triggered, monitored, alarm cleared and system running at normal operating levels. Activated D1 and placed W1/2 in remote/auto. Will monitor Cl2 dosage from train 2 remotely, appears to operate normally. Informed ROC. | Queensville Wells No. 1 and 2 | 2025-11-13
CENTRAL | November | Change motor oil in 1 and 2 motors | Queensville Wells No. 1 and 2 | 2025-11-14
CENTRAL | November | On site to complete the station check and collect operational samples. -Changed chlorine cylinder bank A with Divya P -Topped up ammonia tank 1 -Topped up silicate day tanks 556L -> 798L Verified analyzers: Influent Free Chlorine @ 12:40 Grab: 2.90 mg/L Analyzer: 2.94 mg/L Effluent Free Chlorine @ 12:31 Grab: 2.72 mg/L Analyzer: 2.68 mg/L Treated Free Chlorine @ 12:33 Grab: 0.18 mg/L Analyzer: 0.22 mg/L Treated Total Chlorine @ 12:49 Grab: 3.24 mg/L Analyzer: 3.24 mg/L -Entered data into PD sheet -Checked trends | Queensville Wells No. 1 and 2 | 2025-11-17
CENTRAL | November | On site to complete PMs. Notified ROC of relevant alarms. -Completed chlorine gas detector test: test successful, no issues found -Inspected chlorine system: first added dechlor to outfall and opened waste valve to backflush slightly during the testing process. No issues found during testing. -Inspected and performed maintenance on deep well exhaust valves for both wells -Topped up mineral oil for both wells -Completed chlorine analyzer maintenance, Verified analyzers: Influent Free Chlorine @ 10:31 Grab: 2.68 mg/L Analyzer: 2.71 mg/L Effluent Free Chlorine @ 10:15 Grab: 0.10 mg/L Analyzer: 0.14 mg/L Treated Free Chlorine @ 10:12 Grab: 0.09 mg/L Analyzer: 0.10 mg/L Treated Total Chlorine @ 10:12 Grab: 2.70 mg/L Analyzer: 2.73 mg/L | Queensville Wells No. 1 and 2 | 2025-11-18
CENTRAL | November | On site to replace chlorine injector 2 with Ryan B. Wells and chlorine booster pumps placed in local. During the replacement process, a part broke and Ryan has left site to find a replacement. I am leaving the site with wells and booster pumps in local, to resume repair when we have acquired the parts. | Queensville Wells No. 1 and 2 | 2025-11-13
CENTRAL | November | On site to finish PMs. ROC notified of relevant alarms. Inspected ammonia system: Replaced leaky parker fittings on pump to DICE block lines. Pump 1 drawdown was 205 mg/L, pump 2 drawdown was 210 mg/L ? did not adjust max flow setpoint on SCADA after reviewing PD sheet ammonia trends. Tested containment flood alarm. | Queensville Wells No. 1 and 2 | 2025-11-18
CENTRAL | November | On site to complete the station check and collect weekly bacti samples (W11368068). Verified analyzers: Influent Free Chlorine @ 8:02 Grab: 3.09 mg/L Analyzer: 2.94 mg/L Adjusted analyzer based on average of 3 grabs. Analyzer read 3.14 mg/L afterwards. Effluent Free Chlorine @ 8:13 Grab: 2.90 mg/L Analyzer: 2.93 mg/L Treated Free Chlorine @ 8:16 Grab: 0.21 mg/L Analyzer: 0.24 mg/L Treated Total Chlorine @ 8:16 Grab: 3.42 mg/L Analyzer: 3.50 mg/L -Entered data into PD sheet -Checked trends -Topped up ammonia tank 2 -Changed effluent free chlorine analyzer reagents | Queensville Wells No. 1 and 2 | 2025-11-12
CENTRAL | November | On site to complete the station check. Verified analyzers: Influent Free Chlorine @ 13:38 Grab: 2.80 mg/L Analyzer: 2.87 mg/L Effluent Free Chlorine @ 13:33 Grab: 2.82 mg/L Analyzer: 2.79 mg/L Treated Free Chlorine @ 13:11 Grab: 0.26 mg/L Analyzer: 0.21 mg/L Treated Total Chlorine @ 13:11 Grab: 3.29 mg/L Analyzer: 3.15 mg/L -Entered data into PD sheet -Checked trends -Changed treated free chlorine analyzer reagents -Topped up silicate day tanks 316L -> 807L | Queensville Wells No. 1 and 2 | 2025-11-14
CENTRAL | November | On site to complete station check. Verified analyzers: Influent Free Chlorine @ 10:04 Grab: 2.72 mg/L Analyzer: 2.68 mg/L Effluent Free Chlorine @ 10:08 Grab: 2.42 mg/L Analyzer: 2.38 mg/L Treated Free Chlorine @ 10:30 Grab: 0.10 mg/L Analyzer: 0.13 mg/L Treated Total Chlorine @ 10:25 Grab: 3.15 mg/L Analyzer: 3.05 mg/L -Entered data into PD sheet -Checked trends | Queensville Wells No. 3 and 4 | 2025-11-07
CENTRAL | November | Onsite w/ Jason Moore for well 4 Step test Informed ROC (Christian) of ongoings Ran well in manual with flow control valve 45 l/s, 60 l/s and aprox 74 l/s. Collected iron sample @ 11:50 am at 74 l/s Placed wells back to auto | Queensville Wells No. 3 and 4 | 2025-11-06
CENTRAL | November | On site to complete station check and collect operational samples. Verified analyzers: Influent Free Chlorine @ 12:16 Grab: 2.70 mg/L Analyzer: 2.71 mg/L Effluent Free Chlorine @ 12:20 Grab: 2.50 mg/L Analyzer: 2.48 mg/L Treated Free Chlorine @ 12:23 Grab: 0.17 mg/L Analyzer: 0.15 mg/L Treated Total Chlorine @ 12:23 Grab: 3.23 mg/L Analyzer: 3.12 mg/L -Entered data into PD sheet -Checked trends | Queensville Wells No. 3 and 4 | 2025-11-10
CENTRAL | November | Repair chlorine injection line | Queensville Wells No. 3 and 4 | 2025-11-10
CENTRAL | November | Changed silicate dosage setpoint from 9.00 mg/L to 8.00 mg/L. | Queensville Wells No. 3 and 4 | 2025-11-10
CENTRAL | November | On site to complete station check and collect operational samples. Verified analyzers: Influent Free Chlorine @ 12:52 Grab: 2.71 mg/L Analyzer: 2.66 mg/L Effluent Free Chlorine @ 12:49 Grab: 2.60 mg/L Analyzer: 2.65 mg/L Treated Free Chlorine @ 12:38 Grab: 0.19 mg/L Analyzer: 0.17 mg/L Treated Total Chlorine @ 12:38 Grab: 3.43 mg/L Analyzer: 3.48 mg/L -Entered data into PD sheet -Checked trends -Changed reagents for effluent free chlorine analyzer | Queensville Wells No. 3 and 4 | 2025-11-03
CENTRAL | November | Adjusted silicate dose from 10 mg/L to 9 mg/L, this is to bring closer to our bench testing in 2016/2017 We will do dissolved iron samples to monitor the change | Queensville Wells No. 3 and 4 | 2025-11-03
CENTRAL | November | On-site for station check, in-house operational sampling, weekly micro sampling (W11347694), and to adjusted W4 flow to 45L/s ahead of tomorrow?s planned step test. Adjusted W4 to 45L/s and collected raw water sample. Switched to run W3 and collected raw/treated samples, grab/analyzer results as follows (mg/L): Influent Free Cl (08:16): G: 2.86 A: 2.88 Effluent Free Cl (08:17): G: 2.60 A: 2.61 Treated Free Cl (08:18): G: 0.16 A: 0.18 Treated Total Cl (08:20): G: 3.28 A: 3.35 Switched to run ammonia pump 2 as FA grab 0.01mg/L, new grab also 0mg/L FA, adjusted Cl:AMM ratio from 4.3 to 4.1, final FA grab of 0.02mg/L. Will continue to monitor ammonia dosage. Shutdown W3 and informed ROC/Central OPs that Wells are man/off for planned step test tomorrow. Informed Artour Litvinov (PCS) that SCADA OIT needs to be reset as I am unable to login, used remote SCADA while on-site. No other new issues found. | Queensville Wells No. 3 and 4 | 2025-11-05
CENTRAL | November | On site to complete station check. Verified analyzers: Influent Free Chlorine @ 8:14 Grab: 2.80 mg/L Analyzer: 2.75 mg/L Effluent Free Chlorine @ 8:06 Grab: 2.48 mg/L Analyzer: 2.49 mg/L Treated Free Chlorine @ 7:59 Grab: 0.10 mg/L Analyzer: 0.14 mg/L Treated Total Chlorine @ 7:59 Grab: 3.15 mg/L Analyzer: 3.11 mg/L -Entered data into PD sheet -Checked trends | Queensville Wells No. 3 and 4 | 2025-11-28
CENTRAL | November | On site to take silicate for HLW1 Before-74cm After 73.19 cm | Queensville Wells No. 3 and 4 | 2025-11-28
CENTRAL | November | On site to complete station check and collect weekly bacti samples (W11402412). Verified analyzers: Influent Free Chlorine @ 10:56 Grab: 2.62 mg/L Analyzer: 2.68 mg/L Effluent Free Chlorine @ 10:52 Grab: 2.56 mg/L Analyzer: 2.58 mg/L Treated Free Chlorine @ 10:49 Grab: 0.10 mg/L Analyzer: 0.14 mg/L Treated Total Chlorine @ 10:41 Grab: 3.29 mg/L Analyzer: 3.34 mg/L -Entered data into PD sheet -Checked trends | Queensville Wells No. 3 and 4 | 2025-11-26
CENTRAL | November | On site to complete station check and to flush silicate lines. Verified analyzers: Influent Free Chlorine @ 8:15 Grab: 2.66 mg/L Analyzer: 2.72 mg/L Effluent Free Chlorine @ 8:12 Grab: 2.42 mg/L Analyzer: 2.48 mg/L Treated Free Chlorine @ 7:57 Grab: 0.12 mg/L Analyzer: 0.13 mg/L Treated Total Chlorine @ 7:57 Grab: 3.00 mg/L Analyzer: 2.99 mg/L -Entered data into PD sheet -Checked trends Called ROC and notified them of relevant alarms. Added dechlor to the waste chamber and opened waste valve slightly to avoid overdosing silicate while flushing the lines with hot water. Ran lines afterwards to reprime them with silicate. Closed waste valve and returned everything to auto. | Queensville Wells No. 3 and 4 | 2025-11-21
CENTRAL | November | On site to complete station check, collect weekly bacti samples (W11386626) and collect operational iron sample. Verified analyzers: Influent Free Chlorine @ 7:59 Grab: 2.66 mg/L Analyzer: 2.65 mg/L Effluent Free Chlorine @ 7:55 Grab: 2.48 mg/L Analyzer: 2.50 mg/L Treated Free Chlorine @ 7:45 Grab: 0.12 mg/L Analyzer: 0.13 mg/L Treated Total Chlorine @ 7:45 Grab: 3.12 mg/L Analyzer: 3.09 mg/L -Entered data into PD sheet -Checked trends -Topped up mineral oil for wells 3 & 4 -Changed reagents for treated free chlorine analyzer -Topped up silicate day tanks 351L -> 869L | Queensville Wells No. 3 and 4 | 2025-11-19
CENTRAL | November | On-site for station check Recordings in PD sheet Took operational samples Electricians onsite working on new VFD panel. Chlorine booster p2 OOS until new ejector can replace. Station ok | Queensville Wells No. 3 and 4 | 2025-11-24
CENTRAL | November | On site to complete JHSC inspection. Notified ROC. All good. | Queensville Wells No. 3 and 4 | 2025-11-13
CENTRAL | November | -Responded chlorine leak alarm - reviewed trends, chlorine leak alarm came in when wells are not running, highest level=1.39ppm - Checked vent - no leaks - Opened cylinders one by one - no leak -checked every fitting and chlorinator - no leaks - will keep monitoring | Queensville Wells No. 3 and 4 | 2025-11-27
CENTRAL | November | On site to complete PMs, notified ROC of relevant alarms. -Placed wells in manual-off then local -Added dechlor to drain chamber then isolated raw main from contact tank, depressurized raw main -Performed silicate pump drawdowns: 168 mL/min and 166 mL/min for pump 1 and 2 respectively. Max flow setpoints not adjusted. -Returned chlorine booster pump 2 to service ? line still unusable due to issue with ejector, so chlorinator 2 remains in manual-off -Tested and inspected chlorine system while slightly backflushing contact tank to avoid causing high influent chlorine readings on the analyzer: all good -Performed chlorine detector test: all good -Began running wells manually to verify silicate dosing via turbidimeter -Replaced fitting on ammonia pump 1 DICE block. Performed drawdown: 200 mL/min. No max flow setpoint alteration. -Replaced fitting on ammonia pump 2 DICE block. Performed drawdown: 205 mL/min. No max flow setpoint alteration. -Returned wells to auto | Queensville Wells No. 3 and 4 | 2025-11-11
CENTRAL | November | On site to continue work on well 4 VFD upgrade project. | Queensville Wells No. 3 and 4 | 2025-11-12
CENTRAL | November | Enabled schedule mode for W3 Sunday, Monday, Wednesday, Friday from 07:00-08:30. | Queensville Wells No. 3 and 4 | 2025-11-13
CENTRAL | November | On site to complete station check and collect operational iron sample. Verified analyzers: Influent Free Chlorine @ 8:13 Grab: 2.70 mg/L Analyzer: 2.76 mg/L Effluent Free Chlorine @ 8:10 Grab: 2.52 mg/L Analyzer: 2.45 mg/L Treated Free Chlorine @ 8:08 Grab: 0.12 mg/L Analyzer: 0.14 mg/L Treated Total Chlorine @ 8:08 Grab: 3.14 mg/L Analyzer: 3.12 mg/L -Entered data into PD sheet -Checked trends -Topped up ammonia tank 2 -Changed chlorine cylinder bank A with Divya P. | Queensville Wells No. 3 and 4 | 2025-11-17
CENTRAL | November | On site to complete station check and collect weekly bacti samples (W11368068). Verified analyzers while wells running: Influent Free Chlorine @ 12:00 Grab: 2.64 mg/L Analyzer: 2.67 mg/L Effluent Free Chlorine @ 12:03 Grab: 2.56 mg/L Analyzer: 2.61 mg/L Treated Free Chlorine @ 11:58 Grab: 0.12 mg/L Analyzer: 0.14 mg/L Treated Total Chlorine @ 11:58 Grab: 3.31 mg/L Analyzer: 3.25 mg/L -Entered data into PD sheet -Checked trends -Changed treated total analyzer reagents -Notified ROC of relevant alarms then proceeded with monthly chlorine analyzer maintenance, verified by the following grabs: Influent Free Chlorine @ 12:55 Grab: 2.68 mg/L Analyzer: 2.77 mg/L Effluent Free Chlorine @ 12:49 Grab: 0.28 mg/L Analyzer: 0.24 mg/L Treated Free Chlorine @ 12:45 Grab: 0.08 mg/L Analyzer: 0.12 mg/L Treated Total Chlorine @ 12:52 Grab: 3.98 mg/L Analyzer: 3.03 mg/L -Ran well 4 manually to collect raw bacti sample | Queensville Wells No. 3 and 4 | 2025-11-12
CENTRAL | November | On site two continue work on well for VFD upgrade project. Also removed and replaced malfunctioning chlorine room unit heater. | Queensville Wells No. 3 and 4 | 2025-11-11
CENTRAL | November | On site to complete station check and finish PMs. -Inspected and performed maintenance upon well 4 flow control valve -On site when low influent chlorine alarm was received due to cylinder switchover. Grabs taken as follows while monitoring trend recovery: Influent Free Chlorine @ 10:04 Grab: 1.33 mg/L Analyzer: 1.34 mg/L Influent Free Chlorine @ 10:27 Grab: 2.32 mg/L Analyzer: 2.32 mg/L Influent Free Chlorine @ 10:47 Grab: 2.70 mg/L Analyzer: 2.73 mg/L Trends returned to normal and issue resolved. Verified other analyzers: Effluent Free Chlorine @ 11:01 Grab: 1.98 mg/L Analyzer: 2.00 mg/L Treated Free Chlorine @ 11:04 Grab: 0.09 mg/L Analyzer: 0.14 mg/L Treated Total Chlorine @ 11:04 Grab: 2.60 mg/L Analyzer: 2.66 mg/L -Entered data into PD sheet -Checked trends -Collected pH monitoring raw sample for well 4 @ 9:40: 8.13 | Queensville Wells No. 3 and 4 | 2025-11-14
CENTRAL | November | On site to complete PMs, notified ROC of relevant alarms. -Ran generator for monthly test: Hours before: 702h 15m Fuel before: 78.1cm 636L ¦ 77.2cm 627L Run started @ 12:33 On load @ 12:38 Run ended @ 13:46 Cooldown ended @ 13:52 Hours after: 703h 34m Fuel after: 75.6cm 614L ¦ 75.1cm 609L -Collected pH monitoring raw sample for well 3 @ 13:20: 8.12 -Calibrated turbidimeter, which read 0.033 NTU afterwards -Inspected and performed maintenance upon well 3 deep well exhaust valve -Inspected and performed maintenance upon well 4 deep well exhaust valve | Queensville Wells No. 3 and 4 | 2025-11-13
WEST | November | Pumping Station Check Chlorine Grab (mg/L): Free: 0.05 Total: 1.59 No issues on site | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2025-11-10
CENTRAL | November | On site to collect operational sample and continue work on ammonia system DICE blocks fittings. Maintenance on site. Both wells in auto upon leaving. | Queensville Wells No. 3 and 4 | 2025-11-17
WEST | November | On site for the following RHPSWA, JHSC Health and Safety Inspection, Woodland Acres Reservoir and WPS (1M) RHPSWA, Hoist System Inspection, Woodland Acres WPS (3M) KCETDS, King City Dufferin St Elevated Tank, Station Check, (1W) RHPSWA, Ventilation System Inspection, Woodland Acres WPS (1M) RHPSWA, PRV Valve Inspection, Woodland Acres, WPS(1M) RHPSWA, Pump & Motor Inspection, Woodland Acres WPS RHPSWA, Check Valve Service & Inspection, Woodland Acres WPS (3M) RHPSWA, Flood Alarm Test, Woodland Acres WPS (1M) RHPSWA, Discharge Valve & Actuator Exercise & Inspection, Woodland Acres WPS (1M) RHRSWA, Sump Pit System Inspection, Woodland Acres RES (1M) RHRSWA, Flood Alarm Test, Woodland Acres RES (1M) RHRSWA, High/Low Temperature Alarm Test, Woodland Acres RES (1M) RHRSWA, Dehumidifier Inspection & Cleaning, Woodland Acres RES (1M) RHRSWA, Manual Valve Exercise, Woodland Acres RES (?M) RHRSWA, Actuated Valve Exercise & Inspection, Woodland Acres RES (1M) RHRSWA, External Venting Screens Inspection, Woodland Acres RES (1M) RHRSWA, Air Valve Flush, Woodland Acres RES (3M) No issues | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2025-11-07
WEST | November | weekly sample W11347854 West cell @0935 Chlorine Free grab 0.04mg/L Total grab 1.32mg/L Sl1000 Total Chlorine 1.38mg/L FA 0.09mg/L TA 0.31mg/L Mono 1.10mg/L | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2025-11-05
WEST | November | Pumping Station Check Chlorine Grab (mg/L): Free: 0.05 Total: 1.62 No issues on site | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2025-11-03
WEST | November | On site for station check and to collect weekly sample W11402580 East cell @12:35 Chlorine Free grab 0.05mg/L Total grab 1.23mg/L No issues on site | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2025-11-26
WEST | November | Pumping Station Check Chlorine Grab (mg/L): Free: 0.06 Total: 1.77 No issues on site | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2025-11-28
WEST | November | On site for station check and to collect weekly sample W11386786 West cell @12:25 Chlorine Free grab 0.05mg/L Total grab 1.54mg/L Sl1000 Total Chlorine 1.58mg/L FA 0.12mg/L TA 0.37mg/L Mono 1.29mg/L No issues on site | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2025-11-19
WEST | November | Pumping Station Check Chlorine Grab (mg/L): Free: 0.06 Total: 1.70 No issues on site | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2025-11-24
WEST | November | Pumping Station Check Chlorine Grab (mg/L): Free: 0.05 Total: 1.66 No issues on site | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2025-11-20
WEST | November | RHPSWA&RHRSWA. Informed ROC. Onsite to perform annual calibrations. Used calibration mode during the work. Devices were done as below. reservoir 1&2 LIT, PD7 and woodland acre FITs, suction and discharge PIT, Station FIT. Informed ROC before and after calibration of reservoir LIT and Requested to switch over duty accordingly. Put everything back in service. All the related alarms were cleared. No issues. Informed ROC, armed the building and left the site. | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2025-11-27
WEST | November | Pumping Station Check Chlorine Grab (mg/L): Free: 0.05 Total: 1.62 No issues on site | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2025-11-14
WEST | November | On site for station check and to collect weekly sample W11368236 EAST cell @11:25 Chlorine Free grab 0.03mg/L Total grab 1.32mg/L Sl1000 Total Chlorine 1.32mg/L FA 0.13mg/L TA 0.35mg/L Mono 1.10mg/L No issues on site | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2025-11-12
WEST | November | Pumping Station Check Chlorine Grab (mg/L): Free: 0.05 Total: 1.91 No issues on site | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2025-11-17
CENTRAL | November | Investigated recirculating pump, found pressure gauge on outlet of pump to be defective. Replaced with new unit and tested pumps operation, produced approximately 50psi with 37psi of inlet pressure. No other issues to report. Returned pump to auto. | Richmond Hill Bloomington Elevated Tank | 2025-11-10
CENTRAL | November | -Responded power outage - set up portable generator - removed generator when city power restored - performed grab test to verify analyzer readings | Richmond Hill Bloomington Elevated Tank | 2025-11-03
CENTRAL | November | On-site for a station and equipment check, no issues found. Verified analyzers, all readings and grabs entered into PWQ sheet Weekly bacti sample taken. | Richmond Hill Bloomington Elevated Tank | 2025-11-05
CENTRAL | November | On-site for a station and equipment check, no issues found Weekly bacti sample taken, while draining Operational sample taken Changed both reagents in both analyzers Verified analyzers and entered all readings and grabs into PWQ sheet | Richmond Hill Bloomington Elevated Tank | 2025-11-26
CENTRAL | November | On-site for various WO's Notified ROC CL2 analyzer maintenance completed High and Low water level alarms tested JHSC inspection completed Heat trace inspection inlet and outlet Circulation pump run and inspected PRV valve visual inspection completed Low building temp alarms tested Visual inspection of ventilation system completed Comprehensive house cleaning | Richmond Hill Bloomington Elevated Tank | 2025-11-20
CENTRAL | November | On-site for a station and equipment check, no issues found Verified analyzers, entered all readings and grabs into PWQ sheet Took weekly bacti sample | Richmond Hill Bloomington Elevated Tank | 2025-11-19
CENTRAL | November | On-site for a station and equipment check. No issues found Verified analyzers, all readings and grabs entered into PWQ sheet Weekly bacti sample and operational samples taken | Richmond Hill Bloomington Elevated Tank | 2025-11-12
CENTRAL | November | On-site for a station and equipment check, no issues found Weekly bacti sample taken Verified analyzers and entered all readings into PWQ sheet. | Richmond Hill Coon's Elevated Tank | 2025-11-05
CENTRAL | November | On site to diagnose and repair inlet heat trace alarm. R/R RTD. Alarm cleared and unit operating properly. | Richmond Hill Coon's Elevated Tank | 2025-11-03
CENTRAL | November | On-site for a station and equipment check, no issues found Verified analyzers, all readings and grabs entered into PWQ sheet Weekly bacti sample taken General house keeping | Richmond Hill Coon's Elevated Tank | 2025-11-19
CENTRAL | November | On-site for a station and equipment check, no issues found Changed reagents in both analyzers Took bacti sample while draining Operational sample taken. Verified analyzers, entered all readings and grabs into PWQ sheet | Richmond Hill Coon's Elevated Tank | 2025-11-26
CENTRAL | November | Check valve lea | Richmond Hill Coon's Elevated Tank | 2025-11-12
CENTRAL | November | On-site for various WO's Inlet/outlet heat trace inspection completed Circulation pump inspection and test completed CL2 analyzer maintenance completed on both units PRV Valve inspection Low Temp alarm tests ok Ventilation visual inspection completed General housekeeping completed | Richmond Hill Coon's Elevated Tank | 2025-11-18
CENTRAL | November | On-site for a station and equipment check. No issues found Verified analyzers, all readings and grabs entered into PWQ sheet Weekly bacti sample and operational samples taken | Richmond Hill Coon's Elevated Tank | 2025-11-12
EAST | November | On site for station check Chlorine grabs, 13:00 Free Cl - 0.11 mg/L Total Cl - 1.58 mg/L Checked station and equipment Reviewed trends and recorded observations in the shared PWQ sheet Station and equipment okay | Richmond Hill Pugsley Pumping Station | 2025-11-10
EAST | November | On site to adjust the low fuel alarm on the generator. Dan and myself placed the generator into manual and called the roc at 1115 to notify them of the alarms from our work. We made our adjustment so that the generator will go into a warning and not fault at 20% fuel level. When complete we placed gen into auto and cleared alarms. Under direction of oic. | Richmond Hill Pugsley Pumping Station | 2025-11-03
EAST | November | Restarted the Operator Interface Terminal due to Windows updates. Notified the Remote Operations Center and the OIC | Richmond Hill Pugsley Pumping Station | 2025-11-03
EAST | November | On site to complete station check. Pumps are all in manual for the Elgin mills trial isolation. No outstanding alarms on site. No OOS equipment on site. Time: 14:05 Grab (mg/l) Free: 0.08 Total: 1.47 Checked site and trends. Entered data into PWQ sheet. | Richmond Hill Pugsley Pumping Station | 2025-11-03
EAST | November | On site for preventative maintenance work orders with Travis Wyatt Completed Surge valve inspection and maintenance Pumps 1-4 inspection Flood alarm test Housekeeping Control panel light inspection Butterfly valve exercise Generator test JHSC inspection Generator run, loaded Hours Start 370.6 Stop 272.2 Fuel Start 6689 L Stop 6676 L Oil pressure 64 PSI Coolant temperature 162 F Engine speed 1799 RPM Frequency 60 Hz Power 222 kW Current 219 A | Richmond Hill Pugsley Pumping Station | 2025-11-25
EAST | November | On site for station check Chlorine grabs: FCl 0.07 mg/L TCl 1.40 mg/L Recorded observations in the shared PWQ sheet Station and equipment okay | Richmond Hill Pugsley Pumping Station | 2025-11-28
EAST | November | Informed ROC. Performed annual calibration and put instruments in Cal mode while doing the tasks. Devices done were PITs, LIT, FIT and pressure switches. Pump 3 low pressure switch failed calibration and switch contact intermittently malfunctioning. It needs to be replaced and we will informed team lead Eric about it. At the moment, it does not give alarm. All alarms were cleared after the job. No other issues encountered. | Richmond Hill Pugsley Pumping Station | 2025-11-21
EAST | November | On site for station check Grabs: Free Cl - 0.08 mg/L Total Cl - 1.52 mg/L Recorded observations in the shared PWQ sheet Instrumentation remains on site performing annual calibrations Station and equipment okay | Richmond Hill Pugsley Pumping Station | 2025-11-21
EAST | November | Vibration testing | Richmond Hill Pugsley Pumping Station | 2025-11-18
EAST | November | On site for station check. Reviewed scada, duty active. Cell level @ 75 and 76% Visual inspection in and around station. Verification of equipment and instrumentation. Outstanding alarm: None Chlorine residual @ 14:27 hrs Efffluent: FCL= 0.11 mg/l. TCL = 1.65 mg/l P1~ Duty4 P2 ~Duty4 P3 ~ Duty1 P4 ~ Duty1 Station OK, recorded station readings in PWQ sheet. | Richmond Hill Pugsley Pumping Station | 2025-11-14
EAST | November | On site for station check Recorded observations in the shared PWQ and collected grabs Station and equipment okay | Richmond Hill Pugsley Pumping Station | 2025-11-17
WEST | November | -on site to complete station check and lab - plant duty active and high lift duty active -wells 3 and 4 in duty - KMnO4 pump 2 running at 16%, 58 psi, 64.9 ml/min - chlorinator 4 60% open, df 140%, 0.60 kg/hr, vac = -670 mbar - chlorinator 2 29% open, df 170%, 0.27 kg/hr, vac = -830 mbar - recorded data in PWQ sheet - checked equipment - CL17 reagents ok - reviewed trends - no issues found -completed wells 2,3,4 station checks -verified analyzers: 10:50 - high lift treated water TCL analyzer = 3.34 mg/L 10:50 - high lift treated water grab: FCL = 0.00 mg/L TCL = 3.38 mg/L Mono = 3.03 mg/L 10:58 - reservoir TCL analyzer = 3.71 mg/L 10:58 - reservoir grab: TCL = 3.80 mg/L Mono = 3.31 mg/L 11:06 - post filter TCL analyzer = 2.39 mg/L 11:06 - post filter grab: TCL = 2.42 mg/L -filled KMnO4 tank #1 15.7 cm to 80.9 cm -completed drawdowns on KMnO4 pumps: -adjusted pump #1 backpressure valve 65 to 75 psi -pump #1 max flow = 444 ml/min, adjusted scada setpoint 500 to 450 ml/min -pump #2 max flow = 400 ml/min, adjusted scada setpoint 412 to 405 ml/min -will monitor dosages -completed lab, results in PWQ sheet | Schomberg Water Treatment Plant & Wells 2-4 | 2025-11-07
WEST | November | -on site to complete work orders -informed ROC of work -completed cylinder change -completed Rotate chlorinator #4 duty: -vacuum tested chlorinator -put chlorinator #4 into duty for raw water chlorination -completed Filters 1-3, Turbidity Analyzer TU5300, Maintenance and Calibration: -all passed verification -completed UVT lens cleaning and unit flush -completed Diesel Generator Test Run -pre inspection ok -start hours = 532.1 -stop hours = 534.2 -run time = 2.1 hours -start fuel = 1850 L / 1844 L -stop fuel = 1828 L / 1818 L -fuel used = 22 L / 26 L 12:06 - transfer to generator power -activated plant and high lift duty 14:01 - transfer back to utility power -completed Transfer Pump and Motor Inspection -completed Check Valves Inspection, Schomberg WTP W3&4 -completed Electric Actuated Valves Inspection, Schomberg WTP W3&4 -completed Exhaust Fan Inspection, Schomberg WTP W3&4 -completed Pump and Motor Inspection, Schomberg WTP W3&4 -completed Dehumidifier Inspection, Schomberg WTP W3&4 -completed JHSC Health and Safety Inspection -completed Scrubber System Valves, Exercise -no issues, site back to normal operation | Schomberg Water Treatment Plant & Wells 2-4 | 2025-11-06
WEST | November | -on site to complete station check and lab - plant duty active and high lift duty active -wells 3 and 4 in duty - KMnO4 pump 1 running at 15%, 76 psi, 66.1 ml/min - chlorinator 4 61% open, df 140%, 0.60 kg/hr, vac = -690 mbar - chlorinator 2 31% open, df 178%, 0.32 kg/hr, vac = -830 mbar - recorded data in PWQ sheet - checked equipment - CL17 reagents ok - reviewed trends - no issues found -completed wells 2,3,4 station checks -verified analyzers: 09:55 - high lift treated water TCL analyzer = 3.31 mg/L 09:55 - high lift treated water grab: FCL = 0.00 mg/L TCL = 3.24 mg/L Mono = 2.91 mg/L 10:04 - reservoir TCL analyzer =3.84 mg/L 10:04 - reservoir grab: TCL = 3.74 mg/L Mono = 3.58 mg/L 10:13 - post filter TCL analyzer = 2.38 mg/L 10:13 - post filter grab: TCL = 2.44 mg/L -rotated reservoir cells, sample lines and sample pump duties, north cell now in service -filled KMnO4 tank #2 15.8 cm to 84.0 cm -cleaned high lift turbidimeter vial -completed lab, results in PWQ sheet -completed High Lift Discharge Check Valves, Service and Inspection -completed High Lift Pumps, Inspection -completed High Lift Discharge Pressure Relief Valve, Inspection and Test -completed High Lift Pump, Air Relief Valves, Inspection -completed High Lift Actuated Valves, Exercise and Inspection -completed Hoist, Inspection -completed Valve, Butterfly, Surge Tank Isolation, Exercise -completed Fire Pumps and Motors, Inspection -no issues, site back to normal operation | Schomberg Water Treatment Plant & Wells 2-4 | 2025-11-10
WEST | November | -on site to complete station check, lab and to collect samples -sample work order # W11347882 - plant duty active, high lift duty active - KMnO4 pump 1 running at 13%, 66 psi, 65.5 ml/min - chlorinator 1 62% open, df 140%, 0.58 kg/hr, vac = -680 mbar - chlorinator 2 30% open, df 174%, 0.30 kg/hr, vac = -820 mbar - recorded data in PWQ sheet - checked equipment - CL17 reagents ok - reviewed trends - no issues found 09:20 - collected weekly well #3 raw water micro sample 09:20 - collected weekly well #4 raw water micro sample -verified analyzers: 09:37 - high lift treated water TCL analyzer = 3.49 mg/L 09:37 - high lift treated water grab: FCL = 0.03 mg/L TCL = 3.50 mg/L Mono = 3.19 mg/L 09:43 - collected weekly treated water micro sample 09:45 - reservoir TCL analyzer = 3.76 mg/L 09:45 - reservoir grab: TCL = 3.70 mg/L Mono = 3.50 mg/L 09:55 - post filter TCL analyzer = 2.38 mg/L 09:55 - post filter grab: TCL = 2.46 mg/L -completed well #2 station check 10:35 - collected weekly well #2 raw water micro sample -completed lab, results in PWQ sheet -completed Compressed Air System, Inspection -completed Backwash Sump Tank System, Inspection | Schomberg Water Treatment Plant & Wells 2-4 | 2025-11-05
WEST | November | -on site to complete work orders -informed ROC of work -completed CL-17sc Analyzer, Maintenance: -cleaned analyzers, flushed sample lines -verified analyzers after maintenance: 09:49 - high lift treated water TCL analyzer = 3.28 mg/L 09:49 - high lift treated water grab: TCL = 3.30 mg/L 13:09 - reservoir TCL analyzer = 3.63 mg/L 13:09 - reservoir grab: TCL = 3.58 mg/L 13:11 - post filter TCL analyzer = 2.43 mg/L 13:11 - post filter grab: TCL = 2.46 mg/L -completed Chlorine Cylinder Emergency Repair Kit Inspection -completed Chlorine Leak Detector, Test -completed Chlorine Scrubber, Check -completed Chemical System Inspection - Chlorine: -completed vacuum test on chlorinators 1 and 2, no issues -completed KMnO4 Injection Point Cleaning -completed KMNO4 Feed Pumps, Service: -pump #1 max flow = 540 ml/min, increased SCADA max flow setpoint from 460 to 500 ml/min, will monitor dosage calculation -pump #2 max flow = 400 ml/min, SCADA setpoint = 412 ml/min -completed Transfer Pump Air Relief Valves, Inspection -made following process adjustments due to increased filter effluent iron: -decreased plant flow from 40 to 34 l/s -decreased filter #1 max flow from 14 to 12 l/s -decreased filter #2 max flow from 14 to 12 l/s -decreased filter #3 max flow from 12 to 10 l/s -site back to normal operation -activated plant duty and tested chemical systems - no issues | Schomberg Water Treatment Plant & Wells 2-4 | 2025-11-04
WEST | November | -on site to complete station check and lab - plant duty active, activated high lift duty -wells 3 and 4 in duty - KMnO4 pump 1 running at 17%, 66 psi, 78.8 ml/min - chlorinator 1 74% open, df 140%, 0.69 kg/hr, vac = -600 mbar - chlorinator 2 35% open, df 168%, 0.33 kg/hr, vac = -820 mbar - recorded data in PWQ sheet - checked equipment - CL17 reagents ok - reviewed trends - no issues found -completed wells 2,3,4 station checks -completed high lift turbidimeter verification -verified analyzers: 11:07 - reservoir TCL analyzer = 3.86 mg/L 11:07 - reservoir grab: TCL = 3.90 mg/L Mono = 3.56 mg/L 11:16 - high lift treated water TCL analyzer = 3.33 mg/L 11:16 - high lift treated water grab: FCL = 0.00 mg/L TCL = 3.36 mg/L Mono = 3.21 mg/L 11:23 - post filter TCL analyzer = 2.38 mg/L 11:23 - post filter grab: TCL = 2.38 mg/L -filled KMnO4 tank #2 15.9 cm to 82.4 cm -completed lab, results in PWQ sheet | Schomberg Water Treatment Plant & Wells 2-4 | 2025-11-03
WEST | November | -on site to respond to KMnO4 pump 2 leakage and fault alarms -scada showing pump 2 in local after power blip, found pump with communications fault -cycled power to pump - fault cleared -cleaned high lift and filter turbidimeter vials due to frequent high ntu alarms -flushed filter turbidity sample lines -activated plant duty and monitored start up -observed KMnO4 pump 2 run in auto -no issues | Schomberg Water Treatment Plant & Wells 2-4 | 2025-11-01
WEST | November | -on site to complete station check and lab - plant duty active, activated high lift duty active -wells 3 and 4 in duty - KMnO4 pump 1 running at 14.5%, 70 psi, 65.2 ml/min - chlorinator 4 61% open, df 140%, 0.62 kg/hr, vac = -690 mbar - chlorinator 2 27% open, df 160%, 0.27 kg/hr, vac = -840 mbar - recorded data in PWQ sheet - checked equipment - CL17 reagents ok - reviewed trends - no issues found -completed wells 2,3,4 station checks -verified analyzers: 11:16 - high lift treated water TCL analyzer = 3.31 mg/L 11:16 - high lift treated water grab: FCL = 0.00 mg/L TCL = 3.36 mg/L Mono = 2.96 mg/L 11:24 - reservoir TCL analyzer = 3.84 mg/L 11:24 - reservoir grab: TCL = 3.80 mg/L Mono = 3.55 mg/L 11:43 - post filter TCL analyzer = 2.42 mg/L 11:43 - post filter grab: TCL = 2.40 mg/L -filled KMnO4 tank #2 15.5 cm to 81.8 cm -increased KMnO4 pump #1 max flow setpoint 455 to 465 ml/min based on dosage calculation -completed lab, results in PWQ sheet | Schomberg Water Treatment Plant & Wells 2-4 | 2025-11-27
WEST | November | -on site to complete station check and lab - plant duty active and high lift duty active -wells 2 and 3 in duty - KMnO4 pump 1 running at 10.6%, 70 psi, 46.4 ml/min - chlorinator 4 41% open, df 140%, 0.38 kg/hr, vac = -780 mbar - chlorinator 2 23% open, df 168%, 0.23 kg/hr, vac = -860 mbar - recorded data in PWQ sheet - checked equipment - CL17 reagents ok - reviewed trends - no issues found -completed wells 2,3,4 station checks -verified analyzers: 10:07 - high lift treated water TCL analyzer = 3.30 mg/L 10:07 - high lift treated water grab: FCL = 0.02 mg/L TCL = 3.26 mg/L Mono = 3.01 mg/L 10:13 - reservoir TCL analyzer = 3.64 mg/L 10:13 - reservoir grab: TCL = 3.66 mg/L Mono = 3.07 mg/L 10:20 - post filter TCL analyzer = 2.37 mg/L 10:20 - post filter grab: TCL = 2.40 mg/L -increased KMnO4 pump #1 max flow setpoint 450 to 455 ml/min based on dosage calculation -completed lab, results in PWQ sheet | Schomberg Water Treatment Plant & Wells 2-4 | 2025-11-20
WEST | November | Attending site to check RW_GLEL1 gas monitor (W11397861). Found in line filter was plugged. Removed unnecessary filter and cleared alarm. | Schomberg Water Treatment Plant & Wells 2-4 | 2025-11-25
WEST | November | Onsit work investigate filter 1 negative ntu value On arrival noticed ntu analyzer was left on hold out put and had vial clarity error message | Schomberg Water Treatment Plant & Wells 2-4 | 2025-11-21
WEST | November | -on site to complete station check and lab - plant duty active and high lift duty active -wells 3 and 4 in duty - KMnO4 pump 2 running at 10.6%, 58 psi, 41.2 ml/min - chlorinator 4 40% open, df 140%, 0.40 kg/hr, vac = -720 mbar - chlorinator 2 19% open, df 170%, 0.18 kg/hr, vac = -860 mbar - recorded data in PWQ sheet - checked equipment - CL17 reagents ok - reviewed trends - no issues found -completed wells 2,3,4 station checks -verified analyzers: 10:38 - reservoir TCL analyzer = 3.80 mg/L 10:38 - reservoir grab: TCL = 3.76 mg/L Mono = 3.35 mg/L 10:47 - high lift treated water TCL analyzer = 3.34 mg/L 10:47 - high lift treated water grab: FCL = 0.00 mg/L TCL = 3.36 mg/L Mono = 3.01 mg/L 11:00 - post filter TCL analyzer = 2.42 mg/L 11:00 - post filter grab: TCL = 2.38 mg/L -filled KMnO4 tank #1 15.7 cm to 84.3 cm -switched to south reservoir cell, rotated sample lines and pumps -completed lab, results in PWQ sheet | Schomberg Water Treatment Plant & Wells 2-4 | 2025-11-24
WEST | November | On site to replace raw cl2 ejector due to crack on head (where vacuum gauge attaches). Notified ROC of potential alarms related to maintenance. Shutdown SHTP, replaced raw ejector and tested. Shortened tubing length from vacuum gauge to ejector (may be putting additional strain on ejector upper body. Upper body is delicate and prone to cracking / failure). Tested vacuum, holding up to -800mmHg. Placed SHTP back in service and monitored vacuum, rotameter. Appears working correctly. | Schomberg Water Treatment Plant & Wells 2-4 | 2025-11-28
WEST | November | -on site to complete station check, lab and to collect samples -sample work order # W11386814 - plant duty active, high lift duty active - KMnO4 pump 1 running at 16.5%, 70 psi, 73.6 ml/min - chlorinator 4 59% open, df 140%, 0.57 kg/hr, vac = -700 mbar - chlorinator 2 32% open, df 182%, 0.32 kg/hr, vac = -840 mbar - recorded data in PWQ sheet - checked equipment - replaced reservoir CL17 reagents - reviewed trends - no issues found -verified analyzers: 09:08 - high lift treated water TCL analyzer = 3.40 mg/L 09:08 - high lift treated water grab: FCL = 0.04 mg/L TCL = 3.42 mg/L Mono = 3.10 mg/L 09:19 - collected weekly treated water micro sample 09:23 - reservoir TCL analyzer = 3.72 mg/L 09:23 - reservoir grab: TCL = 3.76 mg/L Mono = 3.43 mg/L 09:42 - post filter TCL analyzer = 2.38 mg/L 09:42 - post filter grab: TCL = 2.42 mg/L 09:49 - collected weekly well #3 raw water micro sample 09:49 - collected weekly well #4 raw water micro sample -collected monthly raw water iron and manganese sample - W/O # W11306350 -collected monthly filter effluent iron and manganese samples - W/O # 11348018 -increased KMnO4 pump #1 max flow setpoint 440 to 450 ml/min based on dosage calculation -completed well #2 station check 10:40 - collected weekly well #2 raw water micro sample -filled KMnO4 tank #2 15.6 cm to 82.9 cm -completed lab, results in PWQ sheet | Schomberg Water Treatment Plant & Wells 2-4 | 2025-11-19
WEST | November | Flushed filter 1 ntu analyzer | Schomberg Water Treatment Plant & Wells 2-4 | 2025-11-21
WEST | November | -on site to complete station check, lab and to collect samples -sample work order # W11402542 - plant duty active, high lift duty active - KMnO4 pump 2 running at 16.5%, 58 psi, 65.8 ml/min - chlorinator 4 61% open, df 140%, 0.58 kg/hr, vac = -700 mbar - chlorinator 2 30% open, df 162%, 0.30 kg/hr, vac = -840 mbar - recorded data in PWQ sheet - checked equipment - CL17 reagents ok - reviewed trends - no issues found -verified analyzers: 08:32 - high lift treated water TCL analyzer = 3.16 mg/L 08:32 - high lift treated water grab: FCL = 0.04 mg/L TCL = 3.10 mg/L Mono = 2.78 mg/L 08:37 - collected weekly treated water micro sample 08:40 - reservoir TCL analyzer = 3.73 mg/L 08:40 - reservoir grab: TCL = 3.66 mg/L Mono = 3.29 mg/L 08:46 - post filter TCL analyzer = 2.30 mg/L 08:46 - post filter grab: TCL = 2.38 mg/L 09:03 - power blip occurred shutting down plant, no UV alarms received -cleaned high lift turbidimeter vial -completed well #2 station check 09:50 - collected weekly well #2 raw water micro sample 11:18 - collected weekly well #3 raw water micro sample 11:18 - collected weekly well #4 raw water micro sample -completed lab, results in PWQ sheet | Schomberg Water Treatment Plant & Wells 2-4 | 2025-11-26
WEST | November | -on site to complete hypo cleans on filters -depressurized filters and added 4 L of hypo to each -drained filters to waste until chlorine residual reached bottom of filter -mixed filters with air scour -after soak completed rinsed filters to waste until chlorine residual at bottom of filters had returned to normal -activated plant duty, will monitor start up | Schomberg Water Treatment Plant & Wells 2-4 | 2025-11-25
WEST | November | increased KMnO4 pump 1 max flow 435 to 440 ml/min based on dosage calculation | Schomberg Water Treatment Plant & Wells 2-4 | 2025-11-12
WEST | October | Entry to document site power blip. Site power failure alarm occurred 0802. No UV alarms generated. UV system appears to have shutdown accordingly, UV doses above 40mj/cm2 while filter discharge registered flow. | Schomberg Water Treatment Plant & Wells 2-4 | 2025-10-18
WEST | October | Entry is to document site power blip. Power Failure alarm triggered at 0546. No UV alarms were generated. UV system appears to have shut down accordingly, trending shows UV doses above 40mj/cm2 while flow registered on Filter Discharge. | Schomberg Water Treatment Plant & Wells 2-4 | 2025-10-19
WEST | November | Well 2 Station check #11368198 raw bact. sample (11:25) | Schomberg Water Treatment Plant & Wells 2-4 | 2025-11-11
WEST | November | Received call for post UV analyzer lolo and fault alarms. Rotated sample pump duties and residual recovered. | Schomberg Water Treatment Plant & Wells 2-4 | 2025-11-18
WEST | November | -on site to complete station check and lab - plant duty active and high lift duty active -wells 2 and 3 in duty -completed cylinder change - KMnO4 pump 2 running at 17.5%, 58 psi, 70.6 ml/min - chlorinator 4 61% open, df 140%, 0.58 kg/hr, vac = -700 mbar - chlorinator 2 34% open, df 182%, 0.33 kg/hr, vac = -830 mbar - recorded data in PWQ sheet - checked equipment - CL17 reagents ok - reviewed trends - no issues found -completed wells 2,3,4 station checks -verified analyzers: 09:29 - high lift treated water TCL analyzer = 3.47 mg/L 09:29 - high lift treated water grab: FCL = 0.00 mg/L TCL = 3.42 mg/L Mono = 3.18 mg/L 09:38 - reservoir TCL analyzer = 3.78 mg/L 09:38 - reservoir grab: TCL = 3.70 mg/L Mono = 3.31 mg/L 09:46 - post filter TCL analyzer = 2.33 mg/L 09:46 - post filter grab: TCL = 2.38 mg/L -cleaned high lift turbidimeter vial -completed lab, results in PWQ sheet | Schomberg Water Treatment Plant & Wells 2-4 | 2025-11-17
WEST | November | -on site to collect samples -sample work order # W11368198 08:56 - high lift treated water TCL analyzer = 3.40 mg/L 08:56 - high lift treated water grab: FCL = 0.04 mg/L TCL = 3.34 mg/L 09:00 - collected weekly treated water micro sample 10:05 - collected weekly well #3 raw water micro sample 10:05 - collected weekly well #4 raw water micro sample -completed UV Reactors, Sensor Check -all sensors passed verification -ran UV#2 in local with cooling valves open to complete sensor check -no issues, UV2 returned to OOS -completed drawdown on KMnO4 pump #1 - max flow = 432 ml/min -adjusted SCADA setpoint 450 to 435 ml/min, will monitor dosage | Schomberg Water Treatment Plant & Wells 2-4 | 2025-11-11
WEST | November | -on site to respond to reservoir chlorine analyzer LOLO and fault alarms -found sample pump #1 tubing leaking, no flow to analyzer -replaced tubing and flushed sample lines -analyzer back in service -verified analyzer: 06:12 - analyzer reading = 3.73 mg/L Grab = 3.74 mg/L -completed Low/High Temperature Alarm, Test -completed High/Low Temperature Alarm, Test, Schomberg Well 2 -completed Pressure Relief Valve, Inspection, Schomberg Well 2 -completed Actuated Valve, Exercise, Schomberg Well 2 -completed JHSC Health and Safety Inspection, Schomberg Well 2 -site back to normal operation | Schomberg Water Treatment Plant & Wells 2-4 | 2025-11-18
WEST | November | -on site to complete station check and lab - plant duty active and high lift duty active -wells 2 and 3 in duty - KMnO4 pump 1 running at 16%, 72 psi, 70.5 ml/min - chlorinator 4 61% open, df 140%, 0.59 kg/hr, vac = -700 mbar - chlorinator 2 28% open, df 176%, 0.27 kg/hr, vac = -830 mbar - recorded data in PWQ sheet - checked equipment - CL17 reagents ok - reviewed trends - no issues found -completed wells 2,3,4 station checks -verified analyzers: 09:09 - high lift treated water TCL analyzer = 3.48 mg/L 09:09 - high lift treated water grab: FCL = 0.00 mg/L TCL = 3.52 mg/L Mono = 3.12 mg/L 09:20 - reservoir TCL analyzer = 3.71 mg/L 09:20 - reservoir grab: TCL = 3.64 mg/L Mono = 3.40 mg/L 09:26 - post filter TCL analyzer = 2.44 mg/L 09:26 - post filter grab: TCL = 2.46 mg/L -filled KMnO4 tank #1 16.6 cm to 82.5 cm -completed lab, results in PWQ sheet -reduced filter #1 runtime limit 20 to 18 hours based on high effluent iron | Schomberg Water Treatment Plant & Wells 2-4 | 2025-11-14
WEST | November | On site for station check Rechlor Pre inj (mg/L) Fcl Analyzer: 0.02; Grab: 0.05 TCL Analyzer: 1.61; Grab: 1.79 Fa Analyzer: 0.10; Grab: 0.07 Ta Analyzer: 0.41; Grab: 0.36 Mcl Analyzer: 1.54; Grab: 1.48 Adjusted depolox total from 1.61-1.79mg/L after multiple grabs and chemscan Post inj Fcl Analyzer: 0.02; Grab: 0.05 TCL Analyzer: 1.99; Grab: 2.10 Fa Analyzer: 0.03; Grab: 0.09 Ta Analyzer: 0.42; Grab: 0.43 Mcl Analyzer: 1.90; Grab: 1.75 Reagents all okay | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2025-11-07
WEST | November | On site for station check Rechlor Pre inj (mg/L) Fcl Analyzer: 0.01; Grab: 0.05 TCL Analyzer: 1.71; Grab: 1.81 Fa Analyzer: 0.08; Grab: 0.10 Ta Analyzer: 0.41; Grab: 0.39 Mcl Analyzer: 1.50; Grab: 1.50 Post inj Fcl Analyzer: 0.02; Grab: 0.05 TCL Analyzer: 2.17; Grab: 2.20 Fa Analyzer: 0.03; Grab: 0.09 Ta Analyzer: 0.42; Grab: 0.43 Mcl Analyzer: 1.90; Grab: 1.75 Reagents all okay | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2025-11-10
WEST | November | RHRSTR, JHSC Health and Safety Inspection, East Vaughan BPS, South Richmond Hill RES (1M) VNPSCD, Chemscan Analyzer Maintenance, East VaughanDisinfection Building (1M) Pre inj (mg/L) TCL Analyzer: 1.70; Grab: 1.72 Fa Analyzer: 0.07; Grab: 0.12 Ta Analyzer: 0.44; Grab: 0.40 Mcl Analyzer: 1.45; Grab: 1.53 Post inj TCL Analyzer: 2.10; Grab: 2.14 Fa Analyzer: 0.04; Grab: 0.12 Ta Analyzer: 0.46; Grab: 0.48 Mcl Analyzer: 2.00; Grab: 1.83 VPSCD, Ammonia Feed and Storage Inspection, East Vaughan Disinfection Building (1M) VNPSCD, Chlorine Scrubber Inspection, East Vaughan Disinfection Building (1M) VNPSCD, Chlorine Leak Detector Test, East Vaughan Disinfection Building (1M) VNPSCD, Chlorine Analyzer Maintenance, East Vaughan Disinfection Building (1M) - topped up all reagents VNPS, Chlorine Analyzer Maintenance, East Vaughan Pumping Station (1M) - topped up Ki VPS, Standby Power Generator Test Run and Run Hours log, East Vaughan Pumping Station (1M) Gen start hours 232.0 stop hours 233.1 Fuel start 51% 7038L 78% 1971L day tank Fuel stop 49% 6762L 74% 1870L VNPS, Process Mechanical Air valve flush and inspection PD7, East Vaughan Pumping Station (1M) VNPS, Process Mechanical Air valve flush and inspection PD8, East Vaughan Pumping Station (1M) VPS, Hoist System Inspection, East Vaughan Pumping Station (3M) VPSCD, Chemical System Inspection - Chlorine, East Vaughan Disinfection Building (1M) | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2025-11-04
WEST | November | On site for station check and to collect weekly back same w11347854 Reservoir @10:20 am North Cell Sample Tap: Total: 1.85 mg/L Free: 0.06 mg/L SL1000 TCL 1.81mg/L FA 0.08mg/L TA 0.43mg/L Mono 1.81mg/L West Cell Sample Tap: Total: 1.86mg/L Free: 0.06mg/L South Cell Sample Tap: Total: 1.72mg/L Free: 0.04mg/L Rechlor Pre inj (mg/L) Fcl Analyzer: 0.01; Grab: 0.04 TCL Analyzer: 1.72; Grab: 1.89 Fa Analyzer: 0.12; Grab: 0.10 Ta Analyzer: 0.48; Grab: 0.42 Mcl Analyzer: 1.63; Grab: 1.59 Post inj Fcl Analyzer: 0.02; Grab: 0.05 TCL Analyzer: 2.15; Grab: 2.24 Fa Analyzer: 0.04; Grab: 0.07 Ta Analyzer: 0.46; Grab: 0.44 Mcl Analyzer: 2.07; Grab: 1.90 Reagents all okay | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2025-11-05
WEST | November | On site for station check Rechlor Pre inj (mg/L) Fcl Analyzer: 0.00; Grab: 0.04 TCL Analyzer: 1.78; Grab: 1.87 Fa Analyzer: 0.08; Grab: 0.10 Ta Analyzer: 0.41; Grab: 0.45 Mcl Analyzer: 1.73; Grab: 1.76 Post inj Fcl Analyzer: 0.02; Grab: 0.04 TCL Analyzer: 2.05; Grab: 2.17 Fa Analyzer: 0.04; Grab: 0.09 Ta Analyzer: 0.41; Grab: 0.46 Mcl Analyzer: 1.97; Grab: 1.84 Reagents all okay | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2025-11-03
WEST | November | On site for station check Rechlor Pre inj (mg/L) Fcl Analyzer: 0.00; Grab: 0.05 TCL Analyzer: 1.65; Grab: 1.71 Fa Analyzer: 0.09; Grab: 0.09 Ta Analyzer: 0.41; Grab: 0.38 Mcl Analyzer: 1.53; Grab: 1.48 Post inj Fcl Analyzer: 0.02; Grab: 0.05 TCL Analyzer: 2.01; Grab: 2.06 Fa Analyzer: 0.03; Grab: 0.05 Ta Analyzer: 0.38; Grab: 0.44 Mcl Analyzer: 1.89; Grab: 1.74* *rechlor not active but will continue to monitor mono reading Changed out all CHEMscan reagents | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2025-11-20
WEST | November | On site for station check and to collect weekly back same w11386786 Reservoir @11:05am North Cell Sample Tap: Total: 2.05mg/L Free: 0.05mg/L SL1000 TCL 2.02mg/L FA 0.08mg/L TA 0.41mg/L Mono 1.68mg/L Nitrite 0.001mg/L West Cell Sample Tap: Total: 1.84mg/L Free: 0.05mg/L South Cell Sample Tap: Total: 1.82mg/L Free: 0.06mg/L Rechlor Pre inj (mg/L) Fcl Analyzer: 0.00; Grab: 0.04 TCL Analyzer: 2.06; Grab: 2.07 Fa Analyzer: 0.03; Grab: 0.08 Ta Analyzer: 0.44; Grab: 0. Mcl Analyzer: 1.81; Grab: 1.82 Nitrite: Grab: 0.001 Post inj Fcl Analyzer: 0.02; Grab: 0.05 TCL Analyzer: 2.17; Grab: 2.17 Fa Analyzer: 0.02; Grab: 0.06 Ta Analyzer: 0.39; Grab: 0.43 Mcl Analyzer: 1.93; Grab: 1.85 | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2025-11-19
WEST | November | On site for station check Rechlor Pre inj (mg/L) Fcl Analyzer: 0.00; Grab: 0.05 TCL Analyzer: 1.96; Grab: 2.05 Fa Analyzer: 0.08; Grab: 0.10 Ta Analyzer: 0.45; Grab: 0.44 Mcl Analyzer: 1.76; Grab: 1.72 Post inj Fcl Analyzer: 0.02; Grab: 0.04 TCL Analyzer: 2.21; Grab: 2.22 Fa Analyzer: 0.02; Grab: 0.06 Ta Analyzer: 0.41; Grab: 0.46 Mcl Analyzer: 2.03; Grab: 1.92 Reagents all ok Topped up ammonia tank 2 from 15-75cm | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2025-11-28
WEST | November | On site for station check and to collect weekly back same w11402580 Reservoir @11:15am North Cell Sample Tap: Total: 2.13mg/L Free: 0.06mg/L SL1000 TCL 2.13mg/L FA 0.13mg/L TA 0.48mg/L Mono 1.76mg/L West Cell Sample Tap: Total: 2.02mg/L Free: 0.05mg/L South Cell Sample Tap: Total: 1.98mg/L Free: 0.05mg/L Rechlor Pre inj (mg/L) Fcl Analyzer: 0.00; Grab: 0.05 TCL Analyzer: 1.83; Grab: 1.93 Fa Analyzer: 0.08; Grab: 0.11 Ta Analyzer: 0.41; Grab: 0.43 Mcl Analyzer: 1.72; Grab: 1.64 Post inj Fcl Analyzer: 0.02; Grab: 0.05 TCL Analyzer: 2.10; Grab: 2.06 Ran out of chemkeys Reagents all okay | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2025-11-26
WEST | November | On site for station check Rechlor Pre inj (mg/L) Fcl Analyzer: 0.00; Grab: 0.05 TCL Analyzer: 1.58; Grab: 1.62 Fa Analyzer: 0.05; Grab: 0.06 Ta Analyzer: 0.40; Grab: 0.37 Mcl Analyzer: 1.48; Grab: 1.39 Post inj Fcl Analyzer: 0.02; Grab: 0.05 TCL Analyzer: 2.05; Grab: 2.09 Fa Analyzer: 0.02; Grab: 0.07 Ta Analyzer: 0.41; Grab: 0.45 Mcl Analyzer: 1.92; Grab: 1.78** Topped up ammonia tank 1 from 15-75cm | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2025-11-24
WEST | November | On site for station check Rechlor Pre inj (mg/L) Fcl Analyzer: 0.00; Grab: 0.04 TCL Analyzer: 1.79; Grab: 1.85 Fa Analyzer: 0.10; Grab: 0.07 Ta Analyzer: 0.40; Grab: 0.38 Mcl Analyzer: 1.53; Grab: 1.55 Nitrite: Grab: 0.001 Post inj Fcl Analyzer: 0.02; Grab: 0.05 TCL Analyzer: 2.20; Grab: 2.22 Fa Analyzer: 0.03; Grab: 0.04 Ta Analyzer: 0.41; Grab: 0.41 Mcl Analyzer: 1.99; Grab: 1.86 Nitrite: Grab: 0.001 On site with Jake to change chlorine cylinder bank 2 from 0.7-68kg | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2025-11-17
WEST | November | On site for station check Rechlor Pre inj (mg/L) Fcl Analyzer: 0.00; Grab: 0.04 TCL Analyzer: 1.68; Grab: 1.77 Fa Analyzer: 0.08; Grab: 0.07 Ta Analyzer: 0.41; Grab: 0.37 Mcl Analyzer: 1.52; Grab: 1.51 Nitrite: Grab: 0.000 Post inj Fcl Analyzer: 0.02; Grab: 0.05 TCL Analyzer: 2.19-2.36; Grab: 2.36 Fa Analyzer: 0.02; Grab: 0.05 Ta Analyzer: 0.39; Grab: 0.44 Mcl Analyzer: 2.04; Grab: 1.98 Nitrite: Grab: 0.001 Adjusted Post total from 2.19-2.36mg/L after multiple grabs Topped up ammonia tank 2 from 15-75cm Reagents all okay | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2025-11-14
WEST | November | On site for station check and to collect weekly back same w11368236 Reservoir @10:35 am North Cell Sample Tap: Total: 1.98 mg/L Free: 0.05mg/L SL1000 TCL 2.01mg/L FA 0.07mg/L TA 0.40mg/L Mono 1.66mg/L West Cell Sample Tap: Total: 1.81mg/L Free: 0.04mg/L South Cell Sample Tap: Total: 1.83mg/L Free: 0.05mg/L Rechlor Pre inj (mg/L) Fcl Analyzer: 0.01; Grab: 0.04 TCL Analyzer: 1.72; Grab: 1.81 Fa Analyzer: 0.06; Grab: 0.08 Ta Analyzer: 0.38; Grab: 0.38 Mcl Analyzer: 1.55; Grab: 1.53 Post inj Fcl Analyzer: 0.02; Grab: 0.05 TCL Analyzer: 1.73; Grab: 1.82 Fa Analyzer: 0.04; Grab: 0.08 Ta Analyzer: 0.38; Grab: 0.39 Mcl Analyzer: 1.69; Grab: 1.56 Reagents all okay | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2025-11-12
LINEAR | November | On Nov. 4th Closed the mainline valve on Hwy 27 just outside of the HWY 27 ET property. Isolated and drained the water main from the ET to the aforementioned valve. Nov 5th reopened the mainline valve on HWY 27 Filled the water main to the ET, flushed and took residuals. Total - 1.83 mg/l and Free - 1.62 mg/l. Helped west operator put the ET back online. | Linear Water System | 2025-11-05
LINEAR | November | NMVCBA Onsite to replace failed upstream pressure transmitter Informed ROC. Completed CSE permit. Removed failed PIT. Replaced with new PIT , configured and calibrated Verified readings on scada Closed CSE permit. Informed ROC and left site All pending alarms cleared | Linear Water System | 2025-11-07
LINEAR | November | Attending site to check Upstream VC_PIT1 (W11432048). PIT was replaced last week but continues to bounce between full-scale and open loop. Tightened all related terminals in an effort to eliminate the issue. Suspect that the PAC analog input module may be causing the issues. When this PIT powers on, it goes to about 55% of its span. The trending shows the PIT going to maximum then below minimum which is not typical failure behavior. When the old PIT was replaced last week, it was found to be in working condition. If the problem persists, I will ask PCS to check out the PAC side. ROC was notified before and after maintenance work. | Linear Water System | 2025-11-10
LINEAR | November | Air valve mods on Steeles west of Highway 400 chamber 23-04. North Rock replaced 2 air valves. Chlorine residual- 0.97 mg/l total and 0.02 mg/l free. | Linear Water System | 2025-11-07
LINEAR | November | Replenished dechlorination pucks at McCowan an Stoufville break site. Chlorine residuals Free - 0.04 mg/l Total - 0.00 mg/l | Linear Water System | 2025-11-29
LINEAR | November | Added dechlor pucks at the watermain leak on Stoufville rd. Chlorine residuals Free - 1.80 mg/l Total - 1.84 mg/l | Linear Water System | 2025-11-22
LINEAR | November | Stoufville and McCowan watermain break site. Replenished dechlorination pucks. Residuals Free - 0.03 mg/l | Linear Water System | 2025-11-26
LINEAR | November | A watermain leak was discovered on the 600mm main on Stouffville rd. east of McCowan. Planning to repair the leak is underway and dechlorination will be taking place until the repair is complete. | Linear Water System | 2025-11-21
LINEAR | November | Replenished declorination pucks at 600mm watermain leak site on Stouffville sideroad east of McCowan road. Grab chlorine residuals, free-0.00mg/l total- 0.00mg/l | Linear Water System | 2025-11-30
LINEAR | November | Added declination pucks at the watermain leak on Stouffville Rd. Chlorine residuals Free - 0.00 mg/l Total - 0.00 mg/l | Linear Water System | 2025-11-24
LINEAR | November | Replenished dechlorination pucks at McCowan an Stoufville break site. Chlorine residuals Free - 0.00 mg/l Total - 0.00 mg/l | Linear Water System | 2025-11-28
LINEAR | November | Added declination pucks at the watermain leak on Stoufville rd. Chlorine residuals Free - 1.34 mg/l Total - 2.08 mg/l | Linear Water System | 2025-11-23
LINEAR | November | Replenished dechlorination pucks at McCowan an Stoufville break site. Chlorine residuals Free - 0.00 mg/l Total - 0.00 mg/l | Linear Water System | 2025-11-27
LINEAR | November | Isolated the watermain along 14th ave from Milliken pumping station to Noble Ave in Markham. Relieved pressure in main so contractors could replace isolation and air valves in chamber at Noble. Upon completion the isolation valve and air valve were exercised. Performed an inspection for leaks as well. A residual was taken. Free - 0.07 mg/l Total - 1.59 mg/l The air valve was put into service and all valves were reopened and the watermain put back into service. | Linear Water System | 2025-11-27
LINEAR | November | Stoufville and McCowan watermain break site. Replenished dechlorination pucks. Residuals Free - 0.00 mg/l Total - 0.00 mg/l | Linear Water System | 2025-11-25
LINEAR | November | 10:35 - Isolated air valve in the chamber T0426-06 at around 10:30 am for the AV mods work. 16:45 - AV was replaced by North Rock and was put back in service around 4:40 pm and I grabbed a CL2 residuals. Total Chlorine Residual : 2.01 mg/L Free Chlorine Residual : 0.19 mg/L | Linear Water System | 2025-11-20
LINEAR | November | Steeles Avenue W & Sante Drive System Back to Normal Operation Chlorine Residuals Total: 1.47 mg/L Free: 0.14 mg/L | Linear Water System | 2025-11-11
LINEAR | November | ANVC Onsite for annual calibrations Informed ROC and created CSE permit Used cal mode on scada during the work Instruments calibrated: FIT, PITs and FCV Cleared pending alarms Informed ROC, closed CSE permit and left site No issues | Linear Water System | 2025-11-14
LINEAR | November | Assisted with isolation valve replacement on 16th just east of Warden. Air valve isolation valve and nipple replaced. Residuals - free - 0.03 mg/l total - 1.14 mg/l All valves reopened and the portion of watermain on 16th from Warden to Neufield put back into operation.. | Linear Water System | 2025-11-13
LINEAR | November | Isolated and drained watermain for our contractor Trisan to tap a new drain valve at chamber 3490133-04. Once drain was installed we filled the watermain slowly and than flushed for approximately 1 hour and took grab chlorine residual test. Free chlorine 0.05mg/l Total chlorine 1.50mg/l. All valves are open and the watermain is back in service. | Linear Water System | 2025-11-17
LINEAR | November | Watermain isolated from 16th and Warden (Chamber Id: 93E1623-07) to Nufield Gate (Chamber Id: 93E1623-04) for AV mods work to be performed by North Rock. | Linear Water System | 2025-11-12
WW-NORTH | November | Prepared for upcoming pressure testing of the three forcemains that are currently offline (two 750 mm and one 350 mm brine line) along 2nd Concession Rd Confirmed that the necessary valves were either opened or closed in VC16/VC20, VC15/VC19, and VC4A/VC4B so Liquidlogics can begin filling the mains with water. | North Wastewater Linear System | 2025-11-26
WW-NORTH | November | Performed inspection of sweet vents along 2nd Concession Rd. | North Wastewater Linear System | 2025-11-20
WW-NORTH | November | Performed inspections of the following vortexes and chambers Vortex at T1351-100A (behind 61 Hackett St.) Sluice Gate in U50618-CH04 (Holland Landing Lagoons) Vortex at T1207-02, 44 Bradford St. (Holland Landing SPS). | North Wastewater Linear System | 2025-11-19
WW-NORTH | November | Performed inspections of the following vortexes and chambers Vortex at T1208-44A (south of 2nd Con. SPS) Sluice gate in T0406-397 (Georgina 4 SPS) Vortex at T0409-02 (Morton Ave. OCF). | North Wastewater Linear System | 2025-11-21
WW-NORTH | November | Performed inspections of Georgina 4 SPS forcemain chambers along Woodbine Ave. | North Wastewater Linear System | 2025-11-25
WW-NORTH | November | Assisted representative from Continental Carbon with the installation of two new sweet vents directly south of the river bridge, adjacent to 2nd Concession Rd. | North Wastewater Linear System | 2025-11-12
WW-NORTH | November | Attended for scheduled work orders Notified ROC of work being completed Inspected pinch valves - ran EGSSSC valve in duty 1 for a cycle to test Tested sump pit high level alarm Flushed air relief valves. | Newmarket Pinch Valves | 2025-11-21
WW-WEST | November | On site to install receptacle next to DO analyzer on East aeration tank for future NO2 meter. 2 Analogue cables have been ran back to the PAC and have been labelled NO1 and NO2 for use with the future NO2 meter. | Nobleton Water Resource Recovery Facility | 2025-11-06
WW-WEST | November | Supernated sludge thickening tank and released to holding tank. Completed labs and entered numbers in ace sheets. Completed station check. No issues found. Shut ras pump off at 10:00. Manually wasted 40 m3 in 8 cycles between 11:00 and 13:20. Continued air lifting sand out of filter 3. Made small adjustments to air valves on aeration tanks. Added 1 bag soda ash to each train. Cleaned filtration inlet channel. | Nobleton Water Resource Recovery Facility | 2025-11-06
WW-WEST | November | Supernated sludge thickening tank and released to holding tank. Shut RAS pump off at 10:36. Completed labs and entered numbers in ace sheet. Completed station check. Wasted 50 m3, 5 m3 at a time, 10 minutes apart, between 11:36 and sometimeoclock. Added 2 bags soda ash to each train. Adjusted alum dosage from 230 mg/L to 225 mg/L for each train. Cleaned rags from ras pump 3. | Nobleton Water Resource Recovery Facility | 2025-11-10
WW-WEST | November | Added 1 bag soda ash to each train. Picked 3 gallons of rags from valve stem to train 1. | Nobleton Water Resource Recovery Facility | 2025-11-09
WW-WEST | November | Added 1 bag of soda ash to each aeration tank Batch wasted 30m3 from clarifier 2 Pulled rags from the aeration inlet gates | Nobleton Water Resource Recovery Facility | 2025-11-02
WW-WEST | November | Supernated sludge thickening tank and released to sludge holding tank. Completed labs and entered numbers in ace sheets. Completed station check. No issues found. Shut ras pump off at 9:00. Added 1 bag soda ash to each train. Wasted | Nobleton Water Resource Recovery Facility | 2025-11-07
WW-WEST | November | Added 1 bag soda ash to each train. Shut ras pumps off at 9:43. Set auto wasting to waste 20 m3 per train in 8 cycles between 11 and 13. Return pump 3 running for both trains at approximately 12 l/second. Completed station check. No issues found. Completed labs and entered numbers in ace spreadsheets. | Nobleton Water Resource Recovery Facility | 2025-11-04
WW-WEST | November | Received a call from ROC that aer tank 2 DO was continually dropping Placed tank 2 as the controlling tank for the blowers Returned all blowers to auto | Nobleton Water Resource Recovery Facility | 2025-11-01
WW-WEST | November | On site to address large do variances in the aeration tanks Verified do probes with handheld probe Adjusted air outlet valves for each pass Verified that the do was balancing between each tank Verified equal bubble distribution between tanks | Nobleton Water Resource Recovery Facility | 2025-11-02
WW-WEST | November | Changed aeration tanks controlling do to tank 1 | Nobleton Water Resource Recovery Facility | 2025-11-02
WW-WEST | November | In to Complete Scheduled WO. Received Alum Delivery. Reviewed and Signed Documentation. Alum Tank Level: 0.99 ?> 3.70m. | Nobleton Water Resource Recovery Facility | 2025-11-04
WW-WEST | November | Decanted sludge thickening tank - transferred remaining sludge to holding tank. Completed daily lab and station check - no new issues. Added data into SharePoint. RAS pump 3 running in manual - stopped at 9am to prepare for wasting. Informed ROC of generator run test being performed today. Ran generator at 9:58am - transferred power smoothly. WAS pump 2 set to manual to manually waste 40m3 from clarifier 2 from 10:20am to 11:40am. Placed WAS pump 2 back into manual off and RAS pump 3 back into manual on. Generator run test completed at 10:58am - transferred power back to hydro. During power transfer all WAS and RAS valves closed - placed all valves back into original positions. RAS valve 3 fully open RAS valve 4 throttled at 60% Completed JHSC inspection and checked plant for hazardous waste. Sample bottles made for Tuesday's sampling. | Nobleton Water Resource Recovery Facility | 2025-11-03
WW-WEST | November | Collected monthly samples. Started in house labs. | Nobleton Water Resource Recovery Facility | 2025-11-04
WW-WEST | November | Supernated sludge thickening tank and released to sludge holding tank. Completed labs and entered data in ace spreadsheets. Completed station check. No issues found. Shut ras pumps off at 10:05. Set auto wasting for 50 m3 between 11 and 14:00 in 12 cycles. Added 1 bag of soda ash to each train. Cleaned aeration outlet weirs. Bled condensation from aeration tank air lines. Removed floating solids from tank surface. Maintained DO probes. Set up ?Mega-Lyft? to transfer filter sand from filter 3 to filter 2. | Nobleton Water Resource Recovery Facility | 2025-11-05
WW-WEST | November | Began lab work. | Nobleton Water Resource Recovery Facility | 2025-11-28
WW-WEST | November | Supernated STT and released to SHT. Completed labs and entered numbers in ACE sheets. Shut RAS off at 9:08. Wasted 50 m3 from clarifier 1 in 10 cycles between 10:00 and 12:00. Completed station check. No issues found. Added 2 bags soda ash to each train. Removed floating solids from filtration inlet channel. Cleaned aeration tank outlet weirs. Cleaned UV racks. Cleaned UV effluent channel. Changed oils on grit vortex blowers. | Nobleton Water Resource Recovery Facility | 2025-11-19
WW-WEST | November | Collect samples and complete in house labs Input labs and data into ace sheets No decant on thickening tank, transferred to holding tank. RAS pump 3 manual off. Auto batch wasting enabled to waste 50m3 total from clarifier 1. Clarifier 2 remains OOS. Complete station round and data collection. Added 1x25 kg bag to each aeration basin. Set final effluent composite to run on Sunday for Monday samples | Nobleton Water Resource Recovery Facility | 2025-11-21
WW-WEST | November | Harie Rajamithiran(OIT) working under the direction of Lance Johnson(OIC). -Supernated STT & released to SHT -Shut RAS pump off at 9:06 -Wasted 50m^3 from both trains combined between 10:00 & 12:48 -Completed lab analysis & entered data in Ace sheets -Completed station check, no issues found -Added 2 bags of soda ash in each aeration tank -Cleaned aeration tank outlet weirs -Maintained DO probes -Unplugged RAS P3 & returned to service | Nobleton Water Resource Recovery Facility | 2025-11-26
WW-WEST | November | Completed labs and entered data in ACE sheet. Completed station check. No issues found. Shut RAS off at 12:54. Set auto wasting to waste 20 m3 total between 14:00 and 15:00 in 4 cycles. Returning at ~12 l/sec when done. Added 2 bags soda ash to each train. | Nobleton Water Resource Recovery Facility | 2025-11-28
WW-WEST | November | Added 1 x 25kg bag of soda ash to each aeration basin. | Nobleton Water Resource Recovery Facility | 2025-11-30
WW-WEST | November | Supernated STT. Found sand washer for cell 2, sand filter 4 plugged. Unplugged sand washer and restored proper operation. Started ?MegaLyft? to transfer sand from sand filter 2 to sand filter 3. Completed labs and entered numbers in ACE sheets. Completed station check. No issues found. Added 2 bags soda ash to each train. Released sludge to SHT. Shut RAS off at 12:00. Set auto wasting for 20 m3 total for both trains between 13:00 14:00. Investigated scum pump 1. Found it to work just fine at the moment. Put scum pump back in service. Changed oil in sludge holding tank blower 1 and 2. | Nobleton Water Resource Recovery Facility | 2025-11-27
WW-WEST | November | Harie Rajamithiran(OIT) under the direction of Lance Johnson(OIC) -Verified online DO meters -Removed floating solids from aeration tank surface -Changed oil & Inspected filters/belts on aeration blower 2 & 3 | Nobleton Water Resource Recovery Facility | 2025-11-26
WW-WEST | November | Added 1 bag of soda ash to each aeration tank | Nobleton Water Resource Recovery Facility | 2025-11-23
WW-WEST | November | Harie Rajamithiran(OIT) working under the direction of Gavin Walker(OIC) Cleaned aeration channel Cleaned out filter reject pit Changed oil on air compressor#2 (notified ROC of the work being performed) | Nobleton Water Resource Recovery Facility | 2025-11-24
WW-WEST | November | - Received alum delivery at 7:36. Checked certificate of authenticity. Signed all papers. Received from 0.96 m to 3.66 m. No issues while receiving - Collected weekly regulatory samples - Performed in-house lab and recorded readings on SharePoint. Due to low alkalinity, added 3 bags of soda ash to each aeration tank - Decanted the sludge thickening tank. Once done, transferred sludge into the holding tank | Nobleton Water Resource Recovery Facility | 2025-11-24
WW-WEST | November | Supernated STT and released to SHT Completed labs and entered numbers in ACE sheets. Completed station check. No issues found. Shut RAS off at 9:00. Wasted 50 m3 from clarifier 1 between 10:00 and 13:00. Added 2 bags soda ash to each train. Removed floating solids from aeration tanks. Maintained online DO probes. Bled condensation from air lines. Changed aeration blower 1 oil. | Nobleton Water Resource Recovery Facility | 2025-11-20
WW-WEST | November | - Performed station check and recorded readings on SharePoint - Unclogged filter 4 east filter - Removed rags from raw inlet channel - assisted with aeration channel clean out and filter reject pit cleaning | Nobleton Water Resource Recovery Facility | 2025-11-24
WW-WEST | November | Harie Rajamithiran(OIT) working under the direction of Lance Johnson -Worked with Lance Johnson(OIC) | Nobleton Water Resource Recovery Facility | 2025-11-27
WW-WEST | November | Added 2 bags soda ash to each train. Supernated STT and released to SHT. Wasted 50 m3 total between 11:00 and 14:00. Set RAS pump 1 in service and adjusted valves to make flow rates even. Reset service water pumps. Unplugged sand washer on filter 4. | Nobleton Water Resource Recovery Facility | 2025-11-25
WW-WEST | November | Completed work orders with Lance Johnson | Nobleton Water Resource Recovery Facility | 2025-11-19
WW-WEST | November | Supernated STT and released to SHT. Added 2 bags soda ash to each train. Completed labs and entered data in ace sheets. Shut ras pump off at 11:14. Wasted 40 m3 in 5 m3 batches between 12:44 and 14:44. Returning at 15 l/sec when complete. Completed station check. No issues found. Worked on removing ?stuff? from the very bottom of sand filter 3. Received delivery of 60 bags of soda ash. Reviewed and signed shipping document. | Nobleton Water Resource Recovery Facility | 2025-11-11
WW-WEST | November | Supernated STT and released to SHT. Completed labs and entered numbers in ACE sheets. Shut RAS pump off at 8:49. Wasted 25 m3 between 9:57 and 10:55 in 4 batches. Return pump back on when complete. Completed station check. No issues found. Added 2 bags soda ash to each train. Inspected RAS pumps 1 to 3. Pump 3 needs de-ragging. Cleared rags from RAS pump 1. Inspected WAS pumps 1 and 2. Inspected Scum pumps 1 and 2. Scum pump 1 faults when asked to run. Will investigate. Partially exercised filter inlet valves. | Nobleton Water Resource Recovery Facility | 2025-11-13
WW-WEST | November | Shut RAS pump off at 8:57. Wasted 40 m3 between 10:18 and 12:20 in 8 batches. Return pump on when complete. Completed station check. No issues found. Completed labs and entered numbers in ACE sheets. Added 2 bags of soda ash to each train. Inspected clarifiers 1 and 2. Inspected plant sewer pumps. Inspected HWB heat trace. | Nobleton Water Resource Recovery Facility | 2025-11-14
WW-WEST | November | Added 2 bags of soda ash to each aeration tank | Nobleton Water Resource Recovery Facility | 2025-11-15
WW-WEST | November | Supernated STT and released to SHT. Completed labs and entered numbers in ACE sheets. Shut RAS off at 9:05. Wasted 50 m3 between 11:12 and 13:40 in 5 m3 batches, 10 minutes apart. Completed station check. No issues found. Added 2 bags of soda ash to each train. Cleaned and inspected air compressors. Added oil to each compressor. Checked clarifier weirs. Inspected process building sump pumps. ROC received high level alarm. | Nobleton Water Resource Recovery Facility | 2025-11-17
WW-WEST | November | Collected weekly compliance samples. | Nobleton Water Resource Recovery Facility | 2025-11-11
WW-WEST | November | Supernated STT and released to SHT. Shut RAS off at 8:57. Started labs. | Nobleton Water Resource Recovery Facility | 2025-11-14
WW-WEST | November | Diesel Generator, Annual Maintenance and Load Test, Nobleton WRRF (1Y) And 5 Yr system maintenance completed as scheduled without issue. Adjusted cooling sp in gen room to 25?C | Nobleton Water Resource Recovery Facility | 2025-11-18
WW-WEST | November | Collected weekly compliance samples. Supernated STT and released to SHT. Shut RAS pump off at 8:51. Closed aeration outlet to clarifier 2 and opened aeration outlet to clarifier 1. Started labs. | Nobleton Water Resource Recovery Facility | 2025-11-18
WW-WEST | November | Supernated SHT and released to SHT. Completed labs and entered numbers in ACE sheets. Shut RAS off at 8:37. Completed station check. No issues found. Wasted 34 m3 in ~5 m3 increments, 10 minutes apart, between 9:38 and 11:17. Added 2 bags soda ash to each train. Cleaned aeration tank outlet weirs. Bled condensation from aeration tank air lines. Maintained DO probes. Removed floating solids from aeration tank surface. Inspected screenings compactor. Inspected vortex 1 and 2. Inspected grit dewatering screw. Inspected debris auger. | Nobleton Water Resource Recovery Facility | 2025-11-12
WW-WEST | November | Work performed on site, not remotely. Completed labs and entered numbers in ACE sheets. Added 2 bags soda ash to each train. Wasted 51 m3 from clarifier 1 in approximately 5 m3 batches approximately 10 minutes apart. Cleared rags from WAS pump 1 RAS pump 2. Clarifier 1 online. Clarifier 2 half way drained. Inspected RAS pumps 1 and 2. | Nobleton Water Resource Recovery Facility | 2025-11-18
WW-WEST | November | Worked with Lance Johnson. | Nobleton Water Resource Recovery Facility | 2025-11-17
WW-CEAST | November | Called in Satum (Electrician on call ) we checked the breakers and one didn?t complete the transfer - hit the reset button on the control screen and tried transferring again and it switched back to main power again. Went down to B2 level and opened up SCADA screen and reset pump 2 and Satum had to reset pump 5 on the MCC of the pump. All alarms have been cleared and station is back to normal ops except for pumps 1 & 4 which are OOS. | Markham Leslie Pumping Station | 2025-11-03
WW-CEAST | November | Station check complete and the readings have been entered into the sharepoint. Switched rag bin for the weekend | Markham Leslie Pumping Station | 2025-11-07
WW-CEAST | November | -On site to perform a station check. -Entered station readings into SharePoint. -Checked drywell, reset fault on AHU-2, back running in auto now. -Drained condensate from air compressor tanks. -Checked screen room, changed out rag bin, cleared blockage in screw press drain line, flushed screw press drain lines, cleaned rags off conveyor and floor. | Markham Leslie Pumping Station | 2025-11-10
WW-CEAST | November | Got a call from ROC (Anjelica) and there was a power failure - explained to her how to clear and reset pumps 2 & 5 and both pumps cleared. All 4 pumps (2 pumps 1&4 are OOS) are available and only one pump is called for and running. Told ROC to monitor and call if there are any changes. | Markham Leslie Pumping Station | 2025-11-03
WW-CEAST | November | Brent S. and myself trouble shot for pump 3 E. stop trouble. Found UPS system in Benshaw unit required new batteries batteries have now been replaced and system is back online. | Markham Leslie Pumping Station | 2025-11-03
WW-CEAST | November | Record vibration readings for pumps 2,3,5, and 6 | Markham Leslie Pumping Station | 2025-11-03
WW-CEAST | November | On site completed work orders. Station Check (See details on SharePoint) Pumps 2, 3, 5 and 6 available in auto duty rotation every 4 hours. Pumps 1 and 4 out of service for repairs. All standby power generators available in auto. Drained condensates from the surge tanks air compressors. Blew down bubblers. Bar Screen Bin Removal and Replacement - Switched rag bin, pushed out rag bins for pick up by Miller Waste tomorrow. Cleaned/hosed down bar screen room. Odour Control Scrubber System Inspection and Filter Cleaning JHSC Health and Safety Inspection - Lights inside the elevator not working. Archibus created for PS. | Markham Leslie Pumping Station | 2025-11-05
WW-CEAST | November | Weather: 8 C Light Rain Wind: 23 Kmh from WSW Gusts: 50 Kmh On site completed work orders. Station Check (See details on SharePoint) Pumps 2, 3, 5 and 6 available in auto duty rotation every 4 hours. Pumps 1 and 4 out of service for repair. All standby power generators available in auto. Switched pump duty of sump pumps. Drained condensates from the surge tank air compressors. Standby Power Generators Test Run - pre-test checked, ok. Generator 3 got warning alarm when it started to run but continuous running throughout the test run. Was not able to clear said alarm while running. The MTU fault code 1 on the unit itself says, ?92 SS Starter SPD Low.? After the test run, generators 1 and 2 stopped running without problem. Generator 3 got a shutdown alarm and became out of service, which was not able to clear/reset on SCADA. Pump 3 got an emergency stop alarm, which cannot be cleared/reset on SCADA. Checked MCC Benshaw MV Soft Starter, no power. Called Team Leads (D. Kim and B. Van Bakel), Bill will send Electrician to check the issue. Generator 3 alarm on the unit was cleared/reset but not the alarm on the SCADA. Cleared/reset alarm on the MCC by putting the generator in off position, reset shutdown alarm and then put it back in auto. I was able now to clear the alarm at the SCADA. Generator 3 back in service and in auto. Checked bar screens. Switched rag bin. Hazardous Waste Collection and Removal Bypass Sampling Kit Inspection Hoist Inspection | Markham Leslie Pumping Station | 2025-11-03
WW-CEAST | November | On site responded to a communication failure called by ROC. Upon arrival, found generators running. Switchgear T1 line is back but not T2. Cleared alarm on Generator MCC. Acknowledged power is back for line T2, power transferred. Cleared/reset all alarms caused by the power failure. Generators ran for almost two hours. Station back to normal operations. Also, completed station check (See details on SharePoint) Pumps 2, 3, 5 and 6 available in auto duty rotation every 4 hours. Pumps 1 and 4 out of service for repairs. All standby power generators available in auto. Drained condensates from the surge tanks air compressors. Reset alarm on AHU-2 regarding Earth fault 3016/Bypass fault 16. AHU-2 back in service. Checked dry well, ok. Bar Screen Bin Removal and Replacement - Switched rag bin, pushed out rag bins for pick up by Miller Waste tomorrow. Cleaned/hosed down bar screen room. Screw press drain clogged again. Unclogged. While still on site, generators suddenly ran but no power failure. Informed ROC and PCS/SCADA. It seems communication failure is the problem. When SCADA access is back, cleared/reset all alarms. Station back to normal operations. Talked to Kyle Carlen, he?s on the way to check the issue. | Markham Leslie Pumping Station | 2025-11-19
WW-CEAST | November | -On site to respond to power failure reported by ROC. -Upon arrival to site found all three generators running, but only 52-L2 side had transferred to generator power. 52-L1 side still operating on utility power. Pump 1 OOS, VFD Fault active on Pump 2, Pump 3 running in auto, Pump 4 OOS, Pumps 5 and 6 available and in auto. -Also upon arrival to site, 52-L2 Power Source Available already displayed on SCADA. -1733 - Transferred 52-L2 side of station back to utility power after pumping down wet well and placing pumps 1-3 off. -No issues on transfer back to utility power, generators turned off normally after 5min cooldown. -Cleared VFD fault on Pump 2. -Pumps 1 and 4 OOS, Pumps 2,3,5,6, in auto and available. Generators in auto and available. | Markham Leslie Pumping Station | 2025-11-19
WW-CEAST | November | Exercised the 3 main header valves as well as the 4 discharge valves on each pump ( 2 pumps are OOS ) all valves were fully closed then opened with no issues or leaks - also cracked the force main drain valves until I heard flow then closed back up with no issues. Cleared all alarms and station is back to normal ops with pumps 1 & 4 OOS. | Markham Leslie Pumping Station | 2025-11-25
WW-CEAST | November | -On site to complete work orders. -Entered station readings into SharePoint. -Checked drywell, drained condensate from air compressors. -Checked screen room, changed out rag bin, cleared blockage in screw press drain line, flushed drain lines, cleaned rags off conveyors and floor, bar screen oil topped up. -Pumps 1 and 4 OOS. All other pumps in auto and available. -Comprehensive housekeeping tasks completed. | Markham Leslie Pumping Station | 2025-11-24
WW-CEAST | November | On site completed work orders. Station Check (See details on SharePoint) Pumps 2, 3, 5 and 6 available in timed-auto duty rotation every 4 hours. Pump 1 out of service for repair and taken out of site. Pump 4 out of service for repair. All standby power generators available in auto. Switched sump pump duty. Ran one sump pump to removed old/stagnant sewage or water inside the sump pit. Drained condensates from the surge tanks air compressors. Blew down bubblers, cleared/reset alarms afterwards. Checked dry well, ok. Checked bar screens. Switched rag bin. Cleaned/hosed down bar screen room. Bar Screen Bin Removal and Replacement - pushed rag bins outside the screen room for pick up by Miller Waste tomorrow. | Markham Leslie Pumping Station | 2025-11-26
WW-CEAST | November | On site completed Station Check (See details on SharePoint) Pumps 2, 3, 5 and 6 available in timed-auto duty rotation every 4 hours. Pump 1 out of service for repair and taken out of site. Pump 4 out of service for repair. All standby power generators available in auto. Drained condensates from the surge tanks air compressors. Blew down bubblers, cleared/reset alarms afterwards. Checked dry well, ok. Checked bar screens. Switched rag bin. Cleaned/hosed down bar screen room. Pushed rag bins back inside the screen room after being picked up by Miller Waste yesterday. | Markham Leslie Pumping Station | 2025-11-21
WW-CEAST | November | -on site for bar screen 2 fault alarm -reviewed SCADA -inspected screen, no issues visible, oil full -reset alarm on local panel -alarm reset, screen started up -bar screen running normally -reset alarm on SCADA | Markham Leslie Pumping Station | 2025-11-30
WW-CEAST | November | On site in response to wet well 1 and 2 bubbler low pressure alarm. Checked air compressors on-site and confirmed no air is leaking. Manually ran both bubbler compressor to pressurize the vessels and cleared the alarm. Notified ROC | Markham Leslie Pumping Station | 2025-11-14
WW-CEAST | November | On site completed Station Check (See details on SharePoint) Pumps 2, 3, 5 and 6 available in auto duty rotation every 4 hours. Pumps 1 and 4 out of service for repairs. All standby power generators available in auto. Switched pump duty of sump pumps. Found SCADA OIT @ B2 level with blank monitor Informed PCS/SCADA staff (Yash). Created work order request to check it. Drained condensates from the surge tanks air compressors. Cleared/reset bubblers alarm happened last Nov. 15th. Observed no unusual issue with the bubblers. Blew down bubblers, cleared/reset alarms afterwards. Pumps 2 and 5 VFD filters too dirty - replaced filters. Checked dry well, ok. Cleared/reset South Forcemain Valve (RSP_FORM2_MV1) fault alarm. It is now in 100% open, as normal operation. Checked bar screens. Switched rag bin. Screw press drain clogged. Unclogged said drain. Cleaned/hosed down bar screen room. | Markham Leslie Pumping Station | 2025-11-17
WW-CEAST | November | Weather today Overcast and 3 Celsius -On site to complete work orders W11367076, W11367284. -Completed station check. -Entered station readings into SharePoint. -Checked drywell, Okay. -Drained condensate from air compressor tanks. -Checked screen room, Bar Screen Bin Removal and Replacement - Switched rag bin, pushed out rag bins for pick up by Miller Waste tomorrow. -Flushed screw press drain lines, cleaned rags off conveyor and floor. -Pumps #1 and #4 remain OOS. | Markham Leslie Pumping Station | 2025-11-12
WW-CEAST | November | On site to check 4160V switchgear. Shut off pump 2 to check switchgear function. Informed ROC. Pump 2 reset and back in auto. | Markham Leslie Pumping Station | 2025-11-11
WW-CEAST | November | On site completed work orders. Station Check (See details on SharePoint) Pumps 2, 3, 5 and 6 available in auto duty rotation every 4 hours. Pumps 1 and 4 out of service for repairs. All standby power generators available in auto. Drained condensates from the surge tanks air compressors. Oil and filter, ok. Blew down bubblers. Checked dry well, ok. Bar Screen Bin Removal and Replacement - Switched rag bin. Rag bins back inside screen room after picked up by Miller Waste. Cleaned/hosed down bar screen room. Consolidated Monthly Dry Well Pump Floor Inspection Facility have no dry well flood alarm, instead sump pump high high level alarm tested - received by ROC. Auto dialer test - received by ROC. High low temp alarm test - don?t know where it is. Not tested. As per Team Lead, disregard, he will ask Maximo/scheduler staff to remove it from the list. RS Pumps and Motors Inspection Pumps 1 and 4 out of service for repair. Pump 2 @ 0% speed: 950 L/s, 417 kPa, 49 Hz, 129 A, 580 RPM, 454 Kw / @ 100% speed: 1820 L/s, 430 kPa, 60 Hz, 177 A, 716 RPM, 944 Kw Pump 3 Constant Speed: 1300 L/s, 422 kPa, 60 Hz, 98 A, 4020 V Pump 5 @ 0% speed: 915 L/s, 415 kPa, 48 Hz, 124 A, 581 RPM, 433 Kw / @ 100% speed: 1800 L/s, 428 kPa, 60 Hz, 171 A, 716 RPM, 890 Kw Pump 6 Constant Speed: 1160 L/s, 420 kPa, 60 Hz, 97 A, 4020 V Consolidated Monthly Surge tank Inspection - transmitter lines not flushed due to lack of time. Drain valves partially exercised. Surge tanks partially drained. | Markham Leslie Pumping Station | 2025-11-14
EAST | November | On site for station check. Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 1.62mg/l FCL Analyzer: 1.55mg/l Effluent Free Cl2 grab residual: 1.57mg/l FCL Analyzer: 1.58mg/l Effluent Total Cl2 grab residual: 1.83mg/l Inspected turbidimeter. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Mount Albert Wells 1 & 2 | 2025-11-07
EAST | November | On site for monthly maintenance: Conducted Generator Test Run Diesel Generator Run Monthly Test @09:35 hrs Start Runtime: 09:35hrs, Run hours 199.7hrs Fuel Start: 11.9cm/788.6L Stop Runtime: 10:50hrs, Run hours 201.10hrs, Fuel Stop: 11.5cm/755.2 Generator Performance Data recorded below: Battery Cell Levels: OK Battery Terminals/Cables: Ok Oil and Coolant: Ok Amps: 35 Volts: 601 Hertz: 60 RPM: 1800 Oil Pressure: 400KPA Oil Temp: NA Water temp: 78 C No issues during generator run test. Ran Well 2 during run test. JHSC Inspection completed. Made follow up WO for eyewash station in Hypochlorite Room, not enough water pressure in the eyewash. Tested building Hi/Lo alarm. High alarm not working, WO made to have a look. 11:00hrs: Cleaned Influent and Effluent HACH Cl17 Analyzers. Collected Cl2 grab residuals to verify Analyzers after cleaning: Influent Cl2 grab: 1.75mg/l Analyzer: 1.75 mg/l Effluent Cl2 grab: 1.60mg/l Analyzer: 1.66mg/l Conducted silicate and hypo system inspection including injection point cleaning and pump inspection. No issues. Valve exercise, deep well exhaust inspection | Mount Albert Wells 1 & 2 | 2025-11-06
EAST | November | On site to complete station check. No outstanding alarms on site. Well 1 is OOS due to hi concentrations of iron and manganese. Time: 13:50 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.54 1.45 Time: 13:55 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.44 1.49 Total: 1.77 Changed out the influent and effluent CL-17 reagents. Verified analyzers with grabs. Checked site and trends. | Mount Albert Wells 1 & 2 | 2025-11-10
EAST | November | On site for station check. Collected weekly micro samples (W11347666) and Raw PH. Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 1.94mg/l FCL Analyzer: 1.90mg/l 11:50hrs: Effluent Free Cl2 grab residual: 1.74mg/l FCL Analyzer: 1.76mg/l Effluent Total Cl2 grab residual: 2.08mg/l Ran Well #1 in local to waste (not into distribution) to collect raw samples. Ensured chemical pumps were off and isolated from distribution system while running well. Back to local off when complete. Well used for emergency purposes only. Well #1 raw sample collected @ 12:20hrs. Raw PH values: 12:20hrs: Well 1: 7.76 11:50hrs: Well 2: 7.51 Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Mount Albert Wells 1 & 2 | 2025-11-05
EAST | November | On site for station check. Collected in house iron samples. Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 1.86mg/l FCL Analyzer: 1.92mg/l Effluent Free Cl2 grab residual: 1.57mg/l FCL Analyzer: 1.60mg/l Effluent Total Cl2 grab residual: 1.89mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Mount Albert Wells 1 & 2 | 2025-11-03
EAST | November | On site for Well #1 step test with Water Resources. Chemical Pumps in manual off during test. Except for Hypo Pumps, kept them in auto as not to interlock Well 1 so that we could run the well in manual speed setpoint to manipulate the speed and flow rate for step test. *Hypo Pumps not running into system but looped to feed back into Hypo Tank. Will be running well to waste (not into distribution) during step test. No water being directed to users during step test. Ran Well 1 at 12L/S, 24L/S and 37L/S. 11:15hrs: At the 37L/S flow rate, influent lolo alarm came in and well locked out. Backflushed well to increase influent residual back to operating level. Found that some raw water was passing through Well #2 deep well exhaust valve which caused influent reading to decrease. | Mount Albert Wells 1 & 2 | 2025-11-21
EAST | November | Activated system duty and placed well 2 back in auto. | Mount Albert Wells 1 & 2 | 2025-11-21
EAST | November | On site to top up silicate Before 31 cms After 93 cms No issues found | Mount Albert Wells 1 & 2 | 2025-11-25
EAST | November | On site for station check, weekly micro sampling (W11386598), and manganese sampling (W11348741) Well running - 22 L/s, discharge pressure 325 Recorded station readings in PWQ sheets. Reviewed trends, station OK. Verified analyzer readings with grab residuals Influent free analyzer reading high(grab 1.68 and analyzer 1,89), adjusted analyzer after three grab residuals. Put analyzer in prime sequence, gap in SCADA output due to analyzer priming caused well to interlock and shut down. Further grab residuals showed analyzer reading still inaccurate, adjusted analyzer after more consistent grab samples (grab 1.49, analyzer 1.31) Effluent: @ 15:15 Grab free: 1.44 mg/L / Analyzer: 1.44 mg/L Grab total: 1.69 mg/L NTU: 0.043 Collected well 2 Raw sample and treated sample @ 15:18. | Mount Albert Wells 1 & 2 | 2025-11-19
EAST | November | On site for station check. Duty not active, tower Level @ 67%. Placed Well 2 manual off to investigate turbidity analyzer issue. Adjusted flow rate through analyzer, cleared air bubbles and performed calibration with standard. Visual check in and around station. Verified analyzer readings with grab residuals - no adjustments needed. Influent taken 13:51 Free Grab: 1.33 mg/L Analyzer: 1.33 mg/L Effluent taken at 13:56 Free Grab: 1.41 mg/L Analyzer: 1.41 mg/L Total Grab: 1.62 mg/L Visual inspection of chemical systems - all OK. Entered station readings in PWQ sheet. Reviewed trends, equipment ok. Activated system duty 1. | Mount Albert Wells 1 & 2 | 2025-11-24
EAST | November | On site for station check. Duty not active, tower Level @ 69%. Completed Turbidimeter maintenance while well manual off. Manual start Well 2. Visual check in and around station. Verified analyzer readings with grab residuals - no adjustments needed. Influent taken 13:11 Free Grab: 1.91 mg/L Analyzer: 1.97 mg/L Effluent taken at 13:25 Free Grab: 1.62 mg/L Analyzer: 1.56 mg/L Total Grab: 1.83 mg/L Chemical systems: Hypo P2 speed 26%, DF= 100%. DP= 440 kpa. Silicate P1 speed 37%, DP= 500 kpa. Visual inspection of chemical systems - all OK. Entered station readings in PWQ sheet. Reviewed trends, equipment ok. Station ok | Mount Albert Wells 1 & 2 | 2025-11-21
EAST | November | Placed all chemical pumps manual off for sampling well 1 raw water. Local started well #1 @ 11:18 for sampling. After turning well 1 on, noticed flow and pressure was too high - 36 L/s, noticed raw water passing through well 2 exhaust valve. Local stop well. Opened back wash valve for a few mins to prevent raw water from reaching influent chlorine analyzer. Double checked and adjusted well setpoints on SCADA - Re-started well at 11:39 - flow went up to 37 L/s again. Local stopped well at 11:42. Switched well to remote manual mode, set manual speed set point to 8%. Put hypo pumps back in auto and adjusted DICE blocks to pump through drain to tank. No hypo being directed to system. Manual start well 1 at 11:56 Changed manual speed setpoint to 0%. Flow 28.4 L/s Collected W1 raw samples @ 12:16 Stopped W1 @ 12:17 Put all chemical pumps and well 2 back in auto, adjusted pump DICE blocks back to system dosing. | Mount Albert Wells 1 & 2 | 2025-11-26
EAST | November | On site for station check, weekly micro sampling (W11402384) Duty is active - tower level 85% Well 2 running - 21.8 L/s, discharge pressure 328 kpa Recorded station readings in PWQ sheets. Reviewed trends, station OK. Verified analyzer readings with grab residuals: Influent @ 10:59 Grab Free: 1.84 mg/L / Analyzer: 1.88 mg/L Effluent: @ 11:01 Grab free: 1.53 mg/L / Analyzer: 1.52 mg/L Grab total: 1.77 mg/L NTU: 0.042 Collected well 2 Raw sample and treated sample @ 11:06 Chemical systems: Hypo pump 2 speed 26%, DF=93%, DP=460 kpa Chlorinator 1 open 34%, DF=53%, Rotameter: 17 ppd, BP1 DP=1040 kpa Silicate P1 speed 37%, 69.3 ml/min, DP=530 kpa Manual stop well 2 @ 11:12 | Mount Albert Wells 1 & 2 | 2025-11-26
EAST | November | On site for station check, weekly micro sampling (W11386598), and manganese sampling (W11348741) Duty is not active - tower level 69% Called ROC to notify that all chemical pumps manual off for well 1 sampling Local started well #1 @ 11:46 for sampling. Collected W1 raw samples @ 11:58 Stopped W1 @ 12:00 Put all chemical pumps and well 2 back in auto, then activated system duty @ 12:02. | Mount Albert Wells 1 & 2 | 2025-11-19
EAST | November | On site for station check. Duty active, tower level 80% Completed short station check, driveway to station not plowed. Was forced to park on the road. Verified analyzer readings with grab residuals - no adjustments needed. Influent taken 13:27 Free Grab: 1.9 mg/L Analyzer: 1.94 mg/L Effluent taken at 13:30 Free Grab: 1.54 mg/L Analyzer: 1.51 mg/L Total Grab: 1.78 mg/L Visual inspection of chemical systems - all OK. Entered station readings in PWQ sheet. Reviewed trends, equipment ok. Station ok | Mount Albert Wells 1 & 2 | 2025-11-28
EAST | November | On site to top up silicate day tank with silicate from Aurora wells 1-4. Start: 33.4cm/157L Stop: 98.7cm/465L No issues with top up. | Mount Albert Wells 1 & 2 | 2025-11-13
EAST | November | Informed ROC. Performed annual calibration and put instruments in Cal mode while doing the tasks. Devices done were AITs, NIT, FITs, PIT and LITs. Effluent residual dropped to zero ( from 2:19PM to 2:30PM) because we were troubleshooting on it and calibration mode time expired. Wells were not running though. We changed colorimeter and it looked stable. We will keep on monitoring it. Took grabs at the sample line. Influent free chlorine AIT1= 1.59 mg/l Grab= 1.63 mg/l Effluent free chlorine AIT2= 1.60 mg/l Grab= 1.63 mg/l All alarms were cleared after the job. No other issues encountered. | Mount Albert Wells 1 & 2 | 2025-11-18
EAST | November | On site for station check. Duty active, tower Level @ 68%. Visual check in and around station. Verified analyzer readings with grab residuals - no adjustments needed. Influent taken at 14:36 Free Grab: 1.97 mg/L Analyzer: 2.00 mg/L Effluent taken at 14:38 Free Grab: 1.75 mg/L Analyzer: 1.74 mg/L Total Grab: 2.01 mg/L Chemical systems: Hypo P1 speed 28%, DF= 104%. DP= 460 kpa. Silicate P2 speed 37%, DP= 500 kpa. Visual inspection of chemical systems - all OK. Entered station readings in PWQ sheet. Reviewed trends, equipment ok. Station ok | Mount Albert Wells 1 & 2 | 2025-11-17
EAST | November | On site for station check and weekly micro sampling (W11368040) Duty is active - tower level - 75% Well running - 22 L/s, 326 kpa Recorded station readings in PWQ sheets. Reviewed trends, station OK. Called ROC to request all chemical pumps and well 2 placed manual off for sampling well 1 raw. Local started well #1 @ 10:30 for sampling. Collected W1 raw sample @ 10:49 Stopped W1 @10:50 Called ROC and requested Well 2 and chemical pumps back to auto and to activate the system duty. Verified analyzer readings with grab residuals Influent: @ 11:26 Grab free: 1.99 mg/L / Analyzer: 1.97 mg/L Effluent: @ 11:30 Grab free: 1.61 mg/L / Analyzer: 1.61 mg/L Grab total: 1.89 mg/L NTU: 0.048 Collected well 2 Raw sample @ 11:40 and 1/2 treated sample @ 11:38 Chemical systems: Hypo pump 1 running at 28%, DF = 103% Silicate P2 running at 37%, 70.03 mL/min | Mount Albert Wells 1 & 2 | 2025-11-12
EAST | November | On site for station check. Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 1.99mg/l FCL Analyzer: 1.93mg/l Effluent Free Cl2 grab residual: 1.74mg/l FCL Analyzer: 1.80mg/l Effluent Total Cl2 grab residual: 1.99mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Mount Albert Wells 1 & 2 | 2025-11-14
EAST | November | Received Hypo delivery. Start 38cm, stop 88 cm Noticed hypo tk1 drain port leaking. Isolated tk2 so that only tk1 in service in order to draw tk1 down before it can be repaired. | Mount Albert Wells 1 & 2 | 2025-11-18
EAST | November | On site for station check. Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 1.58mg/l FCL Analyzer: 1.60mg/l Effluent Free Cl2 grab residual: 1.63mg/l FCL Analyzer: 1.59mg/l Effluent Total Cl2 grab residual: 1.76mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Mount Albert Well 3 | 2025-11-07
EAST | November | On site to complete station check. Exercised the discharge butterfly valve. Put well in manual at 12:52 to exercise valve put it back to auto at 13:00. No outstanding alarms on site. No OOS equipment. Time: 13:15 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.46 1.49 Time: 13:20 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.44 1.46 Total: 1.82 Verified analyzers with grabs all ok. Checked site and trends. | Mount Albert Well 3 | 2025-11-10
EAST | November | On site for station check. Collected weekly micro samples (W11347666). Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 1.71mg/l FCL Analyzer: 1.74mg/l 11:25hrs: Effluent Free Cl2 grab residual: 1.62mg/l FCL Analyzer: 1.61mg/l Effluent Total Cl2 grab residual: 1.80mg/l 11:30hrs: Raw PH: 7.57 Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Mount Albert Well 3 | 2025-11-05
EAST | November | On site to remove old Silicate transfer pump from site. | Mount Albert Well 3 | 2025-11-20
EAST | November | On site for station check. Collected weekly micro samples (W11386598) and Mn samples (W11348741). Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 1.77mg/l FCL Analyzer: 1.77mg/l 14:50hrs: Effluent Free Cl2 grab residual: 1.68mg/l FCL Analyzer: 1.66mg/l Effluent Total Cl2 grab residual: 1.90mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Mount Albert Well 3 | 2025-11-19
EAST | November | On site for station check. Duty active, tower Level @ 68%. Verified analyzer readings with grab residuals - no adjustments needed. Influent taken 14:58 Free Grab: 1.83 mg/L Analyzer: 1.89 mg/L Effluent taken at 15:01 Free Grab: 1.74 mg/L Analyzer: 1.67 mg/L Total Grab: 1.97 mg/L Chemical systems: Chlorinator 1 open 33%, DF= 50%. Booster P1 DP= 1020 kpa. Silicate P1 speed 41%, D P= 510 kpa. Visual inspection of chemical systems - all OK. Entered station readings in PWQ sheet. Reviewed trends, equipment ok. Station ok | Mount Albert Well 3 | 2025-11-24
EAST | November | Silicate top up: 38.8cm to 63.8cm. | Mount Albert Well 3 | 2025-11-27
EAST | November | On site for station check, and weekly micro sampling (W11402384) Duty is active - tower level 80% Well running - 30 L/s, discharge pressure 398 Recorded station readings in PWQ sheets. Reviewed trends, station OK. Verified analyzer readings with grab residuals: Influent @ 9:42 Grab Free: 1.83 mg/L / Analyzer: 1.87 mg/L Effluent: @ 9:45 Grab free: 1.71 mg/L / Analyzer: 1.76 mg/L Grab total: 1.97 mg/L NTU: 0.044 Collected well 3 Raw sample and treated sample @ 9:50 Chemical systems: Hypo pump 1 speed 34%, DF=100%, DP=460 kpa Chlorinator 1 open 34%, DF=53%, Rotameter: 17 ppd, BP1 DP=1040 kpa Silicate P2 speed 42%, 62.24 ml/min, DP=500 kpa | Mount Albert Well 3 | 2025-11-26
EAST | November | On site for station check. Duty not active, tower Level @ 69%. Completed Turbidimeter maintenance while well manual off. Visual check in and around station. Verified analyzer readings with grab residuals - no adjustments needed. Visual inspection of chemical systems - all OK. Entered station readings in PWQ sheet. Reviewed trends, equipment ok. Station ok | Mount Albert Well 3 | 2025-11-21
EAST | November | On site to place well 3 back in service. Confirmed with Lee that repair is done on chlorine line #1. While openning the main isolation valve, snapped silicate injection #1. Replaced it with a spare injection lance. Primed the line. Tested chlorine booster pump 1 and prime the line. Manual start well 3 with chlorine #1 and silicate P1 in duty 1. Chlorine booster pump 1 discharge pressure = 1050 kpa.? Will place well 3 back to auto remotely later today.? | Mount Albert Well 3 | 2025-11-25
EAST | November | Check broken pvc pipe Replace broken fittings | Mount Albert Well 3 | 2025-11-25
EAST | November | On site for station check. Duty active. Driveway to station not plowed, completed short station check in order to avoid getting stuck in the snow. Verified analyzer readings with grab residuals - no adjustments needed. Influent taken 12:54 Free Grab: 1.78 mg/L Analyzer: 1.81 mg/L Effluent taken at 12:56 Free Grab: 1.68 mg/L Analyzer: 1.70 mg/L Total Grab: 1.90 mg/L Visual inspection of chemical systems - all OK. Entered station readings in PWQ sheet. | Mount Albert Well 3 | 2025-11-28
EAST | November | Changed chlorine cylinder on bank 2. | Mount Albert Well 3 | 2025-11-26
EAST | November | Fitting on chlorine booster line #1 snapped at approximately 15:15. Stopped well pump immediately. Attempted to isolate leak from the injection point, but neither the PVC or brass valve were holding to contain the leak. The leak is still decent, but not much pressure. Decided to isolate well #3 from the system for the night, and address tomorrow with proper materials. Closed isolation valve and depressurized header. The leak from the chlorine booster line has now fully stopped. Left the well 3 in local off, with chlorine booster pump 1 in manual off. Informed On call OIC of the situation, and what actions are to be taken if needed to respond to site at MTW3 | Mount Albert Well 3 | 2025-11-24
EAST | November | Notified ROC (Adam and Carter) that the well would be local off for silicate injection point replacement. Isolated and depressurized water main. Installed a new injection point lance for silicate pump 2. Re-pressurized pipe and backflushed, added de-chlorination pucks to catch basin outside. Primed silicate pump 2. Placed pump 2 back in auto and Changed silicate pump duty rotate back to auto. Manual start well pump and monitor start up. Placed well back in auto. Notified ROC that work was completed and site back to normal. Received chlorine cylinder delivery: 10 delivered, 10 empties removed. | Mount Albert Well 3 | 2025-11-18
EAST | November | On site for monthly maintenance: Inspection of silicate system and silicate injection point inspection and cleaning. 10:45hrs: HACH CL17 Influent and Effluent Analyzer cleaning. Verified Analyzer after cleaning: Influent: 1.53mg/l, Analyzer: 1.56mg/l Effluent: 1.57mg/l, Analyzer: 1.55mg/l Chlorine leak detector test - no issues. Chlorine System inspection and leak test. No issues. Conducted Generator Test Run: Diesel Generator Run Monthly Test @ 12:47hrs Start Runtime: 12:47hrs (Run hrs: 373hrs, 48min) Fuel Start: 92.0/91.3cm/918/910.5L Stop Runtime: 14:00hrs (Run hrs: 374hrs, 57min.) Fuel Stop: 91.3cm/ 90.6/911.4/903.1L Generator Performance Data recorded below: Battery Cell Levels: OK Battery Terminals/Cables: Ok Oil and Coolant: Ok Amps: 49 Volts: 600 Hertz: 60.1 RPM: 1801 Oil Pressure: 56psi Water temp: 180 F No issues during generator run test. Ran Well 3 during run test. JHSC Inspection completed. Exhaust system inspection. | Mount Albert Well 3 | 2025-11-11
EAST | November | On site for station check. Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 1.85mg/l FCL Analyzer: 1.83mg/l Effluent Free Cl2 grab residual: 1.76mg/l FCL Analyzer: 1.72mg/l Effluent Total Cl2 grab residual: 1.92mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Mount Albert Well 3 | 2025-11-14
EAST | November | On site for station check. Activated Duty @ 13:00, tower Level @ 62%. Visual check in and around station. Verified analyzer readings with grab residuals - no adjustments needed. Influent taken at 13:36 Free Grab: 1.67 mg/L Analyzer: 1.68 mg/L Effluent taken at 13:38 Free Grab: 1.80 mg/L Analyzer: 1.80 mg/L Total Grab: 2.01 mg/L Chemical systems: Chlorinator 2 open 33%, DF= 49%. Cl Booster P2 DP= 980 kpa. Silicate P2 speed 41%, DP= 480 kpa. Visual inspection of chemical systems - all OK. Entered station readings in PWQ sheet. Reviewed trends, equipment ok. Station ok Manual stopped well pump to Exercise discharge isolation valve. Silicate injection point #2 broke while valve was being exercised. Silicate P2 manual off and duty rotate disabled Returned well pump to auto after valve exercise completed. | Mount Albert Well 3 | 2025-11-17
EAST | November | On site for station check and weekly micro sampling (W11368040) Duty is active - tower level - 81% Well running - 30 L/s, 397 kpa Recorded station readings in PWQ sheets. Reviewed trends, station OK. Chemical systems: Chlorinator 1 open 34%, DF=53%, Rotameter: 17 ppd Silicate P2 running at 42%, 62.05 ml/min Verified analyzer readings with grab residuals Influent: @ 12:31 Grab free: 1.86 mg/L / Analyzer: 1.85 mg/L Effluent: @ 12:34 Grab free: 1.76 mg/L / Analyzer: 1.72 mg/L Grab total: 1.94 mg/L NTU: 0.063 Collected well 3 Raw sample and treated sample @ 12:40 | Mount Albert Well 3 | 2025-11-12
EAST | November | On site for station check, weekly micro sampling (W11386598), manganese sampling (W11348741), and operational sampling. Tower level - 70% and draining at 11.5 L/s Recorded station readings in PWQ sheets Verified analyzer reading: Outlet @ 10:51 Free Grab: 1.43 mg/L Analyzer: 1.40 mg/L Total Grab: 1.56 mg/L Collected micro sample @10:58 from outlet. Reviewed trends, equipment ok Station ok | Mount Albert North Elevated Tank | 2025-11-19
EAST | November | On site for work orders, notified ROC of alarms being triggered. Chlorine analyzer maintenance: Completed cleaning and verified with grab sample. @ 14:00 Grab: 1.38 mg/L. Analyzer: 1.39 mg/L Building low temperature alarm test - alarm triggered at 14:10, and was cleared. JHSC inspections - all OK. Portable Generator test run Heat Trace inspection. Sump pit inspection. General housekeeping. | Mount Albert North Elevated Tank | 2025-11-18
EAST | November | On site for station check, and weekly micro sampling (W11368040) Tower level - 77% and draining at 13.7 L/s Recorded station readings in PWQ sheets Verified analyzer reading: Outlet @ 9:17 Free Grab: 1.39 mg/L Analyzer: 1.39 mg/L Total Grab: 1.55 mg/L Collected micro sample @9:23 from outlet. Reviewed trends, equipment ok Station ok | Mount Albert North Elevated Tank | 2025-11-12
EAST | November | Under Direction of OIC (Dan Zhou) On Site for; - Station Checks Data in PWQ Excel Workbook Grabs @ 14:17 hrs. FCl: 1.63 mg/L TCL: 1.68 mg/L Equipment OOS: none Facility OK | Stouffville Zone 1 Booster Pumping Station | 2025-11-07
EAST | November | Under Direction of OIC (Dan Zhou) On Site for; - Station Checks Data in PWQ Excel Workbook Grabs @ 12:16 hrs. FCl: 0.68 mg/L TCL: 0.74 mg/L Equipment OOS: none Facility OK | Stouffville Zone 1 Booster Pumping Station | 2025-11-10
EAST | November | 09:41 - placed pumps to man/off and opened FCV to 70 L/s to drain water from STETBR faster. Informed ROC 10:37 - closed FCV - STETBR level is 36% | Stouffville Zone 1 Booster Pumping Station | 2025-11-05
EAST | November | Under Direction of OIC (Stephen Baidy) On Site for; - Station Checks Data in PWQ Excel Workbook Grabs @ 14:47 hrs. FCl: 0.84 mg/L TCL: 1.00 mg/L Equipment OOS: none Facility OK | Stouffville Zone 1 Booster Pumping Station | 2025-11-03
EAST | November | 11:43 - 14:26 opened FCV to 50 l/s. Changed the duty 1 start setpoint from 42% to 60%. | Stouffville Zone 1 Booster Pumping Station | 2025-11-19
EAST | November | 8:38 Opened FCV to deep cycle Zone 1 ET to 40%. Informed ROC. | Stouffville Zone 1 Booster Pumping Station | 2025-11-21
EAST | November | On site to check station and equipment. Pump 2 is running in duty 1 upon arrival. Station readings and chlorine grabs are in PWQ sheet. Reviewed trends, station is under normal operation.? Station generator is OOS due to TSSA project. Backup power is supplied by portable gen set. Contractors are site working.? | Stouffville Zone 1 Booster Pumping Station | 2025-11-21
EAST | November | Under Direction of OIC (Dan Zhou) On Site for; - Station Checks Data in PWQ Excel Workbook Grabs @ 13:05 hrs. FCl: 1.11 mg/L TCL: 1.55 mg/L Equipment OOS: station generator Facility OK | Stouffville Zone 1 Booster Pumping Station | 2025-11-24
EAST | November | Under Direction of OIC (Dan Zhou) On Site for; - Station Checks Data in PWQ Excel Workbook Grabs @ 11:13 hrs. FCl: 1.75 mg/L TCL: 2.98 mg/L Equipment OOS: station generator for TSSA upgrades, mobile generator hooked up. Facility OK | Stouffville Zone 1 Booster Pumping Station | 2025-11-28
EAST | November | 08:32 Opened FCV to 30 l/s. Man/Stop both pumps. 13:55 Closed FCV. Placed pumps back to auto. Updated the tower level low/hi alarm to match with duty start/stop. | Stouffville Zone 1 Booster Pumping Station | 2025-11-11
EAST | November | Under direction of OIC (Dan Zhou) @ 10: 33 hrs. Places BP?s 1/2 back in auto. | Stouffville Zone 1 Booster Pumping Station | 2025-11-14
EAST | November | Deactivate duty. Zone 1 ET is 76%. | Stouffville Zone 1 Booster Pumping Station | 2025-11-14
EAST | November | On site with contractor, Ferguson Electric to test installation of temporary generator. ROC notified. Station transfer test completed with temporary generator. Operator Travis Wyatt on site to monitor operations. Site returned to utility supply. ROC notified. | Stouffville Zone 1 Booster Pumping Station | 2025-11-13
EAST | November | Under Direction of OIC (Dan Zhou) On Site for; - Comprehensive Housekeeping - Manual Valve Exercise (BFV 1,2,3,4 - FCV Isolation Valves) @ 13:04 hrs. Put BP 1 and 2 in manual Off for BFV 1,2,3,4 manual exercise and FCV isolation gate valve exercising. @ 13:09 placed BP 1 and 2 in Auto, BP 1 Duty 1 active | Stouffville Zone 1 Booster Pumping Station | 2025-11-18
EAST | November | Under direction of OIC Danielle Zhou. Worked with contractors, electrician and operator Travis Wyatt, Connected temporary mobile generator to the PS. Tested FLT and STAT inputs to PAC. Tested station on temporary generator via ATS. | Stouffville Zone 1 Booster Pumping Station | 2025-11-13
EAST | November | On Site for; Operational assistance for generator transfer of facility generator to mobile generator for coming TSSA upgrades. @ 12:25 hrs. Zone 1 tower duty activated auto, in timely manner for testing mobile generator on full load, well 3 pump active. @ 13:01 put both BPS in manual off for generator power switch to facility power @ 13:17 hrs. Placed BP?s back in auto, Bp 2 active. | Stouffville Zone 1 Booster Pumping Station | 2025-11-13
EAST | November | Under Direction of OIC (Dan Zhou) On Site for; - Station Checks Data in PWQ Excel Workbook @ 09:54 placed BP 1/2 in manual ON, (instrumentation doing LIT calibration at Zone 1 tower) Grabs @ 10:04 hrs. FCl: 1.09 mg/L TCL: 1.28 mg/L Equipment OOS: facility generator. (Facility hooked up to mobile generator, due to TSSA upgrades on facility generator) Facility OK | Stouffville Zone 1 Booster Pumping Station | 2025-11-14
EAST | November | Under Direction of OIC (Dan Zhou) On Site for; - Station Checks Data in PWQ Excel Workbook Grabs @ 10:33 hrs. FCl: 1.34 mg/L TCL: 1.36 mg/L Total Power, On Site for 5 year generator maintenance Equipment OOS: none Facility OK | Stouffville Zone 1 Booster Pumping Station | 2025-11-17
EAST | November | Attending site for leaking Effluent Total chlorine analyzer (W11420850). Replaced all internal tubing and colorimeter due to water leaking into analyzer from an unknown location. Notified Jack Palmer, so he can keep an eye out for moisture buildup. SCADA calibration mode was used and ROC was notified before and after maintenance work. | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-11-07
EAST | November | On site, troubleshooting pump #2 vfd fault. ROC notified. Vfd presents Line Converter Fault. Power cycling vfd does not resolve. Found opened fuse on holder F11. Replaced fuse and reenergized. Operator Patrick Forbert, returned pump to normal operation. ROC notified. | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-11-07
EAST | November | Attending site to check leak in Total chlorine analyzer - AIT7 (W11420850). Could not find source of water ingress. Removed standing water and observed but could not see any leaking. Will return tomorrow to investigate further. | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-11-06
EAST | November | Vibration testing Pumps 1 2 3 | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-11-06
EAST | November | On site to assist electrical with troubleshooting pump #2 VFD fault. Operated pump 2 a few times after electrical repaired a blown fuse. Pump #2 back in auto @ 14:53. No further issues. | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-11-07
EAST | November | Attended site for station check and chlorine cylinder change Changed chlorine cylinder bank 1 with Travis Wyatt, informed RO Adeela Khan Unable to clear pump 2 VFD fault on station start up - Kyle Rae (Electrician) will attend Checked station and equipment- all okay | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-11-07
EAST | November | On site for station check Verified analyzers while station running, in mg/L, 10:25 Influent total Cl - G 1.44; A 1.43 Effluent free Cl - G 2.11; A 2.26 Effluent total Cl - G >4.40; A 5.00 Simulated free Cl - G 2.00; A 2.01 Recorded observations in the shared PWQ sheet Station and equipment okay | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-11-10
EAST | November | On site to complete station check. Changing chlorine cylinders on site. At 10:35 reset alarm on site. Start: 36/0.0kg Stop: 36/68kg Time: 10:37 Influent Grab (mg/l) Analyzer (mg/l) Total: 1.06 1.10 Time: 10:40 SIM Grab (mg/l) Analyzer (mg/l) Free: 1.86 1.93 Time: 10:42 Effluent Grab (mg/l) Analyzer (mg/l) Free: 2.17 2.18 Time: 10:45 Effluent Grab (mg/l) Analyzer (mg/l) Total: 4.40 4.60 Verified analyzers with grabs. Checked site and trends. No OOS equipment except pump 4 which is in manual to be used as a jockey pump. | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-11-03
EAST | November | Restarted the Operator Interface Terminal due to Windows Updates. Pumps were off. Notified the Remote Operations Center and the OIC. | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-11-03
EAST | November | On site for station check Cleaned chlorine analyzers and tested chlorine leak alarm. Okay to disregard associated alarms. Informed RO Connor Smith of this work. Verified chlorine analyzers after cleaning, 10:40, in mg/L Influent free Cl - G 1.15; A 1.17 Effluent free Cl - G 1.96; A 2.04 Effluent total Cl - G 2.94; A 2.87 Simulated free Cl - G 1.99; A 2.06 Inspected station and equipment, recorded observations in the shared PWQ sheet Found condensation in the effluent free Cl analyzer cabinet and created a work order for Instrumentation - Eric S will attend. No observable issues with the analyzer function, strictly for the purpose of equipment housekeeping and best practice. Genset continues to have an active leak on the oil distribution manifold. Contractor Total Power working on procuring o rings and gasket for repair - okay to run if monitored by on site staff. Station and equipment okay | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-11-05
EAST | November | On site to assist contractor with diesel generator load test. Upon commencement of load test it was noticed that there was an oil leak on the engine. Load test was stopped. Standby generator still operable but outstanding oil leak will need to be repaired. | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-11-04
EAST | November | On site for preventative maintenance work orders Generator contractor, Total Power, on site with Dan Boate to inspect on site generator ? found a leaking oil manifold gasket and working to procure parts for repair. Directed ROC to dispatch on-call operator in the event of a power outage Completed Critical air valve flush and inspection Chlorine cylinder emergency kit inspection Housekeeping Pump 4 motor inspection JHSC inspection Station and equipment okay | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-11-04
EAST | November | On site with Travis Wyatt for chlorine cylinder change (bank 1) Purged prior to changing cylinders. Chlorine cylinder change resulted in chlorine leak alarm. Informed Carter Dunn (RO) working on site. Allowed chlorine scrubber to vent space. Replaced bank 1, set weigh scale and primed hypochlorous acid lines Station back to auto | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-11-27
EAST | November | Changed bank 1 chlorine cylinders. | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-11-19
EAST | November | On site for station check Verified chlorine analyzers, 14:10, in mg/L Influent total Cl - G 1.43; A 1.47 Effluent free Cl - G 1.91; A 1.96 Effluent total Cl - G 4.02; A 4.09 Simulated free Cl - G 1.81; A 1.95 Recorded observations in the shared PWQ sheet Station and equipment okay | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-11-21
EAST | November | Attended site for station check Station was manual off at the time of station check, Joe Mazza and Jackie Saunders changed chlorine cylinder bank 1 Verified chlorine analyzers, 9:30, in mg/L Influent total Cl - G 1.42; A 1.48 Effluent free Cl - G 1.88; A 1.82 Effluent total Cl - G 2.64; A 2.61 Simulated free Cl - G 1.83; A 1.88 Recorded observations in the shared PWQ sheet Security staff on site to repair the swipe card reader Station and equipment okay | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-11-19
EAST | November | On site for station check Verified chlorine analyzers, 9:25, in mg/L Influent total Cl - G 1.36; A 1.38 Effluent free Cl - G 2.04; A 2.08 Effluent total Cl - G 4.40; A 4.73 Simulated free Cl - G 1.77; A 1.74 Recorded observations in the shared PWQ sheet Checked unit heaters, ensured they are running and maintaining station temperature Inspected equipment All okay | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-11-26
EAST | November | On site to check station and equipment. Pump 2 and 3 are running in duty 1 upon arrival. Chlorine booster pump 1 discharge pressure = 240 psi. Chlorinator #1 is running at 41%, 54 kg/d. DF = 84%. Station readings and chlorine grabs are in PWQ sheet. Replaced CL17 reagents for effluent free analyzer.? Changed target chlorine residual setpoint from 2.2 mg/l to 2.1 mg/l.? Reviewed trends, station is under normal operation.? | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-11-24
EAST | November | On site with total power to complete the generator repairs and load test. We installed broken part and confirmed no leaks. Sean P will be returning the generator to station once load test is complete. Called Roc at 1230 to let them know the alarms to expect to see. Under direction of oic | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-11-14
EAST | November | On site for station check Recorded observations in the shared PWQ sheet Station and equipment okay | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-11-28
EAST | November | Changed chlorine cylinders on bank B. | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-11-14
EAST | November | On site for station check. Reviewed scada, duty active, controlling tower @ 64%, system pressure: 673 kpa Visual inspection in and around station Verification of equipment and instrumentation. Verified chlorine analyzers readings. Recorded Station readings in PWQ sheet No issues Outstanding alarm: None Grab Residuals @ 1004-1013 hrs Residual Grab Analyzer FCL 2.07 mg/l. 2.11 mg/l TCL. 4.88 mg/l 5.00 mg/l Sim. FCL 1.90 mg/l. 1.88 mg/l Influent TCL 1.51 mg/l. 1.48 mg/l Chemical system: Chlorinator 2 open at 39%, DF: 74%, Cl booster P2 DP= 1670 kpa Rotated Pump duty (HL) to #2 and 3 in duty 1 | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-11-14
EAST | November | On site for station check Verified chlorine analyzers while station running, 9:10, in mg/L Influent total Cl - G 1.43; A 1.46 Effluent free Cl - G 2.14; A 2.23 Effluent total Cl - G >4.40; A 5.00 Simulated free Cl - G 1.94; A 2.00 Inspected station and equipment, reviewed station trends Recorded observations in shared PWQ sheet Station and equipment okay | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-11-12
EAST | November | Under direction of OIC Joe Mazza, Worked with contractors to connect and test diesel tank interstitial floats. Then tested their inputs and alarms on SCADA. ROC was notified prior and post work. | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-11-18
EAST | November | On site to perform assigned work with Corey Ryan Performed chlorine scrubber media sampling and chlorine scrubber system inspection Station and equipment okay | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-11-11
EAST | November | On site for station check and generator test run Genset hours Start 456.3 Stop 457.6 Fuel Start 2996/2575 L Stop 2996/2507 L Run statistics Oil pressure 59 PSI Oil temperature 181 F Coolant temperature 171 F Speed 1800 RPM Exhaust temperature 700 F Current 176 A Voltage 600 V Power 171 kW Frequency 59.7 Hz Verified chlorine analyzers, 11:10, in mg/L Influent total Cl - G 1.45; A 1.49 Effluent free Cl - G 2.06; A 2.09 Effluent total Cl - G 3.1; A 2.98 Simulated free Cl - G 1.89; A 1.89 Station and equipment okay, back in auto | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-11-17
EAST | November | On site to receive 12 full Cl2 cylinders, sent back 12 empty. | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-11-18
EAST | November | Changed tower low level from 49% to 46%. Changed duty 1 start set point from 45% to 47% to eliminate alarms. | Stouffville Zone 2 Elevated Tank | 2025-11-10
EAST | November | On site responding to High Free Chlorine Reading on HACH Cl17 Analyzer Free reading 2.99mg/l on arrival. Collected Cl2 grab residual @ 19:05hrs: 2.84mg/l. Analyzer reading 2.99mg/l. Cleaned CL17 Analyzer @ 19:05hrs. Collected Cl2 grab residual @19:10hrs: 2.90mg/l. Analyzer reading: 2.96mg/l Adjusted HACH Cl17 Analyzer from 2.96mg/l to 2.90mg/l based on multiple CL2 grab residuals. No issues with Cl2 Analyzer, just receiving higher than normal Cl2 levels into tower. Will check residuals at STW3. | Stouffville Zone 2 Elevated Tank | 2025-11-26
EAST | November | Under Direction of OIC (Dan Zhou) On site for; - Station Checks - Regulatory Sampling, Micro (W11402472) Regulatory samples taken @ 11:01 hrs. Data in PWQ Excel Workbook Grabs @ 11:01 hrs. FCl: 1.57 mg/L, 1.58 mg/L, 1.58 mg/L TCL: 1.76 mg/L Analyzer FCl: 1.44 mg/L @ 11:08 adjusted AIT to 1.58 mg/L Changed AIT reagents Tower Draining Equipment out of Service: None | Stouffville Zone 2 Elevated Tank | 2025-11-26
EAST | November | On site for station check. Collected weekly micro samples (W11368128). Verification of HACH CL17 Chlorine Analyzer: 14:30hrs: Free CL2 grab residual: 1.92mg/l FCL Analyzer: 1.85mg/l Total Cl2 grab residual: 2.18mg/l Checked station readings and verified Cl2 analyzer. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Stouffville Zone 2 Elevated Tank | 2025-11-12
EAST | November | Under Direction of OIC (Dan Zhou) On site for; - Station Checks - Regulatory Sampling, Micro (W11347746) - DWSP Collection 2025 (W11455601) - inlet/Outlet Heat Trace System Inspection - Sump Pit System Inspection - Manual valve exercise - General Housekeeping - AIT Analyzer maintenance/clean - Low Temp Alarm Test - Altitude Valve Inspection - JHSC Health and safety inspection Regulatory samples taken @ 10:50 hrs. @ 10:42 deactivated tower duty for regulatory sampling Data in PWQ Excel Workbook Grabs @ 10:50 hrs. FCl: 1.71 mg/L TCL: 1.86 mg/L Analyzer FCl: 1.74 mg/L @ 10:55 activated tower duty 1 AIT Clean/Maintenance and Verification @ 11:21 hrs. Started Clean @ 11:40 hrs. Exited Clean Grabs @ 12:33 FCl: 1.21 mg/L TCL: 1.56 mg/L Analyzer: FCl: 1.20 mg/L Triggered low temp alarm @ 12:43 hrs. Tower Draining Equipment out of Service: None | Stouffville Zone 2 Elevated Tank | 2025-11-19
EAST | November | Under Direction of OIC (Stephen Baidy) @ 13:35 Changed tower Duty 1 setpoint from; Start Level: 42 %. ?-> 42% Stop Level: 70 % ??> 65% In attempt to further short cycle and refresh water in the tower, gaining a higher residual. | Stouffville Zone 1 Elevated Tank | 2025-11-05
EAST | November | Under Direction of OIC (Stephen Baidy) On site for; - Station Checks - Regulatory Sampling, Micro (W11347746), Flouride (W11347980) - Operational Sampling, Iron, ATP, Temp, FCl, TCl Reg. Sample taken @ 12:40 hrs. Data in PWQ Excel Workbook Grabs @ 12:40 hrs. FCl: 0.59 mg/L TCl: 0.71 mg/L Analyzer: FCl: 0.54 mg/L Temp: 10.2 Degrees Celsius Equipment OOS: None Facility OK | Stouffville Zone 1 Elevated Tank | 2025-11-05
EAST | November | Under Direction of OIC (Dan Zhou) On site for; - Station Checks - Regulatory Sampling, Micro (W11402472) Reg. Sample taken @ 11:46 hrs. Data in PWQ Excel Workbook Grabs @ 11:46 hrs. FCl: 1.05 mg/L TCl: 1.22 mg/L Analyzer: FCl: 1.03 mg/L Equipment OOS: None Facility OK | Stouffville Zone 1 Elevated Tank | 2025-11-26
EAST | November | Under Direction of OIC (Dan Zhou) On site for; - Station checks - Regulatory Sampling, micro (1111386678) Data in PWQ workbook Regulatory samples taken @ 13:16 hrs. Grabs @ 13:16 hrs. FCl: 1.07 mg/L TCl: 1.24 mg/L Analyzer: FCl: 1.05 mg/L FCV @ STPSTL open drawing from zone 1 to zone 2. Equipment out of service: none Station Ok | Stouffville Zone 1 Elevated Tank | 2025-11-19
EAST | November | Under Direction of OIC (Dan Zhou) On site for; - Station Checks - Regulatory Sampling, Micro (W11368128) Reg. Sample taken @ 13:00 hrs. Data in PWQ Excel Workbook Grabs @ 13:00 hrs. FCl: 1.38 mg/L TCl: 1.62 mg/L Analyzer: FCl: 1.32 mg/L Adjusted heat trace system to 10 degrees Celsius ( Maintain Temp) on circuit 1 and 2. Tower heater currently ON. Equipment OOS: None Facility OK | Stouffville Zone 1 Elevated Tank | 2025-11-12
EAST | November | Informed ROC. Performed annual calibration and put instruments in Cal mode while doing the tasks. Devices done were AIT, FIT and LIT. Unclogged and fixed the drain of the chlorine analyzer. Took grabs at the sample line. free chlorine AIT1= 0.96 mg/l Grab= 0.97 mg/l All alarms were cleared after the job. No other issues encountered. | Stouffville Zone 1 Elevated Tank | 2025-11-14
EAST | November | On site for preventative maintenance work orders Completed Chlorine analyzer maintenance Hi/ lo water level alarm test Flood alarm test Sump pit inspection Air valve inspection External venting screen inspection Dehumidifier cleaning and inspection JHSC inspection Housekeeping Station and equipment okay | Markham PD6 Reservoir | 2025-11-06
EAST | November | On site for station check and sampling, W11386706 Collected samples from North cell while draining, 10:30 South cell grabs: Free Cl 0.05 mg/L Total Cl 1.65 mg/L North cell grabs: Free Cl 0.04 mg/L Total Cl 1.53 mg/L; Analyzer - 1.58 mg/L Recorded observations in the shared PWQ sheet Replaced total chlorine CL17 analyzer reagents Station and equipment okay | Markham PD6 Reservoir | 2025-11-19
EAST | November | On site for station check and sampling Micro sampling, YD # W11347774, as well as nitrification monitoring sample, collected from the North cell at 11:25. Verified the total chlorine analyzer at the time, in mg/L Free Cl grab: 0.09 Total Cl grab: 1.16 Total Cl analyzer: 1.13 Recorded observations in the shared PWQ and reviewed station trends. Station and equipment okay | Markham PD6 Reservoir | 2025-11-05
EAST | November | On site for station check and sampling W11402500 Collected samples from North cell while draining at 10:25 and verified analyzer, mg/L South Cell Free Cl - 0.07 Total Cl - 1.46 North Cell Free Cl - 0.01 Total Cl - G 1.33; A 1.42 Recorded observations in the shared PWQ sheet Station and equipment okay | Markham PD6 Reservoir | 2025-11-26
EAST | November | On site for BacT and nitrification sampling and station check Collected samples from North cell, YD # W11368156, 10:05, while station draining Grabs: Free Cl 0.13; Total Cl 1.48 mg/L Analyzer: Total Cl 1.51 mg/L Recorded observations in the shared PWQ sheet Station and equipment okay | Markham PD6 Reservoir | 2025-11-12
CENTRAL | November | 08:45 onsite for station check. 09:24 outstanding settled water turbidity alarm -replace profile. WO previously made. Reset profile config and cleared alarm. Grab 0.125 NTU. Analyzer 0.091. 09:56 completed filter performance review. Both filters 100%. Topped up pacl day tanks. 10:10 verified low lift raw analyzers and recorded in data sheets. 10:46 notified ROC and tested chlorine leak detection and halogen emergency shut off system. No issues. Reset all alarms. 11:15 verified treated analyzers. Free grab: 1.63. Analyzer: 1.62. Total grab: 1.92/1.89/1.90. Analyzer: 1.79. Adjusted to match grab samples. Recorded on data into process and data sheets. No other issues remaining. | Keswick Water Treatment Plant | 2025-11-07
CENTRAL | November | -Performed floc tank cleanning -Performed daily filter performance review - 100% | Keswick Water Treatment Plant | 2025-11-06
CENTRAL | November | On-site for station check Recordings in PD/Lab data sheets Ran hot water flush through raw water sample line Contractors from Ferguson electric onsite for generator install prep work Filter peformance reviewed both filters 100% Station ok | Keswick Water Treatment Plant | 2025-11-10
CENTRAL | November | -Performed daily filter performance review - 100% | Keswick Water Treatment Plant | 2025-11-10
CENTRAL | November | -Performed daily filter performance review - 100% | Keswick Water Treatment Plant | 2025-11-07
CENTRAL | November | Onsite to clean flocc and settling tanks. Drained tanks to sanitary. Sprayed down and cleaned all tanks and settled water channels. Refilled tanks. 14:36 hihi settled water free chlorine 0.50 mg/l one reading. Interlocked lo lifts. Settled water reading residual of service water used to clean channel. Cleared alarm with no issues and low lift pumps resumed filling. All operation back to normal. Settled water conduit low alarm outstanding while low lifts continue to fill. | Keswick Water Treatment Plant | 2025-11-06
CENTRAL | November | Under the direction of Ben Hess, updated the settling tank drain valve delay timer logic inside PAC. Added a offset delay timer to tank 2 drain valve so that in the event of power failure or Tank 1 valve is put in manual, Tank 2 drain valve go though this offset timer to avoid opening both valves at the same time. Added valve not in manual alarm for each valve with the delay of 30 min and Low priority | Keswick Water Treatment Plant | 2025-11-06
CENTRAL | November | -Performed daily filter performance review - 100% | Keswick Water Treatment Plant | 2025-11-05
CENTRAL | November | 09:00 onsite for station check, filter performance, sampling, shoreline observation. W11347596 W11347624 W11347802 W11347596 10:10 interested filter 2 backwash. Run hours at 22.1. 10:16 completed shoreline observation and entered into spreadsheet. 10:30 collected raw water samples. Valved injection chlorine dosing to wet well instead of intake as raw water now below 12 Celsius. 11:05 collected backwash effluent raw sample. 11:22 collected prefiltration raw sample. Settled water turb analyzer has outstanding fault. Replace profile. Created work order w11420895 for instrumentation to replace wiper. 11:42 collected post filtration sample. 12:10 collected treated samples. 12:15 collected backwash effluent treated sample. 12:30 verified filler performance. Both filters at 100%. Topped up pacl and fluoride day tanks. Replaced treated and clearwell influent analyzer reagents. Completed lab work, verified analyzer and recorded data into process sheets. No issues remain onsite. | Keswick Water Treatment Plant | 2025-11-05
CENTRAL | November | On site to respond to from fluoride low alarm ~ 0.58 mg/l. Before arriving onsite, I directed ROC to switch fluoride pumps for improvement but that did not help. 1726 hrs: arrived onsite - Cleaned fluoride sample bowl - Cleaned total analyzer probe - Cleaned fluoride probe. Did a two point calibration on fluoride probe using 0.20 mg/l and 2.00 mg/l solution. During calibrations, noticed both zero and span were both out of range, calibrated and adjusted ranges. Returned fluoride analyzer to service. 1830 hrs: Returned HL pumps into, duty was active, HL pump2 started @50 L/s. Fluoride went into no fluoride alarm ~0.00mg/l after calibration. Offset was at -57. Adjusted to 0.0, got fluoride back up and reading good. Observed system operation about an hour 1920 hrs: Did grab on fluoride ~ analyzer reading @ 0.84 mg/l, grab was 0.863 mg/l. Notified ROC before leaving site. | Keswick Water Treatment Plant | 2025-11-01
CENTRAL | November | Completed filter performance check: filter 1- 100%, filter 2- 100% | Keswick Water Treatment Plant | 2025-11-04
CENTRAL | November | This entry is for kstkwp. Onsite to complete station check. 08:40 Reservoir level at 75% and draining at 50 l/s. Replace chlorine analyzer reagents. 08:56 Verified analyzer (mg/l). Free chlorine: 1.51 Analyzer: 1.49. Total Chlorine grab: 1.85. Analyzer: 1.84. No issues found. | Keswick Water Treatment Plant | 2025-11-03
CENTRAL | November | Onsite for station check. Received pacl delivery to bulk tank of 16 000L. Topped up pack day tanks. 11:00 found co2 adjusted ph analyzer failed with sensor glass fault f124. Cleaned probe, resulting in a false hi hi ph reading of 14. After consulting with Redempto H from instrumentation adjusted inmpedance upper limit from 6000 to 1000. Ph readings returned to normal readings shortly after cleaning. Notified roc of issues. 12:00 activated Georgina duty 1. Placed fluoride p2 in auto and duty 1 to test in operation. 12:25 Verified adj ph analyzer with grab. 7.03 ph. Analyzer 6.98 Completed station rounds, lab work and verified analysers. 13:12 adjusted treated water analyzer floor. Triggered brief turb spike to 1.58 ntu before returning. Grab ntu was 0.047. Analyzer returned to 0.064. 14:08 treated total chlorine grab: 2.03/2.05/2.07 analyzer 2.17. adjusted analyzer to match grab average. Changed post injection chlorine cylinder A with Alex bell. Verified filter performance. Both filters are 100%. Backdated as missed adding to entry but filled in data on process data sheet. No other issues on site. | Keswick Water Treatment Plant | 2025-11-03
CENTRAL | November | Tightened low lift p3 packing. Adjusted clear well level maintain level start from 4.0 m to 4.1 m. Cutoff adjusted from 4.2 to 4.3 m. Pacl dosage adjusted from 12 to l mg/l as settled water turbidity has been consistently low. 14:15 low fluoride fault alarm triggered. Found dousing pump 2 air locked. Cleared air and put back in service. No issues remaining. | Keswick Water Treatment Plant | 2025-11-04
CENTRAL | November | -Reviewed filter turbidity performance | Keswick Water Treatment Plant | 2025-11-27
CENTRAL | November | Completed filter performance check: filter 1- 100%, filter 2- 100% | Keswick Water Treatment Plant | 2025-11-28
CENTRAL | November | Onsite for station check. 08:43 Placed high lift pumps in auto. Station running in duty 1. 09:33 Complete filter performance review. Both filters at 100% and no issues. Topped up pacl day tanks and fluoride day tank. 09:55 verified raw water analyzers. Raw pH grab 8.10. Analyzer 8.68. Adjusted analyzer to match grab average. 10:42 verified treated analyzers. Fluoride grabs 0.77/0.77 mg/l. Analyzer 0.62. 11:40 Adjusted offset to match grabs 12:00. Fluoride grab 0.63/ 0.55/0.57 Analyzer 0.75. Adjusted analyzer to match grab. Completed fluoride analyzer maintenance. Completed settled water pump maintenance. High lifts placed in manual off. 13:47 completed chloride system inspection and vacuum leak tests. Now issues found. Louvers in generator room are stuck open. Created work order for maintenance. Completed lab work and station rounds. Entered data into process sheets. Placed high lifts back in auto. No issues remain on site. | Keswick Water Treatment Plant | 2025-11-21
CENTRAL | November | On site to complete preventative maintenance work orders. Donald M giving field trip to Angelica C. We placed NTU analyzer and chlorine analyzer & pH analyzer for low lift and high lift in calibration mode and informed ROC. - Donald M did NTU analyzer & pH probe cleaning - I did chlorine analyzer cleaning, verified raw water chlorine analyzer free Cl @ 1:07pm G:0.03mg/L A:0.01mg/L. Raw total chlorine analyzer @1:07pm G:0.11mg/L A:0.13mg/L - Clear well analyzer free Cl2 @ 1:19pm G:1.84mg/L A:1.78mg/L - Chlorine repair kit inspection - Turned on Lo lift back on @ 14:20 and undo all analyzer from calibration mode - No issues found Treated Free Cl2 @ 2:00pm G: 1.68mg/L A: 1.74mg/L Treated total Cl2 2:00pm G: 2.09mg/L A: 2.14mg/L | Keswick Water Treatment Plant | 2025-11-20
CENTRAL | November | Filter performance reviewed 100% both filters | Keswick Water Treatment Plant | 2025-11-20
CENTRAL | November | Filter performance reviewed, both filters 100% | Keswick Water Treatment Plant | 2025-11-19
CENTRAL | November | Checked filter performance, both filters 100% | Keswick Water Treatment Plant | 2025-11-24
CENTRAL | November | Onsite for work orders. Found wash water holding tank mixer shaft leaking. Tightened packing. Found raw water sample pump motor to be making a light grinding noise. W11467702 created for maintenance. Washwater settling tube cleaning completed. Ernie onsite and repaired low lift p3 vfd disconnect handle. Placed back in service. No other issues found. | Keswick Water Treatment Plant | 2025-11-25
CENTRAL | November | On site to complete station check and to collect weekly bacti samples W11386734, to collect Algea, Microcystin, geomib samples W11386556. Yash on site to troubleshoot fluoride pump #2 he adjusted the relay and we placed p#2 in D1. Plant off while troubleshooting and inform ROC. At 13:02 initiated backwash for Filter2 - run hours 28.5hrs. Turned off Georgina duty @ 13:08 - Plant running when arrived - Entered data into PWQ sheet & collected samples - Did filter performance check all ok - Topped up PACL day tank - Topped up PACL wash water tank - No issues found Treated Free Cl2 @ 9:00am G: 1.63mg/L A: 1.65mg/L Treated total Cl2 9:00am G: 2.04mg/L A: 2.02mg/L | Keswick Water Treatment Plant | 2025-11-19
CENTRAL | November | Placed all high lifts into auto. | Keswick Water Treatment Plant | 2025-11-19
CENTRAL | November | Onsite with Divya Patel. Changed post inj chlorine cylinder B. Tested filter 1 effluent valve trying to trigger fail to open alarm from 06:42 this morning. Unable to reproduce issue. No other issues remaining, | Keswick Water Treatment Plant | 2025-11-27
CENTRAL | November | Checked filter performance, both 100% | Keswick Water Treatment Plant | 2025-11-25
CENTRAL | November | Onsite for station check. 08:56 Placed high lift pumps in auto. Notified ROC. Cleared outstanding filter 1 backwash oos alarm. Backwash completed earlier this morning with no issues. 09:00 Complete filter performance review. Both filters at 100% and no issues. Topped up pacl day tanks. Ordered co2 to refill co2 tank. Replaced wet well and settled water cl17 analyzer reagents. 09:26 verified raw water analyzers. 10:07 verified treated analyzers. 10:45 High lifts placed in manual off. Completed lab work and station rounds. Entered data into process sheets. 13:00 placed high lifts back into auto. No issues remain on site. | Keswick Water Treatment Plant | 2025-11-24
CENTRAL | November | Reviewed filter performance, both filters 100% | Keswick Water Treatment Plant | 2025-11-21
CENTRAL | November | Completed filter performance check: filter 1- 100%, filter 2- 100% | Keswick Water Treatment Plant | 2025-11-26
CENTRAL | November | Onsite for station check. 11:46 activated filter 2 backwash to offset filter run times. 11:49 pacl p1 fault alarm triggered on SCADA. Notified by ROC. 12:03 collected low lift samples and verified analyzers. 12:05 found that no alarm triggered on pacl p1. Acknowledged and reset alarm. Tested pump in duty with no further issues. Topped up pack day tanks. Completed filter performance recite review. Both filters at 100%. Completed station rounds and lab work. Entered readings into pwq sheets. Recorded co2 delivery. No issues remaining. | Keswick Water Treatment Plant | 2025-11-28
CENTRAL | November | Onsite for station check and sampling. COC - Geomib, algae-asu and ALTOX- W11402342 MBHP and MBTEB - W11402528 09:40 Station running in duty. High lift for 99 l/s. Completed filter performance review. Both filters 100%. Topped up pacl day tanks and fluoride day tank. 09:50 collected raw samples and verified low lift analyzers. Entered data into process sheets. 10:14 adjusted ph analyzer grab. 6.98. Analyzer 7.18. Carbon dioxide flow is high at 118 l/min. Adjusted ph probe to match grab. Co2 flow dropped to 30 l/min. 10:55 collected treated water samples and verified analyzers (mg/): free grab: 1.79. A: 1.78 total grab: 2.08 A: 2.14 Fluoride grab: 0.662 A 0.69 Turbidity grab: 0.069 ntu A: 0.054 Entered reading and data into process and data sheets. 13:02 kstp filter 1 backwash interlock due to washwater holding tank high level. Acknowledged alarm. Filter will backwash once holding tank water is processed. No new issues remain in site. | Keswick Water Treatment Plant | 2025-11-26
CENTRAL | November | 08:48 onsite to complete work orders with Divya Patel. Placed high, washwater and low lift pumps in manual off. 09:11 notified roc running generator test. 09:31 initiated gen test. Fuel at 1938L. Pre inspection ok. Changed post injection chlorine cylinder B. 10:07 placed pumps back in auto. Cleared alarms from generator transfer. Reset filters. Cleared chlorine emergency valve closures alarm. Completed following work orders: hoist inspection. high lift p2 fcv inspection. Station prv inspection and test. Jhsc inspection. Washwater maintenance and inspection. Tested emergency stops. Cleared alarms. Fluoride P1 and p2 maintenance and inspection. 11:20 activated high lift p4 in manual to run generator under load and test fluoride p2. Fluoride pump triggered a speed deviation alarm overnight and again during this test run. Rotated to fluoride p2. 12:04 placed p4 back in manual off. 12:55 completed generator test run. Fuel at 1882 L. Run hour 3 hour and 24 min. Run meter did not capture this. Generator is getting replaced in near future so no with order created. Outstanding raw water turbidity fault. Analyzer sample flow was to more. Adjusted flow and cleared alarm. Ran fluoride pump 2 to site glass and cleared an air lock. 13:00 Ran high lift pump 4 in manual to test fluoride dosing. No issues remaining. 13:28 placed all pumps back in auto. Divya Patel completed air blower maintenance work order. | Keswick Water Treatment Plant | 2025-11-13
CENTRAL | November | Completed daily filter performance review, both filters 100%. | Keswick Water Treatment Plant | 2025-11-13
CENTRAL | November | -Performed daily filter performance review - 100% | Keswick Water Treatment Plant | 2025-11-11
CENTRAL | November | Completed daily filter performance review, both filters 100%. | Keswick Water Treatment Plant | 2025-11-14
CENTRAL | November | Completed daily filter performance review, both filters 100%. | Keswick Water Treatment Plant | 2025-11-17
CENTRAL | November | ROC informed power blip in Georgina are that cause series of alarm. Reviewed SCADA, utility power is available. Reset all alarms and plant is in standby. | Keswick Water Treatment Plant | 2025-11-16
CENTRAL | November | ROC called regarding filter #1 effluent valve fault - unclear of cause. Alarm was able to be reset and filter 1 went back to production. | Keswick Water Treatment Plant | 2025-11-11
CENTRAL | November | On site to complete station check and to collect weekly bacti samples W11368184, to collect Algea, Microcystin, geomib samples W11367998 & to collect GLIP samples W11368418. While collecting raw water sample caused hi NTU & when cane on site noticed Lo lift raw water ph hihi alarm @10:38am. Call Redempto from INST to help with fixing ph analyzer. Adjusted the exceeded limit from 6000 to 10000. Ben Hess on site to assist - Plant running when arrived - Entered data into PWQ sheet & collected samples - Did filter performance check all ok - Topped up PACL day tank - Topped up PACL wash water tank - No issues found Treated Free Cl2 @ 11:50am G: 1.72mg/L A: 1.73mg/L Treated total Cl2 11:50am G: 2.06mg/L A: 2.14mg/L | Keswick Water Treatment Plant | 2025-11-12
CENTRAL | November | Completed daily filter performance review, both filters 100%. | Keswick Water Treatment Plant | 2025-11-12
CENTRAL | November | 07:30 onsite. Low lift LOTO for diver inspection of intake. Precognition valves in manual off. Raw water sample pump off. Tested fluoride pump 2 and triggered speed deviation fault. Yash from PCS looking at it remotely. Hot flushed raw water sample line as requested by divers to ensure sample line is cleared and cleaned. Hot flushed pacl lines and tested pacl flood alarm. 12:56 confirmed with divers impacting complete. Removed low lift LOTO. Placed pumps 1 and 2 back in service. Raw water pump back in service. Perchlorination valves back in auto. Pump 3 disconnect handle lock out is damaged and needs replacement. Left powered off. Created w11452592 for maintenance to replace. Fluoride p2 placed back in service. Intermittent speed deviation issues will still occur but pcs has identified issue to repair later. If alarm triggers rotate to p1. 14:55 placed high lift pumps back in auto. No other issues remaining. . | Keswick Water Treatment Plant | 2025-11-18
CENTRAL | November | 08:30 onsite for station check. Adjusted low lift duty start from 120 mm to 110 mm to reduce number of pump starts on low lift pumps. Placed low lift p3 manual off while Kyle R and Dan B. Investigate vfd not ready alarms triggering intermittently. Both low lift p2 and p3 triggered alarms as electricians worked on them. 10:58 ran HL P2 and p4 in manual on. Fluoride p2 speed deviation alarm triggered. Rotated to p1. W11445975 created for maintenance to troubleshoot. Completed filter performance review. Both filters at 100%. Topped up pacl and fluoride day tanks. 11:20 verified treated analyzers: Fluoride grab: 0.678. Analyzer 0.78. Adjusted to match grab. Verified all analyzers and completed lab work. Entered data into process sheets. 12:34 placed all pumps back in auto. 13:25 adjusted pacl dosage to 10 mg/ from 11. No other new issues found. | Keswick Water Treatment Plant | 2025-11-14
CENTRAL | November | On site with electrician Dan Boate to investigate Low Lift Pump #3 Not Ready Alarms. Input wiring connections in scada cabinet and vfd inspected. All in good condition. Swapped control relay on Pump# 2 and Pump #3 associated with Not Ready Alarm input to test relay function. Pump # 3 returned to normal operation. | Keswick Water Treatment Plant | 2025-11-14
CENTRAL | November | Completed daily filter performance review, both filters 100%. | Keswick Water Treatment Plant | 2025-11-18
EAST | November | Onsite for annual calibrations Informed ROC Used cal mode on scada during the work Instruments calibrated: AIT, FIT, PIT and LIT No adjustments made to AIT . As found =as left 1.60mg/L Informed ROC, armed building and left site | Sutton Elevated Tank | 2025-11-10
CENTRAL | November | Onsite for station check. Station in standby. Topped up pack day tanks. Completed filter performance review. Both filters at 100%. 09:15 collected raw water grab samples. Verified analyzers. 09:59 placed high lift p2 and p3 in manual on. 10:09 collected treated grab samples. Verified analyzers. Recorded all lab and station data into process sheets. Replaced post injection chlorine cylinder A with Divya Patel. Adjusted post injection manual chlorine dosage from 145 to 140 %. Treated free chlorine demand has dropped in the colder weather. 14:18. LOTO all low lift pumps. Stopped raw water sample pump. Notified ROC. Diver contractors will be inspecting intake structure at 0700 November 18th. | Keswick Water Treatment Plant | 2025-11-17
EAST | November | On site to complete station check. Collecting weekly Bac-t Sample. Collecting VOC Samples. W11348660 Weekly Bac-t Sample. W11348632 VOC Samples. No outstanding alarms on site. Time: 11:05 Grab (mg/l) Analyzer (mg/l) Free: 1.35 1.36 Total: 1.65 Verified analyzer with grabs. Checked site and trends. No equipment OOS on site. | Sutton Elevated Tank | 2025-11-05
EAST | November | On site for station check and weekly micro sampling (W11403098) Tower level - 72% and draining at 25 L/s Recorded station readings in PWQ sheets Verified analyzer reading with grab chlorine residuals: @11:20 Grab free: 1.42 mg/L Grab total: 1.78 mg/L Analyzer: 1.38 mg/L Reviewed trends, equipment OOS: none Station ok | Sutton Elevated Tank | 2025-11-26
EAST | November | On site for station check, weekly micro sampling (W11387438) and to complete monthly PMs Tower level - 85% and filling at 31 L/s Recorded station readings in PWQ sheets Verified CL-17 analyzer with grab chlorine residuals @11:00 Grab free: 1.83 mg/L / Analyzer: 1.79 mg/L Grab total: 2.13 mg/L Collected micro sample @11:05 Collected operational ATP sample for in-house lab analysis - Chlorine analyzer maintenance - from 11:24 to 11:51. No issues - Portable gasoline generator test - JHSC health and safety inspection - Low temperature alarm test - Heat trace system inspection - Sump pit / pump inspection - Housekeeping Reviewed trends, Equipment ok Station ok | Sutton Elevated Tank | 2025-11-19
EAST | November | Changed tower hi level alarm from 88% to 92%. The normal fill cycle stops at 90.5%. | Sutton Elevated Tank | 2025-11-19
EAST | November | On site for station check, weekly micro sampling (W11368869) and VOC resamples (W11435975) Tower level - 79% and filling at 35 L/s Recorded station readings in PWQ sheets Verified analyzer reading with grab chlorine residuals @11:50 Grab free: 1.81 mg/L / Analyzer: 1.81 mg/L Grab total: 2.14 mg/L Collected micro sample and VOC samples @11:54 Reviewed trends, equipment OOS: none Station ok | Sutton Elevated Tank | 2025-11-12
EAST | November | On site for station check and equipment verifications Duty is not active - tower level - 71% and draining at 11 L/s Recorded station readings in PWQ sheets Verified analyzer readings with grab chlorine residuals - made the following adjustments Inlet FCL - Grab: 1.85 mg/L / Analyzer: 1.78 mg/L Outlet FCL - Grab: 1.85 mg/L / Analyzer: 1.72 mg/L Outlet TCL - Grab: 2.44 mg/L / Analyzer: 2.58 mg/L Reviewed trends, equipment OOS: None Station ok | Keswick Deer Park Elevated Tank | 2025-11-03
EAST | November | On site to complete station check. Collecting weekly Bac-t Sample. Collecting VOC samples. W11348674 Weekly Bac-t Sample. W11348646 VOC Samples. Cleared outstanding alarms at 10:05. Time: 10:08 Inlet Grab (mg/l) Analyzer (mg/l) Free: 1.78 1.82 Total: 2.30 2.30 Time: 10:13 Outlet Grab (mg/l) Analyzer (mg/l) Free: 1.78 1.85 Total: 2.10 2.47-2.10 After multiple grabs were taken adjusted the treated total analyzer at 10:16 from 2.47mg/l to 2.10mg/l. Checked site and trends. No OOS equipment on site. | Keswick Deer Park Elevated Tank | 2025-11-05
EAST | November | On site for station check and weekly micro sampling (W11387452) Tower level - 64% and filling at 15.6 L/s Recorded station readings in PWQ sheets Verified analyzer readings with grab chlorine residuals Inlet: @10:09 Grab free: 2.06 mg/L / Analyzer: 2.22 mg/L - adjusted based on grabs Grab total: 2.52 mg/L / Analyzer: 2.50 mg/L Outlet: @10:13 Grab free: 1.82 mg/L / Analyzer: 1.90 mg/L Grab total: 2.16 mg/L / Analyzer: 2.18 mg/L Collected micro sample from outlet @10:15 Collected operational ATP sample for in-house lab Reviewed trends, equipment OOS: none Station ok | Keswick Deer Park Elevated Tank | 2025-11-19
EAST | November | On site for station check and weekly micro sampling (W11403112) Tower level - 73% and filling Recorded station readings in PWQ sheets Verified analyzer readings with grab chlorine residuals: Inlet: @10:19 Grab free: 1.78 mg/L / Analyzer: 1.76 mg/L Grab total: 2.15 mg/L / Analyzer: 2.25 mg/L - adjusted based on grabs Outlet: @10:23 Grab free: 1.50 mg/L / Analyzer: 1.45 mg/L Grab total: 1.84 mg/L / Analyzer: 2.02 mg/L - adjusted based on grabs Reviewed trends, Equipment OOS: none Station ok | Keswick Deer Park Elevated Tank | 2025-11-26
EAST | November | On site for station check and equipment verifications Tower level - 63% and draining Recorded station readings in PWQ sheets Verified analyzer readings with grab chlorine residuals - no adjustments needed - Chlorine leak alarm went off just after arrived on site @09:43. Chlorine detector spiked to 0.6 ppm and immediately came back down. Checked for leaks in chlorine room, nothing found. Gas detector reading 0 for 30 mins after alarms cleared. No further issues Reviewed trends, equipment OOS: None Station ok | Keswick Deer Park Elevated Tank | 2025-11-14
EAST | November | On site for station check and equipment verifications Tower level - 63% and draining Recorded station readings in PWQ sheets Verified analyzer readings - made the following adjustments Inlet free analyzer from 1.54 mg/L to 1.74 mg/L Outlet free analyzer from 1.61 mg/L to 1.70 mg/L Chlorine booster pump was starting and stopping frequently due to low flow coming into the tower (Only KSTP was running) flow was fluctuating between 0 and 6 L/s. Adjusted minimum dosing flow from chlorine system from 5 to 7 L/s Reviewed trends, equipment OOS: None Station ok | Keswick Deer Park Elevated Tank | 2025-11-17
EAST | November | On site for monthly maintenance: - Portable gasoline generator test - Ventilation system inspections - Low temperature alarm test - JHSC health and safety inspection - Chemical system inspection chlorine - Chlorine analyzer maintenance - depolox (11:10 to 11:30) Inlet: @11:15 Grab free: 1.61 mg/L / Analyzer: 1.42 mg/L Grab total: 2.00 mg/L / Analyzer: 1.90 mg/L Outlet: @11:19 Grab free: 1.51 mg/L / Analyzer: 1.26 mg/L Grab total: 1.86 mg/L / Analyzer: 1.68 mg/L Reverted chlorine dosing flow start to 5 L/s. Did not correct the issue of stopping and starting with inlet flow fluctuations Chlorine gas alarm was triggered by alarm on the 14th, did not complete today Cleared alarms, station ok | Keswick Deer Park Elevated Tank | 2025-11-18
EAST | November | On site for station check, weekly micro sampling (W11368883) and VOC resamples (W11435973) Tower level - 68% and filling at 15 L/s Recorded station readings in PWQ sheets Verified analyzer readings with grab chlorine residuals: Outlet: @10:25 Grab free: 1.90 mg/L / Analyzer: 1.82 mg/L - adjusted based on grab Grab total: 2.34 mg/L / Analyzer: 2.26 mg/L Inlet: @10:32 Grab free: 2.52 mg/L / Analyzer: 2.29 mg/L - adjusted based on grab Grab total: 3.04 mg/L / Analyzer: 3.04 mg/L Collected micro sample and VOC samples @10:38 Chlorinator #1 Dosage factor: 300% ??>250% Chlorinator #2 Dosage factor: 450% ??> 250% Reviewed trends, equipment OOS: None Station ok | Keswick Deer Park Elevated Tank | 2025-11-12
CENTRAL | November | On site responding to Free chlorine low and Lolo alarms - CMU5 #W11427983. Alarms came in @19:25 Reviewed trends, it has been erratic readings since earlier this morning. The total chlorine analyzer is reading stables, so that indicates an analyzer issue Arrived on site, checked flow to the analyzer, placed analyzer to clean mode. When cleaning the colorimeter, found that the stir bar was missing. Had a spare stir bar, placed it into the unit. Placed unit back to operation. The chlorine value was coming up slowly, but temporarily placed the signal average from 2 to 1 to get readings quicker. Verified analyzer reading @21:25 Grab free: 1.57 mg/L / Analyzer: 1.54 mg/L Placed signal average back to 2. No further issues with free chlorine analyzer. Informed ROC, station ok | Keswick West Park Reservoir | 2025-11-07
CENTRAL | November | Onsite to complete station check 07:34 Reservoir level at 77% and draining at 53 s. 07:49 notified roc and completed chlorine leak alarm test of sensor. 07:50 Verified analyzer (mg/l). Free chlorine: Analyzer 1.51. Analyzer 1.56. Total Chlorine grab: 1.83. Analyzer: 1.82. No issues found. | Keswick West Park Reservoir | 2025-11-07
CENTRAL | November | Onsite to complete work orders and to assist isolation for air valve replacement. 09:00 closed inlet valve 1 and 2. Jhsc inspection. Inspected and test ran gas standby generator. 09:51 Placed free and total chlorine analyzer in calibration mode. Cleaned analyzer s. 10:45 total grab 1.79. Analyzer 1.84. Free grab: 1.51/1.52/1.51 Analyzer: 1.27. Adjusted to match grab samples. Contractors completed air valve replacement. Reopened all valves and tank inlet valves. Gary from linear tested free chlorine from new air valve as free 2.04 mg/l. Notified roc site back online. 11:55 tested chlorine dosing system. No issues found. Left site with no outstanding new issues. | Keswick West Park Reservoir | 2025-11-04
CENTRAL | November | Onsite to complete station check and sampling. VOC - W11349012 MBDW - W11349026 07:56 Reservoir level at 76% and draining at 47 l/s. 08:05 Verified analyzer (mg/l) and collected samples. Free chlorine: 1.55 Analyzer: 1.60. Total Chlorine grab: 1.81. Analyzer: 1.85. No issues found. | Keswick West Park Reservoir | 2025-11-05
CENTRAL | November | Onsite to complete station check. 08:40 Reservoir level at 75% and draining at 50 l/s. Replace chlorine analyzer reagents. 08:56 Verified analyzer (mg/l). Free chlorine: 1.51 Analyzer: 1.49. Total Chlorine grab: 1.85. Analyzer: 1.84. No issues found. | Keswick West Park Reservoir | 2025-11-03
CENTRAL | November | Onsite to complete station check. 07:42 Reservoir level at 79% and draining at 77 l/s. 07:45 Verified analyzer (mg/l) Free chlorine grab: 1.71. Analyzer: 1.72. Total Chlorine grab: 1.97. Analyzer: 2.03 No issues found. | Keswick West Park Reservoir | 2025-11-24
CENTRAL | November | Onsite to complete station check and sampling. Cox W11387581. 13:35 Reservoir level at 74% and draining at 35 l/s. 13:40 Verified analyzer (mg/l) and collected samples. Free chlorine grab: 1.61. Analyzer: 1.63. Total Chlorine grab: 1.93. Analyzer: 1.97. Adjusted chlorine manual dosage from 120% to 118% No issues found. | Keswick West Park Reservoir | 2025-11-19
CENTRAL | November | Donald M & I changed chlorine cylinder, Angelic from ROC on site for training. On site to troubleshoot free chlorine analyzer. Cleaned free & total chlorine analyzer. We also changed tubings for free chlorine analyzer. Verified analyzers Free grabs @ 11:03am G:- 1.70mg/L A:- 1.69mg/L Total grabs @10:00am G:- 1.96mg/L A:- 2.02mg/L | Keswick West Park Reservoir | 2025-11-20
CENTRAL | November | Onsite to complete station check. 07:43 Reservoir level at 66% and draining at 67 ll/s. 07:51 Verified analyzer (mg/l) and collected samples. Free chlorine grab: 1.62. Analyzer: 1.69. Total Chlorine grab: 1.95. Analyzer: 1.99. No issues found. | Keswick West Park Reservoir | 2025-11-21
CENTRAL | November | Onsite to complete station check. 08:16 Reservoir level at 53% and draining at 73 l/s. 08:22 Verified analyzer (mg/l). Free chlorine grab: 1.68. Analyzer: 1.68. Total Chlorine grab: 1.97. Analyzer: 1.98. No issues found. | Keswick West Park Reservoir | 2025-11-28
CENTRAL | November | Received a call from RO Carter Dunn regarding a low free chlorine analyzer alarm at 00:52. Activated duty and monitored for recovery. Free chlorine analyzer recovered at 01:20. Total chlorine analyzer was virtually unchanged during that time. As per the system adverse water quality procedure - For storages in free chlorine systems, including Keswick, an operator must attend site if the analyzer has been <0.05 mg/L for more than 1 hour and take a grab sample. The free chlorine analyzer recovered within the 1 hour requirement Station and equipment okay | Keswick West Park Reservoir | 2025-11-20
CENTRAL | November | Onsite to complete station check and sampling. COC W11403191. 14:11 Reservoir level at 81% and draining at 40 L/s. 14:15 Verified analyzer (mg/l) and collected sample. Free chlorine grab: 1.65. Analyzer: 1.71. Total Chlorine grab: 1.98. Analyzer: 2.00. No issues found. | Keswick West Park Reservoir | 2025-11-26
CENTRAL | November | Onsite for station check Recordings in PD sheet station ok | Keswick West Park Reservoir | 2025-11-11
CENTRAL | November | Onsite to complete station check. 07:44 Reservoir level at 72% and draining at 67 l/s. 07:50 Verified analyzer (mg/l) and collected samples. Free chlorine: Analyzer 1.63/1.64/1.64 Analyzer 1.73. Adjusted analyzer to match grabs. Total Chlorine grab: 1.96. Analyzer: 1.98. Adjusted chlorine manual dosage from 122% to 120% No issues found. | Keswick West Park Reservoir | 2025-11-14
CENTRAL | November | On site to complete station check. - Tower filling level @69% @10L/s - Entered data into PD sheet - Check trends all okay - Checked reagents - Equipment all okay - No issues found Free Cl grab @ 10:26am G: 1.65mg/L A: 1.60mg/L Treated Total Cl grab @ 10:26am G: 1.89mg/L A: 1.94mg/L | Keswick West Park Reservoir | 2025-11-17
CENTRAL | November | On site to complete station check & to collect weekly bacti samples W11368983 & to collect VOC samples W11435976. - Tower draining level @71% @45L/s - Entered data into PD sheet & collected samples - Check trends all okay - Checked reagents - Equipment all okay - No issues found Free Cl grab @ 9:16am G: 1.59mg/L A: 1.65mg/L Treated Total Cl grab @ 9:16am G: 1.98mg/L A: 1.92mg/L | Keswick West Park Reservoir | 2025-11-12
EAST | November | On site for station check. Collected weekly micro samples (W11347652). Verification of HACH CL17 Chlorine Analyzer: 10:35hrs: Free CL2 grab residual: 1.04mg/l FCL Analyzer: 0.99mg/l Total Cl2 grab residual: 1.16mg/l Checked station readings and verified Cl2 analyzer. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Musselman's Lake Elevated Tank | 2025-11-05
EAST | November | On site for station check. Collected weekly micro samples (W11402370). Verification of HACH CL17 Chlorine Analyzer: 11:30hrs: Free CL2 grab residual: 1.11mg/l FCL Analyzer: 1.11mg/l Total Cl2 grab residual: 1.26mg/l Checked station readings and verified Cl2 analyzer. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None | Musselman's Lake Elevated Tank | 2025-11-26
EAST | November | On site for monthly work orders, notified ROC of work being done. Chlorine analyzer maintenance: Completed cleaning and verified with grab sample. @ 11:33 Grab: 1.10 mg/L. Analyzer: 1.09 mg/L Eyewash station wash and re-fill. Manual valve exercise. JHSC inspections - all OK. Portable Generator test run. Building low temperature alarm test - alarm triggered at 10:30, and was cleared. Heat Trace inspection. Sump pit inspection. General housekeeping. | Musselman's Lake Elevated Tank | 2025-11-20
EAST | November | On site for station check. Collected in house iron operational samples. Collected weekly micro samples (W11386584). Verification of HACH CL17 Chlorine Analyzer: hrs: Free CL2 grab residual: 1.05mg/l FCL Analyzer: 1.10mg/l Total Cl2 grab residual: 1.18mg/l Checked station readings and verified Cl2 analyzer. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Musselman's Lake Elevated Tank | 2025-11-19
EAST | November | On site for station check. Collected weekly micro samples (W11368026). Verification of HACH CL17 Chlorine Analyzer: 11:15hrs: Free CL2 grab residual: 1.04mg/l FCL Analyzer: 01.03mg/l Total Cl2 grab residual: 1.18mg/l Checked station readings and verified Cl2 analyzer. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Musselman's Lake Elevated Tank | 2025-11-12
EAST | November | Onsite to perform annual calibration. Informed ROC. Calibration mode was used during the work. Devices were done as below: TWR_LIT, FIT and AIT. Replaced motor for free chlorine analyzer. Informed ROC before and after calibration of TWR_LIT. Took a multiple grabs and adjusted analyzer accordingly. Free grab : 1.08 mg/l, AIT - 1.10 mg/l All the related alarms were cleared. Informed ROC, armed the building and left the site. | Musselman's Lake Elevated Tank | 2025-11-18
EAST | November | On its to complete station check. Time: 14:35 Header Grab (mg/l) Analyzer (mg/l) Free: 1.88 2.37-1.88 Total: 2.34 2.40 Time: 14:40 Inlet Grab (mg/l) Analyzer (mg/l) Free: 1.97 2.01 Total: 2.36 2.41 Time: 14:42 Outlet Grab (mg/l) Analyzer (mg/l) Free: 1.67 1.62 Total: 1.88 1.94 After multiple grabs adjusted the header free residual from a 2.37mg/l to a 1.88mg/l at 14:37. Checked site and trends. | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2025-11-07
EAST | November | On site for monthly maintenance - informed ROC - Dehumidifier inspection and cleaning - Recirculating pump inspection: Was running when arrived on site, all good - JHSC health and safety inspection - Inlet / Outlet Heat trace inspections - Actuated valve exercise - Chlorine scrubber inspection - Ventilation system inspection - Siemens Depolox analyzer maintenance - verified analyzer readings after maintenance Header: @11:05 Grab free: 1.57 mg/L / Analyzer: 1.62 mg/L Grab total: 1.88 mg/L / Analyzer: 1.82 mg/L Inlet: @11:12 Grab free: 1.53 mg/L / Analyzer: 1.58 mg/L Grab total: 1.85 mg/L / Analyzer: 1.72 mg/L Outlet: @11:19 Grab free: 1.58 mg/L / Analyzer: 1.71 mg/L - Adjusted based on grab Grab total: 1.90 mg/L / Analyzer: 1.83 mg/? - adjusted based on grab Equipment back to auto Station ok | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2025-11-06
EAST | November | On site for station check and equipment verifications Duty is not active - Tower level - 75% and draining at 23 L/s Recorded station readings in PWQ sheets Verified analyzer readings with grab residuals - no adjustments needed Reviewed trends, equipment OOS: None Station ok | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2025-11-03
EAST | November | On site to complete station check. Collecting weekly Bac-t Sample. Collecting VOC Samples. W11348674 Weekly Bac-t Sample. W11348646 VOC Samples. Started heaters on site at 09:00. Cleared alarms on site at 09:06. Time: 09:17 Header Grab (mg/l) Analyzer (mg/l) Free: 1.63 1.66 Total: 1.89 1.91 Time: 09:20 Inlet Grab (mg/l) Analyzer (mg/l) Free: 1.80 2.08-1.80 Total: 2.12 2.14 Time: 09:25 Outlet Grab (mg/l) Analyzer (mg/l) Free: 1.65 1.70 Total: 1.92 1.91 At 09:21 adjusted the free residual on the inlet analyzer from 2.08mg/l to 1.80mg/l after multiple grabs were taken. Checked site and trends. No OOS equipment. | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2025-11-05
EAST | November | On site for station check and weekly micro sampling (W11387452) Tower level - 67% and filling at 51 L/s Recorded station readings in PWQ sheets Verified analyzer readings with grab chlorine residuals Inlet: 09:13 Grab free: 1.81 mg/L / Analyzer: 1.62 mg/L - adjusted based on grabs Grab total: 2.32 mg/L / Analyzer: 2.28 mg/L Outlet: @09:17 Grab free: 1.58 mg/L / Analyzer: 1.57 mg/L Grab total: 1.90 mg/L / Analyzer: 1.90 mg/L Header: @09:20 Grab free: 1.54 mg/L / Analyzer: 1.49 mg/L Grab total: 1.89 mg/L / Analyzer: 1.88 mg/L Collected micro sample from header @09:25 Reviewed trends, equipment OOS: None Station ok | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2025-11-19
EAST | November | On site to trigger monthly chlorine test - triggered @09:13 - no issues with leak test or scrubber | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2025-11-27
EAST | November | On site for station check and weekly micro sampling (W11403112) Tower level - 74% and draining at 64 L/s Recorded station readings in PWQ sheets Verified analyzer readings with grab chlorine residuals: @09:33-09:45 Inlet: Grab free: 1.98 mg/L / Analyzer: 1.95 mg/L Grab total: 2.42 mg/L / Analyzer: 2.46 mg/L Outlet: Grab free: 1.65 mg/L / Analyzer: 1.57 mg/L - adjusted analyzer based on grabs Grab total: 1.89 mg/L / Analyzer: 1.91 mg/L Header: Grab free: 1.56 mg/L / Analyzer: 1.46 mg/L - adjusted analyzer based on grabs Grab total: 1.89 mg/L / Analyzer: 1.86 mg/L Collected micro sample from header @09:48 Reviewed trends, equipment OOS: none Station ok | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2025-11-26
EAST | November | On site for station check, weekly micro sampling (W11368883), THM resamples (W11435973) Tower level - 72% and draining Recorded station readings in PWQ sheets Verified depolox analyzer readings - no adjustments needed Header: @09:10 Grab free: 1.59 mg/L / Analyzer: 1.54 mg/L Grab total: 1.94 mg/L / Analyzer: 1.95 mg/L Inlet: @09:14 Grab free: 1.60 mg/L / Analyzer: 1.66 mg/L Grab total: 1.96 mg/L / Analyzer: 2.01 mg/L Outlet: @09:18 Grab free: 1.56 mg/L / Analyzer: 1.50 mg/L Grab total: 1.93 mg/L / Analyzer: 1.93 mg/L Collected micro sample and VOC resamples @09:20 Performed month test run of portable gasoline generator Reviewed trends, equipment OOS: none Station ok | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2025-11-12
EAST | November | On site for monthly maintenance: - Chemical system inspection chlorine - Chlorine gas feed system performance check - Chlorine scrubber check | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2025-11-18
EAST | November | On site for station check and equipment verifications Tower level - 69% and draining at 50 L/s Recorded station readings in PWQ sheets Verified analyzer readings - made the following adjustments Inlet Free Analyzer adjusted from 1.44 to 1.56 mg/L Reviewed trends, equipment OOS: None Station ok | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2025-11-17
EAST | November | Attended site to zero and span calibrate the free chlorine analyzer to match the average of grabs: 0.09 mg/L | Markham Pumping Station | 2025-11-06
EAST | November | On site for station check Verified chlorine analyzers, in mg/L, 11:15 Free Cl - G 0.07; A 0.07 Total Cl - G 1.49; A 1.42 Turned unit heaters on Inspected station and equipment, reviewed station trends Station and equipment okay | Markham Pumping Station | 2025-11-10
EAST | November | On site to complete station check. No outstanding alarms on site. No OOS equipment. Time: 11:23 Grab (mg/l) Analyzer (mg/l) Free: 0.08 0.12 Total: 1.55 1.59 Verified analyzer with grabs. Checked site and trends. | Markham Pumping Station | 2025-11-03
EAST | November | On site for station check. Reviewed scada, Reservoir cells @ 40% and 40% Visual inspection in and around station Verification of equipment and instrumentation. Outstanding alarms: None Verified chlorine analyzers readings: HIHI free chlorine alarm upon arrival, performed zero cal on free chlorine value before taking grab samples. Chlorine residual @ 1131 hrs Effluent: FCL= 0.08 mg/l. TCL = 1.53 mg/l Analyzer: FCL: 0.08 mg/l. TCL: 1.50 mg/l Cleared HIHI free chlorine alarm. Station OK, recorded station readings in PWQ sheet. BP1~ Duty1 BP2 ~Duty1 BP3 ~ Duty2 | Markham Pumping Station | 2025-11-14
EAST | November | On site for station check and preventative maintenance Completed Hoist inspection JHSC inspection Generator test run Flood alarm test Dehumidifier cleaning and inspection Ventilation system inspection Housekeeping Generator test run Hours Start 582.1 Stop 583.2 Fuel Start 731/732 L Stop 703/701 L Statistics Oil pressure 58 PSI Oil temperature 198 F Coolant temperature 183 F Voltage 600 V Current 199 A Power 176 kW Frequency 60 Hz Speed 1800 RPM Exhaust temperature 672 F Verified chlorine analyzers, 12:40, in mg/L FCl - G 0.09; A 0.03 TCl - G 1.41; A 1.39 Recorded observations in the shared PWQ sheet Station and equipment okay | Markham Pumping Station | 2025-11-28
EAST | November | On site for station check Verified chlorine analyzers, 13:00, mg/L Free Cl - G 0.06; A 0.04 Total Cl - 1.43; A 1.49 Station and equipment okay, observations recorded in the PWQ sheet | Markham Pumping Station | 2025-11-21
EAST | November | On site for station check Verified chlorine analyzers, 12:30, mg/L Free Cl - G 0.07; A 0.03 Total Cl - G 1.52; A 1.55 Completed shared PWQ sheet Station and equipment okay | Markham Pumping Station | 2025-11-17
EAST | November | On site for station check and sampling Micro sampling, YD #11347774, as well as nitrification monitoring sample, collected while station draining, 14:10 Verified chlorine analyzers, 14:10, in mg/: Free Cl - G 0.05; A 0.05 Total Cl - G 1.60; A 1.63 Recorded observations in the shared PWQ and reviewed station trends. Station and equipment okay | Markham Milliken Elevated Tank | 2025-11-05
EAST | November | On site to check free residual. Cleared alarms at 12:04. Time: 12:08 Grab (mg/l) Analyzer (mg/l) Free: 0.05 0.14 After multiple grabs were taken adjusted free residual to the average which was 0.05mg/l t 12:10. Will leave the tap running to help with residual control. | Markham Milliken Elevated Tank | 2025-11-03
EAST | November | On site for station check, preventative maintenance work orders and sampling W11402500 Collected samples while tower draining, 13:20, and verified analyzers in mg/L Free Cl - G 0.06; A 0.06 Total Cl - G 1.56; A 1.52 Completed JHSC inspection Chlorine analyzer maintenance Sump pit inspection Actuated valve inspection (visual) High low water level alarm test Low temperature test Dehumidifier inspection Manual valve exercise Housekeeping Heat trace system inspection Station and equipment okay | Markham Milliken Elevated Tank | 2025-11-26
EAST | November | On site for station check and sampling W11386706 Collected samples, 14:10, in mg/L Free Cl - G 0.04; A 0.05 Total Cl - G 1.72; A 1.65 Recorded observations in the shared PWQ sheet Inspected equipment Station okay | Markham Milliken Elevated Tank | 2025-11-19
EAST | November | Informed ROC. Onsite to adjust chlorine analyzer. Put the device in calibration. Performed Zero calibration for free chlorine analyzer. Took a multiple grabs and adjusted analyzer accordingly. Free Grab - 0.03 mg/l, AL free AIT - 0.03 mg/l Total grab - 1.72 mg/l, AL total AIT - 1.71 mg/l. Put the analyzer back in service. All the related alarms were cleared . No issues. Informed ROC. Armed the building and left the site. | Markham Milliken Elevated Tank | 2025-11-18
EAST | November | Informed ROC. Onsite to perform annual calibration. Calibration mode was used during the work. Devices were done as below: TWR_LIT, AIT, FIT. Replaced the faulty electrode for free chlorine analyzer. Took a multiple grabs and adjusted analyzer accordingly. Free Grab - 0.02 mg/l, Analyzer- 0.02 mg/l Total grab - 1.71 mg/l, Analyzer - 1.72 mg/l. Put everything back in service. All the related alarms cleared. No issues. Informed ROC, armed the building and left the site. | Markham Milliken Elevated Tank | 2025-11-17
EAST | November | On site for station check and sampling W11368156 Collected samples, 13:45, and verified analyzers, mg/L Free Cl - G 0.08; A -0.04 Zeroed and span calibrated free chlorine analyzer Total Cl - G 1.80; A 1.84 Recorded observations in the shared PWQ sheet Station and equipment okay | Markham Milliken Elevated Tank | 2025-11-12
EAST | November | On site for station check and sampling Micro sampling, YD # W11347774, as well as nitrification monitoring sample, collected from the West cell at 12:30. Verified the chlorine analyzer, 12:30, in mg/L Free Cl grab: 0.10 Total Cl grab: 1.37 Free Cl analyzer: 0.09 Total Cl analyzer: 1.46 Adjusted total chlorine analyzer to match average of grabs Recorded observations in the shared PWQ and reviewed station trends. Station and equipment okay | Markham PD5 Reservoir | 2025-11-05
EAST | November | On site for station check and sampling W11386706 Collected samples from the West cell while draining, 11:45 Free Cl - G 0.13; A 0.09 Total Cl - G 1.38; A 1.43 Recorded observations in the shared PWQ sheet East cell offline for rehab - Contractors (Brook) on site Station and equipment okay | Markham PD5 Reservoir | 2025-11-19
EAST | November | On site for station check and sampling W11402500 Collected sample from West Cell at 11:30 while draining, East cell offline Free Cl - G 0.06; A 0.07 Total Cl - G 1.31; A 1.37 Recorded observations in the shared PWQ sheet, including SL1000 grabs for nitrification monitoring Station is in custody of contractor Brook for major capital project, currently working on site Station and equipment okay | Markham PD5 Reservoir | 2025-11-26
EAST | November | On site for preventative maintenance work orders Informed RO Angelica of work being performed Completed High and low water level alarms test Dehumidifier cleaning and inspection JHSC inspection External venting screens Chlorine analyzer maintenance Housekeeping Station currently under construction - cell 2 out of service Station and equipment okay | Markham PD5 Reservoir | 2025-11-11
EAST | November | On site to check temperatures alarm. The unit heater was removed and followed up with contractor. The new heater is in site and will be installed soon. Lowered the low temp setting to around 4 C. Cleared the alarm. | Markham PD5 Reservoir | 2025-11-18
EAST | November | On site for sampling and station check Collected BacT sample from West cell and verified chlorine analyzers, W11368156, 10:50, in mg/L Free Cl - G 0.07; A 0.07 Total Cl - G 1.37; A 1.37 Recorded observations in shared PWQ sheet East cell out of service for rehab by Brook (Contractor) Station and equipment okay | Markham PD5 Reservoir | 2025-11-12
EAST | November | On site to collected micro samples for well #3 raw and treated, following initial raw samples from Wednesday passing Collected samples @11:30 (W11427633) Raw and treated Treated residuals: Grab free: 2.48 mg/L / Analyzer: 2.52 mg/L Grab total: 2.74 NTU: 0.084 Well #3 is back in service - running to system Station ok, informed ROC | Stouffville Well 3 | 2025-11-07
EAST | November | Under direction of OIC (Stephen Baidy) On-site for; - station checks - Start up Well pump 3 Data in PWQ excel Workbook @ 09:58 Manually started up well pump 3 @ 10:49 hrs. Manually Activated Zone 1 tower duty, changed duty setpoint start from 30 % to 42 %, placed zone 1 BPS pumps 1 and 2 in auto Influent Water Grab @ 11:08 hrs. FCl: 2.60 mg/L, 2.66 mg/L, 2.58 mg/L Adjusted AIT to 2.61 mg/L Analyzer FCl: 2.79 mg/L Effluent (Treated Water) Grab @ 11:08 hrs. FCl: 2.48 mg/L TCL: 2.74 mg/L Analyzer: FCl: 2.51 mg/L Equipment OOS: None Facility?s OK | Stouffville Well 3 | 2025-11-07
EAST | November | Under direction of OIC (Dan Zhou) On-site for; - station checks Data in PWQ excel Workbook Influent Water Grab @ 11:08 hrs. FCl: 2.60 mg/L, 2.66 mg/L, 2.58 mg/L Adjusted AIT to 2.61 mg/L Analyzer FCl: 2.79 mg/L Effluent (Treated Water) Grab @ 11:08 hrs. FCl: 2.56 mg/L, 2.60 mg/L, 2.56 Ave = 2.573 Adjusted AIT to 2.57 TCL: 3.02 mg/L Analyzer: FCl: 2.51 mg/L @ 10:36 changed silicate pump duty to pump 2 duty 1 pump 2 duty 2 Equipment OOS: None Facility?s OK | Stouffville Well 3 | 2025-11-10
EAST | November | Informed ROC. Tested the chlorine sensor with 5ppm gas and it was working good. Informed operator Patrick that there seems to be no issue. Left the calibration gas in the well station but it does not have any regulator. | Stouffville Well 3 | 2025-11-03
EAST | November | On site to assist with starting up Well #3 after receiving micro sample results (W11416114 and W11416112) for raw sample collected earlier this week. 09:10hrs: Ran well to waste for a few minutes prior to starting into distribution system. | Stouffville Well 3 | 2025-11-07
EAST | November | Restarted the Operator Interface Terminal due to Windows updates. Well was off. Notified the Remote Operations Center and the OIC. | Stouffville Well 3 | 2025-11-03
EAST | November | Under direction of OIC (Stephen Baidy) On-site for; - station checks - Operational Sampling - Quarterly pH monitoring Data in PWQ excel Workbook Influent Water Grab @ 14:11 hrs. FCl: 0.81 mg/L Analyzer FCl: 0.81 mg/L Effluent (Treated Water) Grab @ 14:11 hrs. FCl: 0.74 mg/L TCL: 0.87 mg/L Analyzer: FCl: 0.68 mg/L Well pH = 8.08 Temp: 12.2 degrees Celsius Alarms; - Influent LO and Effluent LO - due to well 3 being OOS, Well cannot be put in to service until Well 7 development confirmed. May experience LO Influent and Effluent Alarm until this point. Equipment OOS: Well 3 Facility?s equipment Duty off due to Well 7 development. | Stouffville Well 3 | 2025-11-03
EAST | November | Under direction of OIC (Stephen Baidy) On-site for; - station checks - On-site with P.Fobert to run well pump 3 to waste, after raw water runs for undetermined time, sample regs. And take turb samples periodically Data in PWQ excel Workbook @ 09:55 placed silicate pumps and chlorinators in manual off, started up well 3 pump to waste, placed de-chlorination pucks in outfall for possibility of leakage at distribution valve Influent Water Grab @ 10:08 hrs. FCl: 0.90 mg/L Analyzer FCl: 0.91 mg/L Effluent (Treated Water) Grab @ 10:08 hrs. FCl: 0.84 mg/L TCL: 0.96 mg/L Analyzer: FCl: 0.78 mg/L Alarms; - Influent LO and Effluent LO - due to well 3 being OOS, Well cannot be put in to service until Well 7 development confirmed. May experience LO Influent and Effluent Alarm until this point. - Place silicate pumps and chlorinators in manual off. - Running Well pump 3 in local pump to waste in prep for raw reg. Samples Leaving Site: P.Fobert On-Site to monitor Well 3. Equipment OOS: Silicate pumps, chlorinators due to manual off Facility?s equipment Duty off due to Well 7 development. | Stouffville Well 3 | 2025-11-05
EAST | November | On site to run well #3 to waste, and to collect raw samples set, to begin the process of bringing well #3 back online after well #7 testing (future well) Placed chemical systems to manual off. Closed station discharge valve to prevent water from entering the CT tank. Opened backflushing valve. Started well #3 in local to waste @09:55. Added dechlorination pucks to facility outfall. Discharge flow is ~ 20 L/s running to waste Took a raw NTU grab @10:40 - NTU is 0.2 Collected First raw sample @10:45 (W11416112) Performed visual inspection of facility outfall and retention pond, no issues Prepared sodium silicate system and tested pumps, all good for whenever sample results return Collected second raw sample @11:25 (W11416114) Stopped well #3 @11:30 - closed backflushing valve, and re-opened discharge valve to feed Well #3 remains in local off, with chemical pumps OOS until sample results are back. Station ok | Stouffville Well 3 | 2025-11-05
EAST | November | Under direction of OIC (Dan Zhou) On-site for; - station checks - Regulatory Sampling, micro with HPC (W11386678) - DWSP Collection 2025 (W11455601) Data in PWQ excel Workbook Regulatory Samples Taken @ 09:35 Influent Water Grab @ 09:35 hrs. FCl: 2.72 mg/L Analyzer FCl: 2.74 mg/L Effluent (Treated Water) Grab @ 09:35 hrs. FCl: 2.70 mg/L TCL: 3.10 mg/L Analyzer: FCl: 2.72 mg/L Equipment OOS: None Facility?s OK | Stouffville Well 3 | 2025-11-19
EAST | November | Under Direction of OIC (Dan Zhou) On Site for; - Chlorine leak detection test @ 11:42 placed well pump3 in manual off for chlorine leak detection test @ 11:45 performed chlorine leak detection test @ 11:57 returned well pump 3 to auto. | Stouffville Well 3 | 2025-11-20
EAST | November | Under direction of OIC (Dan Zhou) On-site for; - station checks - Regulatory sampling (W11402472) Data in PWQ excel Workbook Regulatory Samples taken @ 10:26 hrs. Influent Water Grab @ 10:26 hrs. FCl: 2.70 mg/L Analyzer FCl: 2.68 mg/L Effluent (Treated Water) Grab @ 10:26 hrs. FCl: 2.72 mg/L TCL: 3.14 mg/L Analyzer: FCl: 2.66 mg/L Equipment OOS: None Facility?s OK | Stouffville Well 3 | 2025-11-26
EAST | November | On site to check station and equipment. Well 3 was man/on to assist zone 1 filling. Station readings and chlorine grabs are in PWQ sheet. Chlorinator is running at 75%, 7 ppd. DF = 281%,? Chlorine booster pump 2 discharge pressure = 110 psi. Silicate P1 discharge pressure = 66 psi. Reviewed trends, station is under normal operation.? | Stouffville Well 3 | 2025-11-21
EAST | November | On site to verify influent CL2 Analyzer: Grab residual: 2.84mg/l Analyzer: 2.78mg/l No adjustments required. | Stouffville Well 3 | 2025-11-26
EAST | November | Under direction of OIC (Dan Zhou) On-site for; - station checks - Operational Sampling with ATP - Chlorine cylinder change - Chemical system inspection Data in PWQ excel Workbook Influent Water Grab @ 10:55 hrs. FCl: 2.80 mg/L Analyzer FCl: 2.73 mg/L Effluent (Treated Water) Grab @ 10:55 hrs. FCl: 2.78 mg/L TCL: 3.26 mg/L Analyzer: FCl: 2.72 mg/L Temp: 10.2 degrees Celsius @ 11:46 put well pump3 in manual off - Changed chlorine cylinder with OIC Dan Zhou - Performed chlorine system inspection with with POIC Dan Zhou During chemical system inspection noticed, loss of vacuum pressure during purge. Team Lead Dan Zhou is looking into recent calibration and annual rebuild records. @ 12:32 hrs. Put well pump 3 back in auto. Equipment OOS: None Facility?s OK | Stouffville Well 3 | 2025-11-24
EAST | November | Under direction of OIC (Dan Zhou) On-site for; - station checks Data in PWQ excel Workbook Influent Water Grab @ 10:26 hrs. FCl: 2.72 mg/L Analyzer FCl: 2.68 mg/L Effluent (Treated Water) Grab @ 10:26 hrs. FCl: 2.72 mg/L TCL: 3.06 mg/L Analyzer: FCl: 2.67 mg/L @ 09:35 hrs. Calibrated and cleaned turbidity meter @ 10:14 hrs. Started well pump3 Manually, Bethesda tower filling. Equipment OOS: None Facility?s OK | Stouffville Well 3 | 2025-11-28
EAST | November | Under direction of OIC (Dan Zhou) On-site for; - station checks Data in PWQ excel Workbook Influent Water Grab @ 08:46 hrs. FCl: 2.74 mg/L Analyzer FCl: 2.79 mg/L Effluent (Treated Water) Grab @ 08:46 hrs. FCl: 2.66 mg/L TCL: 3.00 mg/L Analyzer: FCl: 2.61 mg/L Equipment OOS: None Facility?s OK | Stouffville Well 3 | 2025-11-14
EAST | November | Under direction of OIC (Dan Zhou) On-site for; - station checks - Operational Sampling, (Iron, FCl, TCl, Temp, Turbidity) Data in PWQ excel Workbook Influent Water Grab @ 08:46 hrs. FCl: 2.66 mg/L, 2.64 mg/L, 2.62 mg/L Adjusted influent AIT to 2.65 mg/L Analyzer FCl: 2.79 mg/L Effluent (Treated Water) Grab @ 08:46 hrs. FCl: 2.68 mg/L TCL: 2.94 mg/L Analyzer: FCl: 2.61 mg/L Temp: 10.2 degrees Celsius, 0038 NTU Changed Influent and Effluent AIT reagents Equipment OOS: None Facility?s OK | Stouffville Well 3 | 2025-11-17
EAST | November | Man/Start Well 3 to aid filling of Zone 1 ET. | Stouffville Well 3 | 2025-11-11
EAST | November | @ 13:07 Placed well pump 3 in manual off for mobile generator switch to facility power @ 13:12 hrs. ATS switched back to facility power. @ 13:14 place well 3 back in auto | Stouffville Well 3 | 2025-11-13
EAST | November | Under direction of OIC (Dan Zhou) @ 09:57 placed well pump 3 in auto. | Stouffville Well 3 | 2025-11-14
EAST | November | Under direction of OIC (Dan Zhou) On site for; - Sodium Silicate system inspection and maintenance, injection quill cleaning and hot water flush - Chlorine analyzer Maintenance and cleaning (influent and Effluent AIT) - Turbidity analyzer maintenance/cleaning/calibration - Comprehensive housekeeping - Well 3 Bore Hole inspection Started chlorine analyzer maintenance on AIT 1 and 2 Start Clean @ 10:00 hrs. Exited Clean @ 10:57 hrs. Effluent (Treated Water) AIT verification Grab @ 11:32 hrs. FCl: 2.66 mg/L Analyzer FCl: 2.60 mg/L Influent AIT verification Grab @ 11:35 hrs. FCl: 2.69 mg/L Analyzer FCl: 2.73 mg/L Turbidity Analyzer Maintenance and clean: Clean start @ 10:10 hrs. Exited Clean @ 10:28 hrs. Sodium Silicate system flush: Started @ 11:20 hrs. Performed back flush @ 12:08 hrs. @ 12:12 Put Well pump 3 in manual ON Equipment OOS: None | Stouffville Well 3 | 2025-11-13
EAST | November | ROC called regarding CT not achieved alarm @04:30. Wells had interlocked, requested that ROC leave wells / alarms until 07:30. Incident overview: @04:25 - ROC manual started wells 1 and 2, @04:28 the wells 1 and 2 interlocked on effluent free chlorine low and CT not achieved. Effluent free was 0.35 at the time of the incident, the analyzer was reading 0.35 mg/L before the wells started. During the period that the wells were left off overnight, distribution water had been pulled back to the effluent analyzer - When the wells started, the CT not achieved alarm was generated as the chlorine residual was not high enough to meet the CT requirements. The same incident had occured on October 13th, 2025, where we had filled for adverse water quality, so filed another adverse for todays incident Reviewed trends @07:40. Manual started well #2 @07:59. By 08:12, the effluent chlorine residual is back to 1.63 mg/L, the effluent required is 0.31 mg/L, no further issues with CT. @08:13 - manual started well #1 Verbal notification to MOH @08:35 Laura Tang Verbal notification to SAC @08:41 AWQI #170675 Julian Aristizabal - Environmental Officer Paper work for notice of adverse and the resolution filed @10:00 on November 7th, 2025 Wells 1 and 2 are both running in manual, no further issues at this time | Stouffville Well 1 & 2 | 2025-11-07
EAST | November | Under direction of OIC (Stephen Baidy) On-site for; - Station checks Data in PWQ excel Workbook Influent Water Grab @ 13:40 hrs. Grab FCl: 3.74 mg/L Analyzer FCl: 3.75 mg/L Treated Water (Effluent) Grabs @ 13:40 hrs. Grabs FCl: 2.37 mg/L TCl: 3.02 mg/L Analyzer FCl: 2.35 mg/L Equipment OOS: None Facility OK | Stouffville Well 1 & 2 | 2025-11-07
EAST | November | On site for: Confirming heating block/generator breaker are back in normal position. Generator OK Arm security system. | Stouffville Well 1 & 2 | 2025-11-10
EAST | November | Under direction of OIC (Dan Zhou) On-site for; - Station checks Data in PWQ excel Workbook Influent Water Grab @ 09:38 hrs. Grab FCl: 3.76 mg/L Analyzer FCl: 3.79 mg/L Treated Water (Effluent) Grabs @ 09:38 hrs. Grabs FCl: 1.94 mg/L TCl: 2.36 mg/L Analyzer FCl: 2.00 mg/L Equipment OOS: None Facility OK | Stouffville Well 1 & 2 | 2025-11-10
EAST | November | Placed well #2 to manual on for STETBR fill cycle | Stouffville Well 1 & 2 | 2025-11-09
EAST | November | @ 09:15 Noticed Zone 2 tower filling with a residual of 0.45 mg/L, Called ROC and placed well pumps 1 and 2 in manual ON, in attempt to gain higher residual filling Zone 1 and zone 2 towers as well as distribution system. | Stouffville Well 1 & 2 | 2025-11-05
EAST | November | Under direction of OIC (Dan Zhou) On-site for; - Station checks - Regulatory Sampling, Micro (W11347746) Data in PWQ excel Workbook Influent Water Grab @ 11:48 hrs. Grab FCl: 3.68 mg/L Analyzer FCl: 3.68 mg/L Treated Water (Effluent) Grabs @ 11:48 hrs. Grabs FCl: 2.36 mg/L TCl: 2.90 mg/L Analyzer FCl: 2.34 mg/L Equipment OOS: None Facility OK | Stouffville Well 1 & 2 | 2025-11-05
EAST | November | Restarted the Operator Interface Terminal due to Windows Updates. Notified the Remote Operation Center and the OIC. Wells were off. | Stouffville Well 1 & 2 | 2025-11-03
EAST | November | Under direction of OIC (Stephen Baidy) On-site for; - Station checks - Operational Sampling - Quarterly pH monitoring Data in PWQ excel Workbook Influent Water Grab @ 09:44 hrs. Grab FCl: 3.78 mg/L Analyzer FCl: 3.71 mg/L Treated Water (Effluent) Grabs @ 09:44 hrs. Grabs FCl: 2.26 mg/L TCl: 2.80 mg/L Analyzer FCl: 2.31 mg/L Operational Sampling Well 1 pH: 7.96 Well 2 pH: 8.19 Temp: 10.1 degrees Celsius Equipment OOS: None Facility OK | Stouffville Well 1 & 2 | 2025-11-03
EAST | November | On site to check station and equipment. Duty is not active upon arrival. Cleaned turbidity meter, informed ROC. Changed CL17 reagents. Station readings and chlorine grabs are in PWQ sheet. 12:50 Manual start well 1 to assist zone 1 filling.? Hypo P1 DF = 52%, discharge pressure = 550 kpa. Silicate P2 discharge pressure = 500 kpa. Reviewed trends, station is under normal operation.? | Stouffville Well 1 & 2 | 2025-11-21
EAST | November | On site to investigate malfunctioning exhaust fan. Exhaust fan can?t be repaired and has been removed for disposal. Suitable replacement being sourced. | Stouffville Well 1 & 2 | 2025-11-21
EAST | November | Changed flow setpoint from 22 l/s to 29 l/s for both wells. | Stouffville Well 1 & 2 | 2025-11-21
EAST | November | Under direction of OIC (Dan Zhou) On-site for; - Station checks - Regulatory Sampling, micro, (W11402472) Data in PWQ excel Workbook Regulatory samples taken; - Well 1 raw 09:01 hrs - Treated 09:01 hrs. - Well 2 raw 10:06 hrs. Influent Water Grab @ 09:01 hrs. Grab FCl: 3.60 mg/L Analyzer FCl: 3.66 mg/L Treated Water (Effluent) Grabs @ 09:01 hrs. Grabs FCl: 2.32 mg/L TCl: 3.92 mg/L Analyzer FCl: 2.26 mg/L @ 09:40 switched well pump duty from well 1 duty 1 to well 2 duty 1 @ 09:40 well pump 2 started up in auto Equipment OOS: None Facility OK | Stouffville Well 1 & 2 | 2025-11-26
EAST | November | Under direction of OIC (Dan Zhou) On-site for; - Station checks - Regulatory Sampling, Micro with HPC (W11386678) Data in PWQ excel Workbook Regulatory samples taken @ 08:56 hrs. @ 08:04 Manually started well pump 1 for sampling @ 08:44 switched silicate/hypo pump duty Influent Water Grab @ 08:56 hrs. Grab FCl: 4.36 mg/L Analyzer FCl: 4.29 mg/L Treated Water (Effluent) Grabs @ 08:56 hrs. Grabs FCl: 2.68 mg/L TCl: 3.52 mg/L Analyzer FCl: 2.66 mg/L @ 09:10 manually shut off well pump 1 and placed back in auto, well pump 2 remains in manual on. Equipment OOS: None Facility OK | Stouffville Well 1 & 2 | 2025-11-19
EAST | November | Under direction of OIC (Dan Zhou) On-site for; - Station checks Data in PWQ excel Workbook Influent Water Grab @ 11:54 hrs. Grab FCl: 3.70 mg/L Analyzer FCl: 3.67 mg/L Treated Water (Effluent) Grabs @ 09:01 hrs. Grabs FCl: 2.37 mg/L TCl: 3.06 mg/L Analyzer FCl: 2.39 mg/L Equipment OOS: None Facility OK | Stouffville Well 1 & 2 | 2025-11-28
EAST | November | Under direction of OIC (Dan Zhou) On-site for; - Station checks - Operational Sampling with ATP Data in PWQ excel Workbook Influent Water Grab @ 10:07 hrs. Grab FCl: 3.72 mg/L Analyzer FCl: 3.68 mg/L Treated Water (Effluent) Grabs @ 10:07 hrs. Grabs FCl: 2.28 mg/L TCl: 3.78 mg/L Analyzer FCl: 2.26 mg/L Temp: 10.2 degrees Celsius Equipment OOS: None Facility OK | Stouffville Well 1 & 2 | 2025-11-24
EAST | November | Under Direction of OIC (Dan Zhou) @ 09:59 placed well pumps 1/2 in Auto. | Stouffville Well 1 & 2 | 2025-11-14
EAST | November | Under Direction of OIC (Dan Zhou) On site for Hypo Receiving Tank 1; Start cm: 42.5 cm Stop cm: 193 Start V: 280 L Stop V: 1269 L Tank 2; Start cm: 40.9 cm Stop cm: 192.5 Start V: 269 L Stop V: 1266 L | Stouffville Well 1 & 2 | 2025-11-18
EAST | November | Under direction of OIC (Dan Zhou) On-site for; - Station checks Data in PWQ excel Workbook Influent Water Grab @ 10:55 hrs. Grab FCl: 3.54 mg/L Analyzer FCl: 3.53 mg/L Treated Water (Effluent) Grabs @ 10:55 hrs. Grabs FCl: 2.03 mg/L TCl: 2.60 mg/L Analyzer FCl: 2.02 mg/L Equipment OOS: None Facility OK | Stouffville Well 1 & 2 | 2025-11-14
EAST | November | Under direction of OIC (Dan Zhou) On-site for; - Station checks - Operational Sampling (Iron, FCl, TCl, Temp, Turbidity) Data in PWQ excel Workbook Influent Water Grab @ 11:21 hrs. Grab FCl: 3.66 mg/L Analyzer FCl: 3.66 mg/L Treated Water (Effluent) Grabs @ 11:21 hrs. Grabs FCl: 2.05 mg/L TCl: 2.56 mg/L Analyzer FCl: 2.08 mg/L Temp: 10.5 degrees Celsius Equipment OOS: None Facility OK | Stouffville Well 1 & 2 | 2025-11-17
EAST | November | Under direction of OIC (Dan Zhou) On site for: - Sodium Silicate system inspection and maintenance, injection quill cleaning and hot water flush - Chlorine analyzer Maintenance and cleaning (influent and Effluent AIT) - Turbidity analyzer maintenance/cleaning/calibration - Chemical system inspection and maintenance (chlorine) - Bore Hole inspection - JHSC Health and Safety Checks - Generator Test Run - Sodium Hypochlorite Receiving @ 08:29 hrs. Put Wells 1 and 2 in manual off for PM?s Started chlorine analyzer maintenance on AIT 1 and 2 Start Clean @ 08:37 hrs. Exited Clean @ 09:26 hrs. Effluent (Treated Water) AIT verification Grab @ 09:50 hrs. FCl: 1.20 mg/L Analyzer FCl: 1.21 mg/L Influent AIT verification Grab @ 09:43 hrs. FCl: 1.93 mg/L Analyzer FCl: 1.96 mg/L Turbidity Analyzer Maintenance and clean: Clean start @ 08:56 hrs. Exited Clean @ 09:13 hrs. @ 09:15 begin receiving sodium hypochlorite delivery Hypo Tank 1 Start cm: 47.38 cm Stop cm: 90.46 cm Hypo tank 2 Start cm: 46.72 cm Stop cm: 89.78 cm @ 10:00 hrs. Began Silicate System inspection/cleaning/flush, hypo system inspection and cleaning Generator Test Run: Start Fuel: 1034 L Stop Fuel: 1019 L Start Hours: 657.0 Stop Hours: 658.5 *Generator has been running for hours during load bank test, prior to generator test* Start Time: 12:51 hrs. Pre run checks; Battery Cell Levels: Ok Battery Terminals and Cables: Ok Oil Level: Ok Coolant Level: Ok Fluid Leaks: NO Coolant Recirculating pump: Ok Faulty Gauges: NO @ 12:51 hrs. Switched ATS to Test for generator power @ 12:55 hrs. Placed generator under facility load Well pump 2 in Manual ON @ 12: hrs. Checked generator operating parameters *under load* Operating Current: 55 Amps Operating Frequency: 62 Hz Operating Voltage: 570 Volts/ kilowatts Engine speed: 1750 RPM Water/coolant Temp: 148 f Oil Pressure: 26 psi Oil Temperature: 175 f @ 13:54 Put Well Pump 2 in manual off to switch ATS @ 14:01 hrs. Switched ATS to Normal @ 14:21 Generator finished cool down cycle. @ 14:30 Placed Well pump 1 in auto and well pump 2 in manual ON. Equipment OOS: None Facility OK | Stouffville Well 1 & 2 | 2025-11-11
EAST | November | Onsite for annual calibrations Informed ROC Used cal mode on scada during the work Instruments calibrated : AITs, NIT, LITs, FITs and PIT No adjustments made to AITs. As found = as left Influent A = 1.93 mg/L G = 1.96 mg/L Effluent A = 1.21 mg/L G = 1.20 mg/L Generator rebuild and testing during the work Operations on site All pending alarms cleared Informed ROC and left site | Stouffville Well 1 & 2 | 2025-11-11
EAST | November | Under direction of OIC (Dan Zhou) On-site for; - Station checks - Regulatory Sampling, Micro (W11368128) Data in PWQ excel Workbook @ 09:14 Put well 1 in manual ON, Well 2 ON since Nov 11, 12:56 hrs. Influent Water Grab @ 09:24 hrs. Grab FCl: 4.14 mg/L Analyzer FCl: 4.17 mg/L Treated Water (Effluent) Grabs @ 09:24 hrs. Grabs FCl: 2.14 mg/L TCl: 2.80 mg/L Analyzer FCl: 2.09 mg/L @ 09:36Placed Well pump 2 in Auto. Well pump 1 remains in manual ON. @ 09:56 placed well pump 2 in manual off, staying in single well operation. @ 09:42 rotated silicate pump duty and hypo pump duty Equipment OOS: None Facility OK | Stouffville Well 1 & 2 | 2025-11-12
EAST | November | On site for station check. Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 1.40mg/l FCL Analyzer: 1.46mg/l Effluent Free Cl2 grab residual: 1.37mg/l FCL Analyzer: 1.40mg/l Effluent Total Cl2 grab residual: 1.62mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Site currently undergoing Construction upgrades by Torbear. Equipment out of service: None. | Ballantrae Well 1 & 2 | 2025-11-07
EAST | November | On site to complete station check. Cleared outstanding alarms on site at 10:49. CT tank still OOS due to construction. Time: 10:50 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.89 1.98 Time: 10:53 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.56 1.62 Total: 1.83 Topped up day tank with hypo from bulk tank. Day tank Start: 71cm Stop: 78cm Bulk tank Start: 38.7cm Stop: 35.7cm Verified analyzers with grabs all ok. Checked station and equipment. | Ballantrae Well 1 & 2 | 2025-11-10
EAST | November | On site for station check. On site for operational iron sampling. Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 2.13mg/l FCL Analyzer: 2.04mg/l Effluent Free Cl2 grab residual: 1.66mg/l FCL Analyzer: 1.70mg/l Effluent Total Cl2 grab residual: 1.99mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Site currently undergoing Construction upgrades by Torbear. Equipment out of service: None. | Ballantrae Well 1 & 2 | 2025-11-03
EAST | November | On site for station check. Collected weekly micro samples (W11347652). Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 2.05mg/l FCL Analyzer: 1.97mg/l 08:45hrs: Effluent Free Cl2 grab residual: 1.66mg/l FCL Analyzer: 1.68mg/l Effluent Total Cl2 grab residual: 1.98mg/l Collected Well 1 Raw sample @ 10:10hrs: Changed Well Duties: W2 to D2, W1 to D1. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Site currently undergoing Construction upgrades by Torbear. Equipment out of service: None. | Ballantrae Well 1 & 2 | 2025-11-05
EAST | November | On site to close backflush valve and place wells back into auto. Contractors completed disinfection and flushing for the day. | Ballantrae Well 1 & 2 | 2025-11-26
EAST | November | On site to check station and equipment. Well 1 is in duty 1 and standby. Station readings and chlorine grabs are in PWQ sheet. Reviewed trends, station is under normal operation.? Lowered duty 1 start setpoint from 72% to 50% to deep cycle the tower.? Informed ROC. | Ballantrae Well 1 & 2 | 2025-11-24
EAST | November | Silicate top up 34.79cm to 46.0cm. | Ballantrae Well 1 & 2 | 2025-11-27
EAST | November | On site to provide water for Torbear Contractors for Flushing, Disinfection and Sampling. 09:05hrs: Both wells placed to manual off while contractors take water through backflushing valve and backflow preventer on Well #2. Notified ROC of | Ballantrae Well 1 & 2 | 2025-11-25
EAST | November | On site to place wells pumps in manual off to provide water through back flush port on Well 2 to contractors for pressure testing of Contact Tanks and yard piping. Placed wells back to auto after CT Tanks and yard piping is filled. | Ballantrae Well 1 & 2 | 2025-11-20
EAST | November | On site for station check. Collected weekly micro samples (W11386584). Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 1.93mg/l FCL Analyzer: 2.00mg/l 13:15hrs: Effluent Free Cl2 grab residual: 1.77mg/l FCL Analyzer: 1.71mg/l Effluent Total Cl2 grab residual: 1.85mg/l Collected Well 1 Raw sample @ 13:15hrs: Changed Well Duties: W2 to D2, W1 to D1. Placed both wells in manual - Torbear requesting water from backflow preventer to test CT tanks. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Site currently undergoing Construction upgrades by Torbear. Equipment out of service: None. | Ballantrae Well 1 & 2 | 2025-11-19
EAST | November | On site for station check. Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 1.48mg/l FCL Analyzer: 1.48mg/l Effluent Free Cl2 grab residual: 1.45mg/l FCL Analyzer: 1.43mg/l Effluent Total Cl2 grab residual: 1.62mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Site currently undergoing Construction upgrades by Torbear. Equipment out of service: None. | Ballantrae Well 1 & 2 | 2025-11-21
EAST | November | On site to close back flush valve. Placed wells back in auto. Contractors not requiring any more water. | Ballantrae Well 1 & 2 | 2025-11-27
EAST | November | Placed wells to manual off for contractor work. Require water from backflow preventer. | Ballantrae Well 1 & 2 | 2025-11-27
EAST | November | On site to close back flush valve and restart wells in auto. Contractors do not require any more water for the day. | Ballantrae Well 1 & 2 | 2025-11-25
EAST | November | On site for station check. Collected weekly micro samples (W11402370). Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 1.95mg/l FCL Analyzer: 2.00mg/l 08:25hrs: Effluent Free Cl2 grab residual: 1.76mg/l FCL Analyzer: 1.73mg/l Effluent Total Cl2 grab residual: 1.99mg/l Collected Well 1 Raw sample @ 08:25hrs. Collected Well 2 Raw sample @ 09:00hrs. Changed Well Duties: W2 to D1, W1 to D2. Wells placed to manual off after sampling and backlash valve opened on W2 for contractors to take water for disinfection and flushing of new Contact tanks and piping. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Site currently undergoing Construction upgrades by Torbear. Equipment out of service: None. | Ballantrae Well 1 & 2 | 2025-11-26
EAST | November | On site to place wells back to auto and close back flush valve after Torbear conducted water leak test on new coupling on CT tank connection. | Ballantrae Well 1 & 2 | 2025-11-19
EAST | November | On site for station check. Duty not active, tower Level @ 83%. Verified analyzer readings with grab residuals - no adjustments needed. Influent taken 9:57 Free Grab: 1.52 mg/L Analyzer: 1.52 mg/L Effluent taken at 9:59 Free Grab: 1.47 mg/L Analyzer: 1.45 mg/L Total Grab: 1.68 mg/L Chemical systems: Chlorinator 1 open 33%, DF= 50%. Booster P1 DP= 1020 kpa. Silicate P1 speed 41%, D P= 510 kpa. Visual inspection of chemical systems - all OK. Entered station readings in PWQ sheet. Reviewed trends, equipment ok. Station ok | Ballantrae Well 1 & 2 | 2025-11-28
EAST | November | On site to provide water through Well 2 backflushing line using back flow preventer for Contact Tank pressure test. | Ballantrae Well 1 & 2 | 2025-11-18
EAST | November | On site for station check. Duty not active, tower Level @ 90%. Visual check in and around station - Contractors on site. Verified analyzer readings with grab residuals - no adjustments needed. Influent taken at 10:40 Free Grab: 1.71 mg/L Analyzer: 1.68 mg/L Effluent taken at 10:44 Free Grab: 1.64 mg/L Analyzer: 1.58 mg/L Total Grab: 1.86 mg/L Visual inspection of chemical systems - all OK. Entered station readings in PWQ sheet. Turbidity fault alarm active upon arrival, cleaned vial and cleared alarm. Fault alarm and OOR alarm came back in a few mins later. Removed vial, wiped down vial and o-ring, returned to place and cleared alarms. Reviewed trends, equipment ok. Station ok | Ballantrae Well 1 & 2 | 2025-11-17
EAST | November | On site to place pumps into manual off for pressure testing of new Contact Tanks. Used Pump #2 waste valve to supply water to Contact Tanks using back flow preventer. Conducted station check on site. Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 1.46mg/l FCL Analyzer: 1.42mg/l Effluent Free Cl2 grab residual: 1.39mg/l FCL Analyzer: 1.35mg/l Effluent Total Cl2 grab residual: 1.59mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Site currently undergoing Construction upgrades by Torbear. Equipment out of service: None. | Ballantrae Well 1 & 2 | 2025-11-14
EAST | November | On site for station check. Collected weekly micro samples (W11368026). Collected RAW PH readings: Well 1: 7.88, Well 2: 7.77 Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 1.89mg/l FCL Analyzer: 1.95mg/l 10:05hrs: Effluent Free Cl2 grab residual: 1.71mg/l FCL Analyzer: 1.71mg/l Effluent Total Cl2 grab residual: 1.95mg/l Collected Well 2 Raw sample @ 10:35hrs: Changed Well Duties: W2 to D1, W1 to D2. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Site currently undergoing Construction upgrades by Torbear. Equipment out of service: None. | Ballantrae Well 1 & 2 | 2025-11-12
EAST | November | On site to place pumps into manual off for pressure testing of new Contact Tanks. Used Pump #2 waste valve to supply water to Contact Tanks using back flow preventer. On site for monthly maintenance: 09:30hrs: HACH CL17 Influent and Effluent Analyzer cleaning. Verified Analyzer after cleaning: Influent: 1.68mg/l, Analyzer: 1.71mg/l Effluent: 1.63mg/l, Analyzer: 1.65mg/l Turbidimeter maintenance and calibration completed Conducted Generator Test Run (10:50hrs): Diesel Generator Run Monthly Test: Start Runtime: 10:50hrs (Run hrs: 1001.5) Fuel Start: 83.6cm/829L Stop Runtime: 12:00hrs (Run hrs:1006.3 ) Fuel Stop: 82.0/811L Generator Performance Data recorded below: Battery Cell Levels: OK Battery Terminals/Cables: Ok Oil and Coolant: Ok Amps: 75amps Volts: 600 Hertz: 60 RPM: 1600 Oil Pressure: 55psi Water temp: 160 F No issues during generator run test. Ran Well 2 during run test. JHSC Inspection completed. 11:43hrs: Influent lolo lockout. Backflushed well using sodium thiosulfate pucks at new soak away pit chamber. Checked hypo pumps, noticed hypo pump #2 suction line popped off. Reconnected suction line and re-primed pump. Conducted Silicate and Hypo injection point inspection. Ran hot water through silicate system. | Ballantrae Well 1 & 2 | 2025-11-13
EAST | November | On site to top up silicate tank with silicate from Aurora wells 1-4. Start: 31.7cm/1933L Stop: 38.3cm/2332L No issues with top up. | Ballantrae Well 1 & 2 | 2025-11-13
EAST | November | On site for station check. Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 1.57mg/l FCL Analyzer: 1.50mg/l Effluent Free Cl2 grab residual: 1.56mg/l FCL Analyzer: 1.53mg/l Effluent Total Cl2 grab residual: 1.76mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Site currently undergoing Construction upgrades by Torbear. Equipment out of service: None. | Ballantrae Well 3 | 2025-11-07
EAST | November | On its to complete station check. No outstanding alarms on site. Contact Tank currently OOS due to construction. Time: 11:48 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.98 2.21 Time: 11:55 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.63 1.65 Total: 1.95 After multiple grabs were taken adjusted the influent free CL-17 analyzer from 2.21mg/l to 1.98mg/l at 11:51. At 11:56 shut down well to clean NTU unit due to fault, also at this time informed ROC of well shutting down and NTU being cleaned. NTU alarm cleared and vial is clean. Informed ROC and put well back on at 12:09. | Ballantrae Well 3 | 2025-11-10
EAST | November | Chris IliohanTyler Smith. In to put booster pump back online Joe Mazza put pump 2 in duty 1 no leaks noticed | Ballantrae Well 3 | 2025-11-03
EAST | November | On site for station check. Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 2.07mg/l FCL Analyzer: 2.12mg/l Effluent Free Cl2 grab residual: 1.67mg/l FCL Analyzer: 1.60mg/l Effluent Total Cl2 grab residual: 1.86mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Site currently undergoing Construction upgrades by Torbear. Equipment out of service: None. | Ballantrae Well 3 | 2025-11-03
EAST | November | On site for station check. Cylinder change with Patrick Fobert. Collected weekly micro samples (W11347652). Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 2.10mg/l FCL Analyzer: 2.15mg/l 08:45hrs: Effluent Free Cl2 grab residual: 1.61mg/l FCL Analyzer: 1.64mg/l Effluent Total Cl2 grab residual: 2.11mg/l Silicate P1 airlocked. Was able to fix, silicate dose should return to normal values next station check. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Site currently undergoing Construction upgrades by Torbear. Equipment out of service: None. | Ballantrae Well 3 | 2025-11-05
EAST | November | Chris Iliohan and Tyler Smith in to repair booster pump 2 broken fitting. Unit left in manual off to allow glue to dry | Ballantrae Well 3 | 2025-11-03
EAST | November | On site for station check. Collected weekly micro samples (W11402370). Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 2.10mg/l FCL Analyzer: 2.18mg/l 10:15hrs: Effluent Free Cl2 grab residual: 1.52mg/l FCL Analyzer: 1.51mg/l Effluent Total Cl2 grab residual: 1.82mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Site currently undergoing Construction upgrades by Torbear. Equipment out of service: None. | Ballantrae Well 3 | 2025-11-26
EAST | November | On site to top up silicate: 105 to 190L | Ballantrae Well 3 | 2025-11-27
EAST | November | Adjusted both Cl2 Chlorine Booster pump pressures from 250psi to 210psi. Adjustment made to lower pressure back to normal operating pressure as we are not pushing water through fire hydrant bypass anymore with elevated discharge pressures as before. Adjustment made to Silicate Pumps back to normal operating pressure ranges. | Ballantrae Well 3 | 2025-11-20
EAST | November | On site for station check. Collected weekly micro samples (W11386584). Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 2.10mg/l FCL Analyzer: 2.19mg/l 10:25hrs: Effluent Free Cl2 grab residual: 1.62mg/l FCL Analyzer: 1.69mg/l Effluent Total Cl2 grab residual: 2.07mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Site currently undergoing Construction upgrades by Torbear. Equipment out of service: None. | Ballantrae Well 3 | 2025-11-19
EAST | November | On site for station check. Duty not active, tower Level @ 85%. Verified analyzer readings with grab residuals - no adjustments needed. Influent taken 9:19 Free Grab: 1.42 mg/L Analyzer: 1.40 mg/L Effluent taken at 9:20 Free Grab: 1.31 mg/L Analyzer: 1.28 mg/L Total Grab: 1.52 mg/ Visual inspection of chemical systems - all OK. Entered station readings in PWQ sheet. Reviewed trends, equipment ok. Station ok | Ballantrae Well 3 | 2025-11-28
EAST | November | On site for station check. Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 1.48mg/l FCL Analyzer: 1.46mg/l Effluent Free Cl2 grab residual: 1.45mg/l FCL Analyzer: 1.44mg/l Effluent Total Cl2 grab residual: 1.70mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Ballantrae Well 3 | 2025-11-21
EAST | November | On site for station check. Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 1.48mg/l FCL Analyzer: 1.46mg/l Effluent Free Cl2 grab residual: 1.45mg/l FCL Analyzer: 1.44mg/l Effluent Total Cl2 grab residual: 1.70mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Ballantrae Well 3 | 2025-11-21
EAST | November | On site for monthly maintenance: - Exhaust fan inspections, well oil drip inspection. - Chemical system inspection. @10:45hrs: Placed well manual off to pipe in new effluent line from VC2 after both contact tanks to Effluent Analyzer. Turned off Effluent Analyzer to allow for new pipe in. Notified ROC of activities. Conducted Confined space entry at VC1 to close effluent line from Contact Tank 1 which will be decommissioned for new effluent line coming from both Contact Tanks. 11:45hrs: Tested Chlorine leak detector and inspected CL2 scrubber. No issues. 12:30hrs: New effluent line after both contact tanks now installed on Effluent Analyzer and Turbidimeter. Collected Cl2 grab residual on Effluent line to ensure it matches up with Effluent CL2 Analyzer: Cl2 grab residual: 1.40mg/l, Effluent Analyzer: 1.37mg/l. Enabled CT2 on SCADA. 12:48hrs: Placed well 3 back into auto and monitored well startup, effluent values and turbidity. No issues. Changed Cl2 cylinder. | Ballantrae Well 3 | 2025-11-25
EAST | November | On site to top up silicate with silicate from Aurora wells 1-4. Start: 115cm Stop: 200cm No issues with top up. | Ballantrae Well 3 | 2025-11-13
EAST | November | On site to check station and equipment. Well 3 is in duty 1 and standby. Station readings and chlorine grabs are in PWQ sheet. Reviewed trends, station is under normal operation.? Lowered duty 1 start setpoint from 72% to 50% to deep cycle the tower.? Informed ROC. | Ballantrae Well 3 | 2025-11-24
EAST | November | On site for station check. Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 2.38mg/l FCL Analyzer: 2.20mg/l Effluent Free Cl2 grab residual: 1.86mg/l FCL Analyzer: 1.87mg/l Effluent Total Cl2 grab residual: 2.17mg/l Adjusted HACH CL17 Influent Cl2 Analyzer from 2.20mg/l to 2.38mg/l based on multiple CL2 grab residuals. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Site currently undergoing Construction upgrades by Torbear. Equipment out of service: None. | Ballantrae Well 3 | 2025-11-14
EAST | November | On site for station check. Duty deactivated just after arriving on site, tower Level @ 92%. Visual check in and around station - Contractor on site and working in well house. Verified analyzer readings with grab residuals - no adjustments needed. Influent taken at 9:35 Free Grab: 1.74 mg/L Analyzer: 1.74 mg/L Effluent taken at 9:38 Free Grab: 1.72 mg/L Analyzer: 1.71 mg/L Total Grab: 2.13 mg/L Visual inspection of chemical systems - all OK. Entered station readings in PWQ sheet. Reviewed trends, No outstanding alarms. Station ok | Ballantrae Well 3 | 2025-11-17
EAST | November | On site for station check. Collected weekly micro samples (W11368026). 08:55hrs: Collected raw PH: 7.91 Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 2.30mg/l FCL Analyzer: 2.22mg/l 09:00hrs: Effluent Free Cl2 grab residual: 1.89mg/l FCL Analyzer: 1.87mg/l Effluent Total Cl2 grab residual: 2.30mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Site currently undergoing Construction upgrades by Torbear. Equipment out of service: None. | Ballantrae Well 3 | 2025-11-12
EAST | November | On site for monthly maintenance: 08:50hrs: HACH CL17 Influent and Effluent Analyzer cleaning. Verified Cl2 Analyzers after cleaning: Influent: 1.53mg/l, Analyzer: 1.51mg/l Effluent: 1.51mg/l, Analyzer: 1.48mg/l Tested low temperature alarm. No issues. Leaving site to receive CL2 cylinders at Zone 2 PS. On site for monthly maintenance: 08:50hrs: HACH CL17 Influent and Effluent Analyzer cleaning. Verified Analyzer after cleaning: Influent: 1.53mg/l, Analyzer: 1.51mg/l Effluent: 1.51mg/l, Analyzer: 1.48mg/l Turbidimeter maintenance and calibration completed. JHSC Inspection completed. Conducted Generator Test Run (12:20hrs): Diesel Generator Run Monthly Test: Start Runtime: 12:20hrs (Run hrs: 405hrs, 50min) Fuel Start: 91.68/85.52cm Stop Runtime: 13:24hrs (Run hrs: 406hrs, 52min) Fuel Stop: 91.1/84.8cm Generator Performance Data recorded below: Battery Cell Levels: OK Battery Terminals/Cables: Ok Oil and Coolant: Ok Amps: 17 Volts: 600 Hertz:60 RPM: 1800 Oil Pressure: 60psi Water temp: 171 F No issues during generator run test. Conducted Silicate injection point inspection. Ran hot water through silicate system. Silicate Pumps inspection. Swapped out Silicate P1 diaphragm due to degradation. Reprimed pumps. No issues. | Ballantrae Well 3 | 2025-11-18
EAST | November | Under direction of OIC (Stephen Baidy) On-site for; - Station Checks Data in PWQ excel Workbook (Influent) Grab @ 08:27 hrs. FCl: 2.06 mg/L Analyzer: 2.12 mg/L Effluent (Treated Water) Grabs @ 08:27 hrs. FCl: 1.84 mg/L TCL: 2.02 mg/L Analyzer: 1.85 mg/L Equipment OOS: none Facility OK | Stouffville Reservoir and Wells 5 & 6 | 2025-11-07
EAST | November | Attending site for turbidimeter water leak (W11424836). Reseated sample vial and removed standing water from turbidimeter body and replaced desiccant cartridge. Readings returned to normal and the internal humidity sensor reading is dropping as expected. High lift pumps were turned off during the turbidimeter failure. ROC was notified once turbidimeter was returned to service. | Stouffville Reservoir and Wells 5 & 6 | 2025-11-06
EAST | November | On site to; Change chlorine cylinders with (OIC) Jack Palmer @ 09:21 hrs. Informed ROC of Cylinder change. Performed Chlorine system inspection with jack. Changed chlorine cylinder in bank 2. | Stouffville Reservoir and Wells 5 & 6 | 2025-11-07
EAST | November | Under direction of OIC (Dan Zhou) On-site for; - Station Checks - Switch influent sample line and corresponding flow path to reservoir - Switch high lift duty Data in PWQ excel Workbook (Influent) Grab @ 13:38 hrs. FCl: 1.95 mg/L Analyzer: 1.99 mg/L Effluent (Treated Water) Grabs @ 13:47 hrs. FCl: 1.84 mg/L TCL: 2.00 mg/L Analyzer: 1.86 mg/L @13:57 switched high lift duty from pump 1 duty 2 to pump 1 duty 1 @ 13:59 Switched influent sample line and corresponding flow path to reservoir Equipment OOS: none Facility OK | Stouffville Reservoir and Wells 5 & 6 | 2025-11-10
EAST | November | Under direction of OIC (Stephen Baidy) On-site for; - Preventative Maintenance; UV building Chlorine Analyzer Maintenance and Verification, High lift Building Chlorine Analyzer Maintenance and Verification, Turbidity Analyzer maintenance and verification - JHSC Health and Safety Checks - Monthly Generator Test Run - Chlorine Emergency Repair kit Inspection - Comprehensive housekeeping UV Building Chlorine Analyzer Start Clean @ 09:51 hrs. Stop Clean @ 11:39 hrs. Influent Water Grab @ 11:10 hrs Grab FCl: 1.97 mg/L Analyzer FCl: 2.00 mg/L @09:57 put high lift pumps in manual off for AIT maintenance and cal. And turbidity meter maintenance and cal. High Lift Building Chlorine Analyzer Clean Start @ 09:58 hrs. Exit/Stop Clean @ 10:36 hrs. High lift Building AIT Maintenance Start Clean @ 10:00 Exit/Stop Clean @ 10:44 hrs. Treated Water (Effluent) Grabs @ 11:20 AM Grabs FCl: 1.92 mg/L Analyzer FCl: 1.91 mg/L Turbidity Analyzer Maintenance and calibration Start @ 10:04 hrs. Stop @ 10:40 hrs. ? Upon restarting Turbidity meter, water was leaking from unit around process head. Removed process head, o-ring was not sitting properly and allowed a leak inside the unit. Called Instrumentation and spoke with team lead Eric to create work order for today. High lifts will be off until turbidity meter can be placed back in service. Generator Test Run: Start hours: 9.85 Start time: 13:08 hrs. Stop Hours: 10.95 Stop Time: 14:11 hrs. (excluding cool down time) Run Time hours: 1.1 Start Fuel: 3199 L Stop Fuel: 3183 L Pre run checks; Battery Cell Levels: Ok Battery Terminals and Cables: Ok Oil Level: Ok Coolant Level: Ok Fluid Leaks: NO Coolant Recirculating pump: Ok Faulty Gauges: NO *under facility load (no pumps)* Operating Current: 45 Amps Operating Frequency: 60 Hz Operating Voltage: 594.79 Volts/ kilowatts Engine speed: 1799.5 RPM Water/coolant Temp: 170.6 f Oil Pressure: 38.29 psi Oil Temperature: not on screen, cannot locate oil temp monitoring on OIT screen @ 14:00 Eric from instrumentation confirmed functionality of turbidity analyzer. @ 14:19 placed high lift pumps back in auto, high lift 1 running. Equipment OOS: none Facility OK | Stouffville Reservoir and Wells 5 & 6 | 2025-11-06
EAST | November | Under direction of OIC (Stephen Baidy) On-site for; - Station Checks - Quarterly pH monitoring - Switch Influent Sample line and corresponding flow path to reservoir - Switch High lift Duty Data in PWQ excel Workbook Rotameter Reading Higher than normal (25.5 vs normal 21.5). After investigation with grabs at UV building influent AIT adjusted. @ 11:25 hrs.Adjusted Dosage factor as proposed was higher than Active. Cl2 residual seems to be slowly leveling down to proposed dosage set-point. (Influent) Grab @ 11:10 hrs. FCl: 2.32 mg/L Analyzer: 2.23 mg/L Grab @ 11:10 hrs. FCl: 2.32 mg/L Analyzer: 2.24 mg/L Grab @ 11:10 hrs. FCl: 2.38 mg/L Analyzer: 2.25 mg/L Average FCl Grab: 2.34 mg/L @ adjusted analyzer to 2.34 mg/L @ 11:10 hrs. pH: 7.56 (Effluent) Treated Water Grabs @ 14:21 hrs. Grabs FCl: 2.28 mg/L TCl: 2.68 mg/L Analyzer FCl: 2.30 mg/L @ 12:00 Changed Influent sample line and corresponding flow path to reservoir. @ 12:06 changed high lift duty from pump 1 duty 1 to pump 2 duty 1. Equipment OOS: none Facility OK | Stouffville Reservoir and Wells 5 & 6 | 2025-11-03
EAST | November | On site to repair copper lines | Stouffville Reservoir and Wells 5 & 6 | 2025-11-26
EAST | November | Restarted the Operator Interface Terminal due to Windows updates. Notified the Remote Operations Center and the OIC. Wells were off. | Stouffville Reservoir and Wells 5 & 6 | 2025-11-03
EAST | November | On site to place station back to operation. Lee performed repair on the supply line to chlorine booster pumps. Performed chlorine grab to verify analyzer reading: 14:36 chlorine grab free = 1.01 mg/l, analyzer free = 0.94 mg/l.? Ran both chlorine booster pumps and chlorinators in local. Chlorination system is functioning normally. Increased sample pump speed from 60 rpm to 80 rpm.? Manually dose chlorine into the reservoir until residual recovered. Activated well duty.? Chlorine #1 is running in duty 1. ? Placed high lift pumps back to auto.? Sample pump 2 is running in duty 1. | Stouffville Reservoir and Wells 5 & 6 | 2025-11-25
EAST | November | ROC informed influent chloine lolo. Sample pump 1 was running in duty 1. Switched sample pump to run P2 and placed P1 man/off. | Stouffville Reservoir and Wells 5 & 6 | 2025-11-25
EAST | November | On site to investigate Influent LOLO alarm; Arrive on site to see influent AIT at 0.01 mg/L Grab @ 10:00 hrs. FCl: 0.35 mg/L ON SCADA Well shut down @ 07:35 while Influent dropped @ 07:40 after well shut down. Checking chlorine room, noticed a leak in copper line feeding eyewash station and booster pumps (closed valve and informed Team lead Dan Zhou) Isolated the line by shutting valve leading to leak. Well can be ran in emergency. Leak needs fixing before properly operating the system. Changed chlorine cylinder with OIC Jack Palmer. Well remains out of service. | Stouffville Reservoir and Wells 5 & 6 | 2025-11-25
EAST | November | Under direction of OIC (Dan Zhou) On-site for; - Station Checks - Switch Influent Sample Line and Corresponding Flow Path to Reservoir Data in PWQ excel Workbook (Influent) Grabs @ 14:15 hrs. FCl: 2.08 mg/L Analyzer: 2.11 mg/L Effluent (Treated Water) Grabs @ 14:15 hrs. FCl: 1.95 mg/L TCL: 2.07 mg/L Analyzer: 1.96 mg/L @ 14:36 switched influent sample lines and corresponding flow path to reservoir from west to east Equipment OOS: none Facility OK | Stouffville Reservoir and Wells 5 & 6 | 2025-11-24
EAST | November | Under Direction of OIC (Dan Zhou) On site for; - Station checks - Regulatory Sampling, micro (1111386678) - DWSP Sampling (W11455601) Data in PWQ workbook Regulatory samples taken @ 14:00 hrs. Grabs @ 14:00 hrs. FCl: 1.91 mg/L TCl: 2.10mg/L Analyzer: FCl: 1.94 mg/L Equipment out of service: none Station Ok | Stouffville Reservoir and Wells 5 & 6 | 2025-11-19
EAST | November | Changed chlorine cylinder on the left side. | Stouffville Reservoir and Wells 5 & 6 | 2025-11-19
EAST | November | On Site for; - Chlorine system inspection - Chlorine leak detection test - Chlorine scrubber check @ 13:03 called ROC to inform about PM?s @13:03 shut down well pump 6 for on site work with chlorine system @ 14:24 performed chlorine leak detection test and scrubber functionality. OK ? Worked with OIC Joe Mazza | Stouffville Reservoir and Wells 5 & 6 | 2025-11-20
EAST | November | Under direction of OIC (Dan Zhou) On-site for; - Station Checks Data in PWQ excel Workbook (Influent) Grabs @ 13:46 hrs. FCl: 1.97 mg/L Analyzer: 1.97 mg/L Effluent (Treated Water) Grabs @ 13:46 hrs. FCl: 1.96 mg/L TCL: 2.10 mg/L Analyzer: 2.01 mg/L * Noticed leak around inlet to pilot line (ball valve and elbow)on high lift pump 2. Created work order (W11475747) and informed team lead Dan Zhou. Equipment OOS: none Facility OK | Stouffville Reservoir and Wells 5 & 6 | 2025-11-28
EAST | November | Check leak chlorine room entrance Small leak taped up temporary until can get parts and replace | Stouffville Reservoir and Wells 5 & 6 | 2025-11-25
EAST | November | Onsite for annual calibrations Informed ROC. Asked Joe mazza to place high lifts and wells in manual off Used cal mode on Scada during calibration Instruments calibrated: Reservoir side: AIT, Gas detector, chlorinator, weigh scale, Well 5&6 Side: LITs and FITs AIT: G = 1.94mg/L A = 1.95mg/L No adjustments made Cleared associated alarms Informed ROC. Asked Joe mazza to place high lifts and wells back in auto Armed the building and Left site. | Stouffville Reservoir and Wells 5 & 6 | 2025-11-13
EAST | November | Under direction of OIC (Dan Zhou) On-site for; - Station Checks - Regulatory Sampling, Micro (W11368128) Data in PWQ excel Workbook (Influent) Grab @ 11:10 hrs. FCl: 2.08 mg/L Analyzer FCl: 2.10 mg/L Effluent (Treated Water) Grabs @ 11:10 hrs. FCl: 1.93 mg/L TCL: 2.07 mg/L Analyzer FCl: 1.91 mg/L Equipment OOS: none Facility OK | Stouffville Reservoir and Wells 5 & 6 | 2025-11-12
EAST | November | Onsite for annual calibrations Informed ROC. Asked ROC to place high lifts in manual off Used cal mode on Scada during calibration Instruments calibrated: AIT, NIT, PIT, LIT and FIT AIT: G = 1.93mg/L A = 1.91mg/L No adjustments made Cleared associated alarms Informed ROC. Asked to place high lifts back in auto Left site Contractors busy working on generator | Stouffville Reservoir and Wells 5 & 6 | 2025-11-12
EAST | November | Under direction of OIC (Dan Zhou) On-site for; - Station Checks - Switch Influent Sample Line and Corresponding Flow Path to Reservoir Data in PWQ excel Workbook (Influent) Grabs @ 13:00 hrs. FCl: 2.08 mg/L, 2.06 mg/L, 2.06 mg/L Analyzer: 2.16 mg/L *Adjusted Influent AIT to 2.07 mg/L Effluent (Treated Water) Grabs @ 13:20 hrs. FCl: 1.89 mg/L, TCL: 2.07 mg/L Analyzer: 1.88 mg/L @ 13:34 switched influent sample lines and corresponding flow path to reservoir Equipment OOS: none Facility OK | Stouffville Reservoir and Wells 5 & 6 | 2025-11-17
EAST | November | Under direction of OIC (Stephen Baidy) On Site for; - Station Checks Grabs @ 08:43 hrs. FCl: 1.84 mg/L TCl: 1.99 mg/L Analyzer: FCl: 1.85 mg/L Turb spike due to running air compressor. Equipment out of Service: None Facility OK | Stouffville Highway 48 Booster Pumping Station | 2025-11-07
EAST | November | Under Direction of OIC (Stephen Baidy) On site for Preventative maintenance; - Chlorine analyzer maintenance and verification - Comprehensive Housekeeping Chlorine Analyzer Maintenance and verification Start Clean @ 14:34 Exit/Stop Clean @ 14:54 Grab @ 15:06 FCl:1.87 mg/L Analyzer FCl: 1.82 Turbidity spike due to adjusting flow through bubble trap Equipment OOS: None Station OK | Stouffville Highway 48 Booster Pumping Station | 2025-11-06
EAST | November | Under direction of OIC (Dan Zhou) On Site for; - Station Checks Grabs @ 14:26 hrs. FCl: 1.79 mg/L TCl: 1.78 mg/L Analyzer: FCl: 1.82 mg/L Turbidity spike due to running air compressor. Equipment out of Service: None Facility OK | Stouffville Highway 48 Booster Pumping Station | 2025-11-10
EAST | November | Under direction of OIC (Stephen Baidy) On Site for; - Station Checks Grabs @ 12:30 hrs. FCl: 2.07 mg/L TCl: 2.20 mg/L Analyzer: FCl: 2.03 mg/L Turb spike due to running air compressor. Equipment out of Service: None Facility OK | Stouffville Highway 48 Booster Pumping Station | 2025-11-03
EAST | November | Under direction of OIC (Dan Zhou) On Site for; - Station Checks Data in PWQ Workbook Grabs @ 14:41 FCl: 1.82 mg/L TCL: 1.99 mg/L Analyzer: FCl: 1.80 mg/L Turbidity spike due running air compressor. Equipment out of Service: None Facility OK | Stouffville Highway 48 Booster Pumping Station | 2025-11-28
EAST | November | Under direction of OIC (Dan Zhou) On Site for; - Station Checks Data in PWQ Workbook Grabs @ 14:37 FCl: 1.95 mg/L TCL: 2.12 mg/L Analyzer: FCl: 1.95 mg/L Turbidity spike due running air compressor. Equipment out of Service: None Facility OK | Stouffville Highway 48 Booster Pumping Station | 2025-11-24
EAST | November | Informed ROC. Performed annual calibration and put instruments in Cal mode while doing the tasks. Devices done were AIT, NIT, FIT and PIT. Operator assisted on calibrating the PIT by manually running the pump. Took grabs at the sample line. free chlorine AIT1= 1.89 mg/l Grab= 1.89 mg/l All alarms were cleared after the job. No other issues encountered. | Stouffville Highway 48 Booster Pumping Station | 2025-11-12
EAST | November | Under direction of OIC (Dan Zhou) On Site for; - Station Checks Data in PWQ Workbook Grabs @ 14:37 FCl: 1.74 mg/L TCL: 1.90 mg/L Analyzer: FCl: 1.73 mg/L Changed AIT Reagents. Turbidity spike due running air compressor. Equipment out of Service: None Facility OK | Stouffville Highway 48 Booster Pumping Station | 2025-11-17
EAST | November | Under direction of OIC (Dan Zhou) On Site for; - Operational assistance to instrumentation calibrate (PIT) @ 11:54 put pumps in manual set to zero % pump speed, pump 1 on at zero showing 2 %, PIT in Cal mode @ 12:02 hrs. Discharge PIT back on normal pout of cal mode, BP 1 and 2 back in auto. Turbidity spike due to surge tanks usage. Equipment out of Service: None Facility OK | Stouffville Highway 48 Booster Pumping Station | 2025-11-12
WEST | November | Onsite for station check Site secure No power Site offline No issues observed | King City Wells 3 & 4 | 2025-11-07
WEST | November | Station check (no issues found) Site secure No power Off line | King City Wells 3 & 4 | 2025-11-27
WEST | November | Onsite for station check Site secure No power Site offline No issues observed | King City Wells 3 & 4 | 2025-11-21
WEST | November | Onsite to complete station check and to collect weekly micro sample W11348174 Ran wells 3&4 in local to waste Checked treated residuals mg/L @1313 Total analyzer 2.05 grab 2.08 Free analyzer 0.02 grab 0.02 | Kleinburg Wells 3 and 4 | 2025-11-05
WEST | November | Onsite to complete work orders Generator run Start 411.8 hrs Fuel 30.2 cm / 1561 L Stop 413.4 hrs Fuel 29.3 cm / 1514L Completed jhsc no issues observed Completed monthly ntu calibration with 20 ntu vial Tested chlorine leak detection, no issues Completed monthly cl2 analyzer maintenance Reagents, electrolyte and grit ok Grabs Total analyzer 2.45 grab 2.05 Free analyzer 0.03 grab 0.06 Noticed bubbles in total analyzer adjusted afterwards Exercised manual valves Tested ammonia system | Kleinburg Wells 3 and 4 | 2025-11-06
WEST | November | Onsite for station check and to collect weekly micro sample W11402594 Ran wells 3&4 in local to waste Checked treated residuals mg/l @1235 Total analyzer 1.85 grab 1.90 Free analyzer 0.01 grab 0.04 | Kleinburg Wells 3 and 4 | 2025-11-26
WEST | November | Onsite for station check and to collect weekly micro sample W11386992 Ran wells 3&4 in local to waste Checked treated residuals mg/l @1303 Total analyzer 1.84 grab 1.89 Free analyzer 0.02 grab 0.04 | Kleinburg Wells 3 and 4 | 2025-11-19
WEST | November | Onsite for station check and to collect weekly micro sample W11368250 Ran wells 3&4 in local to waste Checked treated residuals mg/L @1231 Tcl analyzer 1.92 grab 2.01 Fcl analyzer 0.02 grab 0.04 Reagents ok | Kleinburg Wells 3 and 4 | 2025-11-12
WEST | November | increased residual target 3.60 to 3.70 mg/L | Schomberg Elevated Tank | 2025-11-07
WEST | November | filled hypo tank 0.20 to 0.41 m | Schomberg Elevated Tank | 2025-11-06
WEST | November | -on site to complete station check and to collect sample for in house lab analysis - tower filling at 32.1 l/s, level = 18% -hypo pump #1 running at 5%, DF 115%, 352 ml/hr, 72 psi - reviewed trends - CL17 reagents ok - checked equipment -recorded readings in PWQ sheet - no issues found -verified analyzers: 09:34 - common inlet/outlet TCL analyzer = 3.22 mg/L 09:34 - common inlet/ outlet grab: FCL = 0.07 mg/L TCL = 3.20 mg/L Mono = 2.79 mg/L 09:41 - post injection TCL analyzer = 3.57 mg/L 09:41 - post injection grab: TCL = 3.66 mg/L | Schomberg Elevated Tank | 2025-11-07
WEST | November | -on site to complete station check and to collect sample for in house lab analysis - tower draining at 25.1 l/s, level = 41% - reviewed trends - CL17 reagents ok - checked equipment -recorded readings in PWQ sheet - no issues found -verified analyzers: 11:09 - common inlet/outlet TCL analyzer = 3.59 mg/L 11:09 - common inlet/ outlet grab: FCL = 0.00 mg/L TCL = 3.60 mg/L Mono = 3.20 mg/L 11:14 - post injection TCL analyzer = 4.67 mg/L 11:14 - post injection grab: TCL = 4.68 mg/L -decreased residual target from 3.70 to 3.65 mg/L | Schomberg Elevated Tank | 2025-11-10
WEST | November | Responding to Hypo P1, P2 fail to start alarms. Hypo pumps have power, run locally. Test run in manual: pumps fail to start when pump speed at 0%, when placed at manual 20% pumps run normally. Activate duty to monitor startup. Appears that system residuals / post injection residuals are too high to run hypo pumps. Pumps are interlocking when pre/post are above Dose Start SP, and possibly when hypo pumps try to dose at 0% speed or less (due inlet residual being close to target SP). Reset alarms once post-inj residual below 3.50mg/L. Hypo P2 running at 8%. Will inform ROC to place pumps manual off if hypo pumps continue to interlock under similar circumstances. System residuals are typically 2.30mg/L incoming, at 3.30mg/L Rechlor may not be necessary with nuisance alarms. | Schomberg Elevated Tank | 2025-11-10
WEST | November | On site for electrical and heat trace inspection. During inspection it was noticed that the exhaust fan controls for the chemical hut were broken. Created follow up work order. | Schomberg Elevated Tank | 2025-11-10
WEST | November | -on site to complete station check and to collect samples - tower draining at 25.0 l/s, level = 37 % - reviewed trends - CL17 reagents ok - checked equipment -recorded readings in PWQ sheet - no issues found -verified analyzers: 10:54 - common inlet/outlet TCL analyzer = 3.45 mg/L 10:54 - common inlet/ outlet grab: FCL = 0.03 mg/L TCL = 3.54 mg/L Mono = 3.19 mg/L 11:05 - collected weekly micro sample - W/O # W11347882 11:07 - post injection TCL analyzer = 4.30 mg/L 11:07 - post injection grab: TCL = 4.38 mg/L -activated duty to check rechlor operation 11:26 - common TCL analyzer = 3.43 mg/l Grab = 3.58/3.66/3.60 mg/L 11:35 - adjusted common TCL analyzer to 3.61 mg/L based on average of 3 grabs 11:52 - post injection analyzer = 3.41 mg/L grab = 3.73/3.79/3.78 mg/L 11:54 - adjusted post injection analyzer to 3.77 mg/L based on average of 3 grabs 12:17 - post injection analyzer = 3.57 mg/L grabs = 3.28/3.36/3.26 mg/L 12:18 - adjusted post injection analyzer to 3.30 mg/L based on average of 3 grabs -will monitor | Schomberg Elevated Tank | 2025-11-05
WEST | November | -on site to complete station check and to collect sample for in house lab analysis - tower draining at 50.5 l/s, level = 38% - reviewed trends - CL17 reagents ok - checked equipment -recorded readings in PWQ sheet - no issues found -verified analyzers: 09:59 - common inlet/outlet TCL analyzer = 3.53 mg/L 09:59 - common inlet/ outlet grab: FCL = 0.00 mg/L TCL = 3.58 mg/L Mono = 3.42 mg/L 10:05 - post injection TCL analyzer = 3.18 mg/L 10:05 - post injection grab: TCL = 3.24 mg/L | Schomberg Elevated Tank | 2025-11-03
WEST | November | Decreased target residual 3.70 to 3.60 mg/L | Schomberg Elevated Tank | 2025-11-06
WEST | November | -on site to complete station check and to collect sample for in house lab analysis - tower draining at 24.2 l/s, level = 43% - reviewed trends - replaced post injection CL17 reagents - checked equipment - recorded readings in PWQ sheet - no issues found -verified analyzers: 11:28 - common inlet/outlet TCL analyzer = 3.56 mg/L 11:28 - common inlet/ outlet grab: FCL = 0.00 mg/L TCL = 3.56 mg/L Mono = 3.02 mg/L 11:38 - post injection TCL analyzer = 4.40 mg/L 11:38 - post injection grab: TCL = 4.48 mg/L | Schomberg Elevated Tank | 2025-11-20
WEST | November | -on site to complete station check and to collect sample for in house lab analysis - tower draining at 27.4 l/s, level = 39% - reviewed trends - CL17 reagents ok - checked equipment -recorded readings in PWQ sheet - no issues found -verified analyzers: 10:16 - common inlet/outlet TCL analyzer = 3.55 mg/L 10:16 - common inlet/ outlet grab: FCL = 0.00 mg/L TCL = 3.56 mg/L Mono = 3.10 mg/L 10:23 - post injection TCL analyzer = 4.54 mg/L 10:23 - post injection grab: TCL = 4.60 mg/L | Schomberg Elevated Tank | 2025-11-27
WEST | November | -on site to complete station check and to collect sample for in house lab analysis - tower draining at 24.0 l/s, level = 35% - reviewed trends - CL17 reagents ok - checked equipment -recorded readings in PWQ sheet - no issues found -verified analyzers: 09:44 - common inlet/outlet TCL analyzer = 3.43 mg/L 09:44 - common inlet/ outlet grab: FCL = 0.00 mg/L TCL = 3.38 mg/L Mono = 2.89 mg/L 09:54 - post injection TCL analyzer = 4.13 mg/L 09:54 - post injection grab: TCL = 4.04 mg/L | Schomberg Elevated Tank | 2025-11-24
WEST | November | -on site to complete station check and to collect samples -filled hypo tank 78 to 137 L - tower draining at 25.0 l/s, level = 34 % - reviewed trends - CL17 reagents ok - checked equipment -recorded readings in PWQ sheet -no issues found -verified analyzers: 10:24 - common inlet/outlet TCL analyzer = 3.53 mg/L 10:24 - common inlet/ outlet grab: FCL = 0.06 mg/L TCL = 3.46 mg/L Mono = 2.93 mg/L 10:27 - collected weekly micro sample - W/O # W11402542 10:38 - post injection TCL analyzer = 4.74 mg/L 10:38 - post injection grab: TCL = 4.64 mg/L | Schomberg Elevated Tank | 2025-11-26
WEST | November | Changed hypo lines out Primed lines | Schomberg Elevated Tank | 2025-11-25
WEST | November | Increased chlorine set point 3.6 to 3.7 mg/L | Schomberg Elevated Tank | 2025-11-25
WEST | November | -on site to complete station check and to collect samples - tower draining at 27.2 l/s, level = 45 % - reviewed trends - CL17 reagents ok - checked equipment -recorded readings in PWQ sheet - no issues found -verified analyzers: 11:02 - common inlet/outlet TCL analyzer = 3.57 mg/L 11:02 - common inlet/ outlet grab: FCL = 0.01 mg/L TCL = 3.52 mg/L Mono = 3.03 mg/L 11:09 - collected weekly micro sample - W/O # W11386814 11:13 - post injection TCL analyzer = 4.20 mg/L 11:13 - post injection grab: TCL = 4.28 mg/L | Schomberg Elevated Tank | 2025-11-19
WEST | November | Station Check (no issues found) Input data to PWQ (without SL1000) 11:55 Verified CL17s (mg/L) Common Free: Grab 0.12 Total: Grab 3.26, A 3.19 (reagent change) Post Total: Grab 4.30, A 4.21 12:20 #112368198 weekly samples | Schomberg Elevated Tank | 2025-11-11
WEST | November | -on site to complete work orders: -completed Low Temperature Alarm, Test -completed Inlet/Outlet Heat Trace System, Inspection -completed Outlet Heat Trace System, Inspection -completed Gasoline Generator, Test Run -completed JHSC Health and Safety Inspection -completed Sodium Hypochlorite Pump, Maintenance -both pumps max flow = 133 ml/min -found leaking fitting on pump #2 discharge line - replaced -found hypo containment flood switch corroded and not triggering alarm, created follow up work order for replacement -completed CL-17sc Analyzer, Maintenance: -tower filling, turned hypo system off 10:21 - 10:38 - analyzers in clean mode -cleaned cells, flushed sample lines -verified analyzers after maintenance: 10:42 - common inlet/outlet TCL analyzer = 3.26 mg/L 10:42 - common inlet/ outlet grab: TCL = 3.24 mg/L 10:56 - post injection TCL analyzer = 3.65 mg/L 10:56 - post injection grab: TCL = 3.70 mg/L -completed Manual Valve, Exercise -no outstanding issues, site back to normal operation | Schomberg Elevated Tank | 2025-11-18
WEST | November | -on site to complete station check and to collect sample for in house lab analysis - tower draining at 25.3 l/s, level = 48% - reviewed trends - CL17 reagents ok - checked equipment -recorded readings in PWQ sheet - no issues found -filled hypo tank 70 to 116 L -verified analyzers: 11:35 - common inlet/outlet TCL analyzer = 3.50 mg/L 11:35 - common inlet/ outlet grab: FCL = 0.00 mg/L TCL = 3.44 mg/L Mono = 2.99 mg/L 11:40 - post injection TCL analyzer = 3.45 mg/L 11:40 - post injection grab: TCL = 3.56 mg/L | Schomberg Elevated Tank | 2025-11-17
WEST | November | Decreased target 3.65 to 3.60 mg/L | Schomberg Elevated Tank | 2025-11-14
WEST | November | -on site to complete station check and to collect sample for in house lab analysis - tower draining at 24.4 l/s, level = 29% - reviewed trends - CL17 reagents ok - checked equipment -recorded readings in PWQ sheet - no issues found -verified analyzers: 10:09 - common inlet/outlet TCL analyzer = 3.57 mg/L 10:09 - common inlet/ outlet grab: FCL = 0.00 mg/L TCL = 3.54 mg/L Mono = 2.95 mg/L 10:16 - post injection TCL analyzer = 4.40 mg/L 10:16 - post injection grab: TCL = 4.36 mg/L | Schomberg Elevated Tank | 2025-11-14
EAST | November | On site for monthly work orders Wash water suspended solids fault and wash water chlorine high alarms came in @12:08, along with wash water pump lockouts. No water was going back to the lake at the time of the alarms. Found that the wash water chlorine analyzer was overflowing the sample bowl, reduced flow and cleaned analyzer. Also cleaned TSS probe. No further issues. Repaired leak on hypo line at the PSW injection points, replaced two leaking fittings. Reprimed lines, and tested for leaks all good. | Georgina Water Treatment Plant | 2025-11-06
EAST | November | Reviewed MIT and daily filter performance on all trains - all passed. Deactivated duty for Sutton at 10:10 Deactivated duty for Keswick at 10:58 This is to complete UV work order. W11392348 UV System Maintenance. Put UV 1 and 2 in manual at 11:04. Informed ROC of work orders being completed Completed clear well and contact tank analyzer maintenance from 11:25-11:52. Verified analyzers Time: 11:30 CT1 Grab (mg/l) Analyzer (mg/l) Free: 2.86 2.82 Time: 11:35 CW1 Grab (mg/l) Analyzer (mg/l) Free: 2.62. 3.76-2.62 zeroed analyzer at 11:40 and made adjustments after multiple grabs at 11:44 from 2.79mg/l to 2.62mg/l. Time: 11:50 CT2 Grab (mg/l) Analyzer (mg/l) Free: 1.98 1.99 Time: 11:32 CW2 Grab (mg/l) Analyzer (mg/l) Free: 1.78 1.85 At 11:55 completed outfall to lake and Suspended Solids analyzer cleaning. Time: 12:05 Out to Lake Grab (mg/l) Analyzer (mg/l) Free: 0.02. 0.00-0.02 zeroed analyzer at 12:06 and after zeroing took multiple grabs and adjusted analyzer at 12:08 from 0.00mg/l to 0.02mg/l. UV1 completed calibration and is back in auto. UV2 is manual off for the night due to bulb having low UVT intensity. Any changes in trends and alarms created are due to work orders being completed. Plant back in operation at 14:45. | Georgina Water Treatment Plant | 2025-11-06
EAST | November | To review trends and record trains MITs - To review trends and record filter daily performance, - To review permeate UV trends, no issues - Wet well mussel plate inspection completed Operations and Adjustments: Drained and replaced new Lamp and sleeve on UV bank 2 -1-1, pilled in water in the leak detector area, placed UV off and turned power off from the UV panel, to allow area to dry. Deactivated auto duty rotate for UV system - ROC/OIC on call notified Draining UV header for maintenance has caused low flow to Permeate turbidity analyzers causing them to fault. Filled header back up and cleared alarm on analyzers no issues. Low Lift Station: Chlorine analyzers: Both existing and newly installed chlorine analyzer and pH probes are running concurrently. 12:27 hrs: prepared LL station for shut down to reconnect power to LL pump4 as requested by contractor onsite. Notified ROC Equipment OOS: - Sludge pump3 emergency stop alarm - GAC3 FCV deviation - UV system bank 2 | Georgina Water Treatment Plant | 2025-11-07
EAST | November | On site for station check, equipment verifications and lab analysis Duty is not active - Tower level Completed Plant PWQ sheets and Lab data sheets Completed UV #2 calibration after it was left off for the weekend with S. Baidy and Jackie S. Recorded values in UV PWQ sheets Operations and adjustments: - Clearwell #1 analyzer adjusted: 2.25 ----> 2.08 mg/L - Post Chlorine analyzer adjusted: 1.63 ----> 1.97 mg/L - Sutton Free chlorine analyzer adjusted: 1.84 ----> 1.99 mg/L - Sutton Total chlorine analyzer adjusted: 2.24 ----> 2.36 mg/L - Keswick Fluoride analyzer adjusted: 0.92 mg/L ----> 0.72 mg/L - Sutton Fluoride analyzer adjusted: 0.87 mg/L ----> 0.64 mg/L - Duty rotated clearwell chlorinators - placed chlorinator #6 to D1, chlorinator #5 to off - Duty rotated backpulse valves - placed backpulse fill valve #1 to D1 - Duty rotated air compressors: Placed Kaeser compressor to D1 Activated system duty @15:04 - Placed UV 2 in D1 to run after calibration @15:21 - backpulse tank #1 fill valve fail to open - placed valve #2 to D1 Reviewed trends, equipment OOS: None Station ok | Georgina Water Treatment Plant | 2025-11-10
EAST | November | Reviewed the following on scada - To review trends and record trains MITs - To review trends and record filter daily performance, - To review permeate UV trends, no issues - Wet well mussel plate inspection completed Operations and Adjustments: Open UV2 effluent valve, to bring back water from the GAC to top up UV2 header while influent valve remained in close position. Turned power on from the UV panel, to calibrate UV2 after replacing lamp and sleeve on 1-1. Draining UV header for maintenance has caused low flow to Permeate turbidity analyzers causing them to fault. Filled header back up and cleared alarm on analyzers no issues. Low Lift Station: 1340 hrs: Notified ROC that contractor and PCS want to test P4 Placed FILT1 train1 raw water LCV1 and overflow reject valve opened Ran LL pump4 in local, then stopped. Ran LL pump4 in manual at an increment of 0, 25, 50, 75 and 100% speed as requested by contractor and technicians for data collection 1405 hrs: PCS requested pump be placed in manual on and @ 25% speed. Chlorine analyzers: Both existing and newly installed chlorine analyzer and pH probes are running concurrently. 12:27 hrs: prepared LL station for shut down to reconnect power to LL pump4 as requested by contractor onsite. Notified ROC Equipment OOS: - Sludge pump3 emergency stop alarm - GAC3 FCV deviation | Georgina Water Treatment Plant | 2025-11-10
EAST | November | Reviewed MIT and daily filter performance on all trains - all passed. On site to continue with UV2 system to get it calibrated. Hi lifts and UVs have been placed in manual at 09:14. At this time ROC was also informed of work to be completed. All alarms associated with UV2 are due to bulb replacement and calibration at 09:16. W11392348 UV System Maintenance. Was not able to complete UV2 calibration due to UV2 having other issues. Will figure out issues next week. Let on call operator know about UV issues. New bulb has been replaced for UV2 sensor lamp 1-1. Shut down pumps at low lift due to contractors completing work on pumps at 12:24. Notified PCS about PAC Panel Control Power Fail. PCS will be in on Monday to replace battery. Low lift power is back after work has been done pumps are back to auto at 12:46. Time: 13:06 CT1 Grab (mg/l) Analyzer (mg/l) Free: 2.00 2.56-2.00 after multiple grabs were taken adjusted CT1 at 13:09 from 2.56mg/l to 2.00mg/l. Time: 13:22 Keswick Grab (mg/l) Analyzer (mg/l) Free: 1.98 2.03 Total: 2.42 2.37 Time: 13:25 Sutton Grab (mg/l) Analyzer (mg/l) Free: 1.83 1.88 Total: 2.18 2.25 Activated duty at 13:16. Opened GAC backwash tank valve to fill backwash tank to 6.0m at 13:52. Closed GAC backwash tank valve after getting to 6.04m at 14:00. | Georgina Water Treatment Plant | 2025-11-07
EAST | November | Under direction of OIC. Patrick Fobert. Replaced batteries in UPSs throughout the facility. Worked with Ian Williams. | Georgina Water Treatment Plant | 2025-11-10
EAST | November | Reviewed MIT and daily filter performance on all trains - all passed. On site to complete station check and lab. Collecting following samples. W11347610 Algea and Glip Samples W11347582 S-VOC Samples W11347788 Bac-t Samples Time: 12:03 Keswick Grab (mg/l) Analyzer (mg/l) Free: 2.12 2.14 Total: 2.58 2.52 Time: 12:07 Sutton Grab (mg/l) Analyzer (mg/l) Free: 2.00 2.05 Total: 2.36 2.43 Verified analyzers with grabs. Checked station and trends. | Georgina Water Treatment Plant | 2025-11-05
EAST | November | Reviewed the following on scada - To review trends and record trains MITs - To review trends and record filter daily performance, - To review permeate UV trends, no issues - Wet well mussel plate inspection completed - Shoreline Observation Completed and recorded in PWQ data sheet Switched air compressor duties- placed Kaeser compressor in duty 1 no issues. Low Lift Station: Chlorine analyzers: Both existing and newly installed chlorine analyzer and pH probes are running concurrently. Equipment OOS: - Sludge pump3 emergency stop alarm - GAC3 FCV deviation | Georgina Water Treatment Plant | 2025-11-05
EAST | November | Onsite to change UPS batteries in station UPS?s. | Georgina Water Treatment Plant | 2025-11-10
EAST | November | Reviewed the following on scada - To review trends and record trains MITs - To review trends and record filter daily performance, - To review permeate UV trends, no issues - Wet well mussel plate inspection completed Operations and Adjustments: GAC4 turbidity fault, fault on vial clarity, replaced vial and cleared alarm 13:28 hrs: Adjusted clearwell 2 FCL analyzer reading from 1.65 mg/l to 1.78 mg/l based on 2 grabs 1421 hrs: Adjusted Keswick header TCL analyzer reading from 2.25 down to 2.14 mg/l based on average of 3 grabs 1430 hrs: Adjusted Sutton header TCL analyzer reading from 2.29 down to 2.12 mg/l based on average of 3 grabs Low Lift Station: Chlorine analyzers: Both existing and newly installed chlorine analyzer and pH probes are running concurrently. 10:15 prepared LL station for shut down to disconnect power from LL pump4 as requested by contractor onsite. Notified ROC Equipment OOS: - Sludge pump3 emergency stop alarm - GAC3 FCV deviation | Georgina Water Treatment Plant | 2025-11-03
EAST | November | Put UVs in manual at 09:04 to prevent plant from starting up. Reviewed MIT and daily filter performance on all trains - all passed. Informed ROC of work orders to be completed at 09:55. Completing following work orders: W11347467 Citric Acid Feed System Insp W11347501 NTU Filter Maintenance W11370224 Chlorine Cylinder Repair Kit Insp. W11378805 NH3 Leak Detector Test W11391220 Dehumidifier Element Change Out W11354028 JHSC Insp. W11347566 NTU Keswick/Sutton Maintenance W11345317 CL2 Analyzer Maintenance Header/Hi Lift W11357521 5 Tonne Hoist Insp. Grabs on Keswick and Sutton Chlorine analyzers. Time: 11:33 Keswick Grab (mg/l) Analyzer (mg/l) Free: 1.54 1.56 Total: 1.86 1.84 Time: 11:35 Sutton Grab (mg/l) Analyzer (mg/l) Free: 1.56 1.57 Total: 1.73 1.78 Verified analyzers with grabs no issues. Completing east and west sed tank analyzer work. Time: 11:45 East Sed Tank Grab (mg/l) Analyzer (mg/l) Free: 0.05 0.81-0.05 Time: 12:09 West Sed Tank Grab (mg/l) Analyzer (mg/l) Free: 0.07 0.02-0.07 At 11:47 adjusted the East Sed tank after multiple grabs were taken from 0.81mg/l to 0.05mg/l. At 12:09 adjusted the west Sed tank after multiple grabs were taken from 0.02mg/l to 0.07mg/l. Completing post clear well/header/hi lift analyzer work. Time: 12:34 Hi lift Grab (mg/l) Analyzer (mg/l) Free: 1.60 1.64 Verified analyzer with grab no issues. Between 13:07 and 13:13 cleared NTU alarms associated with GACs and Trains. Put everything back to auto and activated duty at 14:17 made sure to let ROC know that work has been completed for the day. Any changes in trends and alarms created were due to work orders being completed. | Georgina Water Treatment Plant | 2025-11-04
EAST | November | On site to complete station check and lab analysis. Also on site to collect weekly Bac-t Samples, and algae samples. W11386720 Weekly Bac-t Samples. W11387006 GLIP Samples. Reviewed MIT and daily filter performance on all trains - all passed. Low lift analyzers both new and old are running concurrently. Cleared particle count alarms on train 5 at 08:51 outstanding from the day before. Topped up electrolyte for clearwell 1 chlorine analyzer at 09:20. Completed Span calibration on east sed tank analyzer from 09:35-10:30 result is 0.01mg/l after multiple grabs adjusted analyzer from 0.36mg/l to 0.01mg/l at 10:30. Time: 09:50 Keswick Grab (mg/l) Analyzer (mg/l) Free: 1.77 1.75 Total: 2.15 2.11 Time: 09:52 Sutton Grab (mg/l) Analyzer (mg/l) Free: 1.75 1.76 Total: 2.06 2.08 Troubleshooting SRV opening at the low lift. Created work order for instrumentation at 13:42 for the raw water analyzer to be worked on at the low lift. | Georgina Water Treatment Plant | 2025-11-19
EAST | November | Reviewed the following on scada - To review trends and record trains MITs - To review trends and record filter daily performance, - To review permeate UV trends, no issues - Wet well mussel plate inspection completed - Completed shoreline lake observations and recorded in pwq data sheet Operations and Adjustments: Troubleshoot with train 5 backpulse valve, made adjustments and exercised a few time before placing it back in service. Low Lift Station: Equipment OOS: - Sludge pump3 emergency stop alarm - GAC3 FCV deviation | Georgina Water Treatment Plant | 2025-11-26
EAST | November | Under direction of OIC Patrick Fobert. Worked with operations and contractors to commission a flow valve on low lift pump 1. Mapped IO and enabled routines. Tested operation. | Georgina Water Treatment Plant | 2025-11-21
EAST | November | On site for station check, equipment verifications and lab analysis Reviewed MIT and daily filter performance on all trains - all passed and within range - recorded data to PWQ sheets Activated system duty @09:31 - KSTKWP level - 50% Recorded station readings in PWQ sheets and Lab data sheets Operations and adjustments: Verified chlorine analyzer readings: Clearwells, Headers, wash / waste Made the following adjustments to chlorine analyzers: - CW #1 adjusted from 1.98 to 1.82 mg/L - Keswick Free adjusted from 1.93 to 1.84 mg/L - Topped up Sodium hydroxide tank from 33 to 94 L - Completed in-house lab analysis - Duty rotated Raw sample pumps - placed P1 to D1 Reviewed trends Equipment OOS: Sludge Pump #3 Station ok | Georgina Water Treatment Plant | 2025-11-28
EAST | November | @18:28 - plant locked out and shutdown on contact chamber 1 low and Lolo alarms, along with a series of low lift alarms. Contacted Dan B from Lexsan, he will return to site to investigate @19:11 - Adjusted chlorinator #6 dosage factor from 58 to 60% and chlorinator #8 from 120 to 150% - Tested chlorination system with Clearwell SV 2 running in D1 - confirmed chlorine dosing by opening rotameter on chlorinator #6. Placed chlorine system back to auto. @19:45 - opened train #3 inlet valve to test low lift pump 1 - caused tank level high and hihi alarms due to water overflowing to waste tanks (intentionally) @19:52 - stopped low lift P1, no alarms occurred this time during the pump run. Lexsan has returned to site, waiting for Eaton to arrive to continue troubleshooting with Multi Lin - @20:37 Adjusted chlorinator #6 dosage factor back to 60%, as the recirculation pump has brought chlorine residuals back to better levels - Stephen B will continue in his log entry | Georgina Water Treatment Plant | 2025-11-25
EAST | November | On site for monthly maintenance: - Reviewed MIT and daily filter performance on all trains - all passed and no issues. Recorded readings in PWQ sheets Manual backwash on GAC 2: - Placed GAC2 OOS for backwash - @11:36: Placed GAC2 inlet valve to closed, and opened effluent valve to drain filter to 3 m for backwash - @11:57: closed effluent valve, started backwash pump @12:00 - @12:27: Stopped backwash pump and closed backwash valves. - @12:40: Opened FTW valve to start draining to waste. Opened GAC2 inlet valve - @13:55 stopped filter to waste. Placed GAC2 back in service - Topped up backwash clearwell after backwash A lot of low lift FCV alarms were coming in today on pump shutdowns. Worked with PCS Chris Scott to resolve issue for tonight. He had increased the timer on the ramp down on the low lift speed this morning. (Change was made to see if it would help the Surge relief valve from opening frequently) He reverted changes to normal for tonight. Will investigate more tomorrow. Activated system duty @15:06 No further issues on site | Georgina Water Treatment Plant | 2025-11-20
EAST | November | On site to complete GAC 4 back wash. At 09:55 informed ROC of work to be completed. Reviewed MIT and daily filter performance on all trains - all passed. Low lift analyzers both new and old are running concurrently. At 10:07 started filling backwash clear well in anticipation for GAC 4 back wash. At 10:19 stopped filling back wash clear well. At 10:25 started GAC 4 backwash process. Alarms are associated with backwash being completed including NTU alarms on GAC 4. Filtered to waste for 33mins and during this time NTU was 0.067. At 12:27 placed GAC 4 back in service. NTU is below 0.250 and is currently reading 0.087 NTU. Variations in trends are due to backwash being completed on GAC 4. ROC informed of PH probe calibration at 13:17. At 13:40 switched waste water pumps from pump 1 and 2 in duty to pump 1 and 3 in duty. All alarms have been cleared and reset. | Georgina Water Treatment Plant | 2025-11-27
EAST | November | On site to complete trial shutdown for plant shut down tomorrow. Reviewed MIT and daily filter performance on all trains - all passed. Low lift analyzers both new and old are running concurrently. At 10:40 activated duty at the plant to start station check. At 10:43 put train 2 back into maintenance clean mode and activated it. Time: 11:12 Hi Lift Grab (mg/l) Analyzer (mg/l) Free: 1.80 1.73 Time: 11:18 Keswick Grab (mg/l) Analyzer (mg/l) Free: 1.72 1.70 Total: 2.07 1.98 Time: 11:20 Sutton Grab (mg/l) Analyzer (mg/l) Free: 1.68 1.72 Total: 1.94 2.00 Shut down duty at 12:06 to prepare for trial shutdown for tomorrow. Disabled train 4 maintenance clean mode for the trial shutdown. Power has been shut off to the plant at 12:34 and generator is not running due to disconnection for test for tomorrow. Power has been restored at 12:42 all alarms that have come in are due to power supply being shut down. From 12:54-13:00 ack and reset outstanding alarms. Enabled m-cleans on train 4. Entered lab data into PWQ sheets | Georgina Water Treatment Plant | 2025-11-24
EAST | November | Reviewed the following on scada - To review trends and record trains MITs - To review trends and record filter daily performance, - To review permeate UV trends, no issues - Wet well mussel plate inspection completed - Completed shoreline lake observations and recorded in pwq data sheet Operations and Adjustments: 12:00 hrs: did grabs on Keswick header for sample collection FCL = 1.99. TCL = 2.29 Worked on SO2 system, notified ROC before purging and isolating system. Completed work on SO2 system, tested system with both solenoid valves opened, worked, no issues Tested SRV operations at test LL by running raw water pumps in manual Low Lift Station: Both new and existing raw water chlorine analyzers are running concurrently at the LL Calibrated both intake and sedimentation chlorine analyzers, intake analyzer keep dropping to 0.0 mg/l. Created WO for instrumentation team to look at. Equipment OOS: - Sludge pump3 emergency stop alarm - GAC3 FCV deviation | Georgina Water Treatment Plant | 2025-11-19
EAST | November | Disabled train 6, 7, 8 Tuesday?s M-Clean. | Georgina Water Treatment Plant | 2025-11-25
EAST | November | Reviewed MIT and daily filter performance on all trains - all passed. Low lift analyzers both new and old are running concurrently. Activated duty at 08:10. Informed ROC of work to be done at low lift on low lift pump 1 at 08:54. Topped up GAC back wash tank at 08:56 for backwash for next week. Time: 09:58 Keswick Grab (mg/l) Analyzer (mg/l) Free: 1.88 1.88 Total: 2.13. 2.27-2.13 adjusted Keswick total analyzer reading after multiple grabs were taken from a 2.27mg/l-2.13mg/l at 10:04. Time: 10:05 Sutton Grab (mg/l) Analyzer (mg/l) Free: 1.82 1.87 Total: 2.17 2.23 Completed low lift pump 1 testing and commissioning of flow control valve from 11:00am to 12:35pm. Alarms that happened were due to low lift pump 1 testing. | Georgina Water Treatment Plant | 2025-11-21
EAST | November | Disabled train 2 and 3's Monday M-Clean schedule. | Georgina Water Treatment Plant | 2025-11-24
EAST | November | On site to complete station check. Reviewed MIT and daily filter performance on all trains - all passed. Low lift analyzers both new and old are running concurrently. At 09:39 switched duties from pump 1 to pump 3 to test if there were any issues, no issues have been seen. Initiated MIT on train 5 at 13:58 to see if it passes. Time: 12:32 Hi Lift Grab (mg/l) Analyzer (mg/l) Free: 1.86 1.82 Time: 12:45 Keswick Grab (mg/l) Analyzer (mg/l) Free: 1.94 2.57-1.94 Total: 2.17 2.23 At 12:46 took multiple grabs and adjusted the free analyzer from 2.57mg/l-1.94mg/l. Time: 12:52 Sutton Grab (mg/l) Analyzer (mg/l) Free: 1.85 1.92 Total: 2.12 2.16 MIT on train 5 passed at 14:27 train is back in service. | Georgina Water Treatment Plant | 2025-11-26
EAST | November | Reviewed the following on scada - To review trends and record trains MITs - To review trends and record filter daily performance, - To review permeate UV trends, no issues - Wet well mussel plate inspection completed - Completed shoreline lake observations and recorded in pwq data sheet - Notified Property Services to inform security panel operator. Operations and Adjustments: 0826 hrs: Prepared plant for a complete power shut down for the following activities: - New Multilin installation at the LL - Installation of a new butter valve on HL header for pump 4 Notified ROC before shutting down plant. Made ROC aware that shut down will affect both critical and noncritical analyzers Contractor and PCS have connected portable generator to temporarily power up network room equipment. LOTO both isolation valves (actuator and manual valves) on each header (keswick and Sutton) Drained headers back into clear-wells after isolation ALL analyzers at the plant run out of flow due to header being empty for the period. 1535 hrs: Power transferred back to Hydro, no issues Started pressurizing headers - Keswick and Sutton. Restored flow to all analyzers, Notified ROC before activating duty after work completion. 1100 hrs: Activated M-cleans on trains 6, 7 and 8 All trains going through backpulse valves issues and causing shut downs. Was able to exercise or make adjustments to get trains back up and running. 1125 hrs: train 5 backpulse failed to open, tried a few adjustments but that did not work. Will create a WO for CMS - water Low Lift Station: Experienced issues with LL pumps, leading to duty shut down Contractor conducted a few troubleshooting and got station back up and running 1630 hrs: LL pumps issues again, pumps going into uncommanded stops and or hydraulic valves fail to open or close Called contractor back to site for further investigation, found new multilin producing under frequency or out of frequency alarms causing pumps to go into interlocks. 2113 hrs: Issues resolved and plant back to operation again. Rotated LL pumps duty a few times no issues. Equipment OOS: - Sludge pump3 emergency stop alarm - GAC3 FCV deviation - Train 5 backpulse - HL pump3 Did visual inspection of plant before leaving site. | Georgina Water Treatment Plant | 2025-11-26
EAST | November | Attending site to check Inlet Chlorine Analyzer in the lowlift building (W11455963). Analyzer was faulted and reading less than zero sensor current. Replaced electrolyte and membrane cap and calibrated to 1.84mg/L, using treated water line. Returned raw water inlet sample line to analyzer. Will monitor SCADA tomorrow to see if analyzer fault remains absent. ROC was notified before and after maintenance work. | Georgina Water Treatment Plant | 2025-11-19
EAST | November | On site to prep plant for full day shut down. Reviewed MIT and daily filter performance on all trains - all passed. Low lift analyzers both new and old are running concurrently. Shut off m-cleans for trains 6-8 in anticipation for plant shut down. Put hi lift pumps and UVs to manual off at 7:52. Deactivated Sutton duty at 08:13. Put Sutton flow control valves in manual at 08:17. At 08:21 ack and reset train 5 particle counter alarms. Will investigate why that is coming in. Informed ROC at 08:25 of what is happening at the plant today. From 08:45 to 09:00 closing all main line valves for Sutton and Keswick to begin depressurizing header. At 08:54 started pumping down basement sump pit. Started turning analyzers off at 09:04. Header has been drained from 09:05 to 09:20. At 09:52 power to the plant has been shut off for work to be completed. Power reconnected at 15:35 and restored to the plant. At 15:50 started to open up valves for Keswick and Sutton discharge lines. At 16:11 reactivated sludge and wash water pumps. Turning all analyzers back from 16:13 to 14:20. At 14:23 started opening up UV system valves to prime the permeate header line. At 14:31 put UV valves back to auto and closed. ROC has been informed at 16:27 that plant is being put back on line. Put train 5 to off due to suction valve not closing on permeate line properly. At 17:04 duty has been activated, also flow for hi lifts has been adjusted accordingly to 120l/s. At 17:15 shut duty off for the plant due to low lift pumps locking out on a multilin issue. From 17:17 to 17:40 troubleshot the low lift pumps locking issues with the multilin. Issues have been figured out and duty has been activated at 17:41. Plant locked out at 17:45 due to permeate header hihi NTU alarm. Cleaned NTU unit and analyzer cleared alarms. At 17:48 UV 1 shut down due to low flow. Duty activated at 17:50 UV2 is duty 1. Duty is now active | Georgina Water Treatment Plant | 2025-11-25
EAST | November | Work on water pump outside Install new battery rerouted fuel line and got pump to run. | Georgina Water Treatment Plant | 2025-11-24
EAST | November | On site for station check, equipment verifications and lab analysis Completed PWQ sheets and plant rounds Manual backwash on GAC 1: - Duty is active, will be doing the backwash while the plant is running - @09:00: Placed GAC1 inlet valve to closed, and drained GAC to clearwell for backwash to 3.0 m - @09:22: closed effluent valve, placed GAC1 OOS on the filtration setpoints - @09:26: Attempted to start Backwash pump #2 - but it interlocked on a low flow alarm. Investigated BW P2, found that it was showing a run status on SCADA, but not actually running. Tried to start pump in local, but it would not start. Created WO for maintenance / electrical to investigate. - @09:30: Started Backwash pump #1 to complete GAC backwash. - @09:58: Stopped backwash pump after filter is filled to 4.75 m. Allowed filter to rest post backwash - @10:07: Started filter to waste. @10:54: Stopped filter to waste, and placed GAC 1 back into service. NTU is 0.168 Worked with Artour from PCs to troubleshoot the low lift hydraulic valves issues that have been occuring since yesterday. Were able to resolve the issues so the valves / pumps timers are working correctly on the pump stops. Tested each pump individually to make sure they were all working. No further issues. Informed ROC of work done and alarms to disregard. Used train #2 to direct water to while testing low lift pumps with the plant off. Generated high and hihi alarms. Activated system duty again @15:15 to ensure everything runs okay after low lift work Station ok | Georgina Water Treatment Plant | 2025-11-21
EAST | November | Reviewed the following on scada - To review trends and record trains MITs - To review trends and record filter daily performance, - To review permeate UV trends, no issues - Wet well mussel plate inspection completed - Completed shoreline lake observations and recorded in pwq data sheet Outstanding Alarms: - Hydraulic vlv failed to open LL pump 1 and 4 Ack and reset, placed LL pump1 in duty 1 and 2 as back up pmp Operations and Adjustments: 1040 hrs: Activated duty for a station check before mock shutdown. 1109 hrs: Particle counter OOS alarm came in, found power issues caused particle counter to go OOS, moved to power cord to a different socket to correct the issue. 1134 hrs: Switched air compressors, placed BOGE compressor in lead duty. Deactivated duty for mock shut down, notified ROC Testing done, notified cleared all alarms, notified ROC before leaving site. Low Lift Station: - Hydraulic vlv failed to open LL pump 1 and 4 Ack and reset, placed LL pump1 in duty 1 and 2 as back up pmp Both new and existing raw water chlorine analyzers are running concurrently at the LL Equipment OOS: - Sludge pump3 emergency stop alarm - GAC3 FCV deviation | Georgina Water Treatment Plant | 2025-11-24
EAST | November | On site with Dan Boate to investigate malfunctioning backwash pump BWP30002. Tested pump from hand control station and remotely from SCADA. Pump operates normally. Problem could not be replicated. Operator on site, Patrick Forbert notified. | Georgina Water Treatment Plant | 2025-11-28
EAST | November | Called ROC at 09:33 for the lockout of low lift pump 1. At 09:40 locked out both the VFD and the discharge valve on low lift pump 1. Contractors have been informed of lockouts that are in place. Completing following work orders: W11389703 Comprehensive Housekeeping Chemical Room W11374181 Permeate/BP Pump Maintenance W11337537 Fluoride Pump 2 Maintenance W11336993 Fluoride Pump 1 Maintance W11386483 mussel Plate Inspection. Completed work orders with out any issues. Informed on call operator of locked out low lift pump 1. | Georgina Water Treatment Plant | 2025-11-20
EAST | November | Reviewed the following on scada - To review trends and record trains MITs - To review trends and record filter daily performance, - To review permeate UV trends, no issues - Wet well mussel plate inspection completed Operations and Adjustments: 11:00 hrs: Received Hypo, tank level at start = 0.30 m stopped @ 1.29 m Worked on SO2 system, notified ROC before purging and isolating system. Low Lift Station: Reset raw water sample pump 3 - comm fail alarm Equipment OOS: - Sludge pump3 emergency stop alarm - GAC3 FCV deviation | Georgina Water Treatment Plant | 2025-11-18
EAST | November | ROC informed of power blip in Georgina area. Reset all alarms except generator fault.? Utility power is available.? Will attend site to check the generator status.? | Georgina Water Treatment Plant | 2025-11-16
EAST | November | On site to complete following work orders: W11343549 Comprehensive Housekeeping W11339322 Caustic Soda Pump Inspection W11336983 JHSC Low Lift W11336616 Flow control Valve Test W11339309 SBS Pump Inspection W11357509 2 Tonne Hoist Inspection W11357497 2 Tonne Hoist Inspection W11335113 Pump and Motor Inspection W11378816 CL2 Leak Detector Test W11371761 Clearwell Drain Pump Insp/Maint. Put UVs is manual off at 11:46 due to work orders being completed at this time. Informed ROC of work being completed. | Georgina Water Treatment Plant | 2025-11-11
EAST | November | Started duty at 11:40 for both Keswick and Sutton. Reviewed MIT and daily filter performance on all trains - all passed. Time: 12:40 Keswick Grab (mg/l) Analyzer (mg/l) Free: 1.68 1.74 Total: 2.02 2.08 Time: 12:43 Sutton Grab (mg/l) Analyzer (mg/l) Free: 1.84 1.82 Total: 1.93 1.94 Entered data into lab PWQ sheet Contacted ROC that NTU at Lo lift will be calibrated. Started calibration at 14:16 on NTU unit at Lo lift. No issues with calibration. | Georgina Water Treatment Plant | 2025-11-14
EAST | November | Worked on hypo lines. Placed hypo pumps in manual off to allow pumbing to cure. ROC and oncall operator notified | Georgina Water Treatment Plant | 2025-11-12
EAST | November | Manual off UVs and Sutton PRVs. | Georgina Water Treatment Plant | 2025-11-13
EAST | November | Onsite working with contractor and ETO (Consultant) to re-span instruments for PMP3 and PMP4 Low Lift pumping Station Pressure Indicating Transmitters. (LLP_PMP3/4_PIT1) from 1600 kPa to 1034 kPA. Put instruments in calibration mode during work performed, no issue with operations. Completed task, pumps available. | Georgina Water Treatment Plant | 2025-11-13
EAST | November | Under direction of OIC, Patrick Fobert. Tested all UPSs for drawdown. Recorded all serial numbers and asset numbers. | Georgina Water Treatment Plant | 2025-11-11
EAST | November | Performing station checks for low lift. Exercised the screen and there is no water spraying. Brett from ETO advised new PRV control and found it in Close position. Tested it local open and water resumed. Placed the selector switch to remote. Initiated screen sequence again, it had sequence fault and E-Stop alarm. Verified that E-Stop is not engaged. Brett will inform contractor of the issue.? 13:00 calibrated both raw and low lift AIT readings to match with 3 grabs' average. Raw total chlorine grab = 0.26 mg/l. Lowlift total chlorine grab = 0.35 mg/l.? Other readings are in PWQ sheet. 14:01 on duty shut off, low lift surge relief valve open alarm came in and resulted series of low lift alarms. Reset all alarms. Changed Low lift electrical room hihi temp alarm from 25 to 30. It is currently at 26 C.? Lexan adjusted the limit for Screen's breaker and cleared the E-Stop alarm. Initiated the screen cycle, it completed the cycle without any issue.? Disabled Thursday?s M cleans on train 1 and 2. Placed both hypo pumps man/off. Equipment OOS: Sludge P3. | Georgina Water Treatment Plant | 2025-11-12
EAST | November | ROC informed train 7 shut down on hihi turbidity. Reviewed trends, it happened during backwash cycle.? Initiated another backwash on train 7.? Placed it back into production. No issues.? | Georgina Water Treatment Plant | 2025-11-14
EAST | November | On site to complete station check and in house lab. Reviewed MIT and daily filter performance on all trains - all passed. Collecting weekly Bac-t Samples. Collecting VOC resamples. Collecting weekly microcystin/algae samples. W11435974 VOC Samples W11367984 Microcystin/Algae samples W11368170 Weekly Bac-t Sample At 09:33 activated both Keswick and Sutton duties Time: 11:07 Keswick Grab (mg/l) Analyzer (mg/l) Free: 1.88 1.89 Total: 2.22 2.25 Time: 11:10 Sutton Grab (mg/l) Analyzer (mg/l) Free: 1.88 1.96 Total: 2.10. 2.30-2.10 after multiple grabs adjusted Sutton Total from a 2.30mg/l to a 2.10mg/l at 11:17. SBS delivery and top up at 13:26 Lab data has been entered into PWQ sheet. | Georgina Water Treatment Plant | 2025-11-12
EAST | November | 16:55 Stephen informed that Sutton PRV failed to open in remote and local. Requested ROC to engage town of Georgina oncall operator to open their Zone valve to supply to Sutton ET.? As of 17:04 SUET = 5.25m or 56%.? 17:47 Confirmed with Stephen that Town of Georgina OP (Will) is coming to site to open zone valve and his ETA is around 6:30pm. Bill V.B. Is also dispatched to site by Linear team to assist with the valve in chamber 43-01. | Georgina Water Treatment Plant | 2025-11-13
EAST | November | On site to complete station check and completing generator run. Informed ROC of what is happening. Reviewed MIT and daily filter performance on all trains - all passed. At 09:45 adjusted the intake analyzer after multiple grabs from 0.07mg/l to 0.12mg/l. Deactivated m clean for train 3 at 09:50 so that generator run can be completed. Switched compressors from the BOGE to the Kaiser at 10:28. Topped up sodium hydroxide from 41L to 81L Activated duty for Keswick and Sutton at 10:57. Reactivated m clean for train 3 at 10:59. Turned train 2 off and on to prime it and put it back in service. Any alarms associated with generator run have been ack and reset Adjusted CT1 free analyzer after multiple grabs were taken at 13:02 from 2.84mg/l to 2.61mg/l. Adjusted post clearwell free analyzer after multiple grabs were taken at 13:14 from 2.04mg/l to 1.90mg/l. Adjusted the Sutton free and total chlorine analyzer readings at 13:19 from 2.03mg/l to 1.91mg/l for free and from 2.14mg/l to 2.24mg/l for total, after multiple grabs were taken. Deactivated duty for generator switch over at 13:54 for both Sutton and Keswick. Before Diesel Generator Test Run Sheet running generator, the following were inspected: - [ ] Battery cell levels - [ ] Battery terminal and cables - [ ] Oil level - [ ] Coolant level - [ ] Fluid leaks - [ ] Coolant Recirculating pump - [ ] Faulty gauges Diesel generator start time: 10:55 hrs Diesel hours at start: 507.34 Fuel Level @ start: * Tank #1 ~ 0.91m * Tank #2 ~ Start time: 10:55 After 30 min of running: * Operating current = 250 A * Operating frequency = 60 Hz * Operating voltage = 600 V * Engine speed = 2100 RPM * Water temperature = 170 F * Oil temperature = 195 F * Oil pressure = 105 psi * Fuel pressure. = ? * Pyrometer/Exhaust = 684/706 F Stopped and transferred power to hydro @ 14:01 hrs Diesel generator hours after shutdown: 510:62 hrs * Tank #1 ~ 0.83m * Tank #2 ~ Additional information/ Observations: Activated duty and conducted generator test under load, no issues Entered data into PWQ sheet. Ack and reset all alarms on site associated with generator run. Put system back to auto at 14:17. | Georgina Water Treatment Plant | 2025-11-17
EAST | November | Reviewed the following on scada - To review trends and record trains MITs - To review trends and record filter daily performance, - To review permeate UV trends, no issues - Wet well mussel plate inspection completed Operations and Adjustments: Open UV2 effluent valve, to bring back water from the GAC to top up UV2 header while influent valve remained in close position. Turned power on from the UV panel, to calibrate UV2 after replacing lamp and sleeve on 1-1. Draining UV header for maintenance has caused low flow to Permeate turbidity analyzers causing them to fault. Filled header back up and cleared alarm on analyzers no issues. Low Lift Station: 1340 hrs: Notified ROC that contractor and PCS want to test P4 Placed FILT1 train1 raw water LCV1 and overflow reject valve opened Ran LL pump4 in local, then stopped. Ran LL pump4 in manual at an increment of 0, 25, 50, 75 and 100% speed as requested by contractor and technicians for data collection 1405 hrs: PCS requested pump be placed in manual on and @ 25% speed. Chlorine analyzers: Both existing and newly installed chlorine analyzer and pH probes are running concurrently. 12:27 hrs: prepared LL station for shut down to reconnect power to LL pump4 as requested by contractor onsite. Notified ROC Equipment OOS: - Sludge pump3 emergency stop alarm - GAC3 FCV deviation | Georgina Water Treatment Plant | 2025-11-11
EAST | November | On site for monthly maintenance: Informed ROC - Reviewed MIT and daily filter performance on all trains - all passed, within range and no issues - Chlorine leak detector test - Chemical room and Tonner room - Air dryer inspections - Air compressor maintenance and compressed air system inspection - Air blowers inspections @15:04 - Activated system duty - KSTKWP level - 61% @15:14 - Permeate common header turbidity hi and hihi alarms came in - caused by air in the lines to the analyzer, cleared air from lines and NTU reading came back down. Also causing trains 1 and 8 to shutdown, and have turbidity spikes due to the rapid stop. @15:16 - UV #1 shutdown due to low water flow, caused by all of the trains not being able to run due to permeate common header turbidity hihi alarms. UV #2 alarms also generated but cleared. High lift pump #3 also stopped running @15:20 due to no UV running. Duty rotated to UV #2 @15:18. Train #1 Permeate turbidity hihi alarms came in @15:27 when initiated backwash. NTU is still high at 180 mNtu and analyzer is erratic due to air bubbles. Left off for now 15:28 - UV #2 running and high lift pump #2 started - trains #2 to #7 are available to run Initiated backwash on train #8 @15:36 and placed back into service - cleared turbidity fault alarm. @15:55 - Placed train #1 into backwash, it went through backwash okay and went back to standby. Turbidity came back down. No further issues Cleared all alarms, informed ROC, station ok | Georgina Water Treatment Plant | 2025-11-11
EAST | November | Reviewed the following on scada - To review trends and record trains MITs - To review trends and record filter daily performance, - To review permeate UV trends, no issues - Wet well mussel plate inspection completed Operations and Adjustments: Notified ROC about the todays WOs: - hypo line repairs - Linear doing isolation and pressure tests on both Keswick and Sutton header in the distribution system. - Contractor and PCS and Instrumentation working on site to work on LITs and PITs and new VFD after installation Resume work hypo line for M-cleans, depressurized PSW line and ran hypo pumps in local to test for leaks after repairs Returned valves and pumps on hypo system to auto, no issues Optioned hypo pumps and lines Returned trains 1 and 2 M-clean schedule to enable mode, initiated M clean on train 3. Inspected hypo chemical system for leaks during chemical injection in M clean mode, no leaks observed. 1600 hrs: Linear done with valve isolation test and reopened all valves. 1622 hrs: tried to operate Sutton header PRVs, but both did not open. PRVs will not open in local either. 1640 hrs: notified TL and Supervisor, Interim procedure for Sutton water system, Town of Georgina operator was called out to open a valve in their system to allow the plant to fill the tower though their system while to operations get solution for header valve. 1710 hrs: activated duty for keswick towers top up. 1930 hrs: Maintenance got valve issue corrected ~ broken shear pin. Activated Sutton tower duty, PRV1 opened and started supplying water to the tower. Asked Town of Georgina operator to close their valve now that we have the Sutton header valve working. Notified ROC and follow-up with email. Low Lift Station: 1150 hrs: Ran LL pump3 for test, hydraulic valve failed to open after few mins of running @ 137 l/s then shut down, cleared alarm and restart pump3 no issues afterwards. Placed train 1 raw water valve in manual and opened, to run LL pumps through during testing. 1600 hrs: Linear done with valve isolation test and reopened all valves. 1622 hrs: tried to operate Sutton header PRVs, but both did not open. PRVs will not open in local either. 1640 hrs: notified TL and Supervisor, Interim procedure for Sutton water system, Town of Georgina operator was called out to open a valve in their system to allow the plant to fill the tower though their system while to operations get solution for header valve. 1930 hrs: Maintenance got valve issue corrected ~ broken shear pin. Activated Sutton tower duty, PRV1 opened and started supplying water to the tower. Asked Town of Georgina operator to close their valve now that we have the Sutton header valve working. Notified ROC and follow-up with email. 1220 hrs: Test run LL pump4 Equipment OOS: - Sludge pump3 emergency stop alarm - GAC3 FCV deviation | Georgina Water Treatment Plant | 2025-11-13
EAST | November | On-site to for station check Worked on sulphur dioxide system | Georgina Water Treatment Plant | 2025-11-17
EAST | November | On site to check generator fault alarm. Found it had "over crank" light on and breaker was tripped. Reset the breaker and the over crank alarm on generator panel, then alarms on SCADAS cleared.? Activated plant duty. West Park Tank level is 62%.? Plant is back to normal operation. | Georgina Water Treatment Plant | 2025-11-16
EAST | November | Reviewed the following on scada - To review trends and record trains MITs - To review trends and record filter daily performance, - To review permeate UV trends, no issues - Wet well mussel plate inspection completed Operations and Adjustments: Notified ROC about the todays WOs: - hypo line repairs - Linear doing isolation and pressure tests on both Keswick and Sutton header in the distribution system. - Contractor and PCS and Instrumentation working on site to work on LITs and PITs and new VFD after installation Resume work hypo line for M-cleans, depressurized PSW line and ran hypo pumps in local to test for leaks after repairs Returned valves and pumps on hypo system to auto, no issues Optioned hypo pumps and lines Returned trains 1 and 2 M-clean schedule to enable mode, initiated M clean on train 3. Inspected hypo chemical system for leaks during chemical injection in M clean mode, no leaks observed. 1600 hrs: Linear done with valve isolation test and reopened all valves. 1622 hrs: tried to operate Sutton header PRVs, but both did not open. PRVs will not open in local either. 1640 hrs: notified TL and Supervisor, Interim procedure for Sutton water system, Town of Georgina operator was called out to open a valve in their system to allow the plant to fill the tower though their system while to operations get solution for header valve. 1710 hrs: activated duty for keswick towers top up. 1930 hrs: Maintenance got valve issue corrected ~ broken shear pin. Activated Sutton tower duty, PRV1 opened and started supplying water to the tower. Asked Town of Georgina operator to close their valve now that we have the Sutton header valve working. Notified ROC and follow-up with email. Low Lift Station: 1150 hrs: Ran LL pump3 for test, hydraulic valve failed to open after few mins of running @ 137 l/s then shut down, cleared alarm and restart pump3 no issues afterwards. Placed train 1 raw water valve in manual and opened, to run LL pumps through during testing. 1220 hrs: Test run 1600 hrs: Linear done with valve isolation test and reopened all valves. 1622 hrs: tried to operate Sutton header PRVs, but both did not open. PRVs will not open in local either. 1640 hrs: notified TL and Supervisor, Interim procedure for Sutton water system, Town of Georgina operator was called out to open a valve in their system to allow the plant to fill the tower though their system while to operations get solution for header valve. 1930 hrs: Maintenance got valve issue corrected ~ broken shear pin. Activated Sutton tower duty, PRV1 opened and started supplying water to the tower. Asked Town of Georgina operator to close their valve now that we have the Sutton header valve working. Notified ROC and follow-up with email. Equipment OOS: - Sludge pump3 emergency stop alarm - GAC3 FCV deviation | Georgina Water Treatment Plant | 2025-11-13
WW-CEAST | November | -On site to complete work orders. -Station check completed, readings entered into SharePoint. -Dry well flood alarm test completed and confirmed by ROC. -High/low temp alarm test completed and confirmed by ROC. -Monthly JHSC inspection completed, no issues noted. -Monthly diesel generator test run completed, readings entered into SharePoint. -1205 - Transferred site to generator power. -1308 - Transferred site back to utility power. -Hazardous waste collection and removal completed, no items removed from site this month. -All pumps available and in auto. | Aurora Henderson Sewage Pumping Station | 2025-11-03
WW-CEAST | November | Station check complete and the readings have been entered into the sharepoint Upon arrival, noticed pumps 3 and 4 low flow alarm outstanding on the alarm banner from this morning around 9:38am. Cleared the alarm and reviewed trend. Spotted few ultrasonic lit dips/spikes in past few days which caused back up mode to kick in/out which likely caused the pump low flow issue. Placed station in PAC mode with LIT2 in lead duty. Wet well selection placed manual as well. Reported issue to CPD/WSP/CEWW team | Aurora Henderson Sewage Pumping Station | 2025-11-07
WW-CEAST | November | Informed ROC. Performed annual calibration and put instruments in Cal mode while doing the tasks. Devices done were FITs, LITs, LEL sensor and forcemain PITs. All alarms were cleared after the job. No other issues encountered. | Aurora Henderson Sewage Pumping Station | 2025-11-25
WW-CEAST | November | -On site to perform a station check. -Station readings entered into SharePoint. -Checked valve room and generator. -Pumps in auto and available. -Station in PAC mode due to ongoing LIT1 level fluctuations. | Aurora Henderson Sewage Pumping Station | 2025-11-28
WW-CEAST | November | On site for station check (See details on SharePoint). All pumps available in all-stop auto duty rotation. Pump 4 currently running in auto as duty 1 with 55 L/s flow at 313 kPa. Standby power generator available in auto. Station operations normal. | Aurora Henderson Sewage Pumping Station | 2025-11-24
WW-CEAST | November | -On site to complete work orders. -Entered station readings into SharePoint. -Checked generator and valve room. -Station check completed. -Comprehensive housekeeping tasks completed. -Site is in PAC mode due to LIT1 level fluctuations. | Aurora Henderson Sewage Pumping Station | 2025-11-21
WW-CEAST | November | Onsite to wrap up annual calibrations Informed ROC Used cal mode on scada during the work Calibrated RSP 1 to 4 discharge PITs Cleared associated alarms Informed ROC and left site Operations on site for station check | Aurora Henderson Sewage Pumping Station | 2025-11-28
WW-CEAST | November | -On site to perform a station check. -Entered station readings into SharePoint. -Station in PAC mode due to LIT1 fluctuations. -Checked valve room and generator. -Odour control scrubber system inspection completed, checked media and filters. | Aurora Henderson Sewage Pumping Station | 2025-11-17
WW-CEAST | November | -On site to complete work orders. -Entered station readings into SharePoint. -Checked generator and valve room. -Station check completed. -Station in PAC mode due to LIT1 fluctuations. -RS pump discharge valve actuator, exercise and inspection completed. -Manual valve exercise completed, fully exercised all valves. -RS pump inspection completed, all pumps have approximately 55L/s at 50% speed. -Check valve inspections completed. -Air relief valve inspection completed. | Aurora Henderson Sewage Pumping Station | 2025-11-14
WW-CEAST | November | -On site to place wet well backup mode back to PAC. LIT1 still getting sporadic spikes in its readings causing pumps to go into backup mode. -Cleared alarms on site, all pumps in auto and available. | Aurora Henderson Sewage Pumping Station | 2025-11-11
WW-CEAST | November | AECOM have requested a setpoint adjustment for the system negative inlet/suction pressure. Setpoints adjusted from 1.2kPa to -1.5kPa. Changes initiated @ 12pm. Both Fans in AUTO @ 60 & 65% w/ Stack Flow between 7000-7200 m3/h. Air Flow through Stack is also dependent upon the sanitary flows on Yonge St. More WW Flows will equal less air flow from system as the air head space is reduced. | Oak Ridges Air Management Facility | 2025-11-05
WW-CEAST | November | -On site to perform a station check. -Entered station readings into SharePoint. -Completed site walkthrough. -Nutrient tank 3/4 full. -NAC noted small amount of algae growth in nutrient lines coming from tank. Biorem scheduled to be on site later today, will be further discussed. -Temporary generator off site, permanent generator now in operation on site. | Oak Ridges Air Management Facility | 2025-11-10
WW-CEAST | November | -On site to perform a station check. -Entered station readings into SharePoint. -Completed site walkthrough. -Filled nutrient tank. -Exhaust fan 1 remans OOS. -Temporary generator still be used on site. | Oak Ridges Air Management Facility | 2025-11-03
WW-CEAST | November | Notified that the Recirculation Pumps cannot run in Remote/Manual without being interlocked by the process. Modified code to allow for operations to run the pump/s in remote/Manual mode, bypassing the high pressure and low flow alarm for maintenance procedures. (Contractor onsite and was attempting to isolate pump issues and could not run the pump based on previous code). Following pump repairs, the branch of new code will be deleted. | Oak Ridges Air Management Facility | 2025-11-24
WW-CEAST | November | On site checked station (See details on SharePoint). Fan 1 and 2 running in auto. Damper 1 in auto. Damper 2 in local mode but 100% open. Nutrient tank at 1/2 full - contractor working for some tubing connections. Filling valve closed. Standby power generator available in auto. Tested outlet air exhaust stack sample port using MSA gas monitor with pump probe for a few minutes, reading 0 ppm for H2S. At 10:3am, NAC and Biorem requested to turn off the fans so they could check the recirculation pumps. At 10:50am, fans back up running. Station back to normal operations. At 11:50am, back on site to assist NAC/Biorem to check recirculation pumps. At 12:15pm, fans 1 and 2 turned off. Ran recirculation pumps one by one in manual. Found recirculation pump 2 at Bioscrubber Unit 2 is noisy when running. NAC/Biorem LOTO the pump and will pull it out of site to be checked in their shop. At 12:40pm, fans 1 and 2 back up running in auto. Station back to normal operation. | Oak Ridges Air Management Facility | 2025-11-24
WW-CEAST | November | Onsite today to assist contractor the modifications of DMP1 and DMP2. Contractor Sub damaged incoming damper motherboard during service, causing the valve to be inoperable. Needed to add bypass code for Local/Remote and Fault status. System is operating as per normal now, with the damper 1 in LOCAL, OPEN to 100%. If a Train shuts down, the valve will remain open as the damper control has been left in LOCAL due to damage. If the power is turned OFF to the valve, (a switch located just above the valve actuator) the valve is spring closed, and will seal the reactor, and everything upstream. This equipment will be replaced by the contractor once a replacement is available. | Oak Ridges Air Management Facility | 2025-11-20
WW-CEAST | November | -On site to perform a station check. -Entered station readings into SharePoint. -Odour Control System operating in Emergency Mode, Fan 2 in manual off. NAC performing work on bubble dampers on Fan 2 train. -Nutrient tank at 3/4 full. -Tested outlet air exhaust stack sample port using MSA gas monitor with pump probe for several minutes, reading 0ppm for H2S. | Oak Ridges Air Management Facility | 2025-11-17
WW-CEAST | November | Remotely assisted AECOM testing. Changed Fan 1 and 2 inlet pressure setpoint from -2.15 kpa to -2.18 kpa. Noticed media diff kpa is twice higher for Train 1/Fan 1, notified AECOM. Discharge stack airflow fluctuating around 9200 m3/hr | Oak Ridges Air Management Facility | 2025-11-14
WW-CEAST | November | On site to assist with multiple testing scenario with AECOM. Tested Train 1 running only scenario. Emergency operating mode alarm kicked in. Fan 1 successfully operating based on emergency mode setpoint. Fan 1 speed @ 71%, suction press @ -1.36 kpa, stack discharge @ 5100 m3/hr Tested Train 2 running only scenario. Emergency operating mode alarm kicked in. Fan 2 successfully operating based on emergency mode setpoint. Fan 2 speed @ 68%, suction press @ -1.17 kpa, stack discharge @ 5200 m3/hr | Oak Ridges Air Management Facility | 2025-11-12
WW-CEAST | November | AECOM & CD have requested further increase from -1.5kPa to -2.0kPa and now another further increase to -2.15kPa to attempt to acheive 9100m3/hr. Currently Fan Speeds @ 77% # 1 & 72% #2 w/ Exhaust Stack Flows @ 9000m3/hr. | Oak Ridges Air Management Facility | 2025-11-05