## Aurora SPS
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS
12134179 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12134179 | 5 | 2025-11-03 10:02 | 2025-11-03 08:15 | Philip Romito (WW-CEAST) @ Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility - AUSSMP Date Work Completed: 2025-11-03 08:15 ————————————————————— -On site to perform a station check. -Entered station readings into SharePoint. -Checked drywell and air compressors. -Pump 1 placed OOS over the weekend due to MV2 valve faults. Tested Pump 1 MV2 valve locally with no issues. Test ran Pump 1 with no issues. Left Pump 1 in auto, duty 1. -Checked screen room, raked rag bin, topped up bar screen oil, cleaned rags off conveyors. -Test ran Pump 3 in manual for one duty cycle, Flowmeter still waiting on parts for replacements, no other issues noted with pump 3. Pummp 3 remains OOS, but can be run in an emergency. -All dump pad lines are in auto and available. ————————————————————— • Attachments: 0
12137667 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12137667 | 3 | 2025-11-04 07:56 | 2025-11-04 07:55 | Philip Romito (WW-CEAST) @ Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility - AUSSMP Date Work Completed: 2025-11-04 07:55 ————————————————————— -On site to assist maintenance team with repairs to wet well equalization valve pedestal. -Isolated Wet Well 1 and placed OOS to facilitate repairs to equalization valve. Monitored flows and levels throughout the day. -Responded to Line 1 Overtorque alarm this morning at the dump pad. Alarm came in at 05:25am. Isolated line and back flushed large amount of rags. Testes valve with no issues, cleared alarms, returned Line 1 to service. -Placed steel bin back outside of dump pad. Cleaned grating, drain channels, and walkways. Cleaned out drain pit behind building as well. -Maintenance has finished work on valve for today, but will need to return another day in the future. Equalization valve is now operational again and has been opened. Opened isolation gates back up and returned Wet Well 1 to service, along with pumps 1 and 2. -Pump 3 remains OOS due to Flowmeter fault, but can be used in an emergency. ————————————————————— • Worked With: Matthew Turner, Terry Cantwell • Attachments: 0
12153895 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12153895 | 3 | 2025-11-10 08:03 | 2025-11-10 08:03 | Philip Romito (WW-CEAST) @ Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility - AUSSMP Date Work Completed: 2025-11-10 08:03 ————————————————————— -On site to perform a station check. -Entered station readings into SharePoint. -Checked drywell and air compressors. -Found Air Compressor 1 with the air filter housing broken off of the unit. Placed the compressor to local off/OOS and created work request for maintenance team to repair issue. -Checked screen room, changed out rag bin, bar screen oil full. -Checked dump pad, found Line 3 with an outstanding Overtorque alarm from 14:35 on Nov. 7. Isolated and flushed line, cleared and reset fault. -Inspected heat trace at dump pad, all heat trace working properly. -Pump 3 remains OOS with Flowmeter fault, but can be run in an emergency. -Air Compressor 1 OOS. ————————————————————— • Attachments: 0
12154088 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12154088 | 1 | 2025-11-10 11:51 | 2025-11-10 11:49 | Bill Van Bakel (WW-MAINT) @ Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility - AUSSMP Date Work Completed: 2025-11-10 11:49 ————————————————————— On site to repair the air filter on the compressor. The compressor is back in duty ————————————————————— • Attachments: 0
12165665 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12165665 | 1 | 2025-11-13 15:42 | 2025-11-13 12:30 | Philip Romito (WW-CEAST) @ Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility - AUSSMP Date Work Completed: 2025-11-13 12:30 ————————————————————— -On site to investigate booster pump pressure issues at dump pad. Tested booster pump operation under various scenarios, but did not notice any obvious issues. Booster pumps working as intended, but take a very long time to pressurize tank. Booster pumps are reaching 690kpa stop setpoint, but no trucks on site this afternoon as well. Will relay findings to operations team and CPD. -Replaced rag bins following pick up, steel bin removed from screen room. ————————————————————— • Worked With: Terry Reed • Attachments: 0
12177575 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12177575 | 5 | 2025-11-19 08:04 | 2025-11-19 08:04 | Philip Romito (WW-CEAST) @ Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility - AUSSMP Date Work Completed: 2025-11-19 08:04 ————————————————————— -On site to complete work orders. -Station check completed, readings entered into SharePoint. -Checked drywell. -Air compressors, inspection and cleaning completed. -Checked screen room, raked rag bin, cleaned conveyors, bar screen oil topped up. -Dump pad inspection and cleaning completed, cleaned grating and drain trough, cleaned walkways, cleaned out drain pit behind building. -Placed silver steel bin back down by dump pad. -Multiple haulers mentioned concerns regarding dump pad line valves closing too early before loads were fully emptied. Relayed concerns to CPD/PCS/by-law teams. -Ran Pump 3 for a couple duty cycles in manual. -Pump 3 remains OOS with Flowmeter fault, can be run in emergencies. -WW maintenance team on site to look at unit heaters 3 and 4 in screen room. Both unit heaters were placed OOS for motor overloading, due for replacement. ————————————————————— • Worked With: Brent Ste-Croix, Satnam Mann • Attachments: 0
12181109 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12181109 | 1 | 2025-11-20 14:17 | 2025-11-20 09:15 | Philip Romito (WW-CEAST) @ Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility - AUSSMP Date Work Completed: 2025-11-20 09:15 ————————————————————— -On site to complete consolidated surge tank inspection work orders. -Surge tank and system inspection completed. -Surge tank valve and actuator, exercise and inspection completed. Exercised all valves, SURG_TK2_MV2 East valve kept getting Overtorque Alarms around 90% open. Issue had previously been noted and work request created, will follow-up on status of work request. -Surge tank drain line inspection completed. -Surge tank transmission line flushing completed. Flushed out both surge tank transmission lines. Cleared blockages in both transmission drain lines. Cleaned floors and reset alarms. -Checked dump pad while on site, no issues noted, all lines available. -Pump 3 remains OOS with Flowmeter fault, but can be used in an emergency. ————————————————————— • Worked With: Terry Reed • Attachments: 0

## Leslie SPS
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS
12142743 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12142743 | 4 | 2025-11-05 09:47 | 2025-11-05 09:46 | Marcos Tungcol (WW-CEAST) @ Markham Leslie Pumping Station - LSSS Date Work Completed: 2025-11-05 09:46 ————————————————————— On site completed work orders. Station Check (See details on SharePoint) Pumps 2, 3, 5 and 6 available in auto duty rotation every 4 hours. Pumps 1 and 4 out of service for repairs. All standby power generators available in auto. Drained condensates from the surge tanks air compressors. Blew down bubblers. Bar Screen Bin Removal and Replacement - Switched rag bin, pushed out rag bins for pick up by Miller Waste tomorrow. Cleaned/hosed down bar screen room. Odour Control Scrubber System Inspection and Filter Cleaning JHSC Health and Safety Inspection - Lights inside the elevator not working. Archibus created for PS. ————————————————————— • Attachments: 0
12171546 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12171546 | 3 | 2025-11-17 09:46 | 2025-11-17 09:45 | Marcos Tungcol (WW-CEAST) @ Markham Leslie Pumping Station - LSSS Date Work Completed: 2025-11-17 09:45 ————————————————————— On site completed Station Check (See details on SharePoint) Pumps 2, 3, 5 and 6 available in auto duty rotation every 4 hours. Pumps 1 and 4 out of service for repairs. All standby power generators available in auto. Switched pump duty of sump pumps. Found SCADA OIT @ B2 level with blank monitor Informed PCS/SCADA staff (Yash). Created work order request to check it. Drained condensates from the surge tanks air compressors. Cleared/reset bubblers alarm happened last Nov. 15th. Observed no unusual issue with the bubblers. Blew down bubblers, cleared/reset alarms afterwards. Pumps 2 and 5 VFD filters too dirty - replaced filters. Checked dry well, ok. Cleared/reset South Forcemain Valve (RSP_FORM2_MV1) fault alarm. It is now in 100% open, as normal operation. Checked bar screens. Switched rag bin. Screw press drain clogged. Unclogged said drain. Cleaned/hosed down bar screen room. ————————————————————— • Attachments: 0

## Bogart SPS
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS
12193563 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12193563 | 1899-12-31 | 2025-11-26 15:18 | 2025-11-26 10:30 | Terry Reed (WW-CEAST) @ Newmarket Bogart Creek Sewage Pumping Station - NMSSHS Date Work Completed: 2025-11-26 10:30 ————————————————————— Met with Town of Newmarket water to figure out the water meter,, they tried a few things but are going to half to re schedule to run a new line or replace meter ————————————————————— • Attachments: 0

## Newmarket SPS
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS
12134217 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12134217 | 1 | 2025-11-03 10:50 | 2025-11-03 10:39 | Bill Van Bakel (WW-MAINT) @ Newmarket Sewage Pumping Station & Equalization Tank - NMSSBP Date Work Completed: 2025-11-03 10:39 ————————————————————— On site for bar screen 1oos found missing roller skates and one missing 2 bolts. Replaced the roller and put it back in auto. Also open the channel ————————————————————— • Worked With: Christian Streef, Terry Reed • Attachments: 0
12134298 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12134298 | 1 | 2025-11-03 12:02 | 2025-11-03 10:28 | Terry Reed (WW-CEAST) @ Newmarket Sewage Pumping Station & Equalization Tank - NMSSBP Date Work Completed: 2025-11-03 10:28 ————————————————————— Helped Bill and Christian get bar screen 1 running again,, opened up channel gate for bar screen 1 after turning it back on (took LOTO off panel switch.) - Christian also greased all the sprockets on the bar screen, levelled off bin and pushed the empty one back into the screening room. Emptied garbage cans in the building into the rag bin. Took station readings and entered into SharePoint,, reviewed trends - all OK. ————————————————————— • Attachments: 0
12146783 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12146783 | 4 | 2025-11-06 13:59 | 2025-11-06 07:45 | Philip Romito (WW-CEAST) @ Newmarket Sewage Pumping Station & Equalization Tank - NMSSBP Date Work Completed: 2025-11-06 07:45 ————————————————————— -On site to complete work orders. -Consolidated wet well work orders completed. -Bar screen cleaning and lubrication completed. -Screw conveyor cleaning and lubrication completed. -Sluice gate valve exercises completed, all valves fully exercised. -Wet well cleaning and inspection completed. -Wet well valve exercises completed. -Tipping bucket operational checks completed, tested each bucket multiple times, hosed down inside of north EQ to remove bugs and spider webs. -Consolidated surge tank inspection work orders completed: -Surge tank and system inspection completed. -Surge tank valve exercises and inspection completed. -Surge tank drain valve exercise and flush completed. -Surge tank transmission lines flushed. -Facility overflow inspection completed. -Wet well high level alarm test completed and confirmed by ROC. -Pump 2 remains OOS for repairs. ————————————————————— • Worked With: Terry Reed • Attachments: 0
12197564 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12197564 | 11 | 2025-11-28 09:01 | 2025-11-28 09:00 | Marcos Tungcol (WW-CEAST) @ Newmarket Sewage Pumping Station & Equalization Tank - NMSSBP Date Work Completed: 2025-11-28 09:00 ————————————————————— On site completed work orders. Station Check (See details on SharePoint) All pumps available in timed auto duty rotation every 3 hours, except, pump 2, which is still out of service for repair. Pump taken out of site. Standby power generator available in auto. Checked dry well, ok. Checked bar screens. Levelled out the bin in the screening room and emptied the top of the auger. Cleaned/hosed down the floor and flushed out the drain hose as well as the screen for the auger. Pushed rag bin back inside the screen room after picked up by Miller Waste yesterday. Consolidated Monthly Dry Well Pump Floor Inspection Dry Well Flood alarm Test - received and confirmed by ROC. Sump Pit Inspection Auto Dialer Alarm Test - 3 times tested but not received by ROC. Created work order (W11475581) to CMS to check the issue. Air Compressor Inspection High Low Temp Alarm Test - Station don’t have the capability to test the high low temperature alarm, however, it will alarm when the temperature is above or below temperature setpoints. RS Pump and Motor Inspection Pump 1 - @ 0% speed: 120 L/s, 139 kPa, 108 Amps, 617 V, 39 Hz; @35% speed: 230 L/s, 158 kPa, 153 Amps, 617 V, 46 Hz Pump 2 - Out of service. Pump 3 - @ 0% speed: 156 L/s, 135 kPa, 126 Amps, 371 V, 769 RPM, 39 Hz; @ 35% speed: 256 L/s, 150 kPa, 181 Amps, 445 V, 920 RPM, 46 Hz Pump 4 - @ 0% speed: 140 L/s, 125 kPa, 99 Amps, 615 V, 39 Hz; @ 35% speed: 239 L/s, 122 kPa, 155 Amps, 614 V, 46 Hz Check Valves Inspection ————————————————————— • Attachments: 0

## Mt. Albert WRRF
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS
12129872 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12129872 | 1 | 2025-11-01 17:59 | 2025-11-01 17:51 | Chris Rodie (WW-CEAST) @ Mount Albert Water Resource Recovery Facility - MTSP Date Work Completed: 2025-11-01 17:51 ————————————————————— -on site to fix sand filter 1 module 2 which was not backwashing sand properly -this is in response to the high total phosphorus in the comp sample for the lab earlier today, which was 0.088, which is above the objective value of 0.070. -backwashing lance which cleans sand was clogged, pulled lance, cleared any bigger particles and reinstated lance, restored air flow and backwashing of sand looked normal, this was my response to being above the internal objective, sample was still below compliance objective of 0.1 mg/L TP -will return tomorrow for the Sunday lab, will check composite sample and see if Total phosphorus is trending downward -sand filter 1, module 1 seems to be backwashing but slightly underperforming as well, perhaps this week it can be investigated as well -currently both module 1 and 2 are backwashing -notified ROC of work, had CMU5 W11407901 for sand filter 1 maintenance which I returned to site for -W11407732 for Saturday Lab earlier in the day ————————————————————— • Attachments: 0
12130025 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12130025 | 4 | 2025-11-02 11:21 | 2025-11-02 11:21 | Philip Romito (WW-CEAST) @ Mount Albert Water Resource Recovery Facility - MTSP Date Work Completed: 2025-11-02 11:21 ————————————————————— -On site for lab analysis and sludge handling. -Completed lab analysis and entered results into SharePoint. -Decanted STT to headworks, emptied tank into SHT. -Added one bag of soda ash to each aeration tank. -Batch wasted 8m3, ran RAS pump 1 at 100% speed when returning to service. -Found both modules in sand filter 1 clogged with sand piling up. Underdrain blocked around both air lifts. Cleared out excess sand, pulled air lifts, cleared out under drains. Both sand filter cells in operation and working normally now. -Final effluent total phosphorous value elevated at 0.091mg/L. Batch wasting completed today, sand filter blockages cleared out, alum dosing levels still elevated at 195mg/l in aeration and 15mg/l in filter. -Clarifier 1 OOS, WAS pump 2 OOS, RAS pumps 2 and 3 OOS. ————————————————————— • Attachments: 0
12138062 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12138062 | 6 | 2025-11-04 11:17 | 2025-11-04 11:16 | Daniel Kim (WW-CEAST) @ Mount Albert Water Resource Recovery Facility - MTSP Date Work Completed: 2025-11-04 11:16 ————————————————————— Received alum delivery 1.25m -> 3.74m. Checked inlet channel level flatline issue noted by ROC. Checked the inlet chamber and no obstruction/issues found which would have caused the flatlining issue. Created CMU2 for INST. RAS pump 3 will remain OOS overnight. RAS 1 and 2 back in service Put clarifier 1 back in service. Ras 2 dedicated to clarifier 1 and Ras 1 dedicated to clarifier 2 Approximately 86m3 of clarifier effluent diverted to lagoon between 2:00pm and 3:30pm for clarifier maintenance ————————————————————— • Worked With: Barry Middleton • Attachments: 0
12146431 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12146431 | 4 | 2025-11-06 08:20 | 2025-11-06 08:20 | Barry Middleton (WW-CEAST) @ Mount Albert Water Resource Recovery Facility - MTSP Date Work Completed: 2025-11-06 08:20 ————————————————————— Weather today Partly cloudy and 1 Celsius -On site to complete work orders W11340330, W11352649, W11352454, W11351269, W113352441, W11352428. -Completed in-house lab analysis and station check. -Entered lab and station readings into SharePoint. -Post filtration/UV channel hose down. -Post aeration alum mixing chamber clean out. -RAS/WAS inlet channel inspection and hose down. -Reset composite sampler for tomorrow. -Ran RAZ pumps #1 and #2 at 100% to clear them out for a bit - all back to auto as well as speed back to auto. -Added two bags of soda ash to each aeration tank. -Decanting STT into the Headworks. -Transferred the sludge and processing. -Batch wasted 10m3 from Clarifier #1 and #2. -Ras pump #3 in manual OOS. ————————————————————— • Attachments: 0
12158011 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12158011 | 2 | 2025-11-11 14:11 | 2025-11-11 14:10 | Barry Middleton (WW-CEAST) @ Mount Albert Water Resource Recovery Facility - MTSP Date Work Completed: 2025-11-11 14:10 ————————————————————— Weather today Snow and -3 Celsius -On site to complete work orders W11360441, W11363719, W11362736, W11364311, W11362238, W11362347, W113362320, W11361211. -Completed station check. -Entered station readings into SharePoint. -Collected weekly sewage samples at 8:40 am under W11363719. -Reset composite sampler for weekend sampling. -Ran RAZ pumps #1 and #2 at 100% to clear them out for a bit - all back to auto as well as speed back to auto. -Added two bags of soda ash to each aeration tank. -Sand filter filter-reject drain line flush. -Grit tank Blowers 1 and 2 inlet filter, pulleys, and oil check. -Sludge holding tank Blowers 1 and 2 inlet filter, pulleys, and oil check. -Sump Pumps maintenance. -Odour control system OOS. -Ras pump #3 in manual OOS. ————————————————————— • Attachments: 0
12167939 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12167939 | 1 | 2025-11-14 12:57 | 2025-11-14 12:57 | Barry Middleton (WW-CEAST) @ Mount Albert Water Resource Recovery Facility - MTSP Date Work Completed: 2025-11-14 12:57 ————————————————————— Weather today Clear and 0 Celsius -On site to complete work orders W11360441, W11375811, W11262387, W11362373. -Completed in-house lab analysis. -Entered lab readings into SharePoint. -Post aeration alum mixing chamber clean out. -RAS Pump 1, 2, and 3 inspection. -WAS Pump 1 and 2 inspection. -Reset composite sampler for weekend. -Ran RAZ pumps #1 and #3 at 100% to clear them out for a bit - all back to auto as well as speed back to auto. -Added two bags of soda ash to each aeration tank. -Decanting STT into the Headworks. -Transferred the sludge and processing. -Batch wasted 20m3 from Clarifier #1. -Ras pump #3 back in service. -Odour control system OOS. ————————————————————— • Attachments: 0
12189945 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12189945 | 3 | 2025-11-25 14:07 | 2025-11-25 11:30 | Philip Romito (WW-CEAST) @ Mount Albert Water Resource Recovery Facility - MTSP Date Work Completed: 2025-11-25 11:30 ————————————————————— -On site to perform a station check. -Entered readings into SharePoint. -Verified sand filter operation and alum dosing. -Added a second bag of soda ash to each aeration tank. -OCU OOS due to motor failure. ————————————————————— • Worked With: Kevin Shaji • Attachments: 0
12193467 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12193467 | 1 | 2025-11-26 14:14 | 2025-11-26 14:13 | Barry Middleton (WW-CEAST) @ Mount Albert Water Resource Recovery Facility - MTSP Date Work Completed: 2025-11-26 14:13 ————————————————————— Weather today Overcast and 9 Celsius -On site to complete work orders W11396438, W11401734, W1145767, W11459168, W11361271, W11362295, W11361283, W11362692. -Completed station check. -Entered station readings into SharePoint. -Operator support for headworks building channel coating inspection. -Travelling screen maintenance. -Grit vortex 1 and 2 maintenance. -Screw Press maintenance. -Reset composite sampler for tomorrow. -Ran RAZ pumps #1 at 100% to clear them out for a bit - all back to auto as well as speed back to auto. -Added two bags of soda ash to each aeration tank. -Decanting STT into the Headworks. -Transferred the sludge and processing. -Clarifier 2 is now isolated, also partially drained and put out of service to accommodate the works to be done by contractor. -Odour control system OOS. -RAS Pump 1 and WAS Pump 1 in manual off and out of service. ————————————————————— • Attachments: 0

## King City SPS
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS

## Schomberg WRRF
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS
12193246 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12193246 | 8 | 2025-11-26 09:09 | 2025-11-26 14:30 | Marcus Remonde (WW-WEST) @ Schomberg Water Resource Recovery Facility - SHSP Date Work Completed: 2025-11-26 14:30 ————————————————————— In to Complete Scheduled WOs. Notified ROC. Opened Clarifier #1 RAS/WAS Manual Suction Valve. Closed RAS/WAS Suction Header Manual Interconnect Valve for Pump Dedication. RAS Pump #1 Manual On @ 100% Speed for Clarifier #1 Drawdown. RAS Pump #2 Manual On @ 7% Speed to Maintain Clarifier #2 RAS Service Flow. Lowered and Activated Decant Pump. Experienced Power Loss Event Whilst On-site, Generator Activated Automatically. Utility Power Restored and Transferred with No Issues. Reviewed SCADA, Restored Duties and Cleared Associated Alarms. Decant Complete, Raised and Deactivated Decant Pump. Clarifier #1 Drawdown Process Complete. Returned RAS/WAS Suction Valves and Header to Service. RAS Pumps #2-3 in Auto and Duty, Pump #3 in Auto, OOS. Completed Grit Dewatering Screws #1 and 2 Inspections and Service. Drained and Replaced Oil Reservoirs. Automatic Grease Applicators OK. Returned to Service. Completed Screenings Compactor Inspection and Service. Drained and Replaced Oil Reservoirs. Flushed Drainage Line. Returned to Service. Completed Aer. DO Sensor Maintenance. Placed Probes in Calibration Mode. Cleaned and Inspected Units, No Issues Found. Returned to Service. ————————————————————— • Attachments: 0
12187458 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12187458 | 4 | 2025-11-24 07:20 | 2025-11-24 07:30 | Marcus Remonde (WW-WEST) @ Schomberg Water Resource Recovery Facility - SHSP Date Work Completed: 2025-11-24 07:30 ————————————————————— Remotely Placed Supernatant Drain Valve in Manual Open. Remotely Rotated WAS Pump Duties. Pump #1 Manual Off, Pump #2 in Auto. Remotely Rotated RAS Pump Duties. Pump #3 in Duty #1, Pump #1 in Duty #3, OOS. Remotely Placed Scum Valve in Manual Discharge. Activated Scum Pump #2 in Manual. Scum Tank Drawdown Complete. Returned All to Auto and Service. Decant Complete. Remotely Closed Supernatant Valve in Manual. ————————————————————— • Attachments: 0 • [REMOTE ENTRY]
12180830 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12180830 | 7 | 2025-11-20 08:52 | 2025-11-20 14:35 | Marcus Remonde (WW-WEST) @ Schomberg Water Resource Recovery Facility - SHSP Date Work Completed: 2025-11-20 14:35 ————————————————————— In to Complete Scheduled WOs. Notified ROC. Lowered and Activated Decant Pump. Decant Complete, Raised and Deactivated Decant Pump. Opened Clarifier #1 RAS/WAS Manual Suction Valve. Closed RAS/WAS Suction Header Manual Interconnect Valve for Pump Dedication. RAS Pump #1 Manual On @ 100% Speed for Clarifier #1 Drawdown. RAS Pump #3 Manual On @ 40% Speed to Maintain Clarifier #2 RAS Service Flow. Adjusted Clarifier Eff. Alum Dosage Set-point Based On In-House and External Laboratory Results: 15 —> 18 mg/L. GFL On-site for Sludge Load. Sludge Transfer Valve Local Open, Transferred Thickened Sludge. Transfer Valve Returned to Manual Closed. Cleared Associated Alarm. Completed Filter Inlet TSS Sensor Inspection. Placed Unit in Calibration Mode Locally, Cleaned Probe. No Issues Found. Returned to Service. Clarifier #1 Drawdown Process to be Continued. Returned RAS/WAS Suction Valves and Header to Service. RAS Pumps #1-2 in Auto and Duty, Pump #3 in Auto, OOS. ————————————————————— • Attachments: 0
12177672 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12177672 | 9 | 2025-11-19 09:48 | 2025-11-19 14:20 | Marcus Remonde (WW-WEST) @ Schomberg Water Resource Recovery Facility - SHSP Date Work Completed: 2025-11-19 14:20 ————————————————————— In to Complete Scheduled WOs. Notified ROC. Lowered and Activated Decant Pump. Decant Complete, Raised and Deactivated Decant Pump. Sludge Transfer Valve Manual Open, Transferred Thickened Sludge. Transfer Valve Returned to Manual Closed. Opened Clarifier #1 RAS/WAS Manual Suction Valve. Closed RAS/WAS Distribution Header Manual Interconnect Valve for Pump Dedication. RAS Pump #1 Manual On @ 100% Speed for Clarifier #1 Drawdown. RAS Pump #3 Manual On @ 45% Speed to Maintain Clarifier #2 RAS Service Flow. Created Follow Up WO to Address Aer. Blowers #2 and 3 Malfunctioning Vacuum Gauges —> W11455733. Completed Debris Auger Service and Inspection. Drained and Replaced Oil. No Issues Found. Returned to Service. Cleared Associated Alarms. Completed WAS Pump #1 Inspection due to Previous WAS Lo/LoLo Flow Alarms. Removed Suction Line and Check Valve Cover. Cleared Obstructions and Debris, Flushed Units. Returned to Service and Tested in Manual with No Issues. Cleared Associated Alarms. Clarifier #1 Drawdown Process to be Continued. Returned RAS/WAS Suction Valves and Header to Service. RAS Pumps #1-2 in Auto and Duty, Pump #3 in Auto, OOS. Completed Aer. DO Sensor Maintenance. Placed Probes in Calibration Mode. Cleaned and Inspected Units, No Issues Found. Returned to Service. ————————————————————— • Attachments: 0
12171592 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12171592 | 8 | 2025-11-17 10:41 | 2025-11-17 14:20 | Marcus Remonde (WW-WEST) @ Schomberg Water Resource Recovery Facility - SHSP Date Work Completed: 2025-11-17 14:20 ————————————————————— In to Complete Scheduled WOs. Notified ROC. Rotated WAS Pump Duties. Pump #2 Manual Off, Pump #1 in Auto. Rotated RAS Pump Duties. Pump #1 in Duty #1, Pump #3 in Duty #3, OOS. Adjusted Auto Wasting Time Frame. WAS Pump Start: 14:00 —> 15:00. Completed Sludge Blower Building Room Supply Fan Filter Replacement with No Issues. Found UV Bank #1 (A) with Outstanding Local Alarm. Tested Unit in Manual. Rack #5 Showing No Power. Placed Bank in Manual Off. Notified On-site Maint. Electrician. Electrical Inspection of UV Bank #1 (A), Rack #5 Rendered a Blown Fuse. Fuse Replaced and Bank Tested in Manual with No Issues. Returned to Auto and Service. Cleared Associated Local Alarm. Completed Filter Reject Pumps #1 and 2 Inspections with No Issues. Tested Filter Reject Sump Hi Level Float, Confirmed Reception by the ROC. Returned All to Service and Cleared Associated Alarms. Completed Sludge Holding Tank Overflow Manual Valve Exercise with No Issues. Returned to Service. Completed Sludge Holding Tank Hi Float Alarm Test. Confirmed Reception by the ROC. Returned to Service. Cleared Associated Alarm. ————————————————————— • Worked With: David Dougherty • Attachments: 0
12149937 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12149937 | 1 | 2025-11-07 18:05 | 2025-11-07 18:02 | Lance Johnson (LEADS) @ Schomberg Water Resource Recovery Facility - SHSP Date Work Completed: 2025-11-07 18:02 ————————————————————— Responding to RAS and WAS pump low flow alarms. Closed valve from clarifier 1 and opened valve between pumps to put pump 1 as duty 1 and pump 2 as duty 2. Pump 3 plugged and out of service for the weekend. ————————————————————— • Attachments: 0
12149604 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12149604 | 11 | 2025-11-07 08:44 | 2025-11-07 16:05 | Marcus Remonde (WW-WEST) @ Schomberg Water Resource Recovery Facility - SHSP Date Work Completed: 2025-11-07 16:05 ————————————————————— In to Complete Scheduled WOs. Conducted Clarifier #1 Weir, Scum Trough and Launder Cleaning. Filter Inlet Valves Closed, Filter Diversion Valve to Lagoon Open @ 08:50. Lowered and Activated Decant Pump. Flushed and Recirculated Scum Tank. Placed Scum Valve in Manual Discharge and Activated Scum Pump #1 in Manual. Scum Tank Drawdown Complete. Returned All to Auto and Service. Cleaning Complete. Filter Inlet Valves Open, Filter Diversion Valve Closed @ 10:35. Diverted Approx. 65 m3 or 65 000 L to the Lagoon. Reported to York Incident Notification. Rotated Service Clarifier for Continued CPD and Contractor Work. Clarifier #2 Inlet Valve Manual Open, Aer. Tanks #1 and 2 Outlet Interconnect Gate Valve Manual Open, Clarifier #1 Inlet Valve Manual Closed. Placed RAS Pump #3 in Manual, Manual Speed @ 100% for Clarifier #1 Drawdown Process. RAS Pump #2 Manual Off. Decant Complete, Raised and Deactivated Decant Pump. Sludge Transfer Valve Manual Open, Transferred Thickened Sludge. Transfer Valve Returned to Manual Closed. Activated Aer. Tank and Clarifier Effluent Alum Line Hot Water Dosing Based on Seasonal Temperatures. Contractor On-site to Complete Clarifier #2 Drive Rake Modifications. Unit Deactivated for the Duration of Contractor Work. Dedicated RAS and WAS Pump #1 to Clarifier #1. Activated RAS Pump #1 in Manual, Manual Speed @ 100%, RAS Pump #3 Manual Off. Rotated WAS Pump Duties. Pump #1 Manual Off, Pump #2 in Auto. WAS Pump #2 and RAS Pumps #2 and 3 Dedicated to Clarifier #2. Completed Filter Inlet TSS Sensor Inspection. Placed Unit in Calibration Mode Locally, Cleaned Probe. No Issues Found. Returned to Service. WAS Pump #2 in Local On for Testing Purposes. Returned to Auto and Service. Placed RAS Pumps #2 and 3 in Duty and Auto, RAS Pump #3 Active in Duty #1. Clarifier #1 Drive Rake Over-torque Alarm Active, Notified by ROC. Cleared Alarm and Tested Unit with No Issues. Contractor Work Complete. Placed Clarifier #1 OOS and Clarifier #2 in Service. Cleared Associated Alarm. ————————————————————— • Attachments: 0

## Black Creek SPS
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS

## Nobleton WRRF
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS
12183722 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12183722 | 2 | 2025-11-21 11:01 | 2025-11-21 10:58 | Daniel Hirstwood (LEADS) @ Nobleton Water Resource Recovery Facility - NBSP Date Work Completed: 2025-11-21 10:58 ————————————————————— Collect samples and complete in house labs Input labs and data into ace sheets No decant on thickening tank, transferred to holding tank. RAS pump 3 manual off. Auto batch wasting enabled to waste 50m3 total from clarifier 1. Clarifier 2 remains OOS. Complete station round and data collection. Added 1x25 kg bag to each aeration basin. Set final effluent composite to run on Sunday for Monday samples ————————————————————— • Attachments: 0 | on SCADA no longer issue
1

## Kleinburg WRRF
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS
12177618 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12177618 | 2 | 2025-11-19 08:48 | 2025-11-19 08:48 | Matthew Turner (WW-MAINT) @ Kleinburg Water Resource Recovery Facility - KBSPF Date Work Completed: 2025-11-19 08:48 ————————————————————— Onsite to complete aeration tank repair. Work completed. Allow parts to cure. Operations can then partially fill tank and inspect for any additional leaks. ————————————————————— • Worked With: Terry Cantwell, Bill Van Bakel • Attachments: 0
12165601 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12165601 | 1 | 2025-11-13 14:07 | 2025-11-13 14:05 | Young Jung (WW-WEST) @ Kleinburg Water Resource Recovery Facility - KBSPF Date Work Completed: 2025-11-13 14:05 ————————————————————— - Shelved KBSPR_AER_TK2_AIR2_OOR and KBSPR_AER_TK2_NIT_FLT due to aeration tank being OOS for ladder installation and maintenance work ————————————————————— • Attachments: 0 • [REMOTE ENTRY]
12150143 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12150143 | 6 | 2025-11-08 15:52 | 2025-11-08 15:51 | Lance Johnson (LEADS) @ Kleinburg Water Resource Recovery Facility - KBSPF Date Work Completed: 2025-11-08 15:51 ————————————————————— On site for bar screen and press no power alarms. Found this to be the case. Called on-call electrician. Added 8 bags soda ash to hopper. Kyle Rae found heat trace for the screw was causing power fuses to blow in the screen and press control panel. Turned heat trace off. Will create work order to have heat trace repaired. (W11428320) ————————————————————— • Attachments: 0
12150148 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12150148 | 1 | 2025-11-08 17:38 | 2025-11-08 17:33 | Kyle Rae (W-MAINT) @ Kleinburg Water Resource Recovery Facility - KBSPF Date Work Completed: 2025-11-08 17:33 ————————————————————— On site with operations to investigate loss of power to Mechanical Bar Screen panel. Found opened fuse feeding 120v control transformer. Further investigation found cause to be faulty heat trace. Heat trace currently inoperative and requires investigation and possible replacement. Mechanical Bar Screen panel reenergized and returned to normal operation. ROC notified. ————————————————————— • Attachments: 0

## Humber SPS
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS

## Pine Valley
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS

## Holland Landing SPS
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS
12183705 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12183705 | 1 | 2025-11-21 10:35 | 2025-11-21 10:31 | Bill Van Bakel (WW-MAINT) @ Holland Landing Sewage Pumping Station - HLSSBS Date Work Completed: 2025-11-21 10:31 ————————————————————— On site for check valve 3 pressure leak. Found no external leaks so I will order a new cylinder ————————————————————— • Attachments: 0

## Joe Dales SPS
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS | 1

## Keswick WRRF
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS
12138213 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12138213 | 3 | 2025-11-04 15:10 | 2025-11-04 15:09 | Tyson Cornish (WW-NORTH) @ Keswick Water Resource Recovery Facility - KSSP Date Work Completed: 2025-11-04 15:09 ————————————————————— Performed facility station check Completed Lab analysis: Data in Sharepoint Collected Weekly Samples: Sewage (W11343583) Collected Monthly Samples: Alkalinity (W11343569) and Sludge (W11343194) Decanted Sludge holding tanks: 2 & 3 Transferred Sludge holding tank: 2 Inspected headworks: leveled grit bin and raked bar screen Added 10 bags of Soda Ash Rotated headworks screening channel duty Duty 1 = Channel 2 Duty 2 = Channel 1 Hot water tank OOS- Notified property services ————————————————————— • Attachments: 0
12187567 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12187567 | 3 | 2025-11-24 09:42 | 2025-11-24 09:41 | Matthew Turner (WW-MAINT) @ Keswick Water Resource Recovery Facility - KSSP Date Work Completed: 2025-11-24 09:41 ————————————————————— Investigate hypo leak, tightened flange bolts leak tested with water. Flange still has leak. Drain water from tank and remove tank bulk head to investigate further. Removed bulk head new gasket and hardware required. Hypo tank OOS until repair is completed ————————————————————— • Worked With: Terry Cantwell • Attachments: 0
12195166 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12195166 | 1 | 2025-11-27 12:40 | 2025-11-27 12:38 | Terry Cantwell (WW-MAINT) @ Keswick Water Resource Recovery Facility - KSSP Date Work Completed: 2025-11-27 12:38 ————————————————————— On site to gather information for sodium hypo tank fitting. Found tank manufacturer and serial number for the tank. Contacted manufacturer and they will respond with availability of parts once I send follow-up photos of parts. ————————————————————— • Attachments: 0

## Queensville SPS
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS
12149632 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12149632 | 1 | 2025-11-07 09:19 | 2025-11-07 09:15 | Bill Van Bakel (WW-MAINT) @ Queensville West Sewage Pumping Station - QVSSSC Date Work Completed: 2025-11-07 09:15 ————————————————————— On site for the sump pump hi alarm. Relocated the first float so it won’t hang up with the other floats found the second and third float are not floating. I will have a electrician replace them ————————————————————— • Attachments: 0
12180866 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12180866 | 1 | 2025-11-20 09:47 | 2025-11-20 09:46 | Neil Ott (WW-NORTH) @ Queensville West Sewage Pumping Station - QVSSSC Date Work Completed: 2025-11-20 09:46 ————————————————————— Attended for station check Recorded station readings in rounds sheet Checked dry well - p.3 running in duty Channel grinder OOS Reviewed SCADA/trends. ————————————————————— • Attachments: 0

## Sutton WRRF
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS
12154169 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12154169 | 3 | 2025-11-10 13:54 | 2025-11-10 13:49 | Chase James (WW-NORTH) @ Sutton Water Resource Recovery Facility - SUSP Date Work Completed: 2025-11-10 13:49 ————————————————————— Plant checks completed Increase wasting on SBR 1&2 from 120sec to 240sec on both Fill lagoon chamber and back flush inlet due to low flows Disconnect sludge pad hose for haulers due to frozen lines Made W/O for sludge heat trace pad Decant and transfer sludge Complete lab and enter data into SharePoint Plug in heat lines on decant arms and air valves ————————————————————— • Attachments: 0
12174543 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12174543 | 5 | 2025-11-18 10:24 | 2025-11-18 10:21 | Chase James (WW-NORTH) @ Sutton Water Resource Recovery Facility - SUSP Date Work Completed: 2025-11-18 10:21 ————————————————————— Batch waste SBR tank 2 Increased wasting on tank 2 from 360sec to 420sec Decant and transfer sludge tank SBR 2 air valve local closed and in Maintenance mode for maintenance team to install blow off system aeration blowers 1-3 off as well Shelve division EQ valve fault and over torque alarms- faulty valve since the day it was installed and we do not use UV issues- looking into problems, UVT and dose showing 0 but the UV 1A and B are on with an intensity of 100 Clean UV transmittance probe under direction of Eric Simanovskis potential problem is UVT is not connecting to UV system Weekly samples taken and delivered to Harry Walker Parkway Manually Deacon SBR two well maintenance worked on new flow off-line ————————————————————— • Attachments: 0
12183887 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12183887 | 1 | 2025-11-21 14:37 | 2025-11-21 14:33 | Tyson Cornish (WW-NORTH) @ Sutton Water Resource Recovery Facility - SUSP Date Work Completed: 2025-11-21 14:33 ————————————————————— Performed facility station check Completed Lab analysis: Data in Sharepoint Inspected headworks: leveled grit bin and raked bar screen Decanted sludge tank Continued troubleshooting UV:. -Wiper group reset to 1 again; investigated trends and involved PCS. Suspect a faulty connection. Work order created for further investigation on PCS end (W11461797) ————————————————————— • Worked With: Chase James • Attachments: 0
12187721 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12187721 | 2 | 2025-11-24 14:20 | 2025-11-24 14:18 | Chase James (WW-NORTH) @ Sutton Water Resource Recovery Facility - SUSP Date Work Completed: 2025-11-24 14:18 ————————————————————— Complete lab and enter data into SharePoint Plant checks completed Decant and transfer sludge after GFL remove load Pump out chambers Rotate septage duty pumps pump one now duty one UV rotation wiper back in Auto1-4 Found FIT 4 totalizer having a negative number after the flows stop Contractors on site working around hedge Road chamber ————————————————————— • Attachments: 0
12189974 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12189974 | 1 | 2025-11-25 14:56 | 2025-11-25 14:53 | Kyle Carlen (PCS) @ Sutton Water Resource Recovery Facility - SUSP Date Work Completed: 2025-11-25 14:53 ————————————————————— Onsite as directed by MS (PCS Supervisor) to replace PLC responsible for UV. Onsite, setup PLC with program, IP, security and switched out processor, downtime approx 5min. Confirmed system connectivity and SCADA operation with Tyson. ————————————————————— • Worked With: Tyson Cornish • Attachments: 0
12193399 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12193399 | 1 | 2025-11-26 12:29 | 2025-11-26 12:27 | Chris Colangelo (WW-NORTH) @ Sutton Water Resource Recovery Facility - SUSP Date Work Completed: 2025-11-26 12:27 ————————————————————— Onsite for daily operations Review scada/trends Decant stt plus transfer after load taken Collect in house lab samples Check station Clear rags from barscreen area Filters ok Complete lab - data in sharepoint PCS and electrical onsite to continue UV investigation 12:20 Alert roc filter feed pumps off for duration of UV work ————————————————————— • Attachments: 0
12193462 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12193462 | 1 | 2025-11-26 14:09 | 2025-11-26 14:06 | Artour Litvinov (PCS) @ Sutton Water Resource Recovery Facility - SUSP Date Work Completed: 2025-11-26 14:06 ————————————————————— Under direction of OIC Chris Colangelo, Worked with Chris and Tyson Cornish to troubleshoot UV panel PLC controller. Replaced power supply and put the panel power on UPS to isolate transfer switch. ————————————————————— • Attachments: 0