## Operational Issues
PERSONGROUP | LOGBOOK_MONTH | LDTEXT | DESCRIPTION | EVENTDATE
WW-NORTH | December | Assisted maintenance on relocating suction header PIT. It was lower down 191cm (18.7kPa). Adjusted the offset to compensate the new location and PIT should read -18.7 (kPa) at atmosphere. Pump 1 to 3 were completed today. Pump 1 and 2 run without any issues. Pump 3 will be running once duty is activated. No other issues encountered. | Keswick Water Resource Recovery Facility | 2025-12-15
WW-NORTH | December | Attended for sludge handling Decanted/transferred sludge thickening tanks Switched WAS feed to sludge thickening tank 2 Checked bar screen and raked bin. | Keswick Water Resource Recovery Facility | 2025-12-14
WW-NORTH | December | On site to move the pits on the back pulse lines finished 1-3 will return tomorrow for 4-5 | Keswick Water Resource Recovery Facility | 2025-12-15
WW-NORTH | December | On site to install new donker bolts and gaskets Found crack in tank to lower bolt hole is open Chris brought plastic welder and cleaned up and welded plastic tank Installed bolts and added RTV to lower donker bolt. Cut bolts to size and installed flange with new gasket. Installed coupling between flange and valve with new gasket. Advised to allow RTV to cure and then test the tank on Monday. | Keswick Water Resource Recovery Facility | 2025-12-12
WW-NORTH | December | sludge handling. batch waste into STT1. station checks lab and readings Trains 1 to 3 relocated PIT sensor. topped up hypo tank. filled large hypo tank with water to test for leak. | Keswick Water Resource Recovery Facility | 2025-12-15
WW-NORTH | December | Onsite for daily operations review scada/trends decant stt 1 and 3 collect in house lab samples complete lab enter data in sharepoint check station rake and level grit bin Receive hypo delivery | Keswick Water Resource Recovery Facility | 2025-12-10
WW-NORTH | December | Switched WAS feed to sludge thickening tank 1. | Keswick Water Resource Recovery Facility | 2025-12-13
WW-NORTH | December | Switched WAS feed to sludge thickening tank 2. | Keswick Water Resource Recovery Facility | 2025-12-11
WW-NORTH | December | Received call from ROC regarding train 4 shutdown - reset alarm and train went into standby. | Keswick Water Resource Recovery Facility | 2025-12-11
WW-NORTH | December | Programmed heated hypo recovery clean on train 2 | Keswick Water Resource Recovery Facility | 2025-12-11
WW-NORTH | December | Performed facility station check Completed Lab analysis: Data in Sharepoint Decanted Sludge holding tanks: 1, 2 & 3 Transferred Sludge holding tanks: 1 & 3 Inspected headworks: leveled grit bin and raked bar screen Topped up hypo day tank Completed weekly PM Work order: -Alum chemical panel valve exercise -Membrane 1-5 Turbidimeter maintenance -Clarifier Scum system and weir cleaning Completed monthly PM work orders: -RAS pumps 1-6 inspection -RAS/WAS Sump pumps inspection -Scum pumps inspection Scheduled Recovery cleans on membranes 1, 3 & 4 | Keswick Water Resource Recovery Facility | 2025-12-12
WW-NORTH | December | on site 0700hrs sludge handling. Batch waste int STT1. Decanted and transferred STT2. STT2 now fed by WAS . station checks lab and readings collected samples and delivered to Harry Walker. Sub#'s 11414493,11414897,11414883 | Keswick Water Resource Recovery Facility | 2025-12-02
WW-NORTH | December | on site 0700hrs sludge handling. decant STT1 and 2. Now feeding WAS to STT2. station checks. lab and readings. Generator test run. | Keswick Water Resource Recovery Facility | 2025-12-04
WW-NORTH | December | Switch WAS feed from sludge tank 3 to tank 1 Review area SCADA | Keswick Water Resource Recovery Facility | 2025-12-06
WW-NORTH | December | Transfer sledge tank two and three after decant completed Turn on heaters in basement Turn off exhaust fan in sludge transfer pump room Area SCDA review | Keswick Water Resource Recovery Facility | 2025-12-07
WW-NORTH | December | Performed assigned EZMax work orders: - Air compressors 1, 2 inspection - Air dryer 1, 2 inspection - Membrane trains 1-5 actuator blow downs - UV system 1, 2 system inspection - Membrane room actuator inspection | Keswick Water Resource Recovery Facility | 2025-12-02
WW-NORTH | December | Attending site to check issue with Alum Tank LIT1 (W11480057). Found transmitter not powered on. Cycled power to transmitter and it booted up normally. Cleared SCADA alarms and notified Chris Colangelo. | Keswick Water Resource Recovery Facility | 2025-12-02
WW-NORTH | December | heavy snow over night, plowing could have been better. sludge handling station checks lab and readings weekly samples, W11480832. Delivered to Harry walker | Keswick Water Resource Recovery Facility | 2025-12-30
WW-NORTH | December | Decant tanks 2&3 | Keswick Water Resource Recovery Facility | 2025-12-07
WW-NORTH | December | Performed station check Completed lab analysis and entered readings into SharePoint Checked head works - levelled bin and cleared bar screen Decanted and transferred STT 1 and 2 Batch wasted 80m3 Collected weekly samples (W11434651) Recorded OCU numbers Adjusted Alum chemical feed rates - System #1 from 75 to 70 - System #2 from 80 to 70 Completed assigned EZMax work orders: - Inspected aeration tanks 1, 2 DO probes - Inspected membrane air compressors - Clarifier 1-4 maintenance - Drained and rinsed membranes 1 and 3 | Keswick Water Resource Recovery Facility | 2025-12-09
WW-NORTH | December | Worked on plumbing for seal water on Vortex Removed old plumbing and built new piping including an ASCO valve. Found effluent pump runs constantly in manual at 60% and one pump is in manual off Found effluent pressure low and not causing pump to cycle. Investigated and found effluent system has no pressure tanks and SCADA will only let one pump run. Recommend system improvements. | Keswick Water Resource Recovery Facility | 2025-12-01
WW-NORTH | December | on site 0700hrs sludge handling. Decant and transfer STT1 and 3. WAS now feeding STT3 station checks lab and readings health and safety hypo delivery received Maintenance on site for Vortex work, assisted with SCADA diagnosis. Work order issued for alum tank1 LIT issue. plow truck on site for 2nd time today to complete Fridays work. | Keswick Water Resource Recovery Facility | 2025-12-01
WW-NORTH | December | sludge handling. station checks lab and readings turbidimeter and tss maintenance ocu maintenance uv rotation all chemical containment floats tested. | Keswick Water Resource Recovery Facility | 2025-12-03
WW-NORTH | December | On site to finish wiring and testing on channel 2 filling seal water for vortex grit pump 1 and 2. Completed. | Keswick Water Resource Recovery Facility | 2025-12-03
WW-NORTH | December | Performed station check Completed lab analysis and entered readings into SharePoint Decanted and transferred STT Checked head works - cleared bar screen and levelled bin Ran portable generator Checked diesel room compressor Inspected admin, sludge, and scum sump systems Topped up caustic tank with 4 jugs Topped up temporary hypo tank to 1200L *Changed out air dryer filter on membrane air compressor #1 | Keswick Water Resource Recovery Facility | 2025-12-05
WW-NORTH | December | Transferred Hypo to day tank. Stopped sludge transfer pumps. | Keswick Water Resource Recovery Facility | 2025-12-27
WW-NORTH | December | Performed facility station check Completed Lab analysis: Data in Sharepoint Decanted Sludge holding tanks: 2 & 3 Transferred Sludge holding tanks: 3 Inspected headworks: leveled grit bin and raked bar screen Topped up hypo day tank Scheduled heated hypo R- clean for trains 1 & 3 @ 1900 today | Keswick Water Resource Recovery Facility | 2025-12-31
WW-NORTH | December | Started decanting STT 2 and 3 | Keswick Water Resource Recovery Facility | 2025-12-27
WW-NORTH | December | Completed lab and entered into sharepoint Decanted all 3 sludge tanks batch wasted into STT 1 Switched WAS flow to STT 3 Opened and close valve for grit vortex 2 and cleared failed to close alarm cleaned turbidimeter on train 3 and cleared OOR alarm power dip reset clarifiers, floc mixer and aeration blower Disabled OOR alarm from train 3 turbidimeter Cleaned all 5 turbidimeters Programmed heated R-clean on train 4 and 5 | Keswick Water Resource Recovery Facility | 2025-12-29
WW-NORTH | December | Programmed heated hypo r-clean on train 1 and 5 | Keswick Water Resource Recovery Facility | 2025-12-24
WW-NORTH | December | sludge handling. station checks lab and readings. | Keswick Water Resource Recovery Facility | 2025-12-17
WW-NORTH | December | sludge handling. Batch waste into STT1 station checks lab and readings collected weekly samples, delivered to Harry walker. | Keswick Water Resource Recovery Facility | 2025-12-16
WW-NORTH | December | programmed heated R-clean on Train 5 | Keswick Water Resource Recovery Facility | 2025-12-16
WW-NORTH | December | Switch WAS feed from stt 2 to stt 1 | Keswick Water Resource Recovery Facility | 2025-12-20
WW-NORTH | December | Onsite for daily operations Review scada/trends Decant stt 1 and 2 plus transfer Collect in house lab samples Complete lab Enter data in sharepoint Top up hypo tank Check station Rake/level bin | Keswick Water Resource Recovery Facility | 2025-12-19
WW-NORTH | December | Assisted maintenance on relocating suction header PIT. It was lower down 191cm (18.7kPa). Adjusted the offset to compensate the new location and PIT should read -18.7 (kPa) at atmosphere. Pump 4 and 5 were completed and operator put it back in service. No other issues encountered. | Keswick Water Resource Recovery Facility | 2025-12-16
WW-NORTH | December | On site to finish moving the pits on the back pulse line for the membranes | Keswick Water Resource Recovery Facility | 2025-12-16
WW-NORTH | December | Programmed heated hypo r-clean on train 1,4 and 5 for the weekend | Keswick Water Resource Recovery Facility | 2025-12-19
WW-NORTH | December | sludge handling. Batch waste into STT1 station checks lab and readings Captor lo lo alarm back to 0.2 from 0.1, Lo and Lo Lo reenabled received Captor delivery. | Keswick Water Resource Recovery Facility | 2025-12-18
WW-NORTH | December | Programmed heated R-clean on train 2 and 3 | Keswick Water Resource Recovery Facility | 2025-12-17
WW-NORTH | December | Informed ROC, Onsite to troubleshoot O2 alarms for Odour room and grit room. Calibrated both O2 Gas Detectors. Readings back to normal. No issues. Informed ROC and left the site | Keswick Water Resource Recovery Facility | 2025-12-19
WW-NORTH | December | on site 0700hrs sludge handling. Batch waste into STT1. station checks alum delivery received. grit bins 1 and 2 removed and dumped by hauler. New liners installed on return. weekly samples collected and delivered to Harry walker. sub# 11466760. | Keswick Water Resource Recovery Facility | 2025-12-23
WW-NORTH | December | sludge handling. Batch waste into STT1. Now feeding WAS to STT2 station checks lab and readings | Keswick Water Resource Recovery Facility | 2025-12-22
WW-NORTH | December | Switched WAS feed to sludge thickening tank 2 Lowered captor lolo alarm from 0.2 to 0.1 m due to low chemical level. | Keswick Water Resource Recovery Facility | 2025-12-16
WW-NORTH | December | Onsite for sludge handling Begin decanting stt 1 and 2 Review scada Transfer stt 1 and 2 plus raise sliptubes Switch was feed to stt 3 | Keswick Water Resource Recovery Facility | 2025-12-21
WW-NORTH | December | Programmed heated hypo r-clean on train 2 and 3 for 7pm | Keswick Water Resource Recovery Facility | 2025-12-22
WW-NORTH | December | Checked station Viewed HMI and trends Checked dry well area Recorded readings in SharePoint | Holland Landing Sewage Pumping Station | 2025-12-11
WW-NORTH | December | Checked lagoons Recorded levels | Holland Landing Lagoons | 2025-12-04
WW-NORTH | December | Checked lagoons Recorded measurements | Holland Landing Lagoons | 2025-12-15
WW-NORTH | December | Checked station Viewed HMI and trends Checked diesel containment Checked dry well area Recorded readings in SharePoint | Holland Landing Sewage Pumping Station | 2025-12-15
WW-NORTH | December | Checked station Viewed HMI and trends Checked dry well area Checked diesel containments Recorded readings in SharePoint | Holland Landing Sewage Pumping Station | 2025-12-01
WW-NORTH | December | On site to check on channel grinder e stop. Reset and ran grinder in reverse. Put in auto seems channel went down and cleared alarms. | Holland Landing Sewage Pumping Station | 2025-12-29
WW-NORTH | December | Checked station Viewed HMI and trends Checked dry well area Recorded readings in SharePoint | Holland Landing Sewage Pumping Station | 2025-12-04
WW-NORTH | December | Checked station Viewed HMI and trends Checked dry well area Recorded readings in SharePoint | Holland Landing Sewage Pumping Station | 2025-12-31
WW-NORTH | December | Checked station Notified ROC of potential alarms Ran diesel generator - No issue Completed H+S inspection Completed sump pit inspections Viewed HMI and trends Checked dry well area Recorded readings in SharePoint | Holland Landing Sewage Pumping Station | 2025-12-08
WW-NORTH | December | In to complete comprehensive house keeping work order Swept floors Refilled toilet paper and hand soap Cleaned toilet | Holland Landing Sewage Pumping Station | 2025-12-23
WW-NORTH | December | Checked station Viewed HMI and trends Checked dry well area Recorded readings in SharePoint | Holland Landing Sewage Pumping Station | 2025-12-22
WW-NORTH | December | Checked station Viewed HMI and trends Checked dry well area Completed hoist inspection Recorded readings in SharePoint | East Gwillimbury 2nd Concession Sewage Pumping Station | 2025-12-15
WW-NORTH | December | Checked station Viewed HMI and trends Ran each pump @ 100% P1 - 80.5 L/s P2 - 81 L/s P3 - 68.5 L/s Checked dry well area Recorded readings in SharePoint | Holland Landing Sewage Pumping Station | 2025-12-18
WW-NORTH | December | Received call from ROC regarding recirculation loop mode failure - re-enabled recirc loop and monitored SCADA for a pump cycle. | East Gwillimbury 2nd Concession Sewage Pumping Station | 2025-12-15
WW-NORTH | December | Checked station Met Honeywell to fix outstanding alarm Viewed HMI and trends Checked dry well area Recorded readings in SharePoint Cleared outstanding alarms | East Gwillimbury 2nd Concession Sewage Pumping Station | 2025-12-11
WW-NORTH | December | Onsite to troubleshoot overflow flowmeter. Informed ROC. Performed mapping. Will monitor further for flow reading spikes on SCADA. Informed ROC, armed the building and left the site. | East Gwillimbury 2nd Concession Sewage Pumping Station | 2025-12-19
WW-NORTH | December | Checked station Viewed HMI and trends Notified ROC of potential alarms Completed diesel test run - No issues Completed H+S inspection Completed condensed drywell work order Recorded readings in SharePoint Station back to normal power | East Gwillimbury 2nd Concession Sewage Pumping Station | 2025-12-01
WW-NORTH | December | Checked station Viewed HMI and trends Checked dry well area Recorded readings in SharePoint | East Gwillimbury 2nd Concession Sewage Pumping Station | 2025-12-04
WW-NORTH | December | Checked station Viewed HMI and trends Checked dry well area Recorded readings in SharePoint | East Gwillimbury 2nd Concession Sewage Pumping Station | 2025-12-22
WW-NORTH | December | Checked station Viewed HMI and trends Checked dry well area Recorded readings in SharePoint | East Gwillimbury 2nd Concession Sewage Pumping Station | 2025-12-31
WW-NORTH | December | Took vibration readings on pump 2 | East Gwillimbury 2nd Concession Sewage Pumping Station | 2025-12-09
WW-NORTH | December | Checked station Met Honeywell on site Could not get hatch open - frozen closed Viewed HMI and trends Checked dry well area Recorded readings in SharePoint | East Gwillimbury 2nd Concession Sewage Pumping Station | 2025-12-08
WW-NORTH | December | Checked station Viewed HMI and trends Checked dry well area Recorded readings in SharePoint | East Gwillimbury 2nd Concession Sewage Pumping Station | 2025-12-18
WW-NORTH | December | In to complete comprehensive house keeping work order Swept diesel room and HMI room Cleaned toilet | East Gwillimbury 2nd Concession Sewage Pumping Station | 2025-12-23
WW-NORTH | December | Checked station Viewed HMI and trends Checked dry well area Checked diesel containment Recorded readings in SharePoint | Queensville West Sewage Pumping Station | 2025-12-15
WW-NORTH | December | Checked station Viewed HMI and trends Checked dry well area Completed consolidated dry well work orders Recorded readings in SharePoint | Queensville West Sewage Pumping Station | 2025-12-11
WW-NORTH | December | On site for the channel grinder over load Davr and Satnam check the motor and found no issues. We tried to pull the grinder but were unable. Operations will isolate and clean the inlet side of the grinder and we will return at a later date | Queensville West Sewage Pumping Station | 2025-12-12
WW-NORTH | December | Checked station Viewed HMI and trends Checked dry well area Recorded readings in SharePoint | Queensville West Sewage Pumping Station | 2025-12-08
WW-NORTH | December | Checked station Viewed HMI and trends Checked dry well area Checked diesel containment Recorded readings in SharePoint | Queensville West Sewage Pumping Station | 2025-12-01
WW-NORTH | December | Performed Wet Well inspection - Tested Hi level alarm - Exercised valves - Inspected comminutor | Queensville West Sewage Pumping Station | 2025-12-03
WW-NORTH | December | Checked station Viewed HMI and trends Ran each pump @ 100% P2 - 71.8 L/s P3 - 64.9 L/s Checked dry well area Recorded readings in SharePoint | Queensville West Sewage Pumping Station | 2025-12-18
WW-NORTH | December | Checked station Viewed HMI and trends Checked dry well area Recorded readings in SharePoint | Queensville West Sewage Pumping Station | 2025-12-31
WW-NORTH | December | In to completed comprehensive house keeping work order Checked and emptied full garbage bins Swept floors of diesel room and main HMI room Restocked toilet paper and hand soap in bathroom Cleaned toilet | Queensville West Sewage Pumping Station | 2025-12-23
WW-NORTH | December | Checked station Viewed HMI and trends Notified ROC of any potential alarms Completed diesel generator test run - No issue Completed hoist inspection Completed H+S inspection Recorded readings in SharePoint | Queensville West Sewage Pumping Station | 2025-12-04
WW-NORTH | December | Checked station Viewed HMI and trends Wet well entry to open bypass screens Pulled one block from bypass gate to wetwell1 and two from gate to wetwell2 H2S started to alarm so entrant exited wet well Checked dry well area Recorded readings in SharePoint | Queensville West Sewage Pumping Station | 2025-12-22
WW-NORTH | December | Onsite to troubleshoot WWEL overflow FIT. Informed ROC Checked scada trends. Visual random spikes in flow but no actual flow occurring Checked all terminations inside transmitter - no issues found Cycled thru parameters in setup - all ok Cycled power to transmitter (reboot) Will monitor on scada to see if flow spikes return Informed ROC, armed building and left site | Queensville West Sewage Pumping Station | 2025-12-17
WW-NORTH | December | Performed station check Entered readings into SharePoint Drained temp unit Flushed blow downs | Morton Avenue Air Management Facility | 2025-12-11
WW-NORTH | December | Performed facility station check Data in sharepoint Flushed blowdown Drained outside media unit Equipment OOS: none | Morton Avenue Air Management Facility | 2025-12-15
WW-NORTH | December | Completed monthly PM work orders: -JHSC H&S inspection -Blower 1 & 2 inspection (Electricians replaced #1 VFD yesterday). Placed blower 1 to duty 1 -Recirculation pump and strainer inspection -Fan body and drip leg drainage | Morton Avenue Air Management Facility | 2025-12-10
WW-NORTH | December | Performed station check Entered readings into SharePoint Drained temp unit Flushed blowdowns | Morton Avenue Air Management Facility | 2025-12-29
WW-NORTH | December | Performed station check Entered readings into SharePoint Drained temporary unit Flushed blow down | Morton Avenue Air Management Facility | 2025-12-01
WW-NORTH | December | On site to replace VFD for fan #1. Replaced, setup VFD, tested fan 1 in auto. Ok. Fan 1 back in service, left in auto duty. | Morton Avenue Air Management Facility | 2025-12-09
WW-NORTH | December | Shelved irrigation flow fault alarm. | Morton Avenue Air Management Facility | 2025-12-09
WW-NORTH | December | Performed station check Entered readings into SharePoint Drained temp unit Flushed blow downs | Morton Avenue Air Management Facility | 2025-12-22
WW-NORTH | December | Onsite to check station Enter data in sharepoint Flush blowdown Drain/reposition flex hose | Morton Avenue Air Management Facility | 2025-12-18
WW-NORTH | December | Attended for daily operations Performed station check Completed lab and entered readings into ACE sheet Decanted sludge holding/thickening tanks and started transfer while hauler took load Hosed bar screen and surrounding area Changed lagoon wet well low level alarm from 0.8 to 0.7 m Checked sand filters AC Electric working in MCC room. | Sutton Water Resource Recovery Facility | 2025-12-11
WW-NORTH | December | Made changes to the Septage Receiving system per the attached work order tested the functionality of the pump control on and off timers to control the transfer pumps as well as the Aysix permissive on tank hihi alarm. Made SREC_LIT1_HIHI_ALRM unlatched so it will clear on level less than setpoint. Added trend pens for volume and volume remaining based on process engineer memo in work order. | Sutton Water Resource Recovery Facility | 2025-12-11
WW-NORTH | December | Attended for daily operations Performed station check Completed lab and entered readings into ACE sheet Decanted sludge holding/thickening tanks and initiated transfer Adjusted EQ tank start/stop setpoints (start 1.0 to 1.1 m, stop 0.8 to 1.0 m) Adjusted plant influent flow hihi alarm from 130 to 155 L/s to reduce interlocking of lagoon pumps Hosed bar screen and surrounding area Checked sand filters. | Sutton Water Resource Recovery Facility | 2025-12-12
WW-NORTH | December | Attended for daily operations Performed station check Completed lab and entered readings into ACE sheet Decanted sludge holding/thickening tanks and initiated transfer while hauler took load Reduced filter flow max bias from 23 to 20 L/s Hosed bar screen and surrounding area Checked sand filters - worked on filters A1 and B2. | Sutton Water Resource Recovery Facility | 2025-12-15
WW-NORTH | December | Attended for sludge handling Decanted sludge thickening tank and initiated transfer Hosed bar screen and surrounding area. | Sutton Water Resource Recovery Facility | 2025-12-14
WW-NORTH | December | Attended for daily operations Performed station check Completed lab and entered readings into ACE sheet Decanted sludge holding/thickening tanks and initiated transfer Collected weekly regulatory samples and delivered to Newmarket Hosed bar screen and surrounding area Rolled out headworks bins for pick up Increased filter feed max flow bias from 17 to 20 L/s Placed channel 1 UV banks in local off due to malfunctioning outlet gate, and notified ROC that the channel will be OOS tonight. | Sutton Water Resource Recovery Facility | 2025-12-09
WW-NORTH | December | Uv gate repair, removed actuator new nut required | Sutton Water Resource Recovery Facility | 2025-12-10
WW-NORTH | December | Attended for daily operations Performed station check Completed lab and entered readings into ACE sheet Decanted sludge holding/thickening tanks and initiated transfer while hauler took load Hosed bar screen and surrounding area Increased filter feed max flow bias from 20 to 23 L/s Completed scheduled work orders Cleaned DO probes Checked sand filters - worked on filter B3. Flushed EQ tank drain line Checked filter reject sump pumps Terry/Matt (mechanical) were here to work on UV channel 1 gate Eric (instrumentation) was here to work on UVT system AC Electric was here to begin work on security camera setup. | Sutton Water Resource Recovery Facility | 2025-12-10
WW-NORTH | December | Attending site to replace UV transmittance transmitter (W11452693). Transmitter was replaced but the uv sensor still had an error once the probe was submerged in the channel. Hach service will have a look and repair or replace the sensor. It will be reinstalled once received in early 2026. ROC was notified before and after maintenance activities. | Sutton Water Resource Recovery Facility | 2025-12-10
WW-NORTH | December | On site to work on basin 2 purge valve. Completed wiring. Tested valve. Ok. Tested remote valve operation via SCADA with operations. Valve is functioning properly. | Sutton Water Resource Recovery Facility | 2025-12-05
WW-NORTH | December | Decant and transfer sludge Hose and clean bar screen Walk around plant check filters | Sutton Water Resource Recovery Facility | 2025-12-07
WW-NORTH | December | Attended for daily operations Performed station check Completed lab and entered readings into ACE sheet Decanted sludge holding/thickening tanks and initiated transfer Hosed bar screen and surrounding area Adjusted filter flow max bias setpoint from 15 to 17 L/s to account for lagoon flow Completed scheduled work orders Inspected UV system and initiated wiper sequence Inspected and grease bar screen Ran both septage pumps and exercised valves Checked sand filters and performed maintenance on mega lift Brent/Dave (electrical) here to work on SBR #2 purge valve. | Sutton Water Resource Recovery Facility | 2025-12-05
WW-NORTH | December | Attended for daily operations Performed station check Completed lab and entered readings into ACE sheet Decanted sludge thickening tank and initiated transfer while hauler took load Hosed bar screen and surrounding area Received fault alarm on lagoon flowmeter - notified instrumentation of issue and disconnected power to unit so it will not read flow Checked into flow readings on SBR diversion EQ line - removed snow from the flume and the reading returned to 0 L/s Checked sand filters. | Sutton Water Resource Recovery Facility | 2025-12-01
WW-NORTH | December | Attended for daily operations Performed station check Completed lab and entered readings into ACE sheet Decanted sludge holding/thickening tanks and initiated transfer Hosed bar screen and surrounding area Disabled UV channel low level probes - caused faults overnight Completed scheduled work orders Inspected chemical pumps Checked sand filters - mega-lifted filters A2 and B3 Bill (mechanical) was here to work on water line for septage haulers. | Sutton Water Resource Recovery Facility | 2025-12-08
WW-NORTH | December | Attended for daily operations Performed station check Completed lab and entered readings into ACE sheet Decanted sludge thickening tank and initiated transfer Collected weekly regulatory samples for delivery to Newmarket Lowered alum dosage from 170 to 160 mg/L Raised SBR #1 WAS run time from 360 to 420 s Hosed bar screen and surrounding area Checked sand filters - worked on filter B3 Had to open gate for Miller Waste (their access card was not working). | Sutton Water Resource Recovery Facility | 2025-12-02
WW-NORTH | December | Low diesel fuel alarm came in. changed LoLo alarm from 20cm to 15 and Low alarm from 30 to 20cm | Sutton Water Resource Recovery Facility | 2025-12-03
WW-NORTH | December | Attended for daily operations Performed station check Completed lab and entered readings into ACE sheet Decanted sludge thickening tank and initiated transfer Turned off sludge holding tank blowers at end of day for a decant tomorrow Hosed bar screen and surrounding area Completed scheduled work orders Rotated UV banks - 1B on, 2B off, adjusted minimum dosage setpoint to 35 mJ/cm2 Entered influent meter chamber open/close valves in order to flush High St flowmeter bypass line Greased/exercised lagoon diversion valves for both mains, High St valve faulted on overtorque and Dave (electrical) made some adjustments Checked sand filters. | Sutton Water Resource Recovery Facility | 2025-12-04
WW-NORTH | December | UV disinfection bypass at the Sutton wastewater treatment facility. Samples have been collected and delivered to 145 harry walker Cause: One of the two discharge gates malfunctioned. The issue has been identified, and gate valve will be fixed. The plant is now operating normally through UV channel 2 Time start- 09:33am stop- 09:53am Volume 24m3 MECP: Jeremy Weiss # 1-PW6YJE York region public health: Kathryn Damas # 4297300 conservation authority has been emailed | Sutton Water Resource Recovery Facility | 2025-12-09
WW-NORTH | December | On site to replace the hose bib at the dump pad. I asked Chase to test the next day when the glue dries. | Sutton Water Resource Recovery Facility | 2025-12-08
WW-NORTH | December | Attended for daily operations Performed station check Completed lab and entered readings into ACE sheet Decanted sludge thickening tank and initiated transfer while hauler took load Hosed bar screen and surrounding area Turned on lagoon return pumps and adjusted low flow alarm from 0.3 m to 0.8 m Completed scheduled work orders and notified ROC of work being completed Performed standby generator test run and recorded readings in rounds sheet Start: 597.1 h Stop: 598.7 h Run time: 1.6 h Tested diesel containment flood alarm - in @ 9:32 Performed H&S inspection Checked site chambers Hosed SBR inlet channel Checked sand filters Checked for hazardous waste - removed used oil from site. | Sutton Water Resource Recovery Facility | 2025-12-03
WW-NORTH | December | Attending site to remove UVT sensor from UV channel for shipping to Hach, for evaluation due to an error in the device (W11452693). Removed sensor and cleaned debris from housing. Will return to service once repairs have been made by the manufacturer. | Sutton Water Resource Recovery Facility | 2025-12-02
WW-NORTH | December | Onsite for sludge handling Decant stt to 2.5m and transfer Clear rags from barscreen area Check filters | Sutton Water Resource Recovery Facility | 2025-12-21
WW-NORTH | December | SHT blowers in manual off for decanting tomorrow | Sutton Water Resource Recovery Facility | 2025-12-18
WW-NORTH | December | On site to program UV Channel 1 actuator with Sean Peoples. Energized actuator and set open and closed limits. Tested actuator operation in local and remote/auto with Chase James. | Sutton Water Resource Recovery Facility | 2025-12-22
WW-NORTH | December | Attended for daily operations Performed station check Completed lab and entered readings into ACE sheet Decanted sludge thickening tank and initiated transfer while hauler took load Hosed bar screen and surrounding area Checked sand filters - mega lifted filter B3 Diverted 308 m3 combined from the three pumping stations to the lagoon from 10:19-14:05 while WESSUC cleaned grit vortexes and headworks inlet pit Kyle/Sean (electrical) were here to program UV channel 1 outlet actuator, left channel 1 UVs in local off for the night. | Sutton Water Resource Recovery Facility | 2025-12-22
WW-NORTH | December | Attended for daily operations Performed station check Completed lab and entered readings into ACE sheet Decanted sludge thickening tank and initiated transfer Hosed bar screen and surrounding area Checked SBR air relief valves Checked sand filters. | Sutton Water Resource Recovery Facility | 2025-12-31
WW-NORTH | December | Decant sludge holding and sludge, thickening tanks Clean and shovel bar screen area Complete lab and enter data into SharePoint Plant checks completed | Sutton Water Resource Recovery Facility | 2025-12-29
WW-NORTH | December | Onsite for daily operations Review scada/trends Decant stt Clear rags from barscreen area Collect in house lab samples Collect weekly regulatory samples Check filters Check station | Sutton Water Resource Recovery Facility | 2025-12-30
WW-NORTH | December | On site to open gate for GFL sludge hauler card would not work for him. Transferred to STT | Sutton Water Resource Recovery Facility | 2025-12-27
WW-NORTH | December | decanted STT for load out today. Also decanted SHT and left gate down and blowers in manual. Refilled STT after load out | Sutton Water Resource Recovery Facility | 2025-12-27
WW-NORTH | December | Attended for daily operations Performed station check Completed lab and entered readings into ACE sheet Decanted sludge thickening tanks and initiated transfer while hauler took load Hosed bar screen and surrounding area Checked sand filters - mega lifted filter A1 Bill/Terry (mechanical) were here to work on UV channel 1 gate. | Sutton Water Resource Recovery Facility | 2025-12-17
WW-NORTH | December | Grit vortex #2 bypass gate installed due to system failure. Vortex chamber is full of grit. Pumped down and notified supervisor and team lead to get a vac truck Decant and transfer sludge Check air relief on sludge blowers Found a bracket broken on the new air compressors . Will be fixed under warranty Grease SBR decant arms Exercise gate valve Clear rags from inlet gates | Sutton Water Resource Recovery Facility | 2025-12-16
WW-NORTH | December | Attended for daily operations Performed station check Completed lab and entered readings into ACE sheet Decanted sludge thickening tanks and initiated transfer Hosed bar screen and surrounding area Performed oil changes on SBR and SHT blowers Checked sand filters - mega lifted filter A1. | Sutton Water Resource Recovery Facility | 2025-12-18
WW-NORTH | December | Attended for daily operations Performed station check Completed lab and entered readings into ACE sheet Decanted sludge thickening tank and initiated transfer Collected weekly regulatory samples for delivery to Newmarket Hosed bar screen and surrounding area Received alum delivery Turned off sludge holding blowers for a decant tomorrow Completed scheduled work orders and notified ROC of work being completed Performed alum drawdown tests and flushed alum line with hot water Rolled out headworks bins for pick up Completed UV rotation - tested new gate in channel 1, then returned bank 2B to service Checked sand filters - worked on mega lift repairs Consultant was here to look at air compressor bracket deficiency. | Sutton Water Resource Recovery Facility | 2025-12-23
WW-NORTH | December | On site to reinstall the actuator on channel 1 UV. The electrician will come at a later date to program it | Sutton Water Resource Recovery Facility | 2025-12-17
WW-NORTH | December | Attended for daily operations Performed station check Completed lab and entered readings into ACE sheet Decanted sludge holding/thickening tanks and initiated transfer? Collected weekly regulatory samples for delivery to Newmarket Reduced filter flow max bias from 20 to 18 L/s Rolled out headworks bins for pickups Hosed bar screen and surrounding area Checked sand filters - worked on filter B3. | Sutton Water Resource Recovery Facility | 2025-12-16
WW-NORTH | December | Attended for daily operations Performed station check Completed lab and entered readings into ACE sheet Decanted sludge thickening/holding tanks and initiated transfer while hauler took load Returned sludge holding blowers to auto Lowered filter max flow bias from 18 to 16 L/s Hosed bar screen and surrounding area Insulated heat trace lines around SBR gearboxes Checked sand filters. | Sutton Water Resource Recovery Facility | 2025-12-19
WW-NORTH | December | Attended for daily operations Performed station check Completed lab and entered readings into ACE sheet Decanted sludge thickening/holding tanks and initiated transfer while hauler took load Returned sludge holding blowers to auto Hosed bar screen and surrounding area Checked sand filters. | Sutton Water Resource Recovery Facility | 2025-12-24
WW-NORTH | December | Performed facility station check Data in sharepoint Completed monthly PM work order -Heat trace inspection Equipment OOS: Odour control system | Keswick Sewage Pumping Station | 2025-12-15
WW-NORTH | December | Completed monthly PM work orders -Hoist inspection -Consolidated dry well inspection Sump pump 2 not working Auto dialer test not working -Odour control scrubber system inspection Odour control system communication loss and still outstanding: CPD (J. Oliveira) was notified . VFD controller has no power. Attempted to run OCS in local; MCC illuminates and shows running but upon inspection of the OCS, motor is not running. SCADA showed auto and not running the entire time. | Keswick Sewage Pumping Station | 2025-12-10
WW-NORTH | December | Performed station check Entered readings into SharePoint Checked trends and alarms (Odour control system still off due to power issues) *Switched exhaust air fan 8 in odour control room to local off in order to close dampers. | Keswick Sewage Pumping Station | 2025-12-11
WW-NORTH | December | Onsite to wrap up annual calibrations Informed ROC Used cal mode on scada Modified RSP discharge pipe trees for easier flushing and maintenance. Calibrated discharge PITs Calibrated generator LIT Cleared associated alarms Informed ROC, armed building and left site | Keswick Sewage Pumping Station | 2025-12-12
WW-NORTH | December | Onsite to perform annual calibration. Informed ROC. Used the calibration mode. Devices were done as below: WEL_LITs, PMP_FITs, PMP2_PIT. Put everything back in service. All the related alarms were cleared. No issues. Informed ROC, armed the building and left the site. | Keswick Sewage Pumping Station | 2025-12-03
WW-NORTH | December | Performed station check Entered readings into SharePoint No outstanding alarms | Keswick Sewage Pumping Station | 2025-12-01
WW-NORTH | December | Onsite to check station Review scada/trends Clear info alarms Enter data in sharepoint | Keswick Sewage Pumping Station | 2025-12-04
WW-NORTH | December | Performed station check Entered readings into SharePoint Completed assigned EZMax work orders: - Diesel generator run (entered readings into SharePoint) - JHS Inspection - Wet well hi level alarm - Hazardous waste removal When transferring back to hydro a "Odour Control System Communication Loss Alarm" came in on SCADA - Noticed the VFD controller had no power to it - Attempted resetting alarm as well as running OCF in local with no success - Station still under warrantee so will reach out to project coordinator for next steps. | Keswick Sewage Pumping Station | 2025-12-08
WW-NORTH | December | Onsite to reset channel grinder 1 overload alarm and investigate generator warning/fault/low battery caused by power blip Run channel grinder in local reverse. Reset alarm and return to normal operation Check generator - HMI shows battery under voltage warning Will return with battery charger Back onsite with Kevin K. Put charger on generator batteries to charge. Clear low battery/fault and warning. Run generator in local to test functionality - no apparent issues. Leaving big battery booster onsite, left battery maintainer attached to batteries Batteries still under warranty, will reach out to CPD | Keswick Sewage Pumping Station | 2025-12-24
WW-NORTH | December | Performed station checked Entered readings into SharePoint Checked trends and alarms | Keswick Sewage Pumping Station | 2025-12-29
WW-NORTH | December | On site for boiler fault. Reset alarm was flame loss during operation alarm. All ok | Keswick Sewage Pumping Station | 2025-12-29
WW-NORTH | December | Performed station check Entered readings into SharePoint Reviewed trends | Keswick Sewage Pumping Station | 2025-12-22
WW-NORTH | December | Attended for boiler fault Reset alarm on unit (burner fault) and on SCADA and notified ROC upon completion. | Keswick Sewage Pumping Station | 2025-12-31
WW-NORTH | December | On site to response to power dip, second time today. Grinder and pumps 2,3 and 4 VFD faulted. Grinder restarted and cleared fault on its own. had to reset pump VFDs and reset VFDs for wetwell fans and ourdour control room 4 in total. All back to normal | Keswick Sewage Pumping Station | 2025-12-27
WW-NORTH | December | Onsite to reset boiler fault Clear alarm and monitor operation | Keswick Sewage Pumping Station | 2025-12-21
WW-NORTH | December | On site to check sump pump 2. Ran in hand, wasn?t pumping water. Checked pump. Adjusted pump position in pit. Tried again in hand, pump 2 pumped the sump pit all the way down. Suspect blockage that is now clear. | Keswick Sewage Pumping Station | 2025-12-19
WW-NORTH | December | Checked station Viewed HMI and trends Ran each pumps @ 100% P1 - 201 L/s P2 - 210 L/s P3 - 214.2 L/s P4 - 168.2 L/s Checked dry well area Recorded readings in SharePoint | Keswick Sewage Pumping Station | 2025-12-18
WW-NORTH | December | Onsite responding to W11529110 boiler fault Reset fault and monitor operation | Keswick Sewage Pumping Station | 2025-12-19
WW-NORTH | December | Reset faulted VFDs caused by brief power blip | Keswick Sewage Pumping Station | 2025-12-29
WW-NORTH | December | Attended for station check Recorded station readings in rounds sheet Checked generator enclosure Forestry was here marking trees for removal Reviewed SCADA/trends. | Sutton Woodriver Bend Sewage Pumping Station | 2025-12-15
WW-NORTH | December | Attended for station check Recorded station readings in rounds sheet Checked generator enclosure Left gate unlocked for upcoming contractor access needs Reviewed SCADA/trends. | Sutton Woodriver Bend Sewage Pumping Station | 2025-12-11
WW-NORTH | December | Monthly diesel test run completed Enter data into SharePoint Station checks completed | Sutton Woodriver Bend Sewage Pumping Station | 2025-12-08
WW-NORTH | December | Station checks completed JH&S check completed Diesel hut ok Enter data into SharePoint Unable to view HMI screen | Sutton Woodriver Bend Sewage Pumping Station | 2025-12-04
WW-NORTH | December | Attended for station check Recorded station readings in rounds sheet Checked generator enclosure Reviewed SCADA/trends - OIT screen not loading properly. | Sutton Woodriver Bend Sewage Pumping Station | 2025-12-01
WW-NORTH | December | Station checks completed Enter data into SharePoint Install spill water hazard signage Diesel hut ok | Sutton Woodriver Bend Sewage Pumping Station | 2025-12-18
WW-NORTH | December | Monthly diesel run completed Station checks completed Enter data into SharePoint | Sutton Woodriver Bend Sewage Pumping Station | 2025-12-08
WW-NORTH | December | Station checks completed Enter data into SharePoint Record water meter reading Diesel hut ok | Sutton Woodriver Bend Sewage Pumping Station | 2025-12-24
WW-NORTH | December | Station checks completed Enter data into SharePoint Diesel hut ok | Sutton Woodriver Bend Sewage Pumping Station | 2025-12-29
WW-NORTH | December | Attended for station check Recorded station readings in rounds sheet Reviewed SCADA. | Sutton South River Sewage Pumping Station | 2025-12-15
WW-NORTH | December | Adjusted wet well high level alarm from 1.8 to 1.6 m. | Sutton South River Sewage Pumping Station | 2025-12-12
WW-NORTH | December | Attended for station check Recorded station readings in rounds sheet Reviewed SCADA. | Sutton South River Sewage Pumping Station | 2025-12-11
WW-NORTH | December | Test pump 1 in hand Amps, RPM, and hz are the same as pump 2 -No flow Enter data into SharePoint Hatches secure | Sutton South River Sewage Pumping Station | 2025-12-04
WW-NORTH | December | Attended for station check Recorded station readings in rounds sheet Reviewed SCADA. | Sutton South River Sewage Pumping Station | 2025-12-01
WW-NORTH | December | Station checks completed Enter data into SharePoint Hatches secure | Sutton South River Sewage Pumping Station | 2025-12-29
WW-NORTH | December | Station checks completed Hatches secure JH&S check completed Low temp | Sutton South River Sewage Pumping Station | 2025-12-24
WW-NORTH | December | Responding to Hight level alarm Georgina township flushing hydrant into manhole west of the station. Asked them to stop. Level reached 1.32 Both pumps running in auto Levels back down to normal operation | Sutton South River Sewage Pumping Station | 2025-12-16
WW-NORTH | December | Attended for station check Recorded station readings in rounds sheet Checked pump house - p.2 running in duty Found dialer in alarm, phone line dead Reviewed SCADA/trends. | Sutton High Street Sewage Pumping Station | 2025-12-11
WW-NORTH | December | Wetwell duty start/stop setpoints have been changed for longer run times of the pumps to help scour forcemain. Duty 1 start was 1.65m changed to 1.85m and stop was 1.3m now 1.0m duty 2 start was 1.85 changed to 1.95m stop is 1.4m and was not changed. Minimum speed of both pumps was changed to start at 100%. | Sutton High Street Sewage Pumping Station | 2025-12-10
WW-NORTH | December | Attended for station check Recorded station readings in rounds sheet Checked pump house - p.1 running in duty Reviewed SCADA/trends. | Sutton High Street Sewage Pumping Station | 2025-12-15
WW-NORTH | December | Adjustments made so that both duty 1 and duty 2 start setpoints are 1.85m so both pumps will run | Sutton High Street Sewage Pumping Station | 2025-12-15
WW-NORTH | December | Monthly diesel test run completed JH&S check completed Hi/low temperature alarm Station checks completed Enter data into SharePoint | Sutton High Street Sewage Pumping Station | 2025-12-08
WW-NORTH | December | Station checks completed Enter data into SharePoint Pump house ok | Sutton High Street Sewage Pumping Station | 2025-12-22
WW-NORTH | December | Attended for station check Recorded station readings in rounds sheet Checked pump house - p.2 running in duty Reviewed SCADA/trends. | Sutton High Street Sewage Pumping Station | 2025-12-01
WW-NORTH | December | Station checks Enter data into SharePoint Run pump 1 @100% 2? air relief on line leaving the station in passing water back. Will create work order | Sutton High Street Sewage Pumping Station | 2025-12-04
WW-NORTH | December | Station checks completed Enter data into SharePoint Pump house ok | Sutton High Street Sewage Pumping Station | 2025-12-29
WW-NORTH | December | Station checks completed Enter data into SharePoint Pump house ok Run pump 1 @ 100% | Sutton High Street Sewage Pumping Station | 2025-12-24
WW-NORTH | December | Changed duty 2 start from 1.85m to 1.95m | Sutton High Street Sewage Pumping Station | 2025-12-22
WW-NORTH | December | Station checks completed Enter data into SharePoint pump at 100% speed Pump house ok Grease surge valve | Sutton High Street Sewage Pumping Station | 2025-12-18
WW-NORTH | December | Performed station check Entered readings into SharePoint Compressive housekeeping Checked OCU - ok | Keswick Joe Dales Sewage Pumping Station | 2025-12-11
WW-NORTH | December | Under direction of OIC Kevin Kerek, Worked with contractors to commission and calibrate diesel tank LITs. ROC notified. | Keswick Joe Dales Sewage Pumping Station | 2025-12-11
WW-NORTH | December | Performed station check Entered readings into SharePoint Completed assigned EZMax work orders: - Hoist inspection - Odour control inspection - Consolidated bar screen and screw press inspection | Keswick Joe Dales Sewage Pumping Station | 2025-12-15
WW-NORTH | December | Performed station check Entered readings into SharePoint Checked OCU Reviewed trends and alarms | Keswick Joe Dales Sewage Pumping Station | 2025-12-15
WW-NORTH | December | Performed station check Entered readings into SharePoint Checked trends and alarms | Keswick Joe Dales Sewage Pumping Station | 2025-12-29
WW-NORTH | December | Performed station check Entered readings into SharePoint No outstanding alarms | Keswick Joe Dales Sewage Pumping Station | 2025-12-01
WW-NORTH | December | Onsite to check station and complete work orders Review scada/trends Enter data in sharpeoint Alert roc Diesel test run Transfer station to diesel power at 10:00hrs JHSC inspection diesel data in sharepoint Transfer station back to hydro at 10:57hrs Heat radiator exchange inspection Hoist inspection OCU inspection | Keswick Joe Dales Sewage Pumping Station | 2025-12-04
WW-NORTH | December | Checked station Viewed HMI and trends Ran each pump @ 100% P1 - 57.44 L/s P2 - 59.85 L/s P3 - 55.37 L/s Checked dry well area Recorded readings in SharePoint | Keswick Joe Dales Sewage Pumping Station | 2025-12-18
WW-NORTH | December | Onsite to complete work orders Alert roc Sump pit inspection Drywell flood - alarm came in on scada at 11:33hrs Dialer test Check valve inspection Manual valve exercise Air valve flush Hi/low temp: alarm did not trigger, will alert TL | Keswick Joe Dales Sewage Pumping Station | 2025-12-05
WW-NORTH | December | Performed station check Entered readings into SharePoint Checked OCU - ok | Keswick Joe Dales Sewage Pumping Station | 2025-12-22
WW-NORTH | December | Performed station check Entered readings into SharePoint Checked bar screen and bin Reviewed trends and alarms | Georgina No. 4 Sewage Pumping Station | 2025-12-11
WW-NORTH | December | Onsite to check station Review scada/trends Enter data in sharepoint Check screen room | Georgina No. 4 Sewage Pumping Station | 2025-12-04
WW-NORTH | December | Performed station check Entered readings into SharePoint Checked bar screen and bin | Georgina No. 4 Sewage Pumping Station | 2025-12-29
WW-NORTH | December | Checked station Viewed HMI and trends | Georgina No. 4 Sewage Pumping Station | 2025-12-01
WW-NORTH | December | Performed station check Entered readings into SharePoint Completed assigned EZMax work orders: - JHS inspection - Diesel test run - Dry well consolidated work order - Hazardous waste collection / removal (none on site) | Georgina No. 4 Sewage Pumping Station | 2025-12-01
WW-NORTH | December | Performed station check Entered readings into SharePoint Checked bar screen and bin | Georgina No. 4 Sewage Pumping Station | 2025-12-22
WW-NORTH | December | Station checks completed Enter data into SharePoint Run bar screen and auger in hand | Georgina No. 4 Sewage Pumping Station | 2025-12-18
WEST | December | Station Check (no issues found) Input data to PWQ 13:25 Verified Depolox (mg/l) Free: Grab 0.03, A 0.05 Total: Grab 1.58, A 1.59 | Woodbridge East Booster Pumping Station | 2025-12-04
WEST | December | Onsite for station check Duty active Checked residuals mg/l @1217 Total analyzer 1.64 grab 1.45 Free analyzer 0.06 grab 0.05 Adjusted total analyzer | Woodbridge East Booster Pumping Station | 2025-12-12
WEST | December | Onsite for station check Checked residuals mg/l @1133 Total analyzer 1.53 grab 1.47 Free analyzer 0.06 grab 0.04 | Woodbridge East Booster Pumping Station | 2025-12-15
WEST | December | Onsite for station check Duty not active Checked residuals mg/l @1355 Total analyzer 1.56 grab 1.56 Free analyzer 0.05 grab 0.04 | Woodbridge East Booster Pumping Station | 2025-12-01
WEST | December | Onsite for station check Duty not active Checked residuals mg/l @1045 Total analyzer 1.38 grab 1.45 Free analyzer 0.04 grab 0.02 | Woodbridge East Booster Pumping Station | 2025-12-30
WEST | December | Onsite for station check Duty active Checked residuals mg/l @1145 Total analyzer 1.58 grab 1.58 Free analyzer 0.06 grab 0.03 | Woodbridge East Booster Pumping Station | 2025-12-08
WEST | December | Onsite to complete work orders Completed jhsc Ran pumps for pump inspection added grease to pumps Did maintenance on cl2 analyzer Electrolyte and grit ok Took grabs Total analyzer 1.57 grab 1.52 Free analyzer 0.06 grab 0.05 Replaced eye wash solution | Woodbridge East Booster Pumping Station | 2025-12-18
WEST | December | Onsite for station check Duty not active Checked residuals mg/l @1045 Total analyzer 1.41 grab 1.39 Free analyzer 0.05 grab 0.05 | Woodbridge East Booster Pumping Station | 2025-12-24
WEST | December | Onsite for station check Duty Active checked residuals mg/l @1329 Total analyzer 1.54 grab 1.47 Free analyzer 0.05 grab 0.03 | Woodbridge East Booster Pumping Station | 2025-12-23
WEST | December | Onsite for station check and to collect weekly micro sample Deactivated duty to get sample on down cycle Checked residuals mg/l @1012 Total grab 1.65 Free grab 0.09 Sl1000 Mcl grab 1.53 T nh3 grab 0.35 F nh3 grab 0.14 No2 grab 0.004 | Woodbridge East Elevated Tank | 2025-12-10
WEST | December | Onsite to complete work orders Completed jhsc Tested sump pump and flood Ran portable generator with no issues | Woodbridge East Elevated Tank | 2025-12-17
WEST | December | Onsite for station check and to collect weekly micro sample W11420538 Tower draining Checked residuals mg/l @1142 Total grab 1.71 Free grab 0.02 Sl1000 Mcl grab 1.68 No2 grab 0.004 F nh3 grab 0.08 T nh3 grab 0.41 | Woodbridge East Elevated Tank | 2025-12-03
WEST | December | On site for station check and to collect bacti sample wo#w11484178 Residuals (Colorimeter) @11:05 Free: 0.06mg/L Total 1.60mg/L Took generator for king city power outage No issues on site | Woodbridge East Elevated Tank | 2025-12-29
WEST | December | Onsite for station check and to complete weekly micro sample W11470772 Tower draining Checked residuals mg/l @0853 Total grab 1.70 Free grab 0.02 Sl1000 Mcl grab 1.56 No2 0.003 F nh3 0.08 T nh3 0.39 | Woodbridge East Elevated Tank | 2025-12-22
WEST | December | Onsite for station check and to collect weekly micro sample W11455496 Deactivated duty to get sample on down cycle Checked residuals mg/l @12:25 Total grab 1.70 Free grab 0.05 Sl1000 Mcl grab 1.69 T nh3 grab 0.42 F nh3 grab 0.09 No2 grab 0.004 | Woodbridge East Elevated Tank | 2025-12-16
WEST | December | Onsite for station check and to collect weekly micro sample W11439387 Checked residuals mg/l @1157 Total grab 1.40 Free grab 0.06 Sl1000 Mcl grab 1.16 F nh3 grab 0.07 T nh3 grab 0.30 No2 grab 0.003 | Woodbridge West Elevated Tank | 2025-12-10
WEST | December | Onsite for station check and to collect weekly micro sample W11420538 Deactivated duty to get sample on downcycle Checked residuals mg/L @1230 Total grab 1.41 Free grab 0.04 Sl1000 Mcl grab 1.29 No2 grab 0.004 F nh3 grab 0.11 T nh3 grab 0.36 Reactivated duty afterwards | Woodbridge West Elevated Tank | 2025-12-03
WEST | December | On site for station check and to collect bacti sample wo#w11484178 Residuals (Colorimeter) @10:45 Free: 0.05mg/L Total 1.28mg/L No issues on site | Woodbridge West Elevated Tank | 2025-12-29
WEST | December | Onsite to complete work orders Completed jhsc Tested hi/lo temp Ran portable generator with no issues Security system kept arming itself and causing intrusion alarms notified team lead | Woodbridge West Elevated Tank | 2025-12-18
WEST | December | Onsite for station check and to collect weekly micro sample Deactivated duty to get sample on downcycle Checked residuals mg/L @1310 Total grab 1.56 Free grab 0.02 Sl1000 MCL grab 1.29 T nh3 grab 0.30 F nh3 grab 0.05 No2 grab 0.004 | Woodbridge West Elevated Tank | 2025-12-16
WEST | December | Onsite for station check and to collect weekly micro sample W11470772 Tower draining Checked residuals mg/l @1018 Total grab 1.49 Free grab 0.01 Sl1000 Mcl grab 1.37 F nh3 grab 0.06 T nh3 grab 0.32 | Woodbridge West Elevated Tank | 2025-12-22
WW-CEAST | December | On site for PIT leak on pump 5. Replaced a 3/4 nipple | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-12-10
WW-CEAST | December | On site for Station Check (See details on SharePoint) All pumps available in timed auto duty rotation every 3 hours, except, pump 3, which is in manual/duty 7, out of service, discharge flow fault. Currently, 3 duty pumps are running with a flows of 1109 L/s. Standby power generators available in auto. Checked dry well, ok. Checked bar screens. Levelled rags from the rag bin. Cleaned bar screen room. Removed rags/dirt from the conveyor motor box. Pushed rag bins back inside the screen room after picked up by Miller Waste yesterday. All lines available at the dump pad for haulers to use. Checked Unit Heaters 3 and 4 inside the bar screen room. Verified and confirmed, they are not working. Power is ON but no heat coming out. There is LOTO tag in the MCC, which says, ?motor thermal overload tripped.? Informed Acting Team Lead (Philip R.). | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-12-12
WW-CEAST | December | Switched force main to west only for now - waiting on a decision due to the amount of snow fall. Took station readings and entered into SharePoint,, reviewed trends - all looks good. Checked both compressors oil/belt - ok. Put 2 bins out for pick up after snow plowing was completed. Went down and checked the dump pad - it was in good shape, it had been plotted and salted - need a couple more bags of salt for the yellow salt bin. Mopped out the washroom and cleaned the sink, EQ building where the OC is , is clean. East forcemain work was cancelled, I did fully close the east forcemain valve to see if the flow slowed down but no change was noticed. Opened the east forcemain valve back up and put it back in remote. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-12-10
WW-CEAST | December | On site completed work orders. Station Check (See details on SharePoint) All pumps available in timed auto duty rotation every 3 hours, except, pump 3, which is in manual/duty 7, out of service, discharge flow fault. Standby power generators available in auto. Checked dry well, ok. Checked bar screens. Levelled rags from the rag bin. Cleaned bar screen room. Removed rags/dirt from the conveyor motor box. All lines available at the dump pad for haulers to use. Consolidated Monthly Dry Well Pump Floor Inspection 1 - Auto Dialer Alarm Test - received by ROC. 2 - High Low Temperature Alarm Test - received by ROC. 3 - Dry Well Flood Alarm Test - received by ROC. 4 - Sump Pit Inspection 5 - RS Pump and Motor Inspection Pump 1 (VFD) - @ 0% speed, 315 L/s, 770 kPa, 357 A, 517 V, 54 Hz, 1077 Rpm; 40% speed, 380 L/s, 786 kPa, 459 A, 536 V, 55 Hz, 1116 Rpm Pump 2 (VFD) - @ 0% speed, 290 L/s, 766 kPa, 364 A, 517 V, 54 Hz, 1077 Rpm; 40% speed, 390 L/s, 773 kPa, 443 A, 536 V, 56 Hz, 1116 Rpm Pump 3 (Constant) - Out of service Pump 4 (Constant) - 474 L/s, 757 kPa, 450 A, 598 V, 60 Hz Pump 5 (VFD) - @ 0% speed, 316 L/s, 765 kPa, 375 A, 517 V, 54 Hz, 1077 Rpm; 40% speed, 388 L/s, 782 kPa, 463 A, 536 V, 55 Hz, 1115 Rpm Pump 6 (VFD) - @ 0% speed, 288 L/s, 771 kPa, 364 A, 517 V, 54 Hz, 1077 Rpm; 40% speed, 380 L/s, 771 kPa, 459 A, 536 V, 55 Hz, 1115 Rpm 6 - Check Valves Inspection 7 - Air Compressors Inspection Cleared/reset all alarms Station back to normal operations. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-12-15
WW-CEAST | December | On site completed work orders. Consolidated Wet Well Inspection, Overflow 1 - High Level Alarm Test - received and confirmed by ROC 2 - Bar Screen Cleaning/Lubrication 3 - Screw Conveyor Clean/Lubrication 4 - Sluice Gate Valve/Actuator Exercise 5 - Wet Well Valve Exercise 6 - Wet Well Inspection and Cleaning 7 - Facility Overflow Inspection/Clean 8 - Tipping Bucket Operational Check Consolidated Monthly Surge Tanks Inspection 1 - Surge Tank and System Inspection 2 - Surge Tank Valve and Actuator Exercise and Inspection 3 - Surge Tank Drain Valve Inspection 4 - Transmitter Line Flushing Before Level and Pressure: Tank 1 - 2.00 m/592 kPa Tank 2 - 2.02 m/601 kPa After Flushing Transmitter: Tank 1 - 1.97 m/594 kPa Tank 2 - 1.98 m/601 kPa | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-12-04
WW-CEAST | December | On site to assist contractor Ainsworth with Transformer oil testing. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-12-08
WW-CEAST | December | On site completed work orders. Station Check (See details on SharePoint) All pumps available in timed auto duty rotation every 3 hours, except, pump 3, which is in manual/duty 7, out of service, discharge flow fault. Standby power generators available in auto. Checked dry well, ok. Checked bar screens. Levelled rags from the rag bin. Cleaned/hosed down bar screen room. Flushed/hosed down screw press drain. All lines available at the dump pad for haulers to use. AUSSSR Disposal Facility, Heat Trace System Inspection - cleared/reset heat trace #2 alarm. All setpoints parameters, ok. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-12-08
WW-CEAST | December | On site completed work orders. Station Check (See details on SharePoint) All pumps available in timed auto duty rotation every 3 hours, except, pump 3, which is in manual/duty 7, out of service, discharge flow fault. Checked dry well, ok. Checked bar screens. Levelled rags from the rag bin. Cleaned bar screen room. Switched rag bin. All lines available at the dump pad for haulers to use. Checked Unit Heaters 3 and 4 inside the bar screen room. It seems they are working because there is heat inside, however, there is LOTO tag in the MCC, which says, ?motor thermal overload tripped.? Informed Team Lead (Daniel Kim). Air Dryer Inspection and Cleaning | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-12-05
WW-CEAST | December | On site completed Station Check (See details on SharePoint) All pumps available in timed auto duty rotation every 3 hours, except, pump 3, which is in manual/duty 7, out of service, discharge flow fault. All standby power generators available in auto. Checked dry well. Checked bar screens. Levelled rags from the rag bin. Cleaned/hosed down bar screen room. Hosed down screw press drain, clogged. Added oil on the reservoir tank. All lines available at the dump pad for haulers to use. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-12-01
WW-CEAST | December | On site completed Station Check (See details on SharePoint) Pumps 2, 4, 5 and 6 available in timed auto duty rotation every 3 hours. Pump 3, which is in manual/duty 7, out of service due to discharge flow fault. Pump 1 is in manual/duty 7. Standby power generators available in auto. Checked dry well, Ok. All lines available in auto at the dump pad for the haulers. Checked bar screens. Rotated bin. Cleaned bar screen room of rags. Two rag bins pushed outside last week not pick up by Miller Waste. Called Customer Service (Melissa), she said, it will be picked up tomorrow. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-12-29
WW-CEAST | December | On site completed work orders. Station Check (See details on SharePoint) Pumps 2, 4, 5 and 6 available in timed auto duty rotation every 3 hours. Pump 3, which is in manual/duty 7, out of service due to discharge flow fault. Pump 1, which is in manual/duty 7, out of service due to leakage alarm. Standby power generators available in auto. Checked dry well, ok. Checked bar screens. Levelled rags from the rag bin. Cleaned bar screen room. Flushed screw press drain. Removed rags/dirt from inside the conveyor motor box. All lines available in auto at the dump pad for haulers. EQ Tanks Odour Control Scrubber System Inspection | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-12-22
WW-CEAST | December | On site completed work orders. Station Check (See details on SharePoint) All pumps available in timed auto duty rotation every 3 hours, except, pump 3, which is in manual/duty 7, out of service, discharge flow fault. Standby power generators available in auto. Checked dry well, ok. Checked bar screens. Levelled rags from the rag bin. Cleaned/hosed down bar screen room. Removed rags/dirt from the conveyor motor box. Flushed screw press drain. Added oil to the reservoir tank of screen 1. All lines available at the dump pad for haulers to use. Air Compressors Inspection and Cleaning. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-12-17
WW-CEAST | December | Weather: -6 C Cloudy Wind: 14 Kmh from SSW On site completed work orders. Station Check (See details on SharePoint) All pumps available in timed auto duty rotation every 3 hours, except, pump 3, which is in manual/duty 7, out of service, discharge flow fault. Checked dry well, ok. Checked bar screens. Levelled rags from the rag bin. Cleaned bar screen room. Switched rag bin. All lines available at the dump pad for haulers to use. Air Compressors Inspection and Cleaning Hazardous Waste Collection and Removal JHSC Health and Safety Inspection - two lighting fixtures at B1 above air compressors not working. Work order created. Standby Power Generators Test Run - pre-test checked, ok. Generators started and stopped running without problem. Cleared/reset all alarms. Generators back in auto and available. Station back to normal operations. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-12-03
WW-CEAST | December | -investigated pump 1 leakage alarm and mv2 actuator fault alarm -actuator display is blank, and not displaying status, needs to be looked at by electrical -pump 1 leakage alarm is outstanding, WO created for maintenance | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-12-20
WW-CEAST | December | Rotated bins in screen room Inspected site | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-12-27
WW-CEAST | December | Took station readings and entered into SharePoint,, reviewed trends - checked and pumps are in all stop Duty rotation. Station running under normal ops - no issues were found. | Newmarket Green Lane Pumping Station | 2025-12-15
WW-CEAST | December | On site for Station Check (See details on SharePoint) All pumps available in timed auto duty rotation every 3 hours, except, pump 3, which is in manual/duty 7, out of service, discharge flow fault. Standby power generators available in auto. Checked dry well, ok. Checked bar screens. Levelled rags from the rag bin. Switched rag bin. Cleaned bar screen room. Lines 1 and 2 available in auto at the dump pad for haulers to use. Line 3 interlocked due to overtorque. Unclogged line 3. Cleared/reset alarm. Line 3 is now available in auto. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-12-19
WW-CEAST | December | On site completed work orders. Station Check (See details on SharePoint) Pumps 2, 4, 5 and 6 available in timed auto duty rotation every 3 hours. Pump 3, which is in manual/duty 7, out of service due to discharge flow fault. Pump 1, which is in manual/duty 7, out of service due to leakage alarm. Standby power generators available in auto. All lines available in auto at the dump pad for the haulers. Dewatered EQ Tanks from 11 m3 to 5 m3. Cleared/reset dehumidifier alarm. Air Compressors Inspection and Cleaning Screen Bin Removal and Replacement - completed by Daniel Kim. Levelled rags. Switched bin. Pushed out rag bins to be pick up by Miller Waste. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-12-24
WW-CEAST | December | On site to drain leakage chamber on pump #1. Filled with glycol. Pump drained approx 10L. Filled about 8L. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-12-24
WW-CEAST | December | Weather today Overcast and -4 Celsius -On site to complete work orders W11482489, W11481886, W11472947. -Completed station check. -Entered station readings into SharePoint. -Pumps 2, 4, 5 and 6 available in timed auto duty rotation every 3 hours. -Pump 3, which is in manual/duty 7, out of service due to discharge flow fault. -Pump 1 is in manual/duty 7. -Standby power generators available in auto. -Checked dry well, Ok. -All lines available in auto at the dump pad for the haulers. -Checked bar screens. Rotated bin. Cleaned bar screen room of rags. -Two rag bins pushed outside last week not pick up by Miller Waste. -SCADA Review. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2025-12-31
WW-CEAST | December | Took station readings and entered into SharePoint,, reviewed trends- all good. Pumps in all stop Duty rotation. Station running under normal ops - no issues were found. | Newmarket Green Lane Pumping Station | 2025-12-12
WW-CEAST | December | I took station readings and entered into SharePoint,, reviewed trends,, Marcos tested the Hi wet well alarm(confirmed by ROC) and Marcos also ran each pump. Pump 1 has a higher flow rate as it was pulled and cleaned in the fall. Both pumps run at 40%. Station running under normal ops - no issues were found. | Newmarket Green Lane Pumping Station | 2025-12-17
WW-CEAST | December | Kevin took station readings and entered into SharePoint,, show Kevin where pump hrs are and VFDs for the pumps. Reviewed trends - all good. Station running under normal ops- no issues were found. | Newmarket Green Lane Pumping Station | 2025-12-05
WW-CEAST | December | Took station readings and entered into SharePoint,, reviewed trends and checked pumps are in all top Duty rotation. Completed H&S inspection- all good. Station running under normal ops - no issues were found. | Newmarket Green Lane Pumping Station | 2025-12-01
WW-CEAST | December | Took station readings and entered into SharePoint,,, reviewed trends, checked auto duty rotation - all is working well. Station running under normal ops - no issues were found. | Newmarket Green Lane Pumping Station | 2025-12-08
WW-CEAST | December | On site for Station Check (See details on SharePoint) Both pumps available in all stop auto duty rotation. Standby power generator connected to Newmarket PS (NMSSBP). Station operations normal. SCADA is trending. No outstanding alarm. | Newmarket Green Lane Pumping Station | 2025-12-29
WW-CEAST | December | Took station readings and entered into SharePoint,, reviewed trends - all good and look at pump flows. Pump 2 hasn?t been cleaned out yet it runs a little longer. Station running under normal ops - no issues were found. | Newmarket Green Lane Pumping Station | 2025-12-19
WW-CEAST | December | -On site to complete work orders. -Station check completed, readings entered into SharePoint. -Verified sand filter operation and alum dosing. -Pulled and inspected DO probes. -Travelling screen maintenance completed. Cleaned out back compartment and greased unit. Created work request for failed bearing on brush shaft. -Screw press maintenance completed. -Grit dewatering screw press maintenance completed. -Clarifier 2 remains OOS for weir cover installation. WAS Pump 1 OOS, RAS Pump 1 OOS. -OCU OOS due to failed motor. -Aeration Blower 3 OOS, but can be run in local. | Mount Albert Water Resource Recovery Facility | 2025-12-12
WW-CEAST | December | -station check of site -reviewed SCADA -inspected site -entered data into SharePoint -cleaned UV reactor 1B with Terry Reed, duty 1 after, dosing with no issues/alarms -hose down UV channel -cleaned aeration alum injection -cleaned RAS chamber -station okay | Mount Albert Water Resource Recovery Facility | 2025-12-11
WW-CEAST | December | Completed in-house lab Analysis (See details on SharePoint) Decanting STT into the Headworks. Transferred the sludge and processing. Batch wasted 10m3. Grit Vortex 1&2 maintenance completed Added 2 bags of soda ash into each aeration tank. | Mount Albert Water Resource Recovery Facility | 2025-12-12
WW-CEAST | December | -lab analysis and sludge handling -reviewed SCADA -inspected site -entered data into SharePoint -decanted sludge thickening tank, wasted remaining sludge to holding tank -wasted 10 m3 from clarifier 1 to sludge thickening tank -added 4 bags of soda ash total to aeration tanks -cleaned RAS chamber -cleaned alum chamber -electrician Dave is working with contractor for generator load testing -clarifier 2 remains OOS for contractor work -station okay | Mount Albert Water Resource Recovery Facility | 2025-12-15
WW-CEAST | December | -On site to complete work orders. -Decanted STT to headworks, then emptied tank into SHT. -Added two bags of soda ash to each aeration tank. -Completed lab analysis, entered results into SharePoint. -Batch wasted 10m3, ran RAS pumps at 100% speed when returning to service. -Station check completed, readings entered into SharePoint. -Verified alum dosing and sand filter operation. -DO probe verification completed. -Scum pumps 1-2 inspection completed. -WAS pumps 1-2 inspection completed. -Aeration Blower 3 OOS. -Clarifier 2 OOS for weir cover installation, WAS Pump 1 OOS, RAS Pump 1 OOS. | Mount Albert Water Resource Recovery Facility | 2025-12-10
WW-CEAST | December | On site to assist contractor Total Power with Diesel generator PM and Load Test. Completed | Mount Albert Water Resource Recovery Facility | 2025-12-15
WW-CEAST | December | After doing the UV bulbs went through aeration blowers, sludge blowers and grit blowers all belts are OK and oil is minimum half full or better. All are working fine. | Mount Albert Water Resource Recovery Facility | 2025-12-11
WW-CEAST | December | Completed sludge processing along with the lab work and entered results into SharePoint,, wasted 10m3 and added 4 bags of soda ash. Station running under normal ops- WAS pump 1 is OOS due to work on the clarifier. | Mount Albert Water Resource Recovery Facility | 2025-12-14
WW-CEAST | December | Completed in-house lab Analysis (See details on SharePoint) Decanting STT into the Headworks. Transferred the sludge and processing. Batch wasted 10m3. DO meter verification work order completed. Sump pump maintenance, air compressor maintenance WO completed Added 2 bags of soda ash into each aeration tank. | Mount Albert Water Resource Recovery Facility | 2025-12-11
WW-CEAST | December | -On site to complete work orders. -Decanted STT to headworks, then emptied tank to SHT. -Completed lab analysis, entered results into SharePoint. -Added two bags of soda ash to each aeration tank. -Batch wasted 8m3. Ran RAS pumps at 100% when returning to service. -Monthly JHSC H&S inspection completed, no issues noted. -1157 - Transferred site to generator power. -1305 - Transferred site back to utility power. -Monthly diesel generator test run completed, readings entered into SharePoint. -Generator start hours: 486.2, stop hours: 487.5, run time: 1.3hrs. -Post aeration alum chamber and RAS inlet chambers cleaned out. -Clarifier 2 is drained and OOS for weir cover installation. -RAS Pump 1 and WAS Pump 1 OOS while Clarifier 2 is OOS. | Mount Albert Water Resource Recovery Facility | 2025-12-01
WW-CEAST | December | -station check of site of site completed -reviewed SCADA -inspected site -entered data into SharePoint -rotated bin in screen room as necessary -hazard waste removal, disposed of 4 buckets of old oil at 380 bayview oil drop off -station okay | Mount Albert Water Resource Recovery Facility | 2025-12-01
WW-CEAST | December | Check leaking backflow filter building Install 1st check rubber repair kit and relief port rubber repair kit test Passed | Mount Albert Water Resource Recovery Facility | 2025-12-04
WW-CEAST | December | On site for the Weekend Sludge Handling/Processing. Decanted STT, dumped remaining sludge into the SHT. Turned off decant pump afterwards. Checked Headworks, ok. Added two bags of Soda Ash into each Aeration Tanks. Removed rags from the Aeration Tanks inlet/outlet sluice gates. Checked DO probes. Checked Alum dosing injection points from the pre-filter and post-aeration tanks. Batch wasted 10 m3. Short blasted RAS Pumps 2 and 3 to get desired flows of around 12 L/s at 0% speed. Also, completed in-house Lab Analysis (See details on SharePoint) | Mount Albert Water Resource Recovery Facility | 2025-12-07
WW-CEAST | December | -on site to complete station check -reviewed SCADA -inspected site -entered data into SharePoint -station okay | Mount Albert Water Resource Recovery Facility | 2025-12-05
WW-CEAST | December | -reviewed SCADA -completed work orders -cleaned UV Channel -inspected clarifiers, could not clean weirs due to launder covers installed on clarifier 1, and clarifier 2 is already cleaned for the contractor work | Mount Albert Water Resource Recovery Facility | 2025-12-03
WW-CEAST | December | Station check/lab complete and the readings have been entered into the sharepoint. Contractors onsite still working on clarifier 2 launder cover. Clarifier 2 OOS. Batchwasted 10m3 and dosed 4 bags of soda ash in total Weekly YD sample w.o complete/ delivered to 145 HWP | Mount Albert Water Resource Recovery Facility | 2025-12-02
WW-CEAST | December | -On site to complete lab analysis and sludge handling. -Emptied STT to SHT. -Completed lab analysis, entered results into SharePoint. -Added two bags of soda ash to each aeration tank. -Batch wasted 10m3, ran RAS pumps at 100% when returning to service. -Completed site walkthrough with Jacobs. -Clarifier 2 OOS for weir cover installation, WAS pump 1 OOS, RAS pump 1 OOS. -Aeration Blower 3 OOS, but can run in local. | Mount Albert Water Resource Recovery Facility | 2025-12-05
WW-CEAST | December | Informed ROC. Performed calibration on Raw sewage FIT and put it in Cal mode while doing the task. All alarms were cleared after the job. No other issues encountered. | Mount Albert Water Resource Recovery Facility | 2025-12-02
WW-CEAST | December | Received alum delivery Tank 1.27 to 3.97 meters Uploaded COA and bill of lading to work order Driver was new to delivering chemicals off site at 16:57 | Mount Albert Water Resource Recovery Facility | 2025-12-04
WW-CEAST | December | -On site to complete work orders. -Decanted STT to headworks, then emptied tank into SHT. -Completed lab analysis, entered results into SharePoint. -Batch wasted 8m3. Mistakenly also batch wasted 8m3 from OOS Clarifier 2. -Ran RAS pumps at 100% speed when returning to service. -Added two bags of soda ash to each aeration tank. -Station check completed, readings entered into SharePoint. -Verified sand filter operation and alum dosing. -Clarifier 2 OOS, WAS Pump 1 OOS, RAS Pump 1 OOS. -Contractors on site working on installing Clarifier 2 weir covers. -Aeration Blower 3 had multiple Failed to Start Alarms this afternoon. Failed to start in auto and manual multiple times. Found small air leak on discharge coupling, tightened bolts, air no longer leaking. Also found air leak on discharge header coupling, also tightened bolts and air is no longer leaking. Test ran Aeration Blower 3 in local with no issues, but again failed to start in manual or auto. Will create work request for maintenance team to continue troubleshooting. Inspected belts, filter, oil levels, but found no issues. | Mount Albert Water Resource Recovery Facility | 2025-12-03
WW-CEAST | December | -station check of site -reviewed SCADA -inspected site -entered data into SharePoint -cleaned RAS/WAS chamber -cleaned alum injection chamber -flushed reject drain for sand filters -rotated screen room bin as necessary -flushing alum pumps and system with hot water now that the backflow preventer has been rebuilt, rotating duty on alum chemical pumps so both systems get flushed -station okay | Mount Albert Water Resource Recovery Facility | 2025-12-08
WW-CEAST | December | -station check of site completed -reviewed SCADA -inspected site -entered data into into SharePoint -flushed reject drain on sand filters -station okay | Mount Albert Water Resource Recovery Facility | 2025-12-02
WW-CEAST | December | -On site to complete lab analysis and sludge handling. -Decanted STT to headworks, tank then emptied into SHT. -Completed lab analysis, entered results into SharePoint. -Batch wasted 10m3, ran RAS pumps at 100% speed when returning to service. -Added two bags of soda ash to each aeration tank. -Clarifier 2 remains OOS for weir cover installation, WAS pump 1 and RAS pump 1 also OOS. | Mount Albert Water Resource Recovery Facility | 2025-12-08
WW-CEAST | December | -station check of site completed -lab analysis of site completed -data entered into SharePoint -reviewed SCADA -inspected site -started decant pump on sludge thickening tank, wasted remaining sludge to holding tank -wasted 14 m3 of sludge from clarifier 1 to sludge thickening tank -added 4 bags of soda ash total to aeration tanks -waiting on alum delivery -cleaned RAS chamber, cleaned alum injection chamber -station okay | Mount Albert Water Resource Recovery Facility | 2025-12-04
WW-CEAST | December | -station check of site completed -lab analysis completed -samples collected and dropped off by Kevin Shaji -reviewed SCADA -inspected site -entered data into SharePoint -decanted sludge thickening tank, wasted remaining sludge to holding tank -wasted 10m3 of sludge from clarifiers to sludge thickening tank -added 4 bags of soda ash to aeration tanks -received soda ash delivery, uploaded bill of lading to work order -rotated bins in screen room -began diverting clarifier effluent to lagoon at 08:12, for clarifier 2 cleaning by contractors, to ensure sand filters do not get clogged with debris/algae -diversion was from 08:12 to 14:33, approximately 319 m3 of clarifier effluent was diverted to the lagoon -station okay | Mount Albert Water Resource Recovery Facility | 2025-12-09
WW-CEAST | December | -on site to complete lab analysis and sludge handling -reviewed SCADA -inspected site -entered data into SharePoint -started decanting sludge thickening tank, wasted remaining sludge to holding tank -wasted 10 m3 of sludge from clarifiers to sludge thickening tank -added 4 bags of soda ash total to aeration tanks -clarifier 2 which was put back online Friday, looks good, total phosphorus in effluent sample has dropped since Friday?s lab -ran RAS pumps 100% manual speed after wasting to clear rags, back to auto speed -station okay | Mount Albert Water Resource Recovery Facility | 2025-12-21
WW-CEAST | December | Collected YD sample @ 9:20 | Mount Albert Water Resource Recovery Facility | 2025-12-30
WW-CEAST | December | -On site for lab analysis and sludge handling work. -Clarifier 2 had been filling with effluent water overnight. Ice is now completely gone. Turned off effluent pump 2 and removed hose from clarifier. Test ran Clarifier 2 in auto with no issues. Observed multiple arm rotations with no issues, then opened Clarifier 2 inlet gate from aeration tanks. Continued to let RAS Pumps pull from Clarifier 1 for several hours. Following batch wasting, placed WAS Pump 1 and RAS Pump 1 back into service. Test ran RAS pump 1 and ran at 100% speed to test flows, no issues noted. -Clarifier 2 back in service, WAS pump 1 and RAS pump 1 also now back in service. -Re-valved RAS pumps, RAS pumps 1 and 2 are now valved to draw from Clarifier 2 and RAS pumps 3 is valved to draw from Clarifier 1. -Decanted STT to headworks, emptied STT to SHT following batch wasting. -Added two bags of soda ash to each aeration tank. -Completed lab analysis, entered results into SharePoint. -Batch wasted 10m3, ran RAS pumps at 100% speed when returning to service. -Verified sand filter operation and alum dosing. -Aeration Blower 3 OOS, but can be run in local. | Mount Albert Water Resource Recovery Facility | 2025-12-19
WW-CEAST | December | Completed in-house lab Analysis (See details on SharePoint) Decanting STT into the Headworks. Transferred the sludge and processing. Batch wasted 20m3. | Mount Albert Water Resource Recovery Facility | 2025-12-24
WW-CEAST | December | -On site for lab analysis and sludge handling work. -Decanted STT to headworks, then emptied tank into SHT. -Added two bags of soda ash to each aeration tank. -Completed lab analysis, entered results into SharePoint. -Batch wasted 10m3, ran RAS pumps at 100% speed when returning to service. -Clarifier 2 OOS, WAS Pump 1 OOS, RAS Pump 1 OOS. -Aeration Blower 3 OOS, but can be run in local. | Mount Albert Water Resource Recovery Facility | 2025-12-16
WW-CEAST | December | -on site for lab analysis and sludge handling -reviewed SCADA -inspected site -entered data into SharePoint -decanted sludge thickening tank to holding tank -wasted 14 m3 of sludge from from clarifiers to sludge thickening tank -ran RAS pumps manual speed 100% after wasting to clear rags, back to auto speed -added 4 bags of soda ash total to aeration tanks -station okay | Mount Albert Water Resource Recovery Facility | 2025-12-27
WW-CEAST | December | -station check of site -reviewed SCADA -inspected site -entered data into SharePoint -flushed reject drain lines on sand filters -station okay | Mount Albert Water Resource Recovery Facility | 2025-12-23
WW-CEAST | December | Completed in-house lab Analysis (See details on SharePoint) Decanting STT into the Headworks. Transferred the sludge and processing. Batch wasted 10m3. Added 2 bags of soda ash into each aeration tank. | Mount Albert Water Resource Recovery Facility | 2025-12-18
WW-CEAST | December | -station check of site -reviewed SCADA -inspected site -entered data into SharePoint -cleaned alum injection chamber -cleaned RAS chamber -hosed UV channel -Sand Filter Service Filter #1 -clarifier 2 is OOS, began filling clarifier 2 with effluent water -disregard final effluent flow lolo alarm, this is due to filling clarifier 2 with effluent water, which is robbing from the flowmeter -clarifier 2 will be put back online tomorrow -station okay | Mount Albert Water Resource Recovery Facility | 2025-12-18
WW-CEAST | December | -On site for lab analysis and sludge handling. -Decanted STT to headworks, then emptied tank into SHT. -Added two bags of soda ash to each aeration tanks. -Weekly samples collected. -Shovelled and salted stairs and walkways. -Lab analysis completed, results entered into SharePoint. -Batch wasted 20m3, ran RAS pumps at 100% speed when returning to service. -Sand filter drain line flush completed. -RAS inlet chamber and post aeration alum chambers cleaned out. -Station check completed, readings entered into SharePoint. -Verified alum dosing and sand filter operation. -Headworks O2 LoLo alarm outstanding. | Mount Albert Water Resource Recovery Facility | 2025-12-30
WW-CEAST | December | -station check of site -weekly waste water samples completed -dropped off raw and effluent samples to 145 HWP fridge for pickup -inspected site -entered data into SharePoint -reviewed SCADA -flushed sand filter reject drains -inspected crane hoist in UV room and blower room -station okay | Mount Albert Water Resource Recovery Facility | 2025-12-16
WW-CEAST | December | -station check of site -reviewed SCADA -inspected site -entered data into SharePoint -added 4 bags of soda ash total -station okay | Mount Albert Water Resource Recovery Facility | 2025-12-24
WW-CEAST | December | -station check and lab analysis of site -reviewed SCADA -entered data into SharePoint -inspected site -lab completed -station check completed -added 4 bags of soda ash total to aeration tanks -decanted sludge thickening tank, wasted remaining sludge to holding tank -wasted 8 m3 of sludge from clarifier 1 to sludge thickening tank -station okay | Mount Albert Water Resource Recovery Facility | 2025-12-17
WW-CEAST | December | -station check of site -reviewed SCADA -inspected site -entered data into SharePoint -fixed grease nipple on bar screen and greased bar screen -rotated bin in screen room as necessary -Housekeeping for garage -station okay | Mount Albert Water Resource Recovery Facility | 2025-12-22
WW-CEAST | December | -On site to complete lab analysis and sludge handling. -Decanted STT to headworks. -Added two bags of soda ash to each aeration tank. -Completed lab analysis and entered results into SharePoint. -Batch wasted 20m3, ran RAS pumps at 100% speed when returning to service. -OCU motor repairs delayed until early next year. -Aeration blower 3 OOS, can be run in local. | Mount Albert Water Resource Recovery Facility | 2025-12-23
WW-CEAST | December | -station check of site -lab analysis and sludge handling -reviewed SCADA -inspected site -entered data into SharePoint -decanted sludge thickening tank -wasted thickening tank to holding tank -wasted 20m3 of sludge from clarifiers to thickening tank -added 4 bags of soda ash to aeration tanks -station okay | Mount Albert Water Resource Recovery Facility | 2025-12-29
WW-CEAST | December | -station check of site -lab analysis and sludge handling -inspected site -reviewed SCADA -entered data into SharePoint -decanted sludge thickening tank, wasted reaming sludge to holding tank -wasted 20 m3 of sludge from clarifiers to thickening tank -added 4 bags of soda ash to aeration tanks -total phosphorus was slightly high, inspected alum injection points, all okay, will monitor, sand filters looked normal -cleaned alum injection chamber for aeration tanks | Mount Albert Water Resource Recovery Facility | 2025-12-31
WW-CEAST | December | -On site to complete work orders. -Decanted STT to headworks, then emptied tank into SHT. -Added two bags of soda ash to each aeration tank. -Received delivery for new OCU fan motor. Placed motor in garage, installation planned for tomorrow. -Completed lab analysis, entered results into SharePoint. -Batch wasted 16m3, ran RAS pumps at 100% speed when returning to service. -Cleaned out RAS inlet chamber and post aeration alum chamber. Removed rags from aeration tank inlet gates -Cleaned off DO probes, reattached air blow-off lines to both probes, both had become disconnected. -Aeration blower 3 OOS, but can be run in local. | Mount Albert Water Resource Recovery Facility | 2025-12-22
WW-CEAST | December | Station Check (See details on SharePoint). Both pumps available in all-stop auto duty rotation. Standby power generator available in auto. Checked dry well, ok. Reset sampling program due to missed samples. Cleaned floor near sampler due to raw sewage found on the floor. | Mount Albert Pumping Station | 2025-12-15
WW-CEAST | December | -On site to perform a station check. -Entered station readings into SharePoint. -Checked drywell and generator. | Mount Albert Pumping Station | 2025-12-12
WW-CEAST | December | -station check of site and work orders -reviewed SCADA -inspected site -entered data into SharePoint -monthly generator test run -JHSC inspection -no hazardous waste to remove Generator Start Hours: 615.3 Generator Stop Hours: 616.7 Run Time: 1.4 hrs Fuel Start: 968L Fuel Stop: 946L Fuel Used: 22L -started generator at 08:55, transfer successful -generator off at 10:23, test successful -station on utility power -site okay | Mount Albert Pumping Station | 2025-12-01
WW-CEAST | December | -station check of site -reviewed SCADA -entered data into SharePoint -inspected site -called PCS on call Chris Scott to have local HMI reset -station okay | Mount Albert Pumping Station | 2025-12-08
WW-CEAST | December | Collected weekly YD sample and programmed the comp sampler for next week | Mount Albert Pumping Station | 2025-12-02
WW-CEAST | December | -on site for station check -reviewed SCADA -inspected site -entered data into sharepoint -completed consolidated dry well work order -notified ROC of dry well flood alarm test -completed hoist inspection -station okay | Mount Albert Pumping Station | 2025-12-05
WW-CEAST | December | -On site for hydrostatic LIT2 issue -Hydrostatic sensor is reading high whenever pump 1 runs. -tried running site in backup mode LIT1, however hydrostatic alarms still come in when pump 1 is duty 1 -put backup mode back to auto, and pump 1 manual off duty 3, so hydrostatic doesn?t generate alarms -both pumps are okay, the issue is just LIT2 -called PCS Kyle Carlen to try and make a work around to disable LIT2 alarms, best option was to just leave pump 1 off for time being, can be ran in emergencies if pump 2 fails -all alarm set points are left normal, just running pump 2 in duty 1 for time being -called Parth Patel, he is will come to site Monday to inspect/replace hydrostatic sensor -wet well hatch locks are frozen and could not visually inspect them -will return with heat gun or bolt cutters on Monday when Parth comes to work on LIT2 -notified ROC of site status -best option other than replacing hydrostatic sensor is leaving pump 1 off, and using pump 2, pump 1 is available in case of emergencies, both pumps are pumping normally | Mount Albert Pumping Station | 2025-12-26
WW-CEAST | December | -On site for site walkthrough with Jacobs. | Mount Albert Pumping Station | 2025-12-05
WW-CEAST | December | -station check of site -reviewed SCADA -inspected site -entered data into SharePoint -station in PAC mode on LIT 1 ultrasonic due to hydrostatic LIT erratic readings -hydrostatic LIT is no longer spiking on reviewing trends, will wait a few days before restoring it back to backup control mode ?auto? -station okay | Mount Albert Pumping Station | 2025-12-29
WW-CEAST | December | -backup mode switched to PAC mode -LIT1 is controlling duty -had to take it out of auto backup mode due to now pump 2 was also triggering LIT2 to spike -alarms for LIT2 will still come in, but not trigger backup mode -both pumps back to auto, and in duty rotation -PAC mode a recommendation from Kyle Carlen | Mount Albert Pumping Station | 2025-12-26
WW-CEAST | December | -station check of site -reviewed SCADA -entered data into SharePoint -inspected site -station okay | Mount Albert Pumping Station | 2025-12-19
WW-CEAST | December | On site to take YD sample. Unable to take the sample as comp bottle is empty. Found sampling hose is clogged with solid which likely caused this issue. Back flushed the sampling line with hot water. Re-tested the sampler, it is now working as intended. Reset the sampler for next Wednesday. Notified Dean L/CEWW team that raw sample could not be taken today | Mount Albert Pumping Station | 2025-12-30
WW-CEAST | December | -station check of site -reviewed scada -inspected site -entered data into SharePoint -hosed floor -station okay | Mount Albert Pumping Station | 2025-12-22
WW-CEAST | December | Took station readings and entered into SharePoint,, reviewed trends and pump flows and they all look good. Checked both compressors oil/belts - OK. Pushed bin back in and levelled out the bin in use,, emptied the top of the auger and flushed out screen and drain hose. Sent dry well flood alarm and diaper alarm through diaper - it shows up on the dialer screen but ROC does NOT receive the alarm - I will talk to Graham. Verified sump pump operation and also checked the check valves. | Newmarket Sewage Pumping Station & Equalization Tank | 2025-12-12
WW-CEAST | December | Here to complete WOs - completed Diesel test run along with the station readings and entered all values into SharePoint. Completed H & S inspection - no issues found and there was no hazardous waste to dispose of. Checked both compressors oil/belts - OK and also emptied the top of the auger in the screening room and pushed bin out for pick up. I had Kevin with me today and explained all operations that were completed today. All alarms have been cleared, pump 2 is OOS. | Newmarket Sewage Pumping Station & Equalization Tank | 2025-12-03
WW-CEAST | December | Station Check completed (See details on SharePoint). Changed screen bins and flushed the drain screen and drain hose. Placed the bar screen bin outside for removal. Air compressors inspection completed. Everything looks normal | Newmarket Sewage Pumping Station & Equalization Tank | 2025-12-10
WW-CEAST | December | Kevin Took station readings and entered into SharePoint,, pushed bin back in and cleared out the top of the auger and flushed out drain screen as well as the hose. Checked both compressors oil/belts -OK and also cleaned up racking area and then swept out both office and washroom then mopped them both. Station running under normal ops - pump 2 is OOS. | Newmarket Sewage Pumping Station & Equalization Tank | 2025-12-05
WW-CEAST | December | Took station readings and entered into SharePoint,,, reviewed trends - all good. Levelled off bin in the screening room and emptied the top of the auger,, flushed out drain screen as well as the drain hose - moved bin over to fill the other half. Checked both compressors oil/belts - OK. Also checked pump floor - all good. Station running under normal ops - pump 2 is OOS. Bar screen 1 is back in service and inlet channel has been opened. | Newmarket Sewage Pumping Station & Equalization Tank | 2025-12-08
WW-CEAST | December | On site for bar screen 1 over torque. Found loose bolts on the motor bracket and also adjusted the sensor. Had Terry open the channel and put it back in auto | Newmarket Sewage Pumping Station & Equalization Tank | 2025-12-08
WW-CEAST | December | -On site during remote SCADA outage due to upgrades on network equipment. Monitored station during outage, station operated normally throughout entire duration. Outage lasted from 0908-0949am. -Pump 2 remains OOS. | Newmarket Sewage Pumping Station & Equalization Tank | 2025-12-09
WW-CEAST | December | On site responded to a call from the ROC regarding mechanical screen 1 overtorque alarm. Cleared/reset fault alarm, ran bar screen for several cycles, ok. Bar screen back in service. At around 10: 11 am, it overtorque again. Found rake hitting the scraper when it is running. Cleared/reset alarm, ran again, again it is hitting the scraper. Put bar screen out of service. Closed Sluice Gate MV1. Created work order request to CMS for repair. Informed ROC (Carter D.). | Newmarket Sewage Pumping Station & Equalization Tank | 2025-12-07
WW-CEAST | December | Checked barscreen 1 due to over torque. No issues noted with rollers or alignment. Ran barscreen and found multiple stationary bars have broken welds Unit did not fault during test run. | Newmarket Sewage Pumping Station & Equalization Tank | 2025-12-31
WW-CEAST | December | Took station readings and entered into SharePoint,, reviewed trends - all looks good. Checked pumps are in floor - all good and checked both compressors oil/belts - ok. Levelled off the bin in the screening room and moved it over a bit, emptied the top of the auger and cleaned the corner of bar screen 1. Oil level on both bar screens - OK. Station running under normal ops - no issues found,, Pump 2 is OOS. | Newmarket Sewage Pumping Station & Equalization Tank | 2025-12-01
WW-CEAST | December | Took station readings and entered into SharePoint,, reviewed trends - all good. Checked both compressors oil/belts - ok. Levelled off bin in the screening room and flushed out top screen of the auger as well as the drain hose. Went over and cleaned the top floor of the north building of the EQ tanks. Station running under normal ops - pump 2 is OOS. | Newmarket Sewage Pumping Station & Equalization Tank | 2025-12-15
WW-CEAST | December | Clean screen room Rotate bin as necessary Inspect site | Newmarket Sewage Pumping Station & Equalization Tank | 2025-12-27
WW-CEAST | December | Took station readings and entered into SharePoint,, reviewed trends - good pump flow and pump floor looks OK. Pushed bin back in and washed down floor. Completed the audible test with PS - all went well. Will be back after meeting. | Newmarket Sewage Pumping Station & Equalization Tank | 2025-12-19
WW-CEAST | December | On site in response to mech screen 1 overtorque alarm. Found the torque sensor arm slightly loose, tightened the connection and ran the screen on hand mode for 5 cycles. No issues observed. Changed out the rag bin. Cleaned the screen room and cleared the solids/rags on auger outlet as it was packed. | Newmarket Sewage Pumping Station & Equalization Tank | 2025-12-30
WW-CEAST | December | There?s a problem with bar screen 2 auger,, the rags weren?t dropping down. Got a ladder a started emptying the shoot from the top - got a little over half way and started pressing down with the fork and some rags started dropping. Watched the top of the auger and rags were coming out. Checked the top of bar screen 2 and the rags were moving and dropping down - all cleared. Shovelled mess on the floor into the bin and put tools/ladder back. All bar screens and augers back to auto and running forward. | Newmarket Sewage Pumping Station & Equalization Tank | 2025-12-19
WW-CEAST | December | -bar screen 1 overtorque alarm came back in, was addressed earlier in the day by Daniel Kim -bars screen 1 inlet gate closed for the night, barscreen will be investigated in the morning -likely it may need addressing by maintenance as this alarm has came in a few times in the last week -bar screen 2 remains in service | Newmarket Sewage Pumping Station & Equalization Tank | 2025-12-30
WW-CEAST | December | On site for Station Check (See details on SharePoint) All pumps available in auto duty rotation every 3 hours. Standby power generator available in auto. Checked dry well, ok. Checked bar screens, ok. | Newmarket Sewage Pumping Station & Equalization Tank | 2025-12-30
WW-CEAST | December | On site to install pump 2. The pump is wired and flooded and ready to run once the operators lock is off. | Newmarket Sewage Pumping Station & Equalization Tank | 2025-12-23
WW-CEAST | December | Station Check completed (See details on SharePoint). Bar screen 2 hopper was completely filled with rags. The surrounding area of the conveyor was a mess in the morning. Daniel helped with emptying the hopper and cleaning the mess on the floor. we took apart the top cover of the screen conveyor to clean and inspect. Once it was established nothing was stuck inside, Bill helped us in putting back the covers. We cleaned the floor with bleach towards the end. | Newmarket Sewage Pumping Station & Equalization Tank | 2025-12-22
WW-CEAST | December | Took station readings and entered into SharePoint,, reviewed trends - all looks good. Checked both compressors and the pump floor - all good and emptied the top part of the auger and flushed out both the screen at the top of the auger as well as the drain hose. Pushed the bin out for pick up and then washed down the floor and put a new bin in for the week. Marcos and I went downstairs and Marcos exercised all surge tank valves and flushed the transmitters while I exercised all the gates and washed down the floor a the gates in the wet well. Pump 2 is still OOS but the rest of the station is running under normal ops. | Newmarket Sewage Pumping Station & Equalization Tank | 2025-12-17
WW-CEAST | December | On site completed work orders. Put pump 2 back in service and in auto duty rotation after CMS fixed the problem. Ran for almost an hour without any issues encountered, producing great discharge flows. @ 0% speed 164 L/s, 150 kPa, 122 A, 384 V, 798 RPM, 40 Hz; @ 25% minimum auto setpoint speed 278 L/s, 139 kPa, 153 A, 432 V, 896 RPM, 45 Hz; @ 50% speed 333 L/s, 174 kPa, 182 A, 479 V, 995 RPM, 50 Hz Station Check (See details on SharePoint) All pumps available in auto duty rotation every 3 hours. Standby power generator available in auto. Checked dry well, ok. Checked bar screens, ok. Air Compressors Inspection and Cleaning Screen Bin Removal and Replacement - completed by Chris Rodie. Pushed out rag bins to be pick up by Miller Waste. | Newmarket Sewage Pumping Station & Equalization Tank | 2025-12-24
WW-CEAST | December | -on site for bar screen 1 over torque -reset bar screen monitored, took a few resets to start working normal again, rake is level, chains are on. -no issues visible -reset alarms -inlet gate can be closed remotely if it trips again tonight it can be investigated by mechanical tomorrow if it continues -site okay, pump 2 remains OOS, and will be reinstated tomorrow | Newmarket Sewage Pumping Station & Equalization Tank | 2025-12-23
WW-CEAST | December | Took station readings and entered into SharePoint,, reviewed trends - all good. Checked pump floor - no issues,, also checked scrubber filter screen , readings just over 2 but there?s no water to wash it off due to winter temps. Station running under normal ops - no issues were found. | Newmarket Bogart Creek Sewage Pumping Station | 2025-12-12
WW-CEAST | December | Took station readings and entered into SharePoint,, reviewed trends - all good,, checked pump floor - no issues. Contractor was here cleaning the over flow pipes out with someone from York region. Station running under normal ops - no issues were found. | Newmarket Bogart Creek Sewage Pumping Station | 2025-12-15
WW-CEAST | December | Here to complete WOs - verified operation of the seal water tank by lifting the float and allowing water to flow into the tank. Verified operation of all 3 cranes - 1 has controller and 2 are manual,, exercised all 4 suction valves and could only get actuators 2 & 3 to work in manual. | Newmarket Bogart Creek Sewage Pumping Station | 2025-12-02
WW-CEAST | December | Took station readings and entered into SharePoint,, informed ROC of the WOs I have,, completed Diesel test run - no issues with transfer of power either way and entered readings into SharePoint , also the dealer alarm/ dry well flood alarm and the alarm when testing the safety shower down stairs as well as the Hi/Low temp alarms - all were confirmed by ROC ( Adam). No Hazardous waste to dispose of, verified operation of the sump pumps and washed down floor after checking air valves,, check valves OK as well. Pump 1:@16%=82.1L/s,,Pump2@100%=204.7L/s,Pump 3:@16=101.1L/s and Pump 4@15%=80.6L/s. Also completed H&S inspection- no issues found. Also greased motors 1,2 & 4. All alarms were cleared and informed ROC station is working properly. | Newmarket Bogart Creek Sewage Pumping Station | 2025-12-01
WW-CEAST | December | Took station readings and entered into SharePoint,,, showed Kevin pump trends and how the Duty rotates,, explained pump 2 being a constant and that it is not part of the Duty rotation. Station running under normal ops - no issues were found. | Newmarket Bogart Creek Sewage Pumping Station | 2025-12-05
WW-CEAST | December | Took station readings and entered into SharePoint,, reviewed trends - all good. Checked pump floor - no issues,, station running under normal ops - no issues were found. | Newmarket Bogart Creek Sewage Pumping Station | 2025-12-08
WW-CEAST | December | -sump pumps not producing flow -pumped down flood in basement, site is dry now -pump 3 manual off as air valve is leaking water, can be ran in emergencies -Satnam Mann from electrical is on site to investigate pump issue -site is dry and sump pumps can be replaced tomorrow -portable sump pump issue setup to quickly pump down any future floods -site okay until tomorrow | Newmarket Bogart Creek Sewage Pumping Station | 2025-12-29
WW-CEAST | December | Took station readings and entered into SharePoint,, reviewed trends - all looks good. Checked pump floor - good. Station running under normal ops - no issues were found. | Newmarket Bogart Creek Sewage Pumping Station | 2025-12-19
WW-CEAST | December | -station check of site -Reviewed SCADA -inspected site -entered data into SharePoint -basement has a minor flood, sump pumps aren?t producing flow, yet they are on in auto and in hand, require maintenance?s help | Newmarket Bogart Creek Sewage Pumping Station | 2025-12-29
WW-CEAST | December | On site checked B2/sump pit for flooding issue due to sump pumps not working. Found flooded again. Ran sump pump installed temporarily. Found the cause of flooding. Seal water tank continues overflowing to the overflow drain. Tank float is broken. Closed valve for the meantime. CMS replaced with new sump pumps - ran tested, ok. Seal water tank overflow float replaced. Installed new tank level float. Cleared/reset all alarms. Also, remotely asked the assistance of PCS/SCADA (Kyle Carlen) for the seal water system alarm that won?t clear. Station back to normal operations. | Newmarket Bogart Creek Sewage Pumping Station | 2025-12-30
WW-CEAST | December | Weather today Mostly Cloudy and -1 Celsius -On site to complete work orders W11481211, W11414038. -perform a station check. -Entered station readings into SharePoint. -JHSC Health and Safety Inspection. -Open Sluice gate MV-2. | SEC Boxgove Corrosion Control Facility | 2025-12-02
WW-CEAST | December | On site completed work orders. Station Check (See details on SharePoint) H2O2 Pump 3 running in auto as duty 1 with a flow of 17.5 L/hr at 25% speed. H2O2 Pump 2 in auto as standby. H2O2 Pump 1 in manual. Peristaltic Pump Inspection | SEC Boxgove Corrosion Control Facility | 2025-12-09
WW-CEAST | December | Weather today Overcast and 1 Celsius -On site to complete work orders W11467524, W11466599, W11466438. -perform a station check. -Entered station readings into SharePoint. -Peristaltic pump Inspection. -Hydrogen Peroxide Chemical Ejectors. | SEC Boxgove Corrosion Control Facility | 2025-12-23
WW-CEAST | December | -station check of site -reviewed SCADA -inspected site -entered data into SharePoint -station okay | SEC Boxgove Corrosion Control Facility | 2025-12-30
WW-CEAST | December | On site for chemical pump 3 leak alarm Replaced tube in chemical pump 3 Tested pump 3, all three pumps are in auto Reviewed SCADA and reset alarms | SEC Boxgove Corrosion Control Facility | 2025-12-31
WW-CEAST | December | -Remotely placing Tank 1 Outlet Valve from manual to auto. Tank 1 is now operating in duty 1. Tank 1 is still filled with water and is being used to further test the chemical pumps during their warranty period until the next chemical delivery is made. Chemical Pump 3 running in auto, duty 1. -Also placed Chemical Pump 1 back into service, now also running in auto as duty 1. | SEC Boxgove Corrosion Control Facility | 2025-12-16
WW-CEAST | December | On site completed work orders. Station Check (See details on SharePoint) Fans 1 and 2 currently running in auto as duty 1 and 2, respectively. Fan 3 in auto, as standby. Standby power generator available in auto. Nutrient Tank Batch Mixing - filled tank 2 with water. Tanks 1 and 3 full. Odour Control Fans Impeller Bearing Lubricated Sump Pump Test/Maintenance Ventilation System Inspection Water Supply Pumps Actuators Exercised and Inspection Recirculation Pumps and Strainer Inspection | SEC Markham Odour Control Facility | 2025-12-09
WW-CEAST | December | On site for Ventilation System Inspection and Chemical Tank Inspection. | SEC Boxgove Corrosion Control Facility | 2025-12-16
WW-CEAST | December | Attending site to replace failing oxygen sensor (W11500466). SEOC_ODOR_G021 was replaced and SCADA alarms were cleared. ROC was notified after sensor replacement. | SEC Markham Odour Control Facility | 2025-12-09
WW-CEAST | December | Gather vibration readings for fans 1 and 2 Fan 3 is not working. | SEC Markham Odour Control Facility | 2025-12-05
WW-CEAST | December | Weather today Mostly Cloudy and -1 Celsius -On site to complete work order W11413929, W11413437, W11413950, W11413922, W11413451, W11413458. -Completed station check. -Entered station and Generator readings into SharePoint. -Fans 2 and 3 currently running in auto as duty 2 and 1, respectively. Fan 1 in standby. -Nutrient Tank Batch Mixing - all nutrient tanks have water. -Odour Control Fans Impeller Bearing Lubrication Hoist System Inspection -Blower Inspection -JHSC Health and Safety Inspection - 11 lighting fixtures at the Carbon Unit Room and 3 lighting fixtures at the Fans Room, not working. These are previously reported and request already submitted to CMS. Standby Power Generator Test Run - pre-test checked, ok. -Generator started and stopped without a problem. -Cleared/reset all alarms created by doing this work order. -Generator back to auto and available. -Station back to normal operations. | SEC Markham Odour Control Facility | 2025-12-02
WW-CEAST | December | -station check of site -reviewed SCADA -inspected site -entered data into SharePoint -station okay | SEC Markham Odour Control Facility | 2025-12-30
WW-CEAST | December | On site to complete work order. Mist Eliminator Filters Cleaned and Replace - some dirty filters replaced (Needs some more to replace). Mist eliminators are ok. Also, cleared/reset alarm regarding damper flood alarm. Chamber dewatered. | SEC Markham Odour Control Facility | 2025-12-16
WW-CEAST | December | Weather today Partly Cloudy and -11 Celsius -On site to complete work orders W11423114, W11441264, W11441794, W22777, W11441823. -Completed station check. -Entered station readings into SharePoint. -Fan 1 currently running in auto. -Fan 2 in auto as standby. -JHSC Health and Safety inspection. -Electric Valve actuator exercise and inspection. -Heat trace system inspection. -Standby Power Generator test run. -Standby power generator available in auto -All gas monitors have normal readings. -Station operations normal. | SEC Fairport Air Handling Facility (Shaft 4) | 2025-12-11
WW-CEAST | December | Onsite to repair fan belts and check pulley alignment. Corrected fan motor pulley misalignment replaced faulty belts blower 1-2 Both fans back in auto available | SEC Fairport Air Handling Facility (Shaft 4) | 2025-12-02
WW-CEAST | December | Weather today Partly Cloudy and 5 Celsius -On site to complete work order W11457225. -Completed station check. -Entered station readings into SharePoint. -Fan 2 currently running in auto. -Fan 1 in auto as standby. -Standby power generator available in auto -All gas monitors have normal readings. -Station operations normal. | SEC Fairport Air Handling Facility (Shaft 4) | 2025-12-18
WW-CEAST | December | Weather today Snow and -9 Celsius -On site to complete work orders W11411443, W11422812. -Completed station check. -Entered station readings into SharePoint. -Fan 1 currently running in auto. -Fan 2 in auto as standby. -Standby power generator available in auto -All gas monitors have normal readings. -Station operations normal. | SEC Fairport Air Handling Facility (Shaft 4) | 2025-12-05
WW-CEAST | December | Collect vibration readings on motors and fans. | SEC Fairport Air Handling Facility (Shaft 4) | 2025-12-05
WW-CEAST | December | Weather today Snow and -9 Celsius -On site to complete work orders W11411443, W11422690, W11422494, W1141906. -Completed station check. -Entered station readings into SharePoint. -Fan 1 currently running in auto as duty 1 with an airflow of 25,650 m3/hr at 0% speed. -Fan 2 in auto as standby. -Electric valve actuator exercise and inspection. -Standby Power Generator test run. -Standby power generator available in auto -All gas monitors have normal readings. -Station operations normal. | SEC Altona Air Handling Facility (Shaft 6/7) | 2025-12-04
WW-CEAST | December | Weather today Partly Cloudy and -11 Celsius -On site to complete work orders W1141201, W11441931, W11441921, W11441604. -Completed station check. -Entered station readings into SharePoint. -Fan 1 currently running in auto as duty 1 with an airflow of 25,650 m3/hr at 0% speed. -Fan 2 in auto as standby. -Hoist system inspection. -Ventilation system inspection. -Heat trace system inspection. -Standby power generator available in auto -All gas monitors have normal readings. -Station operations normal. | SEC Altona Air Handling Facility (Shaft 6/7) | 2025-12-11
WW-CEAST | December | Weather today Snow and -7 Celsius -On site to complete work order W11448485. -On site to perform a station check. -Unable to unlock gate the e-key padlock is malfunctioning. -Station appears to be operating normal. -Fan is running, condensate is draining, no odours detected on site. | Bayview & Steeles Air Management Facility | 2025-12-15
WW-CEAST | December | Weather today Overcast and -7 Celsius -On site to complete work order W11422680. -JHSC Health and Safety inspection. | SEC Altona Air Handling Facility (Shaft 6/7) | 2025-12-05
WW-CEAST | December | Weather today Clear and -5 Celsius -On site to complete work order W11430601. -JHSC Heath and Safety inspection. -On site to perform a station check. -Heater element: 94.9 F. -Hydro meter: 267562 kWh. -Station is operating normally. -Fan is running, condensate is draining, no odours detected on site. | Bayview & Steeles Air Management Facility | 2025-12-08
WW-CEAST | December | Weather today A few clouds and -4 Celsius -On site to complete work order W11464243. -On site to perform a station check. -Heater element: 100.7 F. -Hydro meter: 270037 kWh. -Station is operating normally. -Fan is running, condensate is draining, no odours detected on site. | Bayview & Steeles Air Management Facility | 2025-12-22
WW-CEAST | November | Replaced filters for the mist eliminators and took them back to Leslie PS and washed them out,,, Hydro: 265841Kwh and heater: 99.1 degrees. No odour detected and station running under normal ops. | Bayview & Steeles Air Management Facility | 2025-11-28
WW-CEAST | December | Weather today Clear and -14 Celsius -On site to complete work orders W11410471, W11410762. -JHSC Heath and Safety inspection. -On site to perform a station check. -Heater element: 106.7 F. -Hydro meter: 266349 kWh. -Station is operating normally. -Fan is running, condensate is draining, no odours detected on site. | Bayview & Steeles Air Management Facility | 2025-12-01
WW-CEAST | December | On site for Station Check. Heater Element - 93.6 F Hydro Meter Reading - 271448 kWh VFD Chiller no reading. Fan and motor running. No bad smell at time of site visit. Station operations normal. | Bayview & Steeles Air Management Facility | 2025-12-29
WW-CEAST | December | -On site to complete work orders. -Turned off fan from 10:40-10:55am for maintenance activities. -Removed all old mist eliminator filters and replaced with clean spare filters. -Mist eliminator filter, clean & replace completed. -Odour control scrubber inspection, filter cleaning completed. -Fan placed back into service and Fan Not Running dialer alarm reset before leaving site. | Bayview & Steeles Air Management Facility | 2025-12-17
WW-CEAST | December | Weather today Snow and -9 Celsius -On site to complete work orders W11411443, W11422833, W11422480, W11422198, W11423207. -Completed station check. -Entered station readings into SharePoint. -JHSC Health and Safety inspection. -Nutrient tanks batch mixing - pumps offline. Tanks full. -Fan 1 running in auto. -Fan 2 running in auto. -Standby Power Generator test run. -Standby power generator available in auto. | SEC Pickering Odour Control Facility (York/Durham) | 2025-12-04
WW-CEAST | December | Weather today Partly Cloudy and -11 Celsius -On site to complete work orders W1141285, W11440813. -Completed station check. -Entered station readings into SharePoint. -Nutrient tanks batch mixing - pumps offline. Tanks full. -Fan 1 in Local electrical currently working on VFD for fan 1. -Fan 2 running in auto. -Standby Power Generator test run. -Standby power generator available in auto. | SEC Pickering Odour Control Facility (York/Durham) | 2025-12-11
WW-CEAST | December | -station check of site -inspected site -reviewed SCADA -entered data into SharePoint -nutrient tank batching -station okay | SEC Pickering Odour Control Facility (York/Durham) | 2025-12-30
WW-CEAST | December | On site for sluice gate valves exercises. York Durham Boundary Meter Chamber, Chamber 34-BONMC Outlet (In front of YDOC) York Durham Boundary Meter Chamber, Chamber 34-BONMC Inlet (In front of YDOC) YDSS Interceptor Sewer Control Valve Chamber, Chamber T0618-01 (Leslie/South of 19th Ave) Richmond Hill Aurora WW Meter Chamber 3393131-GVSOUTH (Yonge/Bloomington) | Central-East Wastewater Linear System | 2025-12-23
WW-CEAST | December | Weather today Partly Cloudy and 5 Celsius -On site to complete work orders W11457246, W11456907, W11471894. -Completed station check. -Entered station readings into SharePoint. -Blower inspection. -Nutrient tanks batch mixing - pumps offline. Tanks full. -Fan 1 in auto but not running electrical wil return to work on the VFD for fan 1. -Fan 2 running in auto. -Standby Power Generator test run. -Standby power generator available in auto. | SEC Pickering Odour Control Facility (York/Durham) | 2025-12-18
WW-CEAST | December | Weather today Overcast and 1 Celsius -On site to complete work orders W11466563, W11466557, W11466217. -Completed station check. -Entered station readings into SharePoint. -impeller bearing lubrication. -Nutrient tanks batch mixing and tanks are full. -Fan 1 running in auto. -Fan 2 running in auto. -Standby power generator available in auto. | SEC Pickering Odour Control Facility (York/Durham) | 2025-12-23
WW-WEST | December | Completed the station check Entered data into SharePoint Test ran rs pumps Everything operating as intended | Vaughan Black Creek Pumping Station | 2025-12-12
WW-CEAST | December | -visually inspected 3 Mount Albert Forcemain chambers for infiltration and damage -no issues present, chambers are dry -inspected outfall for Mount Albert WRRF, no issues | Central-East Wastewater Linear System | 2025-12-19
WW-WEST | December | Completed the Check valve inspection, Dry well flood alarm test, Sump pit inspection, RS pump / motor inspection, RS pump ball valve and actuator inspection, Suction valve and actuator inspection / exercise, High low temp alarm test Inspected and cleaned the wet well Cleaned and lubricated the barscreen | Vaughan Black Creek Pumping Station | 2025-12-11
WW-WEST | December | Remotely cleared building room temperature Lo Lo north and south alarm. Cleared suction fan and exhaust fan alarms. Cleared screen differential high alarm | Vaughan Black Creek Pumping Station | 2025-12-08
WW-WEST | December | Remotely Rotated Scrubber Blower Duties. Blower #2 in Duty #1. | Vaughan Black Creek Pumping Station | 2025-12-04
WW-WEST | December | Checked station and trends, and recorded readings on SharePoint Levelled bin and cleaned area | Vaughan Black Creek Pumping Station | 2025-12-02
WW-WEST | December | On site to install new south forcemain drain valve nut bushing. Checked flange bolts to ensure tightness. Tested valve movement. Valve is ready to be put back in service. | Vaughan Black Creek Pumping Station | 2025-12-03
WW-WEST | December | - Checked station and recorded readings on SharePoint - Levelled bin - Notified supervisor to escalate the previously created archibus to address the black creek Lo Lo temperature - Performed weekly pump test. Ran each pumps 1-5 manually, one at a time, and recorded readings. Check valve for pump 3 not closing. Work order already created Pump 1: 587 L/s, pressure 295 kPa Pump 2: 452 L/s at 100%, pressure 266 kPa Pump 3: 128 L/s at 100% speed, pressure 214 kPa Pump 4: 465 L/s at 100% speed, pressure 279 kPa Pump 5: 561 L/s at 100% speed, pressure 286 kPa - seal water pressure relieve valve tested. Cleaned strainers after isolating, all very clean. checked valve operation. No issues - Found leak on service water line and the insulation is full of water. Does not seem like condensation due to the sheer amount water dripping. Located on B1. Created work order - Found another leak on the sanitary drain prime line located on B1. WO created | Vaughan Black Creek Pumping Station | 2025-12-05
WW-WEST | December | - Levelled bin and pushed bin out - Performed JHSC inspection. No issues - Performed station check and recorded readings on SharePoint. No new issues. Building low temperature resolved - Notified ROC of the work being performed - Tested low and high temperature alarm. alarm received - Reduced seal water pressure - Inspected the generators and fuel level. Generator 1 has a coolant leak near the engine and coolant line rubber connection. Tightened the rubber connection to stop the leak. Started the generator at 10:48. Recorded readings on SharePoint after 30 minutes, no issues. Ran for approximately one hour. Runtime for generator 1 from 476.9 hrs to 477.9 hrs - Started generator 2 at 12:00. Recorded readings after 30 minutes. Run time for generator 2 from 489.6 hrs to 490.6 hrs. No issues with readings. - Fuel level readings before: 98 cm (6300 L). After gen test 97 cm (6180 L) - Checked for hazardous waste. None found - Inspected the odour control unit. Belt was noisy and became much more quiet after fittings were greased. Filters below 2.5 inch and does not need cleaning - Reset alarms caused by generator test. | Vaughan Black Creek Pumping Station | 2025-12-09
WW-WEST | December | Returned empty bin. Completed station check. No issues found. | Vaughan Black Creek Pumping Station | 2025-12-30
WW-WEST | December | - Raked bin and cleaned area. Pushed bin out for pickup - Checked screen and topped up oil hopper - Performed weekly pump test. Ran each pumps 1-5 manually, one at a time, and recorded readings. Check valve for pump 3 not closing. Work order already created Pump 1: 573 L/s, pressure 304 kPa Pump 2: 446 L/s at 100%, pressure 267 kPa Pump 3: 130.7 L/s at 100% speed, pressure 215 kPa Pump 4: 457 L/s at 100% speed, pressure 271 kPa Pump 5: 560.9 L/s at 100% speed, pressure 288 kPa - bell contractor onsite working on security system - Checked station and recorded readings on SharePoint. Reset tripped radiator fan 3 | Vaughan Black Creek Pumping Station | 2025-12-23
WW-WEST | December | Completed the station check Entered data into SharePoint Pushed the rag bins back inside Inspected the force main chamber Inspected the hoist | Vaughan Humber Pumping Station | 2025-12-12
WW-WEST | December | - Inspected and flushed air relief valves for north and south forcemain - Performed station check and recorded readings on SharePoint. No new issues - Bell contractor onsite with York employee to work on the security system - To place forcemain 1 back into service. Manually drew down the wet well with pump 2. Placed all pumps off (e stop alarm triggered). Then closed interconnect valve between forcemain 1 and 2. Opened forcemain 1 isolation valve. - Used pump 2 VFD pump set at 0% manual speed to repressurize the forcemain 1s. Slowly ramped up speed to 60%. South forcemain discharge pressure Lo Lo and Lo alarm triggered - Once done, placed all pumps back in service and in duty rotation, and in auto speed. No issues - Put up overflow signage near the overflow discharge point | Vaughan Black Creek Pumping Station | 2025-12-16
WW-WEST | December | Completed the station check Entered data into SharePoint Test ran all rs pumps Everything operating as intended | Vaughan Black Creek Pumping Station | 2025-12-19
WW-WEST | December | In to Complete Scheduled WO. Reviewed SCADA and Trends. No Issues Found. Screen Room Roll Up Door Frozen. Main Breaker Tripped On Attempt to Open. Reset Breaker, However, No Power Returned to Unit. No Additional Breaker Found Tripped within Electrical Panel. Deactivated Main Breaker. Notified TL and Supervisor. Levelled and Adjusted Bins. No Other Issues Found. | Vaughan Humber Pumping Station | 2025-12-14
WW-WEST | December | - On site for weekly regulatory samples - Checked station and recorded readings on SharePoint. No new issues - Pushed bin out for pick up | Vaughan Humber Pumping Station | 2025-12-02
WW-WEST | December | Completed the station check Entered the data into sharepoint Test ran the generator Placed pumps in manual off for each power transfer Inspected the generator heat exchanger Completed the JHSC inspection Placed the rag bins outside for pick up Completed the consolidated dry well inspection Tested the dry well flood alarm Tested the sump pit Tested the high low temperature alarms Tested the auto dialer Test ran the RS pumps in manual P1 ? 642L/s ? 442kpa P2 ? 644.8L/s ? 434kpa P3 ? 585.6L/s ? 510kpa P4 ? 507.9L/s ? 616kpa P5 ? 507.8L/s ? 581kpa | Vaughan Humber Pumping Station | 2025-12-09
WW-WEST | December | In to Complete Scheduled WO. Reviewed SCADA and Trends. No Issues Found. Levelled and Adjusted Bins. No Issues Found. | Vaughan Humber Pumping Station | 2025-12-07
WW-WEST | December | Checked station and trends, and recorded readings on SharePoint. No new issues Levelled bin | Vaughan Humber Pumping Station | 2025-12-05
WW-WEST | December | Leveled the rag bins Everything operating as intended | Vaughan Humber Pumping Station | 2025-12-27
WW-WEST | December | Collected the weekly raw sewage sample | Vaughan Humber Pumping Station | 2025-12-09
WW-WEST | December | On site to look at check valves 2 and3. Tighten the packing on 2 and stopped the leak. Had the operators removed the locks from pump 3. Back flow is about 4 ls which does not drive the pump. The pump can be left in duty and if the back flow gets worse we will revisit it at a later date | Vaughan Humber Pumping Station | 2025-12-24
WW-WEST | December | Placed rag bins back inside Put pump 3 back in service and test ran it to ensure proper check valve operation Everything operating as intended | Vaughan Humber Pumping Station | 2025-12-24
WW-WEST | December | Onsite to place bar screen 2 back in auto. | Vaughan Humber Pumping Station | 2025-12-30
WW-WEST | December | Completed the station Check Entered data into SharePoint Pushed the rag bins outside for pick up Cleaned and lubricated the bar screen Tested the wet well overflow alarm and confirmed roc received the alarm Everything operating as intended | Vaughan Humber Pumping Station | 2025-12-16
WW-WEST | December | Raked bins. | Vaughan Humber Pumping Station | 2025-12-21
WW-WEST | December | - Pushed bin out for pickup - Checked station and recorded readings on SharePoint - Found pump 2 check valve o ring/seal leaking. Created work order - Found pump 3 check valve not fully closing. Created work order. Placed pump 3 out of service and locked out and tagged out. Fully closed inlet and discharge valve, and locked out and tagged out. - Collected weekly regulatory samples | Vaughan Humber Pumping Station | 2025-12-23
WW-WEST | December | Collected the weekly sewage sample | Vaughan Humber Pumping Station | 2025-12-16
WW-WEST | December | Completed the station check Entered data into SharePoint Collected weekly samples Pushed rag bins outside Everything operating as intended | Vaughan Humber Pumping Station | 2025-12-30
WW-WEST | December | Remotely Responded to Filter #2 Inlet Gate Valve Failed to Open Alarm Communicated by the ROC. Acknowledged and Reset Alarm. Cycled Valve in Manual with No Issues. Returned to Auto and Placed in Duty #1, No Recurrence of Alarm. Notified ROC and Updated SCADA Shift Report. | Kleinburg Water Resource Recovery Facility | 2025-12-13
WW-WEST | December | Station checks, SharePoint readings and review of continuous monitoring data. Push in empty miller waste bins. Level rags in bins under mechanical screens. | Vaughan Humber Pumping Station | 2025-12-19
WW-WEST | December | Completed daily lab and station check - no new issues added data into SharePoint. Set final effluent sampler for Sunday Turned RAS off at 8:40am and manually wasted 8m3 per clarifier from 10am to 10:50am. RAS back in operation upon wasting completion. Inspected circular plant aeration blowers. Belts and oil levels good. Ran each blower manually with no issues. Opened WAS_MV3 to sludge holding tank to work on WAS pump 3. Isolated WAS pump 3 and placed into LOTO. De-ragged pump. Pump still seized and unable to run after trying to run in manual. Dan, Young, and Harie onsite to assist. Placed WAS pump 3 back into LOTO and isolated. Was able to get the rest of the rags out and able to move the coupler. Put WAS pump 3 back online and ran manually with no issues. Returned WAS_MV3 to closed. | Kleinburg Water Resource Recovery Facility | 2025-12-12
WW-WEST | December | In to Complete Scheduled WOs. Topped Up Soda Ash Hopper ?> 14 Bags. Inspected Filter #2 Inlet Gate Valve. No Mechanical Issues Found. WAS Pump #1 and 2 Manual On and Off Intermittently and Sequentially for Wasting. Wasting Complete, Reset Batch Wasting Set-point. RAS Pumps #1 and 3 Running in Auto. Wasted 10 m3 from Each Clarifier. | Kleinburg Water Resource Recovery Facility | 2025-12-14
WW-WEST | December | Remotely Enabled Batch Waste Set-point. RAS Pumps Auto Off in Preparation for Wasting @ 10:15. | Kleinburg Water Resource Recovery Facility | 2025-12-14
WW-WEST | December | Collected regulatory samples. Completed daily lab and station check. Added data into SharePoint. Added 7 bags of soda ash to hopper. Inspected odour control unit and completed data sheet. Auto wasted 30m3 from 10am-12pm. Manually wasted an extra 10m3 from clarifier 1. Resumed RAS upon wasting completion Winterized diversion tank. | Kleinburg Water Resource Recovery Facility | 2025-12-02
WW-WEST | December | Completed daily lab and station check no new issues added data into SharePoint. Enabled batch wasting mode at 10am and set auto waste for 20m3 from 11am to 12pm. Manually wasted an extra 5m3 from clarifier 2. RAS returned to operation when wasting complete. Added 8 bags of soda ash to hopper. Cleaned rags from bar screen and confirmed operation. Manually ran filters to confirm operation and hosed filters down. Opened WAS_MV3 to sludge holding to clear interlock on WAS pumps 3 and 4 to complete monthly inspection. WAS pump 4 low on oil due to loose bolt. Tightened bolt and added extra oil. Ran pump locally and confirmed operation. Placed pump back into local off. WAS pump 3 oil level good. Ran manually and coupler seized shortly after running. Stopped pump and placed back into local off. Informed team lead of pump seizing for further investigation. Returned WAS_MV3 to close to sludge holding tank | Kleinburg Water Resource Recovery Facility | 2025-12-11
WW-WEST | December | Reset Filter Reject sump pump 1 e stop alarm and cleared, ran multiple cycles without tripping again- continuing to monitor throughout the day. Completed daily lab and station check - no new issues added data into SharePoint. Enabled batch wasting mode at 9am and set WAS to auto waste to waste 20m3 from 10am to 11am wasting 10m3 from each clarifier. Reset RAS pumps upon wasting completion. Increased soda ash dosage from 7.25seconds/h to 7.50seconds/h. Due to decreased alkalinity results in lab. Added 8 bags of soda ash to hopper, cleaned bar screen and distribution chamber stem. Inspected RSHW_BLO 1 and 2. Both have good oil levels and clean filters. Ran both to confirm operation. Cleared rags from aeration tank. Noticed leak on effluent hydrant beside aeration tank getting worse, created WO- W11516113. Released condensation from aeration tank lines. | Kleinburg Water Resource Recovery Facility | 2025-12-15
WW-WEST | December | Remotely Responded to Reject Sump Pump #1 E-Stop Alarm Communicated by the ROC. Alarm has been Recurrent and Requires Closer Maintenance Inspection. Created WO ?> W11515727. Alarm Remains Outstanding. | Kleinburg Water Resource Recovery Facility | 2025-12-15
WW-WEST | December | Completed daily lab and station check - no new issues added data to SharePoint. Enabled batch wasting mode at 9:10am and began wasting at 9:50am. Wasted 15m3 from each clarifier. Total of 30m3 wasted. RAS pumps resumed after wasting completed Added 10bags of soda ash to hopper. Cleared rags from bar screen. Confirmed headworks heat trace is operating. Exercised distribution chamber butterfly valves and picked rags from distribution chamber stem. Cleaned and verified D.O probes. Ran hose from hydrant to aeration outlet to help with foam in aeration tanks. Inspected both final effluent and raw samplers - both in good shape and programmed to run. Called ROC to inform of hi level sump alarms being tested. Confirmed pump, float operation and high level alarm of the headworks sump pit. Confirmed pump, float operation and high level alarm in tertiary building sump pit. | Kleinburg Water Resource Recovery Facility | 2025-12-10
WW-WEST | December | Completed daily lab and station check - added data Into SharePoint. Turned RAS off at 8:27am and set WAS to waste 30m3 from 9am to 11am. RAS resumed when wasting completed. WAS set back to manual. Added 8 bags of soda ash into hopper. Increased soda ash dosage run time from 6.75seconds/h to 7.00seconds/h. Exercised RAS/WAS valves. Alum line to aeration tank 2 still frozen. Dan Hirstwood onsite to attempt to melt ice in lines but unsuccessful. Maintenance will be onsite tomorrow to try to replace line. Leaving aeration tank 2 inlet gates closed until alum line is fixed. | Kleinburg Water Resource Recovery Facility | 2025-12-04
WW-WEST | December | Completed daily lab and station check - no new issues added data into SharePoint. Turned RAS pumps off at 9:45am. Manually wasted 10m3 per clarifier between 10:40am and 11:40am. RAS put back into operation upon wasting completion. Increased soda ash runtime from 7.00seconds/h to 7.25seconds/h Maintenance onsite to fix frozen alum line - work on alum line completed, opened valve to alum so alum is dosing to aeration tank 2. Alum dosing for tank 2 set to 140mg/L Alum dosing for tank 1 lowered from 275mg/L to 140mg/L. Bill is also working on hydrant leak. Hydrant leak repaired Opened inlet gate to Aeration tank 2 which is now full and back online. Adjusting air valves to balance DO. Opened clarifier 2 RAS valve to aeration tank 2. RAS now flowing from clarifier 1 to aeration tank 1 and clarifier 2 to aeration tank 2. Interconnect between aeration tanks closed. Unshelved aeration tank 2 DO and TSS out of range alarms: KBSPR_AER_TK2_NIT1_FLT_SHLV KBSPR_AER_TK2_AIT2_OOR_SHLV KBSPR_AER_TK2_AIT1_OOR_SHLV Added 9 bags of soda ash to hopper. | Kleinburg Water Resource Recovery Facility | 2025-12-05
WW-WEST | December | - Received alum delivery at 8:00. Signed all papers and checked authenticity, all okay. Received alum from 0.81 m to 3.48 m. - Pumped down scum tank in manual - GFL took a load of sludge - Transferred sludge from the thickening tank 2 to the holding tank - Performed in-house lab and recorded readings on SharePoint - Added 9 bags of soda ash into the hopper - Enabled RAS batch wasting mode at 8:10. Wasted 16.43 m^3 from train 1 and 3.46 m^3 from train 2 then reset RAS batch wasting mode once done - Checked station and recorded readings on SharePoint - Unclogged a drain in the soda ash room - Checked for rags on aeration tank outlet. None found - Cleaned lab and took out garbage - Enabled aeration basin 2 back DO on aeration blower setpoints. Lowered aeration basin DO setpoints to 3.00 ppm from 3.3 ppm | Kleinburg Water Resource Recovery Facility | 2025-12-08
WW-WEST | December | Alum dosing line was frozen including the saturated insulation wrap from the dosing point to the wall. Plumbed in a new dosing point at the end of the aeration and thawed line from wall out. Confirmed flow and operations put the alum back into service. Tank 2 DO and TSS probes reinstalled as well. Aeration tank 2 back in service. | Kleinburg Water Resource Recovery Facility | 2025-12-05
WW-WEST | December | In to Complete Scheduled WOs. Topped Up Soda Ash Hopper ?> 15 Bags. Enabled Batch Waste Set-point. RAS Pumps Auto Off in Preparation for Wasting @ 08:40. Placed Clarifier Helical Skimmers in Manual On for Scum Tank Flushing. Returned to Auto and Service. Found Screening Press Drain Line and Dewatering Screen Clogged. Flushed Drainage Line and Screen, Cleaned and Tidied HWs. WAS Pump #1 and 2 Manual On and Off Intermittently and Sequentially for Wasting. Wasting Complete, Reset Batch Wasting Set-point. RAS Pumps #2 and 4 Running in Auto. Wasted 15 m3 from Each Clarifier. | Kleinburg Water Resource Recovery Facility | 2025-12-07
WW-WEST | December | GFL On-site for Sludge Load. Remotely Placed Sludge Thickening Tank #1 and 2 Outlet Valves in Manual Open, Transferred Thickened Sludge. Outlet Valves Returned to Manual Closed. | Kleinburg Water Resource Recovery Facility | 2025-12-03
WW-WEST | December | Attending site to check SECT_FIT1 issues (W11500632). Checked FIT for faults and simulated flow by injecting mA onto the loop. ROC was notified before and after maintenance work was performed. | Kleinburg Water Resource Recovery Facility | 2025-12-09
WW-WEST | December | Completed daily lab and station check - added data into SharePoint. Water Hydrant by aeration tanks frozen and cracked - put wash pumps into manual off to isolate until it can be fixed. Alum line to aeration tank frozen 2 frozen - hot water turned on to try to melt through ice build up. Aeration tank 2 cleaning completed - began filling tank 2, opened inlet valve to fill and put 2 pumps in tank 1 to pump to tank 2. Closing inlet valve overnight but leaving pumps on. Due to filling tank 2, low flow through filters and UVs causing alarms. UV is on and treating. UV ch 1 common minor alm UV ch1 low flow alm UV ch 2 common minor alm UV ch 2 low flow alm. Enabled wasting mode at 10am and set WAS pumps to auto waste 30m3 from 11am to 1pm. Upon wasting completion RAS pumps back in operation. Added 6 bags of soda ash to hopper Cleaned and verified DO probes. | Kleinburg Water Resource Recovery Facility | 2025-12-03
WW-WEST | December | Wessuc onsite to continue aeration tank 2 clean. Daily lab completed and data added into SharePoint. Enabled wasting mode at 10am and set WAS pumps to auto to auto waste 15m3 from each tank between 11am and 1pm. Upon wasting completion WAS pumps placed back into manual and RAS placed back in operation. Cleaned scum tank. Bled condensation from aeration lines. Removed rags from aeration outlet. Added 8 bags of soda ash to hopper. Increased soda ash set points from 6.25seconds/h to 6.50seconds/h. Confirmed soda ash hopper is functioning properly. | Kleinburg Water Resource Recovery Facility | 2025-12-01
WW-WEST | December | Diversion tank header was frozen. Thawed out header and reseated pump. Pump flow established and eventually pushed through the ice and is now at full capacity. Diversion tank has dropped approx 10? from start. Ops will continue to monitor and once pumped will winterize the header today. | Kleinburg Water Resource Recovery Facility | 2025-12-02
WW-WEST | December | Collected weekly regulatory samples. Completed daily lab and station check - no new issues. Added data into SharePoint. Wasted 15.04m3 from clarifier 1 and wasted 10.07m3 from clarifier 2. Added 8 bags of soda ash to hopper. Completed odour control unit inspection and filled inspection sheet. Created WO for outstanding generator room temp alarm. Filter reject sump pump 1, RSMP_PMP1 - E stop alarm came in at 2:21pm after pump ran - found breaker had tripped in MCC room. Reset breaker and cleared alarm. RSMP_PMP1 ran in duty with no issues. Will continue to monitor. | Kleinburg Water Resource Recovery Facility | 2025-12-09
WW-WEST | December | Decanted sludge thickening tank. Transferred remaining sludge to holding. Completed daily lab and station check - no new issues. Added data into SharePoint. Enabled batch wasting at 10:30am and set auto waste for 40m3 from 11am to 1pm. RAS back in operation upon wasting completion. WAS pumps back in manual. Added 10 bags of soda ash to hopper. | Kleinburg Water Resource Recovery Facility | 2025-12-19
WW-WEST | December | Harie Rajamithiran(OIT) working under the direction of Daniel Hirstwood(OIC) -Entered aeration tank#2 for maintenance activities, replaced worn out membrane diffusers, added new membrane diffusers and caps on empty heads -Started filling aeration tank#2 using 2 submersible pumps with flow coming from aeration tank#1 -Opened inlet gate to aeration tank#2 -Alum lines are frozen on aeration tank#2, torched the ends a little bit to try and melt the ice, unsuccessful and will attempt again tomorrow -Discovered a leak at the hydrant near aeration tank#1, maintenance was arrived and made a temporary patch. To drain the hydrant, wash pumps were turned off and maintenance will come back to fix the hydrant. | Kleinburg Water Resource Recovery Facility | 2025-12-03
WW-WEST | December | Attending site to check error on Alum tank LIT (W11475752). There are currently no active alarms in the device. Power to the device was cycled. Will monitor SCADA and close work order if issue does not happen again before the tank is filled on December 8. ROC was notified before and after maintenance activity. | Kleinburg Water Resource Recovery Facility | 2025-12-01
WW-WEST | December | - Wessuc arrived on site to continue work on the aeration tank and pump out diversion tank - Diversion tank is roughly 1 m full and the pumps are frozen. Opened diversion valve by 46% to allow very little flow of sewage into the diversion tank to melt the frozen layer and pumps. Once done, closed the diversion valve and pumped contents back into the headworks. Diversion flow detected alarm triggered due to this. - Notified ROC of the work being performed - Performed JHSC inspection. All okay. Received eyewash alarms - Checked for hazardous waste. None found - Inspected vortex blowers 1 and 2. Filters, belt and oil are all okay. Tested in hand to observe operation, all okay. Checked bin for grit, no issues - Inspected the generator and fuel level, all okay. Started the generator at 10:10. Recorded readings on SharePoint after 30 minutes, no issues. Ran for approximately one hour. Runtime for generator 1 from 424.4 hrs to 425.3 hrs - Started generator 2 at 12:04. Recorded readings after 30 minutes. Run time for generator 2 from 400.6 hrs to 401.8 hrs. No issues with readings. - Fuel level readings before: tank 1 at 0.91 m, tank 2 at 0.93 m, and gen 2 day tank at 1.11 m. Fuel readings after: tank 1 at 0.91 m, tank 2 at 0.93 m, and gen 2 day tank at 1.1 - Cleared UV alarms caused by the generator tests. UV dose was applied at all times - Inspected diversion tank blowers 1 and 2. Filters, belt and oil are all okay. Test ran both with no issues. Triggered diversion tank uncommanded stop and general alarm - Started filling the offline clarifier to prevent components from freezing | Kleinburg Water Resource Recovery Facility | 2025-12-01
WW-WEST | December | - Notified ROC of the work being performed - Unplugged submersible pump that?s pumping into aeration tank 2 - Closed all aeration tank outlet gates to push mlss into tank 2. Once nearly full. Reopened south outlet gates on tank 2 - Inspected sludge tank blower 1 and 2. Filters, belt and oil are all okay. Triggered out of range, e stop and temperature alarms - Inspected aeration blower 1. Filters, belt and oil are all okay. Switched main duty to aeration 1 after to inspect blower 2. Triggered e stop alarm - Inspected aeration blower 2. Filters, belt and oil are all okay. Triggered e stop alarm - Exercised scum tank 3 valve. Fully opened scum tank valve and closed - Inspected circular plant clarifier and drive. Oil is all good. Did not test run due to hose being placed inside to fill with water to winterize and potential to get caught. - Inspected RAS pumps 1-4. No issues. Oil and coupling are all good - Inspected WAS pumps 1-2. No issues. Oil and coupling are all good | Kleinburg Water Resource Recovery Facility | 2025-12-04
WW-WEST | December | In Responding to Reject Sump Pump #1 E-Stop Alarm. Contacted Maintenance (Elec.) for Assistance. Maintenance Investigation Rendered Faulty Pump Safe Relay, Replaced Unit and Tightened Loose Connections. No Other Issues Found. Tested Pump in Local, Several Inconsistent Breaker Trips Occurred. Reset Fault and Returned to Duty for In Service Testing. Cleared Associated Alarms. Notified ROC and Updated Shift Report. | Kleinburg Water Resource Recovery Facility | 2025-12-09
WW-WEST | December | In KBSPCP PAC - modify the low flow cut-off(clamp) from 0.5 to 2.0 in the AI AOI for SECT_FIT1 to match instrumentation's change that was applied earlier this week. | Kleinburg Water Resource Recovery Facility | 2025-12-19
WW-WEST | December | Auto wasting 25m3 from each clarifier Added 16 bags of soda ash to the hopper | Kleinburg Water Resource Recovery Facility | 2025-12-27
WW-WEST | December | - Notified ROC of the work order being performed - Performed annual alum pump drawdown test. Replaced couple alum connection while performing the work. Will correct the issue sometime in the future. Pump 1,2, 4, 6 are at or above the rated pump capacity. Pump 3 is 2 l/s less than the rated capacity at 17.1 l/s. Could not do drawdown test on pump 5 due to crystallization on the drawdown cylinder. - sent the results and graph to team lead and supervisor - checked the alum pump duties, calving and dosage after the work order is complete. Reset alarms generated due to the work | Kleinburg Water Resource Recovery Facility | 2025-12-18
WW-WEST | December | Collected regulatory weekly samples. Completed daily lab and station check - no new issues. Added data into SharePoint. Enabled batch wasting mode at 9am and set auto waste for 20m3 from 10am to 11am. When completed manually wasted an extra 5m3 from each clarifier. When completed reset RAS pumps. Increased soda ash run time from 7.50seconds/h to 8.00seconds/h due to decreasing alkalinity in lab. Added 9 bags of soda ash to hopper. Cleared rags from bar screen and distribution chamber stem. Inspected odour control unit and completed inspection form. | Kleinburg Water Resource Recovery Facility | 2025-12-16
WW-WEST | December | Filter reject sump pump 1 e stop alarm present upon arrival, reset and cleared alarm. Filter reject sump pump 1 e stop alarm came back in at 9:51am - reset and cleared alarm - so far alarm has not come back in and has run multiple cycles. This is a known issue with a work order made, will continue to monitor. Completed daily lab and station check - no new issues. Added data into SharePoint. Auto wasted 50m3 from 10am to 1pm. WAS pumps back in manual and RAS back in operation after wasting completion. Added 9 bags of soda ash to hopper. Cleaned rags from bar screen. Bled condensation from aeration condensation line. | Kleinburg Water Resource Recovery Facility | 2025-12-22
WW-WEST | December | - For foam control on aeration tank 2. Connected a hose to the existing length of hose hosing aeration tank 1 outlet - Removed dead ducks from aeration inlet - Removed rags from aeration outlet - Manually pumped down the scum tank to 0.45 m. No issues | Kleinburg Water Resource Recovery Facility | 2025-12-22
WW-WEST | December | Completed daily lab and station check - no new issues. Added data into SharePoint. Low level diesel tank alarms have been cleared. Enabled batch wasting mode at 8:50am and set auto waste from 10am- 12pm for 40m3. WAS pumps placed back in manual and RAS back in operation upon wasting completion. Filter reject sump pump 1 estop alarm came in at 10:35am - reset and alarm cleared. Will continue to monitor. Added 10 bags of soda ash to hopper. Cleaned rags from bar screen and confirmed operation. Cleaned rags from diversion valve stem. Cleaned and verified aeration tank DO probes. Samplers set and ready for next week. | Kleinburg Water Resource Recovery Facility | 2025-12-24
WW-WEST | December | Collected weekly regulatory samples. Completed daily lab and station check - no new issues. Added data into SharePoint. Created WO for diversion tank lvl hihi alarm. Reset filter reject sump pump 1 e stop alarm. Enabled batch wasting at 9am and set auto waste for 20m3 from 10am to 11am. Upon wasting completion WAS pumps placed back in auto and RAS back in operation. Added 12 bags of soda ash to hopper. Cleaned bar screen. Inspected odour control unit and completed inspection form. | Kleinburg Water Resource Recovery Facility | 2025-12-30
WW-WEST | December | Completed daily lab and station check - no new issues added data into SharePoint Enabled batch wasting mode at 9am and set auto waste from 10am to 12pm. Wasted 16.96m3 from clarifier 1 and 21.62m3 from clarifier 2. RAS back on after wasting completion. WAS pumps placed back into manual. Added 9 bags of soda ash to hopper. Cleaned rags from bar screen and diversion tank valve stem. Worked with Young on alum pump drawdown tests. | Kleinburg Water Resource Recovery Facility | 2025-12-18
WW-WEST | December | Completed daily lab and station check - no new issues. Added data into SharePoint. Enabled batch wasting at 9am and set auto waste for 20m3 from 10am to 11am. Upon wasting completion WAS pumps placed back into manual and RAS resumed. Drain line from bar screen auger clogged - unclogged and flushed. Picked rags from diversion chamber valve stem. Cleaned and verified DO probes. Pulled rags and debris from aeration tank outlet and Used hose to break up foam. Added 12 bags of soda ash to hopper. Reset and cleared filter reject sump pump 1 e stop alarm | Kleinburg Water Resource Recovery Facility | 2025-12-31
WW-WEST | December | Collected regulatory weekly samples. Completed daily lab and station check - no new issues data entered into SharePoint. Enabled batch wasting at 8:50am. Set auto waste for 40m3 from 10am to 12pm. WAS pumps placed back in manual upon wasting completion and RAS pumps back in operation. Added 10 bags of soda ash to hopper. Cleaned rags from bar screen. Inspected odour control unit and filled out inspection sheet - no issues. Inspecting diesel fuel tanks for cause of low alarms when tanks are full - discovered cap removed from tank 1 with potential leak. Also discovered leaking from the day tank. Could not confirm reason for low level alarms. Informed team lead. Contractors contacted and arrived onsite to respond at 2:30pm. Tested filter bypass and confirmed with ROC. | Kleinburg Water Resource Recovery Facility | 2025-12-23
WW-WEST | December | Added 15 bags to soda ash hopper. Picked rags from valve stems. Checked auto wasting. Working as expected. | Kleinburg Water Resource Recovery Facility | 2025-12-21
WW-WEST | December | Attending site to make adjustments to SECT_FIT1, as requested by Anna Lacourt and Matt Spitzig. Changed Low flow cut off from 0.667 to 2.0 L/s. Changed milliamp error mode from LOW to HOLD. Tuned milliamp output. ROC notified before and after adjustments were made | Kleinburg Water Resource Recovery Facility | 2025-12-16
WW-WEST | December | On site to repair the yard hydrant leak. Braze the cracks and tested it and no leaks. 2 hydrants need to be replaced by a contractor because a backhoe is needed for the job | Kleinburg Water Resource Recovery Facility | 2025-12-22
WW-WEST | December | Completed daily lab and added data into SharePoint. Enabled batch wasting mode at 10am and set auto waste for 50m3 from 11am to 1pm. WAS pumps placed back into manual upon wasting completion and RAS pumps reset. Verified and cleaned aeration tank DO probes. | Kleinburg Water Resource Recovery Facility | 2025-12-17
WW-WEST | December | - Notified ROC of the work being performed. - Inspected UV 1 and 2. No new issues - Cleaned UV channel with hose and air compressor - Cleaned wash pump screen after lock out. Wash pump discharge pressure low alarm, fail to start and unavailable alarm triggered due to the work. No issues cleaning. Placed wash pumps back into operation once done | Kleinburg Water Resource Recovery Facility | 2025-12-22
WW-WEST | December | Decanted sludge thickening tank. Filter reject sump pump 1 e stop alarm present on arrival - reset and cleared alarm. Diversion tank lvl hihi alarm present on arrival - diversion tank is not high, alarm faulty most likely due to ice forming on level sensor. Attempted to wipe level sensor to clean but unsuccessful in clearing alarm. Will continue to monitor. Completed daily lab and station check - due to low alkalinity in lab increased run time from 8.00seconds/hour to 8.50seconds/hour. Added data into SharePoint. Enabled batch wasting at 9am and set auto waste for 40m3 from 10am to 12pm. Upon wasting completion WAS pumps set back to manual and RAS back in operation. Cleaned scum tank. Bled aeration condensation line. Pulled rags from aeration tank outlets. Added 15 bags of soda ash to hopper. Cleaned rags from bar screen and confirmed operation. Cleaned rags from diversion chamber valve stem. | Kleinburg Water Resource Recovery Facility | 2025-12-29
WW-WEST | December | - Checked Kleinburg headworks eyewash. Eyewash expires in February. Will leave a new eyewash solution for future use - Inspected grit dewatering press. No issues. Grit seen in bin. - Inspected travelling bar screen. Greased z fittings. No issues. Teeth okay. Cleaned inside - Inspected screenings compactor. No issue - Inspected vortex 1 and 2. Greased z fittings. No issues - Added 9 bags of soda ash into the hopper - Checked station and recorded readings on SharePoint. No new issues - GFL took a load of sludge - Contractors onsite for TSSA upgrade | Kleinburg Water Resource Recovery Facility | 2025-12-17
WW-WEST | December | Enabled 230 minute wasting timer. Set auto wasting for 40 m3 in 8cycles between 12:00 and 14:00. Set was pumps to auto. | Kleinburg Water Resource Recovery Facility | 2025-12-21
WW-WEST | December | Checked station and trends, and recorded readings on SharePoint. No new issues | King City Pumping Station | 2025-12-02
WW-WEST | December | Pushed bin out for pick up Cleaned screen room and flushed drain line Performed bar screen lubrication | King City Pumping Station | 2025-12-11
WW-WEST | December | Completed the station check Entered data into SharePoint Pushed the rag bin back inside Everything operating as intended | King City Pumping Station | 2025-12-12
WW-WEST | December | - Notified ROC of the work being performed - Inspected the generators and fuel level. Started the generator at 9:12. Recorded readings on SharePoint after 30 minutes, no issues. Ran for approximately one hour. Runtime for generator 1 from 659.5 hrs to 660.5 hrs - Fuel level before test for diesel tank 1 at 83 cm (814 L) and diesel tank 2 at 82.5 cm (809 L). After diesel test, tank 1 at 82.3 cm (807 L) and tank 2 at 81.5 cm (799 L) - Tested sump pit operation and manually lifted float. Sump pump turned on, no issues - Tested dry well flood alarm, alarm received on SCADA and Dialer. ROC received the alarm on the auto dialer and scada. No issues - Tested the test function on the auto dialer. Received on the local dialer but not by ROC - Tested diesel containment flood alarm. Alarm received on SCADA - Performed JHSC inspection. All okay. Tested eyewash, no issues - Tested building Hi and Low temperature alarm. Alarm received - Checked for hazardous waste, none found - Inspected hoist system, all okay - Tested and inspected pump, motor and check valves. All okay. | King City Pumping Station | 2025-12-10
WW-WEST | December | Checked station and recorded readings on SharePoint. No new issues Checked headworks. Cleaned screen and floors. Flushed drain line | King City Pumping Station | 2025-12-05
WW-WEST | December | Arrived on site to reset pump 1 after it faulted due to ongoing power issue. Generator running upon arrival. Noticed the street lights are out of power too. Notified on call operator to monitor the town?s power outage. Pump 1 and 2 are in duty rotation. Pump 3 is in duty 3 and in manual and will be used in case of emergencies. | King City Pumping Station | 2025-12-29
WW-WEST | December | Checked station and recorded readings on SharePoint. Checked bin room. Cleaned area and flushed drain line Generator room dampers stays open and does not close. Upon inspection, damper control panel fails to get information. BR3 is tripped and trips when the power to the panel is turned on. Created work order to address the issue | King City Pumping Station | 2025-12-09
WW-WEST | December | On site with Renown to perform motor winding analysis. Could not find any issues during Hi-pot testing. Will continue to investigate. | King City Pumping Station | 2025-12-19
WW-WEST | December | Upon responding to the pump failure at King city we were able to observe pump 1 running in auto. Pump 2, Pump 3 both faulted at the drive displaying a F37 fault which means one of two things. Phase loss or Phase imbalance. We were able to check the line voltage and it was above 600v and around 350 phase to ground on each phase. We reset Pump 2 and let it Run through a cycle. The output off the drive was 350v on each phase to ground which is right around where it should be while operating. The current across the phases was put by over 20a between phase B -A,C (A128 B108 C127) this leads me to believe the windings on the motor have seen spikes and are deteriorating . While operating the soft start is displaying A code of A37 Which, according to the manual means there is a current imbalance on the motor, should the imbalance go outside this threshold. It will give us the same F 37 fault That is displayed during a phase loss which we were able to see on Scada here this morning. We performed tests on pump three and then pump one and all three pumps are giving us the same information. I've informed Bill and we will be looking at servicing these pump motors as soon as possible | King City Pumping Station | 2025-12-19
WW-WEST | December | Completed station check. No issues found. | King City Pumping Station | 2025-12-30
WW-WEST | December | On site to reset all pumps that were knocked oos due to power blips Reset pumps, wet wells, bar screen and screw compactor Pumped down the wet wells Had to reset the pumps another 3 times due to power issues Left pump 3 oos as a back up pump | King City Pumping Station | 2025-12-28
WW-WEST | December | Pushed bin out for pick up Flushed drain line and cleaned area | King City Pumping Station | 2025-12-17
WW-WEST | December | Checked station and trends. No new issues. Recorded readings on SharePoint | King City Pumping Station | 2025-12-23
WW-WEST | December | Set pump 1 to manual off/duty 4 in order to maintain availability in the event of power blips. | King City Pumping Station | 2025-12-19
WW-WEST | December | On site to check station and trends. No new issues | King City Pumping Station | 2025-12-16
WW-WEST | December | In to Investigate Gas Detector Warning and Fault Alarms Communicated by the ROC. Gas Detector Rendering a Low O2 Fault @ 18.2%. Dry Well Supply Fans Appear to be Running, However, Several Effluent Fan VFDs in Fault. Notified WW-West Staff for Safety Precautions and Request for Property Service?s Investigation. | Nobleton Janet St. Sewage Pumping Station | 2025-12-14
WW-WEST | December | Notified by email that RS pumps 2 & 3 were OOS following a power blip. Arrived and reset the disconnect on RS Pump 3 and the reset button on RS pump 2 MCC. Reset alarms on SCADA. Station checks, SharePoint readings and review of continuous monitoring data. Push in miller waste bin. | King City Pumping Station | 2025-12-19
WW-WEST | December | Harie Rajamithiran(OIT) working under the direction of Daniel Hirstwood(OIC) -Completed station check, no abnormalities found -Made remote log entry, but work was completed on-site | Nobleton Janet St. Sewage Pumping Station | 2025-12-12
WW-WEST | December | Remotely Responded to Gas Detector Critical and Fault Alarms Communicated by the ROC. Critical Alarm Acknowledged and Reset. Fault Alarm Remains Outstanding. No Indications of Dry Well Leak Observed. Instructed ROC to Disregard in the Interim. | Nobleton Janet St. Sewage Pumping Station | 2025-12-13
WW-WEST | December | On site to inspect the o2 sensor and found that the buildings sensor is faulty Created a workorder to address this | Nobleton Janet St. Sewage Pumping Station | 2025-12-15
WW-WEST | December | Completed station check. No issues found. Checked check valves. Tested dry well flood alarm. ROC received alarm. Inspected sump. ROC received alarm. Tested temperature alarms. ROC received alarm. Tested autodialler. ROC received alarm. Checked air relief valve. Checked raw sewage pump motors. Checked raw sewage pumps: P1: 60 l/sec at 98%. P2: 58 l/sec at 100%. P3: 62 l/sec at 94%. | Nobleton Janet St. Sewage Pumping Station | 2025-12-05
WW-WEST | December | Worked with Harie. | Nobleton Janet St. Sewage Pumping Station | 2025-12-09
WW-WEST | December | Collected weekly snd monthly compliance samples. Completed station check. No new issues found. Entered data in spreadsheet. | Nobleton Janet St. Sewage Pumping Station | 2025-12-02
WW-WEST | December | Harie Rajamithiran(OIT) working under the direction of Lance Johnson(OIC) -Completed generator run test -Generator run test time from 453:39:00 - 454:39:00, fuel volume 1541.28L to 1540L -Completed health and safety inspection -Completed hoist inspection | Nobleton Janet St. Sewage Pumping Station | 2025-12-09
WW-WEST | December | On site to weld pipe on suction side of pump 1 Isolated valves and drained down pipes Pump is not isolating Retried and adjusted stops on suction line. Still not isolating. Operator ran pumps to lowest level achievable and reclosed suction line. Pump 1 still not isolating. Valves are closed and pump 1 is locked out. | Nobleton Janet St. Sewage Pumping Station | 2025-12-16
WW-WEST | December | Collected weekly compliance samples. Completed station check. No issues found. Entered data in spreadsheet. | Nobleton Janet St. Sewage Pumping Station | 2025-12-09
WW-WEST | December | Harie Rajamithiran(OIT) working under the direction of Lance Johnson(OIC) -completed house-keeping | Nobleton Janet St. Sewage Pumping Station | 2025-12-24
WW-WEST | December | Ran pumps and cycled valves trying to clear blockage and enable pump 1 to be isolated. Also opened check valve to try and pump back into wetwell and clear valve blockage. Unable to isolate wetwell Excessive amounts of rocks in wetwell preventing suction valve from closing. Recommend welding pipe during wetwell cleaning. | Nobleton Janet St. Sewage Pumping Station | 2025-12-16
WW-WEST | December | NBSSJA - Attending site to check oxygen sensor (W11516155). Found O2 sensor has failed. Replaced sensor and calibrated. Cleared associated SCADA alarms. ROC was notified before and after sensor replacement. | Nobleton Janet St. Sewage Pumping Station | 2025-12-17
WW-WEST | December | Completed station check. No issues found. Pumped down wetwell to assist maintenance. Inspected raw sewage sampler. Collected weekly compliance samples. | Nobleton Janet St. Sewage Pumping Station | 2025-12-16
WW-WEST | December | Completed manual valve exercise work order. | Nobleton Janet St. Sewage Pumping Station | 2025-12-23
WW-WEST | December | Log made in error. | Nobleton Janet St. Sewage Pumping Station | 2025-12-16
WW-WEST | December | Completed station check. No issues found. | Nobleton Janet St. Sewage Pumping Station | 2025-12-19
WW-WEST | December | Completed station check. No issues found. Collected weekly compliance samples. | Nobleton Janet St. Sewage Pumping Station | 2025-12-30
WW-WEST | December | Test ran the generator Tested the dry well flood alarm Tested the building high low temp alarms Tested the auto dialer Inspected the check valves, sump pit and air valves Completed the jhsc inspection Manually exercised valves Inspected the ocu and mist eliminator | Vaughan Pine Valley Pumping Station | 2025-12-10
WW-WEST | December | Collected weekly compliance samples. Completed station check. No issues found. | Nobleton Janet St. Sewage Pumping Station | 2025-12-23
WW-WEST | December | Checked station and trends, and recorded readings on SharePoint. No new issues | Vaughan Pine Valley Pumping Station | 2025-12-05
WW-WEST | December | Completed the station check Entered days into SharePoint Everything operating as intended | Vaughan Pine Valley Pumping Station | 2025-12-12
WW-WEST | December | Checked station and trends. No new issues. Recorded readings on SharePoint | Vaughan Pine Valley Pumping Station | 2025-12-23
WW-WEST | December | Completed the station check Entered data into SharePoint Everything operating as intended | Vaughan Pine Valley Pumping Station | 2025-12-09
WW-WEST | December | Checked station and trends, and recorded readings on SharePoint. No new issues | Vaughan Pine Valley Pumping Station | 2025-12-02
WW-WEST | December | Station checks, SharePoint readings and review of continuous monitoring data. Odour control fan belt is broken. Replaced with new belt and put unit back into service. | Vaughan Pine Valley Pumping Station | 2025-12-19
WW-WEST | December | Completed the station check Entered data into SharePoint Everything operating as intended | Vaughan Pine Valley Pumping Station | 2025-12-30
WW-WEST | December | Completed the station check Entered data into SharePoint Everything operating as intended | Vaughan Pine Valley Pumping Station | 2025-12-16
WW-WEST | December | Completed the yearly maintenance on the vortexes, I did not change the oil as Marcus changed the oil last year Verified the DO probes Rebuilt the alum pumps and replaced any worn parts | Schomberg Water Resource Recovery Facility | 2025-12-15
WW-WEST | December | In to Complete Scheduled WOs. Notified ROC. Lowered and Activated Decant Pump. Rotated WAS Pump Duties. Pump #2 Manual Off, Pump #1 in Auto. Rotated RAS Pump Duties. Pump #1 in Duty #1, Pump #3 in Duty #3, OOS. Decant Complete, Raised and Deactivated Decant Pump. Sludge Transfer Valve Manual Open, Transferred Thickened Sludge. Transfer Valve Returned to Manual Closed. Placed Scum Pump #2 in Manual On, Recirculated Scum Tank, Returned to Manual Off. Placed Scum Valve in Manual Discharge and Activated Scum Pump #2 in Manual. Scum Tank Drawdown Complete. Returned All to Auto and Service. Rebuilt Alum Pumps #6 and 7. Returned to Service and Tested Units. No Issues Found. | Schomberg Water Resource Recovery Facility | 2025-12-15
WW-WEST | December | In to Complete Scheduled WOs. Notified ROC. Lowered and Activated Decant Pump. Decant Complete, Raised and Deactivated Decant Pump. Sludge Transfer Valve Manual Open, Transferred Thickened Sludge. Transfer Valve Returned to Manual Closed. OOS Aer. Tank #2 Filling Process Complete. Deactivated and Removed Plant Service Water Line. Completed Process Building and Blower Building Sump System Inspections. Tested Hi Level Float Alarms. Confirmed Reception by the ROC. No Issues Found. Returned to Service. Cleared Associated Alarms. Completed Scum Pumps #1 and 2 Inspections. Couplings and Oil Levels OK. Greased Bearings. Returned to Service. | Schomberg Water Resource Recovery Facility | 2025-12-12
WW-WEST | December | Remotely Responded to RAS Pumps #3 No Flow Alarm Communicated by the ROC. Remotely Rotated RAS Pump Duties. Pump #2 in Duty #1, Pump #3 in Duty #3, OOS. Flow Restored and Alarm Cleared. | Schomberg Water Resource Recovery Facility | 2025-12-11
WW-WEST | December | In to Complete Scheduled WOs. Notified ROC. Lowered and Activated Decant Pump. Placed Plant Service Water Line in OOS Aer. Tank #2 and Commenced Filling Process for CPD Led Foundation Leak Investigation. Decant Complete, Raised and Deactivated Decant Pump. Sludge Transfer Valve Manual Open, Transferred Thickened Sludge. Transfer Valve Returned to Manual Closed. Placed Scum Pump #2 in Manual On, Recirculated Scum Tank, Returned to Manual Off. Placed Scum Valve in Manual Discharge and Activated Scum Pump #2 in Manual. Scum Tank Drawdown Complete. Returned All to Auto and Service. Completed RAS Pumps #1-3 and WAS Pumps #1 and 2 Inspections. Oil Levels and Couplings OK. Greased Bearings. No Issues Found. Returned to Service. Cleared Associated Alarms. Completed Aer. DO Sensor Maintenance. Placed Probes in Calibration Mode. Cleaned and Inspected Units, No Issues Found. Returned to Service. OOS Aer. Tank #2 Filling Process to be Continued. Deactivated and Removed Plant Service Water Line. | Schomberg Water Resource Recovery Facility | 2025-12-10
WW-WEST | December | In to Complete Scheduled WOs. Notified ROC. Lowered and Activated Decant Pump. Received Alum Delivery. Reviewed and Signed Documentation. Alum Tank Levels: 0.90/0.90 ?> 2.34/2.36m. Decant Complete, Raised and Deactivated Decant Pump. Sludge Transfer Valve Manual Open, Transferred Thickened Sludge. Transfer Valve Returned to Manual Closed. Identified Possible Diatomaceous Particles within FE Holding Tank and FE Composite Samples, Potentially Affecting and Increasing FE TSS Results. Particles Do Not Appear to be Present in Clarifier Effluent or UV Channel. Reference Attached Photos. Notified TL and Supervisor. Identified Potential Slow Diesel Generator Fuel Leak Located on the Units?s Fuel Return Line. Leak is Contained within Fuel Containment and Does Not Appear to be Free Flowing. Notified TL and Appropriate Staff for Further Inspection. Completed Aer. DO Sensor Maintenance. Placed Probes in Calibration Mode. Cleaned and Inspected Units, No Issues Found. Returned to Service. | Schomberg Water Resource Recovery Facility | 2025-12-03
WW-WEST | December | In to Complete Scheduled WOs. Notified ROC. Lowered and Activated Decant Pump. Placed Plant Service Water Line in OOS Aer. Tank #2 and Commenced Filling Process for CPD Led Foundation Leak Investigation. Decant Complete, Raised and Deactivated Decant Pump. Investigated RAS Pump #3, No Issues Found. Returned to Duty #1 for Testing, Pump Producing Flow, No Recurrence of Flow Alarm. Completed Grit Dewatering Screw #1 and 2 Inspections. Topped Up Oil Reservoirs. No Other Issues Found. Returned to Service. Completed Debris Auger Inspection. Oil Levels OK. No Issues Found. Returned to Service. Cleared Associated Alarm. Completed Sludge Holding Tank Overflow Float Alarm Test. Confirmed Reception by the ROC. Returned to Service. Cleared Associated Alarm. | Schomberg Water Resource Recovery Facility | 2025-12-11
WW-WEST | December | In to Complete Reg. Sampling and Scheduled WOs. Lowered and Activated Decant Pump. Placed Plant Service Water Line in OOS Aer. Tank #2 and Commenced Filling Process for CPD Led Foundation Leak Investigation. Decant Complete, Raised and Deactivated Decant Pump. OOS Aer. Tank #2 Filling Process to be Continued. Deactivated and Removed Plant Service Water Line. | Schomberg Water Resource Recovery Facility | 2025-12-09
WW-WEST | December | In to Complete Scheduled WOs. Notified ROC. Lowered and Activated Decant Pump. Placed Plant Service Water Line in OOS Aer. Tank #2 and Commenced Filling Process for CPD Led Foundation Leak Investigation. Placed Scum Pump #2 in Manual On, Recirculated Scum Tank, Returned to Manual Off. Placed Scum Valve in Manual Discharge and Activated Scum Pump #2 in Manual. Scum Tank Drawdown Complete. Returned All to Auto and Service. Decant Complete, Raised and Deactivated Decant Pump. Sludge Transfer Valve Manual Open, Transferred Thickened Sludge. Transfer Valve Returned to Manual Closed. Completed Filter Inlet TSS Sensor Inspection. Placed Unit in Calibration Mode Locally, Cleaned Probe. No Issues Found. Returned to Service. Completed Aer. Blowers #1-4 Inspections. Filters OK. Replaced Belts on Aer. Blower #3. Topped Up Oil Reservoirs on Aer. Blowers #1 and 4. No Other Issues Found. Returned All to Service. Cleared Associated Alarms. OOS Aer. Tank #2 Filling Process to be Continued. Deactivated and Removed Plant Service Water Line. | Schomberg Water Resource Recovery Facility | 2025-12-05
WW-WEST | December | In to Complete Scheduled WOs. Notified ROC. Lowered and Activated Decant Pump. Placed Plant Service Water Line in OOS Aer. Tank #2 and Commenced Filling Process for CPD Led Foundation Leak Investigation. Decant Complete, Raised and Deactivated Decant Pump. Rotated WAS Pump Duties. Pump #1 Manual Off, Pump #2 in Auto. Rotated RAS Pump Duties. Pump #3 in Duty #1, Pump #1 in Duty #3, OOS. Sludge Transfer Valve Manual Open, Transferred Thickened Sludge. Transfer Valve Returned to Manual Closed. Completed Vortex #1 and 2 Inspections. Removed Rags and Debris from Impellers. Topped Up Oil Reservoirs and Greased Bearings. No Other Issues Found. Returned to Service. Completed Travelling Screen and Screenings Compactor Inspections. Oil Levels OK. Greased Bearings and Flushed Drainage Lines. No Issues Found. Returned to Service. Cleared Associated Alarms. Completed Sludge Holding Tank Overflow Manual Valve Exercise with No Issues. Returned to Service. OOS Aer. Tank #2 Filling Process to be Continued. Deactivated and Removed Plant Service Water Line. | Schomberg Water Resource Recovery Facility | 2025-12-08
WW-WEST | December | In to Complete Reg. Sampling and Scheduled WOs. Lowered and Activated Decant Pump. Decant Complete, Raised and Deactivated Decant Pump. Completed Clarifier #1 and 2 Inspections. Chain Drives OK. Topped Up Clarifier #2 Oil Reservoir. No Other Issues Found. Returned to Service. Cleared Associated Alarm. | Schomberg Water Resource Recovery Facility | 2025-12-02
WW-WEST | December | In to Complete Scheduled WOs. Lowered and Activated Decant Pump. Decant Complete, Raised and Deactivated Decant Pump. Sludge Transfer Valve Local Open, Transferred Thickened Sludge. Transfer Valve Returned to Manual Closed. Completed Grit Vortex Blowers #1 and 2 Inspections and Oil Changes. Belts and Filters OK. Drained and Replaced Oil Reservoirs. Returned to Service. Cleared Associated Alarms. Completed Sludge Holding Tank Blowers #1 and 2 Inspections and Oil Changes. Belts and Filters OK. Drained and Replaced Oil Reservoirs. Returned to Service. Cleared Associated Alarms. Completed Sludge Blower Building Room Supply Fan Filter Replacement with No Issues. | Schomberg Water Resource Recovery Facility | 2025-12-04
WW-WEST | December | In Responding to UV System Major Fault Alarm Communicated by the ROC. Found UV Bank B with a Burnt Bulb, Whilst UV Bank A Continues to Experience Possible Fuse Related Issues with Rack #5 (WO Already Generated ?> W11475704). Both Banks Running Simultaneously in Auto. Placed Both Units in Manual Locally. Deactivated UV B and Replaced Burnt Out Bulb. Tested Unit, No Further Issues Found. Returned Both to Auto and Service. Cleared Associated Alarm. UV Bank A to Remain in Auto and Alarm Locally Until WO Request Completed by Maintenance. | Schomberg Water Resource Recovery Facility | 2025-12-07
WW-WEST | December | Remotely Placed Supernatant Drain Valve in Manual Open. Remotely Rotated WAS Pump Duties. Pump #2 Manual Off, Pump #1 in Auto. Remotely Rotated RAS Pump Duties. Pump #1 in Duty #1, Pump #3 in Duty #3, OOS. Remotely Responded to Alum Pumps #6 and 7 No Flow Alarms. Acknowledged and Reset Alarms. Returned Both Pumps to Duty. Decant Complete. Remotely Closed Supernatant Valve in Manual. | Schomberg Water Resource Recovery Facility | 2025-12-01
WW-WEST | December | In to Complete Scheduled WOs. Notified ROC. Lowered and Activated Decant Pump. Decant Complete, Raised and Deactivated Decant Pump. Sludge Transfer Valve Manual Open, Transferred Thickened Sludge. Transfer Valve Returned to Manual Closed. Transferred Station to Generator Power with No Issues. Acknowledged and Cleared Associated Alarms. Placed Scum Valve in Manual Discharge. Activated Scum Pump #2 in Manual. Scum Tank Drawdown Complete. Returned All to Auto and Service. Transferred Station Back to Utility Power with No Issues. Cleared Associated Alarms. Completed JHSC Inspection with No Issues. | Schomberg Water Resource Recovery Facility | 2025-12-01
WW-WEST | December | In to Complete Scheduled WOs. Notified ROC. Lowered and Activated Decant Pump. Maintenance (Elec.) On-site to Investigate UV System Bank A, Rack #5 Fuse Issue. Maintenance On-site to Investigate Aer. Blowers #2 and 3 Vacuum Gauge Issues. Rotated Blower Duties Several Times to Accommodate. Decant Complete, Raised and Deactivated Decant Pump. UV System Bank A Locally Placed in Manual Off for Low UV Intensity Concerns Until Maint. Repairs Completed. Notified On-Call Ops Staff. Completed Sand Filter and Clarifier Weir Inspections. No Issues Found. | Schomberg Water Resource Recovery Facility | 2025-12-18
WW-WEST | December | In to Complete Scheduled WOs. Lowered and Activated Decant Pump. Decant Complete, Raised and Deactivated Decant Pump. Sludge Transfer Valve Manual Open, Transferred Thickened Sludge. Transfer Valve Returned to Manual Closed. Placed Scum Pump #2 in Manual On, Recirculated Scum Tank, Returned to Manual Off. Placed Scum Valve in Manual Discharge and Activated Scum Pump #2 in Manual. Scum Tank Drawdown Complete. Returned All to Auto and Service. | Schomberg Water Resource Recovery Facility | 2025-12-19
WW-WEST | December | Reset clarifier after power outage. Duties and alarms reset remotely. | Schomberg Water Resource Recovery Facility | 2025-12-23
WW-WEST | December | In to Complete Scheduled WOs. WAS Pump #1 Cumulatively Auto-Wasted 167 m3 Over the Span of the Weekend. Lowered and Activated Decant Pump. Rotated WAS Pump Duties. Pump #1 Manual Off, Pump #2 in Auto. Rotated RAS Pump Duties. Pump #3 in Duty #1, Pump #1 in Duty #3, OOS. Decant Complete, Raised and Deactivated Decant Pump. Sludge Transfer Valve Manual Open, Transferred Thickened Sludge. Transfer Valve Returned to Manual Closed. Completed Alum Pumps #6 and 7 Drawdown Testing and Panel Board Cleaning. Returned to Service. | Schomberg Water Resource Recovery Facility | 2025-12-22
WW-WEST | December | In to Complete Scheduled WOs. Lowered and Activated Decant Pump. Tested Alum Pumps #6 and 7 for Recurring No Flow Alarms. Testing Complete, Cleared Associated Alarms. Created Follow Up WO ?> W11523891. Decant Complete, Raised and Deactivated Decant Pump. Sludge Transfer Valve Manual Open, Transferred Thickened Sludge. Transfer Valve Returned to Manual Closed. | Schomberg Water Resource Recovery Facility | 2025-12-17
WW-WEST | December | Completed the station check and daily lab work Entered data into SharePoint Cleaned up around site Everything operating as intended | Schomberg Water Resource Recovery Facility | 2025-12-29
WW-WEST | December | Reset the clarifier drive Everything operating as intended | Schomberg Water Resource Recovery Facility | 2025-12-29
WW-WEST | December | Harie Rajamithiran(OIT) working under the direction of Gavin Walker(OIC). -Collected weekly compliance samples -Completed lab analysis, no abnormalities found -Completed station check, no abnormalities found -Supernated sludge thickening tank and transferred to holding tank | Schomberg Water Resource Recovery Facility | 2025-12-30
WW-WEST | December | Remotely Reviewed SCADA and Trends. Recurrent Screen Room O2 Concentrations Hi and HiHi Alarms Outstanding. Created WO for Instrumentation ?> W11526277. | Schomberg Water Resource Recovery Facility | 2025-12-18
WW-WEST | December | Onsite for call out due to UV bank 1B major fault alarm due to blown bulb. UV bank 1A in local off for repairs. Set UV bank 1A to manual on to replace blown bulb UV bank 1B bulb out in rack 5 bulb 1. Replaced. UV bank 1B back in auto and UV bank 1A back in local off. | Schomberg Water Resource Recovery Facility | 2025-12-30
WW-WEST | December | On site for major UV fault caused by blown bulb in bank B, rack 5, bulb 6. Replaced bulb. Reset alarms. | Schomberg Water Resource Recovery Facility | 2025-12-19
WW-WEST | December | Troubleshoot blower 2 and 3. Found blower 2 pressure gauge is not receiving enough air pressure to register. Cleaned filter and no change. Removed brass filter and gauge is operational. Blower 3 filter minder gauge is not working. New gauge is required. | Schomberg Water Resource Recovery Facility | 2025-12-18
WW-WEST | December | In to Complete Scheduled WOs. WAS Pump #2 Auto-Wasted 56 m3 Overnight. Lowered and Activated Decant Pump. Recirculated Scum Tank with Scum Pump #2 in Manual On. Placed Scum Valve in Manual Discharge for Scum Tank Drawdown, Drawdown Complete. Returned All to Auto and Service. Decant Complete, Raised and Deactivated Decant Pump. Sludge Transfer Valve Manual Open, Transferred Thickened Sludge. Transfer Valve Returned to Manual Closed. Completed Aer. DO Sensor Maintenance. Placed Probes in Calibration Mode. Cleaned and Inspected Units, No Issues Found. Returned to Service. | Schomberg Water Resource Recovery Facility | 2025-12-24
WW-WEST | December | Collected weekly samples | Schomberg Water Resource Recovery Facility | 2025-12-30
WW-WEST | December | In to Complete Reg. Sampling and Scheduled WOs. WAS Pump #2 Auto-Wasted 59 m3 Overnight. Lowered and Activated Decant Pump. Identified Slow Diesel Generator Fuel Leak Located on the Units?s Diesel Fuel Filters. Leak is Contained within Fuel Containment and Does Not Appear to be Free Flowing. Notified TL and Appropriate Staff for Further Inspection. Completed Filter Inlet TSS Sensor Inspection. Placed Unit in Calibration Mode Locally, Cleaned Probe. No Issues Found. Returned to Service. Decant Complete, Raised and Deactivated Decant Pump. | Schomberg Water Resource Recovery Facility | 2025-12-23
WW-WEST | December | Remotely Reviewed SCADA and Trends. Station Recovered from Power Loss Event. Notified ROC and On-Call Staff Member. Returned RAS Pumps #2 and 3 and Sludge Holding Tank Blowers #1 and 2 to Duty. | Schomberg Water Resource Recovery Facility | 2025-12-23
WW-WEST | December | On site to change a bulb in UV bank b Everything operating as intended | Schomberg Water Resource Recovery Facility | 2025-12-26
WW-WEST | December | Completed the daily lab work and uploaded it to SharePoint Higher final tss and tp are due to a uv channel cleaning | Schomberg Water Resource Recovery Facility | 2025-12-17
WW-WEST | December | In to Complete Reg. Sampling and Scheduled WOs. Notified ROC. Tested Alum Pumps #6 and 7 for Recurring No Flow Alarms. Testing Inconclusive, Cleared Associated Alarms. Lowered and Activated Decant Pump. Decant Complete, Raised and Deactivated Decant Pump. Placed UV Bank A in Manual On in Conjunction with Bank B in Auto. Completed UV/FE Channel Clean-Out with No Issues. Returned UV Bank A to Auto. | Schomberg Water Resource Recovery Facility | 2025-12-16
WW-WEST | December | Supernated STT. Didn't release to SHT. Completed labs and entered data in ACE sheets. Completed station check. No issues found. Adjusted UV system such that bank B shall remain in lead duty for 100 days. Set bank A back to auto. Cleaned and verified DO probes. | Schomberg Water Resource Recovery Facility | 2025-12-31
WW-WEST | December | Checking Alum Pump stroke setpoints on SCADA based on request by OIC. Hit left "apply" button on alum setpoints screen while navigating. checked with OIC if any values would be different after hitting apply. no changes were made. setpoints were all the same as before. all ok. | Schomberg Water Resource Recovery Facility | 2025-12-18
WW-WEST | December | Created remote log entry but work was conducted on-site . Harie Rajamithiran(OIT) working under the direction of Marcus Remonde (OIC) -completed lab analysis ,no abnormalities found -completed station check ,no abnormalities found -collected weekly compliance samples | Schomberg Water Resource Recovery Facility | 2025-12-16
WW-WEST | December | In to Complete Station Check. Reviewed SCADA and Trends. Cleared Outstanding Hi Pressure Alarm. ROC Returned Pump #1 to Auto Speed Remotely. No Other Issues Found. | Schomberg Dr. Kay Pumping Station | 2025-12-12
WW-WEST | December | In to Complete Scheduled WOs. Notified ROC. Transferred Station to Generator Power with No Issues. Acknowledged Associated Alarms. Reviewed SCADA and Trends. Wet Well Level Trends During Pump #1 Duty Runs are Elongated and Indicate Low Output Flows. Placed Pump #1 in Manual Speed @ 100% for Pump Efficiency Testing and Flushing. Manually Rotated Pump #1 into Duty #1. Created Follow Up WO for Maint. Regarding Pump #1 Flow Efficiency ?> W11508749. Completed Hi/Lo Temperature Alarm Test. Confirmed Reception by the ROC. Returned to Service. Cleared Associated Alarms. Transferred Station Back to Utility Power with No Issues. Cleared Associated Alarms. | Schomberg Dr. Kay Pumping Station | 2025-12-11
WW-WEST | December | In to Complete Station Check. Reviewed SCADA and Trends. Cleared Outstanding LoLo and Loss of Echo Alarms Associated with Ultrasonic LIT. Temporary Sensor Reading Error Indicated by Trends. Issue Self Rectified, No Others Found. | Schomberg Dr. Kay Pumping Station | 2025-12-02
WW-WEST | December | Remotely Placed Pump #1 in Manual Speed @ 100% for Pump Testing. Pump Testing Complete. Remotely Returned Pump #1 to Auto Speed. | Schomberg Dr. Kay Pumping Station | 2025-12-08
WW-WEST | December | Pulled pump 1 Separated pump from bowl Removed ball of rags Reinstalled pump and tested operation okay | Schomberg Dr. Kay Pumping Station | 2025-12-03
WW-WEST | December | In to Complete Station Check. Reviewed SCADA and Trends. No Issues Found. | Schomberg Dr. Kay Pumping Station | 2025-12-05
WW-WEST | December | In to Complete Scheduled WOs and Monitor Station During Network Updates Conducted by PCS. Notified ROC. Completed JHSC and Hazardous Materials Inspections with No Issues. Reviewed SCADA and Trends. No Issues Found. Network Updates Complete with No Issues to Station. | Schomberg Dr. Kay Pumping Station | 2025-12-09
WW-WEST | December | On site due to p1 vfd fault Reset the vfd, everything operating as intended | Schomberg Dr. Kay Pumping Station | 2025-12-29
WW-WEST | December | Harie Rajamithiran(OIT) working under the direction of Gavin Walker(OIC) -Completed station check , no abnormalities found. | Schomberg Dr. Kay Pumping Station | 2025-12-30
WW-WEST | December | In to Complete Scheduled WO and to Assist Maint. with Pump #1 Inspection. Notified ROC. Completed Wet Well Hi Level Alarm Test. Confirmed Reception by the ROC. Returned to Service. Cleared Associated Alarms. Reviewed SCADA and Trends. No Issues Found. Bypass Chamber Inspection OK. Removed and Inspected Pump #1. Cleared Obstructions from Pump Suction and Adjusted Wear Ring. Returned to Service. Cleared Associated Alarms. Tested Unit in Duty #1 with No Issues. | Schomberg Dr. Kay Pumping Station | 2025-12-17
WW-WEST | December | In to Complete Station Check. Reviewed SCADA and Trends. Cleared Outstanding Generator Running Alarm. No Other Issues Found. | Schomberg Dr. Kay Pumping Station | 2025-12-23
WW-WEST | December | In to Complete Station Check. Reviewed SCADA and Trends. No Issues Found. | Schomberg Dr. Kay Pumping Station | 2025-12-16
WW-WEST | December | In to Complete Station Check. Reviewed SCADA and Trends. Cleared Outstanding Generator Running Alarm. Surge Protector Issuing Audible Alarm. Phases A and C Indicated as Requiring Replacement. Phase C and Ground OK. Notified On-Call Maint. Electrician. Created Follow Up WO ?> W11528991. Audible Alarm Silenced. | Schomberg Dr. Kay Pumping Station | 2025-12-19
ROC | December | Adam Button signing in snowing -10 | ROC General | 2025-12-13
ROC | December | Christian Van Beek signing in. Weather: -10C and clear. | ROC General | 2025-12-11
ROC | December | SEOC6/7- Dominque from Honeywell is on site | ROC General | 2025-12-10
ROC | December | QVW12 - Theodore from ABPMC leaving site. | ROC General | 2025-12-10
ROC | December | Carter Dunn Signing In, -1D/Clear | ROC General | 2025-12-12
ROC | December | SEOC4 - Contractor onsite checking card reader | ROC General | 2025-12-12
ROC | December | SECC- Mike L done on site | ROC General | 2025-12-12
ROC | December | SEOC- Jon from property services is done on site | ROC General | 2025-12-12
ROC | December | STW56 - Christian from Ferguson Electric on site | ROC General | 2025-12-15
ROC | December | Adam Button signing out | ROC General | 2025-12-15
ROC | December | Christian Van Beek signing out. | ROC General | 2025-12-15
ROC | December | Connor Smith signing out | ROC General | 2025-12-10
ROC | December | NMW15 and NMETYS - Kevin N. from YorkNet will be attending both sites 14:54 - Kevin is finished at both sites | ROC General | 2025-12-11
ROC | December | Adam Button signing in | ROC General | 2025-12-10
ROC | December | KBSP - Garrick from Ferguson Electric off site. | ROC General | 2025-12-10
ROC | December | STPSTL - Theodore from AB onsite 11:21 - Theodore AB leaving site | ROC General | 2025-12-11
ROC | December | Angelica Chepiga signing in, weather -12C | ROC General | 2025-12-14
ROC | December | STPSTL - Garrick from Ferguson entering site | ROC General | 2025-12-11
ROC | December | KSSP - Ben Han from property services on site to work on the heating system in the OCF building. | ROC General | 2025-12-15
ROC | December | SUSP - Terry G. from property services called to inform that he is on site and will be checking the card readers. 12:56 - Terry is finished on site | ROC General | 2025-12-11
ROC | December | GWTP- Laurena from York is on site KSETDP- Donny from Landmark is on site | ROC General | 2025-12-12
ROC | December | Adam Button signing in | ROC General | 2025-12-14
ROC | December | NBW3- Influent free Cl2 lolo switch alarm came in. Found well in man/off. Tim H heading to site with Stephen B QVW34- Jerry Z and Alex B on site to work on Cl2 system and troubleshoot leak. Alex B req CMU5 for site revisit later to confirm leak has been resolved. Created CMU5 W11511250 #CMU5 **WRONG BOOK** | ROC General | 2025-12-12
ROC | December | GWTPLL - Terry G finished at site. Doors closed, site locked, but issue with alarm. Security aware and responding to issue. | ROC General | 2025-12-12
ROC | December | SECC- Jon from property services is on site for fire testing ANW23- Terry from property services is on site 10:44- SECC- Jon from property services is done onsite | ROC General | 2025-12-12
ROC | December | Angelica Chepiga signing out | ROC General | 2025-12-15
ROC | December | SEOC6/7 - Contractor onsite checking card reader | ROC General | 2025-12-12
ROC | December | Pesticon Pest Control visiting the following sites today: JDSS, KSTKWP, KSSSQW, KSTP, KSOCMA, KSETWB, KSETDP, GRSSWA, GWTPLL, GWTP, SUSSWB, SUETDR, SUSP, SUSSHS. | ROC General | 2025-12-15
ROC | December | Christian Van Beek signing out. | ROC General | 2025-12-10
ROC | December | STW3 - Water Resources leaving site | ROC General | 2025-12-11
ROC | December | SEOC67- Dominque from Honeywell is done on site Adam Button signing out | ROC General | 2025-12-10
ROC | December | Adeela Khan signing in. Weather: -12 and snowing | ROC General | 2025-12-11
ROC | December | NMETDD - Aaron from the DNS team leaving site. | ROC General | 2025-12-10
ROC | December | KBSP - Garick from Ferguson epoxy work | ROC General | 2025-12-11
ROC | December | Ethan Ullalkar signing in | ROC General | 2025-12-11
ROC | December | STETBR - David C. from CPD is on site for an inspection 12:58 - David is finished on site | ROC General | 2025-12-11
ROC | December | Adeela Khan signing out | ROC General | 2025-12-11
ROC | December | NMW15 - Samir from Yorknet on site to continue with the fiber installations. | ROC General | 2025-12-02
ROC | December | KSTP- Drew from Ferguson on site | ROC General | 2025-12-03
ROC | December | STPSTL- Christian from Ferguson electric is done on site | ROC General | 2025-12-03
ROC | December | Adam Button signing in -5 clear | ROC General | 2025-12-06
ROC | December | Stouffville, Cody from OCWA is doing flushing | ROC General | 2025-12-01
ROC | December | QVW12, Stephen from AB is on site | ROC General | 2025-12-04
ROC | December | NMETYS - Samir from yorknet on site to work on the fiber system. | ROC General | 2025-12-02
ROC | December | Adeela Khan signing out | ROC General | 2025-12-06
ROC | December | BLSS - Ben from PS onsite checking drywell | ROC General | 2025-12-08
ROC | December | BLSS - Ben Han from property services on site to inspect the heating system. | ROC General | 2025-12-08
ROC | December | KBSP - Christian from Ferguson Electric leaving site. | ROC General | 2025-12-09
ROC | December | BLSS - Dom from Honeywell leaving site QVETQS - Terry leaving site | ROC General | 2025-12-09
ROC | December | Wrong logbook | ROC General | 2025-12-08
ROC | December | Connor Smith signing in -2C snow | ROC General | 2025-12-09
ROC | December | Carter D signing Out | ROC General | 2025-12-05
ROC | December | Pest control - attending following sites. KSETWB, PVSS, VNETAG, BLSS, HMSS, VNETFD | ROC General | 2025-12-09
ROC | December | RHPSPA - Franco from property services on site to work on the card readers. 07:26 - RHPSPA - Franco leaving site and heading to JFRS | ROC General | 2025-12-04
ROC | December | Christian Van Beek signing in. Weather: -9 and clear. | ROC General | 2025-12-09
ROC | December | NMETYS, Samir from Yorknet is headed to site | ROC General | 2025-12-02
ROC | December | QVW12 - AB project onsite for generator work | ROC General | 2025-12-09
ROC | December | Adam Button signing out | ROC General | 2025-12-06
ROC | December | KSETDP - Thomas leaving site with Landmark | ROC General | 2025-12-09
ROC | December | RHAMF - Dave from North American Construction is headed to site | ROC General | 2025-12-06
ROC | December | Adam Button signing in -2 clear | ROC General | 2025-12-05
ROC | December | Christian Van Beek signing out. | ROC General | 2025-12-03
ROC | December | SHSP - Theodore on site for a fuel leak investigation KSTP - Drew from Ferguson Electric leaving site. EGSSSC - Joe O finished and leaving site | ROC General | 2025-12-03
ROC | December | Ethan U signing in Weather -9. | ROC General | 2025-12-04
ROC | December | SHSP - Theodore from ABPMC leaving site. | ROC General | 2025-12-03
ROC | December | STW12, Dominic from Honeywell is on site 15:50, Dominic is finished on site | ROC General | 2025-12-04
ROC | December | Carter Dunn Signing In, -2D/Snowing | ROC General | 2025-12-07
ROC | December | Christian Van Beek signing out. | ROC General | 2025-12-09
ROC | December | Adam Button signing out | ROC General | 2025-12-01
ROC | December | MKETFA - Khaled from IAM on site with a contractor for geotechnical investigation. KSETDP - Jun Jie from CPD on site with Landmark to initiate the maintenance. | ROC General | 2025-12-04
ROC | December | RHAMF1, Dave N from North American construction is on site | ROC General | 2025-12-05
ROC | December | QVW12, Christian from Ferguson Electric is leaving site | ROC General | 2025-12-05
ROC | December | Adeela Khan signing out | ROC General | 2025-12-05
ROC | December | STPSTL - Dre from Ferguson onsite working on ventilation | ROC General | 2025-12-08
ROC | December | QVW12 - Drew from Ferguson Electric on site to complete a generator load bank test. Drew does not expect any alarms to be triggered. | ROC General | 2025-12-02
ROC | December | Pesticon Pest Control will be visiting these sites today: SEOC, YDOC, SECC, MKPSSA, MKETFA, LSSS. | ROC General | 2025-12-02
ROC | December | JDSS - Stephen from ABPMS leaving site. Stephen also informed he has a team at QVW12 which triggered the smoke detector alarm. | ROC General | 2025-12-04
ROC | December | Connor Smith signing out | ROC General | 2025-12-04
ROC | December | SEOC OCF, Rotated Blower Duty so blower 3 is in D1 and blower 2 is in D2 for Matt S 12:46, Rotated Blowers back to original duty, Blower 1 failed to start up with no alarms persisting. Blower 1 in D1 and Blower 2 in D2 | ROC General | 2025-12-05
ROC | December | NMMCHW, Rob P on site, testing flood and temp alarms on site | ROC General | 2025-12-04
ROC | December | Ethan U signing in | ROC General | 2025-12-08
ROC | December | Christian Van Beek signing out. | ROC General | 2025-12-08
ROC | December | Carter Dunn Signing In, -6D/Clear | ROC General | 2025-12-04
ROC | December | JDSS- Drew from Ferguson Electric is on site | ROC General | 2025-12-03
ROC | December | Stouffville Zone 1/2, Cody from OCWA is doing flushing in both zones | ROC General | 2025-12-04
ROC | December | NBSSJA - Ben Han from property services leaving site. | ROC General | 2025-12-02
ROC | December | BLW3, Franco from Property services is on site | ROC General | 2025-12-05
ROC | December | STRS48, Drew from Ferguson Electric is on site | ROC General | 2025-12-04
ROC | December | Adam Button signing out | ROC General | 2025-12-07
ROC | December | Connor Smith signing out | ROC General | 2025-12-02
ROC | December | SUETDR, Terry G from Property services is on site | ROC General | 2025-12-04
ROC | December | MKETFA - Khaled from IAM leaving site. | ROC General | 2025-12-04
ROC | December | STPSTL- Christian from Ferguson Electric is on site | ROC General | 2025-12-03
ROC | December | Christian Van Beek signing in. | ROC General | 2025-12-02
ROC | December | Adam Button signing in | ROC General | 2025-12-03
ROC | December | MARS, Courtney from Tobare is on site | ROC General | 2025-12-01
ROC | December | VNPSAP, Will from Chubb is on site | ROC General | 2025-12-01
ROC | December | STPSTL - Christian from Ferguson Electric leaving site. QVW12 - Theodore from ABPMC leaving site. | ROC General | 2025-12-08
ROC | December | QVW12 - Theodore from Ab finished at site SEOC - Ben from PS finished at site | ROC General | 2025-12-09
ROC | December | MARS - Courtney from Torbear on site. | ROC General | 2025-12-09
ROC | December | KSTP - Terry G from property services leaving site after checking card readers. | ROC General | 2025-12-09
ROC | December | SEOC OCF - Hameed from ETO engineering on site for a quick investigation. KSSSQW- Christine F on site to install padlocks. | ROC General | 2025-12-08
ROC | December | KSSSQW- Ben from property services is on site | ROC General | 2025-12-01
ROC | December | Christian Van Beek signing in. Weather: -12C and clear. STETBR / STETTL - Cody from OCWA flushing zone 1 and zone 2 today. | ROC General | 2025-12-08
ROC | December | LSSS - Jon from property services on site with an elevator contractor to work on the elevator car lights. | ROC General | 2025-12-09
ROC | December | EGSSSC - Joe Oliviera from CPD on site. | ROC General | 2025-12-03
ROC | December | KSETDP - Terry G from property services on site. 13:51 - KSETDP - Terry G finished and leaving site. | ROC General | 2025-12-08
ROC | December | KSETDP - Jun Jie from IAM leaving site with landmark. | ROC General | 2025-12-08
ROC | December | AUW14- William Chubb onsite. 19:05- Offsite | ROC General | 2025-12-09
ROC | December | YDOC - Hameed from ETO Engineering on site for an inspection. | ROC General | 2025-12-08
ROC | December | KSTP - Dereck from Aquazition flushing | ROC General | 2025-12-08
ROC | December | Ethan Ullalkar signing out. | ROC General | 2025-12-20
ROC | December | Adeela Khan signing in. Weather: 6C and windy | ROC General | 2025-12-18
ROC | December | Ethan Ullalkar signing out. | ROC General | 2025-12-29
ROC | December | Angelica Chepiga signing in | ROC General | 2025-12-29
ROC | December | Adam Button signing out | ROC General | 2025-12-22
ROC | December | MTW12 - Dominic from Honeywell on site. | ROC General | 2025-12-16
ROC | December | Angelica Chepiga signing out | ROC General | 2025-12-23
ROC | December | Connor Smith signing out | ROC General | 2025-12-23
ROC | December | NBSP, Jeff from Key Shack is on site | ROC General | 2025-12-19
ROC | December | Ethan U signing in Weather 0. | ROC General | 2025-12-28
ROC | December | Ethan Ullalkar signing out. | ROC General | 2025-12-26
ROC | December | Christian Van Beek signing out. | ROC General | 2025-12-18
ROC | December | Christian Van Beek signing out. | ROC General | 2025-12-27
ROC | December | Connor Smith signing out | ROC General | 2025-12-30
ROC | December | STRS48- Andrew from Ferguson Electric is on site 10:24- STRS48- Andrew from Ferguson Electric is done on site | ROC General | 2025-12-22
ROC | December | KSTP- Andrew from Ferguson onsite. | ROC General | 2025-12-30
ROC | December | Ethan Ullalkar signing out. | ROC General | 2025-12-30
ROC | December | KBSP - Stephen from ABPMC leaving site. | ROC General | 2025-12-18
ROC | December | STETTL- Jeff from Keyshack offsite. | ROC General | 2025-12-31
ROC | December | YDOC OCF, Jeff from keyshack is leaving site | ROC General | 2025-12-19
ROC | December | Adam Button signing out | ROC General | 2025-12-16
ROC | December | MTW12 - Jeff from keyshack on site to work on the security and lock system. | ROC General | 2025-12-16
ROC | December | SHSP- Andrew from Ferguson onsite. | ROC General | 2025-12-23
ROC | December | STPSTL- Drew from Ferguson offsite. | ROC General | 2025-12-17
ROC | December | KSTP - Christian from Ferguson Electric leaving site. | ROC General | 2025-12-19
ROC | December | STETTL -Jeff from key shack is on site | ROC General | 2025-12-31
ROC | December | KBSP - Stephen from AB leaving site. | ROC General | 2025-12-23
ROC | December | STRS48- Drew from Ferguson electric on site | ROC General | 2025-12-22
ROC | December | Angelica Chepiga signing in | ROC General | 2025-12-30
ROC | December | Ethan Ullalkar signing out. | ROC General | 2025-12-21
ROC | December | Ethan U signing in Weather: 3c | ROC General | 2025-12-20
ROC | December | NBSP - Jeff from keyshack finished and leaving site. Headed to YDOC. | ROC General | 2025-12-19
ROC | December | Connor Smith signing in 3C Clear | ROC General | 2025-12-17
ROC | December | QVW12 - Christian from Ferguson Electric off site. | ROC General | 2025-12-16
ROC | December | Angelica Chepiga signing in, weather -4C | ROC General | 2025-12-16
ROC | December | Christian Van Beek signing out. | ROC General | 2025-12-16
ROC | December | Received a phone call from David Johnson (2892315264) reporting a broken gate on the ground at the Mullock and Saint john's location, behind Tim Hortons on Yonge st., NMW136 verified with Ryan B site. Corporate security has been notified on the issue. Mobile security will attend site. | ROC General | 2025-12-16
ROC | December | Connor Smith signing out | ROC General | 2025-12-16
ROC | December | MAPS - Chris from property services on site to test the fire alarm. | ROC General | 2025-12-16
ROC | December | Carter D Signing In, 5D/Clear | ROC General | 2025-12-29
ROC | December | KBSP- Steven from AB onsite | ROC General | 2025-12-16
ROC | December | AURSBS - Mark from Process Optimization group on site. 13:53 Mark leaving site and heading to AUW14. | ROC General | 2025-12-23
ROC | December | GWTP - Niel from Liftsafe engineering on site for a crane inspection. | ROC General | 2025-12-18
ROC | December | STRS48, Garrick from Ferguson Electric is on site | ROC General | 2025-12-19
ROC | December | Connor Smith signing in -5C Snowy | ROC General | 2025-12-31
ROC | December | Carter Dunn Signing In, -11D/Clear | ROC General | 2025-12-30
ROC | December | Angelica Chepiga signing out | ROC General | 2025-12-30
ROC | December | Ethan U signing in Weather -9. | ROC General | 2025-12-27
ROC | December | Carter D Signing Out | ROC General | 2025-12-19
ROC | December | Carter Dunn Signing In, -6D/Clear | ROC General | 2025-12-20
ROC | December | Carter D signing in, -2D/Clear | ROC General | 2025-12-28
ROC | December | NMSSBP - Patrick from property services finished and leaving site. | ROC General | 2025-12-19
ROC | December | Carter Dunn Signing Out | ROC General | 2025-12-28
ROC | December | Ethan U signing in Weather -9. | ROC General | 2025-12-29
ROC | December | Pest Control visiting following sites- AURSBS, AUETAD, AUSSYS, AUPSRR, AUW14, AUPSOH, AUW57, AUSS, AUW6, AUETFC, AUPSWS | ROC General | 2025-12-17
ROC | December | Carter Dunn Signing In, 4D/Rain | ROC General | 2025-12-19
ROC | December | STRS48 - Garrick from Ferguson Electric leaving site. | ROC General | 2025-12-19
ROC | December | Ethan U signing in Weather -4. | ROC General | 2025-12-19
ROC | December | KSTP - Christian from Ferguson leaving site | ROC General | 2025-12-18
ROC | December | YDOC OCF, Jeff from Keyshack is on site | ROC General | 2025-12-19
ROC | December | Christian Van Beek signing in. Weather: -6C and clear. | ROC General | 2025-12-26
ROC | December | MKETSA- Ahmed from YRP onsite. | ROC General | 2025-12-22
ROC | December | SUSP - Terry G from property services on site to work on the security card readers. | ROC General | 2025-12-18
ROC | December | STPSTL - Chrsitian from Ferguson | ROC General | 2025-12-17
ROC | December | Adam Button signing out | ROC General | 2025-12-31
ROC | December | STETBR - Lane from Town of Stouffville will be flushing in zone 1 today. | ROC General | 2025-12-18
ROC | December | Adam Button signing in -10 Clear | ROC General | 2025-12-21
ROC | December | Carter D Signing In, -4D/Clear | ROC General | 2025-12-21
ROC | December | Connor Smith signing out | ROC General | 2025-12-18
ROC | December | YDOC- Johnathan from Property Services onsite. | ROC General | 2025-12-22
ROC | December | KSSP- Franco from Property Services offsite | ROC General | 2025-12-22
ROC | December | Angelica Chepiga signing in | ROC General | 2025-12-23
ROC | December | STPSTL - Drew from Ferguson back onsite | ROC General | 2025-12-17
ROC | December | Adam Button signing in | ROC General | 2025-12-30
ROC | December | AUSS, Patburte from Property Services is on site, testing fire alarms 08:35, Patburte is finished on site | ROC General | 2025-12-19
ROC | December | Christian Van Beek signing in. Weather: -11C and clear. | ROC General | 2025-12-27
ROC | December | MARS - Courtney from Torbear is on site | ROC General | 2025-12-19
ROC | December | Adeela Khan signing in. Weather: -7C and snowing | ROC General | 2025-12-31
ROC | December | Christian Van Beek signing in. Weather: -7 C and clear. | ROC General | 2025-12-16
ROC | December | Angelica Chepiga signing out | ROC General | 2025-12-18
ROC | December | Connor Smith signing in | ROC General | 2025-12-18
ROC | December | Christian Van Beek signing in. | ROC General | 2025-12-19
ROC | December | Adeela Khan signing in. Weather: 3C and cloudy | ROC General | 2025-12-23
ROC | December | Christian Van Beek signing in. Weather: -2C and clear. | ROC General | 2025-12-24
ROC | December | Adam Button signing out | ROC General | 2025-12-30
ROC | December | STETTL - Corey from Stouffville water called to inform he will be sampling in zone 2 for fifteen minutes to collect a sample. | ROC General | 2025-12-19
ROC | December | Carter Dunn Signing In, -1D/Clear | ROC General | 2025-12-22
ROC | December | STPSTL - Drew from Ferguson electric on site. | ROC General | 2025-12-18
ROC | December | Adam Button signing in | ROC General | 2025-12-31
ROC | December | SUSP - Terry G. finished on site. Informed ops on site | ROC General | 2025-12-18
ROC | December | Angelica Chepiga signing out | ROC General | 2025-12-17
ROC | December | NBSP- Jeff from Keyshack offsite. | ROC General | 2025-12-23
ROC | December | Angelica Chepiga signing in | ROC General | 2025-12-24
ROC | December | KBSP - Theodore from ABPMC leaving site. | ROC General | 2025-12-16
ROC | December | Carter Dunn Signing Out | ROC General | 2025-12-23
ROC | December | Angelica Chepiga signing in | ROC General | 2025-12-23
ROC | December | GWTP, Ligag H from GO Pro Consulting is heading to site to collect samples | ROC General | 2025-12-19
ROC | December | Carter Dunn Signing Out | ROC General | 2025-12-31
ROC | December | AUSSYS- Jeff from Keyshack is on site 13:43-AUSSYS- Jeff from Keyshack is done on site | ROC General | 2025-12-31
ROC | December | Connor Smith signing in -12C Windy | ROC General | 2025-12-30
ROC | December | Connor Smith signing out | ROC General | 2025-12-31
ROC | December | KSTP- Andrew from Ferguson electric is done on site | ROC General | 2025-12-30
ROC | December | Angelica Chepiga signing out | ROC General | 2025-12-29
ROC | December | ARPS- Discharge flow lolo alarm came in while pump was running. Residuals look okay close to D1 shutdown and looks like pump is ramping down its speed causing lower flows. | All Water System ROC General | 2025-12-13
ROC | December | NMVCBA- Placed valve in man/open at 20L/s to help slow drain of NMETHW | All Water System ROC General | 2025-12-13
ROC | December | NMW12- Effluent free Cl2 fault reset. Will monitor well start up | All Water System ROC General | 2025-12-13
ROC | December | Ethan Ullalkar signing out. | All Water System ROC General | 2025-12-11
ROC | December | Adeela Khan signing out | All Water System ROC General | 2025-12-11
ROC | December | STETTL - Noted tower is below duty start due to restricted flow program from STPSMR. STETBR is active and pulling from the system of STETTL. STETBR fill cycle almost complete. Deactivated STETBR to allow STETTL to recover. | All Water System ROC General | 2025-12-11
ROC | December | YWS+NYWS normal | All Water System ROC General | 2025-12-15
ROC | December | NMETHW - Deactivated duty 1 while NMETIB fills. | All Water System ROC General | 2025-12-10
ROC | December | QVW34- Chlorine Room Gas Leak Alarm, CL2 Emergency Valve Closure Active Alarm. Placed wells in manual. Notified Donald M. Valve Closure System was tested today. Requested to disregard. Call if Hi or HiHi Alarms are triggered. CONSULT | All Water System ROC General | 2025-12-11
ROC | December | VNPS PD7/PD8 - Lee F on site to complete vibration testing. Will cycle through pumps as needed. | All Water System ROC General | 2025-12-10
ROC | December | YWS+NYWS normal | All Water System ROC General | 2025-12-13
ROC | December | Christian Van Beek signing out. | All Water System ROC General | 2025-12-10
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-11
ROC | December | VNRSKS- Deactivated D1 | All Water System ROC General | 2025-12-10
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-11
ROC | December | Ethan Ullalkar signing out. | All Water System ROC General | 2025-12-12
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-13
ROC | December | KSTP- Finished fluoride hi alarm came in. Residual spiked and recovered. Notified Patrick F of alarm and directed to reset alarm as trends have stabilized #consult | All Water System ROC General | 2025-12-13
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-13
ROC | December | YWS+NYWS normal | All Water System ROC General | 2025-12-13
ROC | December | MKVCSA- Rob P on site for winter change over | All Water System ROC General | 2025-12-12
ROC | December | Carter Dunn Signing In, -1D/Clear | All Water System ROC General | 2025-12-12
ROC | December | YWS + NYWS normal | All Water System ROC General | 2025-12-12
ROC | December | QVW34 - Place both wells in man/off position as chlorinators remain OOS | All Water System ROC General | 2025-12-11
ROC | December | YWS+NYWS normal | All Water System ROC General | 2025-12-15
ROC | December | JFPS - Lee F on site to complete vibration testing on the pumps. Lee has requested that each pump be activated for five minutes to obtain the readings. Activated pump 1. Will cycle the pumps as necessary. | All Water System ROC General | 2025-12-10
ROC | December | SUETDR - Phil D on site to complete chlorine analyzer maintenance and low temperature alarm test. | All Water System ROC General | 2025-12-10
ROC | December | RHRSTR- Power failure alarm came in. VNPS- Power failure and utility not availability and process sump P1/2 fault alarm able to clear all alarms site back on utility | All Water System ROC General | 2025-12-10
ROC | December | GWTP - Patrick F onsite, disregard chemical room gas level fault. Caused hen filling bisulfate tank. UV are placed man/off by operator. | All Water System ROC General | 2025-12-12
ROC | December | YWS+NYWS normal | All Water System ROC General | 2025-12-13
ROC | December | MKRSMR - Cell 2 Forward Flow hi/hihi alarms. Trends indicate fluctuating forward flow for the past hour. Possibly a flowmeter issue. Flow increased when RHPSPA Duty activated. Called Patrick F. He will check SCADA and monitor for now. GWTP - ZW7 CIP Feed inlet V failed to open, CIP water flow low alarm. Notified Partick F. He will check SCADA and monitor. # Consult | All Water System ROC General | 2025-12-14
ROC | December | RHRSTR- Able to reset power fail alarm VNPS- Process sump P1/2 fault alarm came in during power outage. Was able to clear both alarms. Site okay | All Water System ROC General | 2025-12-10
ROC | December | NBW3 - Station turbidity fault alarm. Checked site, well is off no water directed to users. Trending shows turbidity is stable and within normal range. Able to reset alarm. | All Water System ROC General | 2025-12-12
ROC | December | QVW34 - Donald M & Alex B onsite to work on leak | All Water System ROC General | 2025-12-11
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-11
ROC | December | MARS / MAPS - Joe W is on site and will be completing chlorine analyzer maintenance. | All Water System ROC General | 2025-12-10
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-14
ROC | December | MARS- Cell1 (North) Lvl Hi Alarm RHMCMD- Placed valve in manual RHRSTR- Deactivated duty | All Water System ROC General | 2025-12-14
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-12
ROC | December | NBW3 - Dan B onsite. Working on chlorine containment float switch. Testing hypo containment flood alarm. | All Water System ROC General | 2025-12-11
ROC | December | STPSTL - Dan Z has placed the pumps manual/off for a deep cycle of the STETBR tower. The low alarm setpoint for STETBR has been changed to 40% to mirror the deep cycle. | All Water System ROC General | 2025-12-15
ROC | December | MKETFA - TO (Mehdi) informed they are exercising valves. May experience low pressure temporarily during exercise. | All Water System ROC General | 2025-12-11
ROC | December | HLETYS - Ammonia pump 1 and pump 2 fault alarm. Checked site, tower is filling and chemical system is active. Able to reset alarms, ammonia pumps activated. Will monitor system. | All Water System ROC General | 2025-12-10
ROC | December | BVPS- Free Cl2 fault alarm. Alarm cleared upon acknowledgement Jack P on site for sampling QVW34- Influent free Cl2 hihi alarm came in. Switching back to one well operation causing spike. Alarm cleared upon acknowledgment | All Water System ROC General | 2025-12-10
ROC | December | NBW3- Influent free Cl2 lolo switch alarm came in. Found well in man/off. Tim H heading to site with Stephen B QVW34- Jerry Z and Alex B on site to work on Cl2 system and troubleshoot leak. Alex B req CMU5 for site revisit later to confirm leak has been resolved. Created CMU5 W11511250 #CMU5 | All Water System ROC General | 2025-12-12
ROC | December | STPSMR- Jackie P on site having issue with OIT. Notified Artour L who will investigate. | All Water System ROC General | 2025-12-12
ROC | December | QVW34 - Donnald M onsite with Alex B working on chlorinator to replace regulator | All Water System ROC General | 2025-12-12
ROC | December | NBW3- Influent free Cl2 hi alarm came in. Reset after 3 mins as trends recovered NMW12- Combined and Treated Cl2 lo alarms came in. Well not active no water directed to users | All Water System ROC General | 2025-12-13
ROC | December | NMW15- Placed well in man/off for Kingsley M to restart OIT | All Water System ROC General | 2025-12-10
ROC | December | NMETIB- Deactivated duty NMVCBA- Adjusted back to 40L/s NMVCIB- Adjusted back to 80L/s | All Water System ROC General | 2025-12-14
ROC | December | YWS + NYWS NORMAL Angelica Chepiga signing out | All Water System ROC General | 2025-12-14
ROC | December | AURSBS - Post injection total chlorine hi alarm. Checked site, chlorination system is active. Trending shows a variable reading for the total and combined chlorine residuals. Will M attending site assisted by Jerry Z. | All Water System ROC General | 2025-12-10
ROC | December | RHMCMD - Security intrusion alarm. Followed up with Gary P, confirmed he is onsite and will be testing flood alarm | All Water System ROC General | 2025-12-12
ROC | December | GWTP - Clearwell 1 chlorine hi alarm. Disregard as per shift report | All Water System ROC General | 2025-12-12
ROC | December | NMETIB - Activated D1 to offset with NMETHW | All Water System ROC General | 2025-12-14
ROC | December | STETTL - Tarvis W on site to complete work orders including the JHSC Checks, sump pit inspection, low temperature alarm test and chlorine analyzer maintenance if possible. | All Water System ROC General | 2025-12-15
ROC | December | HUB1 Server - Yash S restarting server. | All Water System ROC General | 2025-12-15
ROC | December | NMTKKC - Joe D finished at site, revert stop setpoint back to 75% | All Water System ROC General | 2025-12-12
ROC | December | VNPS PD8 - Following Lee F pump testing changed the duty 1 and duty 2 status to the pumps that were currently running in manual mode. Once the duty 1 was assigned to the running pumps placed them in auto mode. Pump 2 (duty 2) deactivated. Waited a period of time and then re-activated the pump in manual until the duty is finished. | All Water System ROC General | 2025-12-15
ROC | December | Ethan Ullalkar signing in | All Water System ROC General | 2025-12-11
ROC | December | NMW136- Combined Cl2 lo alarm came in recovered after 3 mins alarm cleared | All Water System ROC General | 2025-12-13
ROC | December | HLW1- Influent free Cl2 hi alarm came in on well start up. recovered after 3 mins cleared alarm | All Water System ROC General | 2025-12-13
ROC | December | HLW2- Changed flow control valve flow setpoint from 50L/s to 40L/s | All Water System ROC General | 2025-12-13
ROC | December | NMW12- Effluent free Cl2 fault came back in while well running. did not pass contact tank. Notified Ryan B will check SCADA #consult | All Water System ROC General | 2025-12-13
ROC | December | HLW2- Changed flow set points from 45L/s to 50L/s | All Water System ROC General | 2025-12-13
ROC | December | YWS+NYWS normal | All Water System ROC General | 2025-12-13
ROC | December | NMTKKC- Outlet total Cl2 lolo alarm came in. Sudden dip in trends but recovered right away cleared alarm RHMCMD- Placed back in auto | All Water System ROC General | 2025-12-13
ROC | December | NMW136 - Jason G. is on site and will be cleaning the analyzers, turbidimeters, and will be testing the chlorine leak alarm. Directed to disregard associated alarms until work is complete | All Water System ROC General | 2025-12-11
ROC | December | NMVCIB- Change flow set point from 40L/s to 80L/s NMVCBA- Changed flow set point from 80L/s- 40L/s ANVCPL- Change flow set point from 110L/s to 100L/s NMETIB-DeactivatedD1 at 72% to offset from NMETHW as per shift report to offset from NMETHW | All Water System ROC General | 2025-12-15
ROC | December | MTETNL, Historian Heartbeat, Notified Artour L, he will look into it CMU5: W11511619 | All Water System ROC General | 2025-12-12
ROC | December | RHMCMD, Placed valve man/closed | All Water System ROC General | 2025-12-12
ROC | December | BLW12 - Kyle C working on site/transferring system. Dan Z is aware as per Kyle C. | All Water System ROC General | 2025-12-15
ROC | December | STETTL - Travis W cleaning chlorine analyzers. | All Water System ROC General | 2025-12-15
ROC | December | Gluzen Ramos Ong signing in | All Water System ROC General | 2025-12-15
ROC | December | YWS + NYWS NORMAL | All Water System ROC General | 2025-12-14
ROC | December | STETTL/STETBR- Andrew from OCWA is flushing in zone 1/2 | All Water System ROC General | 2025-12-15
ROC | December | MARS - Called Toronto Water (Zoran) and requested max flow to MARS due to ARPS emergency shutdown. VNRSKS- Deactivated duty and then swapped supply pumps from MAPS to VNPS to reduce demand on MARS while ARPS is down. | All Water System ROC General | 2025-12-15
ROC | December | MKPSSA - Jack P on site, running generator and testing flood alarm. Runing pumps MKRSMR - Building flood alarm, Joe M testing alarm , will clean chlorine analyzers and test Res Hi/Low level alarms. MKRSEM - Zoran from Toronto water called, in preparation to curtailment will run 2 pumps to fill Res. | All Water System ROC General | 2025-12-15
ROC | December | SHTP - Filter 2 Post Rinse NIT Nigh alarm - Benson S on site, will check. | All Water System ROC General | 2025-12-15
ROC | December | VNPS PD8 - Lee F on site for pump testing. Duty 1 and 2 just activated. Lee requested switch pump 1 and pump 3 to pumps 2 and 4 . Placed all pumps on man, switching pumps one in a time. | All Water System ROC General | 2025-12-15
ROC | December | BVPS - Activated D1. | All Water System ROC General | 2025-12-15
ROC | December | Angelica Chepiga signing out | All Water System ROC General | 2025-12-15
ROC | December | YWS + NYWS Normal Christian Van Beek signing out. | All Water System ROC General | 2025-12-15
ROC | December | KSTKWP- Chlorinator 1 failed to close alarm. Chlorinator is currently closed, reset alarm. | All Water System ROC General | 2025-12-15
ROC | December | HLETYS- Cole W on site testing chemical pumps GWTP- Clearwell 1 Cl2 hi alarm outstanding notified Patrick F. who will continue to monitor MTW3- Shaun P done work on generator leaving site MKVCSA- Rob P on site | All Water System ROC General | 2025-12-12
ROC | December | SHTP - Filter 2 post rinse NIT hi alarm. Checked site, filter just went through a backwash. Able to reset alarm as per the shift report. | All Water System ROC General | 2025-12-15
ROC | December | AUW14 - Activated two wells in manual mode to prolong the drain cycle of AURSOH while ARPS is down. Informed area ops. | All Water System ROC General | 2025-12-15
ROC | December | RHMCMD - Place back in auto | All Water System ROC General | 2025-12-12
ROC | December | KSTKWP - Gas chlorinator 1 failed to close alarm. Called Ryan B who stated that this alarm can be left outstanding overnight and he will attend to it tomorrow. | All Water System ROC General | 2025-12-15
ROC | December | AUW14 - Pump 1 fail to start on a multilin trip alarm. Checked site, well was running when the multilin trip alarm triggered. Rotated duty 1 to pump 2 and placed AUW1 in manual/off mode. Sent email to OCO. | All Water System ROC General | 2025-12-15
ROC | December | ARPS - Airport Rd Pressure LoLo alarm, notified Central/West OP about ARPS emergency shutdown. | All Water System ROC General | 2025-12-15
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-13
ROC | December | NMETIB, Activated D1 | All Water System ROC General | 2025-12-13
ROC | December | STETBR, Tower lo alarm, placed STW13 in man/on RHMCMD, Placed valve man/closed | All Water System ROC General | 2025-12-13
ROC | December | Angelica Chepiga signing in, weather -8C | All Water System ROC General | 2025-12-15
ROC | December | Christian Van Beek signing in. RHMCMD - Closed valve and placed in auto mode. | All Water System ROC General | 2025-12-15
ROC | December | ARPS - Jerry from Peel/OCWA called with update. Contractors on site investigating, no flow to YR. Jerry will call with next update in 2-3 hours. | All Water System ROC General | 2025-12-15
ROC | December | HLW2- Treated total and combined CL2 lolo alarms came in. Analyzer dropped out and well not active. No water directed to users trends recovered after 6 mins alarms cleared | All Water System ROC General | 2025-12-15
ROC | December | MARS - ARPS supply feed is back online. Called Toronto Water and requested they reduce to normal flow. | All Water System ROC General | 2025-12-15
ROC | December | NBW2 - Rick L and Parth P on site to work on the influent free chlorine analyzer. Tim H also on site, Rick L will be coordinating work with Tim. | All Water System ROC General | 2025-12-15
ROC | December | VNRSKS - Swapped supply pumps from VNPS to MAPS. Activated duty 1. | All Water System ROC General | 2025-12-15
ROC | December | STPSMR- Heather from York region is done on site. Placed P1 man/off MAPS- Dan B req to call Alectra for site visit as there is no power after field crews inspected infrastructure. Spoke with Scott who will reach out to operations for more details req Dan B to reach out himself to triage issue. Notified Dan B who will reach out to Alectra to resolve issue STW12- Heather from York region on site req both wells to run. Notified Dan Z. Dan Z will reach out to Heather VNPS- Lee F done on site | All Water System ROC General | 2025-12-10
ROC | December | STPSMR - Joe M and Jack P completed work on site. | All Water System ROC General | 2025-12-15
ROC | December | NBET27 - Tim H headed to site for chlorine analyzer maintenance. NBVW2 - Tim H will be attending site to work on the chlorine analyzers. | All Water System ROC General | 2025-12-15
ROC | December | AUW14 - Activated a third well pump to provide additional flow while ARPS is down. | All Water System ROC General | 2025-12-15
ROC | December | ARPS - Airport Free Ammonia fault , value is normal, cleared alarm. | All Water System ROC General | 2025-12-15
ROC | December | NBET27- Outlet free Cl2 lo alarm came in. Tim H on site trouble shooting analyzer | All Water System ROC General | 2025-12-12
ROC | December | MKRSEM - Request TO (Brent) to put on 2 pumps | All Water System ROC General | 2025-12-12
ROC | December | VNRSKS- Activated D1 NMVCBA- change flow set pint from 20L/s to 40L/s | All Water System ROC General | 2025-12-13
ROC | December | MTW3 - Kyle R working on site, will deenergize Building system for a few hours. | All Water System ROC General | 2025-12-15
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-10
ROC | December | MARS- David D has switched station back to utility power and leaving site. | All Water System ROC General | 2025-12-10
ROC | December | GWTP- Sutton header fluoride lo alarm came in. Notified Patrick F. Keswick line dosing okay and directed to disregard. #consult | All Water System ROC General | 2025-12-13
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-13
ROC | December | NMW15- Ammonia Tank 1 Vlv Failed to Close Alarm. Well running in schedule mode and duty 1 switched to tank 2. Attempted to close tank 1 vlv in manual but would not close. Schedule mode finished and placed well in manual. Emailed Ryan B. | All Water System ROC General | 2025-12-13
ROC | December | NMVCBA- Changed valve from 40 to 80L/s NMVCIB- Changed valve from 80 to 40L/s | All Water System ROC General | 2025-12-13
ROC | December | NMVCBA- Placed valve in manual 20L/s 04:20- Placed valve back to auto. | All Water System ROC General | 2025-12-10
ROC | December | YWS + NYWS Normal Connor Smith signing out | All Water System ROC General | 2025-12-10
ROC | December | Adeela Khan signing in. Weather: -12 and snowing | All Water System ROC General | 2025-12-11
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-12
ROC | December | KCETFS - Valve room Eyewash Flow alarm came in. Called Joe W. who informed he triggered that alarm and to disregard for the time being | All Water System ROC General | 2025-12-11
ROC | December | RHMCMD - Closed valve and then placed in auto mode. | All Water System ROC General | 2025-12-10
ROC | December | YWS+NYWS normal | All Water System ROC General | 2025-12-13
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-14
ROC | December | STETBR - Tower Level Lo alarm came in. Placed STW1 and STW3 man/on, as per interim | All Water System ROC General | 2025-12-11
ROC | December | ARPS - Tegbeer from Peel/OCWA called/informed Discharge header leaking from OCWA/ARPS side, will stop pumps, no ETR for now. | All Water System ROC General | 2025-12-15
ROC | December | STETBR - Low level alarm, placed STW12, STW3 man mode (currently running) for ET fill cycle. | All Water System ROC General | 2025-12-14
ROC | December | NMVCBA- Changed flow setpoints from 80L/s to 40L/s NMVCIB- Changed flow setpoints from 40L/s to 80L/s GWTP- Train 2 transmembrane Pressure lo alarm came in. Alarm cleared as acknowledged. Pressure within range 19:05- GWTP- Train 2/5 transmembrane Pressure lo alarm came in. Notified Patrick F. Directed to disregard as they filters are close to going into backwash | All Water System ROC General | 2025-12-14
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-11
ROC | December | YWS+NYWS normal | All Water System ROC General | 2025-12-13
ROC | December | GWTP - Yash S will be working remotely on the GWTP server. Yash will be triggering a historian heartbeat alarm that can be disregarded. | All Water System ROC General | 2025-12-15
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-11
ROC | December | BVPS - Discharge Free Chlorine HiHi alarm came in. Disregarded as per shift report | All Water System ROC General | 2025-12-11
ROC | December | Christian Van Beek signing in. Weather: -10C and clear. | All Water System ROC General | 2025-12-11
ROC | December | SHETCS - hypo building low temp alarm. Ambient temperature is well below freezing, there is potential for chlorine lines to be affected. Called Jordan B who stated that the heating system has changed recently and that the chlorine system should be okay for tonight. Directed to disregard the alarm until tomorrow at 09:00. #consult | All Water System ROC General | 2025-12-11
ROC | December | NMW12- Effluent free Cl2 fault alarm came in. Well not active. D1 almost active and will try to reset alarm to lift interlock on wells. STETTL- Tower not filling with D1 active. Called Patrick F to inquire about drawing down STETBR and back feeding from zone 1 to help fill during STPSMR reduction in pumping test. Directed to let tower float while zone 1 fills and not to make any changes that may affect test. Will continue to monitor #consult | All Water System ROC General | 2025-12-13
ROC | December | NMETHW- Activated D1 to offset from NMETIB | All Water System ROC General | 2025-12-13
ROC | December | MTW3 - Sean P onsite working on generator | All Water System ROC General | 2025-12-12
ROC | December | HLEYYS - Ammonia pump 1 & 2 failed to start. Hypo pump 1 running. Able to clear, informed Tim H & Benson S of alarm as well as issue with trend in hypo pump 1 speed indication dropping drastically and picking back up for a period of itme within the last hour. Benson S aware and looking into issue | All Water System ROC General | 2025-12-12
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-12
ROC | December | RHMCMD - Placed valve in manual and opened. YWS + NYWS Normal | All Water System ROC General | 2025-12-12
ROC | December | Adam Button signing in -10 Clear | All Water System ROC General | 2025-12-14
ROC | December | RHMCMD - Back to auto. | All Water System ROC General | 2025-12-15
ROC | December | QVW12- Generator fault alarm came in able to clear alarm | All Water System ROC General | 2025-12-14
ROC | December | King Township- Matt W from King Township (416-559-5100) is responding to watermain break at 13097 Keele St. and notified ROC that there is quite a bit of ice forming on the road and req. to see if roads can dispatch a salter to site. Called Roads dispatch spoke with Abdullah to have someone attend site to deal with the road conditions. Notified Matt W that salter has been dispatched KLPSWL- Historian heartbeat alarm came in Trends flatlined. Notified Artour L. Created CMU5 W11511874 19:35-KLPSWL- Artour L was able to clear historian heartbeat alarm and trends look okay. #CMU5 | All Water System ROC General | 2025-12-14
ROC | December | HLETYS- ammonia pump 1/2 failed to start alarm came in reset alarms. Likely due to not enough flow to allow chemical system to dose appropriately. Notified Jordan as the alarm came back in after 2 resets. Directed to increase flow at HLW2 valve chamber from 40 to 45L/s to see if extra flow will be able to correct dosing issues. #consult | All Water System ROC General | 2025-12-13
ROC | December | GWTP - Patrick F requested Clearwell fill permeate valve man/close. | All Water System ROC General | 2025-12-15
ROC | December | NBW37 - Parth P and Rick L leaving site. | All Water System ROC General | 2025-12-15
ROC | December | VNPS PD8- Placed P2 back in auto | All Water System ROC General | 2025-12-16
ROC | December | STW12/STW3 - Place well 1 and 3 back in auto | All Water System ROC General | 2025-12-12
ROC | December | GWTP - Pressurized Vestibule Lo Temperature alarm, notified Patrick F. He will check SCADA. # Consult | All Water System ROC General | 2025-12-14
ROC | December | KBPS27 - Historian heartbeat alarm, notified Artour L. He will check SCADA. | All Water System ROC General | 2025-12-15
ROC | December | MTW3 - Kyle R finished on site. MAPS - Lee F finished on site, pumps back to normal OP. | All Water System ROC General | 2025-12-15
ROC | December | AUW14 - Deactivated pump 2 (Duty 3) and placed pump 1 and pump 3 (duty 1) in auto mode. Duty is active so pump 1 and 3 will remain active. | All Water System ROC General | 2025-12-15
ROC | December | STPSMR - Jack P with Joe M on site, reverting site back to 2 pumps OP/ working on chlorine regulator. Jack P requested If receive chlorine leak alarm, disregard for the duration of the work. | All Water System ROC General | 2025-12-15
ROC | December | Adam Button signing in -10 Clear | All Water System ROC General | 2025-12-15
ROC | December | NMTKKC - Joe D requested to change duty 1 stop from 75 to 80%. Made duty stop change | All Water System ROC General | 2025-12-12
ROC | December | NMW15- Combined CL2 lo alarm came in. Well is man/off for the night no water directed to users | All Water System ROC General | 2025-12-15
ROC | December | RHMCMD- Placed valve in man closed 0% | All Water System ROC General | 2025-12-15
ROC | December | YWS+NYWS normal | All Water System ROC General | 2025-12-15
ROC | December | YWS+NYWS normal | All Water System ROC General | 2025-12-15
ROC | December | GWTP - Patrick F & Phil D onsite. Working on low lift turbidity, chlorine, Health & safety, flood alarm, chlorine leak, chlorine scrubber | All Water System ROC General | 2025-12-11
ROC | December | YWS+NYWS normal | All Water System ROC General | 2025-12-16
ROC | December | Adam Button signing in snowing -10 | All Water System ROC General | 2025-12-13
ROC | December | Adam Button signing out | All Water System ROC General | 2025-12-12
ROC | December | NMETHW - Deactivate duty 1 as Ivsbridge activated | All Water System ROC General | 2025-12-11
ROC | December | NBW3- Station Turbidity Fault Alarm. Second time this alarm has come in. Well not running. Placed in manual and will email West Ops. | All Water System ROC General | 2025-12-11
ROC | December | MARS- Cell1 (North) Lvl Hi Alarm RHMCMD- Placed in manual RHRSTR- Deactivated duty | All Water System ROC General | 2025-12-11
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-11
ROC | December | AURSBS- Chlorine GCLR 2 Vlv Fail to Open Alarm. Alarm cleared. | All Water System ROC General | 2025-12-11
ROC | December | STW12- Placed well 2 back into auto STW3- Placed well 3 back into auto | All Water System ROC General | 2025-12-10
ROC | December | NBW3 - Station turbidity fault. Known issue with flow sensor on the NTU, flow reading incorrectly. Tim H aware from this morning and okay to disregard. Turbidity reading within range | All Water System ROC General | 2025-12-11
ROC | December | STPSMR - Heather from York Region is on site to complete flow testing. Heather needs one pump active for one hour. Duty is off. Contacted Dan Z =to ensure area ops are aware, they are. Placed all other duty pumps manual/off and activated the duty so one pump runs at STPSMR. | All Water System ROC General | 2025-12-10
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-11
ROC | December | HLPSYS - Generator running status. Followed up with Benson S, confirmed he is onsite & Running generator, and testing temp 11:43 - Leaving site HLETYS - Benson S will be working on deplox analyzer as well | All Water System ROC General | 2025-12-11
ROC | December | BLW12 - Dan Z. is on site and will be running both wells simultaneously as part of a test for the commissioning of the new chlorine contact tank. Dan informed that everything will be back to normal by the end of the day | All Water System ROC General | 2025-12-11
ROC | December | NMW136 - Combined Chlorine and Treated total chlorine lo alarms came in. Wells are not running and water is not being directed to users | All Water System ROC General | 2025-12-11
ROC | December | Connor Smith signing out | ROC General | 2025-12-11
ROC | December | GWTPLL - Terry G from PS onsite looking into emergency lighting SEOC6/7 - Johnathan leaving site | ROC General | 2025-12-12
ROC | December | QVW12 - Drew from Ferguson Electric on site. QVETQS - Terry G from property services on site to inspect the emergency light systems. | ROC General | 2025-12-15
ROC | December | Adam Button signing out | ROC General | 2025-12-12
ROC | December | KSTP- Dan B and Ernie H done on site QVW34- Donald M done on site Cl2 system is okay | All Water System ROC General | 2025-12-12
ROC | December | MKRSEM, Notified Toronto operator brent to stop pumping to the res | All Water System ROC General | 2025-12-13
ROC | December | MKRSEM- Called Toronto (Brett) and requested 2 pumps on. | All Water System ROC General | 2025-12-14
ROC | December | RHMCMD- Placed in manual at 0% YWS+NYWS normal | All Water System ROC General | 2025-12-14
ROC | December | QVW12- Generator Fault Alarm. Alarm cleared. | All Water System ROC General | 2025-12-14
ROC | December | STETBR- Tower level hi alarm came in. Placed STW12/STW3 back in auto as per interim | All Water System ROC General | 2025-12-15
ROC | December | YWS+NYWS normal Adam Button signing out | All Water System ROC General | 2025-12-15
ROC | December | KBSP - Drew from Ferguson Electric on site. | ROC General | 2025-12-15
ROC | December | NBW5 - Silicate Pump 1 Fault and Leakage alarms came in. Checked site. Duty just activated and silicate pump 2 is unavailable. Called Jordan B. who directed to place well man/off and will attend site. CMU5 Created W11508931 NBW3 - Jordan will attend site for the Influent Free Chlorine LoLo switch. CMU5 created W11508923 #CMU5 | All Water System ROC General | 2025-12-11
ROC | December | RHAMF - Jamie from North American construction called and asked for the alarms on site to be cleared. Alarms on site cleared but the make up air unit failed to start again. Jamie on site and is investigating. | ROC General | 2025-12-10
ROC | December | AUPSRR- Will M on site working on Chem scan | All Water System ROC General | 2025-12-10
ROC | December | BVPS- Rick L done on site | All Water System ROC General | 2025-12-10
ROC | December | VNPS - Rob from CPD on site for inspection. 13:00 Off site. | ROC General | 2025-12-15
ROC | December | NMSSBP - Milad from security informed of fire panel alarm, looked into issue today and appeared was worked on earlier in day. PS building operator informed to disregard (no name on hand) Security will also further look into issue on Monday | ROC General | 2025-12-19
ROC | December | YWS + NYWS NORMAL | All Water System ROC General | 2025-12-14
ROC | December | NBW5 - Rick L and Parth P finished and leaving site. TIm H on site. NBW3/7 - Parth P and Rick L on site for turbidity analyzer maintenance. | All Water System ROC General | 2025-12-15
ROC | December | STW3 - Travis W onsite working on CL17 & turbidity analyzer NMETIB - Joe D testing eyewash, flood, & temp alarm | All Water System ROC General | 2025-12-11
ROC | December | Christian Van Beek signing in. Weather: -3 and snow. | ROC General | 2025-12-10
ROC | December | Christian Van Beek signing in. Weather: -3 and snow. | All Water System ROC General | 2025-12-10
ROC | December | AUPSRR - Post injection free chlorine hihi alarm. Checked site, reservoir recently started filling which activated the chlorination system. Trending shows a spike of the free chlorine residual reading which returned to normal range within one reading interval. Reset alarm. | All Water System ROC General | 2025-12-10
ROC | December | SEOC - Johnathan from PS onsite YDOC - Franko from PS finished at site | ROC General | 2025-12-12
ROC | December | YWS + NYWS NORMAL | All Water System ROC General | 2025-12-14
ROC | December | YWS+NYWS normal RHMCMD- Place valve in man open 100% | All Water System ROC General | 2025-12-15
ROC | December | AUW14- Jerry Z heading to site to investigate building flood alarm created CMU5 W11511463 #CMU5 | All Water System ROC General | 2025-12-12
ROC | December | SEOC OCF - Ben from Property Services is on site changing a filter for the makeup air unit 13:52 - Ben is finished on site | ROC General | 2025-12-11
ROC | December | HMSS - Steve from York Regional Doors on site. | ROC General | 2025-12-16
ROC | December | STRS48- Drew from Ferguson onsite. | ROC General | 2025-12-17
ROC | December | NBW2- influent free Cl2 lolo switch alarm came in interlocking well. Notified Tim H. Will investigate on site | All Water System ROC General | 2025-12-10
ROC | December | Connor Smith signing out | ROC General | 2025-12-14
ROC | December | Carter D Signing out | All Water System ROC General | 2025-12-13
ROC | December | MAPS/JFRS- Reverted Maple to Jefferson Feed | All Water System ROC General | 2025-12-14
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-14
ROC | December | NMETIB- Activated duty | All Water System ROC General | 2025-12-14
ROC | December | YWS + NYWS Normal Connor Smith signing out | All Water System ROC General | 2025-12-14
ROC | December | QVW12 - Garrick from Ferguson onsite. Known issue with generator fault alarm. Confirmed this alarm is unprompted and does not prevent generator from running. Will be looked into further tomorrow as well | ROC General | 2025-12-11
ROC | December | Ethan Ullalkar signing out. | ROC General | 2025-12-11
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-11
ROC | December | Connor Smith signing in 0C Snowy | ROC General | 2025-12-10
ROC | December | Connor Smith signing in 0C Snowy | All Water System ROC General | 2025-12-10
ROC | December | VNETAG - Tower low level alarm. Checked site, suction side valve for the pump station VNPSAP is manual closed. Called Jordan B who is not aware of why the valve would be manual closed. No details in the log books. Placed valve in auto. Valve opened and pump activated. #consult | All Water System ROC General | 2025-12-10
ROC | December | BVPS- Disch Free Chlor Hi Alarm. Emailed Donald M. Can disregard as well as hihi if it comes in. | All Water System ROC General | 2025-12-10
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-10
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-10
ROC | December | MKRSEM- Called Toronto (Peter) and requested pumps off. | All Water System ROC General | 2025-12-11
ROC | December | Connor Smith signing out | All Water System ROC General | 2025-12-11
ROC | December | QVW12 - Drew from Ferguson Electric is finished on site | ROC General | 2025-12-11
ROC | December | KSTP - CO2 Adjusted pH LoLo alarm came in. Interlocked the low lifts. High lifts were interlocked due to a filter in a backwash. Called Patrick F. who will take a look 18:07 - Patrick called back to inform that there may be an issue with the analyzer. He will continue to monitor and directed to disregard the filter 2 Backwash failed as the low lifts are still interlocked and he has placed all high lifts in man/off for the time being. If the pH does not come back, he will attend site. 18:39 - Patrick called back to inform that the alarm cleared. Patrick informed he will leave the plant off for the night by leaving the hi lifts man/off #CONSULT | All Water System ROC General | 2025-12-11
ROC | December | VNPSCD - Pre injection Total chlorine hi alarm came in. Checked site. Levels came back down within 2 mins and alarm cleared. | All Water System ROC General | 2025-12-11
ROC | December | BLW3 - Rob from CPD on site. | ROC General | 2025-12-15
ROC | December | ANW23 - Property service leaving site | ROC General | 2025-12-12
ROC | December | STRS48 - Drew from Ferguson Electric leaving site. | ROC General | 2025-12-15
ROC | December | NBW2 - Parth P and Rick L leaving site and heading to NBW5 to work on chlorine analyzers. | All Water System ROC General | 2025-12-15
ROC | December | Adam Button signing in -10 Clear | ROC General | 2025-12-15
ROC | December | MTETNL - Arthur L working on the OIT. Arthur directed to disregard the historian heartbeat alarm. | All Water System ROC General | 2025-12-15
ROC | December | MAPS PD8 - Lee F on site for pump testing. Lee has requested that pump 1 and pump 3 be activated for testing followed by pump 4. Made changes to duty and activated the duty band. | All Water System ROC General | 2025-12-15
ROC | December | AURSBS - Activated Duty 1 | All Water System ROC General | 2025-12-15
ROC | December | EGSSSC - Dominic from Honeywell is on site 09:12 - Dominic is finished on site | ROC General | 2025-12-11
ROC | December | Angelica Chepiga signing in | ROC General | 2025-12-15
ROC | December | Christian Van Beek signing in. | ROC General | 2025-12-15
ROC | December | AUSSSR- Chinmay from CPD with contractors on site/troubleshooting equipment. Disregard alarms for the duration of the work. 08: 40 Chinmay from CPD with contractors leaving site. | ROC General | 2025-12-15
ROC | December | QVW34 - Alex B on site to complete a station check. Later Donald M and possible Ryan B will be on site to work on the outstanding chlorine leak detection system issue. Alex B requested a CMU5 for themself and Donal M. Created CMU5#W11515911 KSETWB - Phil D on site to complete work orders including chlorine leak detection test, chlorine analyzer maintenance, valve exercising, chemical system inspections and chlorine scrubber inspection. #CMU5 | All Water System ROC General | 2025-12-15
ROC | December | Ethan Ullalkar signing out. | ROC General | 2025-12-12
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-12
ROC | December | QVW12- Theodore from AB is on site | ROC General | 2025-12-10
ROC | December | RHAMF - Jamie from North American construction called again to troubleshoot the Makeup air unit. Jamie asked to clear the fail to start alarm. Cleared alarm and monitored activation, the alarm returned and Jamie mentioned that the VFD was not reading any current levels. Attempted to start the unit in manual mode but the unit would not transition to manual mode through SCADA. Jamie has no other options but to leave the alarm outstanding and continue investigations tomorrow. | ROC General | 2025-12-10
ROC | December | LSSS- John from property services is on site | ROC General | 2025-12-01
ROC | December | Christian Van Beek signing in. | ROC General | 2025-12-04
ROC | December | Christian Van Beek signing out. | ROC General | 2025-12-04
ROC | December | Ethan Ullalkar signing out. | ROC General | 2025-12-05
ROC | December | QVW12 - Christian from Ferguson Electric is on site responding to an alarm | ROC General | 2025-12-05
ROC | December | QVW12 - Christian from Ferguson Electric on site to complete sheet metal work on the generator exhaust system/ | ROC General | 2025-12-08
ROC | December | GWTPLL - Card reader replaced. Site unable to arm still. Terry will escalate further to security to inform of issue | ROC General | 2025-12-09
ROC | December | QVW12 - Theodore from ABPMC on site for fuel system replacement. Temporary generator is set up and on stand by. | ROC General | 2025-12-03
ROC | December | Adam Button signing out | ROC General | 2025-12-03
ROC | December | Ethan U signing in | ROC General | 2025-12-09
ROC | December | Ethan Ullalkar signing out. | ROC General | 2025-12-08
ROC | December | Connor Smith signing out | ROC General | 2025-12-03
ROC | December | STETTL - Lane from Stouffville Water will be flushing in Zone 2 today. | ROC General | 2025-12-02
ROC | December | Keswick - Derek from Aquazition flushing KSETDP - Mark from Process engineering, site orientation and measurements with contractors 10:33 - Mark finished at site. Contractor remains onsite but will follow up end of day | ROC General | 2025-12-08
ROC | December | SEOC Shaft 4 - Hameed from ETO Engineering on site for an inspection. 14:22 - SEOC - Hameed leaving site. 14:22 - BLSS - Ben Han leaving site. | ROC General | 2025-12-08
ROC | December | NMETDD - Samir from YorkNet leaving site. | ROC General | 2025-12-08
ROC | December | STPSTL - Christian from Ferguson Electric on site for pipe work. | ROC General | 2025-12-02
ROC | December | MARS, Courtney from Tobare is on site | ROC General | 2025-12-05
ROC | December | GWTP, Kevin from Magnum Fire is on site 14:19, Kevin is leaving site | ROC General | 2025-12-04
ROC | December | GWTP, Terry G from property services is leaving site | ROC General | 2025-12-04
ROC | December | Connor Smith signing in 0C Cloudy | ROC General | 2025-12-03
ROC | December | Carter Dunn Signing In, -6D/Clear | ROC General | 2025-12-02
ROC | December | YDOC - ETO engineering onsite | ROC General | 2025-12-08
ROC | December | KSETWB - Terry G finished at site | ROC General | 2025-12-08
ROC | December | Carter Dunn Signing In, -14D/Clear | ROC General | 2025-12-05
ROC | December | KSETDP, Jun ji from IAM is leaving site | ROC General | 2025-12-04
ROC | December | Connor Smith signing in -6C Snowy | ROC General | 2025-12-01
ROC | December | Adam Button signing in | ROC General | 2025-12-01
ROC | December | Christian Van Beek signing in. Weather: -6 and clear. | ROC General | 2025-12-03
ROC | December | SEOC OCF - Ben Han from property services on site to complete maintenance on a heater coil | ROC General | 2025-12-09
ROC | December | BLETNL - Wes from Town of Stouffville will be flushing in the Ballantrae water system today. | ROC General | 2025-12-09
ROC | December | JDSS, Christian from Ferguson Electric is on site | ROC General | 2025-12-01
ROC | December | KBSP - Drew from Ferguson onsite for epoxy work | ROC General | 2025-12-08
ROC | December | KBSP - Christian from Ferguson Electric on site to complete epoxy work. | ROC General | 2025-12-09
ROC | December | QVETQS - Terry onsite checking card reader | ROC General | 2025-12-09
ROC | December | Adeela Khan signing in | ROC General | 2025-12-05
ROC | December | Ethan Ullalkar signing out. | ROC General | 2025-12-09
ROC | December | NMETDD - Samir from Yorknet on site for fiber testing. | ROC General | 2025-12-08
ROC | December | Christian Van Beek signing out. | ROC General | 2025-12-24
ROC | December | NMSSBP - Patrick from Property services on site to complete a fire alarm test. | ROC General | 2025-12-19
ROC | December | Pesticon Pest control will be visiting the following sites today: NBW2, NBW3, NBW5, NBET, NBET27. | ROC General | 2025-12-18
ROC | December | KSTP- Gerrick from Ferguson offsite. | ROC General | 2025-12-22
ROC | December | QVW12 - Mark from Process Optimization group leaving site. | ROC General | 2025-12-23
ROC | December | MTW12 - Jeff from Keyshack leaving site. | ROC General | 2025-12-16
ROC | December | HMSS = Steve from York Regional Doors off site. | ROC General | 2025-12-16
ROC | December | QVW12, Garrick from Ferguson Electric is on site | ROC General | 2025-12-19
ROC | December | SHSP - Samir from Yorknet on site for fiber work. | ROC General | 2025-12-16
ROC | December | STRS48 - Drew from Ferguson Electric on site for patch work. | ROC General | 2025-12-18
ROC | December | NBSP - Jeff from Keyshack on site. | ROC General | 2025-12-23
ROC | December | Adam Button signing out | ROC General | 2025-12-21
ROC | December | Carter Dunn Signing Out | ROC General | 2025-12-20
ROC | December | QVW12- Christian Ferguson Electric onsite. | ROC General | 2025-12-17
ROC | December | Angelica Chepiga signing out | ROC General | 2025-12-24
ROC | December | MKETFA- Ahmed from YRP is done on site | ROC General | 2025-12-22
ROC | December | STRS48 - Drew from Ferguson Electric on site. STPSMR - Christian from Ferguson Electric leaving site. | ROC General | 2025-12-16
ROC | December | Connor Smith signing in 0C Snowy | ROC General | 2025-12-23
ROC | December | KSTP- Gerrick from Ferguson onsite. | ROC General | 2025-12-22
ROC | December | GWTP- Jeff from Property Services onsite testing fire alarms. | ROC General | 2025-12-22
ROC | December | KSSP- Franco Property Services onsite. | ROC General | 2025-12-22
ROC | December | Christian Van Beek signing out. | ROC General | 2025-12-28
ROC | December | Ethan Ullalkar signing in | ROC General | 2025-12-18
ROC | December | QVW12 - Christian from Ferguson finished at site | ROC General | 2025-12-17
ROC | December | Adeela khan signing out | ROC General | 2025-12-24
ROC | December | Town of Stouffville - Sean flushing zone 1 & 2 | ROC General | 2025-12-17
ROC | December | KBPS27 - Christian from AB finished at site | ROC General | 2025-12-17
ROC | December | Christian Van Beek signing in. Weather: 1 C and clear. | ROC General | 2025-12-18
ROC | December | Ethan Ullalkar signing out. | ROC General | 2025-12-27
ROC | December | SHSP- Andrew from Ferguson onsite. | ROC General | 2025-12-23
ROC | December | Christian Van Beek signing out. | ROC General | 2025-12-19
ROC | December | Connor Smith signing in | ROC General | 2025-12-16
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-15
ROC | December | BLSS- Chris from Property Services onsite for fire test. | ROC General | 2025-12-16
ROC | December | Ethan Ullalkar signing out. | ROC General | 2025-12-18
ROC | December | AUW14- Lee F req P1 be placed in auto for testing placed P1 in auto | All Water System ROC General | 2025-12-12
ROC | December | NMETIB, Deactivated D1 NMVCIB, Placed flow back to 80L/sec NMVCBP, Placed flow back to 40L/sec | All Water System ROC General | 2025-12-12
ROC | December | HLW2, Intrusion alarm, FMC called, notified them to contact security RHMCMD, Placed valve man/open RHRSTR, Deactivated D1 | All Water System ROC General | 2025-12-12
ROC | December | RHRSTR, Activated D1 | All Water System ROC General | 2025-12-13
ROC | December | BVPS- Rick L on site to work on pump discharge PITs | All Water System ROC General | 2025-12-10
ROC | December | MKRSEM- Called Toronto (Peter) and requested pumps on. | All Water System ROC General | 2025-12-10
ROC | December | Adam Button signing in MAPS PD7- Found P4 OOS due to hi pressure switch info alarm. Reset alarm pump back in service | All Water System ROC General | 2025-12-11
ROC | December | STPSTL - Artour L. is on site and will be testing the diesel fuel tank LIT 11:00 - Artour L. called back to inform that he is finished on site | All Water System ROC General | 2025-12-11
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-10
ROC | December | 18:00- Connor Smith signing in -8C Clear 18:04- Adam Button signing in 18:07- SHETCS- Hypo Pump 1 Failed to Start Alarm came in. Reset alarm. Pump running okay. 18:15- Adam Button signing out 18:25 NMVCBA- Changed from 40L/s to 60L/s 19:03- STW12- Placed in auto STW3- Placed in auto 20:00- YWS + NYWS Normal 20:55- EZMax Back online | All Water System ROC General | 2025-12-13
ROC | December | NMETIB- Deactivated duty | All Water System ROC General | 2025-12-10
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-11
ROC | December | STW12- Placed wells 1,2 in auto STW3- Placed well 3 in auto | All Water System ROC General | 2025-12-11
ROC | December | SHTP- Filter 2 Turbidity Hi Alarm. Backwash just completed. Reset alarm as per SCADA Report | All Water System ROC General | 2025-12-11
ROC | December | MKRSEM- Free Cl2 fault res fault alarm came in. Jack P on site sampling will be able to reset when done sampling MTW12- Placed well 2 in man/off for generator load test | All Water System ROC General | 2025-12-10
ROC | December | HLW1 Combined Cl2 lo alarm came in on well start up. Trends recovered after 6 mins alarm cleared | All Water System ROC General | 2025-12-10
ROC | December | YWS + NYWS NORMAL | All Water System ROC General | 2025-12-14
ROC | December | NMETIB - Deactivated Duty 1. | All Water System ROC General | 2025-12-14
ROC | December | NBW2- During SCADA check noticed that effluent analyzer free Cl2 reading higher than influent analyzer consistently during 2 last runs. Placed in man/off and emailed West Water team | All Water System ROC General | 2025-12-14
ROC | December | AUW14- Jerry Z on site to test Cl2 leak test, and clean turbidity analyzers and Cl2 analyzers | All Water System ROC General | 2025-12-12
ROC | December | AUPSRR- Will M on site to work on chem scan | All Water System ROC General | 2025-12-12
ROC | December | NMW15 - Talha H. called to inform that he would like to reboot the well. Duty is currently active and well is running. Duty is close to deactivate. Placed well man/off as the heartbeat would interlock the well 12:12 - Talha called back to inform that he is finished with the reboot. Alarm has been cleared. Duty is no longer active and well is placed back to auto | All Water System ROC General | 2025-12-11
ROC | December | MARS - Power failure alarm. Joe W on site for sampling. Generator running to provide power to site. MAPS PD8 - All pumps have faulted on a VFD not ready alarm due to the power failure. Joe W on site and can reset the VFD faults. MAPS PD7 - Pump 1 and pump 3 not ready alarms. Alarms were triggered by the power failure. Pump 2 and pump 4 have no alarms and have rotated into duty 1. Those pumps will be available once the power fail restart inhibit clears. Joe W will reset the alarms on pump 1 and pump 3. | All Water System ROC General | 2025-12-10
ROC | December | YWS + NYWS NORMAL | All Water System ROC General | 2025-12-14
ROC | December | QVW34- Donald M Alex B and Ben H on site for ejector replacement. Will be triggering CL2 leak and emergency closure system. Will notify ROC when done on site | All Water System ROC General | 2025-12-10
ROC | December | VNRSKS - Site power failure alarm and sump pump overload alarms. Checked site, no generator on site. Able to clear alarms. | All Water System ROC General | 2025-12-10
ROC | December | HLETYS - Ammonia pumps 1&2 failed to start alarms. Increased flow control valve setpoint from 40 to 42l/s as per Jordan B. Alarms cleared. # Consult | All Water System ROC General | 2025-12-14
ROC | December | AUW14 - Lee F working on pump 1. Request to run well in auto. Unable to clear multilin trip. Rotate pump 1 & 3 in duty 1 to prepare and test pump 1. Lee F will try and clear multilin alarm | All Water System ROC General | 2025-12-12
ROC | December | STPSMR- Garrick from Ferguson Electric is on site performing generator load test. No alarms expected OPs on site | All Water System ROC General | 2025-12-12
ROC | December | MKETFA - Jackie S. is on site and will be completing an actuated valve exercise and inspection. 09:38 - Called Toronto Water (Paul) and requested the pump in manual. 09:45 - Jackie called to inform that she is finished with the valve exercising and Toronto can place their pump back to auto. Jackie also informed that she will be testing the hi/low water level, low temp alarm, and will be completing chlorine analyzer maintenance. 09:46 - Called Toronto Water (Mehdi) and requested to place the pump back to auto | All Water System ROC General | 2025-12-11
ROC | December | GWTP- Patrick F on site for GAC 4 backwash | All Water System ROC General | 2025-12-12
ROC | December | QVW12 - Alex B onsite running generator | All Water System ROC General | 2025-12-12
ROC | December | GWTP - GAC1,3,4 High level alarms - Notified Patrick F , he is on site , will check. Gas chlorinators 6/6 Hi Vacuum alarms, OP changing chlorine toners.Patrick F requested disregard alarms. | All Water System ROC General | 2025-12-15
ROC | December | Adam Button signing in | All Water System ROC General | 2025-12-10
ROC | December | MAPS PD7- P3 discharge valve 1 uncommanded close P3 uncommand stop. reset alarms | All Water System ROC General | 2025-12-12
ROC | December | MARS- Called David D for an update on power issues. He is onsite waiting for Alectra. CONSULT | All Water System ROC General | 2025-12-10
ROC | December | MAPS/JFRS- Initiated Maple to Jefferson Feed. | All Water System ROC General | 2025-12-14
ROC | December | RHMCMD- Placed back into auto | All Water System ROC General | 2025-12-14
ROC | December | SHETCS- Hypo P1 uncoamnded stop alarm came in. Reset alarm | All Water System ROC General | 2025-12-14
ROC | December | MTW3- Silicate P2 speed OOR alarm came in. Pump not running and duty not active cleared alarm | All Water System ROC General | 2025-12-14
ROC | December | MKRSEM- Called Metro spoke with Brett to stop pumping to reservoir | All Water System ROC General | 2025-12-15
ROC | December | Angelica Chepiga signing in, weather -12C | All Water System ROC General | 2025-12-14
ROC | December | ANVCPL- Change flow setpoint from 100L/s to 110L/s to help increase flow to central and central east Newmarket systems as NMETHW is slowly draining with duty active | All Water System ROC General | 2025-12-14
ROC | December | KSTKWP- Chlorinator 1 failed to close alarm came in. Chlorinator is currently closed reset alarm | All Water System ROC General | 2025-12-14
ROC | December | QVW34 - Chlorine Room Gas Leak Alarm came in. Interlocked the wells. Called Ryan B. who will take a look soon | All Water System ROC General | 2025-12-11
ROC | December | JFPS - Lee F finished and leaving site. | All Water System ROC General | 2025-12-10
ROC | December | AUW14- Lee F on site to replace solenoid on waste flow valve for P1. P1 man/off AUETAD- Donald M on site working on Cl2 analyzers and will be testing building temp alarm | All Water System ROC General | 2025-12-12
ROC | December | QVW34- Cl2 leak alarm and emergency closure active. Called Donald M. No longer on site. Notified Ryan B. Wells will be offline for the weekend unless needed. Placed wells 3 4 in man/off | All Water System ROC General | 2025-12-12
ROC | December | NMVCBA- Changed flow setpoint from 40L/s to 80L/s NMVCIB- Changed flow setpoint from 80L/s to 40L/s | All Water System ROC General | 2025-12-12
ROC | December | YWS+NYWS normal | All Water System ROC General | 2025-12-14
ROC | December | RHRSTR- Deactivated D1 | All Water System ROC General | 2025-12-15
ROC | December | Linear Operations System - Dwayne L informed of a PRV chamber that has a leak. Dwayne has dispatched Rob P, Gary P, Matt H, and Harsh P to attend site and requested a CMU5. Created CMU5#W11515929 #CMU5 | All Water System ROC General | 2025-12-15
ROC | December | Adam Button signing out | All Water System ROC General | 2025-12-10
ROC | December | QVW12 - Influent free chlorine hihi alarm. Checked site, well recently activated. Trending shows a spike of the influent free chlorine reading which returned to normal range within one reading interval. Reset alarm. | All Water System ROC General | 2025-12-10
ROC | December | BLW12 - Joe M called to inform that the wells will be manual off until approximately 14:00 today. Joe will place the wells in auto mode once the work is complete. | All Water System ROC General | 2025-12-10
ROC | December | NMTKKC- Outlet total Cl2 lolo alarm came in residual never dropped below lo or lolo setpoint. Cleared alarm | All Water System ROC General | 2025-12-14
ROC | December | GWTP - Train 8 Transmembrane Pressure Lo alarm came in. Value turned normal and alarm cleared | All Water System ROC General | 2025-12-11
ROC | December | HLETYS - Post injection combined chlorine hi alarm. Increased hypo pump 1 max flow from 180 to 185. | All Water System ROC General | 2025-12-12
ROC | December | AUW14- Building flood alarm came in. Notified Lee F who will investigate on site 11:05- AUW14- Lee F called back no flood on site will try to clear | All Water System ROC General | 2025-12-12
ROC | December | ARPS- Total ammonia fault alarm came in. Residual dropped back into normal range within 2 mins alarms cleared | All Water System ROC General | 2025-12-15
ROC | December | MKRSEM- Called Metro spoke with Medhi to start two pumps to fill reservoir | All Water System ROC General | 2025-12-16
ROC | December | Ethan U signing in | ROC General | 2025-12-12
ROC | December | Christian Van Beek signing out. | ROC General | 2025-12-12
ROC | December | Adam Button signing in -14 clear | ROC General | 2025-12-12
ROC | December | NBW3- Station turbidity fault alarm came in. Known issue with flow to analyzer trends look okay and within normal range. Able to clear alarm | All Water System ROC General | 2025-12-12
ROC | December | VNETFD- Deactivated D1 to help tower cycle better | All Water System ROC General | 2025-12-12
ROC | December | STETTL/STETBR- Andrew from OWCA flushing in zone 1/2 | All Water System ROC General | 2025-12-12
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-12
ROC | December | Ethan U signing in | All Water System ROC General | 2025-12-12
ROC | December | Adam Button signing in -14 clear | All Water System ROC General | 2025-12-12
ROC | December | NMW136- Influent free CL2 lo alarm came in. Trends recovered after 3 mins alarm cleared | All Water System ROC General | 2025-12-12
ROC | December | STW12 / STW3 - Activated STW1 and STW3 while STETBR fills. | All Water System ROC General | 2025-12-12
ROC | December | STETBR- Comm loss on site alarm reset as acknowledged BLETNL- Comm loss on site alarm reset as acknowledged BLW3- BLW3- BLETNL comm alarm came in trends okay reset alarm | All Water System ROC General | 2025-12-12
ROC | December | Carter D signing in, -1D/Clear | ROC General | 2025-12-01
ROC | December | Connor Smith signing in -6C Clear | ROC General | 2025-12-02
ROC | December | Christian Van Beek signing out | ROC General | 2025-12-02
ROC | December | Adam Button signing in | ROC General | 2025-12-22
ROC | December | Connor Smith signing in -7C Clear | ROC General | 2025-12-22
ROC | December | Carter Dunn Signing Out | ROC General | 2025-12-22
ROC | December | Angelica Chepiga signing in, weather -7C | ROC General | 2025-12-25
ROC | December | Ethan U signing in Weather -8. | ROC General | 2025-12-26
ROC | December | Angelica Chepiga signing out | ROC General | 2025-12-26
ROC | December | Ethan Ullalkar signing out. | ROC General | 2025-12-17
ROC | December | STRS48 - Drew from Ferguson electric leaving site. | ROC General | 2025-12-17
ROC | December | Connor Smith signing out | ROC General | 2025-12-17
ROC | December | Angelica Chepiga signing in, weather +2C | ROC General | 2025-12-17
ROC | December | YWS+NYWS normal | All Water System ROC General | 2025-12-16
ROC | December | SHETCS- Outlet flow hi alarm came in. Quickly recovered and returned to normal flow. Cleared alarm 02:24- SHETCS- Outlet flow hi alarm came in again but quickly recovered. Will continue to monitor and email West Water OPs of potential overnight flushing and or water theft | All Water System ROC General | 2025-12-16
ROC | December | RHRSTR- Deactivated D1 at 83% | All Water System ROC General | 2025-12-16
ROC | December | RHMCMD- Placed in man open 100% | All Water System ROC General | 2025-12-16
ROC | December | SHTP- Well 2 uncommanded start alarm came in. Well not active reset alarm AUPSRR- Post injection free Cl2 hi alarm came in. Residual recovered quickly and cleared alarm | All Water System ROC General | 2025-12-16
ROC | December | STETBR- Tower level hi alarm came in. STW12/STW3- Placed wells back in auto as per interim | All Water System ROC General | 2025-12-16
ROC | December | Richmond Hill - Dwayne L informed RH had experienced a water main break on Yonge & N Eglin Mills. No current impact to our sites | All Water System ROC General | 2025-12-11
ROC | December | NBW3 - Influent Free Chlorine LoLo switch alarm came in. Checked site. Well is interlocked. Spoke to Tim H. who directed to reset alarms if the influent levels go back to optimal range. Tim also directed to disregard station turbidity fault | All Water System ROC General | 2025-12-11
ROC | December | STRS48 - Water Resources (2893384752) is on site and requested the hi lift pump be running. Placed hi lift pump man/on | All Water System ROC General | 2025-12-11
ROC | December | MTW12 - Sean P on site to complete a generator oil change and test run. | All Water System ROC General | 2025-12-10
ROC | December | KCETDS - Jordan B. called to inform that he is on site and will be cleaning the chlorine analyzers, testing the low temp alarm, and will be testing the eyewash. Directed to disregard these alarms until work is complete | All Water System ROC General | 2025-12-11
ROC | December | Adam Button signing out | All Water System ROC General | 2025-12-11
ROC | December | NMW15 - Influent Free Chlorine Hi alarm came in. Level came back to optimal range and alarm cleared | All Water System ROC General | 2025-12-11
ROC | December | AUW14 - Well pump 1 multilin trip and fail to start alarms. Checked site, well was running when alarms triggered. Placed well manual/off, rotated duty 1 to pump 2 and sent email to area ops. | All Water System ROC General | 2025-12-11
ROC | December | NMETHW - Activate duty 1 while NMETIB drains. | All Water System ROC General | 2025-12-11
ROC | December | MTETNL- Joe M req D1 activated for sampling. Activated D1 MTW3- VFD by pass alarm came in. Notified Joe M. Directed to leave well in auto and running. Will investigate later today NBW5 - Influent free lo alarm came in on well start up. Trends recovered after 3 mins alarm cleared | All Water System ROC General | 2025-12-10
ROC | December | MKRSEM - Low level alarm. Called Toronto Water (Peter) and requested they activate two pumps to push flow to MKRSEM. | All Water System ROC General | 2025-12-11
ROC | December | STW12- Placed well 2 back into auto STW3- Placed well 3 back into auto | All Water System ROC General | 2025-12-01
ROC | December | RHMCMD- Placed valve in manual RHRSTR- Deactivated duty | All Water System ROC General | 2025-12-02
ROC | December | NMW12, Jason G on site, Cleaning the Cl2 analyzer and the turbidity analyzers | All Water System ROC General | 2025-12-02
ROC | December | Hub Server 3/4 Reset, Kingsley M will be resetting the hub 3/4 server later today | All Water System ROC General | 2025-12-01
ROC | December | NMETHW - Deactivated duty 1 while NMETIB fills. | All Water System ROC General | 2025-12-02
ROC | December | SHETCS - Hypo pump 1 fail to start alarm. Checked site, duty rotated to hypo pump 2. Cleared alarm. | All Water System ROC General | 2025-12-03
ROC | December | NBW3, Influent Free Cl2 hihi, adjusted cl2 1 dosing factor from 60 to 58% | All Water System ROC General | 2025-12-01
ROC | December | GWTP- Wash water Cl2 residual hi alarm came in. Notified Patrick F. Patrick F just cleaned analyzer and will verify if it is reading correctly | All Water System ROC General | 2025-12-03
ROC | December | NMTKKC, Rotated Chemical Reformation pumps so pump 1 is in D1 for Joe D | All Water System ROC General | 2025-12-01
ROC | December | Hub 3 Server Reset, Kingsley M resetting hub 3 server | All Water System ROC General | 2025-12-01
ROC | December | AUPSWS - Lee F on site to grease pumps. Lee requested that pump 4 be placed manual/on. Lee will call when he wishes to swap pumps. | All Water System ROC General | 2025-12-02
ROC | December | KCETDS - Outlet Total Chlorine LoLo alarm came in. Checked site. Trends indicate a dip in trends. Total chlorine recovered in 5 mins. Alarm cleared | All Water System ROC General | 2025-12-05
ROC | December | EGMCRW - Dan B on site to complete work on a pressure transmitter. | All Water System ROC General | 2025-12-04
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-03
ROC | December | MARS- Cell1 (North) Lvl Hi Alarm RHMCMD- Placed valve in manual RHRSTR- Deactivated duty | All Water System ROC General | 2025-12-04
ROC | December | NVW12 and QVW12 - Talha H rebooting OIT and directed to disregard the historian heartbeat alarms. | All Water System ROC General | 2025-12-03
ROC | December | BLW12 - Joe M. is on site with contractors to get the wells back up and running. Directed to disregard any alarms that come in until work is complete | All Water System ROC General | 2025-12-06
ROC | December | YWS + NYWS Normal Adeela Khan signing out | All Water System ROC General | 2025-12-06
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-01
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-04
ROC | December | MARS - Cell 1 Lvl Hi alarm came in RHMCMD - Placed in manual RHRSTR - Deactivated duty | All Water System ROC General | 2025-12-01
ROC | December | YWS + NYWS normal | All Water System ROC General | 2025-12-01
ROC | December | AUVCBS, Placed valve back to auto. Redempto B finished working on the analyzers at AURSBS | All Water System ROC General | 2025-12-01
ROC | December | NMW12- Turbidity exceeding hi alarm. No alarm outstanding at time. Same issue came in on day shift. Rotated from silicate P1 to P2 and disable all stop duty rotation emailed Central water team | All Water System ROC General | 2025-12-05
ROC | December | NMETHW- Donald M was able to get the heat trace to clear ice. LIT reading normally. Will continue to monitor level and revert changes made. AURSBS- Post injection total Cl2 hi alarm came in. Trends look elevated notified Donald M. Will check SCADA. 20:44- AURSBS- Donald M heading to site created CMU5 W11491869 #CMU5 #consult | All Water System ROC General | 2025-12-05
ROC | December | VNPS CD - Rick L finished and leaving site. | All Water System ROC General | 2025-12-04
ROC | December | NBW3, Well 3 placed man/on by Joe W, he will be freshening up the line | All Water System ROC General | 2025-12-04
ROC | December | BVPS- Placed P2/4 in man/off. once inhibit cleared placed P1-4 in auto | All Water System ROC General | 2025-12-03
ROC | December | GWTP- ZW1 memb tank level lo alarm came in. Cleared upon acknowledgment level okay | All Water System ROC General | 2025-12-06
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-07
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-07
ROC | December | HLW1 - Benson S on site to complete work orders including a flow valve exercise, chlorine scrubber inspection, chlorine leak alarm test, Chlorin and turbidity analyzer maintenance, JHSC checks and chemical system inspections. AURSBS - WIll M on site to complete a chlorine leak detection test and silicate containment alarm test. | All Water System ROC General | 2025-12-04
ROC | December | Adam Button signing in -2 clear | All Water System ROC General | 2025-12-05
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-06
ROC | December | NMVCIB- Changed flow setpoint from 40L/s to 80L/s NMVCHW- Changed flow setpoint from 80L/s to 40L/s AURSBS- Post Injection total Cl2 hihi alarm came in Chem system did not interlock placed chemical system in man/off notified Donald M. Donald M dropped target post injection combined Cl2 to 2.9mg/L and placed chem system back online. BLW12- Station turbidity fault came in. Cannot reset placed wells in man/off and emailed East water team about outstanding alarm | All Water System ROC General | 2025-12-07
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-06
ROC | December | KCPSDS - Activated duty 1 in preparation for interim | All Water System ROC General | 2025-12-08
ROC | December | SHTP - Rick L, Parth P and REdempto B leaving site | All Water System ROC General | 2025-12-09
ROC | December | VNP7 - Place pumps back in man/off RHPSPA - Noticed pumps 2-4 are in duty 1. Rotate pump 3 into duty 4. Called Jack P for update with site. Chris S will be attending to replace PAC card and Dan B onsite as well GWTP - Patrick F & Phil D onsite working on GAC & Turbidity | All Water System ROC General | 2025-12-09
ROC | December | MAPS PD8 - Kyle R finished. placed pumps in auto mode. | All Water System ROC General | 2025-12-02
ROC | December | YWS+NYWS normal | All Water System ROC General | 2025-12-06
ROC | December | Christian Van Beek signing in. Weather: -9 and clear. | All Water System ROC General | 2025-12-09
ROC | December | SHTP/SHETCS - Activated duty 1 for hi lifts to help fill tower for interim procedure | All Water System ROC General | 2025-12-09
ROC | December | Wrong logbook entry | All Water System ROC General | 2025-12-09
ROC | December | STW3 - Historian heartbeat. Locked out well. Able to clear alarm and pump came back on | All Water System ROC General | 2025-12-09
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-09
ROC | December | KSETWB - Artour L. is on site to check a fibre cable. 12:54 - Artour is finished on site | All Water System ROC General | 2025-12-05
ROC | December | ANVCPL- Placed valve in man 40L/s to help slow NMETHW drain | All Water System ROC General | 2025-12-05
ROC | December | YWS+NYWS normal | All Water System ROC General | 2025-12-05
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-06
ROC | December | ARPS- Total Ammonia fault alarm came in. Trends recovered after 3 mins alarm cleared | All Water System ROC General | 2025-12-06
ROC | December | Hub Server 1 Reset, Kingsley M will be resetting servers 1 and 2 today. Hub server 1 will be the first server to be reset. Activated D1 at NBET to get the tower full so the reset can be smooth | All Water System ROC General | 2025-12-02
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-07
ROC | December | MARS - Hi level came in. Activated duty 1 at VNRSKS 03:42 - Activated AURSBS Duty 1 | All Water System ROC General | 2025-12-08
ROC | December | NMETIB- Deactivated duty. NMVCBA- reverted back to 40L/s NMVCIB- reverted back to 80L/s | All Water System ROC General | 2025-12-04
ROC | December | MTW12 - Hypo Pump 2 Failed to Start alarm came in. Checked site. Hypo Pump 1 rotated to duty 1 and is running. Reset alarm. Will monitor | All Water System ROC General | 2025-12-06
ROC | December | Adam Button signing in -5 clear | All Water System ROC General | 2025-12-06
ROC | December | NBW3- Influent free Cl2 hi alarm came in on well start up. Trends recovered after 3 mins alarm cleared | All Water System ROC General | 2025-12-06
ROC | December | STETBR- Tower level lo alarm came in. STW12- Placed P1 in man/on as per interim STW3- Placed P3 in man/on as per interim | All Water System ROC General | 2025-12-06
ROC | December | RHRSTR - Adjusted duty 1 setpoints from 65-85% to 70-90% as per the interim procedure. Also adjusted the lo/lolo level alarms from 58/45% to 60/50% | All Water System ROC General | 2025-12-08
ROC | December | JFPS - Jordan B on site to complete a generator test run. | All Water System ROC General | 2025-12-09
ROC | December | AUW57 - Donald M on site. | All Water System ROC General | 2025-12-08
ROC | December | NMW12 - Station Turbidity Alarm came in. Rotated silicate pumps so that Silicate pump 2 is in duty 1. Will continue to monitor 08:39 - Level came back to optimal range and alarm cleared | All Water System ROC General | 2025-12-05
ROC | December | ARPS, Airport Rd Total Ammonia lolo alarm, contacted Bineesh from OCWA, informed the ROC that the analyzers are OOS and there is an operator taking a grab every 30 minutes. | All Water System ROC General | 2025-12-01
ROC | December | SHTP- Hypo Pump 1 Failed to Start. Hypo Pump 2 running in duty 1. Cleared alarm. | All Water System ROC General | 2025-12-01
ROC | December | HLETYS, Eric S is finished on site | All Water System ROC General | 2025-12-05
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-02
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-02
ROC | December | Christian Van Beek signing out. | All Water System ROC General | 2025-12-04
ROC | December | JFRS- Deactivated D1 /2 | All Water System ROC General | 2025-12-07
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-08
ROC | December | YWS + NYWS normal | All Water System ROC General | 2025-12-08
ROC | December | BLW3 - Joe M called to inform that electrical work will be taking place today. Joe M directed to place the well manual/off and disregard associated alarms until the work is completed. | All Water System ROC General | 2025-12-09
ROC | December | STETBR - Tower Level Hi alarm came in. Placed STW1 and STW3 back to auto, as per interim | All Water System ROC General | 2025-12-06
ROC | December | YDSS + YNSS Normal | All Water System ROC General | 2025-12-09
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-09
ROC | December | RHMCMD - Placed valve man/on | All Water System ROC General | 2025-12-08
ROC | December | Network Update - Called back John D confirming we are okay to put system back to normal operations QVW12, QVW34, NMW12, NMW13, NMW15, AUPSOH pumps 3 & 4, place all back into auto NMVCIB - Setpoint change back to 40L/s NMVCBA - Setpoint change back to 80L/s | All Water System ROC General | 2025-12-09
ROC | December | HLPSYS- Sean P on site to disconnect Generator to replaced battery cables | All Water System ROC General | 2025-12-01
ROC | December | STPSMR - Noticed only 1 pumps running on duty 1. During day only 1 pumps was running on duty but with evening demand tower still draining. Informed Stephen B of issue, he will followup with Dan Z. 17:55 - Change pump 1 to duty 1 STW12 - Both wells in duty 1. Well 1 sporadic flow. Informed Stephen B. Placed well 2 duty 2. STW3 - Influent free chlorine hi. Monitored and reading dropped within range Consult | All Water System ROC General | 2025-12-08
ROC | December | RHRSPA - Jack P onsite running generator on load | All Water System ROC General | 2025-12-09
ROC | December | NMTKKC - Joe D hot water flush on chemscan. Disregard offline alarm, chem pumps are man/off for work | All Water System ROC General | 2025-12-09
ROC | December | MKRSEM - Reservoir 1 Level Lo alarm came in. Called Toronto Water (Zoran) and requested 2 pumps on | All Water System ROC General | 2025-12-08
ROC | December | RHPSPA - Jack P onsite, issue with source 2 power returning back to hydro. Jack P followed up electrical Sean P/Tyler Z. Will have someone attend site to fix. Known issue that occurred before. RHVCEM - man/open to 25%, followed by further increase to 50%. Place in combined mode. VNP7 - Place pump 1 & 3 auto | All Water System ROC General | 2025-12-09
ROC | December | QVW12 - Lee F called and would like to grease well pump 1. Duty is very close to starting, activated duty early so Lee can grease the well pump. 14:09 - QVW12 - Lee F finished and leaving site. | All Water System ROC General | 2025-12-09
ROC | December | MKRSEM- Called Toronto (Mehdi) and requested pumps off. | All Water System ROC General | 2025-12-02
ROC | December | STPSTL - Place pumps 1 & 2 back in auto for Stephen B 17:10 - Leaving site | All Water System ROC General | 2025-12-09
ROC | December | MMW1- Well 8 Level Hi Alarm, Well 13 Level Hi Alarm. All dewatering wells showing manual off. Likely due to power blip. Notified Rob P. Requested to place wells 13 and 8 in manual on. Cleared alarms. | All Water System ROC General | 2025-12-09
ROC | December | GWTP- LLP4 hydraulic valve failed to open reset as per shift report | All Water System ROC General | 2025-12-03
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-10
ROC | December | STPSTL - Pump 1 and pump 2 fault alarm. Checked site, duty is not active but is very close to starting. Trending shows the pumps did not activate and then fault. Unable to clear alarms. Called Stephen B who will investigate 15:45 - STPSTL - Pump 1 and 2 fault alarms. Stephen B attending site, created CMU5#W11500610. #CMU5 | All Water System ROC General | 2025-12-09
ROC | December | AUW14 - Ricardo L. is on site for a chlorinator rebuild. Placed all 4 wells man/off for the duration of work 15:31 - Ricardo L. is finished on site | All Water System ROC General | 2025-12-05
ROC | December | NMVCIB - Change setpoint from 80 to 40L/s NMVCBA - CHange setpoint from 40 to 80L/ QVW34 - Man/start well 3 NMETIB - Activate duty 1. Steps done for planned interim of network update | All Water System ROC General | 2025-12-09
ROC | December | STETBR - Tower Level Hi alarm came in. Placed STW2 and STW3 back to auto, as per interim | All Water System ROC General | 2025-12-09
ROC | December | Yonge and North Lake - Shane from YR dispatch called to ask if anyone has called the ROC about any issues at Yonge st and North Lake road in Richmond Hill. YRP called Shane to report a possible mainbreak. No one has reached out to the ROC and no pressure or flow issues noted in Richmond hill at this time. Shane will send an operator to investigate and give the ROC a call back | All Water System ROC General | 2025-12-09
ROC | December | NMW136 - Parth P called to inform he is finished with the work at NMW136 and has requested that NMW13 be activated so they can monitor the activation and operation of the well. Activated NMW13 in manual mode. | All Water System ROC General | 2025-12-09
ROC | December | STW2/3, Placed wells 2/3 man/on 17:37, STW12, When watching the wells run, ROC noticed there was no flow coming from the well, Well pump was running at 100% but no flow, FCV was failing to open. Placed pump to D2 and placed man/off. Placed STW1 in D1 and it started up however no flow has been coming out of well 1 as the FCV1 has failed to open as well. Both valves aren't opening. Placed both pumps man/off then checked STETTL to see if we can fill without both wells. STETTL is currently draining while D1 is active. Checked STETBR, Tower just started its D1 cycle. Contacted Stephen B, notified him that the valves at STW12 aren't opening. He will head to site. Stephen B directed to deactivate duty at STETBR and place STPSTL pumps 1/2 man/off until the issue is resolved at STW12. CMU5: W11488860 | All Water System ROC General | 2025-12-04
ROC | December | STW12, Travis W running the generator on site and doing health and safety alarms | All Water System ROC General | 2025-12-04
ROC | December | Stouffille DWS - Corey T. from Town of Stouffville will be flushing in zone 2 for the duration of the day, starting in the east | All Water System ROC General | 2025-12-05
ROC | December | NMETHW- Donald M on site heat trace not reading correctly. LIT frozen Estimating tower at 67% with around 15L/s leaving tower. Tower LIT in calibration mode placed QVW12/QVW34 in man/off as precaution in case Duty activates. Donald M calling Brent St C (OCO electrical) to troubleshoot issues. YWS+NYWS normal | All Water System ROC General | 2025-12-05
ROC | December | Adeela Khan signing in. Weather: -2 and cloudy | All Water System ROC General | 2025-12-06
ROC | December | AURSBS - Post Injection Free Chlorine alarm came in. Free chlorine levels have been running higher. Called Donald M. who informed that this is a known issue and that the high can be disregarded but call for the Post Injection Free Chlorine HiHi. #CONSULT | All Water System ROC General | 2025-12-06
ROC | December | NBW3, Influent Free Cl2 lolo alarm, Well just started up but the influent dipped down and interlocked the well, will continue to monitor, after 15 minutes, will reset alarm. If residual dips again, will notify operator | All Water System ROC General | 2025-12-01
ROC | December | Connor Smith signing in -2C snow | All Water System ROC General | 2025-12-09
ROC | December | KLW34 - Jake M on site to complete work orders including a generator test, chlorine leak detection test, chemical system maintenance. KLPSWL - Jake M on site and will be completing a PRV inspection and a low temperature test. | All Water System ROC General | 2025-12-02
ROC | December | NMPSKC - Joe D on site for pump testing. Joe will run each pump for approximately ten minutes. | All Water System ROC General | 2025-12-02
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-08
ROC | December | HLW2 - Combined chlorine lolo alarm. Checked site, well is currently OOS and offline for maintenance. No water being directed to users. Trending shows a sudden dip of the combined chlorine reading which recovered within two reading intervals. Reset alarm. | All Water System ROC General | 2025-12-03
ROC | December | HLW2 - Combined Chlorine Lo and Treated Chlorine Lo alarms came in. Well is local/off and water is not being directed to users | All Water System ROC General | 2025-12-06
ROC | December | BLETNL - Kinglsey M rebooting OIT. | All Water System ROC General | 2025-12-09
ROC | December | NBW3 - Tim H heading to site. Running well in manual. Removing suction line and tank. drain hypo tank and replacing liner NBET/NBET27- Tim H will be running generator as well testing temp alarms as well analyzers ANW23 - Activate duty 1 to fill res | All Water System ROC General | 2025-12-09
ROC | December | MTW3 - Historian Heartbeat alarm came in. Called Chris S. who will take a look | All Water System ROC General | 2025-12-05
ROC | December | BLW3 - Sean P on site to complete electrical work. Sean will be disconnecting the site from the hydro power. Well is already manual/off. | All Water System ROC General | 2025-12-09
ROC | December | MKRSEM - Toronto Water (Mehdi) called and asked if they could activate one pump to push flow to MKRSEM for 45 minutes after 16:00 today. Granted permission. | All Water System ROC General | 2025-12-02
ROC | December | AUW57 - well pump 5 emergency stop alarm. Jerry Z onsite placing well OOS for maintenance. | All Water System ROC General | 2025-12-03
ROC | December | RHVCEM - Put back to 15% | All Water System ROC General | 2025-12-09
ROC | December | MKRSEM - Low level alarm. Called Toronto Water (Zoran) to activate two pumps. AURSBS - Post injection free chlorine hihi. Donald M requested a CMU5 to attend site. Created CMU5#W11484598 #CMU5 | All Water System ROC General | 2025-12-03
ROC | December | KSTP, Donald M on site, working on the Cl2 system/silicate system/filters and testing the Cl2 leak alarm | All Water System ROC General | 2025-12-04
ROC | December | KSTP - Rick L & Parth P onsite CL2 work | All Water System ROC General | 2025-12-08
ROC | December | GWTP- ZW8 recover exceed recovery. ZW3 is off and ZW6 in backwash. Notified Stephen B. Directed to disregard alarm is it should go into back wash once other train has completed its backwash cycle. Stephen B also directed to place ZW3 online and if any issues with a single train come up to leave it outstanding for tomorrow as long as all other trains are not in alarm and are available. AURSBS- Activated D1 at 56% #consult | All Water System ROC General | 2025-12-06
ROC | December | QVW34- Treated total Cl2 lo alarm came in. Trends dropped for 3 mins and recovered. Alarms cleared wells are man/off no water directed to users | All Water System ROC General | 2025-12-06
ROC | December | SHETCS- Hypo pump 1 failed to start alarm came in ack and reset alarm | All Water System ROC General | 2025-12-06
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-06
ROC | December | TMC269 - Pressure Hi alarm came in. Monitored for 5 minutes. Called Toronto Water (Zoran) who informed he was filling a tank in their system. Pressure came back to optimal range within 3 mins. Alarm cleared | All Water System ROC General | 2025-12-09
ROC | December | JFRS - Activated duty 2 | All Water System ROC General | 2025-12-09
ROC | December | MAPS PD8 - PD8 Pump 2 fault alarm came in. This occurred after activated duty. Unable to clear. Pump 1 and pump 3 are running in duty 1. Will send an email to the west team | All Water System ROC General | 2025-12-09
ROC | December | MKRSEM - Called Toronto Water (Zoran) to stop pumping to reservoir MARS - Also requested Zoran to go down to normal flow | All Water System ROC General | 2025-12-09
ROC | December | NMETHW, Historian Heartbeat alarm, notified Artour L, he will look into it | All Water System ROC General | 2025-12-04
ROC | December | MKMCEM, Rob P on site testing flood alarms | All Water System ROC General | 2025-12-01
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-08
ROC | December | BVPS- Placed P1 in man/off and placed P2 in man/on after inhibit cleared | All Water System ROC General | 2025-12-03
ROC | December | VNPS PD8- Placed all pumps in manual and stopped P1 | All Water System ROC General | 2025-12-07
ROC | December | AURSBS - Deactivated duty to help slow the drain of MARS AURSOH - Deactivated duty to help slow the drain of AURSBS in preparation for interim | All Water System ROC General | 2025-12-08
ROC | December | NBW56 - Joe W onsite testing chlorine leak, spill, temp, and working on chlorine/turbidity analyzer, running diesel gen | All Water System ROC General | 2025-12-09
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-04
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-09
ROC | December | STRS48 - Influent free chlorine hihi. Checked site, wells recently activated which triggered the chlorination system. Trending shows a spike of the influent free chlorine residual reading which returned to normal range within two reading intervals., | All Water System ROC General | 2025-12-08
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-01
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-02
ROC | December | NMVCBA- Placed valve manual 20L/s to keep NMETIV and NMETHW offset. 03:22- Placed back into auto | All Water System ROC General | 2025-12-02
ROC | December | AUPSOH, Jerry Z on site, running generator and testing temp alarms | All Water System ROC General | 2025-12-02
ROC | December | NMETIB - Total chlorine hihi, combined hihi. Spike in readings after duty active. Readings continue to climb. Informed Donald M, will head to stie CMU = 11488875 20:01 - Donald M finished at site. Analyzers reading within range | All Water System ROC General | 2025-12-04
ROC | December | Carter Dunn Signing In, -9D/Clear | All Water System ROC General | 2025-12-05
ROC | December | VNPS PD7 - Lee F on site to complete pump greasing. Lee has requested that each pump be ran individually for approximately five minutes. Will rotate pumps as needed. | All Water System ROC General | 2025-12-08
ROC | December | SHETCS - Hypo pump 2 uncommanded stop alarm. Checked site, duty rotated to pump 1. Operations normal, reset alarm. | All Water System ROC General | 2025-12-02
ROC | December | STW12- Placed well 2 back into auto STW3- Placed well back into auto | All Water System ROC General | 2025-12-02
ROC | December | NMETIB- Deactivated duty | All Water System ROC General | 2025-12-03
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-04
ROC | December | MKRSEM- Called Toronto (Brett) and requested pumps off. | All Water System ROC General | 2025-12-04
ROC | December | STPSMR - Stephen B. called to inform that he is finished on site and that the site is back to normal. Stephen requested a CMU5 for the leak. CMU5 created W11491819 #CMU5 | All Water System ROC General | 2025-12-05
ROC | December | NMETIB - Activate duty 1 | All Water System ROC General | 2025-12-04
ROC | December | AURSBS - Post injection free chlorine hihi alarm. Checked site, chemical system recently activated as flow started leaving the reservoir to AURSOH. Trending shows the free chlorine drop and then spike again. Ben H investigating. 15:17 - AURSBS - Ben H has informed that jerry Z will respond to site. Created CMU5#W11484548 #CMU5 | All Water System ROC General | 2025-12-03
ROC | December | MKPSSA, Placed Pump 1 man/on | All Water System ROC General | 2025-12-07
ROC | December | BLW12, Joe M on site, running generator and cleaning analyzers, directed to disregard alarms on site till Joe M is finished | All Water System ROC General | 2025-12-02
ROC | December | NMETIB- Deactivated D1 to offset from NMETHW | All Water System ROC General | 2025-12-03
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-03
ROC | December | NMETIB- Activated D1 at 48% to offset from NMETHW | All Water System ROC General | 2025-12-03
ROC | December | BLW12, Dan Z running well 1 to waste | All Water System ROC General | 2025-12-04
ROC | December | NMW15 - Influent free chlorine hihi alarm. Checked site, well recently activated. Trending shows the influent free chlorine spiked and returned to normal range within two reading intervals. Reset alarms. | All Water System ROC General | 2025-12-08
ROC | December | Adeela Khan signing in. Weather: -8 and cloudy | All Water System ROC General | 2025-12-08
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-08
ROC | December | HLETYS - Activated duty 1 in preparation for interim YWS + NYWS Normal | All Water System ROC General | 2025-12-09
ROC | December | VNPS PD7 - Placed pumps man/of and placed pump 1 and 3 at MAPS PD7 in auto, to help lower levels at MARS | All Water System ROC General | 2025-12-09
ROC | December | NMTKKC - Activated duty 1 NMTKBS - Activated duty 1 AURSOH - Activated duty 1 in preparation for interim | All Water System ROC General | 2025-12-09
ROC | December | STW12 - Placed STW1 man/off as per Stephen B. | All Water System ROC General | 2025-12-08
ROC | December | AUPSRR - Historian heartbeat alarm. Checked site, operations normal and no impact to trends. Unable to clear alarm. Contacted Chris S. | All Water System ROC General | 2025-12-08
ROC | December | KSTP - RIck L and Parth P leaving site after investigating the finished water total chlorine and fluoride fault alarms. | All Water System ROC General | 2025-12-08
ROC | December | YWS + NYWS Normal Connor Smith signing out | All Water System ROC General | 2025-12-02
ROC | December | KSETDP - Patrick F informed that KSETDP is being drained and isolated today for maintenance work and installation of a check valve. Patrick stated that if a low pressure alarm triggers he would like to be contacted. | All Water System ROC General | 2025-12-02
ROC | December | MKRSEM- Called Toronto (Zoran) and requested pumps off. | All Water System ROC General | 2025-12-03
ROC | December | Christian Van Beek signing in. Weather: -6 and clear. | All Water System ROC General | 2025-12-03
ROC | December | Hub1 Server - Kingsley M completing a server restart. | All Water System ROC General | 2025-12-02
ROC | December | Carter Dunn Signing Out | All Water System ROC General | 2025-12-02
ROC | December | GWTP- Patrick F on site to work on backpulse valve on train 5. Will be working on compressor with Jack P later on but no alarms expected | All Water System ROC General | 2025-12-03
ROC | December | AUPSRR, Chemscan analyzer was having issues, made CMU5 for Parth P CMU5: W11481431 | All Water System ROC General | 2025-12-02
ROC | December | Carter Dunn Signing Out | All Water System ROC General | 2025-12-01
ROC | December | QVW12 - Well 1 building smoke detector alarm. Contacted Alex B who is not on site but will discuss with Ryan B and Ben H to determine next steps. 12:06 - QVW12 - Stephen from ABPMC called to inform that their team triggered the smoke alarm and no response is needed. Informed Alex B. | All Water System ROC General | 2025-12-04
ROC | December | HLETYS, Eric S on site calibrating the pre cl2 analyzer STPSMR, Stephen B/Travis W on site changing cl2 cylinders | All Water System ROC General | 2025-12-05
ROC | December | MTW3 - Sean P on site for generator test and PM's. Sean has requested that the well be deactivated during the load transfer test. Contacted Jackie S to confirm she does not need the well on for an y of her PM's. Placed well manual off. | All Water System ROC General | 2025-12-04
ROC | December | MTW3- Generator not in auto alarm outstanding. Notified Jackie P. Jackie P let contractors on site and are working on generator | All Water System ROC General | 2025-12-03
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-04
ROC | December | STW12 - Place well 1 in man/on | All Water System ROC General | 2025-12-04
ROC | December | VNP8 - Rotate pump 2 & 3 to duty 1 & 2 fir Lee F | All Water System ROC General | 2025-12-08
ROC | December | YWS+ NYWS Normal Adam Button signing out | All Water System ROC General | 2025-12-03
ROC | December | AUVCBS - Rob P in site. | All Water System ROC General | 2025-12-04
ROC | December | BLW12 - Joe M called to inform the well is going to remain offline overnight. All outstanding alarms can be disregarded | All Water System ROC General | 2025-12-03
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-03
ROC | December | Carter D signing in, -1D/Clear | All Water System ROC General | 2025-12-01
ROC | December | QVW34- Placed well 3 in man/on for Alex B Influent free Cl2 hihi alarm came in on well start up. Recovered after 3 mins alarm cleared | All Water System ROC General | 2025-12-01
ROC | December | MTETNL, Jackie S on site, doing tower PMs. Working on chemical analyzers and testing temp alarms | All Water System ROC General | 2025-12-04
ROC | December | HLETYS, Benson S is on site. Sharon Valve, Placed valve back to auto | All Water System ROC General | 2025-12-05
ROC | December | AURSBS - Post Injection Total Chlorine HiHi and Post Injection Combined Chlorine alarms came in. Levels did come back down to optimal range within 5 mins. Gave William M. a call just to inform | All Water System ROC General | 2025-12-05
ROC | December | QVW34 - Donald M. is on site adjusting analyzers. This caused the wells to interlock. Donald informed that he is working to clear the alarms and the interlock | All Water System ROC General | 2025-12-05
ROC | December | NMTKKC, Joe D on site, working on the chemical pumps/systems, Testing flood alarms, directed to disregard alarms SHTP, David T on site, doing health and safety/Cl2 maintenance/Cl2 Leak alarm and may run the generator | All Water System ROC General | 2025-12-04
ROC | December | AN23 - Ben son S on site to complete work orders including generator test, JHSC checks, Turbidity analyzer maintenance, chlorine analyzer maintenance and hypo system maintenance. | All Water System ROC General | 2025-12-02
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-02
ROC | December | HLW2 VC FCV2//Sharon VC, Placed both valves man/closed. Changed the flow set point from HLW2VCFCV2 from 40 to 0L/sec. Notified Benson S about these changes, he is fine with them currently. Reason for this operational change is Ryan B is losing to much flow on his end at NMETHW and needs to slow that down. | All Water System ROC General | 2025-12-04
ROC | December | VNRSKS, Deactivated D1 to allow MARS to recover Hub 2 Server, Kingsley M is restarting the server VNPS PD7, Suct Hdr Free CL2 hi alarm, notified Jacob M who is on site, he will look into it | All Water System ROC General | 2025-12-04
ROC | December | SHETCS - Hypo pump 1 and 2 failed to start alarms. Checked site, tower is filling. Reset alarms, pumps failed two more times. Called Benson S who will check SCADA and determine if a site visit is needed. 06:53 - SHETCS - Hypo pumps failed to start alarm. Following the call with Benson, reset the alarms one more time. Pump 1 activated and did not fail. Benson called back and the ROC informed Benson that the pump has activated. Benson stated that an area operator would check the pumps later today. #consult | All Water System ROC General | 2025-12-08
ROC | December | AURSBS - activated duty 1 to fill the reservoir for the interim procedure VNRSKS - Activated duty 1 to fill the reservoir for the interim procedure TMC317 - Called Toronto Water (Peter) and requested additional flow as ARPS will be going offline at 08:00 and MARS Supply flow will be limited after that. | All Water System ROC General | 2025-12-08
ROC | December | Christian Van Beek signing in. | All Water System ROC General | 2025-12-04
ROC | December | Adam Button signing out | All Water System ROC General | 2025-12-01
ROC | December | YWS + NYWS Normal Connor Smith signing out | All Water System ROC General | 2025-12-03
ROC | December | STRS48- Influent free Cl2 hihi alarm came in trends recovered reset after 3 mins | All Water System ROC General | 2025-12-03
ROC | December | HLETYS, Ammonia Pumps 1/2 Failed to start, notified Benson S, directed to change ammonia flow set point from 0.3 to 0.29. Alarms were able to be reset | All Water System ROC General | 2025-12-01
ROC | December | MKRSEM - Peter from TO informed they are shutting down pumps temporarily for curtailment on their side for 3 hours. | All Water System ROC General | 2025-12-08
ROC | December | HLW2 - Combined chlorine lolo alarm. Checked site, well is offline for maintenance no water being directed to users. Trending shows a sudden dip of the combined chlorine residual which recovered within two reading intervals. Reset alarm. | All Water System ROC General | 2025-12-08
ROC | December | Ethan Ullalkar signing out. | All Water System ROC General | 2025-12-08
ROC | December | JFRS - Deactivated duty 3 VNPS PD7 - Placed pump 4 back to auto | All Water System ROC General | 2025-12-08
ROC | December | SHTP - Dave T on site to check the UVT analyzers. May see associated alarms. | All Water System ROC General | 2025-12-08
ROC | December | MKRSEM - Toronto Water (Peter) called to inform they have received a notice to curtail and would like to push flow to MKRSEM so they can accomplish their curtailment goal later today. Gave permission to activate two pumps to push flow to MKRSEM for approximately two hours. | All Water System ROC General | 2025-12-08
ROC | December | NMW12- Combined Cl2 lo alarm came in on well start up. Trends recovered after 3 mins alarms cleared | All Water System ROC General | 2025-12-03
ROC | December | NMW136- Influent free hihi alarm came in residual recovered after 3 mins alarms cleared | All Water System ROC General | 2025-12-03
ROC | December | BVPS- Placed P3 in man/off and Placed P4 in man/on after inhibit cleared | All Water System ROC General | 2025-12-03
ROC | December | NMW136, Combined Cl2 lolo alarm, Abnormal Dip occurred, dip recovered after 2 readings. Well were off when this happened | All Water System ROC General | 2025-12-04
ROC | December | BVPS, Notified Rick L that we have hit duty 1 start and that pumps need to come back on, Rick L informed the panel that starting the pumps won't affect their work and that this should affect residuals. Placed BVPS pumps 1-4 back to auto | All Water System ROC General | 2025-12-04
ROC | December | GWTP- Jack P running generator for 20 mins. Patrick P directed to disregard UV alarms generated. No issues. | All Water System ROC General | 2025-12-03
ROC | December | Adeela Khan signing out | All Water System ROC General | 2025-12-05
ROC | December | QVW34- CL2 room gas leak alarm came in again Cl2 emergency valve closure active. Notified Donald M. Directed to disregard unless hihi alarm comes in as they have already tested the system and found no leaks and placed wells in man/off. Donald M notified ROC that the emergency closure system works as intended. Wells will remain off for weekend | All Water System ROC General | 2025-12-05
ROC | December | KCETDS- Activated D1 | All Water System ROC General | 2025-12-06
ROC | December | YWS+NYWS normal MKRSEM- Reservoir 1 lo alarm came in. Called Metro spoke with Mehdi to start two pumps | All Water System ROC General | 2025-12-06
ROC | December | SHTP, David T on site, working on the UVT/CL2/Turbidity/Permanganate analyzers/systems. Directed to disregard theses alarms till he is finished on site | All Water System ROC General | 2025-12-02
ROC | December | STETTL//NRETCR//MKPSSA, Evgeni S resetting OIT | All Water System ROC General | 2025-12-02
ROC | December | NMETIB- Activated D1 to offset from NMETHW as per shift report YWS+NYWS normal | All Water System ROC General | 2025-12-06
ROC | December | RHMCMD- Placed in man/open RHRSTR- Deactivated D1 at 79% | All Water System ROC General | 2025-12-06
ROC | December | AURSBS - Parth P finished and leaving site. | All Water System ROC General | 2025-12-02
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-05
ROC | December | Christian Van Beek signing out. | All Water System ROC General | 2025-12-12
ROC | December | Carter D signing out | ROC General | 2025-12-07
ROC | December | ANVCPL- Placed FCV1 in auto | All Water System ROC General | 2025-12-05
ROC | December | NMETIB- Deactivated D1 at 73% to offset from NMETHW as per shift report | All Water System ROC General | 2025-12-06
ROC | December | Christian Van Beek signing out. | ROC General | 2025-12-25
ROC | December | Christian Van Beek signing in. Weather: -1C and clear. | ROC General | 2025-12-25
ROC | December | YWS+NYWS normal | All Water System ROC General | 2025-12-16
ROC | December | MTW12 - Sean P finished on site. Placing well in auto mode. | All Water System ROC General | 2025-12-10
ROC | December | BVPS- Placed P2/3 in D1 for Rick L on site for calibrations | All Water System ROC General | 2025-12-10
ROC | December | AURSBS, Changed controlling cell back to Cell 2, Redempto B finished working on the LIT calibrations | All Water System ROC General | 2025-12-01
ROC | December | MARS - Called Toronto Water (Paul) and requested to increase to normal flow | All Water System ROC General | 2025-12-05
ROC | December | AURSBS - Redempto B and Parth P on site for annual calibrations. | All Water System ROC General | 2025-12-02
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-02
ROC | December | QVW43- Influent Free Chlorine LoLo Switch. Interlocked wells. Wells were not running at the time. Will email Central Ops | All Water System ROC General | 2025-12-03
ROC | December | AURSBS- Red B req o change controlling reservoir cell from 2 to 1 for calibrations. Changes controlling cell to Cell 1 STPSTL- Comms loss on site. Able to reset alarm STPSMR- Comm loss on site. Able to reset MTW3- Comms loss on site. No visuals on SCADA overview but came back after 3 mins alarm cleared STW12- Comms loss on site able to reset alarms MTW12- Comms loss on site able to reset alarms Notified Ian W about Comms issues in Stouffville/Mt Albert systems Created CMU5 W11479942 MARS Generator 1/2 faults outstanding able to clear Generator 2 fault notified Jordan about generator 1 fault outstanding will head to site. Created CMU5 W11479950 | All Water System ROC General | 2025-12-01
ROC | December | QVW12, Alex B on site, running generator, cleaning Cl2 analyzers, testing gas leak alarm, directed to disregard until Alex leaves site 09:02, Alex B called, informed the ROC that there are contractor on site and that the operator will not be running the generator today | All Water System ROC General | 2025-12-02
ROC | December | NMTKKC - Joe D called and directed to revert the duty 1 stop level from 80% to 75%. Made changes. | All Water System ROC General | 2025-12-02
ROC | December | YWS+NYWS normal | All Water System ROC General | 2025-12-06
ROC | December | Christian Van Beek signing out. | All Water System ROC General | 2025-12-03
ROC | December | MTW3, Sean P on site, running generator on load and doing PMs on generator | All Water System ROC General | 2025-12-04
ROC | December | Carter Dunn Signing In, -6D/Clear | All Water System ROC General | 2025-12-04
ROC | December | STW12- Phil D and Electricians well be on site for well rehab today. Wells will be off for work BLETNL- Activated D1 | All Water System ROC General | 2025-12-01
ROC | December | Adeela Khan signing in. Weather: -6 and flurries | All Water System ROC General | 2025-12-07
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-07
ROC | December | NMTKKC - Joe D. called to inform that he is on site and directed to increase the duty 1 stop to 80%. 13:00 - Called Joe D. who directed to place the duty stop back to 75% | All Water System ROC General | 2025-12-05
ROC | December | MKRSEM, Notified Toronto operator Paul to start filling the res | All Water System ROC General | 2025-12-05
ROC | December | YWS+NYWS normal | All Water System ROC General | 2025-12-07
ROC | December | MKRSEM- Reservoir 1 hi alarm came in. Called Metro spoke with Paul to stop pumping to reservoir | All Water System ROC General | 2025-12-07
ROC | December | Adam Button signing out YWS+NYWS normal | All Water System ROC General | 2025-12-07
ROC | December | MTW3 - Jackie S onsite running generator, testing eyewash, chemical system inspection, chlorine leak, and maintaince on chlorine & turbidity lines | All Water System ROC General | 2025-12-09
ROC | December | ANMCBL - Newmarket Hi flow alarm came in. Checked site. Noticed ANVCPL pushing hi flows and NMETHW is draining even with the duty active. Suspected main break. Called Donald M. who will take a look on SCADA #CONSULT | All Water System ROC General | 2025-12-07
ROC | December | QVW12/QVW34- Placed wells back in auto | All Water System ROC General | 2025-12-05
ROC | December | YWS+NYWS normal | All Water System ROC General | 2025-12-06
ROC | December | STETBR- Tower level lo alarm came in STW12- Placed P1 on man/on as per interim STW3- Placed P3 in man/on as per interim | All Water System ROC General | 2025-12-06
ROC | December | AURSBS - Activated duty 1 KCETDS - Activated duty 1 in preparation for interim | All Water System ROC General | 2025-12-09
ROC | December | AUW14 - Placed all wells back to auto | All Water System ROC General | 2025-12-09
ROC | December | BLW3 - Joe M onsite chlorine analyzer cleaning, turbidimeter, chlorine leak. Running diesel generator after as well | All Water System ROC General | 2025-12-09
ROC | December | Ethan U signing in | All Water System ROC General | 2025-12-08
ROC | December | Christian Van Beek signing out. | All Water System ROC General | 2025-12-08
ROC | December | ARPS - David from Peel informed they are able to put 1 pumps back into auto | All Water System ROC General | 2025-12-09
ROC | December | MTW12 - Jackie S onsite to let contractor in for work on generator. Disregard related alarms | All Water System ROC General | 2025-12-09
ROC | December | KSTP - Ryan B requested CMU for Parth P for CO2 analyzer probe replacement. CMU = 11497126 | All Water System ROC General | 2025-12-08
ROC | December | AURSBS - Eric S. is on site 15:19 - Eric S. is finished on site | All Water System ROC General | 2025-12-05
ROC | December | MKPSSA, Placed pump 1 man/off | All Water System ROC General | 2025-12-07
ROC | December | GWS- Derrick from Aquazitoin is flushing in system | All Water System ROC General | 2025-12-01
ROC | December | Hub 1 Reset, Kingsley M is resetting hub 1 KLET27, Deactivated D1 | All Water System ROC General | 2025-12-02
ROC | December | KSTP - Ryan B onsite flushing raw water line | All Water System ROC General | 2025-12-09
ROC | December | VNMCYS- Site Power Failure Alarm. PAC Control Panel Power Fail. Outage shown in area on Alectra Map. No estimated time of restoration. Will monitor and email Rob P. if issue not resolved. VNMCYS- PAC Communication Failure. Estimated Time of Restoration according to Alectra is 05:00 to 07:00 AM | All Water System ROC General | 2025-12-09
ROC | December | KSETDP - Patrick F called to inform that the tower is isolated and now draining to waste. All other Keswick storages are back to normal operations. | All Water System ROC General | 2025-12-02
ROC | December | NMVCBA- Placed valve manual 40L/s to try and keep NMETIB and NMETHW offset. 01:53- Placed back into auto | All Water System ROC General | 2025-12-09
ROC | December | RHPSPA- Hydro Power Failure Alarm. Alarm Cleared | All Water System ROC General | 2025-12-09
ROC | December | BLW3 - Joe M on site to complete a chlorine leak detection test. | All Water System ROC General | 2025-12-09
ROC | December | JFPS- Noticed Only one pumps running as OOS pumps was in duty 1. Placed pump 1 into duty 1 and pump 2 into duty 5 | All Water System ROC General | 2025-12-09
ROC | December | BVSP - Lee F on site to conduct vibration testing on the pumps. Lee has requested that pump 1 and 3 be activated first. Placed all pumps in manual mode for control and activated pump 1 and then three with a delay period between. Will rotate pumps as necessary | All Water System ROC General | 2025-12-03
ROC | December | NBW2 - Joe W on site to complete work orders including turbidity analyzer maintenance, chlorine analyzer maintenance and chlorine leak detection test. | All Water System ROC General | 2025-12-02
ROC | December | NMW12 - Wells placed man/off NMW13 - Wells placed man/of NMW15 - Well placed man/off QVW12 - Wells placed man/off QVW34 - Wells placed man/off. Alex B onsite as well and will be testing chlorine leak Wells placed man/off for scheduled Hub server work by John D | All Water System ROC General | 2025-12-09
ROC | December | Ethan U signing in Weather -8. | All Water System ROC General | 2025-12-09
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-08
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-05
ROC | December | QVW34- Donald M. and Stephen B done on site No leak found but ensured all components were tightened. Gas level in Cl2 room showing no readings | All Water System ROC General | 2025-12-05
ROC | December | MKRSEM- Reservoir 1 hi level alarm came in. Called Metro spoke with Mehdi to stop pumping to reservoir | All Water System ROC General | 2025-12-06
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-07
ROC | December | Carter D signing out | All Water System ROC General | 2025-12-07
ROC | December | STETBR - Tower Level Lo alarm came in. Placed STW1 and STW3 in manual as per interim | All Water System ROC General | 2025-12-07
ROC | December | BLW12- Station Turbidity Fault Alarm. Wells not running. Unable to reset alarm. Placed wells in manual and emailed Stephen B/East Ops | All Water System ROC General | 2025-12-09
ROC | December | Adeela Khan signing out | All Water System ROC General | 2025-12-01
ROC | December | GWTP - Phil D and Patrick F on site to complete UV system maintenance. Phil D directed to disregard alarms. | All Water System ROC General | 2025-12-09
ROC | December | SHSP - Parth P & Red B onsite update both filter analyzer | All Water System ROC General | 2025-12-09
ROC | December | NMVCBA- Placed valve in manual 60L/s | All Water System ROC General | 2025-12-02
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-02
ROC | December | NMVCBA- Adjusted from 40 to 80L/s NMVCIB- Adjusted from 80 to 40L/s 01:30- Reverted changes | All Water System ROC General | 2025-12-02
ROC | December | NMW136 - Red B onsite checking treated total Cl2 analyzer. Man/stop well 13 for work NBW3 - Effluent free chlorine hihi. Tim H onsite. Tim H backflushed after hihi and confirmed no water went to distribution. Able to clear alarms and well back in service | All Water System ROC General | 2025-12-09
ROC | December | STETBR- Tower level lo alarm came in STW3- Placed P3 in man/on STW1 running in manual already. STPSTL P1 lolo flow alarm came in. P 1 stopped after failing to achieve desired flow. Notified Travis W | All Water System ROC General | 2025-12-03
ROC | December | NMW136, John D resetting OIT on site | All Water System ROC General | 2025-12-02
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-02
ROC | December | KSETDP- Outlet Free CL2 LoLo Alarm. Tower is offline. | All Water System ROC General | 2025-12-02
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-03
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-03
ROC | December | STETBR - Dan Z called to inform that she has initiated a deep cycle of STETBR. Dan Z has placed the STPSTL pumps manual off and opened the FCV at STPSTL. Area Ops will revert changes at the end of the day as necessary. | All Water System ROC General | 2025-12-03
ROC | December | MKRSEM- Called Toronto (Paul) and requested pumps on. | All Water System ROC General | 2025-12-02
ROC | December | NMTKKC, Joe D is finished on site NMPSKC, Joe D running generator on site, testing temp alarms, directed to disregard at this time | All Water System ROC General | 2025-12-02
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-07
ROC | December | VNETAG- Inlet flow hi alarm came in. value exceeding hihi alarm set point as well. Called Metro spoke with Mehdi to see if they were doing anything on their end. Nothing out of normal operations. Mehdi dropped a pump at Keele and flow returned to normal at VNETAG. Alarms cleared | All Water System ROC General | 2025-12-06
ROC | December | KSTP - Ryan B. called to inform that PCS will be working on site and will have the plant off for the duration of work. | All Water System ROC General | 2025-12-05
ROC | December | NMTKBS - Kingsley M. will be restarting the OIT | All Water System ROC General | 2025-12-05
ROC | December | YWS+NYWS normal | All Water System ROC General | 2025-12-06
ROC | December | RHMCMD- Placed Valve in auto | All Water System ROC General | 2025-12-05
ROC | December | BLETNL - Joe M. called and directed to activate duty 1 | All Water System ROC General | 2025-12-06
ROC | December | SHETCS- Hypo P1/2 uncommanded stop alarm came in. Reset alarms | All Water System ROC General | 2025-12-07
ROC | December | Carter Dunn Signing In, -2D/Snowing | All Water System ROC General | 2025-12-07
ROC | December | NMETIB, Activated to have towers offset | All Water System ROC General | 2025-12-07
ROC | December | Christian Van Beek signing in. Weather: -12C and clear. | All Water System ROC General | 2025-12-08
ROC | December | AURSOH - Activated duty 1 to fill the reservoir for the interim procedure. | All Water System ROC General | 2025-12-08
ROC | December | MAP7 - Place pumps 1-4 man/off VNP7 - Place pump 1 & 3 auto and activate duty 1 in order to draw from Teston to prolong duty cycle. Done as ARPS planned shutdown in active 10:32 - Revert back to normal operations with VNP7 & MAP7 | All Water System ROC General | 2025-12-08
ROC | December | AUETFC - Rick L and Parth P finished and leaving site. | All Water System ROC General | 2025-12-08
ROC | December | VNRSKS - Activated Duty 1 | All Water System ROC General | 2025-12-08
ROC | December | GWTP - Wash Water Chlorine Residual Hi alarm came in. Checked site. Plant is running, wash pumps 2 and 3 are running. Called Stephen B. who directed to disregard until the hihi level comes in and he would like a call back #CONSULT | All Water System ROC General | 2025-12-08
ROC | December | KSTP, Donald M on site, working with contractor who is working on the generator. They will be running the generator | All Water System ROC General | 2025-12-02
ROC | December | MTW12 - Jackie S on site to complete work orders including chlorine analyzer maintenance, chemical systems maintenance, hi/ow temperature alarm test and generator test. | All Water System ROC General | 2025-12-02
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-01
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-01
ROC | December | STETBR - Tower Level Hi alarm came in. Placed STW1 and STW3 back to auto, as per interim | All Water System ROC General | 2025-12-05
ROC | December | Adam Button signing out | All Water System ROC General | 2025-12-06
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-06
ROC | December | BLW12- Joe M called the ROC to inform that both wells are back online with both contact tanks in service. Joe M is leaving site | All Water System ROC General | 2025-12-06
ROC | December | AURSBS- Activated D1 HLW2- Treated total Cl2 lo alarm and combined Cl2 lolo alarm came in. Checked trends looks like analyzer dropped out and recovered after 3 mins alarms cleared | All Water System ROC General | 2025-12-07
ROC | December | YWS+NYWS normal | All Water System ROC General | 2025-12-07
ROC | December | AUETFC - Rick L and Parth P on site for annual calibrations | All Water System ROC General | 2025-12-08
ROC | December | RHMCMD - Man/close SHETSC - Dave T requested CMU for Eric S for both hypo pumps CMU = 11497043 | All Water System ROC General | 2025-12-08
ROC | December | KSETWB - Terry G onsite for card reader replacement | All Water System ROC General | 2025-12-08
ROC | December | Hub 4- Kingsley M done server reset | All Water System ROC General | 2025-12-01
ROC | December | NMETHW- LIT reading 82% D1 stop at 75% and drainings at 40L/s but still rising. Notified Donald M of potential LIT frozen. Heading to site created CMU5 W11491853 #CMU5 | All Water System ROC General | 2025-12-05
ROC | December | GWTP- Low lift P2 hydraulic valve uncommanded close rest as per shift report | All Water System ROC General | 2025-12-01
ROC | December | STW12 - Stephen B finished at site. STETBR - Place pumps back in auto | All Water System ROC General | 2025-12-04
ROC | December | MARS - Request TO (Bret) to drop to min flow | All Water System ROC General | 2025-12-05
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-01
ROC | December | HLETYS - Post Injection Combined Chlorine Hi alarm came in. Checked site. Duty is active. Increased hypo pump 2 max flow to lower dose, as per shift report 03:39 - Alarm came in again. Increased hypo pump 2 max flow again 04:02 - Level is steady at optimal range and alarm has cleared | All Water System ROC General | 2025-12-01
ROC | December | YWS + NYWS normal | All Water System ROC General | 2025-12-01
ROC | December | AUETOH - Activate duty 1 to as AURSOH filling as Wellington valve is slow to close and approaching hi level | All Water System ROC General | 2025-12-05
ROC | December | GWTP- Sutton header fluoride lo alarm came in. SUETDR D1 not active no water directed to users. Keswick line Fluoride residual okay and Sutton Line recovering. Left alarm outstanding | All Water System ROC General | 2025-12-03
ROC | December | NMTKKC, Joe D is finished on site | All Water System ROC General | 2025-12-04
ROC | December | RHMCMD - Placed valve in auto mode. | All Water System ROC General | 2025-12-03
ROC | December | RHMCMD, Placed valve man/closed | All Water System ROC General | 2025-12-07
ROC | December | MKRSMR - Cell 2 Forward Flow hi/hihi alarms came in. Checked site. Trends indicate fluctuating forward flow for the past hour. Could be a flowmeter issue. Called Stephen B. no answer. 21:00 - Stephen called back and will take a look on SCADA 21:31 - Stephen called back to inform that he did some valve changes and to monitor for an hour. Stephen also directed to place MV6 and MV1 back to auto if the alarm doesnt come back for an hour 22:30 - Called Stephen B. and directed to place the MV1 and MV6 back to auto. Stephen would like an email if the alarm came back in and directs to manipulate MV6 and MV1 again if the alarm persists #CONSULT | All Water System ROC General | 2025-12-07
ROC | December | BLETNL, Kingsley M resetting OIT | All Water System ROC General | 2025-12-05
ROC | December | ARPS, Bineesh from OCWA called, they have operators on site working on the ammonia chemical system, everything is running fine on their end, may experience ammonia alarms but can be disregarded at this time | All Water System ROC General | 2025-12-01
ROC | December | AUPSRR- Aaron C rebooting network to help with slow connection speeds. Will lose comms during reboot but should not exceed 10 mins | All Water System ROC General | 2025-12-01
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-08
ROC | December | QVW12, Alex B on site with Drew from Ferguson Electric, Generator Fault alarm to be disregarded as Drew is working on the generator | All Water System ROC General | 2025-12-02
ROC | December | STW1. Tyler Z/Kyle R on site, getting pump 1 back in operation | All Water System ROC General | 2025-12-02
ROC | December | NMETIB - Activated duty 1 to keep level offset from NMETHW RHMCMD - Closed valve and placed in auto mode. | All Water System ROC General | 2025-12-04
ROC | December | NMETIB - Deactivate duty 1 | All Water System ROC General | 2025-12-04
ROC | December | BLW12 - Joe M called to inform he will be powering down the analyzers on site while contractors complete the new contact tank tie in. Joe M directed to disregard associated alarms. | All Water System ROC General | 2025-12-03
ROC | December | MKRSEM- Called Toronto (Paul) and requested pumps on. | All Water System ROC General | 2025-12-01
ROC | December | SHTP- FILT 1 Turbidity Hi Alarm. Backwash just completed. Reset alarm as per SCADA Report. | All Water System ROC General | 2025-12-01
ROC | December | RHMCMD- Placed valve back into auto. | All Water System ROC General | 2025-12-02
ROC | December | BLETNL- Travis from town of Stouffville req to flush in system. Notified Dan Z directed to postpone until later this week or next week. Notified Travis from Stouffville the request cannot be carried out today | All Water System ROC General | 2025-12-03
ROC | December | BVPS - Stephen B will be on site to complete work orders including the generator test run, JHSC checks, analyzer maintenance, valve exercising and flood alarm test. | All Water System ROC General | 2025-12-02
ROC | December | BVPS - Talha H working on the OIT. Directed to disregard the historian heartbeat alarm. | All Water System ROC General | 2025-12-02
ROC | December | VNPS, Rick L on site, working on the Cl2 system, Placed BVPS pumps man/off | All Water System ROC General | 2025-12-04
ROC | December | MTW3 - Sean P informed that he has completed his work and the site can go back into operation. Cleared alarms and placed well in auto mode. Activated well start. | All Water System ROC General | 2025-12-04
ROC | December | Carter Dunn Signing Out | All Water System ROC General | 2025-12-04
ROC | December | HLETYS, Sean P is finished on site | All Water System ROC General | 2025-12-01
ROC | December | BLW12 - Joe M headed to site to assist with electrical upgrades. BLW12 will be offline all day. | All Water System ROC General | 2025-12-03
ROC | December | RHMCMD- Placed valve in manual RHRSTR- Deactivated duty | All Water System ROC General | 2025-12-03
ROC | December | Carter Dunn Signing In, -6D/Clear | All Water System ROC General | 2025-12-02
ROC | December | Christian Van Beek signing in. | All Water System ROC General | 2025-12-02
ROC | December | BLETNL- Activated duty Interim Procedure | All Water System ROC General | 2025-12-03
ROC | December | Adam Button signing in | All Water System ROC General | 2025-12-03
ROC | December | BLW12- Tyler Z on site and will be disconnecting power to site for work today | All Water System ROC General | 2025-12-03
ROC | December | RHMCMD- Placed valve in manual closed | All Water System ROC General | 2025-12-03
ROC | December | NMETHW, Deactivated D1, notified Alex B on the changes ROC are making to the system | All Water System ROC General | 2025-12-01
ROC | December | RHMCMD, Placed valve man/closed | All Water System ROC General | 2025-12-01
ROC | December | NMTKBS- Deactivated D1 to help AUPSOH recover | All Water System ROC General | 2025-12-01
ROC | December | Hub 4- Kingsley M rebooting server MARS- Cell 2 hihi alarm outstanding notified Jordan B. Will investigate | All Water System ROC General | 2025-12-01
ROC | December | QVW12 - Influent free chlorine hihi alarm. Checked site, well recently activated. Trending shows a sudden spike of the influent free chlorine which returned to normal range within one reading interval | All Water System ROC General | 2025-12-03
ROC | December | AURSBS, Post Injection Tot Cl2 hi alarm, notified Will M, he will inform Donald M of the alarm | All Water System ROC General | 2025-12-04
ROC | December | Connor Smith signing in -6C Snowy | All Water System ROC General | 2025-12-01
ROC | December | AURSBS- Scrubber gas leak alarm came in. Notified Red B. on site working an monitor NBW3- Influent free Cl2 hihi alarm came in on well start up cleared after 3 mins | All Water System ROC General | 2025-12-01
ROC | December | NMW136 - Place well 13 back in auto | All Water System ROC General | 2025-12-09
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-09
ROC | December | Christian Van Beek singing out. | All Water System ROC General | 2025-12-09
ROC | December | KSTP- CO2 Adjusted pH LoLo. Interlocked Low Lift Pumps. Filter 1,2 Level Lo Alarm. Settl Water Cond Level LoLo Alarm. Notified Stephen B. Requested to clear pH Alarm. Low Lifts started back up, requested to clear other alarms once recovered. pH reading is still fluctuating. Requested to place high lift pumps man/off if it happens again and notify via email. 01:01- KSTP- CO2 Adjusted pH LoLo Alarm came in again and interlocked Low Lift Pumps. Placed High Lift Pumps in manual/off and emailed Stephen B and Central Ops. CONSULT | All Water System ROC General | 2025-12-10
ROC | December | MTW12- Jackie S on site to test eye wash stations | All Water System ROC General | 2025-12-01
ROC | December | Adeela Khan signing out | All Water System ROC General | 2025-12-09
ROC | December | AUPSWS - Will M on site to complete work orders including a generator test with Total Power, low temp alarm test, flood alarm test and sump pit inspection | All Water System ROC General | 2025-12-09
ROC | December | SCADA Security Risk, Email was sent early in the night, email didn't have any relevant information, as per SCADA security SOP, notified Chris S just incase, emailed him the email that was send, he is looking into it. consult | All Water System ROC General | 2025-12-07
ROC | December | GWTP- Low lift 3 hydraulic valve uncommanded close alarm came in reset as per interim VNETFD- Deactivated D1 to help tower cycle better | All Water System ROC General | 2025-12-01
ROC | December | VNRSKS- Activated D1 | All Water System ROC General | 2025-12-06
ROC | December | RHMCMD - Placed valve to auto | All Water System ROC General | 2025-12-06
ROC | December | RHMCMD - Man/close | All Water System ROC General | 2025-12-05
ROC | December | Initiating MARS to JFRS feed | All Water System ROC General | 2025-12-07
ROC | December | Reverted MARS to JFRS changes RHMCMD- Placed in manual RHRSTR- Deactivated D1 | All Water System ROC General | 2025-12-07
ROC | December | MKRSEM - Called Toronto Water (Mehdi) and requested two pumps to help fill reservoir 03:28 - Called Toronto Water (Mehdi) and requested to stop pumping to reservoir | All Water System ROC General | 2025-12-07
ROC | December | NMETIB/NMETHW - To support the filling of both towers at the same time, placed NMVCIB at 40 L/s AND NMVCBA at 80 L/s 01:01 - Placed the valves back to normal. 01:02 - Deactivated NMETIB to help support the offset of NMETHW/NMETIB | All Water System ROC General | 2025-12-07
ROC | December | JFPS - Noticed only 1 pump running in duty 1. Pump 2 rotated back to duty 1 which is OOS. Rotated duties so that pump 1 and 3 are in duty 1 and currently running to help fill PD9 | All Water System ROC General | 2025-12-09
ROC | December | YWS + NYWS normal | All Water System ROC General | 2025-12-09
ROC | December | NMW12 - Jay G on site to complete maintenance on the silicate system. Jay will be placing analyzers in calibration mode and will be relieving pressure on the silicate system during his work. Will see associated alarms. | All Water System ROC General | 2025-12-09
ROC | December | NMETIB - Deactivated duty 1 NMVCIB - Place valve at 80 L/s NMVCBA - Placed valve at 40 L/s Confirmed with Donald M. #CONSULT | All Water System ROC General | 2025-12-06
ROC | December | SHETCS- Hypo P1 uncommanded stop alarm. Reset alarm as per shift report KSTP- Raw water turbidity fault alarm came in. Quick spike recovered quickly. Disregard as per shift report | All Water System ROC General | 2025-12-06
ROC | December | STPSTL- P2 lo flow alarm came in P1 started up as P2 shutdown. P1 lo flow alarm came in shortly after. Monitored P2 restart to see if flow recovers. P2 lo flow stopped pump again placed in man/off and monitors P1 restart. discharge flow rec lolo alarm came in as well as P1 lo flow again. Placed in man/off. Issue seems to come in when both towers are near D1 start STETTL- Activated D1 at 55% will allow supply to STETTL establish and try to restart pumps at STPSTL for STETBR fill cycle 22:55- STPSTL- Placed P1 back in auto. Flow established and within normal range. Placed P2 back in auto and cleared outstanding alarms | All Water System ROC General | 2025-12-06
ROC | December | YWS+NYWS normal | All Water System ROC General | 2025-12-07
ROC | December | SHETCS- Hypo pump 1 uncommanded stop alarm. Reset. P1 started up okay | All Water System ROC General | 2025-12-01
ROC | December | AURSBS - Ben H on site and will be closing the inlet valve (PSV1). There is a bypass on site that is always open to allow flow past the valve. Ben requested that associated alarms be disregarded. | All Water System ROC General | 2025-12-02
ROC | December | KSETDP, Phil D/Patrick F on site, testing temp alarms and flood alarms. Site is currently draining and will be isolated later in the day | All Water System ROC General | 2025-12-02
ROC | December | RHMCMD - Placed valve in auto | All Water System ROC General | 2025-12-08
ROC | December | AUW14 - Placed well man/on 02:52 - Placed well back to auto | All Water System ROC General | 2025-12-08
ROC | December | Carter D signing Out | All Water System ROC General | 2025-12-05
ROC | December | SHTP - Filter 2 turbidity hi alarm came in. Checked site. Filter 1 was going through a backwash. Noticed turbidity levels have come back down to optimal range. | All Water System ROC General | 2025-12-08
ROC | December | HLETYS, Ammonia Pumps 1/2 fail, notified Benson S, he will look into it RHMCMD, Placed valve man/closed | All Water System ROC General | 2025-12-05
ROC | December | MTETNL, Jackie S on site, Cleaning the chemical analyzers and testing temp alarms | All Water System ROC General | 2025-12-04
ROC | December | QVW34- Cl2 room gas leak/emergency valve closure alarm interlocking pumps and chlorinators. Checked site looks like small leak is register on analyzer. Notified Donald M. On site at AURSBS troubleshooting deplox analyzer. Donald M req ROC to contact Stephen B that second operator needs to attends site in investigate leak. Notified Stephen B who will attend site once Donald M finishes at AURSBS. Created CMU5 for both Donald M and Stephen B to attend site W11491880 #CMU5 | All Water System ROC General | 2025-12-05
ROC | December | AURSBS- Donald M done on site deplox analyzer within normal range. heading to QVW34 with Stephen B | All Water System ROC General | 2025-12-05
ROC | December | NRETCR, Evgeni S resetting OIT on site | All Water System ROC General | 2025-12-02
ROC | December | BVPS, Talha H resetting OIT, directed to disregard heartbeat alarms | All Water System ROC General | 2025-12-02
ROC | December | HLW2 - Benson S onsite working on chlorine and ammonia system inspection as well as chlorine gas test and PRV, temp, health & safety, silicate system inspection. | All Water System ROC General | 2025-12-09
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-10
ROC | December | MARS- Cell1 (North) Lvl Hi Alarm. RHMCMD- Placed valve in manual RHRSTR- Deactivated duty | All Water System ROC General | 2025-12-10
ROC | December | NMETIB - Activated duty 1 while NMETHW drains. | All Water System ROC General | 2025-12-09
ROC | December | SHTP - Dave T called to inform a contractor is on site to complete a very short test of the generator off load. | All Water System ROC General | 2025-12-08
ROC | December | BVPS - Activate duty 1 to assist with moving flow to preserve MAPS as ARPS planned shutdown active RHMCMD - Man/open | All Water System ROC General | 2025-12-08
ROC | December | ANVC - Chris S on site to complete UPS battery tests. | All Water System ROC General | 2025-12-08
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-05
ROC | December | Adeela Khan signing in | All Water System ROC General | 2025-12-05
ROC | December | Ethan Ullalkar signing out. | All Water System ROC General | 2025-12-05
ROC | December | AUW14 - Placed the duty 1 wells in manual mode to increase the drain cycle time and reduce the burden on AURSBS and MARS while ARPS is offline. VNRSKS - Swapped supply pumps from MAPS top VNPS to reduce demand on MARS. | All Water System ROC General | 2025-12-08
ROC | December | KSETDP, Artour L on site working with network. Working on the fiber networks | All Water System ROC General | 2025-12-05
ROC | December | AUW14- Influent free Cl2 hi alarm came in. Trends recovered after 6 mins alarm cleared | All Water System ROC General | 2025-12-05
ROC | December | AURSBS- Post Injection total Cl2 hi alarm came in. Notified Donald M. who adjusted post injection total Cl2 hihi alarm from 3.75 to 3.70 and directed to disregard hi alarm for night but to call for hihi and ensure chem system locks out if hihi comes in #consult | All Water System ROC General | 2025-12-06
ROC | December | BVPS - Revert back to normal operations after ARPS shutdown. Put duty 1 stop/start back to 65-85%. Lo/Lolo alarms set to 58 & 45% | All Water System ROC General | 2025-12-09
ROC | December | ARPS - David from Peel informed work is complete and they are okay to put total of 3 pumps into auto. | All Water System ROC General | 2025-12-09
ROC | December | NMVCIB- Changed flow setpoint from 80L/s to 40L/s NMVCHW- Changed flow setpoint from 40L/s to 80L/s HLETYS/HLW2/HLPSYS- PAC comm fail alarm came in. Cleared upon acknowledgement. Trends okay | All Water System ROC General | 2025-12-06
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-07
ROC | December | STW12 - Place well 2 man/on STW3 - Place man/on as Bethesda filling | All Water System ROC General | 2025-12-09
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-10
ROC | December | Adeela Khan signing out | All Water System ROC General | 2025-12-08
ROC | December | KCETDS - Activate duty 1 | All Water System ROC General | 2025-12-08
ROC | December | NBW3 - Effluent Free Chlorine Lo alarm came in. Checked site. Well recently activated. Effluent Free levels went back to optimal range within 10 mins. Alarm has been cleared | All Water System ROC General | 2025-12-08
ROC | December | JFPS - Pump 2 was left in man/on by operator due to cavitation as stated in shift report. This caused res to drop to lo level. Rotated pump 1 to duty 1. Placed pump 4 man/off to prevent pump 4 running on duty 3 NRETCR - Deactivate duty 1 | All Water System ROC General | 2025-12-08
ROC | December | QVW12 - Generator Fault alarm came in. Checked site. Wells are not running and site is still running on hydro power. After 2 mins, alarm cleared. Will monitor 01:38 - Alarm came back in. Checked site. Site was again connected to hydro power and not connected to the generator. Will send an email to the central team | All Water System ROC General | 2025-12-08
ROC | December | NMVCBA - Placed Valve in manual to help offset NMETIB and NMETHW 05:47 - Placed valve back to auto | All Water System ROC General | 2025-12-08
ROC | December | GWTP- Train 8 TMP lo alarm came in cleared upon acknowledgement | All Water System ROC General | 2025-12-30
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-20
ROC | December | NRETCR, Activated D1 JFRS, Activated D2 to help start moving water from RHRSTR RHMCMD, Placed valve back to auto | All Water System ROC General | 2025-12-20
ROC | December | YWS + NYWS normal | All Water System ROC General | 2025-12-24
ROC | December | Adeela Khan signing in. Weather: 6C and windy | All Water System ROC General | 2025-12-18
ROC | December | Ethan U signing in Weather: 3c | All Water System ROC General | 2025-12-20
ROC | December | AUW14 - Place wells back in auto | All Water System ROC General | 2025-12-20
ROC | December | HLW1 - Duty not active, combined chlorine lolo. Monitored for the night. Reading not coming back up, interlocked well. Will email oncall in the morning and continue monitoring site | All Water System ROC General | 2025-12-21
ROC | December | BLW12 - Generator running, Hydro One responding, estimated restoration time is 5:45 | All Water System ROC General | 2025-12-21
ROC | December | Carter Dunn Signing Out | All Water System ROC General | 2025-12-31
ROC | December | MARS- Called Metro spoke with Mehdi to go back to one small pump | All Water System ROC General | 2025-12-30
ROC | December | YWS + NYWS Normal Connor Smith signing out | All Water System ROC General | 2025-12-17
ROC | December | NMTKBS - Activated duty in preparation for interim | All Water System ROC General | 2025-12-24
ROC | December | Angelica Chepiga signing out | All Water System ROC General | 2025-12-24
ROC | December | YWS + NYWS NORMAL | All Water System ROC General | 2025-12-17
ROC | December | Connor Smith signing in | All Water System ROC General | 2025-12-16
ROC | December | YWS + NYWS NORMAL | All Water System ROC General | 2025-12-17
ROC | December | RHPSPA - Lee F on site to complete vibration testing and greasing of the pump bearings. Lee requested that two pumps be activated. Activated duty 1 as the receiving reservoir is near duty 1 start. Will rotate the duty 1 pumps as necessary to facilitate Lee's work. | All Water System ROC General | 2025-12-19
ROC | December | Gluzen Ramos Ong signing in | All Water System ROC General | 2025-12-18
ROC | December | YWS + NYWS normal | All Water System ROC General | 2025-12-31
ROC | December | YWS+NYWS normal NMTKKC- Placed FCV1 in man/closed to help fill NMTKBS | All Water System ROC General | 2025-12-21
ROC | December | YWS+NYWS normal | All Water System ROC General | 2025-12-21
ROC | December | NMTKKC, Activated D1 | All Water System ROC General | 2025-12-22
ROC | December | MARS, notified Toronto operator Paul to go back to normal flow KCETDS, Deactivated D1 RHMCMD = placed man/closed | All Water System ROC General | 2025-12-22
ROC | December | GWTP - Truck Bay Low Temperature alarm came in. Will send an email to East team | All Water System ROC General | 2025-12-31
ROC | December | STPS48- P2 VFD fault outstanding. Notifed Patrick F. Patrick F attended site earlier today. Reset and cleared alarm | All Water System ROC General | 2025-12-31
ROC | December | AUW57- Combined Cl2 lo alarm came in well man/off no water directed to users | All Water System ROC General | 2025-12-22
ROC | December | MARS - Low level alarm. RHRSTR - Duty just started. TMC317 - Called Metro(Zoran) requested increase flow to MARS. | All Water System ROC General | 2025-12-23
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-30
ROC | December | NMW12, Well 1 Forward Flow hi alarm, notified Ryan B, he will look into it | All Water System ROC General | 2025-12-29
ROC | December | ROC SCADA Room, After the rain/wind storm, ROC experienced some damages, ROs believed it would be a good idea to check the SCADA room to make sure everything is still in working order. As an extra precaution, notified Saurabh M that we will be entering the SCADA room just to verify everything is fine. When RO Carter D/Angelic C, entered the SCADA room, both verified that there was no damage and then closed the door and made sure it was locked. | All Water System ROC General | 2025-12-29
ROC | December | RHPSPA - Lee F called to inform he ahs completed the maintenance on pumps 3 and 4. Deactivated duty, rotated duty 1 to pumps 1 and 2 and then reactivated the duty. | All Water System ROC General | 2025-12-19
ROC | December | SHTP/SHETCS- Power Failure. Notified David T. He will look into it. | All Water System ROC General | 2025-12-17
ROC | December | Received a call from the York Durham Environmental lab regarding a request for re-sample. See below information for details. Verbally informed system ORO, Jason Garnett as this request was sent after hours. Forwarded relevant email information as well. Date and time of call: 19/12/2025 15:40 Date and time of email: 19/12/2025 16:03 Lab contact Name, phone number and email: Rebecca Massimi, 905 686 0041, Rebecca.Massimi@durham.ca Chain of Custody number : W11454665 (Field ID's 241, 252, 242) Date of sample: 12/16/2025 Sampler name: Will Mather Remote operator name: Christian Van Beek | All Water System ROC General | 2025-12-19
ROC | December | GWTP, Train 3 Placed back to the ON position as per Phil D 12:12, Train 3 failed to go into the "ON" position, notified Phil D of this change. While talking on the phone with Phil D, Train 4 had a shutdown alarm/Backpulse Pump 2 not available alarm, Phil D will look into this issue 12:34, Phil D is heading to site CMU5: W11529194 | All Water System ROC General | 2025-12-20
ROC | December | NMETIB- Deactivated duty NMVCBA- Changed from 80 to 40L/s NMVCIB- Changed from 40 to 80L/s | All Water System ROC General | 2025-12-22
ROC | December | STPSTL- Discharge Flow FWD LoLo, Pump 2 Low Flow Alarm. Pump 2 interlocked and pump 1 started in duty 1. STETTL- Activated duty STW12- Placed wells 1,2 in manual STW3- Placed well in manual | All Water System ROC General | 2025-12-16
ROC | December | AUETFS - Jerry Z onsite testing temp alarm | All Water System ROC General | 2025-12-18
ROC | December | VNRSKS- Kingsley M rebooting OIT | All Water System ROC General | 2025-12-17
ROC | December | Angelica Chepiga signing in, weather +2C | All Water System ROC General | 2025-12-17
ROC | December | MAPS PD8 - Kyle R on site with ABB technician to work on the VFD of pump 1 and 3. Placed pump 1 and 3 manual off. Pump 2 and 4 are duty 1 and available. | All Water System ROC General | 2025-12-18
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-29
ROC | December | ARPS - Pump 4 running in pressure mode, confirmed with Jerry from Peel. | All Water System ROC General | 2025-12-17
ROC | December | BVPS - Deactivated duty 1 | All Water System ROC General | 2025-12-24
ROC | December | BLETNL - Tower level hi alarm. Checked site and noticed BLW12 was manual/on. Called Joe M who stated he was finished on site and the well can go back to auto. Made changes. | All Water System ROC General | 2025-12-16
ROC | December | YWS+NYWS normal Adam Button signing out | All Water System ROC General | 2025-12-22
ROC | December | SHTP - UV 1 Minor Fault alarm. Called Dave T who is on site and investigating. | All Water System ROC General | 2025-12-24
ROC | December | Angelica Chepiga signing out | All Water System ROC General | 2025-12-18
ROC | December | GWTP- Sutton Header Fluoride Lo Alarm. Came in on startup. Recovered back to normal. Will notify East Ops. | All Water System ROC General | 2025-12-30
ROC | December | QVW34 - Activated Duty 2 as per Donald M. | All Water System ROC General | 2025-12-30
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-31
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-24
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-18
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-18
ROC | December | HLW1- treated total free Cl2 hi alarm came in Notified Cole W directed changed ammonia ratio from 5.9 to 5.4 due to issues with ammonia dosing throughout week. Cole W also directed to call back in 20 mins if treated free Cl2 residual doesn't return to normal. #consult | All Water System ROC General | 2025-12-21
ROC | December | MARS- Called Metro spoke with Zorhan to reduce flow to reservoir | All Water System ROC General | 2025-12-21
ROC | December | YWS+NYWS normal | All Water System ROC General | 2025-12-21
ROC | December | QVW12 - Alex B running well 1 in man/on, opening with tie valve open HLETYS - PAC communication failure, HLW1/HLW2 - Comm failure to tower. Informed Yash S, will look into issue | All Water System ROC General | 2025-12-17
ROC | December | RHRSTR- Activated D1 | All Water System ROC General | 2025-12-22
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-31
ROC | December | NMVCBA- Placed valve in man/open 40L/s RHVCMD- Placed valve in auto | All Water System ROC General | 2025-12-31
ROC | December | NMETHW- Activated D1 | All Water System ROC General | 2025-12-31
ROC | December | YWS + NYWS Normal Christian Van Beek signing out. | All Water System ROC General | 2025-12-25
ROC | December | BVPS - Satnam M called to inform he needs the assistance of the contracted after hours Electrical Company. Contacted Ainsworth after hours response as per the procedure and requested their assistance. Provided details to the Ainsworth dispatch who will contact their on call electrician and have them attend site. ETA will be communicated to either ROC or Satnam M. Called On call water manager Cristina S as per the procedure to inform of the current situation. | All Water System ROC General | 2025-12-27
ROC | December | AURSBS - Activated duty 1 to draw down MARS. | All Water System ROC General | 2025-12-27
ROC | December | Ethan U signing in Weather -9. | All Water System ROC General | 2025-12-27
ROC | December | YWS + NYWS Normal Christian Van Beek signing out. | All Water System ROC General | 2025-12-27
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-27
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-27
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-27
ROC | December | JFPS- Tim H onsite running pump 2 in manual | All Water System ROC General | 2025-12-22
ROC | December | MAPS- Placed PD7 Pumps in manual VNPS- Placed PD7 duty 1 pumps into auto | All Water System ROC General | 2025-12-22
ROC | December | ARPS, Pump 5 has come back online, waiting to hear from OCWA operator Jerry that everything is back to normal operation | All Water System ROC General | 2025-12-22
ROC | December | AUW14, Placed wells 2/3/4 back to auto | All Water System ROC General | 2025-12-22
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-19
ROC | December | AUETFC, Activated D1 | All Water System ROC General | 2025-12-22
ROC | December | AUPSRR - Ammonia Pump 2 uncommanded stop alarm came in. Checked site. Ammonia tank level is low. Reset alarm and ammonia pump 2 is now taking from ammonia tank 1. Alarm has cleared. Will monitor | All Water System ROC General | 2025-12-23
ROC | December | NMPSKC - Joe D finished at site | All Water System ROC General | 2025-12-17
ROC | December | Ethan Ullalkar signing out. | All Water System ROC General | 2025-12-27
ROC | December | ROC - Ceiling is leaking from left hand side station. Informed Security to contact after hours PS. They insist on verifying ceiling to send to PS before contacting. 18:50 - Sent pics/video to security via teams after following up with them as no one came to inspect. Security will create work order and dispatch property service 19:37 - Chris from PS arrived, looking into issue | All Water System ROC General | 2025-12-28
ROC | December | GWTP - ZW5 channel 1 & 2 parts counts OOR, disregard as per shift report for part counter OOR alarm | All Water System ROC General | 2025-12-29
ROC | December | KSTP - Backwash pump 2 uncommanded stop alarm , backwash pump 1 is on duty 1/available. Cleared alarm. Pump 2 on duty 2. | All Water System ROC General | 2025-12-23
ROC | December | Connor Smith signing in -7C Clear | All Water System ROC General | 2025-12-22
ROC | December | AURSBS - Parth P and Red B completed work on chlorinator. Requested AUVCBS back to auto, Parth P and Red B will monitor on site. Activated Duty 1. | All Water System ROC General | 2025-12-24
ROC | December | RHRSTR - Deactivate duty 1 to assist with water being directed to MARS | All Water System ROC General | 2025-12-29
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-29
ROC | December | MKRSEM - Request TO (Peter) to drop both pumps STRS48 - Sample pump 1 fault. Sample pump 2 duty 1 running. Generator running status, will monitor site. Nothing on Hydro One outage map as of yet. Email sent to area STPSMR - Fire suppression general fault. Able to clear. Generator running alarm, will monitor. 5:39 - Appears few outages around area but not site not covered on outage map. Called Hydro One (Lucia) to report outage and team will respond. Report #1293 | All Water System ROC General | 2025-12-29
ROC | December | AURSBS - Chlorinator 1 position deviation alarm outstanding ( info alarm). Duty not active/chemical system off. Cleared alarm. | All Water System ROC General | 2025-12-24
ROC | December | AURSBS - Parth P and Red B on site for chlorinator rebuild. Deactivated AURSOH duty and will place AUVCBS man/close . | All Water System ROC General | 2025-12-24
ROC | December | JFPS - WPS discharge flow hi alarm. Checked site, pump 3 running in manual but appears to be shutting down. This triggered a spike in flow. Pump 3 has shut down. Flow is now normal | All Water System ROC General | 2025-12-24
ROC | December | Ethan Ullalkar signing in | All Water System ROC General | 2025-12-18
ROC | December | STPSMR - Placing pumps man/off for testing, initiating system monitoring for zone 2 without pumps. Informed Dan Z. Town flushing in Zone 1. | All Water System ROC General | 2025-12-18
ROC | December | STETBR - Tower Level Lo alarm came in. Placed STW3 man/on as per interim. STW12 are unavailable due to low hypo, but can be run in an emergency | All Water System ROC General | 2025-12-31
ROC | December | QVW12, Donald M contacted the ROC about running AUW57 to increase the influent residual. As we were discussing, RO brough up that we only have 1 well available at QVW12/34, Donald M is heading to site to fix Well 1 so it can be up and running just incase something happens with tonight's rain/wind storm CMU5: W11543492 | All Water System ROC General | 2025-12-28
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-28
ROC | December | STPSMR - Patrick F and Travis W on site for a chlorine cylinder change. | All Water System ROC General | 2025-12-18
ROC | December | BVPS - Utility power not available and generator running. Called Alectra outage reporting center to gather more information regarding the power failure. Alectra Operator informed that there was a report of a momentary power failure around 01:31AM but the system has been restored. This timeline was very nsimilar to the original alarm time of 01:24 on SCADA. Alectra Operator stated that once the on site operators confirm that there is an ongoing Utility power failure they can contact the Alectra Outage Centre for additional support and information. Monitoring system and making changes as needed. | All Water System ROC General | 2025-12-27
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-28
ROC | December | KSTP - CO2 Adjusted pH lolo. Seeing trends appears pH dipped below lolo and started to come back up. | All Water System ROC General | 2025-12-29
ROC | December | STW3 - Place well back in auto | All Water System ROC General | 2025-12-29
ROC | December | NMETIB, Activated D1 to offset towers | All Water System ROC General | 2025-12-28
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-28
ROC | December | AUW14, Placed wells 2/3 back to auto | All Water System ROC General | 2025-12-28
ROC | December | SHTP - Air compressor 1 & 2 fault, hydro power loss. Informed Tim H, will head to site to reset air compressor CMU = 11543526 | All Water System ROC General | 2025-12-28
ROC | December | Adeela Khan signing in. Weather: -2 and cloudy | All Water System ROC General | 2025-12-24
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-29
ROC | December | Angelica Chepiga signing in | All Water System ROC General | 2025-12-29
ROC | December | PHPSPA - Discharge header flow 1 Lolo alarm at duty stop. Cleared alarm. | All Water System ROC General | 2025-12-29
ROC | December | Christian Van Beek signing out. | All Water System ROC General | 2025-12-18
ROC | December | MAPS- Placed PD7 Pumps man/off VNPS- Placed PD7 Duty 1 pumps in auto | All Water System ROC General | 2025-12-30
ROC | December | RHMCMD, Placed valve man/closed | All Water System ROC General | 2025-12-30
ROC | December | MKRSEM, Notified Toronto operator Zoran to stop pumping to the res | All Water System ROC General | 2025-12-31
ROC | December | NMETIB - Deactivated duty to help offset with NMETHW | All Water System ROC General | 2025-12-19
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-31
ROC | December | BVPS - Generator running, utility power failure, normal power not available, control panel power failure. Informed Donald M, will monitor site and we have enough fuel for the night Confirmed Alectra is responding on outage map, no restoration time as of yet Consult 20:44 generator room hihi, due to generator running continuously, will monitor | All Water System ROC General | 2025-12-28
ROC | December | MAP7 - Place pump 1 & 2 man/off VNP7 - Place pump 2 & 3 auto. | All Water System ROC General | 2025-12-26
ROC | December | AURSOH, Deactivated D1 | All Water System ROC General | 2025-12-29
ROC | December | GWTP, Train 2/8 - Transmembrane Pressure Lo alarm, notified Patrick F, directed to disregard alarm | All Water System ROC General | 2025-12-19
ROC | December | AURSOH - Activated Duty 1 @ 50% | All Water System ROC General | 2025-12-18
ROC | December | AURSOH - Activated duty 1 | All Water System ROC General | 2025-12-19
ROC | December | MARS - Cell 1 High level critical alarm came in. Called Cole W. who directed to call Peel Water and shut down pump 4. ARPS - Called Peel Water (Binesh) and requested him to shut down the pump. Binesh informed he will need to talk to his ORO and will get give the ROC a call back 05:05 - Binesh called back to inform he shut down the pump #CONSULT | All Water System ROC General | 2025-12-19
ROC | December | HLW2, Combined Cl2 lolo, abnormal dip occurred, well currently local/off, will monitor, if the dip doesn't recover, will email operator | All Water System ROC General | 2025-12-20
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-22
ROC | December | MKRSEM- Called Toronto (Paul) and requested pumps off | All Water System ROC General | 2025-12-16
ROC | December | HLW1- Combine chlorine low alarm, quick dip. Value recovered, alarm cleared. | All Water System ROC General | 2025-12-17
ROC | December | Carter D Signing Out | All Water System ROC General | 2025-12-19
ROC | December | Ethan Ullalkar signing out. | All Water System ROC General | 2025-12-20
ROC | December | VNRSKS, Activated D1 | All Water System ROC General | 2025-12-20
ROC | December | Christian Van Beek signing in. Weather: -7 C and clear. | All Water System ROC General | 2025-12-16
ROC | December | YWS+NYWS normal Adam Button signing out | All Water System ROC General | 2025-12-16
ROC | December | VNPS PD7 - pumps 2&3 man/off MAPS PD7 - pumps 1&2 to auto. | All Water System ROC General | 2025-12-30
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-31
ROC | December | NMW136 - Influent Free Hi and HiHi alarms came in. Checked site and noticed well just started up. After about 5 mins, levels came back to optimal range and alarm has cleared | All Water System ROC General | 2025-12-31
ROC | December | SHETCS - Dave T onsite working on injection point, hypo pumps, chlorine analyzer, and testing temp alarms | All Water System ROC General | 2025-12-17
ROC | December | RHMCMD - Placed valve man/closed | All Water System ROC General | 2025-12-25
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-21
ROC | December | GWTP- ZW7 CIP Feed Inlet V Failed to Open Alarm. Phil D will look into it. | All Water System ROC General | 2025-12-23
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-29
ROC | December | NMETIB- Deactivated duty | All Water System ROC General | 2025-12-17
ROC | December | STETBR- Jackie S onsite working on Chlorine analyzer maintenance and testing eyewash alarm. | All Water System ROC General | 2025-12-17
ROC | December | Adeela Khan signing in. Weather: -7C and snowing | All Water System ROC General | 2025-12-31
ROC | December | Christian Van Beek signing in. Weather: -2C and clear. | All Water System ROC General | 2025-12-24
ROC | December | STETBR - Town of Stouffville flushing in Zone 1, notified Dan Z. | All Water System ROC General | 2025-12-24
ROC | December | GWTP - Sutton header fluoride low alarm. Checked site, Sutton duty is active. Trending shows a small dip of the fluoride reading which recovered. Reset alarm. | All Water System ROC General | 2025-12-24
ROC | December | NMMCAD - TON Valve Chamber Flood Alarm came in. Called Town of Newmarket On call ( 905 505 5373) as per shift report Adeela Khan signing out | All Water System ROC General | 2025-12-19
ROC | December | Tim H locked out of SCADA. requested assistance of on call PCS. Called Kyle C who will contact Tim H. Created CMU5#W11539435 #CMU | All Water System ROC General | 2025-12-24
ROC | December | YWS + NYWS Normal Christian Van Beek signing out. | All Water System ROC General | 2025-12-24
ROC | December | ARPS - Airport Rd pressure lolo. Checked site, ARPS pumps were shut down by Adeela K who contacted Peel Water/OCWA when the hihi level alarm came in at MARS. Noted that KLPS27 recently activated to fill the KLET27, which is at duty start level. RHMCMD is closed and current system pressure indicate that flow would move away from Vaughan to Richmond hill further decreasing pressure in the system. Toronto pumping less than normal through TMC 317 Keel St corridor. Based on the current interim, called Toronto Water and requested they increase pumping to 30MLD through TMC317 to increase system pressure. | All Water System ROC General | 2025-12-19
ROC | December | QVW34- Lee F onsite locking out well 3 for work. | All Water System ROC General | 2025-12-22
ROC | December | KSTP - Ryan B. doing maintenance on chlorine, turbidity and fluoride analyzers. Also doing JH&C work orders. Will notify when finished on site | All Water System ROC General | 2025-12-18
ROC | December | ARPS, Contacted Jerry from OCWA to turn on 1 pump at their plant as MARS is back to normal levels again | All Water System ROC General | 2025-12-19
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-31
ROC | December | YWS + NYWS normal | All Water System ROC General | 2025-12-31
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-26
ROC | December | YWS + NYWS Normal STW3 - Placed well in manual mode while STETBR fills. | All Water System ROC General | 2025-12-27
ROC | December | BVPS - Pump restart inhibit cleared and pumps began to activate when a second failure occurred. Generator uncommanded shutdown alarm triggered, generator shut down and then re-activated. Monitoring site to determine if operations will continue on generator power. 01:54 - BVPS - Issues persisted, pump inhibits cleared but the pumps faulted again and at the same time the generator triggered an uncommanded stop alarm. The cycling of power on and off also shut down the analyzers which resulted in total and free chlorine out of range alarms. The analyzer readings returned to normal once the generator activated again. Placed all pumps manual/off and contacted Donald M and Satnam M who will both attend site as soon as possible. Created two CMU5's #W11543258 for Donnald M and #W11543265 for Satnam. #consult # CMU5 | All Water System ROC General | 2025-12-27
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-27
ROC | December | STW3 - Place back in auto YWS + NYWS Normal | All Water System ROC General | 2025-12-27
ROC | December | NMETIB - Deactivated duty 1 to help offset with NMETHW, as per shift report | All Water System ROC General | 2025-12-25
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-25
ROC | December | Christian Van Beek signing in. Weather: -1C and clear. | All Water System ROC General | 2025-12-25
ROC | December | YWS + NYWS NORMAL | All Water System ROC General | 2025-12-17
ROC | December | BVPS - Activated duty 1 04:30 - Due to MARS high level, deactivated BVPS duty 1 | All Water System ROC General | 2025-12-18
ROC | December | NMETHW - Deactivate duty 1 | All Water System ROC General | 2025-12-27
ROC | December | SHTP - well 2 pump uncommanded start alarm. Checked site, plant is off. Trending shows the wells recently shutdown as the reservoir hit the duty 1 stop setpoint. Cleared alarm. | All Water System ROC General | 2025-12-27
ROC | December | RHMCMD - Closed valve to 50%. | All Water System ROC General | 2025-12-28
ROC | December | Christian Van Beek signing out. | All Water System ROC General | 2025-12-28
ROC | December | AURSOH, Activated D1 NMTKBS, Activated D1 | All Water System ROC General | 2025-12-28
ROC | December | VNRSKS - Swapped supply pumps to two MAPS pumps | All Water System ROC General | 2025-12-25
ROC | December | YWS + NYWS normal | All Water System ROC General | 2025-12-19
ROC | December | MAPS PD8, Placed pumps 1/2/3/4 back to auto, Sean P is leaving site | All Water System ROC General | 2025-12-19
ROC | December | NBW3- Influent Free Chlorine LoLo Alarm. Interlocked well on startup. Waited a few minutes and restarted well. | All Water System ROC General | 2025-12-22
ROC | December | ARPS, Airport Rd Press Fault, Pump 6 shutdown, contacted David from OCWA, he is looking into the situation to get the pumps back to normal operation 12:44, Contacted Zoran from Toronto, directed him to increase the flow to MARS since ARPS is currently down 13:09, Pump 1 is back in operation and ARPS is running normally now. Pressure issue resolved | All Water System ROC General | 2025-12-29
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-28
ROC | December | QVW12- Influent free Cl2 hihi alarm came in. Trends recovered after 3 mins alarm recovered | All Water System ROC General | 2025-12-21
ROC | December | AUW14 - Place wells back in auto | All Water System ROC General | 2025-12-27
ROC | December | MTW3 - Generator running alarm, tower not active. Nothing noted on hydro One map, will monitor 15:20 - Called and informed Dan Z. Will continue to monitor 13:30 - Generator is now off Consult | All Water System ROC General | 2025-12-27
ROC | December | AUW14 - Place wells in man/off | All Water System ROC General | 2025-12-28
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-29
ROC | December | KCPSDS, KCETDS - PAC communication failure alarms, Jordan B heading to site to connect portable generator. KCETFS - Tim H called, site on portable generator power. | All Water System ROC General | 2025-12-29
ROC | December | Adam Button signing out | All Water System ROC General | 2025-12-30
ROC | December | MTW3- Jeff from Keyshack onsite, may receive intrusion alarms. 12:25- Finished onsite. | All Water System ROC General | 2025-12-31
ROC | December | Angelica Chepiga signing in | All Water System ROC General | 2025-12-23
ROC | December | NMPSKC - Joe D working on site with contractors for work. Will be putting flow control valve closed, off for the day. Disregard related alarms. | All Water System ROC General | 2025-12-17
ROC | December | MKRSEM- Called Metro (Zoran)and requested to start two pumps to fill reservoir. | All Water System ROC General | 2025-12-17
ROC | December | MTW12 - Well 2 pump fault, pump not ready MTW3 - Well pump 3 VFD bypass & chlorine sys not available for auto lnlk. Informed Jackie S of outstanding alarm, will be looking into issue | All Water System ROC General | 2025-12-17
ROC | December | KSTP - Flouride res hi, upon checking site appears spiked after a sudden dip prior, analyzer dropped down within range | All Water System ROC General | 2025-12-26
ROC | December | VNPSCD - Jordan B requested to shut off rechlor after generator work. Placed chlorinator 1 & 2 man/off along with ammonia pump 1 & 2 | All Water System ROC General | 2025-12-17
ROC | December | Carter Dunn Signing In, -6D/Clear | All Water System ROC General | 2025-12-20
ROC | December | YWS+NYWS normal | All Water System ROC General | 2025-12-21
ROC | December | AUW14 - Placed wells 2 and 3 in auto mode. NMETIB - Deactivated duty 1 while NMETHW fills. | All Water System ROC General | 2025-12-25
ROC | December | JFPS - WPS Disch Pressure low alarm, activated Duty 1, alarm cleared. | All Water System ROC General | 2025-12-23
ROC | December | VNRSKS - Deactivated duty 1 Switched from VNPS PD7 to MAPS PD7. Placed Pump 1 and 2 man/on at MAPS PD7 | All Water System ROC General | 2025-12-23
ROC | December | MKRSEM - Reservoir 1 Level Lo alarm came in. Checked site. Called Toronto Water (Brett) and requested two pumps on to help fill reservoir. 03:36 - Called Toronto Water (Brett) and requested to stop pumping to reservoir as levels are getting high | All Water System ROC General | 2025-12-23
ROC | December | NBW3- Influent Free Chlorine HiHi. Value recovered. Alarm cleared. | All Water System ROC General | 2025-12-23
ROC | December | KCETDS - Activated duty 1 YWS + NYWS Normal | All Water System ROC General | 2025-12-24
ROC | December | RHMCMD - Placed valve man/closed 05:00 - Placed valve in man/open | All Water System ROC General | 2025-12-24
ROC | December | RHMCMD - Man/open 100% | All Water System ROC General | 2025-12-25
ROC | December | VNRSKS, Deactivated D1 MARS, Contacted Medhi from Toronto to increase the flow to MARS as there is an increase in demand | All Water System ROC General | 2025-12-20
ROC | December | GWTP, Phil D called to say he is finished on site and will be leaving shortly. Notified Phil D of the silicate Tank 1 loss of echo alarm at BLW12. Notified him that the tank level analyzer may not be working properly as trends showed an increase in silicate level from 05:20 to 10:00 then the level completely dropping off. Phil D directed to disregard for the weekend as he isn't concerned that BLW12 will run out of silicate. Last known level was 40cm. BLW12 only runs roughly once to twice a day and should easily make it through the weekend with that amount of silicate. BLW12, Silicate Tank 1 Loss of Echo Alarm | All Water System ROC General | 2025-12-20
ROC | December | STETBR- Tower lo alarm came in STW12- Placed wells 1/2 in man/on STW3- Placed well 3 in man/on as per interim 9:44- STPSTL- P2 lo flow alarm came in reset alarm flow established | All Water System ROC General | 2025-12-21
ROC | December | RHRSTR, Activated D1 to help flow move to MARS from RHRSTR | All Water System ROC General | 2025-12-20
ROC | December | Adam Button signing in | All Water System ROC General | 2025-12-30
ROC | December | Angelica Chepiga signing in, weather -4C | All Water System ROC General | 2025-12-16
ROC | December | MTETNL - Outlet free chlorine Hi alarm, sudden increase in value, cleared in 5 minutes. Activated Duty 1. Value back to normal. Emailed Patrick F. | All Water System ROC General | 2025-12-17
ROC | December | NMETIB - activated Duty 1 to offset with NMETHW. | All Water System ROC General | 2025-12-17
ROC | December | AURSBS, Deactivated D1 | All Water System ROC General | 2025-12-22
ROC | December | GWTP Low lift pump 3 Hydraulic valve failed to open alarm. As per SCADA review reset alarm, back to service. | All Water System ROC General | 2025-12-17
ROC | December | NBW37 - Joe W onsite working on turbidity, chlorine analyzer, generator and pull injection point | All Water System ROC General | 2025-12-17
ROC | December | JFPS, Tyler Z on site running generator in local MAPS PD8, placed pump 1/3 in D1 and pump 2 in D3. Sean P doing pump maint on site | All Water System ROC General | 2025-12-19
ROC | December | GWTP, ZW3 Shutdown Alarm//ZW3 Neutralization Aborted Alarm//Backpulse Flow lolo/Backpulse pump 1 not available alarm, notified Phil D, he will look into it consult | All Water System ROC General | 2025-12-20
ROC | December | MKETFA, Medhi called to informed the RO that he will be doing a valve test on his end | All Water System ROC General | 2025-12-20
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-20
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-20
ROC | December | YWS+NYWS normal | All Water System ROC General | 2025-12-21
ROC | December | QVW34- Alex B called and is testing the Ammonia Containment Flood Float Alarm. | All Water System ROC General | 2025-12-16
ROC | December | YWS + NYWS NORMAL | All Water System ROC General | 2025-12-25
ROC | December | NMTKBS - Activated D1. | All Water System ROC General | 2025-12-17
ROC | December | NMMCAD, TON Valve Chamber Flood Alarm, when the linear team comes in, will notify them of the alarm 07:28, contacted Steve from the town of newmarket about the flood alarm in the meter chamber, Steve will look into if further and get someone to drain the chamber | All Water System ROC General | 2025-12-29
ROC | December | MAPS PD7, Placed pump 2/3/4 in man/off VNPS PD7, Placed pump 3 in auto | All Water System ROC General | 2025-12-29
ROC | December | JFRS, Activated D1 | All Water System ROC General | 2025-12-22
ROC | December | KSETDP - Kingsley M restarting OIT, disregard Historian heartbeat alarm. KLPSWL -Kingsley M restarting OIT, disregard Historian heartbeat alarm. | All Water System ROC General | 2025-12-23
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-22
ROC | December | Angelica Chepiga signing in | All Water System ROC General | 2025-12-24
ROC | December | RHMCMD, Placed valve in auto | All Water System ROC General | 2025-12-29
ROC | December | RHRSTR - Activated duty 1. RHMCMD - Opened to 100%. | All Water System ROC General | 2025-12-25
ROC | December | RHMCMD - Closed valve to 50%. | All Water System ROC General | 2025-12-25
ROC | December | NMW136 - Combine chlorine low alarm. Quick drop. Value recovered in two readings, alarm cleared. | All Water System ROC General | 2025-12-25
ROC | December | JFPS - Lee F requested that pump 2 be placed duty 1 to run for greasing and vibration testing. Made necessary changes. | All Water System ROC General | 2025-12-24
ROC | December | JFPS - Lee F finished on site. Placed P2 man/off and reassigned Duty 1 to P3. | All Water System ROC General | 2025-12-24
ROC | December | JFS- VC UPS ATS Source S2, RES UPS ATS Source S2, WPS ATS Source S2 Not Okay. Alarms cleared. RHPSPA- Hydro Power Failure Alarm. Alarm cleared | All Water System ROC General | 2025-12-31
ROC | December | ARPS- Airport Rd Press Fault Alarm. Pump did not shut down. Cleared alarm. | All Water System ROC General | 2025-12-31
ROC | December | QVW12- Well 2 Forward Flow HiHi Alarm. Recovered after a few minutes. Notified Jerry Z. | All Water System ROC General | 2025-12-31
ROC | December | NRETCR - Activated D1, | All Water System ROC General | 2025-12-18
ROC | December | Carter D signing in, -2D/Clear | All Water System ROC General | 2025-12-28
ROC | December | STRS48, Influent Free Cl2 lolo, Alarm came in later in the night on night shift, placed High Lift pumps 1 and 2 man/off for the time being STETTL, Activated D1 | All Water System ROC General | 2025-12-29
ROC | December | AURSBS - Post injection free ammonia hihi alarm. Checked site, Reservoir just finished a fill cycle. Aurora central not active so the re-chlorination system was not active when this alarm occurred. Will monitor the analyzer reading and inform area operators if it is a prolonged high high value. 19:54 - Ammonia reading did not come down, Aurora central now activating on duty informed Donald M as reformation pumps remain interlocked Consult | All Water System ROC General | 2025-12-29
ROC | December | Ethan Ullalkar signing out. | All Water System ROC General | 2025-12-30
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-30
ROC | December | STW3 - Place well back in auto | All Water System ROC General | 2025-12-30
ROC | December | NMTKKC- Outlet total Cl2 lolo alarm came in residual in normal range reset alarm | All Water System ROC General | 2025-12-31
ROC | December | VNP8 - Sani sump pump 1 & 2 fault. Informed Donald M. Okay to disregard for the night Consult | All Water System ROC General | 2025-12-28
ROC | December | TMC269 - Pressure Lolo, from 10:45-10:52. Confirmed FIT okay, recovered | All Water System ROC General | 2025-12-18
ROC | December | VNRSKS - Swapped supply pumps to one MAPS pump and one VNPS pump to reduce demand on BVPS. | All Water System ROC General | 2025-12-26
ROC | December | NBW3 - Influent free chlorine lolo, reading came back to normal range and cleared alarm | All Water System ROC General | 2025-12-27
ROC | December | STW3- Placed P3 in auto as per interim | All Water System ROC General | 2025-12-31
ROC | December | NMVCIB, Placed valve in manual and set it to 40L/sec to help decrease the flow leaving NMETIB to help allow NMETHW to fill | All Water System ROC General | 2025-12-20
ROC | December | RHRSTR- Deactivated D1 NMW15- Influent free Cl2 lo alarm came in. Recovered after 3 mins alarm cleared | All Water System ROC General | 2025-12-22
ROC | December | BVPS - SCR system fault, followed up with Donald M regarding alarm and gen room temperature reading hihi. Okay to disregard for the night, during phone call generator power shutdown but caused pumps to inhibit. Rotated pump 1 & 3 to duty 1. Consult | All Water System ROC General | 2025-12-28
ROC | December | MAPS PD8 - Sean P and the ABB contractor ready to test pump 4. Duty is currently active with pump 1 and 3 in auto. Placed pumps in manual and activated pump 4 once the shutdown inhibit clears. | All Water System ROC General | 2025-12-19
ROC | December | AUW14, Placed wells 2/4 back to auto | All Water System ROC General | 2025-12-22
ROC | December | VNETFD- Deactivated D1 | All Water System ROC General | 2025-12-22
ROC | December | MTW12- Joe M heading to site and directing to activate MTETNL D1 | All Water System ROC General | 2025-12-22
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-30
ROC | December | RHRSTR - Deactivate duty 1 BVPS - Rotate pump 1 & 3 duty 1 | All Water System ROC General | 2025-12-30
ROC | December | NMETHW - Deactivate duty 1 to offset with Harry Walker | All Water System ROC General | 2025-12-30
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-23
ROC | December | MKRSEM - Called Toronto Water (Brett) and requested two pumps be activated to push flow to MKRSEM. | All Water System ROC General | 2025-12-27
ROC | December | STRS48 - Sample pump 1 fault alarm. Checked site, sample pump 2 rotated into duty 1 and activated. Unable to reset alarm. Sent email to area ops. | All Water System ROC General | 2025-12-27
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-27
ROC | December | BVPS - Donald M and Satnam M on site investigating power failure issues. | All Water System ROC General | 2025-12-27
ROC | December | NMETIB - Deactivated Duty 1 to offset with NMETHW. | All Water System ROC General | 2025-12-30
ROC | December | AURSBS - Donnald M finished work on site, requested AURSOH Duty stop from 85 to 80%. | All Water System ROC General | 2025-12-30
ROC | December | GWTP- ZW5 Channel 1,2 Part Counts Out of Range. Disregard as per SCADA Report. | All Water System ROC General | 2025-12-30
ROC | December | Angelica Chepiga signing in, weather -7C | All Water System ROC General | 2025-12-25
ROC | December | BVPS - Donald M called to inform that he was able to activate two pumps in manual mode. Donald stated that there was an Alectra team nearby that informed them the utility power supply is normal and the station should have power indicating a possible issue with the point of connection between the utility power and the station. Donald and Satnam are investigating. KCETDS - Activated duty 1. | All Water System ROC General | 2025-12-27
ROC | December | AUW14 - Placed wells manual off to prolong the fill cycle of AURSOH, to increase demand on AURSBS and by extension MARS. | All Water System ROC General | 2025-12-27
ROC | December | BVPS - Deactivate duty 1 to reduce flow going to MARS | All Water System ROC General | 2025-12-27
ROC | December | BVPS - Received call from Satnam, they were able to restore power to site after locating breaker switch, called Ainsworth to call off sending electrician. Left voicemail with them. Satnam M leaving site, unable to arm facility. Informed security (Parveern) if mobile security can attend site on their route today and follow up with arming facility as they was a door 4 fault17 in Honeywell alarm according to Satnam. Security will attend today and look into issue | All Water System ROC General | 2025-12-27
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-27
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-30
ROC | December | YWS + NYWS NORMAL | All Water System ROC General | 2025-12-29
ROC | December | AURSOH - Activated duty 1 @ 57%. RHMCMD- Placed man mode/currently open RHRSTR - Deactivated Duty 1 to maintain MARS level. | All Water System ROC General | 2025-12-17
ROC | December | BLW12 - Generator shutoff. HLW1 - Combined chlorine coming back up and able to clear lolo, no longer interlocked | All Water System ROC General | 2025-12-21
ROC | December | NMW15 - Jason G. testing chlorine leak | All Water System ROC General | 2025-12-18
ROC | December | Gluzen Ramos Ong signing out at 14:00 | All Water System ROC General | 2025-12-18
ROC | December | AURSBS - Activated duty 1 | All Water System ROC General | 2025-12-19
ROC | December | Christian Van Beek signing in. Weather: -11C and clear. | All Water System ROC General | 2025-12-27
ROC | December | JFPS - Lee F on site to complete maintenance of JFPS pump 2. Lee requested that pump 1 be deactivated and pump 2 be activated. Placed pumps in manual mode and manipulated pump status for Lee. NBW2 - Tim H on site to complete maintenance on the Turbidimeter. | All Water System ROC General | 2025-12-19
ROC | December | STW3- Artour L working on OIT. Requested well man/off. Disregard heartbeat alarm. 14:35- Artour L finished work. Placed well back into auto. | All Water System ROC General | 2025-12-16
ROC | December | Connor Smith signing out | All Water System ROC General | 2025-12-18
ROC | December | ARPS - Peel (Martin) informed they had a total ammonia lolo alarm which dropped to 0. This was due to operator onsite opening ammonia compartment door which caused the alarm. Rebounded back after 3 min as per Martin. False reading. No alarms came in on our side. | All Water System ROC General | 2025-12-18
ROC | December | JFPS - Noted that pump 2 was in duty 1 and auto. Pump 2 is new and having a slow break in period. Placed the pump manual off and duty 5. Rotated duty 1 to pump 3. | All Water System ROC General | 2025-12-24
ROC | December | MKRSEM - Free chlorine residual fault alarm. Checked site, reservoir is draining. Trending shows a steady reading of the free chlorine and other chlorine residuals. Jack P is on site likely making adjustments. Able to clear alarm. | All Water System ROC General | 2025-12-16
ROC | December | BLW3 - Generator 1 running status alarm. Checked site, generator is running but ATS is pointing to Utility hydro indicating a power blip and not a true loss of power. Will monitor site. 18:33 - BLW3 - Generator has shut down. Operations normal | All Water System ROC General | 2025-12-27
ROC | December | STETBR - Activated duty 1. STW3 - Placed well manual/on while STETBR fills. | All Water System ROC General | 2025-12-27
ROC | December | QVW12 - Well 2 forward flow hihi alarm. Checked site, well recently activated to fill system. Trending shows a short spike of forward flow that has dropped back to normal range. Cleared alarm. | All Water System ROC General | 2025-12-27
ROC | December | MKRSEM - Called Toronto Water (Brett) and requested they deactivate the pumps pushing flow to MKRSEM. GWTP - Low Lift pump 3 hydraulic valve failed to open alarm. Checked site, plant is not running as system is full. Duty rotated to another pump. Cleared alarm. | All Water System ROC General | 2025-12-28
ROC | December | Carter D Signing In, 5D/Clear | All Water System ROC General | 2025-12-29
ROC | December | KCPSDS,KCETDS,KCETFS - Power failure alarms. Power blip, all alarms cleared. | All Water System ROC General | 2025-12-29
ROC | December | RHMCMD- Placed valve back in auto | All Water System ROC General | 2025-12-16
ROC | December | NMVCBP, Changed flow set point from 40 to 80L/sec NMVCIB, Changed flow set point from 80 to 40L/sec 16:56, Reverted changes back to normal operation | All Water System ROC General | 2025-12-29
ROC | December | NMTKKC - Header Combined Chlorine Lo alarm came in. Checked site. Noticed levels back to optimal range and alarm has cleared. Will contiue to monitor | All Water System ROC General | 2025-12-19
ROC | December | KLMCIA - Security intrusion and Meter Chamber flood alarm came in. Shift report indicates this site is OOS. Called Gary P. who directed to disregard until morning as he will attend site in the morning to pump the chamber out #CONSULT | All Water System ROC General | 2025-12-19
ROC | December | STPSTL - Arthur L, Sean P and Drew from Ferguson Electric on site to swap the temporary generator back to the station generator. There may be a load test later today. Arthur will update as needed and has requested that generator alarms be disregarded. | All Water System ROC General | 2025-12-16
ROC | December | STPSTL - Arthur L finished with the generator work on site. leaving. Drew from Ferguson still on site. | All Water System ROC General | 2025-12-16
ROC | December | RHRSTR, Deactivated D1 | All Water System ROC General | 2025-12-23
ROC | December | Connor Smith signing in 0C Snowy | All Water System ROC General | 2025-12-23
ROC | December | KCPSDS- Site power failure, discharge FCV fault, duty just activated, pumps interlocked. KCETFC - Isolation valve fault alarm. KCETDS - control power failure alarms- Notified Jordan B, he will respond. 10:33 - Tim H called, checking power status. Power outage in the area, Hydro 1 assessing damage. OP will attend site to connect portable generator. | All Water System ROC General | 2025-12-29
ROC | December | BVPS, Power has been restored on site | All Water System ROC General | 2025-12-29
ROC | December | KCETDS, Historian Heartbeat, Power has been restored, notified Kyle C, He will look into it CMU5: W11546939 | All Water System ROC General | 2025-12-29
ROC | December | MKRSEM - Request TO (Peter) for min flow | All Water System ROC General | 2025-12-19
ROC | December | GWTP, Sutton Header Fluoride Residual lo alarm, waited for roughly 10 minutes however residual didn't go back to normal range, notified Phil D, directed to disregard both Lo and lolo fluoride alarms from GWTP for the night. consult | All Water System ROC General | 2025-12-20
ROC | December | VNPS PD7, Placed Pump 2 man/off MAPS PD7, Placed pump 2 back to auto | All Water System ROC General | 2025-12-28
ROC | December | VNPS PD7, Placed pump 3 man/off MAPS PD7, Placed pump 1 in auto NRETCR, activated D1 | All Water System ROC General | 2025-12-28
ROC | December | RHMCMD, Placed valve man/open | All Water System ROC General | 2025-12-28
ROC | December | QVW34 - CL2 Emergency Valve Closure Active and Chlorine Room Gas Leak alarms came in. Checked site. Interlocked the wells. Called Donald M. who directed to leave these alarms outstanding and to place both wells man/off. Donald would like a call back if the CL2 Room Gas level hits the hihi. #CONSULT | All Water System ROC General | 2025-12-24
ROC | December | VNRSKS - Activated duty 1 | All Water System ROC General | 2025-12-24
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-25
ROC | December | KCETDS - site back to normal , Tim H requested increase duty start setpoint from 40 to 60%. | All Water System ROC General | 2025-12-29
ROC | December | NMVCBA- Placed valve in man/open at 40L/s to slowdown NMETIB draining. | All Water System ROC General | 2025-12-16
ROC | December | NMW136 - Treated Total and combine chlorine residual low alarms, quick dip. Value recovered, alarms cleared. | All Water System ROC General | 2025-12-16
ROC | December | RHMCMD - man/close to help fill RHRSTR. | All Water System ROC General | 2025-12-17
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-28
ROC | December | AUPSOH - Discharge flow(AU)Low low alarm, duty just activated, alarm cleared. | All Water System ROC General | 2025-12-29
ROC | December | MARS - Called Toronto Water (Zoran) and requested return to normal flow (one small pump) to Res. | All Water System ROC General | 2025-12-29
ROC | December | NMETIB - deactivated duty to offset with NMETHW. | All Water System ROC General | 2025-12-18
ROC | December | MKRSEM, Notified Toronto operator Peter to start pumping to the res | All Water System ROC General | 2025-12-21
ROC | December | KCETDS, Activated D1 RHRSTR, Deactivated D1 RHMCMD, Placed valve man/open to move water from MARS to RHRSTR | All Water System ROC General | 2025-12-22
ROC | December | NBET- Tim H onsite testing low temp and working on chlorine analyzers. | All Water System ROC General | 2025-12-17
ROC | December | NMVCBA- Placed valve in man/open at 40L/s to slowdown NMETIB draining. | All Water System ROC General | 2025-12-17
ROC | December | NMW136 - Combined chlorine lo, dip in trend before coming back within range. Cleared alarm | All Water System ROC General | 2025-12-28
ROC | December | VNPSCD - Chlorine system failure, total and combined hihi. Informed Donald M. Possible issues due to BVPS restarting up again. Will look into issue Consult | All Water System ROC General | 2025-12-28
ROC | December | Angelica Chepiga signing out | All Water System ROC General | 2025-12-29
ROC | December | SHTP- Plant Air Pressure LoLo. Notified Cole W. West team will look into it. | All Water System ROC General | 2025-12-23
ROC | December | VNPS- Jordan B onsite running generator. Deactivated duties and placed in manual. | All Water System ROC General | 2025-12-17
ROC | December | ARPS - Called Peel (Jerry) to place pumps man/off for pressure loop scenario MARS - Called TO (Paul) to request max flow Informed Cristina S that ARPS pumps are all man/off and they will begin work closing valves and testing VNRSKS - Deactivate duty 1, place MAP7 pumps 1-4 man/off. Place VNP7 -pumps 1 & 3 auto and reactivate duty 1 RHRSTR - Activate duty 1 | All Water System ROC General | 2025-12-17
ROC | December | SHTP - Raw water tank level going down hitting lo alarm, informed Tim H of issue, will take a look Consult | All Water System ROC General | 2025-12-29
ROC | December | NMETHW - Activate duty 1 | All Water System ROC General | 2025-12-29
ROC | December | NRETBR - Donald M. testing temp alarms and doing chlorine analyzer maintenance | All Water System ROC General | 2025-12-18
ROC | December | MTW3 - Lee F on site to complete greasing on the lower motor bearing. Lee requested that MTW3 be run for a short duration to complete the work. Placed MTW3 manual/on. | All Water System ROC General | 2025-12-18
ROC | December | Ethan U signing in Weather -4. | All Water System ROC General | 2025-12-19
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-20
ROC | December | SHTP - Air compressor 1 fault, filter 1/3 FCV faults alarms - Power back to normal, generator stopped. Plant was not running. Filter compressor 1 fault alarm outstanding. Emailed Cole W, he will check first thing in the morning. | All Water System ROC General | 2025-12-23
ROC | December | GWTP - Train 7 shutdown, Maintenance clean aborted, backpulse pump 1 N/A, backpulse flow lolo. informed Dan Z, will take a look at system Consult | All Water System ROC General | 2025-12-26
ROC | December | Connor Smith signing in 3C Clear | All Water System ROC General | 2025-12-17
ROC | December | GWTP - CIP clean/recirc flow lo, followed up with Phil D who is onsite. Disregard for the night. Phil D informed we may see an Exceedance alarm, disregard for night as well KSTP - Backwash 1 FVC Modbus failure, backwash 2 in good standing, disregard as per Phil D | All Water System ROC General | 2025-12-18
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-26
ROC | December | Carter Dunn Signing In, 4D/Rain | All Water System ROC General | 2025-12-19
ROC | December | JFPS, Dan B on site, replacing the motor on pump 2. disregard power loss to pump 2 | All Water System ROC General | 2025-12-19
ROC | December | RHRSTR, FMC called to inform of intrusion, notified FMC operator to contact security | All Water System ROC General | 2025-12-20
ROC | December | GWTP - ZW2 Permeate Turbidity HiHi , ZW2 shutdown alarm, notified Phil D. He is on site will check. | All Water System ROC General | 2025-12-23
ROC | December | AUW57- Chris S working on OIT. Disregard Heartbeat Alarm. | All Water System ROC General | 2025-12-23
ROC | December | MKETFA- Parth P onsite working on chlorine analyzer | All Water System ROC General | 2025-12-23
ROC | December | YDSS + YNSS Normal | All Water System ROC General | 2025-12-26
ROC | December | Ethan Ullalkar signing out. | All Water System ROC General | 2025-12-26
ROC | December | STETTL - Tower approaching low level alarm setpoint. Deactivated STETBR fill cycle to allow STETTL to recover. | All Water System ROC General | 2025-12-26
ROC | December | STW3 - Placed well in auto mode. | All Water System ROC General | 2025-12-26
ROC | December | VNRSKS - Swapped supply pumps to two MAPS pumps, zero VNPS pumps. | All Water System ROC General | 2025-12-26
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-30
ROC | December | VNPS - Tim H requested to start BVPS pumps. Activated RHRSTR duty. | All Water System ROC General | 2025-12-24
ROC | December | AUW14 - Man/started Well 1 pump to help with AURSOH level. | All Water System ROC General | 2025-12-24
ROC | December | MAPS PD7- Chris I requested to stop pump 3. P3 is back to normal operation/ Duty 2. | All Water System ROC General | 2025-12-24
ROC | December | GWTP- Patrick F working on GAC 2, UVT analyzer, Keswick and Sutton Header analyzer maintenance, air compressor, Chemical Pump maintenance. | All Water System ROC General | 2025-12-17
ROC | December | QVETQS- Alex B onsite testing h/low water level, deplox work, health and safety, and exercising valves. | All Water System ROC General | 2025-12-17
ROC | December | VNPSAP- Jacob M onsite testing building flood alarm. | All Water System ROC General | 2025-12-17
ROC | December | ARPS - Noticed pumps at airport are off, pressure discharge flow lolo, followed by pressure lolo. Called OWCO (Peter). They are unsure of what occurred and will be following with with Peel. Res @ 60% at moment of occurrence. VNRSKS - Deactivate duty 1. Place MAP7 pump 1 & 2 man/off and place VNP7 pump 2 & 3 auto MARS - Request (Andrew) TO for max flow BVPS - Activate duty 1 13:11 - Peter called back updating he spoke with Peel (Paulvinder) will be looking into issue. Unsure of trigger at this time, they placed pump 5 in manual so DRS doesn't clear and try to start. No estimated time of restoration at this point AUW14 - Place well 1 & 4 man/on to assist 13:35 - Peter from OWCA called back that Peel was able reset issue, they are still unsure of cause of issue but said they are okay to run pump 6 in auto. Monitored for some time, pressure and flow are within range. Will continue to monitor and let run before decreasing flow from Toronto | All Water System ROC General | 2025-12-27
ROC | December | VNRSKS - Deactivate duty 1 VNP7 - Place pump 2 & 3 back man/off MAP7 - Place pumps 1-4 back in auto | All Water System ROC General | 2025-12-17
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-25
ROC | December | VNRSKS - swapped supply pumps from 2 VNPS pumps to one VNPS pump and one MAPS pump to relieve pressure on RHRSTR. | All Water System ROC General | 2025-12-25
ROC | December | MKRSEM - Res low level. Called Metro (Folia) and requested start 2 pumps to fill Res. | All Water System ROC General | 2025-12-25
ROC | December | YWS + NYWS Normal Connor Smith signing out | All Water System ROC General | 2025-12-30
ROC | December | RHMCMD - Man/open | All Water System ROC General | 2025-12-28
ROC | December | YWS + NYWS NORMAL | All Water System ROC General | 2025-12-17
ROC | December | AURSOH - Donald M reguested to change Duty stop from 80 to 85% to keep duty active, will attend AURSBS re-chlor. | All Water System ROC General | 2025-12-30
ROC | December | STETTL - Activated duty 1 to fill system for the interim procedure. | All Water System ROC General | 2025-12-18
ROC | December | Angelica Chepiga signing out | All Water System ROC General | 2025-12-26
ROC | December | VNPS PD7 - Placed all pumps man/off as RHRSTR is low. MAPS PD7 - Placed pump 1 and 2 in auto | All Water System ROC General | 2025-12-31
ROC | December | YWS + NYWS NORMAL | All Water System ROC General | 2025-12-16
ROC | December | MARS- Called Toronto (Brett) and requested decrease flow to one small pump. | All Water System ROC General | 2025-12-23
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-16
ROC | December | SHTP - Raw water tank level lo, followed up with Tim H. Drop filter production flow rate from 34L/s to 32. Consult | All Water System ROC General | 2025-12-30
ROC | December | AURSBS- Deactivated D1 HLW1- Effluent free Cl2 lo alarm alarm came in on well start up. Trends recovered and alarm cleared will continue to monitor | All Water System ROC General | 2025-12-31
ROC | December | AUW57- Influent free Cl2 lo alarm came in. Wells man/off. No water directed to users | All Water System ROC General | 2025-12-31
ROC | December | GWTP- ZW5 Channel 1, 2 Parts Counts Out of Range Alarms. Disregard as per SCADA Report. | All Water System ROC General | 2025-12-30
ROC | December | NBET27 - Parth P and Rick L on site to inspect an analyzer. KCETDS - Outlet total chlorine lolo alarm. Checked site, tower is draining. Trending shows a sudden drop of the total chlorine reading which recovered within two reading intervals. Reset alarm. | All Water System ROC General | 2025-12-16
ROC | December | GWTP- CIP Feed Water Flow Lo Alarm, ZW7 CIP Feed Inlet V Failed to Open Alarm. Notified Phil D. He is working on CIP system and can disregard related alarms. | All Water System ROC General | 2025-12-16
ROC | December | YWS + NYWS NORMAL | All Water System ROC General | 2025-12-16
ROC | December | MKRSEM- Called Metro (Medhi)and requested to start two pumps to fill reservoir. | All Water System ROC General | 2025-12-16
ROC | December | STRS48- Travis W onsite working on Cl analyzers. | All Water System ROC General | 2025-12-17
ROC | December | KCETDS - Activated Duty 1 @ 42%. | All Water System ROC General | 2025-12-17
ROC | December | YWS + NYWS NORMAL | All Water System ROC General | 2025-12-17
ROC | December | RHMCMD, Placed valve man/closed | All Water System ROC General | 2025-12-29
ROC | December | SHTP - Filter panel phase monitor, raw water pumps N/A, came in twice informed Tim H. Will take a look Consult | All Water System ROC General | 2025-12-29
ROC | December | MARS- Called Metro spoke with Poulan to increase flow to reservoir AURSBS- Deactivated D1 ARPS-David called back pressure drop caused pump 1 to shutdown. David was able to start P2. Cause of pressure drop unknown | All Water System ROC General | 2025-12-30
ROC | December | Connor Smith signing out | All Water System ROC General | 2025-12-31
ROC | December | HLETYS - Outlet flow hihi, from 08:45-08:47. Duty not active, recovered. | All Water System ROC General | 2025-12-18
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-18
ROC | December | MARS - Called Toronto Water (Zoran) and requested minimum flow. Zoran informed he can only throttle the pump VNRSKS - Activated duty 1 | All Water System ROC General | 2025-12-19
ROC | December | NMVCIB - Place back into auto JFRS - Deactivate duty 1 & 2 in preparation for Maple to JFRS feed | All Water System ROC General | 2025-12-21
ROC | December | MTW3 - Turbidity Fault Alarm came in. Checked site. Duty is not active. Placed well man/off and will send an email to the east team | All Water System ROC General | 2025-12-01
ROC | December | NMW12 - Effluent Free Chlorine Fault alarm came in. Wells were not running and water was not directed to users. Alarm cleared within 3 mins | All Water System ROC General | 2025-12-01
ROC | December | MAPS PD8 - Activated duty 1 | All Water System ROC General | 2025-12-01
ROC | December | AURSRR - Will M on site to complete a chlorine leak detection test and analyzer maintenance. Will informed that Total Power is on site for generator testing and maintenance. | All Water System ROC General | 2025-12-02
ROC | December | STW12/STW3 - Placed STW2 and STW3 manual on for the fill cycle of STETBR. | All Water System ROC General | 2025-12-02
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-07
ROC | December | NMETYS, Samir from Yorknet is leaving site | All Water System ROC General | 2025-12-02
ROC | December | Christian Van Beek signing out | All Water System ROC General | 2025-12-02
ROC | December | STW12- Placed well 2 in man/on STW3- Placed well 3 in man/on As per interim NMTKKC- Increase D1 Stop from 75% to 80% as per Joe D | All Water System ROC General | 2025-12-01
ROC | December | Ethan U signing in Weather -9. | All Water System ROC General | 2025-12-04
ROC | December | BLW12 - Dan Z leaving site. Site will remain offline and disregard outstanding alarms. Wells local off | All Water System ROC General | 2025-12-04
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-04
ROC | December | RHRSTR - Deactivate duty 1 RHMCMD - Man/open AURSOH -Activate duty 1 | All Water System ROC General | 2025-12-05
ROC | December | BVPS - Stephen B finished and leaving site. | All Water System ROC General | 2025-12-02
ROC | December | KSETDP - outlet free chlorine lo alarm. Tower is drained and offline. | All Water System ROC General | 2025-12-02
ROC | December | AURSBS, Post Injection Comb Chlorine Hi alarm, as per Shift report email that was sent out on Dec 2/2025, Donald M would like a call if the Post Injection hi alarm is triggered, contacted Donald M, he is looking into the issue. When checking the logs at site, Redempto B/Parth P were on site doing calibrations to the analyzers. informed Donald M of these logs consult | All Water System ROC General | 2025-12-02
ROC | December | NMVCBA- Placed back into auto. | All Water System ROC General | 2025-12-02
ROC | December | MAPS PD8, Kyle R on site, working on pump 2, trying to fix the pump fault | All Water System ROC General | 2025-12-02
ROC | December | NMTKKC, Joe D on site doing a Chemscan Hot Flush to the analyzer. Chemscan/Chemical pumps will be off for this. If any issues occur, Joe D would like to be informed | All Water System ROC General | 2025-12-02
ROC | December | STW12, Travis W on site, running generator/Chemical System Maintenance, directed to disregard alarms till he is finished on site. Well will be shutoff | All Water System ROC General | 2025-12-04
ROC | December | AUW57, Jerry Z on site, cleaning the chemical analyzers | All Water System ROC General | 2025-12-04
ROC | December | AUPSRR - Post injection free chlorine hihi alarm. Checked site, trending shows a spike of the free chlorine reading which returned to normal range within one reading interval. Reset alarm. | All Water System ROC General | 2025-12-09
ROC | December | AUPSOH - Gen running, not in auto. Called Jerry Z. Is on site and running generator for W/O. Disregard | All Water System ROC General | 2025-12-09
ROC | December | SHETCS- Hypo Pump 1 Uncmd Stop Alarm. Pump 2 running in duty 1. Cleared alarm. 01:43- Hypo Pump 2 Uncmd Stop Alarm. Hypo Pump 1 took over in duty 1. Cleared alarm | All Water System ROC General | 2025-12-04
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-04
ROC | December | Connor Smith signing in 0C Cloudy | All Water System ROC General | 2025-12-03
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-03
ROC | December | AUETFC- Deactivated D1 | All Water System ROC General | 2025-12-01
ROC | December | YWS + NYWS Normal Connor Smith signing out | All Water System ROC General | 2025-12-04
ROC | December | Adam Button signing in | All Water System ROC General | 2025-12-01
ROC | December | AUW14, Well 1 Waste Flow hihi//Well 1 Pump Waste Flow Open Alarm, Waste valve originally faulted, was able to clear however then these 2 alarms came in. Placed well man/off, sent email to operator | All Water System ROC General | 2025-12-01
ROC | December | AURSOH - Res level low. Informed Donald M, will take a look | All Water System ROC General | 2025-12-08
ROC | December | RHPSPA - Placed all pumps in manual mode to prevent accidental start while the power transfer issues are investigated. | All Water System ROC General | 2025-12-09
ROC | December | Evgeni S Working on MKETFAn1, MKRSEMn1, MKRSMRn1 OITs. Please disregard Historian Heartbeat alarm. | All Water System ROC General | 2025-12-01
ROC | December | NMVCBA- Changed from 40 to 80L/s NMVCIB- Changed from 80 to 40L/s due to NMETIB and NMETHW both active. | All Water System ROC General | 2025-12-03
ROC | December | Connor Smith signing in -6C Clear | All Water System ROC General | 2025-12-02
ROC | December | VNRSKS, Deactivated D1 | All Water System ROC General | 2025-12-01
ROC | December | QVW34 - Alex B onsite, will be running generator and work on turbidimeter | All Water System ROC General | 2025-12-09
ROC | December | SHTP - Chris S rebooting local server. Requested to shut down plant. Informed David T onsite, placed plant off for reboot. | All Water System ROC General | 2025-12-09
ROC | December | MMW1 - Comm loss to Major Mac dewatering RHPSPA - Communication loss to PHPSPA COFTA to RHPSPA - Comm failure. Informed Chris S of Richmond Hill communication loss. PCS will take a look | All Water System ROC General | 2025-12-09
ROC | December | RHMCMD - Placed valve man/closed | All Water System ROC General | 2025-12-08
ROC | December | NMVCBA - Placed back to auto. | All Water System ROC General | 2025-12-17
ROC | December | YWS + NYWS NORMAL | All Water System ROC General | 2025-12-17
ROC | December | NMW15 -Combine chlorine low alarm, well man/off, no water directed to users. | All Water System ROC General | 2025-12-16
ROC | December | STETTL/STETBR- Andrew from OCWA is flushing in zone 1/2 | All Water System ROC General | 2025-12-24
ROC | December | KSTKWP- Donald M onsite for work orders including Cl analyzer and Leak Detection. KSTP- Donald M placed High Lift Pumps man/off in preparation for work later in the day. | All Water System ROC General | 2025-12-17
ROC | December | GWTP- Yash S was able to restore permeate trends on all trains. Will back fill data on Monday to fill gap in trends | All Water System ROC General | 2025-12-21
ROC | December | AUW57- Joe W onsite running well in manual | All Water System ROC General | 2025-12-22
ROC | December | Adeela Khan signing in. Weather: 3C and cloudy | All Water System ROC General | 2025-12-23
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-23
ROC | December | STPSTL - Forward flow lolo alarm. Checked site, duty recently activated. Flow is reading lolo, pump 2 shut down on a low flow alarm and duty rotated to pump 1. Monitored activation. STETBR - Tower low level alarm. Activated STW12/STW3 in manual mode. | All Water System ROC General | 2025-12-25
ROC | December | GWTP- ZW1 Backpulse Inlet V Failed to Open, ZW1 Shutdown. Notified Phil D. Requested to reset alarm and place train back online CONSULT | All Water System ROC General | 2025-12-17
ROC | December | KSTP - Fin water flouride res hi, now within normal range. Informed Phil D. Okay to clear Consult | All Water System ROC General | 2025-12-17
ROC | December | JFPS, KCETDS, KCETFS, NMETHW- Kingsley M rebooting OIT. | All Water System ROC General | 2025-12-16
ROC | December | YWS + NYWS Normal Ethan Ullalkar signing out. | All Water System ROC General | 2025-12-17
ROC | December | NMVCIB- Change flow set point from 80L/s to 40L/s NMVCBA- Placed back to auto and changed flow set point from 40L/s- 80L/s | All Water System ROC General | 2025-12-17
ROC | December | HLW1 - David T requested to call PCS on call (Yash S) and reset OIT/No memory alarm on site. Yash S will check. | All Water System ROC General | 2025-12-23
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-21
ROC | December | AURSBS- Deactivated D1 NBW3- Influent free Cl2 hi alarm came in. Recovered after 3 mins alarm cleared | All Water System ROC General | 2025-12-21
ROC | December | NMETIB- Deactivated D1 as per shift report to offset from NMETHW | All Water System ROC General | 2025-12-21
ROC | December | Gluzen Ramos Ong signing in MARS - adjusted hi level (north cell) from 87 to 85% for ongoing YPFM trial isolation | All Water System ROC General | 2025-12-22
ROC | December | VNETFD - Jacob Muzzin testing generator | All Water System ROC General | 2025-12-18
ROC | December | STW12 / STW3 - Activated wells in manual mode while STETBR fills. | All Water System ROC General | 2025-12-19
ROC | December | JFPS, Placed pump 1 and 3 back to auto, placed pump 2 man/off. Pump 2 will be off for the weekend, Lee F is leaving site | All Water System ROC General | 2025-12-19
ROC | December | AUW57, Jerry Z on site, testing Cl2 leak alarm | All Water System ROC General | 2025-12-19
ROC | December | ARPS, Airport Rd Pressure lolo/Discharge Flow lolo/Total Cl2 lo alarm, Pumps did shutdown, Contacted OCWA operator Peter, he is looking into the situation AURSOH, Deactivated D1 AURSBS, Deactivated D1 AUW14, Placed wells 2/4 man/on to slow down the draining from AURSOH RHRSTR, Activated D1 to get flow moving from RHRSTR to MARS MARS, Contacted Toronto Operator Brent to give increase flow to MARS as ARPS is currently down. Once MARS has gotten back to a normal flow, will request to go back to a small pump | All Water System ROC General | 2025-12-22
ROC | December | GWTP- Tyler ZJ onsite working on Sodium Bisulphate system. | All Water System ROC General | 2025-12-17
ROC | December | VNRSKS - Switched from MAPS PD7 to VNPS PD7 to help increase levels at MARS 01:53 - Switched back to MAPS PD7 | All Water System ROC General | 2025-12-18
ROC | December | NRETBR - Donald M on site to complete work orders including chlorine analyzer, valve exercising and a low temperature alarm test. | All Water System ROC General | 2025-12-18
ROC | December | VNPSCD - Chlorine system failure alarm and pre-injection chlorine analyzer fault alarm. Alarm status changed to normal quickly following alarm trigger. Jordan B signed in on site. Cleared alarms. | All Water System ROC General | 2025-12-18
ROC | December | VNRSKS - Deactivated Duty, VNPS PD7 pumps 2 and 3 man/off, MAPS PD7 pumps 1and 3 to auto. RHMCMD - man/open, to help maintain MARS and RHRSTR levels. | All Water System ROC General | 2025-12-18
ROC | December | MAPS PD7 - all pumps man/off VNPS PD7 - Pumps 2 and 3 to auto. | All Water System ROC General | 2025-12-17
ROC | December | RHMCMD - man/off to help maintain MARS and RHRSTR levels | All Water System ROC General | 2025-12-17
ROC | December | MKMCTA- Meter Chamber Flood Alarm. Called Gary P. No answer. Alarm was cleared by OPS. | All Water System ROC General | 2025-12-22
ROC | December | NBW3 - Influent free chlorine lolo alarm. Checked site, well recently activated to fill the system. The well shutdown and interlocked on the influent free chlorine lolo alarm. Trending shows the influent free chlorine reading recovered and then dropped again while the well was interlocked. Called Joe W who is aware and will check the system. Placed well in manual mode until it can be checked. | All Water System ROC General | 2025-12-24
ROC | December | AUPSRR - Booster pump 2 VFD not ready( info alarm), Booster pump 2 speed OOR alarms on duty shutdown. Notified William M, he will check. | All Water System ROC General | 2025-12-24
ROC | December | MAPS PD8- Kyle R and Sean P onsite with ABB Contractors for VFD work. Pumps 1 and 3 are running. They will begin work on pumps 2, 4. | All Water System ROC General | 2025-12-17
ROC | December | MAPS PD7 - Joe W requested to place P 3 man/off, pump has bearing issues. Reassigned P4 to duty 1. | All Water System ROC General | 2025-12-23
ROC | December | VNRSKS - Activated duty 1 | All Water System ROC General | 2025-12-24
ROC | December | KSTKWP- Gas Chlorinator 1 failed to close. Reset alarm | All Water System ROC General | 2025-12-22
ROC | December | HLETPR - Benson S. and Stephen B. testing temp alarms. Notified Benson S. outstanding intrusion alarm | All Water System ROC General | 2025-12-18
ROC | December | Ethan Ullalkar signing out. | All Water System ROC General | 2025-12-18
ROC | December | RHMCMD - Placed valve in auto YWS + NYWS Normal | All Water System ROC General | 2025-12-19
ROC | December | STRS48 - High lift pump 1 uncommanded stop alarm. Checked site, high lift pump 1 was running when fault triggered. Trending shows normal operations before the fault. Reset alarm and monitored pump start. | All Water System ROC General | 2025-12-16
ROC | December | STPSTL- Travis W. onsite with Ferguson for generator test. He will place STW3 man/off | All Water System ROC General | 2025-12-16
ROC | December | YWS + NYWS Normal Christian Van Beek signing out. | All Water System ROC General | 2025-12-16
ROC | December | MTW3 - Lee F finished on site. Deactivated well and placed in auto. | All Water System ROC General | 2025-12-18
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-19
ROC | December | Christian Van Beek signing in. | All Water System ROC General | 2025-12-19
ROC | December | VNRSKS - Jake M on site to complete the JHSC checks and valve exercising. Jake has placed VNPS PD7 pumps in manual/off for the duration of this work. | All Water System ROC General | 2025-12-19
ROC | December | GWTP- ZW1 Permeate Turbidity value trends showing no data on trends for past few days. Notified Yash S. Will take a look on SCADA. Created CMU5 W11529385 #CMU5 | All Water System ROC General | 2025-12-21
ROC | December | STETBR, Deactivated D1. STETTL is below d1 start STW12/3, placed back to auto | All Water System ROC General | 2025-12-21
ROC | December | NMVCIB, Placed valve in manual and set the flow setpoint to 40L/sec | All Water System ROC General | 2025-12-21
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-21
ROC | December | NMVCBP, Changed flow setpoint from 40 to 80L/sec NMVCIB, Changed flow setpoint from 80 to 40L/sec | All Water System ROC General | 2025-12-22
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-22
ROC | December | KLPS27 - Put system into high pressure mode as per interim | All Water System ROC General | 2025-12-17
ROC | December | STPSMR- Jack P onsite running generator. Will then be doing analyzer maintenance. | All Water System ROC General | 2025-12-17
ROC | December | MTW12 - Place well 2 man/off for Kingsley M reboot of OIT | All Water System ROC General | 2025-12-17
ROC | December | ARPS- Pressure fault alarm came in. Slight dip in trends but recovered did not go below lo setpoint trends look okay | All Water System ROC General | 2025-12-22
ROC | December | MAPS - Chris I and Tyler CS finished on site. STETBR - Low level, Placed man/off STW12 and STW3 pumps for ET fill cycle. | All Water System ROC General | 2025-12-24
ROC | December | NBW5 - Tim H on site, cleaning turbidity meter. | All Water System ROC General | 2025-12-23
ROC | December | AUETOH -Activated duty 1 in preparation for interim | All Water System ROC General | 2025-12-24
ROC | December | NMETIB, Deactivated D1 to keep the towers offset | All Water System ROC General | 2025-12-20
ROC | December | AUW14 - Place wells man/off AURSBS - Activate duty 1, due to MARS approaching hi level KCETDS - Activate duty 1 to prep for MAPS to JFRS feed | All Water System ROC General | 2025-12-20
ROC | December | ARPS - Airport total ammonia fault, able to clear YWS + NYWS Normal | All Water System ROC General | 2025-12-20
ROC | December | YWS + NYWS NORMAL | All Water System ROC General | 2025-12-26
ROC | December | YWS + NYWS NORMAL | All Water System ROC General | 2025-12-26
ROC | December | QVW12- Influent Free Chlorine Hi Alarm. Value recovered. Cleared alarm. | All Water System ROC General | 2025-12-26
ROC | December | NMVCIB- Change flow set point from 80L/s to 40L/s NMVCBA- Changed flow set point from 40L/s- 80L/s | All Water System ROC General | 2025-12-26
ROC | December | STETBR - Tower high level alarm. Placed STW12/STW3 to auto. | All Water System ROC General | 2025-12-26
ROC | December | QVW34 - Treated Total chlorine low alarm, value recovered in 2 readings. Pumps in man/off mode, no water directed to users. | All Water System ROC General | 2025-12-26
ROC | December | End Maple to JFRS feed | All Water System ROC General | 2025-12-21
ROC | December | HLETYS - Post injection combined chlorine high. Checked site, tower is filling and chemical system is active. Trending shows the value hovering slightly above and slightly below alarm setpoint resulting in the alarm triggering multiple times. Called Benson S who is on his way to site. | All Water System ROC General | 2025-12-16
ROC | December | RHMCMD - Man/close valve | All Water System ROC General | 2025-12-19
ROC | December | MARS, Notified Medhi to go back to normal flow | All Water System ROC General | 2025-12-20
ROC | December | VNPS PD7, Placed pump 2/3 man/off MAPS PD7, Placed pumps 1/3 back to auto | All Water System ROC General | 2025-12-20
ROC | December | Adam Button signing in -10 Clear | All Water System ROC General | 2025-12-21
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-26
ROC | December | NMETHW - Activated duty 1 while NMETIB drains. | All Water System ROC General | 2025-12-27
ROC | December | SHTP - UV Reactor 3 Minor fault alarm. David T on site, will check. | All Water System ROC General | 2025-12-24
ROC | December | MTW12- Eyewash alarm came in. Called Joe M. Lee F is onsite working on it. | All Water System ROC General | 2025-12-22
ROC | December | JFRS - Deactivated duty 2 and then duty 1 to prepare reservoir for the Maple to Jefferson Feed. | All Water System ROC General | 2025-12-28
ROC | December | NBET27 - Stephen B on site toi complete chlorine analyzer maintenance, low/hi temp alarm test and JHSC checks. | All Water System ROC General | 2025-12-18
ROC | December | HLW2 - Treated total and combined cl lo. Well off, reading distribution. Confirmed residual blip, recovered. MAP8 - Kyle R. informed maintenance on P3 complete, placed P2 man/off and P3 man/on for additional testing. | All Water System ROC General | 2025-12-18
ROC | December | NMVCBA- Changed from 40L/s to 80L/s NMVCIB- Changed from 80L/s to 40L/s 15:23- Reverted changes | All Water System ROC General | 2025-12-23
ROC | December | NMETHW, Deactivated D1 as it was .1m away from duty deactivation, NMETIB duty just activated | All Water System ROC General | 2025-12-20
ROC | December | AURSOH, Activated D1, Placed AUW2/4 man/off to allow AURSBS to draw down | All Water System ROC General | 2025-12-20
ROC | December | STETBR, Tower level lo alarm, Placed STW1/3 to man/on to help fill the tower as per interim | All Water System ROC General | 2025-12-20
ROC | December | VNETAG - Tower level hi alarm. Jake M on site manually operating the pumps at VNPSAP. | All Water System ROC General | 2025-12-18
ROC | December | NMVCBP, Changed flow setpoint from 40 to 80L/sec NMVCIB, Changed flow setpoint from 80 to 40L/sec 16:09, Reverted changes back to normal | All Water System ROC General | 2025-12-20
ROC | December | VNRSKS- Activated D1 NBW3- Influent free Cl2 hihi alarm came in on well start up. Recovered after 3 mins cleared alarm | All Water System ROC General | 2025-12-21
ROC | December | YWS+NYWS normal | All Water System ROC General | 2025-12-21
ROC | December | QVW12 - Influent free chlorine hi, monitored. Dropped chlorinator dossing from 116 to 113 | All Water System ROC General | 2025-12-18
ROC | December | AURSOH, Deactivated D1, placed AUW2/4 back to auto | All Water System ROC General | 2025-12-20
ROC | December | MKPSSA, Placed pump 3 man/on to help draw down MKRSEM GWTP, Phil D is currently heading to site, he called to see how the system is running. Notified him that a hi fluoride alarm did come in at at KSTP but recovered immediately when he activated the duty. Also a GAC Flow control Valve Deviation alarm came in at GWTP while RO was talking to Phil D, directed to disregard at this time | All Water System ROC General | 2025-12-20
ROC | December | NMW136, Station Turbidity hi alarm, Rotated silicate pump duty so silicate pump 2 is in D1 and silicate pump 1 is in D2. This is the second time this has happened where the turbidity has increased the way it did. Disabled duty rotation so pump 2 stays in D1. Will send email to operator. | All Water System ROC General | 2025-12-20
ROC | December | Adeela khan signing out | All Water System ROC General | 2025-12-24
ROC | December | STW12- Placed wells in auto STW3- Placed well in auto | All Water System ROC General | 2025-12-23
ROC | December | 11:35 BVPS - Power not available, generator running status alarms. Duty not active, pumps off. Notified Jack P. He will attend site later. | All Water System ROC General | 2025-12-29
ROC | December | ARPS, Jerry from OCWA has called their SCADA team and is looking to get one of their pumps back into service, should only take roughly 10 minutes. Will continue to monitor MARS levels | All Water System ROC General | 2025-12-22
ROC | December | HLW2, Treated Total Cl2 lo/Combined Cl2 lolo, Well currently Local/off, site is currently offline | All Water System ROC General | 2025-12-22
ROC | December | ARPS, Jerry called to confirm ARPS is back to normal operation | All Water System ROC General | 2025-12-22
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-22
ROC | December | RHRSTR- Deactivated duty | All Water System ROC General | 2025-12-22
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-23
ROC | December | GWTP - ZW5 channel 1 and channel 2 particle counts out of range alarms. Checked site, train 5 is in production. Trending shows that for approximately one minute the particle count was reading a negative number before returning to normal range. Alarm is not labelled as a compliance alarm. Able to reset alarms. Sent email to on call operator for review. 23:27 - GWTP - ZW5 channel 1 and channel 2 particle counts out of range alarms. After review of the shift report these alarms are a disregard. | All Water System ROC General | 2025-12-27
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-28
ROC | December | MAPS PD7, Placed pumps 1/2 man/off VNPS PD7, Placed pumps 2/3 in auto | All Water System ROC General | 2025-12-28
ROC | December | YWS + NYWS NORMAL | All Water System ROC General | 2025-12-18
ROC | December | AUETOH - Activated Duty 1. | All Water System ROC General | 2025-12-24
ROC | December | MAPS - Chris I. working on P3. Man/start P3 for test. | All Water System ROC General | 2025-12-24
ROC | December | Ethan U signing in Weather 0. | All Water System ROC General | 2025-12-28
ROC | December | Connor Smith signing out | All Water System ROC General | 2025-12-16
ROC | December | TMC316 - Artour L onsite putting panel | All Water System ROC General | 2025-12-17
ROC | December | STRS48 - Travis W onsite with Jackie S for chlorine cylinder change, scrubber check, chlorine leak, and inspection | All Water System ROC General | 2025-12-17
ROC | December | VNRSKS - Activated Duty 1 | All Water System ROC General | 2025-12-18
ROC | December | MARS - High level, Deactivated RHRSTR duty 1. | All Water System ROC General | 2025-12-18
ROC | December | VNETAG - Historian Heartbeat alarm, notified Artour L. He will check SCADA # CMU5 W11520101 | All Water System ROC General | 2025-12-16
ROC | December | VNETFD- Deactivated D1 to help tower cycle. | All Water System ROC General | 2025-12-17
ROC | December | NMETIB Deactivate duty 1 for offset Harry Walker | All Water System ROC General | 2025-12-18
ROC | December | ARPS- Total ammonia fault alarm. Residual recovered and alarms cleared. | All Water System ROC General | 2025-12-16
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-24
ROC | December | MKRSEM - Called Toronto water(Mehdi) and requested start filling Res. | All Water System ROC General | 2025-12-30
ROC | December | AUW14 - Activated a third well in manual mode to help maintain AURSOH level. | All Water System ROC General | 2025-12-24
ROC | December | HLW1 - Benson S informed well 1 not activating while duty 1 active and pump is set to duty 1. No outstanding alarms preventing well from running. Possible PCS related issue, Benson following up with PCS | All Water System ROC General | 2025-12-17
ROC | December | wrong book | All Water System ROC General | 2025-12-18
ROC | December | AUETAD, AURSOH, NMETIB - Activated Duty 1 | All Water System ROC General | 2025-12-24
ROC | December | BLW12 - Station turbidity fault alarm, Jackie S cleaning turbidity meter. | All Water System ROC General | 2025-12-24
ROC | December | HLW1 - Tim H on site backflushing. Flow control valve flow spike during startup fixed by maintenance team. Tyler Z, Lee F attended site. Tim H requested CMU5 W11539442 ( Tim H). CMU5 W11539450 ( Tyler ZJ) | All Water System ROC General | 2025-12-24
ROC | December | AUW14 - Place well 3 man/on to assist with filling for ARPS pressure loop scenario | All Water System ROC General | 2025-12-17
ROC | December | AURSBS- Jerry Z and WIll M onsite working on chlorine system. He will close AUVCBS Valve for work. | All Water System ROC General | 2025-12-17
ROC | December | STPSMR- Jack P working on chlorine analyzers and health and safety work orders. | All Water System ROC General | 2025-12-17
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-30
ROC | December | AUW14, Placed wells 1/2/3/4 to man/off | All Water System ROC General | 2025-12-31
ROC | December | STPSMR/STRS48, Generator Running Alarm, Contacted Hydro One, talked with David, informed him that we have lost power on site and that our generators are currently running, he will send a hydro one operator to investigate further. Will send an email to the East operations team to inform them of the power outage. Will continue to monitor site | All Water System ROC General | 2025-12-31
ROC | December | NMETIB, Activated D1 | All Water System ROC General | 2025-12-31
ROC | December | VNRSKS- Deactivated D1 MAPS PD7- Placed P1/2 in man/off VNPS PD7 Placed P2/4 in auto NMW136- Influent free Cl2 hihi alarm came in om well start up trends recovered after 3 mins alarm cleared | All Water System ROC General | 2025-12-31
ROC | December | RHRSTR- in preparation to YPFM Trial isolation adjusted Duty 1 start point from 65 to 75%, Duty 1 stop point from 85 to 90%. As per Interim memo. | All Water System ROC General | 2025-12-17
ROC | December | NMETIB - Deactivated duty to help offset with NMETHW, as per shift report NMVCBA - Placed valve back to 40 L/s NMVCIB - Placed valve back to 80 L/s | All Water System ROC General | 2025-12-24
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-24
ROC | December | STETBR - Tower Level Hi alarm came in. Placed STW12 and STW3 back to auto, as per interim procedure | All Water System ROC General | 2025-12-25
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-25
ROC | December | QVW34 - Alex B on site with Jason G to continue inspection of the chlorine gas leak detection system. Alex B requested a CMU5. Created CMU5#W11526577 #CMU5 | All Water System ROC General | 2025-12-18
ROC | December | QVW12, Alex B on site, replacing Silicate injection point | All Water System ROC General | 2025-12-19
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-23
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-23
ROC | December | NMETIB - Deactivated duty 1 while NMETHW fills. | All Water System ROC General | 2025-12-26
ROC | December | MARS - Called Toronto Water (Brett) and requested they return to normal flow (one small pump) to MARS | All Water System ROC General | 2025-12-26
ROC | December | BVPS - Utility power failure. Called Ainsworth for an update on the ETA of their electrician. Ainsworth dispatch informed that they have not be able to contact any of their on call electricians and they have not been dispatched to site yet. Called Satnam to update. | All Water System ROC General | 2025-12-27
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-31
ROC | December | VNRSKS - Swapped supply pumps from MAPS to VNPS to reduce the draw from MARS. | All Water System ROC General | 2025-12-25
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-25
ROC | December | NMETIB - Deactivated duty 1 to offset with NMETHW. NMVCIB- flow set point back from 40L/s to 80L/s NMVCBA- flow set point back from 80L/s- 40L/s | All Water System ROC General | 2025-12-26
ROC | December | YWS + NYWS NORMAL | All Water System ROC General | 2025-12-26
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-21
ROC | December | NMW136 - Combined Chlorine Lo alarm came in. Well has been running for a while. Trends indicate a dip. Level came back to optimal range and alarm has cleared. Will monitor | All Water System ROC General | 2025-12-23
ROC | December | QVW12 - Alex B. working on ammonia and chlorination systems, and calibrating turbidimeter | All Water System ROC General | 2025-12-18
ROC | December | AUW14 - Jerry Z. running generator | All Water System ROC General | 2025-12-18
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-29
ROC | December | ARPS- Pressure fault alarm. Slight dip in trends /recovered, trends look okay, alarm cleared. | All Water System ROC General | 2025-12-23
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-28
ROC | December | HLW1 - Well 1 forward flow HiHi alarm. Checked site, duty recently activated. Well flow is reading high. Contacted Benson S who will check the flow setpoints during his station check. | All Water System ROC General | 2025-12-24
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-26
ROC | December | MARS - Request TO (Andrew) for max flow to help fill res for evening demand | All Water System ROC General | 2025-12-26
ROC | December | NMETHW - Deactivated duty 1 to help offset with NMETIB. NMETIB recently activated. | All Water System ROC General | 2025-12-23
ROC | December | AURSBS - Activated duty 1 05:29 - Activated duty 1 | All Water System ROC General | 2025-12-24
ROC | December | STETBR - Activated duty 1. | All Water System ROC General | 2025-12-26
ROC | December | MKRSEM - Called Toronto Water (Brett) and requested they deactivate the pumps pushing flow to MKRSEM. | All Water System ROC General | 2025-12-27
ROC | December | STW3, Placed man/on STETBR, Activated D1 | All Water System ROC General | 2025-12-29
ROC | December | BLW12, Generator Running alarm, Hydro one says power should be back around 18:00. Will pass this on to Night shift RO | All Water System ROC General | 2025-12-29
ROC | December | NMW12- Jason G testing Cl Leak. | All Water System ROC General | 2025-12-17
ROC | December | STPS48 - Travis W confirmed disregard outlet free chlorine lo | All Water System ROC General | 2025-12-17
ROC | December | Carter D Signing Out | All Water System ROC General | 2025-12-29
ROC | December | Carter Dunn Signing In, -11D/Clear | All Water System ROC General | 2025-12-30
ROC | December | Gluzen Ramos Ong signing out | All Water System ROC General | 2025-12-17
ROC | December | MKRSEM- Called Metro (Zoran)and requested to stop pumps. | All Water System ROC General | 2025-12-18
ROC | December | NMVCIB- Change flow set point from 40L/s to 80L/s NMVCBA- Changed flow set point from 80L/s- 40L/s | All Water System ROC General | 2025-12-18
ROC | December | YWS + NYWS NORMAL | All Water System ROC General | 2025-12-18
ROC | December | STETBR- Deactivated duty STW12- Placed wells in auto STW3- Placed well in auto | All Water System ROC General | 2025-12-18
ROC | December | VNPS, RHRSWA, JFRS - Tim H attending these sites today for station checks and work orders. | All Water System ROC General | 2025-12-18
ROC | December | GWTP - Called Phil D regarding Bisulfite pump 2 N/A outstanding. Disregard as per Phil D NBET27 - Stephen B finished at site | All Water System ROC General | 2025-12-18
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-19
ROC | December | HLPSYS - Pump 4 Fault and Discharge Pressure LoLo alarms came in. Checked site. After 5 mins, fault would not clear and discharge pressure did not go back to normal range. Called Cole W. who will head to site. 02:36 - Discharge pressure started to increase and fault on pump 4 cleared. Called Cole W. who will no longer head to site but would like a call back if the pump faults again. #CONSULT | All Water System ROC General | 2025-12-19
ROC | December | AUW57 - Deactivated well and left in manual mode AUW14 - Deactivated well pumps 1 and 4, and placed all wells in auto mode. | All Water System ROC General | 2025-12-24
ROC | December | STW12, STW3- Placed in manual on YWS + NYWS Normal Connor Smith signing out. | All Water System ROC General | 2025-12-22
ROC | December | BVPS - Deactivated duty 1 | All Water System ROC General | 2025-12-24
ROC | December | NBW3 - Influent free chlorine lolo lockout. Tim H will attend site. | All Water System ROC General | 2025-12-29
ROC | December | VNRSKS- Deactivated D1 | All Water System ROC General | 2025-12-22
ROC | December | KSTP - Fin water flouride res fault, lolo res on flouride, & Fin water tot CL2 res fault. Informed Dan Z. Rotated flouride pump 1 to duty 1 as per Dan Z. Consult | All Water System ROC General | 2025-12-26
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-26
ROC | December | Christian Van Beek signing in. Weather: -6C and clear. | All Water System ROC General | 2025-12-26
ROC | December | KSTP - Fin water flouride res lolo, flouride res fault. Flouride pump 1 running. Reading came back up within normal range shortly. | All Water System ROC General | 2025-12-29
ROC | December | AUW14 - Place wells back in auto | All Water System ROC General | 2025-12-29
ROC | December | Adam Button signing out | All Water System ROC General | 2025-12-31
ROC | December | NMETIB- Deactivated duty | All Water System ROC General | 2025-12-23
ROC | December | AUETFC- AUETFC to AUPSWS/ANVCPL comm alarms came in cleared trends okay | All Water System ROC General | 2025-12-22
ROC | December | MAP8 - Kyle R finished at site. Place pumps back in auto | All Water System ROC General | 2025-12-17
ROC | December | NMMCAD + NMMCBR - PAC Comm Fail, since 12:27. Notified Yash S. | All Water System ROC General | 2025-12-18
ROC | December | SHTP - Well pump 2 uncommanded start alarm. Checked site, well pump 2 is faulted. Well pump 3 is active in duty 1. Able to reset the alarm. | All Water System ROC General | 2025-12-26
ROC | December | Stouffville - Rob P called to inform they are opening final connection valve to new line for the Stouffville Zone 1 600mm watermain along Stouffville Road, east of McCowan. This will go into ZOne 2 pumping station. | All Water System ROC General | 2025-12-27
ROC | December | MARS - Request TO (Andrew) to go back to regular flow VNRSKS - Revert changes and put MAP7 pumps 1 & 2 back in auto and VNP7 pumps man/off | All Water System ROC General | 2025-12-27
ROC | December | GWTP - chlorine pump 2 not available alarm. Patrick F working on it. | All Water System ROC General | 2025-12-23
ROC | December | GWTP - Make up air unit 1 coil low temperature alarm. Checked site, unable to locate details of this MUA. Alarm level is critical. Called Dan Z who directed to disregard. #consult | All Water System ROC General | 2025-12-25
ROC | December | Angelica Chepiga signing out | All Water System ROC General | 2025-12-30
ROC | December | HLETPR - Benson S and Stephen B finished and leaving site. | All Water System ROC General | 2025-12-18
ROC | December | MKRSEM - Toronto Water (Paul) called to state that they will be curtailing from 16:00 - 20:00 this evening. Paul requested that one pump be activated for COTFA PD5 to maintain the level at MKRSEM. Paul will need one pump running during the curtailment period. | All Water System ROC General | 2025-12-18
ROC | December | MKRSEM - Called Toronto Water (Mehdi) and requested to stop pumping to reservoir | All Water System ROC General | 2025-12-19
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-29
ROC | December | QVW12, Donald M is requesting both Electrical and mechanical to head to site as Well 1 continues to fail. Contacted both Satnam M and Chris I and informed them of the QVW12 issues. They will both head to site CMU5: W11546794 (Satman) CMU5: W11546802 (Chris) | All Water System ROC General | 2025-12-29
ROC | December | MKRSEM- Called Metro (Medhi)and requested to stop pumps. | All Water System ROC General | 2025-12-17
ROC | December | NMW136 - Combine chlorine low alarm. Quick drop. Value recovered in two readings, alarm cleared. | All Water System ROC General | 2025-12-17
ROC | December | YWS + NYWS NORMAL | All Water System ROC General | 2025-12-18
ROC | December | MTW3- Jackie S onsite working on silicate system. | All Water System ROC General | 2025-12-23
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-23
ROC | December | NBW3 - Influent free chlorine lolo alarm. Checked site, well recently activated. Trending shows a sudden drop of the influent free chlorine reading which interlocked the well. This dip recovered within none reading interval. Rotated the chlorine dosing pump and cleared alarms. Monitored well activation. | All Water System ROC General | 2025-12-25
ROC | December | STW12 - Place well 1 back in auto STW3 - Place well back in auto | All Water System ROC General | 2025-12-19
ROC | December | AUW14 - Place wells back in auto AURSBS - Activate duty 1 | All Water System ROC General | 2025-12-20
ROC | December | RHMCMD, Placed valve man/open | All Water System ROC General | 2025-12-20
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-20
ROC | December | Begin Maple to JFRS feed BVPS - Deactivate duty 1 | All Water System ROC General | 2025-12-21
ROC | December | VNPS PD8- Proc Sump P1/2 Fault PD7 P1/2 Soft starter faults came in interlocking pumps. Not able to reset alarms. Called Jason G. No answer. will try again in 15 mins MAPS PD8- P4 VFD not ready alarm came in not able to reset Placed in man/off emailed West water team NMW12- Combined CL2 lo alarm came in. Well not active no water directed to users. Will clear when residual improves 7:43- VNPS- Jay called back and will attend site to reset alarms. Created CMU5 W11529377 #CMU5 | All Water System ROC General | 2025-12-21
ROC | December | YWS + NYWS Normal Connor Smith signing out | All Water System ROC General | 2025-12-23
ROC | December | GWTP - Backpulse tank fill V failed to open alarm. Valve on man/off. OP on site. 10:48 Patrick F requested disregard Backpulse tank level Hi alarm, he is on site working on it. | All Water System ROC General | 2025-12-29
ROC | December | MAP7 - Man/start pump 1 to help drawdown MARS | All Water System ROC General | 2025-12-21
ROC | December | AUW57- Combined CL2 lo alarm came in on well start up. Will continue to monitor as OPS are running well in manual fro sampling MARS- Called Metro and spoke with Andrew to increase flow to reservoir | All Water System ROC General | 2025-12-22
ROC | December | STRS48 - Chlorinator 2 failed to close alarm, OP remotely worked on Booster pump 2, alarm back to normal/cleared | All Water System ROC General | 2025-12-23
ROC | December | MTW12- MTW12 to MTETNL Comm alarm. Trends okay reset alarms | All Water System ROC General | 2025-12-16
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-25
ROC | December | AUW57, Combined Cl2 lolo, Donald M was running the well in manual and then the combined residual dipped, notified him that the well is now interlocked and that that it didn't clear the contact tank. Once Donald M is at QVW12, he will look into it further but until then, he will leave it off for the night consult | All Water System ROC General | 2025-12-28
ROC | December | YWS + NWYS Normal | All Water System ROC General | 2025-12-28
ROC | December | AUW14, Placed wells 2/4 in man/off so the wells dont start up. This will allow more water to me taken from AURSBS AURSOH, activated D1 | All Water System ROC General | 2025-12-22
ROC | December | MARS, Notified Toronto operator Peter to drop the flow down to minimal as MARS is getting pretty full and all the down stream storages are full | All Water System ROC General | 2025-12-22
ROC | December | AUETOH, Activated D1 | All Water System ROC General | 2025-12-22
ROC | December | VNRSKS, Deactivated D1 | All Water System ROC General | 2025-12-22
ROC | December | Ethan Ullalkar signing out. | All Water System ROC General | 2025-12-29
ROC | December | KSTP, Raw Water Turbidity Fault//Cl2 Emerg Vlv Closure sys Fault, Ryan B on site | All Water System ROC General | 2025-12-29
ROC | December | KSTP- Fin water fluoride res hi alarm came in. On high lift start up but slowly coming back down. Notified Jerry Z will check SCADA | All Water System ROC General | 2025-12-31
ROC | December | GWTP - Backpulse valve failed to open alarm. Checked site, backpulse valve in auto and closed. Able to reset alarm. Monitored site, Backpulse valve 1 opened and closed normal. | All Water System ROC General | 2025-12-25
ROC | December | STW3- Dan Z notified ROC that instrumentation is on site for chlorinator rebuild. Directed to place in man/off. STETBR- Deactivated D1 | All Water System ROC General | 2025-12-22
ROC | December | Ethan Ullalkar signing out. | All Water System ROC General | 2025-12-21
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-19
ROC | December | NMW136, Station Turbidity Hi Alarm, Rotated Silicate pumps so silicate pump 1 is in D2 and silicate pump 2 is in D1 | All Water System ROC General | 2025-12-20
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-19
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-19
ROC | December | Adeela Khan signing out | All Water System ROC General | 2025-12-25
ROC | December | AUETFC - Deactivated duty 1. AUETOH - Deactivated duty 1. NMETIB - Deactivated duty 1. | All Water System ROC General | 2025-12-24
ROC | December | MARS- Called Toronto (Brett) and requested back to normal flow. | All Water System ROC General | 2025-12-17
ROC | December | GWTP- Sutton header fluoride lo alarm came in. SUETDR not active. Notified Patrick F. Will be activated Sutton duty soon which will clear alarm and improve residual | All Water System ROC General | 2025-12-22
ROC | December | STW3- Phil D and Patrick F onsite for cylinder change and chlorine system work. Disregard related alarms. | All Water System ROC General | 2025-12-23
ROC | December | HLPSYS, Benson S/Stephen B on site testing the fire pump | All Water System ROC General | 2025-12-19
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-21
ROC | December | MKRSEM - Request TO (Peter) to drop 2 pumps | All Water System ROC General | 2025-12-21
ROC | December | KCETDS - Activate duty 1 to help with MARS approaching hi level and pull move water as ARPS pressure PIT not triggering off as pressure not exceeding the stop threshold even at hi level | All Water System ROC General | 2025-12-21
ROC | December | VNRSKS - Place pump 1 back in auto AUW14 - Place wells back in auto | All Water System ROC General | 2025-12-21
ROC | December | RHMCMD- Placed back in auto VNRSKS- Deactivated D1 VNPS PD7- Placed P2 in man/on MARS- Called Metro and spoke with Zorhan to increase flow to reservoir | All Water System ROC General | 2025-12-21
ROC | December | Adam Button signing out | All Water System ROC General | 2025-12-21
ROC | December | AURSBS- Activated D1 | All Water System ROC General | 2025-12-22
ROC | December | MARS - Called Toronto Water (Zoran) and requested normal flows | All Water System ROC General | 2025-12-19
ROC | December | Carter Dunn Signing Out | All Water System ROC General | 2025-12-22
ROC | December | Adam Button signing in | All Water System ROC General | 2025-12-22
ROC | December | VNPS- Placed PD7 Pumps man/off MAPS- Placed PD7 pumps in auto | All Water System ROC General | 2025-12-22
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-24
ROC | December | AUW14 - Influent Free Chlorine Lo alarm came in. Checked site. Wells have been running for a while. Checked trends. Looks like a dip and level recovered within 10 mins. Alarm has cleared | All Water System ROC General | 2025-12-24
ROC | December | RHMCMD - Placed valve back to man/open | All Water System ROC General | 2025-12-25
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-25
ROC | December | Angelica Chepiga signing out | All Water System ROC General | 2025-12-23
ROC | December | MAPS - Tyler CS working on generator. Disregard generator alarms for the duration of the work. | All Water System ROC General | 2025-12-24
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-20
ROC | December | MKRSEM - Request TO (Peter) to drop 2 pumps | All Water System ROC General | 2025-12-20
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-20
ROC | December | MAPS PD7, Placed pumps 1/3 man/off as they are D1 pumps VNPS PD7, Placed pumps 2/3 in auto as they are D1 pumps | All Water System ROC General | 2025-12-20
ROC | December | Carter Dunn Signing Out | All Water System ROC General | 2025-12-20
ROC | December | RHMCMD - to auto. | All Water System ROC General | 2025-12-18
ROC | December | NMW136, Changed Cl2 dosing factor from chlorinator 2 from 78 to 75% | All Water System ROC General | 2025-12-29
ROC | December | VNPS PD8- Jordan B finished work. Placed pumps back into auto. VNPS PD8- Placed pumps back into auto. Pump 1 failed on Uncommanded Stop. Placed pump in manual and assigned pump 2 into duty 1. Notified Jordan B. | All Water System ROC General | 2025-12-17
ROC | December | QVW12- Generator Running Status, Gas Scrubber Overload Alarm. Notified Alex B. She will look into it. | All Water System ROC General | 2025-12-22
ROC | December | GWTP- Patrick F onsite will be commissioning new High Lift Pump number 4. Can disregard related alarms. | All Water System ROC General | 2025-12-16
ROC | December | STW12 - Dan Z requested pumps man/off. Can run if needed. | All Water System ROC General | 2025-12-30
ROC | December | MMW1- Power fail on site. Manually started P8/13 cleared alarms | All Water System ROC General | 2025-12-31
ROC | December | QVW34 - Parth P and Rick L headed to site to work on a chlorine gas sensor. | All Water System ROC General | 2025-12-19
ROC | December | NBET27- Parth P finished onsite. | All Water System ROC General | 2025-12-16
ROC | December | KSETWB- Eductor 1 Water Valve Failed to Open, Gas Valve Failed to Open, Cross Chlorination Vlv Failed to Open, Tower Inlet Chlor Vlv Failed to Opn. Alarms cleared. | All Water System ROC General | 2025-12-22
ROC | December | MKETFA - Parth P finished on site. | All Water System ROC General | 2025-12-23
ROC | December | VNRSKS - Deactivated duty 1 AURSBS - Deactivated duty 1 | All Water System ROC General | 2025-12-18
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-18
ROC | December | QVW12 - Tyler ZJ working on well 1 pump VFD. | All Water System ROC General | 2025-12-30
ROC | December | NBW3 - P7 interlocked influent free chlorine Low alarm. Tim H restarting P7 remotely and monitoring. | All Water System ROC General | 2025-12-30
ROC | December | NMVCIB, Placed valve in manual and at 40L/sec | All Water System ROC General | 2025-12-30
ROC | December | QVW34- Ric L onsite for calibrations. Jerry Z placed wells man/off AURSBS- Jerry Z going to site to work on Post Inj Ammonia analyzer | All Water System ROC General | 2025-12-31
ROC | December | AURSBS - Activated duty 1 | All Water System ROC General | 2025-12-23
ROC | December | VNRSKS, Activated D1 | All Water System ROC General | 2025-12-28
ROC | December | KCETDS - Tower level low alarm. Notified Jordan B, he is heading to site. Tim H also will attend site. | All Water System ROC General | 2025-12-29
ROC | December | Angelica Chepiga signing in | All Water System ROC General | 2025-12-30
ROC | December | KLMCIA - Dwayne L requested a CMU5 for Gary Peters regarding his attending site for the meter chamber flood alarm last night. Created CMU5#W11528868. #CMU5 | All Water System ROC General | 2025-12-19
ROC | December | JFPS - Tyler ZJ on site and will be manipulating pumps for maintenance and inspections. | All Water System ROC General | 2025-12-19
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-20
ROC | December | MAPS PD7- Placed P1-4 in man/off VNPS PD7- Placed P3 in man/on AUW14- Placed P2/4 in man/on and manually started P1 | All Water System ROC General | 2025-12-21
ROC | December | HLW1- Forward flow hihi alarm came in. Flow returned to normal and alarm cleared after 2 mins. | All Water System ROC General | 2025-12-21
ROC | December | BVPS - Called back Ainsworth after hours (Shane). Still no ETA for their on-call, and still unable to get a hold of their contact. Confirmed no further action has been taken on their side in escalating further. They will call back when they are able to get a hold of someone 6:50 - Satnam M confirmed he received text from Ainsworth. They are sending a supervisor as on-call was non responsive. Will continue to monitor site | All Water System ROC General | 2025-12-27
ROC | December | AUPSRR- Post injection free Cl2 hihi and Post injection combined lolo alarm came in both trends recovered after 3 mins alarm cleared VNPS PD7- placed P2/3 back in man/off MAPS PD7- Placed P1-4 in auto AUW14- Placed wells 2,3,4 back in auto | All Water System ROC General | 2025-12-21
ROC | December | SHTP- Reservoir total Cl2 lo alarm came in. Notified Dave T. Dave T switched cell and drop was expected and should recover within the hour | All Water System ROC General | 2025-12-22
ROC | December | GWTP - ZW1 Not all devices in auto mode. Checked site, train 1 is going through an MIT process. Backpulse valve not in auto. Changes likely made by area ops. Will monitor site. | All Water System ROC General | 2025-12-18
ROC | December | STETBR - Dan Z deep cycling ET to 40%, placed STPSTL pumps man/off. | All Water System ROC General | 2025-12-30
ROC | December | QVW34 - Chlorine leak, chlorinators N/A, CL2 emergency closure. Followed up with Jason G, disregard for the night as known issue with these chlorinators at site. Leak cleared AURSBS - Activate duty 1 to drawdown MARS hi level | All Water System ROC General | 2025-12-17
ROC | December | Carter Dunn Signing In, -1D/Clear | All Water System ROC General | 2025-12-22
ROC | December | GWTP - Backpulse tank fill valve failed to open alarm. Checked site, backpulse valve is closed and in auto. Able to clear alarm. Monitored site. | All Water System ROC General | 2025-12-25
ROC | December | YWS + NYWS NORMAL | All Water System ROC General | 2025-12-25
ROC | December | KCETDS - Activated D1. | All Water System ROC General | 2025-12-26
ROC | December | GWTP - Backpulse tank fill V failed to open will be outstanding for the weekend as left man/close. Informed by Dan Z STW12 - Hypo tank will not be receiving delivery and due to this leaving well 1 man/off until delivery in the New year. Will not be running either well to assist filling zone 1 as requested by Dan Z due to this too | All Water System ROC General | 2025-12-26
ROC | December | Carter Dunn Signing Out | All Water System ROC General | 2025-12-28
ROC | December | Carter Dunn Signing Out | All Water System ROC General | 2025-12-23
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-27
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-28
ROC | December | NMW136- Combined Cl2 lo alarm came in. Slight dip in trends but recovered after 3 minas alarm cleared | All Water System ROC General | 2025-12-30
ROC | December | AURSBS - Deactivate duty 1 | All Water System ROC General | 2025-12-17
ROC | December | GWTP - ZW1 train 1 shutdown. Backpulse inlet V fail to open. Informed Phil D. Leaving train 1 off for the night Consult | All Water System ROC General | 2025-12-17
ROC | December | AURSBS - Chlorine GCLR 1 Alv fail to open alarm at duty stop. Cleared alarm. | All Water System ROC General | 2025-12-18
ROC | December | KCETDS - Activated duty 1. | All Water System ROC General | 2025-12-28
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-26
ROC | December | AUW14 - Placed two pumps manual/on to slow the drawdown of AURSOH. | All Water System ROC General | 2025-12-25
ROC | December | MARS - High level alarm. Activated MAPS PD8 pumps. RHRSTR - Deactivated Duty 1. | All Water System ROC General | 2025-12-26
ROC | December | ARPS- Cristina S called and requested ARPS start pumping in pressure mode. Called Peel (Jerry). He will start system in pressure mode once confirmed with his Team. 13:46- Jerry from Peel called back and will start one pump in pressure mode. | All Water System ROC General | 2025-12-17
ROC | December | Carter D Signing In, -4D/Clear | All Water System ROC General | 2025-12-21
ROC | December | MARS, Notified Toronto operator peter to decrease the flow to MARS | All Water System ROC General | 2025-12-21
ROC | December | HLW1, Treated Free Cl2 hi Alarm, Rotated ammonia pumps so Ammonia pump 2 is in D1 and ammonia pump 1 is in D2 21:04, Contacted Cole W as the Free Cl2 hasn't recovered, directed to change the ammonia ratio dosage from 5.4 to 4.9. if nothing changes within 30 minutes and the residual remains hi, Cole W would like another call 21:57, contacted Cole W as directed, notified him that the ammonia is still running hi on both the treated and the effluent analyzers, directed to drop the ammonia ratio dosage from 4.9 to 4.2 and rotate the ammonia pumps so that ammonia pump 1 is back in D1. In 20 minutes he would like another call just to verify that everything is dropping 22:20, Notified Cole W as per his request at the 20 minute mark, notified him that the free is still on the higher side but has dropped. The effluent is still holding at the same residual, directed to drop the ammonia ratio from 4.2 to 4.0. if the lo or hi alarm comes in, he would like a call consult | All Water System ROC General | 2025-12-21
ROC | December | Ethan U signing in Weather -6. | All Water System ROC General | 2025-12-26
ROC | December | AURSBS - Activated duty 1. | All Water System ROC General | 2025-12-28
ROC | December | RHMCMD - Closed valve to 0% | All Water System ROC General | 2025-12-28
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-28
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-27
ROC | December | AUW14 - Placed wells in manual and deactivated the running wells to increase demand on AURSBS and by extension MARS. | All Water System ROC General | 2025-12-28
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-28
ROC | December | NMVCIB, Placed valve in manual and changed the flow set point to 40L/sec | All Water System ROC General | 2025-12-28
ROC | December | GWTP- ZW2 Memb tank level hi alarm came in. Continued to monitor recovered and cleared on its own after acknowledgment. | All Water System ROC General | 2025-12-22
ROC | December | QVW12 - Effluent free chlorine hi, reduce chlorine dosing from 117 to 114 | All Water System ROC General | 2025-12-27
ROC | December | MKRSEM - Called Toronto Water (Brett) and requested they activate two pumps to push flow to MKRSEM. | All Water System ROC General | 2025-12-27
ROC | December | MAPS/AURSBS/JFRS - Initiating changes for Maple to Jefferson Feed. | All Water System ROC General | 2025-12-28
ROC | December | VNRSKS - Swapped supply pumps from MAPS to VNPS for next fill cycle. | All Water System ROC General | 2025-12-28
ROC | December | RHMCMD - back to auto | All Water System ROC General | 2025-12-17
ROC | December | Ethan U signing in | All Water System ROC General | 2025-12-17
ROC | December | NMW15- Jason G and Lee F onsite. Lee turned off power to well and Jason G doing work orders including maintenance on all analyzers. Disregard all alarms while onsite. | All Water System ROC General | 2025-12-17
ROC | December | QVW34 - Chlorine room gas leak. Known issue with site, disregard for the night as per shift report. Team will further look into issue tomorrow | All Water System ROC General | 2025-12-17
ROC | December | BVPS - Generator running alarm and Utility power failure alarm. Checked site, generator is running and pumps have shut down. Checked ALectra Outage map, no outage in the area on map. Will monitor site. | All Water System ROC General | 2025-12-27
ROC | December | QVW12 - Well 1 FVD fault, pump VFD not ready, informed Donald M. Okay to run well 2 in duty 1 for weekend. Place well 1 man/off. Consult BVPS - Pump 2 will remain OOS. Rotated pump 1 & 3 duty 1 | All Water System ROC General | 2025-12-27
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-27
ROC | December | GWTP- Patrick F called. He is leaving site. Bisulfite alarms, and ZW7 M Clean Exceeded duration alarm can be disregarded for the night. | All Water System ROC General | 2025-12-16
ROC | December | QVW12- Influent Free Chlorine HiHi Alarm. Value recovered. Cleared alarm. | All Water System ROC General | 2025-12-16
ROC | December | STW2/3, Placed Wells 2/3 in man/on for Stephen B | All Water System ROC General | 2025-12-29
ROC | December | MAPS PD7, Placed pump 1 man/off VNPS PD7, Placed pump 2 in auto | All Water System ROC General | 2025-12-29
ROC | December | ARPS- Pressure fault alarm followed by pump shutdown. Called Peel spoke with David who will investigate | All Water System ROC General | 2025-12-30
ROC | December | VNRSKS - Activated duty 1 to maintain MARS level. | All Water System ROC General | 2025-12-17
ROC | December | Angelica Chepiga signing out | All Water System ROC General | 2025-12-17
ROC | December | BLW3 - Dan Z called to inform that BLW3 will be manual/off all day for contractor work. | All Water System ROC General | 2025-12-19
ROC | December | MKPSSA - Man/stop pump 3 | All Water System ROC General | 2025-12-20
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-20
ROC | December | STW12 - Place well 1 back in auto STW3 - Place well back in auto MKRSEM - Request TO (Peter) to run 2 pumps | All Water System ROC General | 2025-12-20
ROC | December | YWS + NYWS NORMAL | All Water System ROC General | 2025-12-26
ROC | December | MAPS/JFRS/AURSBS - Reverting Maple to Jefferson Feed. | All Water System ROC General | 2025-12-28
ROC | December | VNPS PD7, Placed pump 2 man/off MAPS PD7, Placed pump 2 in auto | All Water System ROC General | 2025-12-28
ROC | December | STW3, Placed well man/on | All Water System ROC General | 2025-12-28
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-21
ROC | December | RHMCMD, Placed valve in man/open RHRSTR, Deactivated D! to help move water over from MARS to RHRSTR | All Water System ROC General | 2025-12-21
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-26
ROC | December | MAPS PD8 - Pump 1 VFD fault. Sean P and ABB contractor on site. Sean P called to inform that the ABB contractor would like to inspect the pump before testing. Placed pump manual/off. Monitored system activation following pump fault. | All Water System ROC General | 2025-12-19
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-29
ROC | December | NMETIB- Joe D requested to activate duty NMETHW- Joe D requested to deactivated duty | All Water System ROC General | 2025-12-16
ROC | December | STETBR - Tower level Hi alarm. Placed STW12, STW3 back to auto. | All Water System ROC General | 2025-12-17
ROC | December | MARS - Hi level, deactivated RHRSTR duty and placed RHMCMD man/open. | All Water System ROC General | 2025-12-17
ROC | December | MAPS PD8 - Sean P on site with an ABB contractor to work on the VFD for pump 4. Sean also requested that pump 1 be placed in duty 1 auto mode for testing. | All Water System ROC General | 2025-12-19
ROC | December | YWS + NYWS Normal Christian Van Beek signing out. | All Water System ROC General | 2025-12-19
ROC | December | QVW12 - Forward flow hihi. Flow increased to hihi shortly before coming down. Rotated Well 1 to duty 1 Well 1 - VFD fault. Occurred earlier this weekend. Placed man/off, rotated well 2 back to duty 1 and informed Donald M of both issues with flow hihi and VFD fault. Consult | All Water System ROC General | 2025-12-28
ROC | December | MAPS- Placed PD7 Pumps in manual/off VNPS- Placed PD7 duty 1 pumps in auto | All Water System ROC General | 2025-12-23
ROC | December | GWTP- ZW7- CIP feed inlet v failed to open and CIp feed flow lo alarms came in. Notified Dan Z will check on SCADA | All Water System ROC General | 2025-12-30
ROC | December | YWS + NYWS NORMAL | All Water System ROC General | 2025-12-18
ROC | December | QVW34- Alex B onsite working on silicate system. Wells are man/off | All Water System ROC General | 2025-12-17
ROC | December | RHRSTR, Activated D1 | All Water System ROC General | 2025-12-19
ROC | December | KCETDS- Historian Heartbeat alarm came in. Trends flatlined. Called Ron V. To inquire of PCS on-call as schedule is not currently available. Ron V will reach out to Matt S. and Notify ROC who to contact 13:34- KCETDS- Matt S Notified ROC that Ian W is on call. Called Ian W. Will check SCADA. Created CMU5 W11551733 AURSBS- Cl2 isolation valve 1 failed to open alarm came in. AURSOH not active and outlet valve at reservoir is slowly closing. Chem system not active. Reset alarm #CMU5 | All Water System ROC General | 2025-12-31
ROC | December | GWTP - Train 7 shutdown. Followed up with Phil D. Looking into issue | All Water System ROC General | 2025-12-17
ROC | December | STRS48 - Sample pump 1 fault. Sample pump 2 running in duty 1. Cross referencing previous reports on this alarm, okay to leave sample pump 2 duty 1. Emailed oncall operator | All Water System ROC General | 2025-12-21
ROC | December | MARS- Called Toronto (Andrew) and requested small pump on. Interim Procedure | All Water System ROC General | 2025-12-22
ROC | December | AUW14, Placed well 3 man/on to help slow down the draining from AURSOH AUETOH, Deactivated D1 | All Water System ROC General | 2025-12-22
ROC | December | KSTKWP- Gas chlorinator 1 failed to close alarm came in again. Notified Ryan B. Placed in man/off and notified Phil D about changes | All Water System ROC General | 2025-12-22
ROC | December | STW3 - Arthur L working on the OIT. Arthur directed to disregard the historian heartbeat alarm. | All Water System ROC General | 2025-12-16
ROC | December | AUPSRR - post-injection free chlorine HiHi alarm. Quick spike, value back to normal/cleared alarm. Duty activated recently. | All Water System ROC General | 2025-12-24
ROC | December | GWTP - Train 1 & 5 shutdown. Reset trains as per Phil D Consult | All Water System ROC General | 2025-12-17
ROC | December | NRETCR - Deactivated D1. | All Water System ROC General | 2025-12-17
ROC | December | YWS + NYWS NORMAL | All Water System ROC General | 2025-12-17
ROC | December | NMVCIB, Placed back to auto | All Water System ROC General | 2025-12-22
ROC | December | AURSBS, Activated D1 | All Water System ROC General | 2025-12-22
ROC | December | NRETCR, Activated D1, once enough water has been taken from JFRS and sent to NRETCR, RO will activate D1 at JFRS so it can start taking water from RHRSTR which will help more flow go from MARS to RHRSTR through the RHMCMD. | All Water System ROC General | 2025-12-22
ROC | December | VNRSKS, Activated D1 | All Water System ROC General | 2025-12-22
ROC | December | MKRSEM, Notified Toronto operator Peter to turn off the pumps at the res | All Water System ROC General | 2025-12-22
ROC | December | GWTP - Backpulse valve failed to open alarm. Checked site, backpulse valve showing auto and closed. Able to reset alarm. | All Water System ROC General | 2025-12-25
ROC | December | BVPS, Activated D1 | All Water System ROC General | 2025-12-22
ROC | December | QVW34 - Influent free chlorine hi, dropped chlorinator 2 dosing from 93 to 90 RHMCMD - Man/close valve | All Water System ROC General | 2025-12-18
ROC | December | STETBR - Tower Level Hi alarm came in. Placed STW12 and STW3 back to auto, as per interim | All Water System ROC General | 2025-12-19
ROC | December | MAP8 - Kyle R onsite requesting to run pump 2 ot test run after working on pump. Placed pumps 1,3,4 man/off to prevent activity when duty starts. Man/start pump 2 | All Water System ROC General | 2025-12-17
ROC | December | MKRSEM - Jackie S on site to complete work orders including hi/low level alarm test, chlorine analyzer maintenance and JHSC checks. MARS /MAPS - Joe W on site for JHSC checks and to test the diesel flood alarm. | All Water System ROC General | 2025-12-18
ROC | December | KSTP - CO2 adjusted pH LoLo alarm. Checked site the plant is active. The low lift pumps are interlocked due to the pH LoLo alarm and the filters are active which is rapidly drawing down the conduit level. The high lift pumps are interlocked due to a filter backwash. Called Dan Z who will check SCADA. #consult | All Water System ROC General | 2025-12-25
ROC | December | MARS, Notified Toronto operator Brent to go back to the low flow he was originally providing to MARS since ARPS has fixed their issue | All Water System ROC General | 2025-12-22
ROC | December | AUW14, Placed wells 2/4 man/off | All Water System ROC General | 2025-12-23
ROC | December | STW12/3, Placed wells 1/2/3 back to auto | All Water System ROC General | 2025-12-23
ROC | December | SHTP/SHETCS, System Power Outage, notified Cole W, He will look into it in the morning when he heads in consult | All Water System ROC General | 2025-12-23
ROC | December | MARS - Called Metro(Zoran) and requested to reduce flow. | All Water System ROC General | 2025-12-18
ROC | December | HLW2 - Treated total and combine chlorine Lo alarms, Site is offline. | All Water System ROC General | 2025-12-18
ROC | December | Connor Smith signing in | All Water System ROC General | 2025-12-18
ROC | December | MTW12 - Silicate pumps 1&2 OOS, Jackie S working on site. | All Water System ROC General | 2025-12-29
ROC | December | AN23 - Kingsley M completing OIT work. May see a historian heartbeat alarm. | All Water System ROC General | 2025-12-18
ROC | December | STPSTL - Diesel tank 1 vacuum, notified Travis W. 11:52 - Travis W. talked to Tyler Z.J., they are aware and will address in future. Confirmed the generator is able to run normally. Will disregard but leave alarm outstanding. | All Water System ROC General | 2025-12-18
ROC | December | YWS + NYWS NORMAL | All Water System ROC General | 2025-12-24
ROC | December | NMVCIB- Change flow set point from 80L/s to 40L/s NMVCBA- Changed flow set point from 40L/s- 80L/s | All Water System ROC General | 2025-12-24
ROC | December | Ethan U signing in Weather -9. | All Water System ROC General | 2025-12-29
ROC | December | VNP7 - Place pump 2 & 3 man/off MAP7 - Place pump 1-4 back on auto | All Water System ROC General | 2025-12-29
ROC | December | Connor Smith signing in -12C Windy | All Water System ROC General | 2025-12-30
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-25
ROC | December | RHMCMD - Closed valve to 50% open to help MARS level recover. | All Water System ROC General | 2025-12-25
ROC | December | MKRSEM - Request TO (Andrew) to drop 1 pump | All Water System ROC General | 2025-12-26
ROC | December | 19:48 - MKRSEM - Reservoir Lo level came in. Toronto Water is currently undergoing energy curtailment until 20:00. 20:02 - MKRSEM - Called Toronto Water (Zoran) and requested two pumps on. Zoran informed that energy curtailment is still happening and will place 2 pumps on within 10 mins 20:02 - MARS - Lo levels. Spoke to Zoran who informed he will increase to normal levels within 10 mins. | All Water System ROC General | 2025-12-18
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-30
ROC | December | Gluzen Ramos Ong signing in STPSMR - Jack P. testing chlorine leak | All Water System ROC General | 2025-12-17
ROC | December | YWS + NYWS Normal | All Water System ROC General | 2025-12-17
ROC | December | Connor Smith signing in -5C Snowy | All Water System ROC General | 2025-12-31
ROC | December | Carter Dunn Signing Out | All Water System ROC General | 2025-12-31
ROC | December | Adam Button signing in AUW14- Placed wells back in auto | All Water System ROC General | 2025-12-31
ROC | December | AURSBS - Activated D1 to maintain MARS level. | All Water System ROC General | 2025-12-30
ROC | December | RHRSTR, Deactivated D1 RHMCMD, Placed valve man/open | All Water System ROC General | 2025-12-31
ROC | December | AURSBS, Activated D1 | All Water System ROC General | 2025-12-31
ROC | December | NMW15 - Influent Free Chlorine low alarm came in. Checked site. Levels came back to optimal range after 5 mins and alarm has cleared | All Water System ROC General | 2025-12-31
ROC | December | Adam Button signing in snowing -10 | All Wastewater System ROC General | 2025-12-13
ROC | December | HLETYS- ammonia pump 1/2 failed to start alarm came in reset alarms. Likely due to not enough flow to allow chemical system to dose appropriately. Notified Jordan as the alarm came back in after 2 resets. Directed to increase flow at HLW2 valve chamber from 40 to 45L/s to see if extra flow will be able to correct dosing issues. **WRONG BOOK ** | All Wastewater System ROC General | 2025-12-13
ROC | December | Ethan Ullalkar signing out. | All Wastewater System ROC General | 2025-12-11
ROC | December | RHAMF1- Phil R notified ROC that Kyle C and contractors will be working on site and to disregard alarms until done | All Wastewater System ROC General | 2025-12-12
ROC | December | Adeela Khan signing out | All Wastewater System ROC General | 2025-12-11
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-10
ROC | December | HMSS- Frank I. from Peel called inquiring about the levels at HMSS due to some OCP probe issues at the OCF on Peels side. Notified Frank that there have been no abnormal trends observed on site. Adam Button signing out | All Wastewater System ROC General | 2025-12-10
ROC | December | Christian Van Beek signing out. | All Wastewater System ROC General | 2025-12-10
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-14
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-12
ROC | December | Connor Smith signing out | All Wastewater System ROC General | 2025-12-11
ROC | December | YDSS + YNSS Normal Connor Smith signing out | All Wastewater System ROC General | 2025-12-10
ROC | December | Connor Smith signing in 0C Snowy | All Wastewater System ROC General | 2025-12-10
ROC | December | Adam Button signing out | All Wastewater System ROC General | 2025-12-11
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-11
ROC | December | NMSSBP- P4 vibration hi alarm came in. Disregard on shift report | All Wastewater System ROC General | 2025-12-13
ROC | December | KSSP - Aeriation tank 1 inlet DO fault. Appears drop in reading for a moment causing fault. Analyzer reading came back within range right away | All Wastewater System ROC General | 2025-12-11
ROC | December | KCSSKR- Young J on site for generator run, eye wash test and diesel containment flood alarm test | All Wastewater System ROC General | 2025-12-10
ROC | December | RHAMF - Jamie from NAC called to request a reset of the MAU pump. Ack/reset as per Gluzen R. | All Wastewater System ROC General | 2025-12-11
ROC | December | KBSP- Filter sluice gate 2 failed to open alarm came in. Notified Marcus R. Will take a look on SCADA 14:06- KBSP- Marcus R called back and was able to reset alarm an exercise gate. Directed to ack reset if it comes back in #consult | All Wastewater System ROC General | 2025-12-13
ROC | December | Carter D Signing out | All Wastewater System ROC General | 2025-12-13
ROC | December | RHAMF1 - Makeup Air Unit Failed to start alarm came in multiple times. Checked site. Looks like someone is on site. Called Terry R. but no response. Will try again 08:32 - Unit 1 Differential Pressure 2 HiHI alarm came in. Spoke to Phil R. who informed that NAC is on site and is triggering the Makeup Air unit alarms. Phil informed that he will let NAC know about the Pressure alarm | All Wastewater System ROC General | 2025-12-11
ROC | December | KCSSKR - Screen Failed to Stop alarm came in. Checked site. Called Gavin W. who directed to disregard as he and Young J. are on site | All Wastewater System ROC General | 2025-12-11
ROC | December | NMSSBP - Terry R onsite testing drywell flood, & dialer | All Wastewater System ROC General | 2025-12-12
ROC | December | Carter Dunn Signing In, -1D/Clear | All Wastewater System ROC General | 2025-12-12
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-13
ROC | December | MTSP- Aeration tan k1 lo do alarm came in placed aeration blower 1 in man/on as per interim | All Wastewater System ROC General | 2025-12-14
ROC | December | QVSSSC - Channel Grinder Emergency Stop alarm came in. Checked site. Called Cameron B. who is on site and will clear alarms 14:24 - Inlet Channel High High switch alarm came in. Disregarded as per shift report | All Wastewater System ROC General | 2025-12-11
ROC | December | KSSP- Aeration tank 1 inlet DO fault alarm came in. Notified Neil O will investigate | All Wastewater System ROC General | 2025-12-12
ROC | December | MTSP - Intrusion alarm, received a phone call from FMC. Terry R on site. | All Wastewater System ROC General | 2025-12-14
ROC | December | BLSS - Young J. called to inform that he is on site and will be testing the wet well overflow alarm, the dry well flood alarm and the hi/low temp alarms. Young directed to disregard alarms until work is complete | All Wastewater System ROC General | 2025-12-11
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-13
ROC | December | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-12-14
ROC | December | SHSP- Marcus R on site to work on RAS and WAS pumps | All Wastewater System ROC General | 2025-12-10
ROC | December | SEOC Shaft 4 - Barry M. is on site and will be running the generator | All Wastewater System ROC General | 2025-12-11
ROC | December | Christian Van Beek signing out. | All Wastewater System ROC General | 2025-12-12
ROC | December | MARS - Level hi alarm. Deactivated RHRSTR. NMETHW - Deactivated NMETHW while NMETIB fills. MKRSEM - Called Toronto Water (Peter) and requested they stop flow to MKRSEM. | All Wastewater System ROC General | 2025-12-12
ROC | December | NBSSJA- Diesel tank level hihi alarm. Disregard alarm as per shift report. | All Wastewater System ROC General | 2025-12-14
ROC | December | SHSP - Gavin W and Marcus R working on Alum pumps 6 and 7. | All Wastewater System ROC General | 2025-12-15
ROC | December | QVSSQS - Rick L, Parth P, Red B onsite working on discharge PIT. May work on diesel LIT later as well | All Wastewater System ROC General | 2025-12-12
ROC | December | KBSP- Lauren S on site to test sump hi level in headworks and filter building | All Wastewater System ROC General | 2025-12-10
ROC | December | MTSP- Aeration tank 1 DO Low alarm. Man/started Aeration Blower 1. | All Wastewater System ROC General | 2025-12-14
ROC | December | YDSS+YNSS NORMAL Angelica Chepiga signing out | All Wastewater System ROC General | 2025-12-14
ROC | December | Adam Button signing in -14 clear | All Wastewater System ROC General | 2025-12-12
ROC | December | KSSP - Hypo pump 1 speed sig error. Hypo pump local off | All Wastewater System ROC General | 2025-12-12
ROC | December | KSSP- Captor tank lo alarm came in will have enough chemical to last weekend. Emailed North Wastewater OPs about chemical level | All Wastewater System ROC General | 2025-12-13
ROC | December | KSSP- Hypo Tank Level HiHi Alarm. Tank is empty. Cleared alarm. | All Wastewater System ROC General | 2025-12-14
ROC | December | YDSS+YNSS normal | All Wastewater System ROC General | 2025-12-13
ROC | December | YDSS+YNSS normal | All Wastewater System ROC General | 2025-12-14
ROC | December | YDSS+YNSS normal | All Wastewater System ROC General | 2025-12-13
ROC | December | YDSS+YNSS normal | All Wastewater System ROC General | 2025-12-15
ROC | December | NBSP- UV minor fault alarm outstanding. Disregard on shift report UV bank 1 b running | All Wastewater System ROC General | 2025-12-12
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-12
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-13
ROC | December | NBSSJA - Gas detector panel fault alarm. Disregard as per the shift report. | All Wastewater System ROC General | 2025-12-15
ROC | December | Gluzen Ramos Ong signing in | All Wastewater System ROC General | 2025-12-15
ROC | December | YDSS+YNSS normal | All Wastewater System ROC General | 2025-12-16
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-12
ROC | December | YDSS + YNSS Normal Connor Smith signing out | All Wastewater System ROC General | 2025-12-14
ROC | December | Adam Button signing in -10 Clear | All Wastewater System ROC General | 2025-12-14
ROC | December | YDSS+ YNSS normal | All Wastewater System ROC General | 2025-12-12
ROC | December | Angelica Chepiga signing in,weather -8C | All Wastewater System ROC General | 2025-12-15
ROC | December | YDSS+YNSS normal Adam Button signing out | All Wastewater System ROC General | 2025-12-15
ROC | December | AUSS- P5 Mv4 failed to open alarm came in reset alarm | All Wastewater System ROC General | 2025-12-16
ROC | December | MTSP - David D on site for generator load test, running generator. Disregard alarms. | All Wastewater System ROC General | 2025-12-15
ROC | December | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-12-15
ROC | December | NBSSJA- Gas Detector Panel Fault alarm came in. Notified Marcus R will take a look on SCADA 7:53-NBSSJA- Marcus R directed to disregard alarm #consult | All Wastewater System ROC General | 2025-12-13
ROC | December | NBSSJA- Diesel tank level hihi alarm came in. Disregard alarm as per shift report | All Wastewater System ROC General | 2025-12-13
ROC | December | 18:00 Connor Smith signing in -8C Clear 18:04: Adam Button signing in 18:05 NMSSBP- Mech Screen Overtorque Alarm Came in. Left Outstanding and emailed Central East Wastewater 18:15- Adam Button signing out 20:00- YDSS + YNSS Normal 20:55- EZMax back online | All Wastewater System ROC General | 2025-12-13
ROC | December | LSSS - PAC Communication failure. Several times it clears and comes back. Informed Artour L, will look into issue | All Wastewater System ROC General | 2025-12-11
ROC | December | MTSP- Aeration Tank 2 DO lo alarm came in. Placed aeration P2 in man/on as per interim 12:40-MTSP- Aeration Tank 2 DO lo alarm cleared. Placed aeration P2 in auto as per interim | All Wastewater System ROC General | 2025-12-13
ROC | December | SUSP- Influent Flow HiHi. Cleared alarm. | All Wastewater System ROC General | 2025-12-10
ROC | December | EGSSSC - Wet Well Overflow Fault alarm came in. Disregarded as per shift report | All Wastewater System ROC General | 2025-12-11
ROC | December | SHSSDK- Placed P1 back in auto speed setpoint 6:19- SHSSDK- Placed P1 back in manual speed setpoint 100% as OPs intentionally have speed to flush pump with workorder issued to investigate efficiency issues | All Wastewater System ROC General | 2025-12-12
ROC | December | NBSP- Process bld gas detection warning alarm came in. Disregard on shift report | All Wastewater System ROC General | 2025-12-13
ROC | December | SHSP- Screen room O2 conc lo alarm came in. Disregard on shift report | All Wastewater System ROC General | 2025-12-13
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-13
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-14
ROC | December | Adam Button signing in | All Wastewater System ROC General | 2025-12-10
ROC | December | NBSSJA- Diesel Tank Level HiHi Alarm. Disregard as per SCADA Report. | All Wastewater System ROC General | 2025-12-10
ROC | December | YDSS+YNSS normal KSSP- Scum chamber 2 hi alarm Disregard on shift report | All Wastewater System ROC General | 2025-12-13
ROC | December | SHSP - Marcus R. is on site and will be working on the two grit dewatering screws as well as testing the sludge holding tank hi level. Directed to disregard related alarms until work is complete | All Wastewater System ROC General | 2025-12-11
ROC | December | KSSP - Kevin K called to inform that maintenance is on site to assist with work on the membrane filtration system. Kevin informed that area ops will be draining the membrane tanks in sequence starting with train 1. Will see associated alarms and this may be a multi day maintenance event. | All Wastewater System ROC General | 2025-12-15
ROC | December | NBSSJA - Gas Detector Panel Fault Alarm. Marcus R requested disregard alarm until tomorrow. | All Wastewater System ROC General | 2025-12-15
ROC | December | RHAMF1- Unit 1 Diff. Pressure 2 Hi Alarm. Previously was disregarded by area OP. Will monitor and email Central East Ops. 16:35 Terry R requested disregard Unit 1 Diff. Pressure 2 Hi and HiHi alarms for the night. # Consult. | All Wastewater System ROC General | 2025-12-14
ROC | December | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-12-14
ROC | December | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-12-14
ROC | December | SUSSSR - Matt T onsite working on pump 1 | All Wastewater System ROC General | 2025-12-11
ROC | December | QVSSSC - Channel grinder E-stop. Grinder local off for weekend. Electrician onsite today working on grinder as overload/fault issues prior. | All Wastewater System ROC General | 2025-12-12
ROC | December | SHSP - Marcus R onsite testing process building/blower building sump/float alarm, and scum pump AUEQSJ - Dehumidifier process fan not run alarm. Disregard as per shift report | All Wastewater System ROC General | 2025-12-12
ROC | December | MTSP- Placed aeration blower 1 back in auto as per interim | All Wastewater System ROC General | 2025-12-14
ROC | December | AUSSYS - P2 flow lolo alarm came in. FLow started to drop and speed increased but flow remained lo. Placed in man/off D5 and rotated duty. Emailed Central east wastewater YDSS+YNSS normal | All Wastewater System ROC General | 2025-12-15
ROC | December | AUSSYS- P1 lo flow alarm came in. P1 only ran for 6 mins and low flow came in on P1 shutdown will monitor next few cycles | All Wastewater System ROC General | 2025-12-15
ROC | December | RHAMF1 - Makeup Air Unit Failed to Start alarm came in multiple times. Called Terry R. who directed to disregard #CONSULT | All Wastewater System ROC General | 2025-12-11
ROC | December | SUSP- UV ch 2 high level/ common critical fault alarms came in. Cleared upon acknowledgment. Alarms come in on UV start as channel is hi as stated in shift report. Trends look okay | All Wastewater System ROC General | 2025-12-14
ROC | December | NMSSBP- P 4 vibration hi alarm came in. Disregard on shift report MTSP- Placed Aeration blower 1 back in auto as per interim AUSS- P6 disch MV2 failed to open alarm came in. Reset alarm | All Wastewater System ROC General | 2025-12-14
ROC | December | YDSS+YNSS normal | All Wastewater System ROC General | 2025-12-14
ROC | December | KBSP- Reject sump P1 e stop. Notified Marcus R directed to disregard for tonight unless P2 faults #consult | All Wastewater System ROC General | 2025-12-14
ROC | December | PVSS - Gavin W on site to complete work orders including a generator test, hi/lo temperature test, dry well flood alarm test and an auto dialer alarm test. | All Wastewater System ROC General | 2025-12-10
ROC | December | Ethan U signing in | All Wastewater System ROC General | 2025-12-11
ROC | December | YDSS+YNSS normal | All Wastewater System ROC General | 2025-12-15
ROC | December | Ethan Ullalkar signing out. | All Wastewater System ROC General | 2025-12-12
ROC | December | Christian Van Beek signing in. Weather: -10C and clear. | All Wastewater System ROC General | 2025-12-11
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-11
ROC | December | LSSS - Amilia onsite requesting pump 6. Rotated pump 6 into duty 1 | All Wastewater System ROC General | 2025-12-12
ROC | December | SUSP - Eric S leaving site. Unable to fix the UV intensity sensor. | All Wastewater System ROC General | 2025-12-10
ROC | December | KSSP - Train 4 membrane tank low alarm, drain tank level hihi alarm and shutdown alarm. Checked site, train 4 going through a sequence event, drain tank was higher than normal but is being pumped down rapidly. Raw water valve is open and filling the tank. Able to clear all alarms except the shutdown alarm. Contacted Niel O who will log into SCADA and reset the filter status. | All Wastewater System ROC General | 2025-12-11
ROC | December | Angelica Chepiga signing in, weather -12C | All Wastewater System ROC General | 2025-12-14
ROC | December | YDSS+YNSS normal | All Wastewater System ROC General | 2025-12-13
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-11
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-11
ROC | December | AUSS - Marcos T testing Drywell flood , temp alarm, dialer alarms. | All Wastewater System ROC General | 2025-12-15
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-12
ROC | December | SHSP- Screen room O2 conc HiHi alarm. Disregard on shift report. | All Wastewater System ROC General | 2025-12-14
ROC | December | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-12-14
ROC | December | Ethan U signing in | All Wastewater System ROC General | 2025-12-12
ROC | December | MTSP - Aeration tank 2 DO low alarm, checked site, switched controlling tank selection to Aeration tank 2 as per SCADA review. | All Wastewater System ROC General | 2025-12-14
ROC | December | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-12-14
ROC | December | HUB 1 Server, Yash S restarted server. SUSP - UV alarms after server restart. Notified Neil O, He will check SCADA. KSSP - UV alarms after server restart. Notified Kevin K, he is on site, will check. | All Wastewater System ROC General | 2025-12-15
ROC | December | SHSP- Screen room O2 hi alarm came in disregard on shift report | All Wastewater System ROC General | 2025-12-14
ROC | December | LSSS - Amelia from sewer use bylaw on site to sample. Amelia requested that pump 6 be placed duty 1 for sampling. Made necessary change. 09:15 - LSSS - Amelia collected two of three samples before the pump shut down on duty stop. Placed the pump in manual mode and activated so Amelia can collect the third sample. Informed Barry M as well. | All Wastewater System ROC General | 2025-12-15
ROC | December | NBSP- UV system minor fault. Disregard on shift report as bank 1b is active | All Wastewater System ROC General | 2025-12-14
ROC | December | Angelica Chepiga signing out | All Wastewater System ROC General | 2025-12-15
ROC | December | YDSS + YNSS Normal Christian Van Beek signing out. | All Wastewater System ROC General | 2025-12-15
ROC | December | YDSS+YNSS normal | All Wastewater System ROC General | 2025-12-16
ROC | December | City of Vaughan- Joe M (416-518-7849) informed ROC the manhole cover that was missing has been put back by city of Vaughan | All Wastewater System ROC General | 2025-12-12
ROC | December | EGSSSC - Flow control valves failed, Recirculation Mode failure alarms - Notified Neil O. He will check SCADA. # Consult | All Wastewater System ROC General | 2025-12-15
ROC | December | Adam Button signing in -10 Clear | All Wastewater System ROC General | 2025-12-15
ROC | December | SHSP - Gavin W working on vortex, disregard alarms. | All Wastewater System ROC General | 2025-12-15
ROC | December | EGSSSC- Power fail on site. Generator running and control panel diesel fuel system power fail. Reset diesel fuel alarms and site back on hydro after 3 mins. Will monitor generator shutdown. YDSS+YNSS normal | All Wastewater System ROC General | 2025-12-15
ROC | December | EGSSSC- Wet well overflow fault came in. Notified Neil O. Directed to disregard alarm and maintenance will have to take a look at flowmeter #consult | All Wastewater System ROC General | 2025-12-15
ROC | December | YDOC OCF - Brent S onsite to work on fan 1 control board. | All Wastewater System ROC General | 2025-12-11
ROC | December | SUSP - Diversion EQ tank level LOE, Lagoon flow lolo, lagoon flowmeter OOS & disregard EQ tank level LOE alarm as per shift report. Neil O onsite | All Wastewater System ROC General | 2025-12-12
ROC | December | Christian Van Beek signing in. | All Wastewater System ROC General | 2025-12-15
ROC | December | AUSSSR- Chinmay from CPD with contractors on site/troubleshooting equipment. Disregard alarms for the duration of the work. 08:40 Chinmay from CPD with contractors leaving site. | All Wastewater System ROC General | 2025-12-15
ROC | December | YDSS+YNSS normal | All Wastewater System ROC General | 2025-12-15
ROC | December | YDSS+YNSS normal | All Wastewater System ROC General | 2025-12-16
ROC | December | Adam Button signing out | All Wastewater System ROC General | 2025-12-12
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-12
ROC | December | MTSP- FMC called about intrusion alarm at admin building. No OPs notified ROC of site visit and directed to contact security | All Wastewater System ROC General | 2025-12-13
ROC | December | RHAMF - Phil R working remotely with the contractor to make changes at RHAMF. Phil directed to disregard alarms. | All Wastewater System ROC General | 2025-12-10
ROC | December | RHAMF1 - Phil R finished with the remote operation of the facility with the contractor. The contractor is still on site working on damper systems and exhaust fan systems. | All Wastewater System ROC General | 2025-12-10
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-10
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-11
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-11
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-10
ROC | December | Christian Van Beek signing in. Weather: -3 and snow. | All Wastewater System ROC General | 2025-12-10
ROC | December | NBSP- UV System Minor Fault Alarm. Disregard as per SCADA Report. | All Wastewater System ROC General | 2025-12-10
ROC | December | BLSS - Noted abnormal trending. Contacted Young J who directed to check the speed control mode of pump 3. The speed setpoint control mode was manual, not auto. Young J directed to place the pump in auto speed setpoint control. Made changes and will check the site later today. | All Wastewater System ROC General | 2025-12-10
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-10
ROC | December | JDSS - Brent St C and Dave D on site to complete a disconnect replacement. The wet well will be pumped down to a manageable level and then power to the site will be disconnected. The window without power will be approximately fifteen minutes. | All Wastewater System ROC General | 2025-12-10
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-11
ROC | December | SHSP- RAS to Aer Tank 2 No Flow Alarm. Notified Marcus R. He will look into it. 04:40- Marcus R. rotated RAS Pump 2 into duty 1. Placed RAS Pump 3 in man/off and cleared alarm. Will look into it today. CONSULT | All Wastewater System ROC General | 2025-12-11
ROC | December | Adam Button signing in | All Wastewater System ROC General | 2025-12-11
ROC | December | JDSS - Artour L finished at site | All Wastewater System ROC General | 2025-12-11
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-11
ROC | December | SUSP - Influent Flow HiHi alarm came in. Flow came back to optimal range and cleared alarm. Will continue to monitor | All Wastewater System ROC General | 2025-12-11
ROC | December | LSSS - Barscreen 2 fault alarm. Checked site, barscreen 2 status is disabled. Barscreen 1 is available. Sent email to area ops. | All Wastewater System ROC General | 2025-12-12
ROC | December | SHSSDK - Marcus R. is on site and will be running the generator and testing the temperature alarms. Directed to disregard alarms until test is complete | All Wastewater System ROC General | 2025-12-11
ROC | December | SUSP - Ian W working on OIT. Disregard HRBT alarm | All Wastewater System ROC General | 2025-12-11
ROC | December | BLSS - Artour L onsite looking into Generator LIT | All Wastewater System ROC General | 2025-12-11
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-11
ROC | December | KSSSQW - Mike B on site to complete work orders including dry well flood alarm and various dialer related alarms. | All Wastewater System ROC General | 2025-12-10
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-12
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-02
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-02
ROC | December | YDOC/SEOC- Aaron C rebooting network to help with slow connection speeds. Will lose comms during reboot but should not exceed 10 mins | All Wastewater System ROC General | 2025-12-01
ROC | December | KSSSQW - REdempto B on site and requested that duty 1 be rotated to pump 1. Made changes. | All Wastewater System ROC General | 2025-12-03
ROC | December | YDOC- Evgeny S rebooting OIT disregard historian heartbeat until work is done | All Wastewater System ROC General | 2025-12-03
ROC | December | Adeela Khan signing in | All Wastewater System ROC General | 2025-12-05
ROC | December | KSSP- Sludge Holding Blwr 1 Hi Dif Press Alarm. Blower 2 took over in duty 1. Will email North Wastewater Ops. | All Wastewater System ROC General | 2025-12-03
ROC | December | RHAMF - Dave from North American Construction called back and would like the pumps in manual. 11:16 - Called Marcos T. who directed to place all recirculation pumps in manual and gave direction to let the contractors know they can run the pumps one by one. Marcos also gave direction to clear the Lo pressure and flow alarms for each individual pump and to continue to monitor 11:19 - Called Dave from NAC back and let him know. He is on site with Jimmy (Electrical Superintendent) and they placed Recirculation pump 1 for system 1 and Recirculation pump 1 for system 2 in local 11:23 - Dave started pump 1 for system 1. 11:30 - After the flow and pressure were back to optimal range, called Marcos to confirm its okay to clear alarms. Marcos directed to clear alarms 11:32 - Called Dave back to inform that pump 1 system 1 alarms have been cleared. Dave started pump 1 for system 2. Cleared alarms after 5 mins 11:40 - Dave called back to inform that he and Jimmy will continue to monitor and if there are any issues to give him or jimmy a call. Dave (780 880 0979) Jimmy (416 826 0586) 11:51 - Pumps remained in local. Called Dave back who informed he would like the pumps to stay in local/on for the remainder of the weekend. Called Marcos T. who will give NAC a call 12:11 - Marcos called back to inform that NAC will be back to place the pumps back to auto 14:20 - Jimmy from NAC called back to inform that he took both pumps out of local and placed them back to auto. As he did this, the original recirculation water flow and pressure alarms came back in. 14:21 - Called Marcos T. who directed to place the pumps in manual and clear the alarms. 14:32 - Called Marcos T. He directed to place all the recirculation pumps back to auto. If the alarms come in again, Marcos would like a call back #CONSULT | All Wastewater System ROC General | 2025-12-06
ROC | December | AUSSSR- Aysix system heartbeat alarm came in reset trends okay | All Wastewater System ROC General | 2025-12-06
ROC | December | Connor Smith signing in -6C Snowy | All Wastewater System ROC General | 2025-12-01
ROC | December | BLSS- Historian Heartbeat Alarm. Notified Ian W. He will look into it. W11480187 CMU5 | All Wastewater System ROC General | 2025-12-01
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-04
ROC | December | NBSSJA, Lance J on site, testing sump/temp/dialer alarms, directed to disregard alarms on site till Lance J finishes on site | All Wastewater System ROC General | 2025-12-05
ROC | December | RHAMF1, Philip R on site with contractors, directed to disregard damper and odour control alarms | All Wastewater System ROC General | 2025-12-04
ROC | December | KSSP - Darren B on site to complete a generator test run. | All Wastewater System ROC General | 2025-12-04
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-05
ROC | December | YDSS+YNSS normal | All Wastewater System ROC General | 2025-12-06
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-06
ROC | December | YDSS+YNSS normal | All Wastewater System ROC General | 2025-12-07
ROC | December | YDOC OCF, Barry M on site, running generator | All Wastewater System ROC General | 2025-12-04
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-05
ROC | December | Christian Van Beek signing out. | All Wastewater System ROC General | 2025-12-04
ROC | December | KSSP - Memb Air blower 1 failed to start. Informed Chase J of alarm. Blower 2 runs okay, place blower 1 man/off for the night Consult | All Wastewater System ROC General | 2025-12-04
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-06
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-07
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-08
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-03
ROC | December | AUEQSJ, Dehumidifier Process Fan Not Run alarm, fan kept failing to start, notified Marcos T as he is still currently out, directed to disregard consult | All Wastewater System ROC General | 2025-12-07
ROC | December | SEOC OCF, Rotated Blower Duty so blower 3 is in D1 and blower 2 is in D2 for Matt S 12:46, Rotated Blowers back to original duty, Blower 1 failed to start up with no alarms persisting. Blower 1 in D1 and Blower 2 in D2 | All Wastewater System ROC General | 2025-12-05
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-06
ROC | December | BLSS - Young J onsite testing eyewash, temp, and generator | All Wastewater System ROC General | 2025-12-09
ROC | December | KSSP - Mike B flushing membrane lines. | All Wastewater System ROC General | 2025-12-09
ROC | December | Christian Van Beek signing out. | All Wastewater System ROC General | 2025-12-03
ROC | December | SHSP - Marcus R. is on site and will be taking a look at the 4 aeration blowers | All Wastewater System ROC General | 2025-12-05
ROC | December | SHSP - Screen Room O2 Conc HiHI alarm came in. Checked site. Disregarded as per shift report | All Wastewater System ROC General | 2025-12-06
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-07
ROC | December | SEOC- Evgeny S working on OIT disregard historian heartbeat alarm until done 10:01- SEOC- Evgeny done with site alarm cleared | All Wastewater System ROC General | 2025-12-01
ROC | December | Carter D signing out | All Wastewater System ROC General | 2025-12-07
ROC | December | SUSP- Noticed that lagoon pump is running but not registering any flow. Notified Chase J. Can disregard. He will add it to SCADA Report. CONSULT | All Wastewater System ROC General | 2025-12-03
ROC | December | SEOC - Aaron C rebooting server | All Wastewater System ROC General | 2025-12-01
ROC | December | KSSP- UV CH. 2 Bank 2A Adjacent Lamp Fail. Disregard as per SCADA Report. | All Wastewater System ROC General | 2025-12-01
ROC | December | Carter Dunn Signing In, -6D/Clear | All Wastewater System ROC General | 2025-12-02
ROC | December | SEOC4, Rotated Fans so Fan 2 is in D1 and Fan 1 is in D2 | All Wastewater System ROC General | 2025-12-05
ROC | December | NMSSBP- Screen 2 diff level trends slightly elevated and have exceeded hi level but not triggering alarms. Notified Marcos T of potential issue as screen 1 is currently out of service due to a over torque alarm. Marcos T directed to disregard hi differential level but call if hihi comes in. Marcos T Req CMU5 for tomorrow morning to attend site after completing workorders at MTSP. 5:06-NMSSBP- Created CMU5 as per Marcos T req W11492083 #consult #CMU5 | All Wastewater System ROC General | 2025-12-06
ROC | December | YDSS+YNSS normal NBSP- Vortex 2 air scour uncmd close alarm came in reset as per shift report | All Wastewater System ROC General | 2025-12-06
ROC | December | SEOC 4 - Matt T on site to complete work on the fans. Requested that alarms be disregarded. LSSS - Jon from property services on site to complete work on the elevator car lights. | All Wastewater System ROC General | 2025-12-02
ROC | December | AUEQSJ - Dehumidifier Process Fan Not run alarm came in. Disregarded as per shift report YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-06
ROC | December | SEOC - OCF Monitor 1 lolo alarm. Disregard as per the shift report. | All Wastewater System ROC General | 2025-12-03
ROC | December | Ethan Ullalkar signing out. | All Wastewater System ROC General | 2025-12-09
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-10
ROC | December | YDSS + YNSS normal | All Wastewater System ROC General | 2025-12-08
ROC | December | Ethan U signing in Weather -8. | All Wastewater System ROC General | 2025-12-09
ROC | December | MTSP - Aeration blower 3 fail to start alarm. Checked site, duty rotated to aeration blower 2 and operations appear normal. reset alarm. | All Wastewater System ROC General | 2025-12-02
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-01
ROC | December | Carter Dunn Signing Out | All Wastewater System ROC General | 2025-12-01
ROC | December | KSOCMA - David D onsite working on fan 1 | All Wastewater System ROC General | 2025-12-09
ROC | December | KSSP - Mike B onsite cleaning DO probe HMSS - Gavin W onsite test generator and dry well flood, temp, and auto-dialer | All Wastewater System ROC General | 2025-12-09
ROC | December | RHAMF1 - Unit 1 Differential Pressure 2 LoLo alarm came in. Checked site. Called Marcos T. who directed to disregard alarm for the night | All Wastewater System ROC General | 2025-12-08
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-01
ROC | December | KBSP - Reject sump pump 1 E-stop. Marcus R onsite requesting electrical. Notified Brent S, will head to site. CMU created for both Brent S & Marcus R CMU = 11500603 | All Wastewater System ROC General | 2025-12-09
ROC | December | KSSSQW - Mike B onsite running diesel & testing hi level wet well | All Wastewater System ROC General | 2025-12-08
ROC | December | QVSSSC- Cam B on site for wet well entry | All Wastewater System ROC General | 2025-12-03
ROC | December | KBSP- UV Ch. 1, 2 Low Flow/Common Minor Alm. Disregard as per SCADA Report. Alarms cleared upon acknowledging. | All Wastewater System ROC General | 2025-12-02
ROC | December | AUSS, Evgeni S on site, resetting OIT | All Wastewater System ROC General | 2025-12-05
ROC | December | Carter Dunn Signing Out | All Wastewater System ROC General | 2025-12-02
ROC | December | RHAMF1, Unit 1/2 Recirculation Water Flow/Pump Pressure lolo alarm, Contacted Marcos T to inform him the recirc pumps are still offline at this time and they're outstanding alarms, don't know if NAC has left site or not. Current interim is expired (Expired on November 17/2025). Contacted Marcos T who hasn't heard anything from NAC , directed to contact Wastewater Manager on call. Contacted Graham B but no response, left a voice message at this time. Will contact Marcos T for an update 17:33, ROC got in contact with Jimmy from NAC, Jimmy informed the RO that they are currently off site and will be back tomorrow morning. The alarms that are currently outstanding can be disregard. Contacted Marcos T to relay the message Jimmy H passed on to the ROC. Marcos T directed to disregard for the night as they will be back tomorrow. Gave a call to Graham B again to just follow up, no response, left a detailed voice message on the events that occurred and that the alarms will be disregarded for the night. 18:55, Graham B called back, informed of the situation that everything has been resolved, consult | All Wastewater System ROC General | 2025-12-05
ROC | December | Ethan Ullalkar signing out. | All Wastewater System ROC General | 2025-12-05
ROC | December | GRSSWA - Artour L. called to inform that he will be working on the site and will lose communications for about 10 mins. Chase J. is aware 12:35 - Artour L. is finished on site | All Wastewater System ROC General | 2025-12-05
ROC | December | KSSP - ZW3 Shutdown and Turbidity OOR alarms came in. Disregarded as per shift report | All Wastewater System ROC General | 2025-12-07
ROC | December | BLSS - Pump Room South Temp LoLo alarm came in. Disregarded as per shift report | All Wastewater System ROC General | 2025-12-08
ROC | December | NBSP - Vortex #1 Air Scour uncommanded close alarm came in. Ack/reset as per shift report | All Wastewater System ROC General | 2025-12-08
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-07
ROC | December | NMEQBP - Historian heartbeat alarm. Kingsley M working on the local OIT. | All Wastewater System ROC General | 2025-12-09
ROC | December | NMSSBP- Mech screen 1 overtorque alarm Screen 2 running in auto okay. Emailed Central East Wastewater OPs. Left alarm outstanding | All Wastewater System ROC General | 2025-12-06
ROC | December | Adam Button signing out | All Wastewater System ROC General | 2025-12-06
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-01
ROC | December | YDSS + YNSS normal | All Wastewater System ROC General | 2025-12-01
ROC | December | NBSP - Vortex 1 and 2 mixer not running alarms. Contacted Lance J who is aware and will reset the alarms. | All Wastewater System ROC General | 2025-12-08
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-08
ROC | December | BLSS - Kingsley M. called to inform he will be resetting the OIT at the pumping station and will trigger a historian heartbeat | All Wastewater System ROC General | 2025-12-05
ROC | December | RHAMF- Station Power Fail, Odour Control System Offline, Makeup Air Unit Failed to Start. Alarms cleared 22:50- Makeup Air Unit Failed to Start. Alarm cleared. | All Wastewater System ROC General | 2025-12-09
ROC | December | KBSP - Marcus R & Brent S finished at site. Alarm clear, back in duty, replace relay and tighten fitting. If sump faults out again disregard for the night. If both fault. Call out | All Wastewater System ROC General | 2025-12-09
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-09
ROC | December | KBSP - Eric S onsite working on influent total analyzer | All Wastewater System ROC General | 2025-12-09
ROC | December | Carter Dunn Signing In, -14D/Clear | All Wastewater System ROC General | 2025-12-05
ROC | December | SEOC - Kingsley M restarting OIT and to disregard heartbeat alarm | All Wastewater System ROC General | 2025-12-08
ROC | December | YDSS+YNSS normal | All Wastewater System ROC General | 2025-12-05
ROC | December | YDSS+YNSS normal | All Wastewater System ROC General | 2025-12-05
ROC | December | NBSSJA - Lance J on site for a generator test. | All Wastewater System ROC General | 2025-12-09
ROC | December | SEOC - OCF fan room 1 GO2 low alarm. Disregard as per the shift report. | All Wastewater System ROC General | 2025-12-03
ROC | December | YDSS+YNSS normal | All Wastewater System ROC General | 2025-12-06
ROC | December | EGSSSC - Wet Well Overflow Fault alarm came in. Checked site. Wet well level is not high. Called Chase J. who directed to disregard as the analyzer will need to be cleaned. #CONSULT | All Wastewater System ROC General | 2025-12-08
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-08
ROC | December | Connor Smith signing in -6C Clear | All Wastewater System ROC General | 2025-12-02
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-04
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-03
ROC | December | SHSP- UV system major fault alarm. Both banks running. Notified Marcus R bank 1a has fuse issue and bank 1b has burnt out bulb. Dosing okay. Marcus R attending site created CMU5 W11492068 #CMU5 | All Wastewater System ROC General | 2025-12-07
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-08
ROC | December | Adeela Khan signing out | All Wastewater System ROC General | 2025-12-09
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-09
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-04
ROC | December | YDSS + YNSS Normal Connor Smith signing out | All Wastewater System ROC General | 2025-12-02
ROC | December | KCSSKR- Generator Running Alarm. Station quickly switched back to utility power. Will monitor. 21:56- Cleared Alarm | All Wastewater System ROC General | 2025-12-02
ROC | December | RHAMF1, Unit 1 Recirculation pump 1/2 Comm Loss/Emergency Stop, talked with Philip R, directed to disregard at this time. He will look into it further | All Wastewater System ROC General | 2025-12-05
ROC | December | STW13, Placed wells 1/3 back to auto | All Wastewater System ROC General | 2025-12-07
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-07
ROC | December | Ethan U signing in | All Wastewater System ROC General | 2025-12-08
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-07
ROC | December | SUSSWB/SUSSHS - Chase J onsite running generator and testing temp alarm | All Wastewater System ROC General | 2025-12-08
ROC | December | NBSP - Lance J on site to complete a generator test run. | All Wastewater System ROC General | 2025-12-08
ROC | December | YDSS + YNSS normal | All Wastewater System ROC General | 2025-12-09
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-09
ROC | December | YDOC/SEOC John D is resetting OITS on site | All Wastewater System ROC General | 2025-12-04
ROC | December | Adeela Khan signing out | All Wastewater System ROC General | 2025-12-08
ROC | December | Christian Van Beek signing in. | All Wastewater System ROC General | 2025-12-02
ROC | December | AUSSSR- Heat tracing controller 2 fault alarm came in. Disregard on shift report | All Wastewater System ROC General | 2025-12-06
ROC | December | YDSS+YNSS normal | All Wastewater System ROC General | 2025-12-06
ROC | December | YDSS+YNSS normal | All Wastewater System ROC General | 2025-12-07
ROC | December | Adam Button signing in | All Wastewater System ROC General | 2025-12-03
ROC | December | KSSP- Historian Heartbeat Alarm. Chris S will look into it. 19:55- Chris S finished. Site back to normal W11484640 CMU5 | All Wastewater System ROC General | 2025-12-03
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-03
ROC | December | LSSS- Amelia from EME is on site req P6 to run for sampling. Rotated P6 in D1. | All Wastewater System ROC General | 2025-12-03
ROC | December | SUSP- Neil O on site to run generator and test diesel containment alarm | All Wastewater System ROC General | 2025-12-03
ROC | December | KBSP - Young J on site to complete maintenance on the sludge blowers, aeration blower, RAS pumps and the offline clarifier. Work will also be continuing on the maintenance of the hydrant system on site and the wash water system remains OOS for the duration of this work. | All Wastewater System ROC General | 2025-12-04
ROC | December | SEOC 6- Talha H restarting OIT 13:32- SEOC 6- Talha H done restart alarm cleared 13:32- NBSP- Lance J. testing eye wash stations on site | All Wastewater System ROC General | 2025-12-01
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-02
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-01
ROC | December | KSSP - Memb train 1 failed to start. Check site, train 1 going through backwash & alarm cleared | All Wastewater System ROC General | 2025-12-04
ROC | December | SEOC4, Rotated Fan Duty so fan 1 is in D1 and fan 2 in D2. Matt S on site working on the fans | All Wastewater System ROC General | 2025-12-02
ROC | December | Ethan Ullalkar singing out | All Wastewater System ROC General | 2025-12-01
ROC | December | SEOC - Aaron M rebooting the router on site. Possible communication alarms and the timeframe for restart is approximately 10 minutes. | All Wastewater System ROC General | 2025-12-02
ROC | December | Adam Button signing in -5 clear | All Wastewater System ROC General | 2025-12-06
ROC | December | YDSS+YNSS normal | All Wastewater System ROC General | 2025-12-07
ROC | December | RHAMF1, Unit 1 Diff. Pressure 2 hi alarm, nothing on shift report, Notified Marcos T, directed to disregard at this current time however if the hihi alarm comes in, directed to give him a call and the company NAP consult | All Wastewater System ROC General | 2025-12-04
ROC | December | Carter Dunn Signing Out | All Wastewater System ROC General | 2025-12-04
ROC | December | AKBSP - Aer basin 2 front DO fault. Trends show issue with front DO fault reading. Disregard for the night as tank 2 removed from service as per shift report | All Wastewater System ROC General | 2025-12-04
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-02
ROC | December | RHAMF1- Unit 1 recirculation flow and pump pressure lolo alarms came in. Emailed Central east wastewater team about outstanding alarms | All Wastewater System ROC General | 2025-12-03
ROC | December | LSSS - Gen 3 warning, pump 5 VFD fault, panel power failure. Checked site, Barry M, Terry C, & David D all onsite | All Wastewater System ROC General | 2025-12-08
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-04
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-04
ROC | December | SEOC Shaft 6/7, Barry M on site running the generator | All Wastewater System ROC General | 2025-12-04
ROC | December | KSSP, Cam B testing sump alarms on site, directed to disregard sump alarms on site till he is finished | All Wastewater System ROC General | 2025-12-05
ROC | December | YDSS + YNSS Normal Connor Smith signing out | All Wastewater System ROC General | 2025-12-04
ROC | December | Christian Van Beek signing in. | All Wastewater System ROC General | 2025-12-04
ROC | December | AUSS, Marcos T/Terry R on site, testing wet well levels and doing safety alarms, directed to disregard alarms on site | All Wastewater System ROC General | 2025-12-04
ROC | December | Adeela Khan signing in. Weather: -2 and cloudy | All Wastewater System ROC General | 2025-12-06
ROC | December | KSSP - Membrane air blower 1 failed to start alarm. Checked site, both membrane blowers are interlocked on a train valves closed interlock. Able to reset the fail to start alarm. | All Wastewater System ROC General | 2025-12-04
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-02
ROC | December | KSSP- Recirc Pump 1 No Flow Alarm outstanding. Notified Chris C. He will look into it. 20:00- Can disregard alarm. CONSULT | All Wastewater System ROC General | 2025-12-02
ROC | December | RHAMF1 - Storage Room Exhaust Fan 1 Overload Alarm came in. Called Chris R. who directed to disregard alarm #CONSULT | All Wastewater System ROC General | 2025-12-01
ROC | December | SEOC - OCF Damper station flood. Disregard as per shift report | All Wastewater System ROC General | 2025-12-08
ROC | December | Adam Button signing out | All Wastewater System ROC General | 2025-12-01
ROC | December | Adeela Khan signing in. Weather: -8 and cloudy | All Wastewater System ROC General | 2025-12-08
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-08
ROC | December | KSSP - Scum Chamber 2 Low Level Alarm came in. Disregarded as per shift report | All Wastewater System ROC General | 2025-12-08
ROC | December | QVSSSC, Channel Grinder Overload Alarm//Inlet Channel Level loss of echo alarm, Cam B is investigating these alarms currently | All Wastewater System ROC General | 2025-12-01
ROC | December | Carter Dunn Signing In, -6D/Clear YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-04
ROC | December | NMSSBP- P4 vibration hihi alarm came in. Vibration rose with pump speed and fell below hihi alarm as speed slowed alarm cleared | All Wastewater System ROC General | 2025-12-05
ROC | December | RHAMF - Unit 1 pH Sensor Lo alarm came in. Sent an email to Marcos T. | All Wastewater System ROC General | 2025-12-06
ROC | December | SHSP- Screen room O2 hihi alarm came in. Disregard on shift report | All Wastewater System ROC General | 2025-12-07
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-03
ROC | December | BLSS- Screen Diff Lvl Hi Alarm. Disregard as per SCADA Report. | All Wastewater System ROC General | 2025-12-01
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-01
ROC | December | Adeela Khan signing out | All Wastewater System ROC General | 2025-12-05
ROC | December | Carter D signing Out | All Wastewater System ROC General | 2025-12-05
ROC | December | NBSP- Marcus R called back. Informed ROC it most likely caused by solids imbalances during colder temperatures. Changed controlling AIT to tank 2. Directed to give time for blowers to start up while DO recovers if issues come back in later | All Wastewater System ROC General | 2025-12-06
ROC | December | Carter Dunn Signing In, -14D/Clear | All Wastewater System ROC General | 2025-12-05
ROC | December | MTSS, Chris R on site, testing flood alarm, directed to disregard | All Wastewater System ROC General | 2025-12-05
ROC | December | Adam Button signing in -2 clear | All Wastewater System ROC General | 2025-12-05
ROC | December | YDSS+YNSS normal | All Wastewater System ROC General | 2025-12-06
ROC | December | KSSP - Cam B. is on site and will be stopping the effluent pumps. Will give a call back when work is complete | All Wastewater System ROC General | 2025-12-05
ROC | December | NBSP- Vortex 1 air scour uncm close alarm came in reset as per shift report | All Wastewater System ROC General | 2025-12-07
ROC | December | Carter D signing in, -1D/Clear | All Wastewater System ROC General | 2025-12-01
ROC | December | KBSP - Young J on site to complete maintenance on the hydrants. Young will be taking the wash pumps out of service for the duration of the maintenance which may last several days. | All Wastewater System ROC General | 2025-12-03
ROC | December | NBSP - Lance J on site to complete a generator test run. | All Wastewater System ROC General | 2025-12-02
ROC | December | SUSP - Lagoon flow LoLo and lagoon Hart comm alarm. Conatcted Chase J who stated that the lagoon pumps are active but the flowmeter is having issues and these alarms can be disregarded. | All Wastewater System ROC General | 2025-12-04
ROC | December | NMSSBP, Mech Screen 1 Overtorque alarm, alarm isn't able to clear, was originally running fine, contacted Marcos T as he will be out today but no response, will call again within 10 minutes 10:16, Marcos T called back, he is currently on site, Mechanical Screen 1 will be OOS for the night | All Wastewater System ROC General | 2025-12-07
ROC | December | Christian Van Beek signing out. | All Wastewater System ROC General | 2025-12-02
ROC | December | AUSSYS, Marcos T on site, running the generator and testing level/health and safety alarms | All Wastewater System ROC General | 2025-12-01
ROC | December | LSSS - Barry M on site for a generator test. | All Wastewater System ROC General | 2025-12-03
ROC | December | KSSP - Inlet channel hihi switch alarm. Channel grinder fault & hihi alarms still disregarded on operator shift report | All Wastewater System ROC General | 2025-12-04
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-05
ROC | December | Adam Button signing out YDSS+YNSS normal | All Wastewater System ROC General | 2025-12-07
ROC | December | KSSSQW - Rick L finished and leaving site. | All Wastewater System ROC General | 2025-12-03
ROC | December | Ethan U signing in Weather -9. | All Wastewater System ROC General | 2025-12-04
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-04
ROC | December | NBSP - Process bld temp hi/lo alarm. Alarm cleared after some time | All Wastewater System ROC General | 2025-12-05
ROC | December | JDSS- Noticed that wet well not cycling while pump 3 running in duty 1. Deactivated duty to allow it to cycle. | All Wastewater System ROC General | 2025-12-01
ROC | December | MTSP- Phil R on site for generator run and JHS checks | All Wastewater System ROC General | 2025-12-01
ROC | December | SEOC6, Talha H working on the OIT at SEOC6s1, please disregard Historian Heartbeat alarm. | All Wastewater System ROC General | 2025-12-01
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-02
ROC | December | SEOC, Barry M on site running the generator | All Wastewater System ROC General | 2025-12-02
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-05
ROC | December | KBSP- Eric S on site to work on alum LIT AUSSYS- Marcos Notifed ROC that force main 1 valve 2 has faulted and has not power after transferring back to utility. Marcos T issued workorder to CMS to take a look. Directed to disregard until CMS can troubleshoot | All Wastewater System ROC General | 2025-12-01
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-03
ROC | December | YDSS + YNSS Normal Connor Smith signing out | All Wastewater System ROC General | 2025-12-03
ROC | December | NMSSBP- Terry R on site for generator run | All Wastewater System ROC General | 2025-12-03
ROC | December | AUSS - Marcos T on site to complete a generator test. | All Wastewater System ROC General | 2025-12-03
ROC | December | NBSP- Brent St C. on site with Lance to rewire aeration basin 2 DO analyzer | All Wastewater System ROC General | 2025-12-03
ROC | December | NMSSHS- Terry R on site for generator run and to test high wetwell alarms and dialer. | All Wastewater System ROC General | 2025-12-01
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-01
ROC | December | GRSSWA- Mike B on site for generator run EGSSSC- Cam B on site for generator run and dry well flood test | All Wastewater System ROC General | 2025-12-01
ROC | December | Ethan U signing in | All Wastewater System ROC General | 2025-12-01
ROC | December | SEOC - Historian heartbeat alarm. Checked site, able to clear alarm. | All Wastewater System ROC General | 2025-12-08
ROC | December | LSSS - Barry M on site with electricians to complete generator testing. | All Wastewater System ROC General | 2025-12-08
ROC | December | HLSSBS - Cam B on site to complete a dry well flood test and a diesel generator test. | All Wastewater System ROC General | 2025-12-08
ROC | December | YDSS + YNSS normal | All Wastewater System ROC General | 2025-12-09
ROC | December | MTSP - Chris R onsite diverting as contractors cleaning clarifier for upgrade. Disregard lo effluent flow. | All Wastewater System ROC General | 2025-12-09
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-02
ROC | December | Christian Van Beek signing in. Weather: -6 and clear. | All Wastewater System ROC General | 2025-12-03
ROC | December | YDSS+YNSS normal Adam Button signing out | All Wastewater System ROC General | 2025-12-03
ROC | December | SHSP- Alum P6/7 no flow alarm came in. Reset as per shift report | All Wastewater System ROC General | 2025-12-01
ROC | December | JDSS - Chris C is on site and will be testing the dry well flood and hi/lo temp alarms | All Wastewater System ROC General | 2025-12-05
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-05
ROC | December | Carter Dunn Signing In, -2D/Snowing | All Wastewater System ROC General | 2025-12-07
ROC | December | SUSP - UV System Critical Failure, Common Critical alarm, UV Ch 1 Bank 1A/ 1B Low Level Fault, and UV system Lo UV Dosage alarms came in. Checked site. UV alarms went Normal after 5 mins. Trends indicate a 2 min drop, but UV system flow rate never hit 0. Called Chase J as directed by the UV Power Disruptions Interim, who confirmed that the levels and the intensity are okay and that as long as alarm was not active for more than 15 mins and that the flow level did not hit 0, then UV's are within compliance and alarms can be disregarded 23:01 - Alarms came back in. Called Chase J. who directed to switch the duties so that channel 2 bank b is in duty 1 and continue to monitor. Chase informed that alarms should clear in a couple mins 23:21 - Alarms have cleared #CONSULT | All Wastewater System ROC General | 2025-12-07
ROC | December | YDSS + YNSS normal | All Wastewater System ROC General | 2025-12-06
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-08
ROC | December | MTSS, Communication Loss to MTSS, Notified Ian W that the alarm has stayed for 10 minutes, he will look into it CMU5: W11481192 | All Wastewater System ROC General | 2025-12-02
ROC | December | Adeela Khan signing in. Weather: -6 and flurries | All Wastewater System ROC General | 2025-12-07
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-07
ROC | December | NBSP - Aeration Basin 1 Back DO Lo alarm came in. Checked site. Nothing on the DO system on the shift report. Called Marcus R. who will take a look at SCADA 02:05 - Marcus called back to inform that the alarm has been cleared and that if the alarm comes back in, place two blowers in manual to get the DO level back up #CONSULT | All Wastewater System ROC General | 2025-12-08
ROC | December | KSSP - Channel Aeration Blower 2 High Differential Pressure alarm came in. Higher priority alarm. Checked site. Aeration blower 1 is running in duty 1. Called Chase J. who directed to disregard for the night #CONSULT | All Wastewater System ROC General | 2025-12-08
ROC | December | JDSS - Chris C on site to complete work orders including a generator test and an eyewash station test. | All Wastewater System ROC General | 2025-12-04
ROC | December | RHAMF1, Marcos T called to inform the ROC that Unit 1 is OOS at this time, directed to disregard at this time | All Wastewater System ROC General | 2025-12-02
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-07
ROC | December | YDSS + YNSS normal | All Wastewater System ROC General | 2025-12-01
ROC | December | MTSS- Chris R on site for generator run | All Wastewater System ROC General | 2025-12-01
ROC | December | SECC OCF, Talha H resetting OIT, directed to disregard historian | All Wastewater System ROC General | 2025-12-02
ROC | December | Connor Smith signing in 0C Cloudy | All Wastewater System ROC General | 2025-12-03
ROC | December | RHAMF - Kyle C and Phil R on site for maintenance and testing. Directed to disregard alarms | All Wastewater System ROC General | 2025-12-04
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-09
ROC | December | SUSP - UV Ch 1 & 2 common minor & fault. Followed up with Neil O. Disregard as are old alarms that were reset. | All Wastewater System ROC General | 2025-12-08
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-03
ROC | December | SEOC - Eric S replaced O2 sensor . Leaving site | All Wastewater System ROC General | 2025-12-09
ROC | December | Connor Smith signing in -2C snow | All Wastewater System ROC General | 2025-12-09
ROC | December | Christian Van Beek signing out. | All Wastewater System ROC General | 2025-12-09
ROC | December | KSSSQW- Rick L and Parth P on site for annual calibrations | All Wastewater System ROC General | 2025-12-03
ROC | December | NBSP- Aeration basin 2 back DO lo alarm came in. Notified Marcus R. Will check SCADA #Consult | All Wastewater System ROC General | 2025-12-06
ROC | December | YDSS + YNSS normal Adeela Khan signing out | All Wastewater System ROC General | 2025-12-06
ROC | December | YDSS+YNSS normal | All Wastewater System ROC General | 2025-12-06
ROC | December | MTSP - DO levels in tank 2 became hi. Placed blower 1 man/off as per shift report 18:15 - DO Levels in tank 1 started dropping. Called Marcos T. who directed to change the DO tank selection so that tank 1 becomes the controlling. Marcos stated that if tank 2's DO starts dropping and hits the lo, switch the DO selection back to tank 2. #CONSULT | All Wastewater System ROC General | 2025-12-07
ROC | December | YDSS + YNSS normal | All Wastewater System ROC General | 2025-12-07
ROC | December | KSSP- UV CH.2 Bank 2A Lamp Fail. Disregard as per SCADA Report. | All Wastewater System ROC General | 2025-12-09
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-10
ROC | December | KSSP- Effluent Pressure Hi Alarm. Alarm cleared. | All Wastewater System ROC General | 2025-12-04
ROC | December | KSSP - UV Ch2 Bank 2A Adjacent Lamp Fail alarm came in. Disregarded as per shift report | All Wastewater System ROC General | 2025-12-08
ROC | December | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-12-17
ROC | December | KSSP- Sldg holding tank 1 fault alarm came in. Disregard on shift report | All Wastewater System ROC General | 2025-12-30
ROC | December | NBSSJA- Matt T onsite working on pump 1. Requested to place pump in manual duty 4. | All Wastewater System ROC General | 2025-12-16
ROC | December | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-12-17
ROC | December | SHSSDK - Marcus R testing hi wet well level as well | All Wastewater System ROC General | 2025-12-17
ROC | December | Gluzen Ramos Ong signing out | All Wastewater System ROC General | 2025-12-17
ROC | December | AUSS- P4 MV2 dich valve failed to open. Reset alarm | All Wastewater System ROC General | 2025-12-21
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-31
ROC | December | SUSP - Neil O informed Maintenance working on UV gate, disregard filter feed pump and UV alarm | All Wastewater System ROC General | 2025-12-17
ROC | December | JDSS- John D rebooting OIT. | All Wastewater System ROC General | 2025-12-16
ROC | December | KBSP - Reject sump pump 1 E-stop alarm. Disregard by SCADA review. Verified sump pump 2 running normally. | All Wastewater System ROC General | 2025-12-29
ROC | December | KCSSKR, Pump 2/3 faulted again notified Dan H the faults came in again, he will inform electrical of the issue and get them to look into it | All Wastewater System ROC General | 2025-12-19
ROC | December | MTSP - Admin building security intrusion alarm. FMC will contact Corp security. | All Wastewater System ROC General | 2025-12-17
ROC | December | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-12-17
ROC | December | Carter Dunn Signing In, -1D/Clear | All Wastewater System ROC General | 2025-12-22
ROC | December | YDSS + YNSS Normal Connor Smith signing out | All Wastewater System ROC General | 2025-12-22
ROC | December | RHAMF1, Unit 1 Diff Pressure 2 HI alarm (came in earlier in the day), Trending shows its slowly increasing and will most likely hit the hihi sometime during the night, in the past an operator was called and when to site to deal with said issue, notified Chris R of this observation and that the hihi will most likely be hit during the night. Directed to disregard at this current time. If 1 fan goes down that is fine however if 2 go down, Chris R would like a call. 21:21, Chris tried getting ahold of NAC but no response on their end, directed to disregard alarm. would still like a call if fans do turn off from the hihi alarm Consult | All Wastewater System ROC General | 2025-12-21
ROC | December | RHAMF1 - Security intrusion alarm, Chris R will contact NAC. | All Wastewater System ROC General | 2025-12-30
ROC | December | 09:05 - SHSP - Marcus R. working on UVs | All Wastewater System ROC General | 2025-12-18
ROC | December | Carter Dunn Signing Out | All Wastewater System ROC General | 2025-12-22
ROC | December | KSSP - Mem chem Rm MUA-7 Temp switch lo, appears local/off, informed Kevin K, disregard for the night Consult | All Wastewater System ROC General | 2025-12-26
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-24
ROC | December | Christian Van Beek signing in. Weather: -11C and clear. | All Wastewater System ROC General | 2025-12-27
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-27
ROC | December | SEOC- O2 monitor hihi and OOR alarms came in. Disregard on shift report | All Wastewater System ROC General | 2025-12-21
ROC | December | NMSSBP, Terry R on site working on the mechanical screens, directed to disregard alarms on site till he is finished | All Wastewater System ROC General | 2025-12-19
ROC | December | SHSSDK- Kingsley M rebooting OIT. | All Wastewater System ROC General | 2025-12-17
ROC | December | Adam Button signing out | All Wastewater System ROC General | 2025-12-31
ROC | December | Connor Smith signing out | All Wastewater System ROC General | 2025-12-31
ROC | December | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-12-26
ROC | December | Ethan U signing in Weather 0. | All Wastewater System ROC General | 2025-12-28
ROC | December | KSSSQW - Boiler 1 fault, informed Chris C, will head to site CMU = 11529110 23:46 - Chris finished at site | All Wastewater System ROC General | 2025-12-19
ROC | December | Connor Smith signing in -7C Clear | All Wastewater System ROC General | 2025-12-22
ROC | December | NBSP - UV system minor fault alarm. Disregard as per shift report. Confirmed UV bank 1B | All Wastewater System ROC General | 2025-12-29
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-23
ROC | December | Carter Dunn Signing Out | All Wastewater System ROC General | 2025-12-23
ROC | December | Angelica Chepiga signing in | All Wastewater System ROC General | 2025-12-24
ROC | December | SUSP- Kevin K called and requested a Vac Truck for a clogged vortex. Notified Dane from WESSUC. | All Wastewater System ROC General | 2025-12-22
ROC | December | KSSSQW - Wet well 1&2 Hi and HiHi level alarms. Kevin K requested disregard alarms, working on pumps. | All Wastewater System ROC General | 2025-12-23
ROC | December | Ethan Ullalkar signing out. | All Wastewater System ROC General | 2025-12-29
ROC | December | SHSP - Alum pump 6 no flow alarm. Notified Gavin W, he is on site, will check. | All Wastewater System ROC General | 2025-12-29
ROC | December | HLSSBS - Kevin K leaving site. All alarms cleared, channel grinder running. KSSP - Alum Chem rm MUA-11 Diff pressure switch alarm- Kevin K requested to disregard alarm. | All Wastewater System ROC General | 2025-12-29
ROC | December | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-12-26
ROC | December | SEOC - Evgeny S working on network switches and ahs directed to disregard the historian heartbeat alarm. | All Wastewater System ROC General | 2025-12-18
ROC | December | YDSS + YNSS normal | All Wastewater System ROC General | 2025-12-23
ROC | December | KSSSQW - Boiler 1 Fault alarm came in. Checked site. Called Neil O. who will head to site. CMU5 Created W11551791 11:44 - Neil O. called back to inform that he is finished on site and that if the alarm comes back in, it can be disregarded for the night #CONSULT | All Wastewater System ROC General | 2025-12-31
ROC | December | *WRONG BOOK ENTRY* | All Wastewater System ROC General | 2025-12-31
ROC | December | SUSP - UV Ch1 common critical alarm, hihg level, system critical failure. Status went to normal, cleared upon acknowledging alarm. UV2b running | All Wastewater System ROC General | 2025-12-28
ROC | December | Ethan Ullalkar signing in Weather: -4 | All Wastewater System ROC General | 2025-12-19
ROC | December | SUSP, UV System Critical Fail//UV CH 1 Common critical/Hi level alarm, Alarm cleared immediately however shift report doesn't say to disregard, also to note, trends are abnormal, contacted Kevin K, he will look into the issue consult | All Wastewater System ROC General | 2025-12-28
ROC | December | LSSS - Bar screen 1 fault, bar screen 2 running. Email sent to area | All Wastewater System ROC General | 2025-12-29
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-29
ROC | December | MTSS - Pump 1 running in hydrostatic mode alarm. Wet well 1 Hydrostatic level low/low. Pump 2 started in hydrostatic mode, 2 pumps on. Pumps stopped, wet well at 1,0m. Both pumps interlocked. Notified Chris R. He will check SCADA. #Consult #CMU5 W11540699 | All Wastewater System ROC General | 2025-12-26
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-27
ROC | December | KSSSQW - Dry well supply fan VFD fault/ not ready. Pump 1-4 VFD fault, hydrostatic/ultrasonic hi. Noticed pump 1 running in local/on. No operator appears signed in onsite. Called Kevin K,m confirmed not on site. During phone call noticed pump1 switched back to auto. Able to clear hi level alarms but VFD related alarms outstanding. Kevin K will head to site. CMU = 11543313 16:25 - Kevin K finished at site | All Wastewater System ROC General | 2025-12-27
ROC | December | KCSSKR - Generator running, no pumps running at the time as may cause faults when switching to generator. Informed Gavin W. Will monitor if pumps can run Consult | All Wastewater System ROC General | 2025-12-28
ROC | December | Adeela Khan signing in. Weather: -2 and cloudy | All Wastewater System ROC General | 2025-12-24
ROC | December | Adam Button signing in | All Wastewater System ROC General | 2025-12-30
ROC | December | Christian Van Beek signing out. | All Wastewater System ROC General | 2025-12-18
ROC | December | Gluzen Ramos Ong signing out at 14:00 | All Wastewater System ROC General | 2025-12-18
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-29
ROC | December | Ethan Ullalkar signing out. | All Wastewater System ROC General | 2025-12-30
ROC | December | MTSS - Chris R finished at site, Left in PAC monde with LIT 1. Hydrostatic alarms may still come in, don't reset. Will continue to monitor. Disregard hydrostatic alarms. SUSP - UV CH.1 high level, critical fault, common critical alarm. All went to normal status and cleared when acknowledged. Site appears fine with Bank 2B running with intensity reading | All Wastewater System ROC General | 2025-12-26
ROC | December | KCSSKR, Generator Running/Pump 1 Fault, Notified Gavin W, he will look into it, once we know who is heading to site, will make CMU5 10:07, Young J is heading to site CMU5: W11546881 | All Wastewater System ROC General | 2025-12-29
ROC | December | Adeela Khan signing in. Weather: -7C and snowing | All Wastewater System ROC General | 2025-12-31
ROC | December | SEOC - Evgeni S finished at site | All Wastewater System ROC General | 2025-12-17
ROC | December | SHSP - Screen Room O2 Cons HiHi alarm, disregard as per SCADA review. | All Wastewater System ROC General | 2025-12-18
ROC | December | Ethan Ullalkar signing out. | All Wastewater System ROC General | 2025-12-20
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-21
ROC | December | Carter D Signing Out | All Wastewater System ROC General | 2025-12-19
ROC | December | YDSS+YNSS normal Adam Button signing out | All Wastewater System ROC General | 2025-12-16
ROC | December | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-12-23
ROC | December | Christian Van Beek signing in. Weather: -2C and clear. | All Wastewater System ROC General | 2025-12-24
ROC | December | HLSSBS, Channel Grinder Emergency Stop, notified Kevin K, directed to disregard for the night 16:13, Kevin K is heading to site CMU5: W11547019 | All Wastewater System ROC General | 2025-12-29
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-31
ROC | December | SHSP - Marcus R called to inform that there will be alarms triggered related to the aeration blower maintenance. Marcus stated they can be disregarded. | All Wastewater System ROC General | 2025-12-18
ROC | December | SUSP- Influent flow fault alarm came notified Chris C. Directed to disregard | All Wastewater System ROC General | 2025-12-22
ROC | December | Angelica Chepiga signing in, weather +2C | All Wastewater System ROC General | 2025-12-17
ROC | December | YDSS+YNSS normal | All Wastewater System ROC General | 2025-12-21
ROC | December | RHAMF1- Unit Diff 1 Pressure 2 hi alarm came in. Notified Chris R. Will take a look on SCADA #consult | All Wastewater System ROC General | 2025-12-21
ROC | December | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-12-24
ROC | December | BLSS- Young J onsite. Shutting down all pumps for switch over to South Force Main | All Wastewater System ROC General | 2025-12-16
ROC | December | YDSS + YNSS Normal Ethan U singing out | All Wastewater System ROC General | 2025-12-17
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-19
ROC | December | EGSSSC - Wet well overflow fault. Checked site, trends indicate normal operations. Disregard alarm as per the shift report. | All Wastewater System ROC General | 2025-12-18
ROC | December | YDSS+YNSS normal | All Wastewater System ROC General | 2025-12-21
ROC | December | SEOC6- Talha H rebooting OIT. Disregard Heartbeat Alarm. | All Wastewater System ROC General | 2025-12-16
ROC | December | RHAMF1- Marcos T onsite with CPD and contractor working on Fan 2. Disregard alarms while onsite. | All Wastewater System ROC General | 2025-12-22
ROC | December | QVSSSC- H2S hihi alarm and inlet channel hi hi switch alarm came in. Notified Cam B. spike in H2S reading while opening by pass. Everyone on site okay. | All Wastewater System ROC General | 2025-12-22
ROC | December | KSSP - In cycle Aeration started alarm. Kevin K will add alarm to SCADA report as disregard. | All Wastewater System ROC General | 2025-12-24
ROC | December | MTSP - Aeration Tank 1 DO Lo alarm came in. Placed blower 1 man/on as per shift report 18:46 - DO was getting high in tank 2. Placed blower 1 back to auto | All Wastewater System ROC General | 2025-12-31
ROC | December | EGSSSC, Parth P/Rick L working on the overflow meter | All Wastewater System ROC General | 2025-12-19
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-26
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-25
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-25
ROC | December | Christian Van Beek signing in. Weather: -1C and clear. | All Wastewater System ROC General | 2025-12-25
ROC | December | KSSSQW - Pump 3 vibration out of range alarm. This alarm has triggered three times and each time pump 3 has been off. Alarm clears every time. If this issue persists will send an email to area ops. | All Wastewater System ROC General | 2025-12-25
ROC | December | Angelica Chepiga signing in, weather -7C | All Wastewater System ROC General | 2025-12-25
ROC | December | Ethan Ullalkar signing out. | All Wastewater System ROC General | 2025-12-26
ROC | December | SUSP - Sludge tank level hihi, confirmed with Kevin K he will be heading their to site today | All Wastewater System ROC General | 2025-12-27
ROC | December | SHSP - UV system major fault alarm. Checked site, UV Bank B is active. Trending shows normal channel water level and normal UV intensity. Attempted to clear alarm, unable to clear. Called Gavin W who directed to disregard until Monday at 09:00. #consult | All Wastewater System ROC General | 2025-12-27
ROC | December | KSSSQW - Pump 3 vibration out of range alarm. Checked site, pump 3 is not running and was not running before the alarm triggered. On going issue. Reset alarm. AUSSSR - Aysix system heartbeat alarm. Able to clear alarm. NMSSBP - Pump 4 vibration hi alarm. Checked site, pump is running in duty 2 at a relatively high, but not abnormal, speed. Able to clear alarm | All Wastewater System ROC General | 2025-12-27
ROC | December | KSSP - ZW3 shutdown alarm on permeate turbidity OOR. Checked site, three membranes are in production with one on stand by and train 3 shut down. Called Kevin K who stated that this membrane can remain shutdown for the remainder of the night. If a second membrane shutdown occurs, Kevin would like to be contacted. | All Wastewater System ROC General | 2025-12-27
ROC | December | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-12-26
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-26
ROC | December | RHAMF- Joe O from CPD onsite with contractor. Requested to reset make up air unit failed to start alarm. | All Wastewater System ROC General | 2025-12-31
ROC | December | YDSS+YNSS normal | All Wastewater System ROC General | 2025-12-21
ROC | December | NMSSBP - Wet well1 & 2 high level, able to clear after next duty became active | All Wastewater System ROC General | 2025-12-28
ROC | December | PVSS- H2S Out of range alarm. Disregard as per SCADA review. | All Wastewater System ROC General | 2025-12-29
ROC | December | EGSSSC, Rick L/Parth P is finished on site | All Wastewater System ROC General | 2025-12-19
ROC | December | AUSSYS, Boiler 1 Fault//Gycol Inlet Pressure lo alarm, Chris R is heading to site. He will also be heading to site. Once he is finished at AUSSYS, he will be heading to AUSS to look at the Pump 1 leakage alarm just to make sure its okay. Pump currently is man/off and will make a cmu maint request for the pump on Monday to be looked at. directed to disregard for weekend CMU5: W11529163 | All Wastewater System ROC General | 2025-12-20
ROC | December | SUSP- UV system major fault/ common major/1 bank 1a+b Major/ system critical failure alarms came in. Plant off and diverting to lagoon. Notified Neil O. directed to disregard | All Wastewater System ROC General | 2025-12-22
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-23
ROC | December | YDSS+YNSS normal | All Wastewater System ROC General | 2025-12-21
ROC | December | Adam Button signing out | All Wastewater System ROC General | 2025-12-30
ROC | December | SUSP- diversion tank level LOE disregard on shift report | All Wastewater System ROC General | 2025-12-30
ROC | December | Angelica Chepiga signing in | All Wastewater System ROC General | 2025-12-23
ROC | December | SUSSWB - Alarm panel low battery/low battery restored alarms on the dialer. No alarms on SCADA, trends normal. | All Wastewater System ROC General | 2025-12-26
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-21
ROC | December | Ethan Ullalkar signing out. | All Wastewater System ROC General | 2025-12-21
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-20
ROC | December | SEOC - OCF O2 monitor 4 lolo. Disregard as per shift report | All Wastewater System ROC General | 2025-12-20
ROC | December | AUSS, Pump 1 Leakage alarm, placed pump 1 man/off, Pump was not running when alarm came in. Will send email to operator so they can look at it on sunday 10:47, Chris R is heading to AUSSYS to look at the Gycol inlet pressure/Boiler fault alarm, once he is done at AUSSYS, he will be heading to AUSS to look at the pump 1 leak alarm | All Wastewater System ROC General | 2025-12-20
ROC | December | Carter Dunn Signing Out | All Wastewater System ROC General | 2025-12-31
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-22
ROC | December | NMVCBP - Marcus T onsite testing hi level | All Wastewater System ROC General | 2025-12-17
ROC | December | Carter Dunn Signing Out | All Wastewater System ROC General | 2025-12-20
ROC | December | RHAMF1- Joe O from CPD heading to site and will be meeting NAC there to troubleshoot MUA. | All Wastewater System ROC General | 2025-12-31
ROC | December | AUSSYS- Kingsley M rebooting OIT. Disregard Heartbeat Alarm. | All Wastewater System ROC General | 2025-12-16
ROC | December | NBSP- UV System Minor fault alarm , checked site, UV Bank 1B is running, disregard alarm as per SCADA review. | All Wastewater System ROC General | 2025-12-16
ROC | December | SHSP- Marcus R called and requested to notify if Alum no flow alarm comes in. | All Wastewater System ROC General | 2025-12-16
ROC | December | Connor Smith signing out | All Wastewater System ROC General | 2025-12-16
ROC | December | KCSSKR - Control panel power fail alarm, cleared right away. Trending ok. | All Wastewater System ROC General | 2025-12-17
ROC | December | KSSP - Kevin K on site with maintenance to complete work on the membrane filtration tanks. Kevin and operators will be draining tanks to complete the maintenance. Kevin K requested all alarms be disregarded. | All Wastewater System ROC General | 2025-12-16
ROC | December | SUSSSR - Pumps in ultrasonic mode. Checked site, trends show a spike of the wetwell level which activated ultrasonic mode. Trending does not show the level declining. Called Niel O who will check SCADA. | All Wastewater System ROC General | 2025-12-16
ROC | December | SHSP- Andrew from Ferguson Electric is on site to work on generator 11:05- SHSP- Andrew from Ferguson Electric is done on site to work on generator | All Wastewater System ROC General | 2025-12-30
ROC | December | YDSS+ YNSS Normal | All Wastewater System ROC General | 2025-12-20
ROC | December | GRSSWA- John D rebooting OIT. | All Wastewater System ROC General | 2025-12-16
ROC | December | NBSP - Sludge thickener level hihi alarm. Checked site, plant was batch wasting to the thickener prior to alarm. Lance J is on site. Will follow up with Lance J if level does not come down throughout the day | All Wastewater System ROC General | 2025-12-16
ROC | December | YDSS + YNSS Normal Connor Smith signing out | All Wastewater System ROC General | 2025-12-17
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-21
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-25
ROC | December | NBSP, Mech Bar Screen General/OOS Alarm, Gavin W is heading to site CMU5: W11546958 | All Wastewater System ROC General | 2025-12-29
ROC | December | SEOC - Evgeny S working on OIT | All Wastewater System ROC General | 2025-12-17
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-25
ROC | December | Connor Smith signing in | All Wastewater System ROC General | 2025-12-16
ROC | December | NMSSBP- Mech screen 1 overtorque alarm, Screen 2 running in auto okay. Notified Chris R, he will attend site. # CMU5 W11536306 | All Wastewater System ROC General | 2025-12-23
ROC | December | YDSS+YNSS NORMAL Angelica Chepiga signing out | All Wastewater System ROC General | 2025-12-17
ROC | December | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-12-18
ROC | December | LSSS, Marcos T on site, working on the bar screen CMU5: W11546867 | All Wastewater System ROC General | 2025-12-29
ROC | December | SHSSDK - Pump1 VFD fault, updated Gavin W of fault, will make his way over shortly | All Wastewater System ROC General | 2025-12-29
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-29
ROC | December | KSSP - Train 3 shutdown, ZW3 permeate turbidity OOR. Informed Kevin K, okay to disregard he started it back up for backwash, will try again if shutdown will leave off for the night. ZW4 TMP control delta high disregard as per shift report Consult | All Wastewater System ROC General | 2025-12-28
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-31
ROC | December | KSSP - UV Panel 1 lamp low intensity alarm. UV1 running, intensity reading 39% | All Wastewater System ROC General | 2025-12-29
ROC | December | Connor Smith signing in -5C Snowy | All Wastewater System ROC General | 2025-12-31
ROC | December | RHAMF1- MAU failed to start alarm outstanding, Dave and Alex from NAC conference called ROC (708-880-0979). Timing sequence issue with change in temps from initially setpoints is causing the failed to start alarm. Site visit required to fix timing issue but Alex will start in manual to allow pre heating sequence to be bypassed and get unit running. | All Wastewater System ROC General | 2025-12-31
ROC | December | NBSP - Mech. Bar screen OOS, general alarm. Informed Gavin W. Disregard for the night Consult | All Wastewater System ROC General | 2025-12-29
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-22
ROC | December | Ethan Ullalkar signing out. | All Wastewater System ROC General | 2025-12-27
ROC | December | KBSP, Diversion Tank Lvl hihi Alarm, nothing on shift report to say to disregard, notified Gavin W, he will look into it. If he doesn't call back, directed to disregard 12:24, Gavin W called back, directed to disregard consult | All Wastewater System ROC General | 2025-12-28
ROC | December | SUSP - UV system critical failure alarm, alarm cleared by OPs. Neil O working on site. | All Wastewater System ROC General | 2025-12-23
ROC | December | KSSP - UV Ch. 1 bank 1A low UV intensity fault, checking site UV1 running with intensity 39% | All Wastewater System ROC General | 2025-12-30
ROC | December | KBSP - Lauren S testing Filter bypass alarm. | All Wastewater System ROC General | 2025-12-23
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-24
ROC | December | Angelica Chepiga signing out | All Wastewater System ROC General | 2025-12-23
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-27
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-27
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-18
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-30
ROC | December | YWS + NYWS Normal | All Wastewater System ROC General | 2025-12-30
ROC | December | SHSP - WAS pump 2 uncommanded stop alarm. Checked site, trending shows that WAS pump 2 was not running when the alarm triggered. Able to reset alarm | All Wastewater System ROC General | 2025-12-25
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-27
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-30
ROC | December | Connor Smith signing in | All Wastewater System ROC General | 2025-12-18
ROC | December | AUSSYS - Marcos T on site to test the high wet well level alarm. | All Wastewater System ROC General | 2025-12-18
ROC | December | Angelica Chepiga signing out | All Wastewater System ROC General | 2025-12-24
ROC | December | NBSSJA - Diesel tank level HiHi alarm, disregard as per SCADA review. | All Wastewater System ROC General | 2025-12-26
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-27
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-27
ROC | December | Carter Dunn Signing In, -6D/Clear | All Wastewater System ROC General | 2025-12-20
ROC | December | BLSS- John D rebooting OIT. | All Wastewater System ROC General | 2025-12-16
ROC | December | SUSP - Bar screen hi level alarm. Checked site, inlet flow recently spiked at SUSSWB pumped down. Able to reset alarm after flows reduced. | All Wastewater System ROC General | 2025-12-27
ROC | December | Carter D Signing In, 5D/Clear | All Wastewater System ROC General | 2025-12-29
ROC | December | SHSP - Marcus R on site to complete UV system maintenance. May see UV related alarms that can be disregarded. | All Wastewater System ROC General | 2025-12-16
ROC | December | Carter D signing in, -2D/Clear | All Wastewater System ROC General | 2025-12-28
ROC | December | YDSS+YNSS normal Adam Button signing out | All Wastewater System ROC General | 2025-12-22
ROC | December | SEOC6- Shaft 6/7 O2 monitor alarm. Disregard as per SCADA review. | All Wastewater System ROC General | 2025-12-23
ROC | December | KSSP - Aeration tank 1 inlet DO fault alarm. Value recovered right away and alarm cleared. | All Wastewater System ROC General | 2025-12-16
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-23
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-19
ROC | December | KBSP, Reject Sump Pump 1 E. Stop Alarm, Critical alarm, As per Lance J shift report, Reject sump pump 1 has been faulting on a E-stop alarm, directed to disregard from shift report. If sump pump 2 alarm comes in will notify operator. Will notify Night ROC of the on going issue | All Wastewater System ROC General | 2025-12-20
ROC | December | YDSS+ YNSS Normal | All Wastewater System ROC General | 2025-12-28
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-19
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-25
ROC | December | MTSS - Sewage pump 1 on hydrostatic mode. Pump 1 running, interlocks pump running drawing wet well to lolo level before shutting down. Informed Chris R, will look into issue & head to site. Requested PCS support on issue as well. Informed Kyle C who look into issue. Place pump 1 man/off CMU (Chris R) = 11543170 CMU (Kyle C) = 11543177 9:51 - Disable duty rotation to keep pump 2 in duty 1 11:03 - Chris R finished at site, will leave pump 1 off for the night due to outstanding issue. Pump 1 can still run if needed but may trigger that hydronic mode tat needs to be reset onsite. Pump 2 will run for the night | All Wastewater System ROC General | 2025-12-26
ROC | December | YDSS+ YNSS Normal | All Wastewater System ROC General | 2025-12-20
ROC | December | Adam Button signing in -10 Clear | All Wastewater System ROC General | 2025-12-21
ROC | December | YDSS+YNSS Normal | All Wastewater System ROC General | 2025-12-21
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-21
ROC | December | SUSP- Neil O finished onsite. Site back to normal operations. | All Wastewater System ROC General | 2025-12-22
ROC | December | GRSSWA - Satnam M finished at site | All Wastewater System ROC General | 2025-12-17
ROC | December | Adeela Khan signing out | All Wastewater System ROC General | 2025-12-19
ROC | December | Christian Van Beek signing in. | All Wastewater System ROC General | 2025-12-19
ROC | December | SHSP - Gavin W finished at site KCSSKR - Informed Gavin W of dewatering press overload, and pump2 & 3 fault after generator shutting down. Will head to site to reset and placed pump 1 in auto CMU = 11543538 | All Wastewater System ROC General | 2025-12-28
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-22
ROC | December | Carter Dunn Signing In, 4D/Rain | All Wastewater System ROC General | 2025-12-19
ROC | December | KSSP - Scum Chmbr 2 pump 2 overload alarm. Disregard as per shift report for Scum pump and tank/chamber alarms | All Wastewater System ROC General | 2025-12-29
ROC | December | SHSP - RAS combined no flow, finding all 3 RAS pumps are showing OOS. Informed Gavin W, will take a look Consult | All Wastewater System ROC General | 2025-12-29
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-17
ROC | December | EGSSSC - Wet well overflow fault alarm, disregard as per SCADA review. | All Wastewater System ROC General | 2025-12-17
ROC | December | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-12-17
ROC | December | MTSS - Chris R remaining on site trying PAC mode after pump 2 still triggering hydrostatic mode | All Wastewater System ROC General | 2025-12-26
ROC | December | SHSP - Gavin W finished at site, Bank 1B back in service | All Wastewater System ROC General | 2025-12-26
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-26
ROC | December | MTSS - Wetwell 1 high level switch, disregard as per Chris R. using LIT1 as controlling now Consult | All Wastewater System ROC General | 2025-12-26
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-26
ROC | December | MTSP - Man/start blower 1 as Aeriation tank DO lo | All Wastewater System ROC General | 2025-12-26
ROC | December | Bayview OCF - Phil R onsite changing filters onsite | All Wastewater System ROC General | 2025-12-17
ROC | December | KSSP - UV Ch 1 bank 1 A lamp fail. Disregard as per shift report | All Wastewater System ROC General | 2025-12-18
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-18
ROC | December | QVSSSC- Inlet Channel High Switch Alarm. Disregard as per SCADA Report. | All Wastewater System ROC General | 2025-12-23
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-30
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-24
ROC | December | Adeela Khan signing in. Weather: 3C and cloudy | All Wastewater System ROC General | 2025-12-23
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-24
ROC | December | Christian Van Beek signing in. Weather: -7 C and clear. | All Wastewater System ROC General | 2025-12-16
ROC | December | NBSP - Eric S finished onsite with O2 sensor | All Wastewater System ROC General | 2025-12-17
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-20
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-20
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-20
ROC | December | SUSP - UV channel 1 high level and common critical alarms. Checked site, UV channel 2 is active. UV channel 1 is not active. Alarm status changed to normal immediately after the alarm was triggered. Alarms reset themselves on acknowledgement. | All Wastewater System ROC General | 2025-12-25
ROC | December | YDSS + YNSS Normal Connor Smith signing out | All Wastewater System ROC General | 2025-12-30
ROC | December | Adam Button signing in | All Wastewater System ROC General | 2025-12-31
ROC | December | KSSP - Makeup Air Unit 5 Differential Pressure switch alarm came in. Disregarded as per shift report KSSP - Alum Chemical Room MUA 11 differential pressure switch hi alarm came in. Checked site. Shift report indicates not to disregard chemical room MUA alarms. Called Neil O. who informed he was in that room today and all is okay and alarm can be disregard until tomorrow #CONSULT | All Wastewater System ROC General | 2025-12-31
ROC | December | NBSSJA- Diesel tank level HiHi alarm, disregard as per SCADA review. | All Wastewater System ROC General | 2025-12-17
ROC | December | Angelica Chepiga signing in | All Wastewater System ROC General | 2025-12-29
ROC | December | AUSSSR - Line 1 flushing valve failed to open , Line 1 failed to close alarms. Cleared alarms. Line 1 available. | All Wastewater System ROC General | 2025-12-17
ROC | December | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-12-17
ROC | December | Connor Smith signing in 3C Clear | All Wastewater System ROC General | 2025-12-17
ROC | December | NMSSBP- Terry C on site to work on barscreen 1 11:57-NMSSBP- Terry C done on site was able to cycle bar screen but will need additional work. Placed in auto and Central east wastewater team will determine whether or not to return it to service for the night | All Wastewater System ROC General | 2025-12-31
ROC | December | YDSS + YNSS Normal Christian Van Beek signing out. | All Wastewater System ROC General | 2025-12-16
ROC | December | NMSSBP- Chris R finished onsite. If overtorque comes back in requested to place Screen 1 Gate 1 Valve closed and leave outstanding until the morning. | All Wastewater System ROC General | 2025-12-23
ROC | December | KSSSQW - Boiler 1 fault alarm. Notified Kevin K, he will check. | All Wastewater System ROC General | 2025-12-29
ROC | December | QVSSSC - Inlet channel High switch alarm, disregard as per SCADA review. | All Wastewater System ROC General | 2025-12-29
ROC | December | KSSP - ZW3 TMP Control Delta High alarm. Disregarded as per shift report | All Wastewater System ROC General | 2025-12-31
ROC | December | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-12-16
ROC | December | Angelica Chepiga signing in | All Wastewater System ROC General | 2025-12-30
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-16
ROC | December | Ethan U signing in Weather -9. | All Wastewater System ROC General | 2025-12-29
ROC | December | BLSS- Gavin W onsite testing high wetwell level alarm. | All Wastewater System ROC General | 2025-12-16
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-31
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-18
ROC | December | Adam Button signing out | All Wastewater System ROC General | 2025-12-21
ROC | December | LSSS- Ric L onsite for work on bar screen differential analyzer 14:20- Finished onsite. | All Wastewater System ROC General | 2025-12-16
ROC | December | SEOC4 - Talha H working on OIT. Disregard heartbeat alarm. | All Wastewater System ROC General | 2025-12-16
ROC | December | Angelica Chepiga signing out | All Wastewater System ROC General | 2025-12-18
ROC | December | NMSSBP- Screw Press Emerg Stop Alarm, Screw Conveyor Emerg Stop Alarm. Called Dan K. He is onsite working on it with Chris R. | All Wastewater System ROC General | 2025-12-22
ROC | December | YDSS+YNSS | All Wastewater System ROC General | 2025-12-21
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-26
ROC | December | SHSP - Screen room O2 concentration hihi. Checked site, trending shows a spike of the O2 concentration. The variability of the readings indicate a possible issue with the sensor. Will monitor. | All Wastewater System ROC General | 2025-12-26
ROC | December | SHSP/SHSSDK- Site Power Fails. Notified Marcus R. He will look into it. | All Wastewater System ROC General | 2025-12-17
ROC | December | Ethan Ullalkar signing in | All Wastewater System ROC General | 2025-12-18
ROC | December | Connor Smith signing out | All Wastewater System ROC General | 2025-12-18
ROC | December | Carter D Signing In, -4D/Clear | All Wastewater System ROC General | 2025-12-21
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-20
ROC | December | Adam Button signing in | All Wastewater System ROC General | 2025-12-22
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-22
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-23
ROC | December | KSSP - Grit vortex 2 iso valve failed to close alarm. Checked site, grit vortex 2 is duty 1 and active. SCADA shows the valve as in auto and travelling. Unable to clear alarm and no details on shift report. Contacted Kevin K who will check SCADA. 20:59 - KSSP - Kevin K called back to inform that he swapped the inlet flow channels and the grit vortex iso valve failed to close alarm can be disregarded until Monday at 09:00 when it will be investigated on site. #consult | All Wastewater System ROC General | 2025-12-27
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-27
ROC | December | GRSSWA - Building security intrusion alarm. FMC will notify corporate security. | All Wastewater System ROC General | 2025-12-16
ROC | December | SUSP - Diversion EQ Tank level LOE alarm, disregard as per SCADA review. | All Wastewater System ROC General | 2025-12-16
ROC | December | Ethan U signing in Weather: 3c | All Wastewater System ROC General | 2025-12-20
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-19
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-20
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-29
ROC | December | SHSP- Screen room O2 conc Hi alarm, disregard as per SCADA review. | All Wastewater System ROC General | 2025-12-18
ROC | December | YDSS + YNSS Normal Christian Van Beek signing out. | All Wastewater System ROC General | 2025-12-25
ROC | December | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-12-25
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-20
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-20
ROC | December | AUSSYS, Boiler 1 Fault, notified Chris R, he will look into it, if a lo temp alarm comes in, he would like a call consult | All Wastewater System ROC General | 2025-12-20
ROC | December | Ethan U signing in Weather: 3c | All Wastewater System ROC General | 2025-12-20
ROC | December | KSSP - Parth P and Rick L on site to complete an inspection of an oxygen sensor. | All Wastewater System ROC General | 2025-12-19
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-29
ROC | December | Adeela khan signing out | All Wastewater System ROC General | 2025-12-24
ROC | December | KBSP - Reject sump pump 1 e stop alarm. Checked site, sump pump 2 is ready and available and rotated into duty 1. Called Lauren S to inform. | All Wastewater System ROC General | 2025-12-24
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-31
ROC | December | YDSS + YNSS Normal Christian Van Beek signing out. | All Wastewater System ROC General | 2025-12-24
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-25
ROC | December | Connor Smith signing in 0C Snowy | All Wastewater System ROC General | 2025-12-23
ROC | December | SHSP- Diesel Generator Alarm. Power blip occurred. Appears that UV shut down and started back up immediately. Notified Lance J. He is on his way to site. SHSSDK- Generator Running Alarm. Power Blip. Cleared alarm. CONSULT | All Wastewater System ROC General | 2025-12-23
ROC | December | SECC, Hydrogen Peroxide Pump 3 Leak/Fault, Notified Chris R, directed to disregard 06:04, Chris S is heading to site CMU5: W11551676 | All Wastewater System ROC General | 2025-12-31
ROC | December | KSSP - Train 3 TMP control delta hi alarm. Checked site, train 3 is the only train in production at the moment. SCADA shows that there are TMP corrective actions in progress. Will monitor site. Shift report directs to disregard alarm. | All Wastewater System ROC General | 2025-12-27
ROC | December | SHSP - UV system major fault. UV still running. Informed Lance J, will head to site to investigate CMU = 11529100 22:50 - Lance J finished at site YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-19
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-24
ROC | December | Ethan U signing in Weather -9. | All Wastewater System ROC General | 2025-12-27
ROC | December | Christian Van Beek signing out. | All Wastewater System ROC General | 2025-12-28
ROC | December | AUSS - wet well hi level, duty 4 active and pumping down wet well, able to clear alarm | All Wastewater System ROC General | 2025-12-28
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-29
ROC | December | YDSS + YNSS Normal KSSP, ZW5 TMP Control Delta Hi Alarm, as per Kevin K shift report, directed to disregard | All Wastewater System ROC General | 2025-12-28
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-28
ROC | December | MTSP - Aeration Tank 1 Do Lo alarm came in. Checked site. Blower 1 which is a duty 2 blower had just started up in auto. After 4 mins, DO levels rose above the lo level. | All Wastewater System ROC General | 2025-12-24
ROC | December | Adeela Khan signing out | All Wastewater System ROC General | 2025-12-25
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-25
ROC | December | MTSP - Thickening tank level fault. Disregard as per shift report | All Wastewater System ROC General | 2025-12-26
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-27
ROC | December | NBSP - Lance J onsite testing High sanitary Serwer pump test | All Wastewater System ROC General | 2025-12-17
ROC | December | NMSSBP- Mech screen 1 over torque alarm came in. Notified Dan K will see if Chris R can attend site. | All Wastewater System ROC General | 2025-12-30
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-30
ROC | December | Christian Van Beek signing in. Weather: 1 C and clear. | All Wastewater System ROC General | 2025-12-18
ROC | December | RHAMF1- Makeup Air Unit Failed to Start. Dave from NAC called and requested to reset alarm and call back if it comes in again. Alarm came back in 5 minutes later. Notified Dave. He will inform the NAC Tech. | All Wastewater System ROC General | 2025-12-31
ROC | December | KSSP - RSHW Grit Room Oxygen LoLo alarm came in. Checked site. Shift report directs to disregard lo alarm. Called Chris C. who directed to disregard alarm for the night. #CONSULT | All Wastewater System ROC General | 2025-12-19
ROC | December | HMSS- Young J isolating pump due to check valve issue. | All Wastewater System ROC General | 2025-12-23
ROC | December | KSSP- Mike B testing gas detectors. | All Wastewater System ROC General | 2025-12-23
ROC | December | KSSP- ZW3 R-Clean Insufficient Chemical Alarm, No R-Clean Sodium Hypo Valves Available, No M-Clean Sodium Hypo Valves Available. Notified Darren B. Can disregard. | All Wastewater System ROC General | 2025-12-23
ROC | December | KBSP- Theodore from AB onsite. | All Wastewater System ROC General | 2025-12-18
ROC | December | RHAMF- Chris R. going to site to meet with CPD to get site back in operation W11533238 CMU5 | All Wastewater System ROC General | 2025-12-22
ROC | December | SHSP, Power Outage/Generator Running Alarm, UVs are still running, Notified Lance J of the power outage, he will head to site. 19:54, December 30/2025, Lance J never received the original CMU5, made him a new CMU5 so there is record of this event. CMU5: W11536061 New CMU5: W11548776 | All Wastewater System ROC General | 2025-12-23
ROC | December | SHSP - UV system major fault. UV Bank 1 B still running, informed Gavin W, will take a look CMU = 11543191 11:34 - No UV system running, appears UV in local off, appears Gavin W onsite YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-26
ROC | December | RHAMF - Unit 2 pH sensor lo alarm. Disregard as per operator | All Wastewater System ROC General | 2025-12-26
ROC | December | Christian Van Beek signing in. Weather: -6C and clear. | All Wastewater System ROC General | 2025-12-26
ROC | December | QVSSSC - Inlet channel high switch, disregard as per shift report | All Wastewater System ROC General | 2025-12-29
ROC | December | KSSP - ZW2 TMP Control Delta High alarm. Disregard TMP alarms as per SCADA report. | All Wastewater System ROC General | 2025-12-29
ROC | December | NMSSHS - Basement flood, sump pumps not running. Chris R called, requested to call electrician on call. Satnam M will attend site. # CMU5 W11546987 | All Wastewater System ROC General | 2025-12-29
ROC | December | KSSP- ZW2 TMP Control Delta High Alarm. Disregard as per SCADA report. | All Wastewater System ROC General | 2025-12-30
ROC | December | MTSP - Aeriation tank 1 DO lo, man/start blower 1 17:10 - Place blower 1 back in auto | All Wastewater System ROC General | 2025-12-27
ROC | December | YDSS + YNSS Normal Connor Smith signing out | All Wastewater System ROC General | 2025-12-23
ROC | December | KSSSQW - Generator Fault, Low Battery and Channel Grinder 1 Overload alarms came in along with Site hydro power failure alarm. Checked site. Likely a power blip as the hydro power fail alarm cleared and KSSP is not affected. Generator Fault, Low Battery and Channel Grinder 1 Overload alarms are outstanding and will not clear. Called Chris C. who directed to leave alarms outstanding until the morning but would like a call back if the hydro failure alarm comes back in. #CONSULT | All Wastewater System ROC General | 2025-12-24
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-24
ROC | December | SHSP - Generator running, clarifier 2 rake drive cut. aeration blower overload. Power blip in area. Informed Gavin W, will head to site to reset clarifier. CMU = 11547046 SHSSDK - Generator running. Informed Gavin W, okay to leave but will watch if pumps fault | All Wastewater System ROC General | 2025-12-29
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-30
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-28
ROC | December | SUSSWB - pump failure on auto-dialer. Site appears okay, no pump issues and pump 1 running with duty cycle | All Wastewater System ROC General | 2025-12-28
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-29
ROC | December | SEOC - OCF Damper station CO2 Low alarm , disregard as per SCADA review. | All Wastewater System ROC General | 2025-12-17
ROC | December | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-12-18
ROC | December | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-12-18
ROC | December | SUSSWB -Dialer alarm, Pump failure. Duty not running, no pump active, no outstanding alarms or issue with pumps on trends. Acknowledge alarm | All Wastewater System ROC General | 2025-12-21
ROC | December | NMSSBP- P4 vibration hi alarm came in. Disregard on shift report | All Wastewater System ROC General | 2025-12-31
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-28
ROC | December | NBSP, Sludge Thickener Level hihi alarm, As per the shift report, directed to disregard | All Wastewater System ROC General | 2025-12-28
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-28
ROC | December | SUSP - EQ tank level hi, monitoring level as it just above the hi but seeing level slowly go down. | All Wastewater System ROC General | 2025-12-29
ROC | December | KSSP/KSSSQW, Power outage on site, UV Major fault//Clarifiers 3/4 not running, Generators running on site, notified Kevin K, he will look into the issue | All Wastewater System ROC General | 2025-12-29
ROC | December | KSSP- Memb Air Blower2 Speed Deviation Alarm, Blower 2 Air Flow Switch Low Alarm, No Membrane Blowers Available Alarm. Notified Neil O. He will look into it. | All Wastewater System ROC General | 2025-12-31
ROC | December | MTSS - Pump 1 running in hydrostatic mode alarm. Wet well 1 Hydrostatic level low/low. Notified Chris R, pump stopped when on the phone with Chris R. Cleared interlock from both pumps. will monitor. # Consult | All Wastewater System ROC General | 2025-12-26
ROC | December | Carter Dunn Signing Out | All Wastewater System ROC General | 2025-12-28
ROC | December | KBSP - Reject sump pump 1 E. stop, confirmed disregard as per Gavin W SHSP - Gavin W finished at site HMSS - Informed Gavin of pump3 speed indication trend spiking to near 100% every run before coming back down as seen on trends, will investigate further tomorrow | All Wastewater System ROC General | 2025-12-29
ROC | December | SECC- Talha H rebooting OIT. Disregard heartbeat alarm. | All Wastewater System ROC General | 2025-12-16
ROC | December | Angelica Chepiga signing in, weather -4C | All Wastewater System ROC General | 2025-12-16
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-30
ROC | December | RHAMF1- Station Power Failure Alarm, Odour Control System Offline, Makeup Air Unit Failed to Start. Alarms cleared | All Wastewater System ROC General | 2025-12-31
ROC | December | SECC- H2O2 pump 2 uncommanded stop alarm came in reset alarm. pump started up okay | All Wastewater System ROC General | 2025-12-31
ROC | December | KSSP - Parth P and Rick L finished on site. | All Wastewater System ROC General | 2025-12-19
ROC | December | KBSP- Eric onsite working on flow meter SECT_FIT1. | All Wastewater System ROC General | 2025-12-16
ROC | December | NMSSBP- Mech Screen 1 Overtorque Alarm. Notified Chris R, He will look into it. 15:14- Chris R requested to manually close inlet gate 1 valve and will leave outstanding for the night. | All Wastewater System ROC General | 2025-12-30
ROC | December | KBSP - Reject Sump Pump 1 E stop alarm came in. Directed to disregard as per shift report but will call if sump pump 2 also faults | All Wastewater System ROC General | 2025-12-31
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-19
ROC | December | SUSP - Neil O working on alum pumps. | All Wastewater System ROC General | 2025-12-23
ROC | December | NMSSBP - Mechanical Screen 1 Overtorque Alarm came in. Screen 2 is running and available. Will send an email to central east wastewater team | All Wastewater System ROC General | 2025-12-31
ROC | December | RHAMF1- Chris R attending site for security intrusion. Created CMU5 W11548604 #CMU5 | All Wastewater System ROC General | 2025-12-30
ROC | December | KCSSKR - pump 1 fault, informed Gavin W, is on route no pumps available. | All Wastewater System ROC General | 2025-12-28
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-25
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-25
ROC | December | KBSP - UV dosage lo, plant 2 influent hihi. Will check on site after King City, disregard plant flow hihi CMU = NBSP - Influent flow hihi, inlet channel high float, disregard for the night | All Wastewater System ROC General | 2025-12-28
ROC | December | SUSP - Diversion EQ tank level LOE, disregard as per shift report | All Wastewater System ROC General | 2025-12-29
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-30
ROC | December | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-12-26
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-26
ROC | December | SHSP - Screen room O2 concentration lolo alarm. Checked site, trending shows a dip of the O2 concentration which returned to normal range. Cleared alarm. | All Wastewater System ROC General | 2025-12-26
ROC | December | KBSP - Reject sump pump 1 Estop alarm. Confirmed Sump pump 2 un auto/running. Disregard as per SCADA review. | All Wastewater System ROC General | 2025-12-30
ROC | December | PVSS- H2S OOR alarm came in. Disregard on shift report | All Wastewater System ROC General | 2025-12-30
ROC | December | KSSP - Captor tank lolo level alarm and neutralization aborted alarm. Called Chris C who will check the system. | All Wastewater System ROC General | 2025-12-18
ROC | December | KSSP - TMP control delta high alarm. Disregard alarm as per shift report. | All Wastewater System ROC General | 2025-12-28
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-28
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-28
ROC | December | EGSSSC - Inlet channel level hihi, came back within normal range, able to clear | All Wastewater System ROC General | 2025-12-28
ROC | December | RHAMF1- Makeup Air Unit Failed to Start. Chris C will look into it. CONSULT | All Wastewater System ROC General | 2025-12-31
ROC | December | KSSSQW - Boiler 1 fault. Known issue from previous night. Operator Chris C directed to disregard if alarm came back during weekend. Email sent to on-call | All Wastewater System ROC General | 2025-12-21
ROC | December | Ethan U signing in Weather -6. | All Wastewater System ROC General | 2025-12-26
ROC | December | KSSP - Alum chem room MUA-11 diff press sw hi. Called Kevin K, disregard for the night. Man/close TK2_MV2 & Man/open TK1_MV2 as requested by Kevin K. Consult | All Wastewater System ROC General | 2025-12-26
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-29
ROC | December | SHSSDK- Marcus R onsite with maintenance working on Pump 1. | All Wastewater System ROC General | 2025-12-17
ROC | December | SUSP - Sludge tank level hihi alarm returned. Area ops should be going to site later today for scheduled overtime. Requested that Ethan U call OCO Kevin K later this morning. | All Wastewater System ROC General | 2025-12-27
ROC | December | KSSP - ZW1 transmembrane pressure hihi alarm and BP Pump 2 back pulse TMP HiHi alarm. Checked site, ZW! is going through an R clean process. The shit report directs to disregard membrane TMP alarms as the membranes work harder in cold weather months. Able to reset all alarms. | All Wastewater System ROC General | 2025-12-27
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-28
ROC | December | Gluzen Ramos Ong signing in | All Wastewater System ROC General | 2025-12-18
ROC | December | KBSP - Young J. working on alum pumps LSSS - applied duty rotation allowing P6 in D1 for EME student (Amelia) testing | All Wastewater System ROC General | 2025-12-18
ROC | December | Ethan U signing in | All Wastewater System ROC General | 2025-12-17
ROC | December | SUSP - Sludge tank hihi level alarm. Checked site, trending shows the sludge tank hit hihi level and then dipped slightly. Able to reset alarm. | All Wastewater System ROC General | 2025-12-27
ROC | December | YDSS + YNSS Normal Christian Van Beek signing out. | All Wastewater System ROC General | 2025-12-27
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-27
ROC | December | KBSP - Aer tank 2 suspended solids fault , alarm cleared. | All Wastewater System ROC General | 2025-12-18
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-21
ROC | December | KCSSKR, Generator Running Status Alarm, notified Gavin W, he will look into it | All Wastewater System ROC General | 2025-12-29
ROC | December | KSSP- Cam B onsite for workorders at headworks including gas detectors and sumps | All Wastewater System ROC General | 2025-12-16
ROC | December | NBSP - UV system minor fault. Disregard as per shift report. UV bank 1B running | All Wastewater System ROC General | 2025-12-20
ROC | December | Angelica Chepiga signing out | All Wastewater System ROC General | 2025-12-26
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-28
ROC | December | AUSS - Pump 5 discharge valve failed to open alarm. Checked site, duty rotated to a new pump which activated. No outstanding issues. Reset alarm. | All Wastewater System ROC General | 2025-12-28
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-28
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-30
ROC | December | Angelica Chepiga signing out | All Wastewater System ROC General | 2025-12-30
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-19
ROC | December | Christian Van Beek signing out. | All Wastewater System ROC General | 2025-12-19
ROC | December | SHSSDK - Power blip to site, causing generator to run SHSP - Diesel gen running, aeriation tank 1 mixer uncmd stop, clarifier 2 rake drive cut, effluent pump 1 & 2 general alarm, sludge blower fan overload. Informed Gavin W who will take a look on SCADA Consult | All Wastewater System ROC General | 2025-12-28
ROC | December | NMSSHS- Basement flood, sump pumps not working. Marcos T requested electrician and mechanical on-call to attend site. Satnam M and Chris I will attend. CMU 5 created yesterday. | All Wastewater System ROC General | 2025-12-30
ROC | December | KSSP - ZW2 TMP Control Delta High alarm came in. Disregarded as per shift report | All Wastewater System ROC General | 2025-12-31
ROC | December | KBSP- Drew from Ferguson requested to have Yash S On Call PCS give him a call regarding programming issues with Diesel Tank LITs, W11536327 CMU5 | All Wastewater System ROC General | 2025-12-23
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-27
ROC | December | RHAMF1- Make up air unit failed to start alarm came in. Notified Chris R who directed to contact NAC. Called Jimmy H to notify them of alarm. jimmy H will look into it | All Wastewater System ROC General | 2025-12-31
ROC | December | SHSSDK - Found generator shut off. Cleared alarm | All Wastewater System ROC General | 2025-12-17
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-21
ROC | December | AUSSSR - Line 3 over torque. Informed Chris R, okay to disregard for the night. Follow-up in case a second line goes down. | All Wastewater System ROC General | 2025-12-17
ROC | December | KSSSQW - Boiler 1 fault alarm. Called Cam B who stated he will check the system. | All Wastewater System ROC General | 2025-12-19
ROC | December | KCSSKR- Satnam M on site to work on pumps. Will be running each pump individually | All Wastewater System ROC General | 2025-12-22
ROC | December | Sutton WRRF Lagoon PS, Both pumps were interlocked, when checking wet well trends, the level was at its highest, no alarms were in to indicate an issue, contacted Chris C just as a precaution as pumps were running for some time, Directed to disregard. consult | All Wastewater System ROC General | 2025-12-23
ROC | December | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-12-18
ROC | December | Ethan Ullalkar signing out. | All Wastewater System ROC General | 2025-12-18
ROC | December | Connor Smith signing in -12C Windy | All Wastewater System ROC General | 2025-12-30
ROC | December | MTSP- Aeration tank 1 low Do alarm. Placed aeration blower 1 in man/on as per SCADA shift report. | All Wastewater System ROC General | 2025-12-25
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-26
ROC | December | JDSS - Satnam M finished at site | All Wastewater System ROC General | 2025-12-18
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-18
ROC | December | NBSSJA- Lance J onsite drawing down wet well. Disregard related alarms. | All Wastewater System ROC General | 2025-12-16
ROC | December | Gluzen Ramos Ong signing in | All Wastewater System ROC General | 2025-12-17
ROC | December | Carter Dunn Signing In, -11D/Clear | All Wastewater System ROC General | 2025-12-30
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-31
ROC | December | Angelica Chepiga signing out | All Wastewater System ROC General | 2025-12-29
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-31
WEST | December | On site for station check Residuals Treated Free Grab: 1.77mg/L, Analyzer 1.74mg/L Post Reservoir Free grab 1.78mg/L, Analyzer 1.77mg/L Pre Reservoir Free grab 2.98mg/L, Analyzer 3.08mg/L No other issues on site | Ansnorveldt Wells 2, 3 & Reservoir | 2025-12-15
ROC | December | MAPS7- Total Wire-to-Water Low Low Alarm. Resulted in pump 4 failing. Placed Pump 2 in auto as second duty 1 pump. | All Water System ROC General | 2025-12-23
ROC | December | JDSS - Satnam M. doing generator maintenance | All Wastewater System ROC General | 2025-12-18
ROC | December | NMW15 - Combine chlorine low alarm, quick dip. Alarm cleared. | All Water System ROC General | 2025-12-24
ROC | December | MKRSEM - Reservoir Lo alarm came in. Called Toronto Water (Zoran) and requested 2 pumps on to fill reservoir 04:04 - Called Toronto Water ( Mehdi) and requested pumps off due to higher levels | All Water System ROC General | 2025-12-24
ROC | December | YWS + NYWS normal | All Water System ROC General | 2025-12-25
ROC | December | AUSS - Noted that the duty 1 rotated to pump 1 which is manual/off and listed as OOS on the shift report. Placed pump 1 in duty 7 and rotated duty 1 to pump 2. Emailed OCO detailing the changes made. | All Wastewater System ROC General | 2025-12-25
ROC | December | HLW1 - Tim H placed Well 1 pump man/off and increased VCFCV2 flow to 60l/s. Area Ops will attend Well 1 site today. | All Water System ROC General | 2025-12-24
ROC | December | Christian Van Beek signing in. Weather: 1 C and clear. | All Water System ROC General | 2025-12-18
ROC | December | STW3- Parth P finished onsite. Chlorinator 2 OOS. Dan Z onsite running well for sampling. | All Water System ROC General | 2025-12-22
ROC | December | AUW14 - Place wells man/off AURSOH - Activate duty 1 to draw down from AURSBS to later help drawdown MARS due to high levels during night | All Water System ROC General | 2025-12-20
ROC | December | RHMCMD, Placed valve man/closed | All Water System ROC General | 2025-12-20
ROC | December | AURSBS - Activated D1 @47%. | All Water System ROC General | 2025-12-25
ROC | December | NRETCR - Lee F working on altitude valve, isolating tower for the duration of the work. William M on site with Lee F. | All Water System ROC General | 2025-12-23
ROC | December | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-12-25
ROC | December | HLW1 - Placed well 1 back to auto, as per Tim H. | All Water System ROC General | 2025-12-24
ROC | December | MARS- Called Toronto (Zoran) and requested increased flow to Maple. | All Water System ROC General | 2025-12-23
ROC | December | KCSSKR - Screen failed to stop, able to clear. Screen is off | All Wastewater System ROC General | 2025-12-28
ROC | December | KSSSQW - Odour exhaust fan emergency stop alarm came in. Checked site. Tyson C. called to inform that all the exhaust fan alarms were triggered by him and Michael B. Tyson directed to disregard alarms for the time being | All Wastewater System ROC General | 2025-12-11
ROC | December | Adeela Khan signing in. Weather: -12 and snowing | All Wastewater System ROC General | 2025-12-11
ROC | December | City of Vaughan - Received call from City of Vaughan (Elizabeth 905-832-2281) afterhours. Call regarding exposed manhole cover. South of Rutherford & Jane street. Checked site on Allpipes. Going South of Rutherford, make a right onto Jane Street. Informed Dan H, will head to site with Young J. CMU = W11511243 | All Wastewater System ROC General | 2025-12-12
ROC | December | YDSS+YNSS normal | All Wastewater System ROC General | 2025-12-13
ROC | December | YDSS+YNSS normal | All Wastewater System ROC General | 2025-12-13
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-10
ROC | December | KSSP- Aeration Tank 1 Inlet Do Fault. Alarm cleared. 02:44- Aeration Tank 1 Inlet DO Fault. Alarm cleared. | All Wastewater System ROC General | 2025-12-10
ROC | December | SUSSHS- Chris C noticed issue with pump 1. Placed in manual off. Pump 2 available in duty 1. | All Wastewater System ROC General | 2025-12-02
ROC | December | LSSS, Rotated duty so pump 6 is in D1, EME student on site taking samples | All Wastewater System ROC General | 2025-12-01
ROC | December | KBSP- Aaron C rebooting APN on site. Notified Lauren of comm disruption | All Wastewater System ROC General | 2025-12-01
ROC | December | MTSP, Aeration Tank 1 DO lo alarm, as per shift report, rotated DO selection from Tank 2 to Tank 1. 17:32, Rotated it back to Tank 1 as tank 2 was about to hit the hi alarm 17:55, Placed Blower 1 man/on to help with the DO at Tank 1 as it is dropping again to the lo level | All Wastewater System ROC General | 2025-12-07
ROC | December | Christian Van Beek signing in. Weather: -12C and clear. | All Wastewater System ROC General | 2025-12-08
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-08
ROC | December | Christian Van Beek signing out. | All Wastewater System ROC General | 2025-12-08
ROC | December | AUSS, Marcos T requests PCS to reset OIT at B1, Notified Artour L, he will look into it | All Wastewater System ROC General | 2025-12-04
ROC | December | Christian Van Beek signing in. Weather: -9 and clear. | All Wastewater System ROC General | 2025-12-09
ROC | December | SHSP, Marcus R on site working on the clarifiers | All Wastewater System ROC General | 2025-12-02
ROC | December | RHAMF1 - Unit 2 recirculation pump 2 E-stop & communication loss. Followed up with Phil R. Disregard for the day. Marcus T will head to site later as well | All Wastewater System ROC General | 2025-12-08
ROC | December | SHSP- Marcus R on site to run generator and test eyewashes on site NMSSHS- Terry R done on site | All Wastewater System ROC General | 2025-12-01
ROC | December | Adeela Khan signing out | All Wastewater System ROC General | 2025-12-01
ROC | December | KBSP, Young J on site, running the generator/testing blowers and eye wash alarms | All Wastewater System ROC General | 2025-12-01
ROC | December | QVSSSC - Cam B on site to complete a generator run test. | All Wastewater System ROC General | 2025-12-04
ROC | December | MTSP - Redempto B and Parth P on site to work on the raw sewage flow meter | All Wastewater System ROC General | 2025-12-02
ROC | December | SHSP - Marcus R on site to complete oil changes for the grit and sludge blowers. | All Wastewater System ROC General | 2025-12-04
ROC | December | SUSP - Chase J & Neil O onsite working on UV. Disregard UV related alarms. KSSP - UV system major fault, common major alarm. Confirmed with Chase J Trojan onsite working on UV and operators are onsite as well SEOC - General HVAC alarm, disregard as per shift report | All Wastewater System ROC General | 2025-12-09
ROC | December | Ethan Ullalkar signing out. | All Wastewater System ROC General | 2025-12-08
ROC | December | SHSSDK- Bill V on site to pull P1 KSSP- Darren B on site to test chemical containment alarms | All Wastewater System ROC General | 2025-12-03
ROC | December | SHSP - Marcus R onsite working on vortex & bar screen | All Wastewater System ROC General | 2025-12-08
ROC | December | RHAMF1, Unit 1 Diff. Pressure 2 hihi alarm, Both fans are still running, will continue to disregard as per Chris R | All Wastewater System ROC General | 2025-12-22
ROC | December | NBSP - UV System Minor fault alarm, disregard alarm as per SCADA report, UV bank 1 B in running. | All Wastewater System ROC General | 2025-12-24
ROC | December | SHSP- Marcus R on site to work on Alum pumps | All Wastewater System ROC General | 2025-12-22
ROC | December | NBSP- Lance J on site working on alum pumps KBSP- Young J on site to work on wash pumps | All Wastewater System ROC General | 2025-12-22
ROC | December | KBSP- Reject sump pmp 1 e stop alarm came in. Disregard on shift report | All Wastewater System ROC General | 2025-12-22
ROC | December | YDSS + YNSS normal | All Wastewater System ROC General | 2025-12-18
ROC | December | Adeela Khan signing in. Weather: 6C and windy | All Wastewater System ROC General | 2025-12-18
ROC | December | KSSSQW - Generator running status, ATS failed to transfer, Odour control system communication loss/e-stop, informed Kevin K 9:04 - Power restored to site, channel grinder back running, odour control system comm loss is a disregard as per shift report. Informed Kevin K of updated status. will not head to site | All Wastewater System ROC General | 2025-12-27
ROC | December | HMSS- Bar Screen 2 Not in Auto Alarm. Notified Gavin W. He will go to site to place back in auto. | All Wastewater System ROC General | 2025-12-30
ROC | December | QVSSSC- Ric L and Parth P onsite working on overflow meter. | All Wastewater System ROC General | 2025-12-17
ROC | December | SUSP - Neil O. doing blower maintenance | All Wastewater System ROC General | 2025-12-18
ROC | December | MTSP- Placed Aeration blower 1 back in auto as per SCADA review. | All Wastewater System ROC General | 2025-12-25
ROC | December | NBSSJA- Gas Detector Panel Fault Alarm. Disregard as per SCADA Report. | All Wastewater System ROC General | 2025-12-16
ROC | December | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-12-29
ROC | December | SHSP - UV system major fault. Bank 1B running, called Gavin W. No response 1:50 - Called back and left voicemail. 2:01 - Called back and no answer. 2:08 - Called Lauren S, she will attend to site CMU = 11547278 | All Wastewater System ROC General | 2025-12-30
ROC | December | YDSS + YNSS Normal | All Wastewater System ROC General | 2025-12-19
ROC | December | SEOC4 - Shaft 4 fan duty rotation imminent, disregard as per shift report | All Wastewater System ROC General | 2025-12-21
ROC | December | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2025-12-16
ROC | December | Carter D Signing Out | All Wastewater System ROC General | 2025-12-29
ROC | December | RHAMF1- Unit 1 Diff. Pressure 2 Hi Alarm. Will email Central East Ops | All Wastewater System ROC General | 2025-12-11
ROC | December | SEOC6 - Shaft 6/7 Fan Duty Rotation Imminent alarm came in. Disregarded as per shift report | All Wastewater System ROC General | 2025-12-08
ROC | December | SUSP - Sludge Tank Level HiHi alarm came in. Checked site. Sent an email to Chase J. | All Wastewater System ROC General | 2025-12-08
WEST | December | THIS IS A MAXIMO SYSTEM TEST, PLEASE IGNORE!!! | Ansnorveldt Wells 2, 3 & Reservoir | 2025-12-13
WEST | December | On site for station check Check Trends: All okay Well off Verified Analyzers 08:40-Post Reservoir Free Grab: 1.66 mg/L, Analyzer 1.60 mg/L 08:45-Post Reservoir (treated) Free- grab 1.60mg/L, Analyzer 1.57mg/L 08:45-Post Reservoir (treated) Free- grab 1.75mg/L Entered Values in PWQ sheet. Equipment okay. | Ansnorveldt Wells 2, 3 & Reservoir | 2025-12-12
WEST | December | on site to Complete Station Check and to collect bacti sample W11438519 Check Trends: All okay. Well running Verified Analyzers 08:55-Pre Reservoir Free Grab: 3.70mg/L, Analyzer 3.63mg/L 09:00-Post Reservoir Free Grab: 1.46mg/L, Analyzer 1.38mg/L 09:05-Post Reservoir (treated) Free- grab 1.44mg/L, Analyzer 1.38mg/L Total grab- 1.54 mg/L. Samples Collected Entered Values in PWQ sheet. Equipment okay | Ansnorveldt Wells 2, 3 & Reservoir | 2025-12-10
WEST | December | -on site to top up and drop off hypo - 28/29 - 50/50 -left to full jugs | Ansnorveldt Wells 2, 3 & Reservoir | 2025-12-09
WEST | December | On site for station check Check Trends: All okay Well off Verified Analyzers 10:00-Post Reservoir Free Grab: 1.52 mg/L, Analyzer 1.48 mg/L 10:05-Post Reservoir (treated) Free- grab 1.52mg/L, Analyzer 1.53mg/L Entered Values in PWQ sheet. Equipment okay. | Ansnorveldt Wells 2, 3 & Reservoir | 2025-12-01
WEST | December | On site for scheduled PM work orders. informed ROC about the works being done. Topped up hypo tanks- 29L,30L/40L,40L Completed the following work orders W11413521 JHSC Health and Safety Inspection W11412970 ANW23, Ansnorveldt Wells 2/3, Generator Test Run Pre check Battery okay- 13.4 V Coolant- Okay Oil - Okay Before Start Start time- 09:59 Run time- 299:48 hr After Stop Stop time-11:04 Run time- 300:57 hr W11414067 ANW23, Ansnorveldt Wells 2/3, Pressure Regulating Valve Maintenance W11414092 ANW23, Ansnorveldt Wells 2/3, Turbidity Analyzer TU5300 Maintenance and Calibration pump 1 max flow- 12.5 ml/Min @ 50% ; Pump 2 max flow- 12.5 ml/Min @ 50% W11414110 ANW23, Sodium Hypochlorite System Maintenance W11414162 ANW23, Ansnorveldt Wells 2/3, Pumps 2 and 3 Strainer Inspection W11414222 ANW23, Ansnorveldt Wells 2/3 , Siemens Depolox 5/Micro 2000 Chlorine Analyzer | Ansnorveldt Wells 2, 3 & Reservoir | 2025-12-02
WEST | December | on site to Complete Station Check and to collect bacti sample W11419151 Check Trends: All okay. Well running Verified Analyzers 13:50-Pre Reservoir Free Grab: 3.40mg/L, Analyzer 3.41mg/L 13:45-Post Reservoir Free Grab: 1.56mg/L, Analyzer 1.56mg/L 13:40-Post Reservoir (treated) Free- grab 1.52mg/L, Analyzer 1.58mg/L Total grab- 1.68 mg/L. Samples Collected Entered Values in PWQ sheet. Equipment okay. | Ansnorveldt Wells 2, 3 & Reservoir | 2025-12-03
WEST | December | On site for station check Check Trends: All okay 09:00-Deactivated Duty and Put both wells manual off for Network Upgrades. monitoring the system. Verified Analyzers 08:56-Post Reservoir Free Grab: 1.46 mg/L, Analyzer 1.38 mg/L 09:02-Post Reservoir (treated) Free- grab 1.44mg/L, Analyzer 1.42mg/L Entered Values in PWQ sheet. 09:50- Put wells back to Auto after network upgrades are done. Equipment okay | Ansnorveldt Wells 2, 3 & Reservoir | 2025-12-09
WEST | December | -on site to complete station check -well duty not active, reservoir = 78% -verified analyzers: 14:18 - treated water FCL analyzer = 1.45 mg/L 14:18 - treated water grabs: Free chlorine = 1.41 mg/L Total chlorine = 1.57 mg/L 14:30 - post reservoir FCL analyzer = 1.46 mg/L Grab = 1.41 mg/L -checked equipment -reviewed trends -recorded readings in PWQ sheet -no issues found | Ansnorveldt Wells 2, 3 & Reservoir | 2025-12-05
WEST | December | on site to Complete Station Check and to collect bacti sample W11454745 Check Trends: All okay. Activated duty, Wells running Verified Analyzers 09:00-Pre Reservoir Free Grab: 3.80mg/L, Analyzer 3.78mg/L 09:10-Post Reservoir Free Grab: 1.69mg/L, Analyzer 1.69mg/L 09:20-Post Reservoir (treated) Free- grab 1.72mg/L, Analyzer 1.67mg/L Total grab- 1.85 mg/L. Samples Collected Entered Values in PWQ sheet. Equipment okay | Ansnorveldt Wells 2, 3 & Reservoir | 2025-12-16
WEST | December | On site for station check Check Trends: All okay Well off Verified Analyzers 12:25-Post Reservoir Free Grab: 1.60 mg/L, Analyzer 1.55 mg/L 12:30-Post Reservoir (treated) Free- grab 1.62mg/L, Analyzer 1.62mg/L 12:30-Post Reservoir (treated) Free- grab 1.82mg/L Entered Values in PWQ sheet. Equipment okay | Ansnorveldt Wells 2, 3 & Reservoir | 2025-12-19
WEST | December | on site to Complete Station Check and to collect bacti sample W11469918 Check Trends: All okay. Activated duty, Wells running Verified Analyzers 14:30-Pre Reservoir Free Grab: 3.76mg/L, Analyzer 3.70mg/L 14:35-Post Reservoir Free Grab: 1.60mg/L, Analyzer 1.55mg/L 14:40-Post Reservoir (treated) Free- grab 1.63mg/L, Analyzer 1.61mg/L 14:40-Total grab- 1.84 mg/L. Samples Collected Entered Values in PWQ sheet. Duty deactivated Equipment okay | Ansnorveldt Wells 2, 3 & Reservoir | 2025-12-22
WEST | December | On site for station check Check Trends: All okay Well off Verified Analyzers 08:12-Post Reservoir Free Grab: 1.48 mg/L, Analyzer 1.50 mg/L 08:15-Post Reservoir (treated) Free- grab 1.51mg/L, Analyzer 1.52mg/L Entered Values in PWQ sheet. Cleaned Turbidity Analyzer vial. Equipment okay | Ansnorveldt Wells 2, 3 & Reservoir | 2025-12-24
WEST | December | W11526315- Year end chemical inventory count. entered values in teams folder. | Ansnorveldt Wells 2, 3 & Reservoir | 2025-12-23
WEST | December | On site for station check Check Trends: All okay Well RUNNING Verified Analyzers 12:10-Post Reservoir Free Grab: 1.42 mg/L, Analyzer 1.43 mg/L 12:12: Pre Reservoir Free Grab: 3.56 mg/L, Analyzer 3.55 mg/L 12:15-Post Reservoir (treated) Free- grab 1.40mg/L, Analyzer 1.45mg/L Entered Values in PWQ sheet. Equipment okay | Ansnorveldt Wells 2, 3 & Reservoir | 2025-12-31
WEST | December | W11526315- Year end chemical inventory count. entered values in teams folder. | Ansnorveldt Wells 2, 3 & Reservoir | 2025-12-23
WEST | December | on site to Complete Station Check and to collect bacti sample W11483468 Check Trends: All okay. Activated duty, Wells running Verified Analyzers 09:05-Pre Reservoir Free Grab: 3.72mg/L, Analyzer 3.80mg/L 09:10-Post Reservoir Free Grab: 1.62mg/L, Analyzer 1.58mg/L 09:15-Post Reservoir (treated) Free- grab 1.63mg/L, Analyzer 1.56mg/L 09:15-Total grab- 1.80 mg/L. Samples Collected Entered Values in PWQ sheet. Duty deactivated Equipment okay | Ansnorveldt Wells 2, 3 & Reservoir | 2025-12-29
CENTRAL | December | -Performed station check - logged station readings into PWQ sheet Grab: free=0.08mg/L total=2.64mg/L@15:35 Analyzer: free=0.07mg/L total=2.55mg/L -Checked Depolox reagents - OK -Collected weekly BacT sample YD# W11439251 & in-house water quality samples | Aurora (East) First Commerce Elevated Tank | 2025-12-10
WEST | December | Restarted the Operator Interface Terminal due to video driver updates. Notified the Remote Operations Center and the OIC. Wells were off during the restart. | Ansnorveldt Wells 2, 3 & Reservoir | 2025-12-18
CENTRAL | December | On-site to investigate Outlet Line Standby Heat Trace Alarm. Upon arrival, unit was showing ?low current alarm? but was maintaining proper temperature. I acknowledged and reset unit, cleared the alarm and seems to be functioning properly. Will monitor remotely | Aurora (East) First Commerce Elevated Tank | 2025-12-09
CENTRAL | December | -Performed station check - logged station readings into PWQ sheet Grab: treated total=2.60mg/L free=0.08mg/L@8:45 Analyzer: treated total=2.61mg/L free=0.07mg/L -Checked Depolox reagents - OK -Collected weekly BacT sample YD #W11420059 & monthly sample YD #11420025 -Reset Outlet line standby heat trace alarm - low current | Aurora (East) First Commerce Elevated Tank | 2025-12-03
CENTRAL | December | Informed ROC. Onsite to perform annual calibration. Used the calibration mode. Performed calibration for Inlet and outlet FITs. Put everything back to service. All the related alarms were cleared. No issues. Informed ROC, armed the building and left the site. | Aurora (East) First Commerce Elevated Tank | 2025-12-08
CENTRAL | December | -Responded sporadic treated total analyzer reading - zeroed and calibrated analyzer | Aurora (East) First Commerce Elevated Tank | 2025-12-02
CENTRAL | December | On-site for a station and equipment check No issues found. Took weekly bacti sample while draining Verified analyzer and entered all readings and grabs into PWQ sheet Free@1403 G:0.11 A:0.12mg/L Total @1406 G:2.60 A:2.59mg/L | Aurora (East) First Commerce Elevated Tank | 2025-12-29
CENTRAL | December | -Finished the following work orders *Dehumidifier inspection *Ventilation inspection *Heat trace inspection *H&S inspection *Depolox analyzer maintenance *Portable generator test run | Aurora (East) First Commerce Elevated Tank | 2025-12-18
CENTRAL | December | Reset and tested outlet standby heat trace system. | Aurora (East) First Commerce Elevated Tank | 2025-12-18
CENTRAL | December | Station Check (no issues found) Input data to PWQ 14:15 Verified Depolox (mg/L) Free: Grab 0.06, A 0.10 Total: Grab 2.60, A 2.58 topped up acetate Heat trace alarm, generated w/o #11533170 14:15 #11470534 sample | Aurora (East) First Commerce Elevated Tank | 2025-12-22
CENTRAL | December | -Performed station check - logged station readings into PWQ sheet Grab: treated free=0.08mg/L total=2.72mg/L@15:45 Analyzer: treated free=0.08mg/L total=2.70mg/L -Checked Depolox reagents - OK -Collected weekly BacT sample YD #W11455350 | Aurora (East) First Commerce Elevated Tank | 2025-12-16
CENTRAL | December | On-site for a station and equipment check, no issues found All readings entered in PWQ sheet | Aurora (East) Wellington Pumping Station | 2025-12-12
CENTRAL | December | Station and equipment check, no issues found. Site running All readings and measurements entered into PWQ sheet | Aurora (East) Wellington Pumping Station | 2025-12-15
CENTRAL | December | On site for station check. 07:56. Pump 4 running in duty at 165 l/s. No issues found. | Aurora (East) Wellington Pumping Station | 2025-12-01
CENTRAL | December | On-site for a station and equipment check, no issues found All readings and measurements entered into PWQ sheet | Aurora (East) Wellington Pumping Station | 2025-12-05
CENTRAL | December | On-site for various WO's -Total Power on-site for semi annual generator testing, inspection and maintenance -Building flood alarm and sump pit inspection completed -Pump and motor visual inspection completed -Station and equipment checked, no issues found. All readings entered into PWQ sheet -Ventilation system visually inspected -JHSC inspection -General housekeeping | Aurora (East) Wellington Pumping Station | 2025-12-09
CENTRAL | December | Grease pumps and motors Vibration readings | Aurora (East) Wellington Pumping Station | 2025-12-02
CENTRAL | December | On site for station check. 07:46. Pump 4 running in duty at 165 l/s. No issues found. | Aurora (East) Wellington Pumping Station | 2025-12-19
CENTRAL | December | On-site for a station and equipment check No issues found All readings entered into PWQ sheet Year end chemical levels inventory completed | Aurora (East) Wellington Pumping Station | 2025-12-23
CENTRAL | December | On-site for a station and equipment check No issues found All readings entered into PWQ sheet | Aurora (East) Wellington Pumping Station | 2025-12-24
CENTRAL | December | -Performed station check - logged station readings into PWQ sheet Grab: free=0.06mg/L total=2.88mg/L@10:25 Analyzer: free=0.06mg/L total=2.88mg/L -Topped up Depolox KI solution -Collected weekly BacT sample YD# W11439251 & in-house water quality samples | Aurora (North) Orchard Heights Elevated Tank | 2025-12-10
CENTRAL | December | Grease bottom motor bearings Motor 3 and 4 | Aurora (North) Orchard Heights Elevated Tank | 2025-12-02
CENTRAL | December | -Performed station check - logged station readings into PWQ sheet Grab: treated total=2.80mg/L free=0.06mg/L@10:35 Analyzer: treated total=2.88mg/L free=0.04mg/L -Checked Depolox reagents - OK -Collected weekly BacT sample YD #W11420059 & monthly sample YD #11420025 -Finished the following work orders *Depolox analyzer maintenance *H&S inspection | Aurora (North) Orchard Heights Elevated Tank | 2025-12-03
CENTRAL | December | -Performed station check - logged station readings into PWQ sheet Grab: treated total=2.80mg/L free=0.02mg/L@11:20 Analyzer: treated total=2.87mg/L free=0.05mg/L -Checked Depolox reagents - OK -Collected weekly BacT sample YD #W11484058 | Aurora (North) Orchard Heights Elevated Tank | 2025-12-29
CENTRAL | December | -Performed station check - logged station readings into PWQ sheet Grab: treated free=0.05mg/L total=2.92mg/L@12:50 Analyzer: treated free=0.05mg/L total=3.00mg/L -Checked Depolox reagents - OK -Collected weekly BacT sample YD #W11455350 | Aurora (North) Orchard Heights Elevated Tank | 2025-12-16
CENTRAL | December | Station Check (no issues found) Input data to PWQ 11:10 Verified Depolox (mg/L): Free: Grab 0.04, A 0.06 Total: Grab 3.10, A 3.04 11:15 #11470534 Sample Topped up Acetate | Aurora (North) Orchard Heights Elevated Tank | 2025-12-22
CENTRAL | December | On-site for a station and equipment check, no issues found. Chemical levels and systems ok Topped up ammonia day tank 1 Verified analyzers and entered grabs and readings into PWQ sheet Pre-injection Free@1047 g:0.06 a:0.06mg/L Pre-injection Total@1055 g:1.89 a:1.80mg/L Post-injection Free@1106 g:0.08 a:0.06mg/L Post-injection Total@1107 g:3.08 a:3.09mg/L | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-12-15
CENTRAL | December | On-site after receiving a call from ROC about post-total analyzer approaching hi alarm. I zeroed free and total then calibrated to 3.04 based on grab. Will continue to monitor remotely | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-12-10
CENTRAL | December | On-site to receive 24 cylinders and return the same amount | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-12-11
CENTRAL | December | On-site for a station and equipment check, no issues found Topped up ammonia day tank 2 Topped up ?green? reagent on Chemscan Chemical levels and systems ok Verified analyzers and entered all measurements and grabs into PWQ sheet Pre-injection Free CL2@1312 g:0.07 a:0.06mg/L Pre-injection Total CL2 @1312 g:1.89 a:1.86mg/L Post-injection Free@1326 g:0.08 a:0.05mg/L Post-injection Total@1326 g:2.90 a:2.94mg/L | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-12-12
CENTRAL | December | *****continued from previous entry***** Pre-injection Free@1308 g:0.08 a:0.06mg/L Pre-injection Total@1312 g:1.75 a:1.68mg/L Post-injection Free@1318 g:0.09 a:0.17 Post-injection Total@1319 g:3.02 a:2.41 adjusted to 3.02mg/L | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-12-10
CENTRAL | December | On-site for a station and equipment check, no issues found Weekly bacti and biweekly operational samples taken Verified analyzers, and entered all readings and grabs into PWQ sheet Adjusted Post Total analyzer based on the average of three grabs. 3.04, 3.00, 3.02mg/L to 3.02 from 2.41mg/L | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-12-10
CENTRAL | December | Roc notified me of treated hihi total alarm triggered. Roc deactivated chemical dosing system. Combined did not exceed 4.0 mg/l and no adverse water directed to users. Lowered dosage set point from 3.1 to 2.9. Placed chemical system back in service. Notified roc of change. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-12-07
CENTRAL | December | On-site for a station and equipment check, no issues found Chemical levels and systems ok Verified analyzers, entered all readings and grabs entered into PWQ sheet Pre-injection: Free CL2 @0859 G: 0.05 A: 0.05mg/L Total CL2 @ 0900 G: 1.97 A: 1.96mg/L Post-injection: Free CL2 @0903 G: 0.04. A: 0.02mg/L Total CL2 @0910 G: 3.36 A: 3.36mg/L | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-12-05
CENTRAL | December | Onsite to investigate post injection hi total chlorine analyzer alarm. 09:18 grab 3.10/3.00/2.90 mg/l. micro2000 :3.65 adjusted to match grab. Replaced analyzer KI reagent. 09:41 grab 3.18. Micro 2000 3.10 mg/l. Chemscan: 3.15 on next reading. No issues remain. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-12-05
CENTRAL | December | Onsite for station check: Verified analyzers Calculated dosages Chemical levels- Ok Depolox reagents- Ok Chemscan reagents- Ok Station/equipment- Ok | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-12-08
CENTRAL | December | 16:40 Roc called about a hi treated total post injection chlorine of 3.64 mg/l. Analyzer tends is somewhat erratic. Chemscan total reading 3.08 mg/l. Adjusted dosage setting from 3.30 to 3.20 mg/l. Analyzer dropped to 3.45 mg/l. Notified roc. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-12-02
CENTRAL | December | Attending site to check Pre and Post Total analyzers (W11488779). Found Pre and Post Free analyzers had no flow. Adjusted flow and performed zero and span calibration on both. Notified Ben Hess. ROC was notified before and after work was performed. Associated alarms were cleared on SCADA. Will return next week to address the Total analyzers. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-12-05
CENTRAL | December | Informed ROC. Performed annual calibration and put instruments in Cal mode while doing the tasks. Devices done were FIT and post-injection analyzers. All alarms were cleared after the job. No other issues encountered. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-12-02
CENTRAL | December | Onsite to investigate post injection chlorine free analyzer reading erratic and jumping from 0.01 to 0.59 mg/l. 16:27 grab 0.06. A 0.03. Analyzer now stable but dosing system has been interlocked. Acknowledged and cleared interlock alarm. 16:38 chlorine system active. Post injection free climbed to 0.28. Grabs remain 0.06 mg/l. Performed a zero point calibration. 16:54 placed dosing system back online. Grab 0.06 mg/l. Jumped to 0.27. Adjusted to match grab. 17:00 grab 0.08. Analyzer 0.07. Adjusted target post injection from 3.2 to 3.3 mg/l. 17:03 grab 0.10. Analyzer 0.09. Placed chlorine train 1 back in auto. No issues remain. Analyzer matches grab. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-12-03
CENTRAL | December | Adjusted post injection combined setpoint from 2.90 to 3.20 mg/L | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-12-08
CENTRAL | December | On-site to investigate high pre-total at 2.48mg¦L on analyzer. Average of 3 grabs, 1.88 1.94 and 2.00 mg/L Adjusted to 1.94mg/L | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-12-04
CENTRAL | December | On-site for a station and equipment check, no issues found. Chemical levels and systems ok, topped up ammonia day tank 2 Took weekly bacti sample while draining Took blended system sample as well Verified analyzers, adjusted free cl2 post injection on analyzer, based on an average of 3 grabs to 0.04 from 0.00mg/L | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-12-03
CENTRAL | December | On-site to test PSV1 with Ryan B, Justin Q, and Matt S. Opened the solenoid valving to put the valve into auto Closed the bypass around PSV1 for the test activated AURSBS and JFRS duty to start pump at maple Able to get flow into both reservoirs concurrently. Needs more programming changes and to refresh the solenoids on PSV1 All changes reversed. PSV1 locally opened, bypass open and all other pumps and valves in auto | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-12-02
CENTRAL | December | On site for station check. 11:44. Outlet flow at o l/s and chloramine boosting is inactive. Reservoir level at 65% and draining. Verified residuals (mg/l): 11:49 Pre-injection chlorine grabs. Free grab: 0.04 Depolox 5: 0.08 Total grab: 2.00 Micro2000: 1.90 Chemscan: 1.97. Monochloramine grab: 1.83. Chemscan: 1.70. Adjusted offsetto match grab. Free ammonia grab: 0.10. Chemscan: 0.09. Total ammonia grab: 0.46. Chemscan: 0.32. Adjusted to match grab. Replaced chlorine chlinder bank A with Redempto H. 12:42 Post-injection chlorine grabs. Instrumentation working on deplox/micro analyzer. Used last readings. Free grab: 0.06 Depolox 5: 0.01. Total grab: 1.88 Micro2000: 1.88 Chemscan: 1.96. Monochloramine grab: 1.79. Chemscan: 1.83 Free ammonia grab: 0.11 Chemscan: 0.07. Total ammonia grab: 0.46. Chemscan: 0.39. No new issues found. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-12-01
CENTRAL | December | Informed ROC. Onsite to perform annual calibrations. Asked Ben Hess to turn off the duty. Used the calibration mode during the work. Devices were done as below: CELL 1&2 LIT, Chlorine room devices, pre injection free and total AIT. Took a multiple grab samples and adjusted analyzer accordingly. Grab Free - 0.03 mg/l, AL pre free AIT - 0.02 mg/l Grab Total - 2.01 mg/l, AL pre Total - 2.01 mg/l. Put everything back in service. All the related alarms were cleared. No issues. ROC turned on the duty. Monitored for a while. No issues. Informed ROC, armed the building and left the site | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-12-01
CENTRAL | December | -Changed chorine cylinders | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-12-09
CENTRAL | December | On-site for various WO's -Ammonia pump and system inspection completed, ensure both PRV's on chemical boards are opening -Draw down completed on both ammonia pumps, both run at 50% for 2 mins. Pump 1=1503mL/min Pump 2= 1594mL/min -Sump pump inspected and tested -JHSC inspection completed -WO W11488642 created to address very difficult to open and close CL2 outside entrance door -CL2 system inspected and CL2 cylinders ordered -Dehumidifier and filters inspected, no issues found | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-12-04
CENTRAL | December | Aur central reservoir level reached 39%. Roc notified of low level alarm. Placed south res chlorine dosing in manual off as instrumentation working on analyzers. 12:35 activated auvcbs at flow mode 200 L/s. Placed metro valve from 70 L/s to 90 L/s. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-12-08
CENTRAL | December | -Responded hihi post-free - Performed grab test post-free=0.24mg/L analyzer reading=0.30mg/L - Call in on-call operator | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-12-03
CENTRAL | December | Notified of hi post inj total by ROC. Analyzer reached 3.66 mg/l. Lowered total hihi alarm from 3.75 to 3.70 and directed roc to shut down dosing if reached. Analyzer continues to drift since calibrations last week. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-12-06
CENTRAL | December | Attending site to check Pre & Post Total chlorine analyzers (W11491833). Operations (Ben) shut off the chemical system so that the analyzers could be worked on. Rebuilt both Total probes with new electrolyte and membranes. Calibrated using dpd colorimeter. Operations (Ben) resumed chemical addition once work was completed. Will monitor SCADA to determine if further action will be required. ROC was notified before and after maintenance work was performed. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-12-08
CENTRAL | December | On site for station check. 12:32. Outlet flow at 492 l/s and chloramine boosting is active. Reservoir level at 72% and draining. Topped up ammonia tank 2. Topped up chemscan KI reagent. Verified residuals (mg/l): 13:16 Pre-injection chlorine grabs. Free grab: 0.03 Depolox 5: 0.06. Total grab: 1.71/1.74/1.70 Micro2000: 1.57 Chemscan: 1.83. Adjusted both analyzers to match grabs. Monochloramine grab: 1.69. Chemscan: 1.66. Free ammonia grab: 0.04. Chemscan: 0.06 Total ammonia grab: 0.37. Chemscan: 0.34. 13:28 Post-injection chlorine grabs: Free grab: 0.06 Depolox 5: 0.05. Total grab: 3.12/3.12/3.12 Micro2000: 2.95 Chemscan: 3.33. Adjusted both analyzer to match grabs. Monochloramine grab: 2.90. Chemscan: 2.96 Free ammonia grab: 0.03 Chemscan: 0.03. No other issues found. Entered data into process sheets. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-12-19
CENTRAL | December | Checked/troubleshoot Ammonia mixer switch reported not working properly. Changed/replaced switch and tested ok. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-12-22
CENTRAL | December | -Performed chlorine overhaul -Changed chlorine cylinders | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-12-17
CENTRAL | December | 29:54 roc called for post inj ammonia hihi of 0.21 mg/l. Interlocked chemical dosing system. Analyzer reading dropped below hihi to 0.18mg/l. Ack and cleared alarm by 20:00. Chemical system resumed dosing. Reviewed station check log data. Free ammonia analyzer offset was bumped up to match grabs. Adjusted chlorine to ammonia ratio to account for higher post injection readings/grab from earlier in the day. 4.5 from 4.4. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-12-29
CENTRAL | December | On-site for a station and equipment check No issues found Taken weekly bacti sample Chemical levels and systems ok Verified analyzers, all readings and grabs entered into PWQ sheet Pre-injection Free@1052 g:0.07 a:0.06mg/L Pre-injection Total@1054 g:1.68 a:1.68mg/L Post-injection Free@1103 g:0.05 a:0.05mg/L Post-injection Total@1103 g:3.02 a:2.93mg/L | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-12-16
CENTRAL | December | On-site for a station and equipment check. Mixer toggle on/off tank 1 not working. Work order created Topped up ammonia day tank 1 Weekly bacti sample taken W11469830 Verified analyzers, and entered all readings and grabs into PWQ sheet PreFree@1017 G:0.04 A:0.06mg/L PreTotal@1017 G:1.68 A:1.68mg/L PostFree@1023 G:0.04 A:0.02mg/L PostTotal@1028 G:1.79 A:1.76mg/L | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-12-22
CENTRAL | December | On-site for a station and equipment check No issues found Topped up both ammonia day tanks Added new KI and acetate solutions for pre-injection analyzer Chemical levels and systems ok Verified analyzers and entered all readings and grabs into PWQ sheet Adjusted FA pre-injection to 0.12 from 0.07mg/L Adjusted FA post-injection to 0.07 from 0.02 both based on SL1000 grabs Pre-injection Free@1141 G:0.04 A:0.06mg/L Pre-injection Total@1143 G:1.65 A:1.61mg/L Post-injection Free@1205 G:0.05 A:0.05mg/L Post-injection Total@1206 G3.14 A:3.17mg/L | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-12-29
CENTRAL | December | Onsite to perform annual maintenance/calibration on both Chlorinators. Informed ROC and they closed the discharge valve. We isolated gas cylinders and purged the lines to the drain. We rebuilt both the chlorinators. performed vacuum test. No leak found. Performed gas calibration discharging it to drain and Performed verification and Put chlorinators back in service. No issues. During calibration, Post injection Total and free chlorine reading spiked and was reading hi. During this time no flow leaving the reservoir and discharge valve was closed. Informed ROC and they opened up the discharge valve. Monitored for a while. No issues. Armed the building and left the site. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-12-24
CENTRAL | December | -Responded Hi post-free ammonia - performed grab test: mono=2.87mg/L free ammonia=0.05mg/L total ammonia=0.62mg/L - Analyzer: mono=3.00mg/L free ammonia=0.07mg/L total ammonia=0.69mg/L - Adjusted post-free ammonia's offset from 0.13 to 0.1 & total ammonia's offset from 0.09 to 0.04 | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-12-31
CENTRAL | December | Onsite to follow up with free ammonia numbers as hihi post injection of 0.21 mg/l recorded last night. 13:54 post injection grab: Free ammonia: 0.0 and 0.0. Analyzer: 0.10. Adjusted analyzer to match. Adjusted chlorine/ammonia ratio from 4.5 to 4.4. 14:10 pre injection free ammonia grab: 0.04. Analyzer 0.13. Adjusted analyzer to match. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-12-30
CENTRAL | December | On-site for a station and equipment check No issues found Changed bank B with J Zhang Topped up ammonia day tank 2 Verified analyzers, entered all readings and grabs into PWQ sheet Pre Free@0919 G:0.07 A:0.06 Pre Total@0919 G:1.68 A:1.68 Post Free@0925 G:0.06 A:0.05 Post Total@0926 G:3.30 A:3.25 | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2025-12-24
CENTRAL | December | Onsite to complete work orders. 09:49 Notified ROC of work. Portable Diesel generator test. Fuel and oil level ok. No issues. 09:57 tested low building temperature alarm. Placed Chlorine analyzer in calibration mode. Replaced micro 2000 acetate reagent. 10:20 verified. Free grab 0.10 mg/l. Analyzer: 0.07. total grabs 2.36/2.44/2.44. Analyzer 2.24. adjusted to match grabs. Heat trace line 1 and 2 both on and ok. No issues found on site. | Aurora (Southwest) Allenvale Elevated Tank | 2025-12-12
CENTRAL | December | On-site for a station and equipment check, no issues found Took weekly bacti and biweekly operational samples while draining Verified analyzers, entered all grabs and measurements into PWQ sheet Free CL2 @1408 g:0.06 a:0.06mg/L Total CL2 @1409 g:2.04 a:2.06mg/L | Aurora (Southwest) Allenvale Elevated Tank | 2025-12-10
CENTRAL | December | On-site for a station and equipment check, no issues found. Took weekly bacti samples while draining Took blended system sample Verified analyzer, entered all readings and grabs into PWQ sheet General housekeeping | Aurora (Southwest) Allenvale Elevated Tank | 2025-12-03
CENTRAL | December | On-site for a station and equipment check. No issues found. Added new KI solution Took weekly bacti sample while draining W11469830 Verified analyzers, entered all readings and grabs into PWQ sheet Free@1109 G:0.07 A:0.07mg/L Total@1119 G:2.15 A:2.20mg/L | Aurora (Southwest) Allenvale Elevated Tank | 2025-12-22
CENTRAL | December | On-site for a station and equipment check. No issues found. Weekly bacti sample taken while draining Verified analyzers and entered all readings and grabs into PWQ sheet Free@1315 G:0.05 A:0.08mg/L Total@1317 G:2.24 A:2.20mg/L | Aurora (Southwest) Allenvale Elevated Tank | 2025-12-29
CENTRAL | December | On-site for a station and equipment check No issues found Weekly bacti sample taken while draining Verified analyzers and entered all readings and grabs into PWQ sheet Free@1148 g: 0.07 a: 0.08mg/L Total@1151 g:2.32 a:2.31mg/L | Aurora (Southwest) Allenvale Elevated Tank | 2025-12-16
CENTRAL | December | -Performed station check - logged station readings into PWQ sheet -Checked Depolox reagents - OK | Aurora Orchard Heights Pumping Station & Reservoir | 2025-12-12
CENTRAL | December | -Performed station check - logged station readings into PWQ sheet Grab: free=0.09mg/L total=3.00mg/L@9:45 Analyzer: free=0.04mg/L total=3.03mg/L -Topped up Depolox buffer solution -Collected weekly BacT sample YD# W11439251 & in-house water quality samples | Aurora Orchard Heights Pumping Station & Reservoir | 2025-12-10
CENTRAL | December | On-site for station check of pumping station. Found heater 1, 2, and 3 tripped. Building is cold but ok. Reset heater breakers and heaters turned on. Reservoir at 55% and draining. Entered data into pumping station process sheets. P3 checkvalve continues to pass water slightly. Previous work order created. No other issues found. Left site. | Aurora Orchard Heights Pumping Station & Reservoir | 2025-12-15
CENTRAL | December | -Performed station check - logged station readings into PWQ sheet -Checked Depolox reagents - OK | Aurora Orchard Heights Pumping Station & Reservoir | 2025-12-09
CENTRAL | December | -Performed station check - logged station readings into PWQ sheet -Checked Depolox reagents - OK | Aurora Orchard Heights Pumping Station & Reservoir | 2025-12-05
CENTRAL | December | -Helped performing semi-annual diesel generator test run | Aurora Orchard Heights Pumping Station & Reservoir | 2025-12-09
CENTRAL | December | -Performed station check - logged station readings into PWQ sheet -Finished the following work orders *Depolox analyzer maintenance *Vent inspection *Pump & motor inspection *Dehumidifier inspection *PRV inspection *H&S inspection *Tested hi/low temp alarm **Diesel generator test run Pre-run inspection - OK Hours Start=200.9 Finish 200.9 Fuel Start=2612L Finish 2620L Tested generator while under load (P3 and P4): RPM- 1800 Volts- 600 Amperes- 79 Hertz- 60 Coolant temp 87oC Oil temp 93oC Oil pressure 444kPa Fuel temp- 87 C | Aurora Orchard Heights Pumping Station & Reservoir | 2025-12-02
CENTRAL | December | -Performed station check - logged station readings into PWQ sheet Grab: treated total=2.86mg/L free=0.08mg/L@9:55 Analyzer: treated total=2.91mg/L free=0.00mg/L -Checked Depolox reagents - OK -Calibrated treated free analyzer based on 3 grab tests -Collected weekly BacT sample YD #W11420059 & monthly sample YD #11420025 | Aurora Orchard Heights Pumping Station & Reservoir | 2025-12-03
CENTRAL | December | -Performed station check - logged station readings into PWQ sheet Grab: treated total=3.10mg/L free=0.03mg/L@11:00 Analyzer: treated total=3.16mg/L free=0.05mg/L -Checked Depolox reagents - OK -Collected weekly BacT sample YD #W11484058 | Aurora Orchard Heights Pumping Station & Reservoir | 2025-12-29
CENTRAL | December | -Performed station check - logged station readings into PWQ sheet Grab: treated free=0.06mg/L total=3.18mg/L@12:20 Analyzer: treated free=0.02mg/L total=3.24mg/L -Checked Depolox reagents - OK -Collected weekly BacT sample YD #W11455350 | Aurora Orchard Heights Pumping Station & Reservoir | 2025-12-16
CENTRAL | December | -Performed station check - logged station readings into PWQ sheet -Checked Depolox reagents - OK | Aurora Orchard Heights Pumping Station & Reservoir | 2025-12-19
CENTRAL | December | -Performed station check - logged station readings into PWQ sheet -Checked Depolox reagents - OK | Aurora Orchard Heights Pumping Station & Reservoir | 2025-12-24
CENTRAL | December | Station Check (no issues found) Input data to PWQ 10:20 Verified Depolox (mg/L): Free: Grab 0.04, A 0.0 (zero cal. , standard cal. to match grabs) Total: Grab 2.96, A 2.95 10:25 #11470534 sample | Aurora Orchard Heights Pumping Station & Reservoir | 2025-12-22
CENTRAL | December | On-site for a station and equipment check, no issues found. Ammonia pump 2 inspected and drawdown completed @25% for 4 mins 211mL/min. All fittings and prv's working well within limits. Verified analyzers and entered all readings and grabs into PWQ sheet Adjust pre-injection FA on Chemscan unit from 0.18 to 0.11 based on SL1000 grab Pre-injection Free CL2@1037 g: 0.05 a:0.04 Pre-injection Total CL2@1039 g:1.76 a:1.81 Post-injection Free CL2@1056 g:0.06 a:0.07 Post-injection Total CL2 @1057 g:2.60 a:2.58 | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2025-12-12
CENTRAL | December | On-site for a station and equipment check, no issues found. Weekly bacti and operational samples taken from outlet Verified analyzers, entered all grabs and measurements into PWQ sheet Adjust pre-injection FA to 0.16 from 0.12 after grab of 0.17mg/L and post total ammonia to 0.60 from 0.42mg/L based on SL1000 grabs Chemical levels and systems inspected and ok Pre-injection Free@1135 g:0.06 a:0.05mg/L Pre-injection Total@1135 g:1.77 a:1.83mg/L Post-injection Free@11:56 g:0.04 a:0.05mg/L Post-injection Total@1200 g:2.58 a:2.58mg/L Zone3 Free@12:03 g:0.03 a:0.04mg/L Zone3 Total@1204 g:2.28 a:2.31mg/L Outlet Free@1221 g: 0.06 a:0.04mg/L Outlet Total@1224 g: 2.36 a:2.32mg/L | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2025-12-10
CENTRAL | December | On-site for a station and equipment check, no issues found Chemical systems and levels ok Verified analyzers, entered all readings and grabs into PWQ sheet Adjust pre-injection Free Ammonia to 0.08 from 0.02 base on a grab of 0.08mg/L on SL1000 Pre-injection free@0900 g:0.06 a:0.06mg/L Pre-injection Total@0904 g:2.32 a:2.32mg/L Post-injection Free@0906 g:0.03 a:0.04mg/L Post-injection Total@0910 g:2.36 a:2.37mg/L | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2025-12-15
CENTRAL | December | Onsite to troubleshoot Chemscan analyzer issue. Analyzer was already in offline mode. Removed the flow cell and cleaned it. Put it back and William performed zero test. Values within range. No issues. Informed ROC and left the site. | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2025-12-02
CENTRAL | December | On-site for a station and equipment check, no issues found. Chemical levels and systems ok Cylinder change bank 1 completed with J Zhang Verified analyzers and entered all measurements and grabs into PWQ sheet Pre-injection: Free CL2 @1244 G:0.03 A: 0.04mg/L Total CL2 @1246 G:1.78 A: 1.75mg/L Post-injection: Free CL2 @1249 G:0.07. A:0.07mg/L Total CL2@1250 G:2.54 A:2.55mg/L Zone 3 Free CL2 @1255 G:0.06 A:0.04mg/L Total CL2 @1255 G:2.28 A:2.29mg/L Res Outlet: Free CL2 @1258 G:0.06 A:0.04mg/L Total CL2 @1306 G:2.17 A: 2.29mg/L | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2025-12-05
CENTRAL | December | On-site for station check. 09:01 Reservoir outlet draining at 43 l/s. Zone 3 running at 70 l/s in duty. Chemical boosting not active. Reservoir level at 70%. Replaced outlet total analyzer reagents. Verified analyzer residuals (mg/l): 09:32 Pre-injection grabs: Free chlorine grab: 0.04. Analyzer: 0.05. Total Chlorine grab: 2.31 CL17 Analyzer: 2.29. Chemscan: 2.37. 09:39 Post-injection grabs: Free chlorine grab: 0.06. Analyzer: 0.05. Total Chlorine grab: 2.30 CL17: 2.30. Chemscan: 2.37. 09:57 Zone 3 grabs: Free chlorine grab: 0.00. Analyzer: 0.04. Total chlorine grab: 2.19 Analyzer: 2.25. 10:04 Reservoir outlet chlorine grab. Free grab: 0.08. Analyzer: 0.04. Total grab: 2.19 Analyzer: 2.24. Station and equipment ok. | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2025-12-01
CENTRAL | December | On-site for various WO's Notified ROC of work orders Completed testing of CL2 gas leak detector sensor, reset halogen systems and cleared interlock All monthly maintenance and cleaning of all analyzers completed Chemscan monthly maintenance completed. unable to get values within range. Called ROC to dispatch on-call Parth Patel to troubleshoot Unable to complete monthly generator testing as Total Power on-site for generator maintenance most of the day. Chemical storage tanks, ammonia, inspected. confirmed spill containment alarm functioning Visual inspection completed of all injection points, no issues found | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2025-12-02
CENTRAL | December | On-site for station check. 1316 Reservoir inlet filling at 53 l/s. Zone 3 Pump 1 and 2 in standby. Chemical boosting active. Reservoir level at 64%. Replaced post injection total and pre injection free analyzer reagents. Topped up ammonia tank 1. Verified analyzer residuals (mg/l): 13:45 Pre-injection grabs: Free chlorine grab: 0.07. Analyzer: 0.04. Total Chlorine grab: 1.81 CL17 Analyzer: 1.79. Chemscan: 1.91. Monchloramine grab: 1.66. Chemscan: 1.67 Free ammonia: 0.15. Chemscan: 0.12 Total ammonia: 0.48. Chemscan: 0.44. 13:55 Post-injection grabs: Free chlorine grab: 0.07. Analyzer: 0.06. Total Chlorine grab: 2.62 CL17: 2.63. Chemscan: 2.69. Monchloramine grab: 2.25. Chemscan: 2.33 Free ammonia: 0.04. Chemscan: 0.02. Total ammonia: 0.48. Chemscan: 0.44. 14:07 Zone 3 grabs: Free chlorine grab: 0.05 Analyzer: 0.04. Total chlorine grab: 2.32 Analyzer: 2.29. 14:12 Reservoir outlet chlorine grab. Free grab: 0.05. Analyzer: 0.04. Total grab: 2.32 Analyzer: 2.28. Station and equipment ok. | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2025-12-08
CENTRAL | December | Low oil in one of the motors top up Top up oil 2 cups | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2025-12-24
CENTRAL | December | On-site for a station and equipment check, no issues found Chemical levels and systems ok. Verified all analyzers and entered all readings and grabs into PWQ sheet Took weekly bacti sample WO- W1419071 And blended system sample W11419384 | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2025-12-03
CENTRAL | December | On-site for station check. Changed chlorine cylinder B with Jerry Z. 10:00 Reservoir inlet filling at 37 l/s. Zone 3 Pump 1 and 2 in standby. Chemical boosting active. Reservoir level at 72%. Replaced zone 3 free and total, pre injection total and post injection free cl17 reagents. Topped up chemscan distilled water. Verified analyzer residuals (mg/l): 10:23 Pre-injection grabs: Free chlorine grab: 0.09. Analyzer: 0.04. Total Chlorine grab: 1.74 CL17 Analyzer: 1.65. Chemscan: 1.74. Monchloramine grab: 1.47. Chemscan: 1.50. Free ammonia: 0.08. Chemscan: 0.04 Total ammonia: 0.34. Chemscan: 0.37. 10:38 Post-injection grabs: Free chlorine grab: 0.11. Analyzer: 0.06. Total Chlorine grab: 2.67 CL17: 2.59. Chemscan: 2.71. Monchloramine grab: 2.27. Chemscan: 2.28 Free ammonia: 0.01. Chemscan: 0.02. Total ammonia: 0.45. Chemscan: 0.53. Adjusted chlorine/ammonia ratio from 4.5 to 4.4. 10:52 Zone 3 grabs: Free chlorine grab: 0.04 Analyzer: 0.04. Total chlorine grab: 2.26 Analyzer: 2.29. 11:10 Reservoir outlet chlorine grab. Free grab: 0.04. Analyzer: 0.04. Total grab: 2.26 Analyzer: 2.25. Station and equipment ok. Entered readings into PD sheets. | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2025-12-19
CENTRAL | December | On-site for a station and equipment check No issues found Weekly bacti sample taken. Chemical levels and systems ok General housekeeping Adjusted pre-injection FA to 0.09 from 0.15mg/L on Chemscan based on SL1000 grabs Verified analyzers, all readings and grabs entered into PWQ sheet Pre-injection Free@1301 g:0.04 a:0.04mg/L Pre-injection Total@1303 g:1.72 a:1.70mg/L Post-injection Free@1308 g:0.10 a:0.09mg/L Post-injection Total@1338 g:2.52 a:2.59mg/L Zone3 Free@1405 g:0.02 a:0.03mg/L Total@1406 g:2.32 a:2.29mg/L Outlet Free@1407 g:0.04 a:0.04mg/L Outlet Total@1416 g:2.36 a:2.31/mgL | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2025-12-16
CENTRAL | December | On-site for a station and equipment check No issues found Topped up ammonia day tank 2 Chemical levels and systems ok Verified analyzers, entered all readings and grabs into PWQ sheet Pre-Free@1039 G:0.06 A:0.05mg/L Pre-Total@1040 G:2.09 A:2.09mg/L Post-Free@1053 G:0.05 A:0.03mg/L Post-Total@1050 G:1.68 A:1.78mg/L Zone 3 Free@1053 G:0.05 A:0.04mg/L Total@1054 G:2.32 A:2.30mg/L Res Outlet Free@1059 G:0.06 A:0.04mg/L Total@1101 G:2.30 A:2.30mg/L | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2025-12-24
CENTRAL | December | On-site for a station and equipment check Floor seemed to have a bit of water accumulated. I moped up but could not find the cause. I will follow up when the team is back first week of January Bacti sample taken from outlet. Chemical levels and systems ok. Verified analyzers and entered all readings and grabs into PWQ sheet Pre-Free@0839 G:0.04 A:0.05mg/L Pre-Total@0842 G:1.86 A:1.82mg/L Post-Free@0848 G:0.05 A:0.06mg/L Post-Total@0850 G:2.50 A:2.59mg/L Zone 3 Free@08:53 G:0.04 A:0.04mg/L Total@0855 G:2.20 A:2.28mg/L Outlet Free@0858 G:0.05 A:0.04mg/L Total@0859 G:2.24 A:2.28mg/L | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2025-12-29
CENTRAL | December | On-site for a station and equipment check. No issues found. Weekly bacti sample taken, W11469830 Verified analyzers and entered all readings and grabs into PWQ sheet | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2025-12-22
CENTRAL | December | -Performed station check - logged station readings into PWQ sheet -Changed effluent free reagents | Aurora Well 5 | 2025-12-12
CENTRAL | December | Changed right chlorine cylinder with Alex B. Received 9 chlorine cylinders. No issues found. Well remain OOS due to pulsing noises. | Aurora Well 5 | 2025-12-15
CENTRAL | December | -Performed station check - logged station readings into PWQ sheet Grab: treated free=0.17mg/L total=2.80mg/L@12:00 influent free=2.74mg/L effluent free=2.38mg/L Analyzer: treated free=0.12mg/L total=2.74mg/L influent free=2.74mg/L effluent free=2.32mg/L -Checked CL17 reagents - OK -Collected weekly BacT sample YD# W11439251 | Aurora Well 5 | 2025-12-10
CENTRAL | December | -Performed station check - logged station readings into PWQ sheet Grab: treated total=3.00mg/L free=0.16mg/L@14:45 influent free=2.66mg/L effluent free=2.50mg/L Analyzer: treated total=2.90mg/L free=0.13mg/L influent free=2.69mg/L effluent free=2.43mg/L -Changed treated total reagents -Collected weekly BacT sample YD #W11420059 | Aurora Well 5 | 2025-12-03
CENTRAL | December | -Performed station check - logged station readings into PWQ sheet -Checked CL17 reagents - OK | Aurora Well 5 | 2025-12-05
CENTRAL | December | Attempt to grease motor bearing | Aurora Well 5 | 2025-12-05
CENTRAL | December | On site to complete station check and collect operational samples. Verified analyzers: Influent Free Chlorine @ 10:19 Grab: 2.74 mg/L Analyzer: 2.70 mg/L Effluent Free Chlorine @ 10:17 Grab: 2.46 mg/L Analyzer: 2.43 mg/L Treated Free Chlorine @ 10:10 Grab: 0.09 mg/L Analyzer: 0.12 mg/L Treated Total Chlorine @ 10:10 Grab: 2.99 mg/L Analyzer: 2.86 mg/L -Entered data into PD sheet -Checked trends -Returned well 5 to auto | Aurora Well 5 | 2025-12-01
CENTRAL | December | -Finished the following work orders *Chemical system inspection *Exhaust damp and fan inspection *Deep well exhaust valve inspection *Turbidimeter maintenance *CL17 analyzer maintenance *H&S inspection | Aurora Well 5 | 2025-12-04
CENTRAL | December | Grease bottom motor bearing Couldn?t grease not running | Aurora Well 5 | 2025-12-02
CENTRAL | December | -Performed station check - logged station readings into PWQ sheet Grab: treated free=0.18mg/L total=2.74mg/L@15:00 influent free=2.64mg/L effluent free=2.38mg/L Analyzer treated free=0.12mg/L total=2.82mg/L influent free=2.68mg/L effluent free=2.34mg/L -Checked CL17 reagents - OK -Collected weekly BacT sample YD #W11455350 & in-house water quality samples | Aurora Well 5 | 2025-12-16
CENTRAL | December | On-site for station check. Powered on well 5. 09:14. Activated well 5 in manual on. Combined lo alarm of 0.57 mg/l triggered but residual increased and cleared on next analyzer reading. Verified chlorine analyzers (mg/l). 10:00. Influent free chlorine grab: 2.62 Analyzer: 2.70. 10:19. Effluent free chlorine grab. 2.09. Analyzer: 2.12 10:24. Treated free chlorine grab: 0.13 CL17: 0.12. 10:24. Treated total chlorine grab: 2.44 CL17: 2.53. Entered data into process sheets. 10:30. Shut down well and disconnected power. Locked out well 5 as per IWS request to investigate well pulsing noises. No other issues found. | Aurora Well 5 | 2025-12-08
CENTRAL | December | -Performed year-end inventory check | Aurora Well 5 | 2025-12-23
CENTRAL | December | -Performed station check - logged station readings into PWQ sheet -Checked CL17 reagent - OK *Tested chlorine leak alarm | Aurora Well 5 | 2025-12-19
CENTRAL | December | -Performed station check - logged station readings into PWQ sheet -Changed treated free reagents | Aurora Well 5 | 2025-12-24
CENTRAL | December | Had to stop the DB so that I could add tags for Schedule Mode, trending wasn?t interrupter. Sire left under normal conditions | Aurora Well 5 | 2025-12-23
CENTRAL | December | 13:55 remotely adjusted floor setpoint from 45 L/s to 35 L/s. Activated well manually. | Aurora Well 5 | 2025-12-28
CENTRAL | December | -Performed station check - logged station readings into PWQ sheet Grab: Treated total=2.78mg/L free=0.16mg/L@10:00 Influent free=2.56mg/L effluent free=2.17mg/L Analyzer: Treated total=2.73mg/L free=0.12mg/L Influent free=2.67mg/L effluent free=2.24mg/L -Checked CL17 reagents - OK -Collected weekly BacT sample YD# W11484058 | Aurora Well 5 | 2025-12-29
CENTRAL | December | Station Check (no issues found) input data to PWQ 12:30 Verified CL17s (mg/l) Influent: Free Grab 2.60, A 2.69 Effluent: Free Grab 1.40, A 1.40 Treated: Free Grab 0.05, A 0.07 Total: Grab 1.90, A 1.87 Influent Free (new reagents) 12:50 #11470534 raw/treat. samples | Aurora Well 5 | 2025-12-22
CENTRAL | December | Onsite for station check. Well offline. Site secure. No issues. | Aurora Well 6 | 2025-12-15
CENTRAL | December | -Performed station check | Aurora Well 6 | 2025-12-02
CENTRAL | December | -Performed H&S inspection | Aurora Well 6 | 2025-12-05
CENTRAL | December | -Performed station check | Aurora Well 6 | 2025-12-09
CENTRAL | December | Station Check (no issues) facility off-line | Aurora Well 6 | 2025-12-22
CENTRAL | December | Change out wasting valve solenoid Cleared alarm on multi link had control run well duty 1 running properly Flood alarm activated cleared on panel | Aurora Wells 1-4 Water Treatment Plant | 2025-12-12
CENTRAL | December | Check solenoid well 1 Wasting valve holding small leak from solenoid Ordered new solenoid | Aurora Wells 1-4 Water Treatment Plant | 2025-12-11
CENTRAL | December | On-site for station check. 10:00 Wells 1-4 running at 135 l/s combined. Topped up silicate day tanks. 10:14 Adjusted turbidity analyzer sample flow up and caused a momentary turbidiyt spike reading to 0.8 NTU. Analyzer dropped back to 0.049 NTU after a minute. 11:16 Verified chlorine analyzers (mg/l): Influent free grab: 2.72/2.70/2.70 analyzer: 2.63. Adjusted to match grab average. Effluent free chlorine grab: 2.66/2.64/2.66vAnalyzer: 2.45. Adjusted to match grab average. Treated free chlorine grab: 0.11 Analyzer: 0.12. Treated total chlorine grab: 2.96 Analyzer: 3.01 Treated monochloramine grab: 2.52 Treated free ammonia grab: 0.05 Treated total ammonia grab: 0.55 Topped up well pump 3 and 4 oil reserves both from half full. No issues found. | Aurora Wells 1-4 Water Treatment Plant | 2025-12-15
CENTRAL | December | -Received 12 chlorine cylinders *Performed H&S inspection | Aurora Wells 1-4 Water Treatment Plant | 2025-12-12
CENTRAL | December | -Reset building flood alarm - the float to sump pump stuck - reset the float - reset flood alarm -Performed station check - logged station readings into PWQ sheet -Changed treated free reagents -Changed chlorine cylinders -Finished the following work orders *CL17 analyzer maintenance *Turbidimeter maintenance *Chlorine leak test | Aurora Wells 1-4 Water Treatment Plant | 2025-12-12
CENTRAL | December | -Performed station check - logged station readings into PWQ sheet Grab: treated free=0.14mg/L total=3.02mg/L@14:25 influent free=2.56mg/L effluent free=2.50mg/L Analyzer: treated free=0.12mg/L total=3.01mg/L influent free=2.55mg/L effluent free=2.49mg/L -Checked CL17 reagents - OK -Collected weekly BacT sample YD# W11439251 | Aurora Wells 1-4 Water Treatment Plant | 2025-12-10
CENTRAL | December | -Finished the following work orders *Air relief valve inspection *Chemical pumps inspection | Aurora Wells 1-4 Water Treatment Plant | 2025-12-09
CENTRAL | December | On-site for station check. 10:58 Wells 1-4 running at 205 l/s combined. Topped up silicate day tanks from 1049 L to 1411 L. 11:48 Verified chlorine analyzers (mg/l): Influent free grab: 2.66 analyzer: 2.67. Effluent free chlorine grab: 2.62 Analyzer: 2.65. Treated free chlorine grab: 0.08 Analyzer: 0.13. Treated total chlorine grab: 3.06 Analyzer: 3.11 Treated monochloramine grab: 2.61 Treated free ammonia grab: 0.03 Treated total ammonia grab: 0.55 No issues found. | Aurora Wells 1-4 Water Treatment Plant | 2025-12-08
CENTRAL | December | Try to grease motor bearings Instrumentation working on chlorine system | Aurora Wells 1-4 Water Treatment Plant | 2025-12-05
CENTRAL | December | Onsite for chlorinators rebuild and calibration Informed ROC and operations ROC placed well duties to manual off Purged chlorine system and isolated Rebuilt chlorinators and performed vacuum leak test - all OK Put chlorine system back in service and performed gas calibration - all OK Operations back flushed and placed duty back to auto Monitored for a while, no issues Informed ROC and operations. Left site | Aurora Wells 1-4 Water Treatment Plant | 2025-12-05
CENTRAL | December | Grease well 4 motor bottom bearing | Aurora Wells 1-4 Water Treatment Plant | 2025-12-02
CENTRAL | December | -Changed chlorine cylinders | Aurora Wells 1-4 Water Treatment Plant | 2025-12-04
CENTRAL | December | -Performed station check - logged station readings into PWQ sheet Grab: treated total=3.12mg/L free=0.16mg/L@12:25 influent free=2.64mg/L effluent free=2.60mg/L Analyzer: treated total=3.02mg/L free=0.13mg/L influent free=2.60mg/L effluent free=2.54mg/L -Checked CL17 reagents - OK -Collected weekly BacT sample YD #W11420059 | Aurora Wells 1-4 Water Treatment Plant | 2025-12-03
CENTRAL | December | -Performed station check - logged station readings into PWQ sheet -Checked CL17 reagents - OK -Backflushed contact tank and restarted wells after chlorinators calibration | Aurora Wells 1-4 Water Treatment Plant | 2025-12-05
CENTRAL | December | On-site for station check. 13:17 Wells 4, 2 and 3 running at 167 l/s. Well 1 in manual off after waste valve hihi flow alarm triggered at 06:16. flow reached 41.92 l/s. Acknowledged and cleared alarm. Tightened waste discharge butterfly valve. Topped up silicate day tanks from 942 L to 1448 L. Topped up ammonia tank 2. 176 to 1139 L. 13:54Verified chlorine analyzers (mg/l): Influent free grab: 2.68/2.70/2.68 analyzer: 2.54. Adjusted to match grab average. Effluent free chlorine grab: 2.58 Analyzer: 2.59. Treated free chlorine grab: 0.14 Analyzer: 0.13. Treated total chlorine grab: 3.00Analyzer: 3.10 Treated monochloramine grab: 2.61 Treated free ammonia grab: 0.24/0.13/0.14 Treated total ammonia grab: 0.76/0.65/0.63 Adjusted chlorine/ammonia ratio from 3.7 to 3.8. Placed week 3 back in auto. Placed well 1 in manual on to test waste flow. Faulted with no flow fault on fit 1 first try. Adjusted the discharge line valve again. No issues found on second attenpt. Entered readings into process data sheets. No issues found. | Aurora Wells 1-4 Water Treatment Plant | 2025-12-01
CENTRAL | December | -Reset W1 multi-line trip alarm - unbalanced alarm on MCC - changed unbalance setting from 6% to 7% -Performed station check - logged station readings into PWQ sheet Grab: treated free=0.11mg/L total=2.76mg/L@11:35 influent free=2.40mg/L effluent free=2.40mg/L Analyzer treated free=0.12mg/L total=2.86mg/L influent free=2.56mg/L effluent free=2.42mg/L -Checked CL17 reagents - OK -Collected weekly BacT sample YD #W11455350 -Calibrated influent free analyzer based on 3 grabs | Aurora Wells 1-4 Water Treatment Plant | 2025-12-16
CENTRAL | December | -Received silicate delivery -Performed diesel generator test run Pre-run inspection - good Hour Start 88.25 Stop 89.55 Fuel Start 7252L Stop 7143L Generator operating stats while under load (P2 and P4): RPM- 1800 Oil pressure-78 Oil temp- 189 F Coolant temp- 179 F Fuel pressure- 102psi Fuel temp- 89F Frequency- 60 Hz Voltage- 603 V Amperage- 205A | Aurora Wells 1-4 Water Treatment Plant | 2025-12-18
CENTRAL | December | Onsite with Jerry Z. To change out chlorine cylinder bank A. | Aurora Wells 1-4 Water Treatment Plant | 2025-12-19
CENTRAL | December | -Changed chlorine cylinders -Performed station check - logged station readings into PWQ sheet -Changed influent free reagents | Aurora Wells 1-4 Water Treatment Plant | 2025-12-24
CENTRAL | December | Station Check (no issues) Input data to PWQ 8:50 Verified CL17s (mg/l) Influent: Free Grab 2.50, A 2.56 Effluent: Free Grab 2.38, A 2.45 Treated: Free Grab 0.08, A 0.11 Total: Grab 2.90, A 2.85 #11470535 samples 8:40 raw (2&4) 9:10 treated 13:15 raw (1&3) Silicate day tank top up | Aurora Wells 1-4 Water Treatment Plant | 2025-12-22
CENTRAL | December | -Performed year-end inventory count | Aurora Wells 1-4 Water Treatment Plant | 2025-12-23
CENTRAL | December | Recorded 13 chlorine cylinders. Returned 24 empty. Picked up 750 L of silicate from bulk tank. Topped up silicate day tanks. | Aurora Wells 1-4 Water Treatment Plant | 2025-12-30
CENTRAL | December | -Performed station check - logged station readings into PWQ sheet Grab: Treated total=3.08mg/L free=0.14mg/L@14:00 Influent free=2.64mg/L effluent free=2.54mg/L Analyzer: Treated total=3.10mg/L free=0.11mg/L Influent free=2.64mg/L effluent free=2.68mg/L -Checked CL17 reagents - OK -Calibrated effluent free analyzer based on 3 grab tests -Collected weekly BacT sample YD# W11484058 | Aurora Wells 1-4 Water Treatment Plant | 2025-12-29
CENTRAL | December | -Changed chlorine cylinders -Performed station check - logged station readings into PWQ sheet -Changed treated total reagents -Topped up W4's drip oil reservoir & adjusted speed to 3 drops per minute | Aurora Wells 1-4 Water Treatment Plant | 2025-12-19
EAST | December | On site for station check. Reviewed scada, duty not active. Cell level @ 72 and 72% Visual inspection in and around station Verification of equipment and instrumentation. Outstanding alarm: None. Free Chlorine HIHI alarm outstanding upon arrival. Verified chlorine analyzers readings. Chlorine residual @ 13:17 hrs Grab: FCL= 0.04 mg/L TCL = 1.36 mg/L Analyzer: FCL 0.23 mg/L TCL= 1.36 mg/L Performed free chlorine zero calibration with no flow condition. Returned flow to normal afterwards. Cleared alarm. Station OK, Recorded station readings into PWQ data sheet Completed air valve maintenance work order. | Bayview Pumping Station | 2025-12-12
EAST | December | Onsite to repair leaks on Discharge PIT 1 and 4 and complete calibrations Informed ROC. ROC placed pump 2 and 3 to duty 1 Used cal mode on scada during the work anyway Replaced manifold seals and tested for leaks - all ok Completed calibrations of 2 PITs Adjusted flow to free/total CL2 analyzer and took grabs Free: A = 0.04 G = 0.04 Total: A = 1.41 G = 1.43 Informed ROC, armed building and left site | Bayview Pumping Station | 2025-12-10
EAST | December | Unable to conduct station due to fire alarm system active upon arrival at the station. Notified ROC, TL and Supervisor for help ROC did not receive alarm, not sure alarm went to FMC or fire department. Supervisor contacting PS response and correction of issues. | Bayview Pumping Station | 2025-12-01
EAST | December | Attended site for station check, station and equipment okay | Bayview Pumping Station | 2025-12-08
EAST | December | On site to complete the following WOs: JHSC Health and Safety Inspection, Surge System Valves Exercise, Discharge Chamber, Surge System Valves Exercise, Discharge Chamber, Dehumidifier Cleaning & Inspection, Valves Exercise, Ventilation System Inspection Pressure Gauges Test, Siemens Analyzer Maintenance, Hoist System Inspection Flood Alarm Test, Sump Pump Maintenance, Check Valve, Service & Inspection, Pump Discharge Valve Actuator Inspection & Exercise, Standby Power GeneratorRun and Run Notified ROC Reviewed scada, duty off, reservoir level at 70% Placed all pumps and discharge valves in manual off Before Diesel Generator Test Run Sheet running generator, the following were inspected: ? Battery cell levels ? Battery terminal and cables ? Oil level ? Coolant level ? Fluid leaks ? Coolant Recirculating pump ? Faulty gauges Diesel generator start time: 1204 hrs Diesel hours at start: 114.5 hrs Fuel Level @ start: ? Tank #1 ~ 2882 L ? Tank #2 ~ 2940 L After 30 min of running: ? Operating current = 250 A ? Operating frequency = 60 Hz ? Operating voltage = 600 V ? Engine speed = 1800 RPM ? Water temperature = 80 C ? Oil temperature = 78 ? Oil pressure = 56 psi ? Fuel pressure. = ? ? Pyrometer/Exhaust = 205/205 C Stopped and transferred power to hydro @ 1450 hrs Diesel generator hours after shutdown: 115.9 hrs ? Tank #1 ~ 2744 L ? Tank #2 ~ 2790 L Additional information/ Observations: Ran pump1 and 4 in manual during generator test under load, no issues | Bayview Pumping Station | 2025-12-02
EAST | December | Vibration readings | Bayview Pumping Station | 2025-12-03
EAST | December | On site to complete station check. Time: 13:45 Grab (mg/l) Analyzer (mg/l) Free: 0.05 0.01 Total: 1.41 1.44 Verified analyzers with grabs all ok. Checked site and trends. No OOS equipment on site. No outstanding alarms on site. | Bayview Pumping Station | 2025-12-05
EAST | December | OIC Donald Moses. Onsite responding to power failure. Generator is shutting down when pumps activate. Found p2 multilin voltages to be unusual. No other issues identified. Restarted pumps 1 and 3 with no issues. Placed p2 manual off. Satnam to remain on site and wait for high voltage electrical contractors to examine switchgear as utility power is still off. | Bayview Pumping Station | 2025-12-27
EAST | December | On site for station check. Reviewed scada, duty active. Cell level @ 78 and 78% Visual inspection in and around station Verification of equipment and instrumentation. Outstanding alarm: None Verified chlorine analyzers readings. Free chlorine reading negative on arrival, perform no flow zero cal and return to normal after. Chlorine residual @ 11:42 hrs Grab: FCL= 0.05 mg/L TCL = 1.49 mg/L Analyzer: FCL = 0.03 mg/L TCL= 1.50 mg/L Station OK, Recorded station readings into PWQ data sheet. | Bayview Pumping Station | 2025-12-18
EAST | December | On site for station check Pump 3 and 4 in duty 1 - directed ROC to ensure one pump assigned lead on each header and to make the change on the next duty cycle Verified chlorine analyzers, 13:45, mg/L FCl - G 0.07; A 0.03 - Zero and span calibrated the FCl analyzer TCl - G 1.38; A 1.42 Recorded observations in the shared PWQ sheet Inspected generator, pumps and equipment Station and equipment okay | Bayview Pumping Station | 2025-12-29
EAST | December | On site for station check Verified analyzer, 13:35, mg/L Free Cl - G 0.03; A 0.01 Total Cl - G 1.43; A 1.45 Recorded observations in the shared PWQ sheet Checked station and equipment Station and equipment okay | Bayview Pumping Station | 2025-12-22
WEST | December | Station Check (no issues found) Input data to PWQ Verified Depolox (mg/L) Free: Grab 0.06, A 0.07 Total: Grab 1.86, A1.82 (topped up Acetate) | East Vaughan Teston Pumping Station | 2025-12-15
WEST | December | Vibration readings | East Vaughan Teston Pumping Station | 2025-12-15
WEST | December | On site to complete station check. Free chlorine Grab: 0.05mg/L Analyzer: 0.07mg/L Total chlorine Grab: 1.95mg/L Analyzer 1.92mg/L Reagents - all ok | East Vaughan Teston Pumping Station | 2025-12-12
WEST | December | Onsite for station check Checked residuals mg/l @1250 Total analyzer 2.02 grab 1.99 Free analyzer 0.00 grab 0.06 Added grit and adjusted free analyzer based on average of multiple grabs Reagents ok Back onsite @1401 To investigate pd7 hi free cl2 Took free grab @1402 Free analyzer 0.32 grab 0.03 Adjusted analzyer | East Vaughan Teston Pumping Station | 2025-12-04
WEST | December | Vibration readings | East Vaughan Teston Pumping Station | 2025-12-10
WEST | December | Grease motor and pumps | East Vaughan Teston Pumping Station | 2025-12-08
WEST | December | OIC Donald Moses 08:10 . Pd8 pumps 2 and 4 placed into auto after confirming ok with Cole W. And ROC last night. | East Vaughan Teston Pumping Station | 2025-12-03
WEST | December | On site to complete station check. Free chlorine Grab: 0.04mg/L Analyzer: 0.01mg/L Total chlorine Grab: 1.98mg/L Analyzer 1.96mg/L Reagents - all ok | East Vaughan Teston Pumping Station | 2025-12-01
WEST | December | On site to complete station check. Free chlorine Grab: 0.06mg/L Analyzer: 0.18mg/L-0.06mg/L Total chlorine Grab: 1.96mg/L Analyzer 2.00mg/L Adjusted free analyzer from 0.18-0.06mg/L after multiple grabs Reagents - all ok | East Vaughan Teston Pumping Station | 2025-12-08
WEST | December | -on site for station check -checked trends -entered readings in PWQ: all ok -verified analyzer 10:15 -analyzer free: 0.08mg/l grab: 0.04mg/l - adjusted -analyzer total: 1.78mg/l grab: 1.98 mg/l - adjusted -reagents all ok | East Vaughan Teston Pumping Station | 2025-12-24
WEST | December | On site to complete station check Neither pump duty active Checked residuals mg/l @1115 Total analyzer 1.98 grab 1.78 Free analyzer 0.08 grab 0.09 Adjusted total analyzer based on average of multiple grabs Reagents OK | East Vaughan Teston Pumping Station | 2025-12-23
WEST | December | Onsite to reset VFD fault on pump 1 and pump 2 PD7 side Also reset process sump pump alarm Possibly caused by power blip Station ops normal | East Vaughan Teston Pumping Station | 2025-12-21
WEST | December | -on site for station check -entered readings in PWQ: all ok -verified analyzer 13:10 -analyzer free: 0.04mg/l grab: 0.06mg/l -analyzer total: 2.04mg/l grab: 2.00mg/l -reagents all ok | East Vaughan Teston Pumping Station | 2025-12-30
WEST | December | OIC Donald Moses. Roc called at 21:31. Chlorine system 2 failure. Post injection total combined reached 3.00 mg/l before chemical system interlocked. Water is being directed into reservoir. No adverse water directed towards users. Acknowledged and cleared alarms. Sudden changes to the inlet flow due to power outages at bvps may have caused dosing spike. Chemical system began dosing again by 21:38. Sani pump faulted earlier in the night but will not need to be reset until tomorrow. Notified roc. No other issues remain. | East Vaughan Teston Pumping Station | 2025-12-28
WEST | December | -on site for station check -completed sanitary flush -took readings in PWQ: all ok -verified analyzer 11:45 -analyzer free: 0.07mg/l grab: 0.04mg/l -analyzer total: 1.85mg/l grab: 1.85mg/l -topped up reagents -equipment all ok | East Vaughan Teston Pumping Station | 2025-12-18
WEST | December | On site for the following VNPSCD, Ammonia Feed and Storage Inspection, East Vaughan Disinfection Building (1M) VNPSCD, Chlorine Scrubber Inspection, East Vaughan Disinfection Building (1M) VNPSCD, Chlorine Analyzer Maintenance, East Vaughan Disinfection Building (1M) VNPS, Chlorine Analyzer Maintenance, East Vaughan Pumping Station (1M) VNPS, Standby Power Generator Test Run and Run Hours log, East Vaughan Pumping Station (1M) Start hours 233.1 stop hours 234.6hrs Start fuel 1848/6834L stop fuel 1986/6531L VNPS, Process Mechanical Air valve flush and inspection - PD7, East Vaughan Pumping Station (1M) VNPS, Process Mechanical Air valve flush and inspection - PD8, East Vaughan Pumping Station (1M) VNPS, PD7/PD8 VFD Air Filter Change, East Vaughan Pumping Station (3M) VNPS, Process Mechanical Lubrication - PD7, East Vaughan Pumping Station (6M) - maintenance greased pumps on 8/12/25 please see elog VNPSCD, Chemical System Inspection - Chlorine, East Vaughan Disinfection Building (1M) Pd7 p1 keeps faulting on uncommanded stop. Watched pump start up unsure of the issue. | East Vaughan Teston Pumping Station | 2025-12-17
WEST | December | On site for station check Site offline all ok | Holland Landing East Elevated Tank | 2025-12-15
WEST | December | Onsite to complete station check Site remains offline. Equipment okay. | Holland Landing East Elevated Tank | 2025-12-01
WEST | December | Onsite to complete station check Site remains offline. Equipment okay. | Holland Landing East Elevated Tank | 2025-12-16
WEST | December | W11441962- Gasoline portable generator test generator put pack into tower after lowering oil level and installing new spark plug. Tested passed and in working condition. W11526315- year end chemical inventory count. values entered in teams folder | Holland Landing East Elevated Tank | 2025-12-23
WEST | December | Onsite to complete station check Site remains offline. Equipment okay. | Holland Landing East Elevated Tank | 2025-12-24
WEST | December | W11440984- JHSC health and safety workorder complete. | Holland Landing East Elevated Tank | 2025-12-17
WEST | December | Onsite to complete station check Site remains offline. Equipment okay. | Holland Landing East Elevated Tank | 2025-12-29
WEST | December | -on site to complete station check -checked equipment -reviewed trends -fire pump running -pump #1 hours = 35421.6 -pump #2 hours = 7730.6 -pump #3 hours = 7307.5 -pump #4 hours = 2220.7 09:18 - collected grab sample: Free chlorine = 0.01 mg/L Total chlorine = 1.98 mg/L -recorded readings in PWQ sheet -no issues found | Holland Landing Sherwood Pumping Station | 2025-12-15
WEST | December | Onsite for scheduled PM work orders Informed ROC about the works being done. W11441417- Low temp Alarm test- completed. W11441962- Gasoline portable generator test Generator didn't start up, took it out of site for maintenance. will use HLETYS generator in case of emergency. informed Team lead/ on call operator. | Holland Landing East Elevated Tank | 2025-12-18
WEST | December | On site for station check. Check trends: All okay. 12:20-Took grab Free: 0.05 mg/L Total: 2.07 mg/L Entered values in PWQ sheet Equipment okay | Holland Landing Sherwood Pumping Station | 2025-12-12
WEST | December | ON site for the following Scheduled PM workorders. Informed ROC about the works being done. W11456956 HLPSYS, JHSC Health and Safety Inspection, W11457173 HLPSYS, Pump 2 Valve, Exercise W11457289 HLPSYS, Low Temperature Alarm, Test W11457506 HLPSYS, Pump 1 Valve, Exercise W11457552 HLPSYS, Pump 3 Valve, Exercise W11457570 HLPSYS, Pump 4 Valve, Exercise W11456466 HLPSYS, Diesel Generator Test Run Pre check Battery okay- 13 V Coolant- Okay Oil - Okay Before Start Start time- 10:23 Run time- 1427.6 hr Fuel level-689L/84.9cm Pumps 1,2,3 running auto according to duty. After Stop Stop time- 11:23 Run time- 1428.7 hr Fuel level-683L/84.2 cm | Holland Landing Sherwood Pumping Station | 2025-12-11
WEST | December | On site for station check. Check trends: All okay. 10:15-Took grab Free: 0.03 mg/L Total: 2.05 mg/L Entered values in PWQ sheet Equipment okay | Holland Landing Sherwood Pumping Station | 2025-12-05
WEST | December | On site for station check. Check trends: All okay. 13:56-Took grab Free: 0.04 mg/L Total: 1.45 mg/L Entered values in PWQ sheet Equipment okay | Holland Landing Sherwood Pumping Station | 2025-12-08
WEST | December | On site for station check. Check trends: All okay. 13:33-Took grab Free: 0.02 mg/L Total: 2.07 mg/L Entered values in PWQ sheet Equipment okay | Holland Landing Sherwood Pumping Station | 2025-12-01
WEST | December | On site for station check. Check trends: All okay. 12:44-Took grab Free: 0.03 mg/L Total: 1.93 mg/L Entered values in PWQ sheet Equipment okay | Holland Landing Sherwood Pumping Station | 2025-12-22
WEST | December | W11526315- Year end chemical inventory count. entered values in teams folder. | Holland Landing Sherwood Pumping Station | 2025-12-23
WEST | December | On site for station check and to investigate Fire Pump failed to start Alarm Informed ROC about the work being done. Opened the discharge drain valve and directed the flow with Dechlorination pucks to the facility Out fall for 5 minutes. Discharge Pressure dropped and fire pumps started and let it run for another 5 minutes. no issues found with pump. Closed the discharge drain valve. Fire pump sopped and returned to Auto Standby. Check trends-All Good. 09:50-Took Grabs Free Cl2 Grab- 0.06 mg/L Total Cl2 Grab- 1.78 mg/L Entered values in PWQ sheet. Equipment okay. | Holland Landing Sherwood Pumping Station | 2025-12-19
WEST | December | On site for station check. Check trends: All okay. 14:10-Took grab Free: 0.03 mg/L Total: 1.53 mg/L Entered values in PWQ sheet Equipment okay | Holland Landing Sherwood Pumping Station | 2025-12-31
WEST | December | on site for station check and weekly bacti samples W11438795 and operational samples. The flow control valve keeps pounding, which makes the entire potable water line pounding too. Adjusted the needle valve to make it stable. also adjusted flow control valve pilot to set the flow from 22 l/s to 20.5 l/s well running Verified Analyzers 12:18- Influent Free Grab: 2.82mg/L, Analyzer: 2.92mg/L 12:30- Effluent Free Grab: 2.70mg/L(2.68,2.70,2.72), Analyzer: 2.48mg/L Adjusted analyzer up to 2.60 mg/L 10:40- Treated Free Grab: 0.15mg/L, Analyzer: 0.18mg/L 10:40- Treated Total Grab: 3.48mg/L Analyzer: 3.41mg/L Collected Samples Reagents all good Changed Chlorine: ammonia ratio from 4.1 to 4.6 based on SL1000 readings Changed Cl2 cylinders with S. Baidy entered values in PWQ sheet. equipment okay. | Holland Landing Well No. 1 | 2025-12-10
WEST | December | On site to fix the Raw water Sample tap leak. Put well manual off. Replaced pressure gauge and the fittings attached to the sample tap. All replaced parts torched and then disinfected with Hypo. start well manually and tested for leak. test passed. Put well back to auto. | Holland Landing Well No. 1 | 2025-12-11
WEST | December | -on site to complete station check -well running in manual -cl2 booster pump # 1 running at 155 psi -chlorinator # 1 26% open dosing 32 ppd, vac = -80 mbar, DF = 106% -silicate pump # 2 running at 34%, 18.7 rpm -ammonia pump # 1 running at 38%, 85 psi, 72 strokes/min -checked equipment -reviewed trends -CL17 reagents ok -verified chlorine analyzers: 10:56 - Treated water analyzers: FCL = 0.17 mg/L TCL = 3.34 mg/L 10:56 - Treated water grabs: FCL = 0.20 mg/L TCL = 3.06/3.06/3.14 mg/L MCL = 2.72 mg/L TNH3 = 0.57 mg/L FNH3 = 0.04 mg/L 11:12 - adjusted treated water TCL analyzer to 3.09 mg/L based on average of 3 grabs 11:18 - Influent FCL Analyzer = 3.05 mg/L 11:18 - Influent grab: Free chlorine = 2.96 mg/L 11:21 - Effluent FCL Analyzer = 2.75 mg/L 11:21 - Effluent grab: Free chlorine = 2.70 mg/L -recorded readings in PWQ sheet -no other issues found | Holland Landing Well No. 1 | 2025-12-15
WEST | December | on site for station check. check trends: all okay Started well manually Verified Analyzers 10:48- Influent Free Grab: 3.04mg/L, Analyzer: 3.10mg/L 10:54- Effluent Free Grab: 2.70mg/L, Analyzer: 2.71mg/L 10:40- Treated Free Grab: 0.19mg/L, Analyzer: 0.18mg/L 10:40- Treated Total Grab: 3.30mg/L Analyzer: 3.38mg/L Reagents all good Treated water Free ammonia reading when ammonia pump 2 is running seemed higher on 2 grabs (0.28 & 0.14). Ammonia pump 1 reads 0.02 mg/L. Put pump 1 in Duty and Duty auto rotation Disabled. Will troubleshoot pump 2 later. Raw water flow drifted from 20.5L/s to 21.5 L/s. Adjusted the piloting of Flow control valve to set the flow to 20.4 L/s entered values in PWQ sheet. equipment okay. | Holland Landing Well No. 1 | 2025-12-12
WEST | December | Dropped off silicate. Day tanks 315 to 669 L total. | Holland Landing Well No. 1 | 2025-12-09
WEST | December | On site for Scheduled PM work orders Informed ROC about the works being done Completed the following workorders W11422376 HLW1, JHSC Health and Safety Inspection W11421590 HLW1, Flow Control Valve, Test W11421705 HLW1, Chlorine Scrubber, Check W11421852 HLW1, Chlorine Gas Detector, Test W11421985 HLW1, Chlorine Analyzer, Maintenance 14:15-Treated Free Grab- 0.07mg/L, Analyzer -0.18 mg/L 14:15-Treated Total Grab- 3.40 mg/L, Analyzer -3.46 mg/L 14:20-Influent Free Grab- 3.10 mg/L, Analyzer -3.00 mg/L 14:18-effluent Free Grab- 2.58 mg/L, Analyzer -2.66 mg/L W11423372 HLW1, Turbidity Analyzer TU5300, Maintenance and Calibration W11423823 HLW1, Chemical System Inspection - Chlorine W11424329 HLW1, Chemical System Inspection - Ammonia Drawdown value matched maxflow set point W11423913 HLW1, Chemical System Inspection - Silicate Drawdown value matched maxflow set point W11458134 HLW1, Chemical System Line and Injection Point Flush - Silica W11423955 HLW1, Cl2 Emergency Repair Kit Inspection | Holland Landing Well No. 1 | 2025-12-04
WEST | December | on site for station check. check trends: all okay Verified Analyzers 13:17- Influent Free Grab: 3.08mg/L, Analyzer: 2.98mg/L 13:15- Effluent Free Grab: 2.62mg/L, Analyzer: 2.54mg/L 12:50- Treated Free Grab: 0.10mg/L, Analyzer: 0.17mg/L 12:50- Treated Total Grab: 3.32mg/L Analyzer: 3.28mg/L Reagents all good Duty deactivated after grab samples are taken. entered values in PWQ sheet. equipment okay. | Holland Landing Well No. 1 | 2025-12-05
WEST | December | Onsite to investigate ammonia issues Sl1000 grab @1423 T nh3 0.47 F nh3 0.00 Mcl 2.46 @1445 T nh3 0.49 F nh3 0.00 Mcl 2.54 Ammonia ratio adjusted Well duty was deactivated remotely Restarted well in manual Adjusted flow to approximately 20.4 L/s Sl1000 grabs @1521 T nh3 0.89 F nh3 0.29 Mcl 2.79 @1532 T nh3 0.84 F nh3 0.28 Mcl 2.81 | Holland Landing Well No. 1 | 2025-12-08
WEST | December | On site for station check and weekly Bacti Samples W11419301 Check trends: All okay Well running Verified Analyzers 10:50-Treated Free Grab- 0.07mg/L, Analyzer -0.17 mg/L 10:50-Treated Total Grab- 3.20 mg/L, Analyzer -3.17 mg/L Samples Taken after Cleaned the Raw water sample tap with 12% Sodium Hypochlorite. 11:15-Influent Free Grab- 3.00 mg/L, Analyzer -3.12 mg/L 11:13-effluent Free Grab- 2.50 mg/L, Analyzer -2.47 mg/L Reagents all okay entered values in pwq sheet. Equipment okay | Holland Landing Well No. 1 | 2025-12-03
WEST | December | on site for station check. check trends: all okay Duty activated for Operational monitoring. Topped up Ammonia tank 1- 17.45cm/81cm Verified Analyzers 12:30- Influent Free Grab: 2.98mg/L, Analyzer: 2.92mg/L 12:27- Effluent Free Grab: 2.60mg/L, Analyzer: 2.52mg/L 12:20- Treated Free Grab: 0.20mg/L, Analyzer: 0.17mg/L 12:20- Treated Total Grab: 3.24mg/L Analyzer: 3.30mg/L Replaced influent free analyzer Reagent. Duty deactivated after grab samples are taken. entered values in PWQ sheet. equipment okay. | Holland Landing Well No. 1 | 2025-12-01
WEST | December | on site for station check. check trends: all okay Activated Duty with both sharon vavlves manual off. Verified Analyzers 10:43- Influent Free Grab: 3.00mg/L, Analyzer: 3.05mg/L 10:50- Effluent Free Grab: 2.56mg/L, Analyzer: 2.48mg/L 10:40- Treated Free Grab: 0.14mg/L, Analyzer: 0.18mg/L 10:40- Treated Total Grab: 3.37mg/L Analyzer: 3.40mg/L Treated Total and Free Reagents changed Topped up Ammonia tnk 2 - 15.64cm/79.64 cm Adjusted flow contol valve to bring down the flow from 24.7 L/s to 21.1 L/s to meet proper mixing. Changed Chlorine ammonia set point from 4.10 to 5 . sharon valve put back to Auto. entered values in PWQ sheet. equipment okay. | Holland Landing Well No. 1 | 2025-12-08
WEST | December | On site to troubleshoot the flow control valve flow spike during startup with L. Ferguson. 13:27- Started the well. Flow spiked again and was putting out 27 L/s till 13:30. adjusted the flow control valve flow to 22 L/s and stut the well off at 14:00 14:05- Started the well. Flow again spiked to 27 l/s. Shut off well at 14:06. Took out pilot valve for repair. 14:37- relieved by T. Hudson | Holland Landing Well No. 1 | 2025-12-24
WEST | December | Onsite to continue troubleshooting ammonia Sl1000 grab @0844 T nh3 0.58 F nh3 0.04 Mcl 2.74 @0859 T nh3 0.63 F nh3 0.10 Mcl 2.66 | Holland Landing Well No. 1 | 2025-12-09
WEST | December | on site for station check and weekly bacti samples W11483632 Well manual on. Check Trends, All okay Verified Analyzers 13:25- Influent Free Grab: 3.10mg/L(avg-3.15,3.05,3.10), Analyzer: 2.76mg/L Adjusted analyzer up to 3.00 mg/L 13:30- Effluent Free Grab: 2.60mg/L(avg-2.61,2.62,2.58) , Analyzer: 2.37mg/L Adjusted analyzer up to 2.60 mg/L 13:45- Treated Free Grab: 0.09mg/L, Analyzer: 0.13mg/L 13:45- Treated Total Grab: 3.05 mg/L(avg-3.00,3.08,3.10) Analyzer: 2.76mg/L Adjusted analyzer up to 2.95 mg/L Collected Samples 13:35-SL1000 Mono- 2.43 mg/l Free NH3- 0.12 Total NH3-0.60 Reagents all good entered values in PWQ sheet. Put well back to auto equipment okay. | Holland Landing Well No. 1 | 2025-12-29
WEST | December | on site for station check. check trends: all okay Duty active, well running manually. Verified Analyzers 13:20- Influent Free Grab: 2.94 mg/L, Analyzer: 3.02 mg/L 13:26- Effluent Free Grab: 2.80mg/L, Analyzer: 2.71mg/L 13:15- Treated Free Grab: 0.10mg/L, Analyzer: 0.18mg/L 13:15- Treated Total Grab: 3.20mg/L Analyzer: 3.13mg/L Reagents all good 13:15- SL1000 Free ammonia grab - 0.37 mg/L 13:25- SL1000 Free ammonia grab - 0.40 mg/L Noticed Ammonia tanks just switched from tank 2 to tank 1 Filled Ammonia tank 2 - 15.58cm/75.5cm Switched the valve duty to Tank 2. 13:50- SL1000 Free ammonia grab - 0.28 mg/L Changed Chlorine:ammonia ratio from 4.6 to 5.1 14:25- SL1000 Free ammonia grab - 0.27 mg/L Switched the valve duty to Tank 1. 14:35- SL1000 Free ammonia grab - 0.22 mg/L chlorine dose changed to manual dosing, Chjanged chlorine:Ammonia ratio from 5.1 to 5.9 15:00-SL1000 Free ammonia grab - 0.08 mg/L total ammonia- 0.61 mg/l mono- 2.70 mg/l Analyzers, system pressure, flow, chemical pump feeds all appear to be normal and consistent. Will troubleshoot further to determine what the cause is. entered values in PWQ sheet. equipment okay. | Holland Landing Well No. 1 | 2025-12-19
WEST | December | Flow valve going high on start up Adjusted pilot sitting at 22 l/s , well keeps going to 27 l/s Rebuild pilot and test still not working Installed new body and rebuilt rubber kit tested and set to 23.5 l/s. Running well working properly | Holland Landing Well No. 1 | 2025-12-24
WEST | December | -on site to troubleshoot flow control valve -well exceeded PTTW while troubleshooting -well interlocked at 13:10 due to low influent - backflushed dechlorinate -tested flow control at 16:26 - set flow to 23l/s -began backflushin again at 16:40 until 17:40 -confirmed backflush with influent total grab at 17:40 1.56mg-l - chloriminated water and man/started well -locked out of SCADA on call network assisted -CT achieved -cleaned NTU analyzer -salted sidewalk/road after backflushing -complete additional ammonia lab -ammonia low set pump 1 max flow 90 - 85min/ml -mono - 2.23 - effluent 2.37 -fnh - 0mg/l -tnh- 0.43mg/l | Holland Landing Well No. 1 | 2025-12-24
WEST | December | on site for station check and weekly bacti samples W11470168 Activated duty with flow control valve manual off. Topped up silicate tank- 51.76cm/230.96L;48.85cm/216.81L to 86.6cm/400L;85.3cm/394L Verified Analyzers 10:52- Influent Free Grab: 3.08mg/L, Analyzer: 3.02mg/L 10:45:55- Effluent Free Grab: 2.80mg/L, Analyzer: 2.75 mg/L 10:30- Treated Free Grab: 0.11mg/L, Analyzer: 0.20mg/L Adjusted treated free analyzer down to 0.16 mg/L 10:30- Treated Total Grab: 3.12mg/L Analyzer: 3.05mg/L Collected Samples Reagents all good entered values in PWQ sheet. equipment okay. | Holland Landing Well No. 1 | 2025-12-22
WEST | December | - on site to change cylinders - 53.2kg - 121.2kg | Holland Landing Well No. 1 | 2025-12-30
WEST | December | -on site to troubleshoot inconsistent ammonia dosing issues -completed drawdowns on pumps: -pump #2 max flow = 95 ml/min, adjusted scada setpoint 110 to 95 ml/min -pump #1 max flow = 109 ml/min, scada setpoint = 105 ml/min -collected treated water grab with ammonia pump #1 running: MCL = 2.19 TNH3 = 0.41 FNH3 = 0.00 -collected grab with ammonia pump #2 running: MCL = 2.60 TNH3 = 0.57 FNH3 = 0.06 -scada currently targeting 0.70 mg/L ammonia dose, decreased ammonia pump #2 max flow setpoint to 85 ml/min to achieve target dose and increased chlorine - ammonia ratio from 3.9 to 4.5 to target 0.61 mg/L ammonia dose -collected grab: MCL = 2.60 TNH3 = 0.54 FNH3 = 0.02 -decreased ammonia pump #2 max flow setpoint 85 to 80 ml/min -collected grab: MCL = 2.69 TNH3 = 0.65 FNH3 = 0.12 -increased ammonia pump #2 max flow setpoint 80 to 83 ml/min -collected grab: MCL = 2.63 TNH3 = 0.72 FNH3 = 0.20 -tested chlorine booster pump / chlorinator #2 - no issues, enabled auto duty rotate -returned pump #2 max flow to 95 ml/min -collected grab: MCL = 2.35 TNH3 = 0.48 FNH3 = 0.02 -replaced degassing valve on ammonia pump #1 -collected grab with ammonia pump #1 running: MCL = 1.64 TNH3 = 0.31 FNH3 = 0.00 -suspect that inconsistent ammonia dosing issue may be due to poor hydraulic mixing after well flow lowered on December 8th. Returned well flow to 24.3 l/s -collected grab with ammonia pump #1 running: MCL = 1.62 TNH3 = 0.32 FNH3 = 0.00 -collected grab with ammonia pump 2 running: MCL = 2.34 TNH3 = 0.49 FNH3 = 0.03 -reduced chlorine ammonia ratio 4.5 to 4.3 -reduced ammonia pump #1 max flow 105 to 95 ml/min -collected grab with ammonia pump #1 running: MCL = 2.55 TNH3 = 0.56 FNH3 = 0.06 -collected grab with ammonia pump 2 running: MCL = 2.61 TNH3 = 0.68 FNH3 = 0.17 -increased ammonia pump #2 max flow 95 to 102 ml/min -collected grab with ammonia pump 2 running: MCL = 2.45 TNH3 = 0.51 FNH3 = 0.03 -will continue to monitor ammonia dosages | Holland Landing Well No. 1 | 2025-12-23
WEST | December | -on site to fix leak process water line fitting -well man/off -disinfected replacement parts and repaired -pressure tested - all ok -started well at 09:50 to troubleshoot flow control valve -flow exceeded PTTW at 09:50 due to pilot tested/maintenance on flow control valve -adjust flow control to 20.4l/s -changed cylinder 64 - 132kg | Holland Landing Well No. 1 | 2025-12-17
WEST | December | -man/stopped well to monitor residual after running at 20.4l/s -treated total dropped normally -placed well back to auto to monitor start up flow -set pump 1 max flow 91 - 90ml/min and pump 2 102- 100ml/min -flow spiked over 27l/s - man/stopped well - min attend | Holland Landing Well No. 1 | 2025-12-24
WEST | December | on site for station check and weekly bacti samples W11454895 well running in auto Verified Analyzers 12:00- Influent Free Grab: 2.92mg/L, Analyzer: 3.02mg/L 11:55- Effluent Free Grab: 2.82mg/L, Analyzer: 2.75 mg/L 11:45- Treated Free Grab: 0.10mg/L, Analyzer: 0.18mg/L 11:45- Treated Total Grab: 3.00mg/L Analyzer: 3.03mg/L Collected Samples Reagents all good entered values in PWQ sheet. equipment okay. | Holland Landing Well No. 1 | 2025-12-16
WEST | December | on site for station check. check trends 08:45-Duty Activated. Well started at 08:49 and was putting out 27L/s till 10:05 and then went down to 24.5L/s. Verified Analyzers 10:00- Influent Free Grab: 3.10mg/L, Analyzer: 3.04mg/L 09:55- Effluent Free Grab: 2.60mg/L, Analyzer: 2.57mg/L 09:35- Treated Free Grab: 0.13mg/L, Analyzer: 0.14mg/L 09:35- Treated Total Grab: 2.90 mg/L Analyzer: 2.87mg/L Replaced effluent free Analyzer reagents SL1000 Grabs -09:45 Mono-2.47 mg/L Free NH3- 0.00 mg/L Total NH3- 0.49 mg/L Adjusted Ammonia pump max flow from 95 mL/min to 91 mL/min SL1000 Grabs -09:45 Mono-2.53 mg/L Free NH3- 0.03 mg/L Total NH3- 0.53 mg/L Investigated Well 1 flow hihi on start up. Put well 1 manual off and restarted well at 10:26. The flow stayed around 27L/s till 10:30 and then went down to 24.5 L/s. Seems like Flow control valve have some issues. Adjusted the flow set point in flow control valve manually from 24.3 L/s to 20.5 L/s. Will troubleshoot the flow control valve later. entered values in PWQ sheet. equipment okay. | Holland Landing Well No. 1 | 2025-12-24
WEST | December | On site for station check Residuals Treated Total Grab: 1.23mg/L Analyzer: 1.30mg/L Treated Free Grab: 0.05mg/L, Analyzer: 0.03mg/L Site offline Changed out treated total reagents No issues on site | Holland Landing Well No. 2 | 2025-12-15
WEST | December | on site for station check. check trends all okay Site offline for rehab Verified Analyzers 09:55- Treated Free Grab: 0.09mg/L, Analyzer: 0.04mg/L 09:55- Treated Total Grab: 2.08mg/L, Analyzer: 2.05mg/L 10:00- Effluent Free Grab: 0.03mg/L Analyzer: 0.06mg/L Reagent All okay. Sharon Valve Grab Total Cl2: 1.80 mg/L entered values in pwq sheet. equipment okay. | Holland Landing Well No. 2 | 2025-12-12
WEST | December | on site for station check. check trends all okay Site offline for rehab Changed the ammonia pump 1& 2 max flow setpoint back to 95 mL/min & 93 mL/min from 115 mL/min and 115 mL/min as directed by C. Warnica Verified Analyzers 11:30- Treated Free Grab: 0.02mg/L, Analyzer: 0.04mg/L 11:30- Treated Total Grab: 2.10 mg/L Analyzer: 2.17 mg/L 11:35- Effluent Free Grab: 0.10 mg/L, Analyzer: 0.05 mg/L Changed effluent free Reagents. entered values in pwq sheet. equipment okay. | Holland Landing Well No. 2 | 2025-12-10
WEST | December | on site for station check. check trends all okay Site offline for rehab Verified Analyzers 12:50- Treated Free Grab: 0.03mg/L, Analyzer: 0.04mg/L 12:50- Treated Total Grab: 1.60mg/L Analyzer: 1.64mg/L 12:45- Effluent Free Grab: 0.05mg/L, Analyzer: 0.07mg/L Reagent All okay. Sharon Valve grab Total Chlorine 1.74mg/L entered values in pwq sheet. equipment okay. | Holland Landing Well No. 2 | 2025-12-03
WEST | December | On site for scheduled PM work orders given below Informed ROC about the works being done before starting. W11434384 HLW2, JHSC Health and Safety Inspection W11432947 HLW2, Chlorine Gas Detector, Test W11433125 HLW2, Chlorine Analyzer Maintenance 14:40- Verified analyzers Treated Free Grab- 0.04mg/L, Analyzer -0.05 mg/L Treated Total Grab- 1.95 mg/L, Analyzer -1.90 mg/L Effluent Free Grab- 0.09 mg/L, Analyzer -0.06 mg/L Influent free analyzer out of service; maintenance not done. W11432692 HLW2, Chlorine Scrubber, Check, W11435515 HLW2, Chemical System Inspection - Ammonia Changed Ammonia pump1 & pump 2 max flow setpoint from 95 mL/min,93 mL/min to 115 mL/min,115 mL/min W11434302 HLW2, Low/High Temperature Alarm, Test W11434462 HLW2, Turbidimeter, Maintenance W11452106 HLW2, Holland Landing Well 2 - HLW2, Dechlorination Puck Dispenser Inspection and cleaning | Holland Landing Well No. 2 | 2025-12-09
WEST | December | on site for station check. check trends all okay Site offline for rehab Verified Analyzers 10:50- Treated Free Grab: 0.02mg/L, Analyzer: 0.05mg/L 10:50- Treated Total Grab: 1.83mg/L Analyzer: 1.81mg/L 10:54- Effluent Free Grab: 0.09mg/L, Analyzer: 0.08mg/L Reagent All okay. Sharon Valve grab Total Chlorine 1.86 mg/L entered values in pwq sheet. equipment okay. | Holland Landing Well No. 2 | 2025-12-01
WEST | December | on site for station check. check trends all okay Site offline for rehab Verified Analyzers 12:10- Treated Free Grab: 0.04mg/L, Analyzer: 0.06mg/L 12:05- Treated Total Grab: 1.49mg/L, Analyzer: 1.56mg/L 12:05- Effluent Free Grab: 0.06mg/L Analyzer: 0.04mg/L Reagent All okay. entered values in pwq sheet. equipment okay. | Holland Landing Well No. 2 | 2025-12-08
WEST | December | on site for station check. check trends all okay Site offline for rehab Verified Analyzers 13:40- Treated Free Grab: 0.02mg/L, Analyzer: 0.04mg/L 13:40- Treated Total Grab: 2.09mg/L Analyzer: 2.05mg/L 13:50- Effluent Free Grab: 0.09mg/L, Analyzer: 0.09mg/L Reagent All okay. Sharon Valve grab Total Chlorine 2.11 mg/L entered values in pwq sheet. equipment okay. | Holland Landing Well No. 2 | 2025-12-05
WEST | December | Changed Treated free analyzer reagents | Holland Landing Well No. 2 | 2025-12-19
WEST | December | on site for station check. check trends all okay Site offline for rehab Verified Analyzers 03:25- Treated Free Grab: 0.04mg/L, Analyzer: 0.03mg/L 03:25- Treated Total Grab: 2.20mg/L, Analyzer: 2.22mg/L 13:30- Effluent Free Grab: 0.03mg/L Analyzer: 0.04mg/L Reagent All okay. Sharon Valve Grab Total Cl2: 2.04 mg/L entered values in pwq sheet. equipment okay. | Holland Landing Well No. 2 | 2025-12-16
WEST | December | on site for station check. check trends all okay Site offline for rehab Verified Analyzers 14:30- Treated Free Grab: 0.02mg/L, Analyzer: 0.04mg/L 14:30- Treated Total Grab: 1.96mg/L, Analyzer: 1.98mg/L 14:32- Effluent Free Grab: 0.04mg/L Analyzer: 0.05mg/L Reagent All okay. entered values in pwq sheet. equipment okay. | Holland Landing Well No. 2 | 2025-12-29
WEST | December | on site for station check. check trends all okay Site offline for rehab Topped up Silicate tank-67.15cm/379.75L to 71.2/402L Verified Analyzers 11:45- Treated Free Grab: 0.03mg/L, Analyzer: 0.03mg/L 11:45- Treated Total Grab: 1.00mg/L, Analyzer: 1.02mg/L 11:50- Effluent Free Grab: 0.02mg/L Analyzer: 0.03mg/L Reagent All okay. Sharon Valve Grab Total Cl2: 1.01 mg/L entered values in pwq sheet. equipment okay. | Holland Landing Well No. 2 | 2025-12-22
WEST | December | W11526315- Year end chemical inventory count. entered values in teams folder. | Holland Landing Well No. 2 | 2025-12-23
WEST | December | on site for station check. check trends all okay Site offline for rehab Verified Analyzers 12:00- Treated Free Grab: 0.03mg/L, Analyzer: 0.04mg/L 12:00- Treated Total Grab: 1.85mg/L, Analyzer: 1.91mg/L 12:35- Effluent Free Grab: 0.05mg/L Analyzer: 0.04mg/L Reagent All okay. entered values in pwq sheet. equipment okay. | Holland Landing Well No. 2 | 2025-12-24
WEST | December | On site for station check and weekly Bacti samples W11438795. Check trends:all okay. Tower filling (65%) Verified Analyzers 14:00-Pre injection FCL- Grab- 0.02 mg/L; Analyzer - 0.04 mg/L TCL- Grab-0.95 mg/L; Analyzer - 0.87 mg/L 14:15-Post injection FCL- Grab- 0.02 mg/L; Analyzer - 0.07 mg/L TCL- Grab-3.52 mg/L; Analyzer - 3.58 mg/L Reagents all good. Deactivated duty, tower draining 14:40- Samples Collected FCL- Grab- 0.06 mg/L TCL- Grab-2.16 mg/L Duty activated. entered values in PWQ sheet | Holland Landing West Elevated Tank | 2025-12-10
WEST | December | On site for station check. Check trends: all okay. Running Well 1 and sharon Valve manually. Tower filling (80%) W11466160- Siemens Depolox 5/Micro 2000, Chlorine Analyzer, Maintenance Verified Analyzers 13:00-Pre injection FCL- Grab- 0.04 mg/L; Analyzer - 0.5 mg/L TCL- Grab-1.79 mg/L; Analyzer - 1.78 mg/L 13:15-Post injection FCL- Grab- 0.03 mg/L; Analyzer - 0.09 mg/L TCL- Grab-3.10 mg/L; Analyzer - 3.05 mg/L Replaced post injection KI reagent. entered values in PWQ sheet Duty deactivated. Equipment okay. | Holland Landing West Elevated Tank | 2025-12-12
WEST | December | -On-site to complete station check -activated system duty for station check, tower = 76% -checked equipment -reviewed trends -depolox reagents ok -rechlor active, reform only -hypo pump #2 running at 13%, 27 strokes/min, 58 psi -verified chlorine analyzers: 09:35 - Grabs from tank: Free Chlorine = 0.05 mg/L Total Chlorine = 1.38 mg/L MCL = 0.29 mg/L TNH3 = 0.36 mg/L FNH3 = 0.31 mg/L NO2 = 0.004 mg/L temp = 10.0 C 09:50 -Pre injection Analyzer readings: Free Chlorine = 0.05 mg/L Total Chlorine = 2.00 mg/L 09:50-Pre injection Grabs: Free Chlorine = 0.06 mg/L Total Chlorine = 1.94 mg/L MCL = 0.37 mg/L TNH3 = 0.35 mg/L FNH3 = 0.28 mg/L 09:53 -Post injection Analyzer readings: Free Chlorine = 0.09 mg/L Total Chlorine = 3.03 mg/L 09:53 -Post injection Grabs: Free Chlorine = 0.08 mg/L Total Chlorine = 2.98 mg/L MCL = 1.48 mg/L TNH3 = 0.36 mg/L FNH3 = 0.07 mg/L -recorded readings in PWQ sheet -no issues found 10:15 - collected another post injection ammonia grab: MCL = 2.00 TNH3 = 0.42 FNH3 = 0.02 | Holland Landing West Elevated Tank | 2025-12-15
WEST | December | -on site to complete following work orders -sump pit inspection: all ok -manual valve exercise: all ok -sensing line heat trace- breaker tripper - reset and unit turned on -riser heat trace - tested all ok -cleaned injection point- all ok - tested -chlorine system inspection - cleaned chemical board and inspected for leaks - tightened fittings - no issue - tested both pumps after injection point all ok | Holland Landing West Elevated Tank | 2025-12-11
WEST | December | On site for station check and weekly Bacti samples W11419301. Check trends:all okay. Tower draining (53%) 08:45- Samples Collected FCL- Grab- 0.03 mg/L TCL- Grab-2.10 mg/L Activated Duty. Changed Flow control valve flow setpoint from 40l/s to 50l/s to fill the tower at 60l/s rate. Verified Analyzers 09:30-Pre injection FCL- Grab- 0.03 mg/L; Analyzer - 0.13 mg/L TCL- Grab-1.74 mg/L; Analyzer - 1.70 mg/L 09:40-Post injection FCL- Grab- 0.05 mg/L; Analyzer - 0.08 mg/L TCL- Grab-3.4 mg/L; Analyzer - 3.34 mg/L Reagents all good. Deactivated the duty. Put flow control valve flow set point back to 40 L/s. entered values in PWQ sheet Pre injection free analyzer electrolyte gel leaking into reservoir .CMU W11484255 created. | Holland Landing West Elevated Tank | 2025-12-03
WEST | December | Received Hypo- 23.3cm,108L/96.8cm,447L | Holland Landing West Elevated Tank | 2025-12-09
WEST | December | On site for station check. Topped up Hypo tank - 20.09 cm/43.92cm Check trends:all okay. Activated Duty. Tower filling (75%) Verified Analyzers 11:20-Pre injection FCL- Grab- 0.03 mg/L; Analyzer - 0.10 mg/L TCL- Grab-1.32 mg/L; Analyzer - 1.34 mg/L 11:40-Post injection FCL- Grab- 0.06 mg/L; Analyzer - 0.07 mg/L TCL- Grab-3.74 mg/L; Analyzer - 3.51 mg/L Reagents all good. entered values in PWQ sheet Equipment okay. | Holland Landing West Elevated Tank | 2025-12-05
WEST | December | On site for station check. Check trends: all okay. Activated Duty. Tower filling (72%) Verified Analyzers 14:15-Pre injection FCL- Grab- 0.05 mg/L; Analyzer - 0.4 mg/L TCL- Grab-1.41 mg/L; Analyzer - 1.43 mg/L 14:30-Post injection FCL- Grab- 0.04 mg/L; Analyzer - 0.07 mg/L TCL- Grab-3.38 mg/L; Analyzer - 3.28 mg/L Reagents all good. entered values in PWQ sheet Duty deactivated. Equipment okay. | Holland Landing West Elevated Tank | 2025-12-08
WEST | December | On site for station check. Check trends:all okay. Activated Duty. Changed Flow control valve flow setpoint from 40l/s to 50l/s to fill the tower at 60l/s rate. Tower filling (76%) Verified Analyzers 14:00-Pre injection FCL- Grab- 0.02 mg/L; Analyzer - 0.10 mg/L TCL- Grab-1.26 mg/L; Analyzer - 1.29 mg/L 14:10-Post injection FCL- Grab- 0.02 mg/L; Analyzer - 0.07 mg/L TCL- Grab-3.24 mg/L; Analyzer - 3.32 mg/L Reagents all good. Deactivated the duty. Put flow control valve flow set point back to 40 L/s. entered values in PWQ sheet Equipment okay. | Holland Landing West Elevated Tank | 2025-12-01
WEST | December | Attending site to replaced Pre-Free electrolyte reservoir due to leak (W11484255). Replaced reservoir and calibrated Free to 0.08mg/L, based on DPD grabs. ROC was notified before and after maintenance activity. Associated SCADA alarms were cleared. | Holland Landing West Elevated Tank | 2025-12-05
WEST | December | Duty active, well 1 and sharon valve in duty 1, but only sharon valve is feeding and well 1 is off in Auto mode. Notified team lead, PCS and ROC W11452290- Ammonia system inspection Pump 1 - max flow showed 100 mL/min after 3 draw down test changed max flow set point from 110 ml/min to 105 ml/min Pump 2- max flow matched max flow in scada. | Holland Landing West Elevated Tank | 2025-12-17
WEST | December | W11526486- Topped up ammonia Tank with 2 bags- 20.6 cm/81.16cm | Holland Landing West Elevated Tank | 2025-12-18
WEST | December | On site for station check and weekly Bacti samples W11483632. Check trends:all okay. Tower Draining (79%) 10:00- Samples Collected FCL- Grab- 0.07 mg/L TCL- Grab-2.56 mg/L Duty Activated. Flow control valve and well 1 in Duty 1. Verified Analyzers 10:45-Pre injection FCL- Grab- 0.04 mg/L; Analyzer - 0.05 mg/L TCL- Grab-2.02 mg/L; Analyzer - 2.10 mg/L 11:45-Post injection FCL- Grab- 0.04 mg/L; Analyzer - 0.09 mg/L TCL- Grab-2.90 mg/L; Analyzer - 2.88 mg/L Reagents all good. Deactivated duty, with well 1 manual on entered values in PWQ sheet Reset Breaker for heat tracer system Leak found in fitting that joints Hypo pump 2 discharge line to the chemical board, noticed broken compression fitting, replaced compression fitting, tested for leaks, leak fixed. equipment all okay. | Holland Landing West Elevated Tank | 2025-12-29
WEST | December | On site for station check and weekly Bacti samples W11454895. Check trends:all okay. Tower filling (75%) Responded to Post injection Combined CL2 high Alarm. Verified Analyzers 10:30-Pre injection FCL- Grab- 0.04 mg/L; Analyzer - 0.03 mg/L TCL- Grab-1.11 mg/L; Analyzer - 1.05 mg/L 10:15-Post injection FCL- Grab- 0.11 mg/L; Analyzer - 0.08 mg/L TCL- Grab-3.70 mg/L; Analyzer - 3.64 mg/L Reagents all good. Changed Target post combined Cl2 set point from 3.30 mg/L to 3.15 mg/L. Changed Inlet free Ammonia set point from 0.31 mg/L to 0.27 mg/L based on SL1000 readings. entered values in PWQ sheet. W11519817- CMU created for the Heat trace system keeps tripping. Deactivated Duty, Tower draining 86% 13:55- Collected samples Grab Free CL2- 0.03 mg/L Grab Total CL2-2.30 mg/L Equipment okay. | Holland Landing West Elevated Tank | 2025-12-16
WEST | December | On site for station check. Check trends: all okay. Activated Duty. Tower filling (50%) Verified Analyzers 13:45-Pre injection FCL- Grab- 0.02 mg/L; Analyzer - 0.0\4 mg/L TCL- Grab-1.53 mg/L; Analyzer - 1.56 mg/L 13:35-Post injection FCL- Grab- 0.03 mg/L; Analyzer - 0.09 mg/L TCL- Grab-3.10 mg/L; Analyzer - 3.07 mg/L Reagents all good. entered values in PWQ sheet Equipment okay. | Holland Landing West Elevated Tank | 2025-12-31
WEST | December | On site for station check. Heat Tracer breaker tripped Again. Flicked it back to On position and get it going. Check trends: all okay. Activated Duty. Tower filling (77%) Verified Analyzers 10:55-Pre injection FCL- Grab- 0.02 mg/L; Analyzer - 0.05 mg/L TCL- Grab-1.84 mg/L; Analyzer - 1.86 mg/L 11:10-Post injection FCL- Grab- 0.07 mg/L; Analyzer - 0.09 mg/L TCL- Grab-2.98 mg/L; Analyzer - 3.00 mg/L Reagents all good. entered values in PWQ sheet Equipment okay. | Holland Landing West Elevated Tank | 2025-12-19
WEST | December | On site for station check and weekly Bacti samples W11470168. Check trends:all okay. Duty Active. Flow control valve and well 1 in Duty 1. Tower filling (76%) Verified Analyzers 13:00-Pre injection FCL- Grab- 0.04 mg/L; Analyzer - 0.05 mg/L TCL- Grab-1.83 mg/L; Analyzer - 1.80 mg/L 13:30-Post injection FCL- Grab- 0.03 mg/L; Analyzer - 0.08 mg/L TCL- Grab-2.96 mg/L; Analyzer - 2.94 mg/L Reagents all good. Deactivated duty, tower draining 13:52- Samples Collected FCL- Grab- 0.02 mg/L TCL- Grab-1.87 mg/L Duty activated. entered values in PWQ sheet | Holland Landing West Elevated Tank | 2025-12-22
WEST | December | W11526315- Year end chemical inventory count. entered values in teams folder. W11529049- HLETYS_BLDS Sodium Hypochlorite Delivery Toped up hypo tank- 57.81cm/270L to 94.4 cm/436L | Holland Landing West Elevated Tank | 2025-12-23
WEST | December | On site to complete 1yr electrical PM. All in good condition. | Holland Landing West Elevated Tank | 2025-12-31
WEST | December | Station Check (no issues found) Input data to PWQ Verified Depoloxs (mg/l) 14:35 PRE Free: Grab 0.06, A 0.02 Total: Grab 0.84, A 0.85 Mono: 0.20 FA: 0.31 TA: 0.35 14:45 POST Free: Grab 0.06, A 0.06 Total: Grab 3.00, A 2.93 Mono: 2.38 FA: 0.10 TA: 0.57 Topped up acetate for both Depolox | Holland Landing West Elevated Tank | 2025-12-24
WEST | December | On site to complete station check. Free Chlorine Grab: 0.05mg/L Total Chlorine Grab: 1.83mg/L No issues on site | Jefferson Pumping Station & Reservoir | 2025-12-12
WEST | December | Checked/troubleshoot heat trace system reported circuit breaker tripping. | Holland Landing West Elevated Tank | 2025-12-22
WEST | December | Pumping Station Check (no issues found) input data to PWQ 12:45 Grab Residuals (mg/l) Free: 0.02 Total: 1.80 | Jefferson Pumping Station & Reservoir | 2025-12-15
WEST | December | Vibration readings 1 3 4 | Jefferson Pumping Station & Reservoir | 2025-12-10
WEST | December | On site for station check and to collect bacti sample wo#11419287 Residuals East Cell cell:@ 12:20 Free: 0.05mg/L Total 2.10mg/L SL1000 readings Total Cl: 2.12mg/L Total NH3: 0.50mg/L Free NH3: 0.13mg/L NH2Cl: 1.87mg/L NO2:0.001mg/L No issues on site | Jefferson Pumping Station & Reservoir | 2025-12-10
WEST | December | On site for station check Maint on site (Tyler Smith) noticed pump 2 vibration and cavitation created work order W11497272 and placed pump in manual off Free Chlorine Grab: 0.05mg/L Total Chlorine Grab: 1.91mg/L No issues on site | Jefferson Pumping Station & Reservoir | 2025-12-08
WEST | December | On site for station check and to collect bacti sample wo#11419287 Residuals West Cell cell:@ 13:15 Free: 0.05mg/L Total 2.05mg/L SL1000 readings Total Cl: 2.06mg/L Total NH3: 0.48mg/L Free NH3: 0.13mg/L NH2Cl: 1.80mg/L NO2:0.000mg/L No issues on site | Jefferson Pumping Station & Reservoir | 2025-12-03
WEST | December | On site to complete station check. Free Chlorine Grab: 0.05mg/L Total Chlorine Grab: 1.84mg/L No issues on site | Jefferson Pumping Station & Reservoir | 2025-12-01
WEST | December | Onsite for station check Duty active Checked residuals mg/l @1455 Total grab 1.85 Free grab 0.04 | Jefferson Pumping Station & Reservoir | 2025-12-04
WEST | December | On site for the following JFRS, JHSC Health and Safety Inspection, Jefferson RES and BPS (1M) JFPS, Standby Power Generator Test Run and Run Hours log, Jefferson WPS (1M) Fuel start 6440L stop 6397L Hrs start 650hrs stop 6:51.5 Runtime 1.5hours JFRS, External Venting Screens Inspection, Jefferson RES (1M) JFPS, PRV Valve Inspection, Jefferson WPS (1Y) JFPS, Sump Pit System Inspection, Jefferson WPS (1M) JFPS, Manual Valves Exercise, Jefferson WPS (3M) JFPS, Actuated Valves Exercise & Inspection, Jefferson WPS (1M) JFPS, Pump & Motor Inspection, Jefferson WPS (1M) - P2 in manual off for cavitation work order created JFPS, Ventilation System Inspection, Jefferson WPS (1M) JFPS, Low Temperature Alarm Test, Jefferson WPS (1M) JFPS, Dehumidifier Inspection & Cleaning, Jefferson WPS (1M) JFRS, Sump Pit System Inspection, Jefferson RES (1M) JFRS, Ventilation System Inspection, Jefferson Valve House (1M) JFRS, Sump Pit System Inspection, Jefferson Valve House (1M) JFRS, Actuated Valve Exercise & Inspection, Jefferson, Valve House (3M) JFRS, Flood Alarm Test Jefferson Valve House (1M) JFRS, Manual Valves Exercise, Jefferson, Valve House (3M) JFRS, Dehumidifier Inspection & Cleaning, Jefferson, Valve House (1M) JFRS, Dehumidifier Inspection & Cleaning, Jefferson, RES (1M) JFPS, Hoist System Inspection, Jefferson WPS (3M) | Jefferson Pumping Station & Reservoir | 2025-12-09
WEST | December | Onsite for station check Checked residuals mg/l @1210 Total grab 1.72 Free grab 0.02 Duty came in switched from p3 to p2 to test | Jefferson Pumping Station & Reservoir | 2025-12-23
WEST | December | Vibration motor 2 and grease Had control start pump 2 Took vibration readings Put 10 shots of grease in motor outbound bearing put 20 shots in inbound bearing Greased pump 10 shouts outbound and 20 shots inbound took new vibration readings motor is green across the board pump still high need to pump out white grease | Jefferson Pumping Station & Reservoir | 2025-12-24
WEST | December | On site for station check and to collect bacti sample wo#11454881 Residuals West Cell cell:@ 13:10 Free: 0.05mg/L Total 1.70mg/L | Jefferson Pumping Station & Reservoir | 2025-12-16
WEST | December | -on site for station check and weekly bacti W11470054 -man/started pump 2 to exercise -took grab and sample from east cell 13:45 -free cl: 0.10mg/l -total cl:1.79mg/l -equipment all ok | Jefferson Pumping Station & Reservoir | 2025-12-22
WEST | December | Free Chlorine Grab: 0.04mg/L Total Chlorine Grab: 1.94mg/L No issues on site | Jefferson Pumping Station & Reservoir | 2025-12-30
WEST | December | -on site for station check -checked trends all ok -entered readings in PWQ: all ok -took chlorine grab 14:10: -free cl: 0.03mg/l -total cl: 1.71mg/l -equipment all ok | Jefferson Pumping Station & Reservoir | 2025-12-18
WEST | December | -on site to complete station checks -checked trends: all ok -entered readings in PWQ: all ok - took chlorine grab 13:40 -free cl: 0.05mg/l -total cl: 1.94mg/l -will run pump 2 for two hours | Jefferson Pumping Station & Reservoir | 2025-12-24
WEST | December | On site for station check and to collect bacti sample wo#11483618 East Cell Residuals East Cell cell:@ 13:30 Free: 0.03mg/L Total 1.90mg/L West Cell @ 13:35 Free 0.01 mg/l. Total 1.87 mg/l SL1000 readings Total NH3: 0.40mg/L Free NH3: 0.07mg/L NH2Cl: 1.67mg/L NO2:0.000mg/L No issues on site | Jefferson Pumping Station & Reservoir | 2025-12-29
WEST | December | Onsite for station check Duty not active Checked residuals mg/l @0935 Total grab 1.93 Free grab 0.03 | King City Dufferin Booster Pumping Station | 2025-12-12
WEST | December | -on site to do the motor swap on pump 2. We removed the motor and installed new one. We tested to confirm operation. Lee F grabbed vibration readings from the pump and motor at 1300 and placed motor back into manual off for the weekend. Dan Boate and myself swapped the temp sensor for the generator hvac and tested to confirm operation by running generator manually at 1400. Cleared alarms from our testing and called ROC to let them know we are done. Under direction of oic. | Jefferson Pumping Station & Reservoir | 2025-12-19
WEST | December | Onsite for station check Duty not active Checked residuals mg/l @1049 Total grab 1.77 Free grab 0.03 | King City Dufferin Booster Pumping Station | 2025-12-15
WEST | December | On site for the following KPSDS, JHSC Health and Safety Inspection, King City WPS (1M) KCPDS, Critical Air Valve Flush and Inspection, King City WPS (1M) | King City Dufferin Booster Pumping Station | 2025-12-11
WEST | December | On site for station check Grabs Free 0.05mg/L Total 1.76mg/L No other issues on site | King City Dufferin Booster Pumping Station | 2025-12-01
WEST | December | Onsite for station check Duty not active Checked residuals mg/L @1045 Total grab 1.97 Free grab 0.01 | King City Dufferin Booster Pumping Station | 2025-12-08
WEST | December | Station Check (no issues found) input data to PWQ Cl2 residual Free Grab: 0.06mg/l Total Grab: 1.83mg/l | King City Dufferin Booster Pumping Station | 2025-12-04
WEST | December | Onsite for station check Duty not active Checked residuals mg/l @0953 Total grab 1.76 Free grab 0.04 | King City Dufferin Booster Pumping Station | 2025-12-24
WEST | December | Onsite for station check Duty not active Checked residuals mg/l @1131 Total grab 2.00 Free grab 0.00 | King City Dufferin Booster Pumping Station | 2025-12-19
WEST | December | Onsite for station check Checked residuals mg/l @1507 Total grab 1.61 Free grab 0.05 | King City Dufferin Booster Pumping Station | 2025-12-22
WEST | December | On site for station check and to collect bacti sample wo# w11438533 Residuals@ 1320 colorimeter Analyzer Total 1.78mg/L Total Grab: 1.82mg/L Analyzer Free 0.03mg/L Free Grab: 0.05mg/L Operational Sampling (SL1000) Total Cl: 1.92mg/L Total NH3: 0.42mg/L Free NH3: 0.09mg/L NH2CL: 1.69mg/L NO2: 0.001mg/L Collected sample for in-house lab Reagents ok No issues on site | King City Dufferin Elevated Tank | 2025-12-10
WEST | December | On site for the following Health and Safety Inspection, King City Dufferin StET KCETDS, Manual Valve, Exercise, King City Dufferin St ET (2M) KCETDS, CL17 Chlorine Analyzer, Maintenance, King City Dufferin St ET (1M) KCETDS, Inlet/Outlet Heat Trace System, Inspection, King City Dufferin St ET (1M) KCETDS, Actuated Valve, Exercise & Inspection, King City Dufferin St ET (1M) KCETDS, Dehumidifier, Cleaning & Inspection, King City Dufferin St ET (1M) KCETDS, Ventilation System, Inspection, King City Dufferin St ET (1M) KCETDS, Low Temperature Alarm Test, King City Dufferin ST ET (1M) KCETDS, Altitude Valve, Inspection, King City Dufferin St ET (6M) | King City Dufferin Elevated Tank | 2025-12-11
WEST | December | Onsite for station check and to collect weekly micro samples W11419273 Tower draining Checked residuals mg/l @0933 Total analyzer 1.94 grab 1.96 Free analyzer 0.04 grab 0.04 Sl1000 Mcl grab 2.01 No2 grab 0.000 F nh3 0.07 T nh3 0.47 | King City Dufferin Elevated Tank | 2025-12-03
WEST | December | Restarted the Operator Interface Terminal due to Video Driver Updates. This is being done to fix a memory leak. | King City Dufferin Elevated Tank | 2025-12-16
WEST | December | On site responding to power failure - generator on route Collected bacti sample w11483604 @11:45 Grabs free 0.05mg/L total 1.54mg/L No power to analyzers Power restored as of 12:37hrs Total analyzer faulted - cleared fault on analyzer took grabs on analyzer at 12:45 grabs 1.58mg/L analyzer 1.60mg/L - all ok Changed anlyzer reagents | King City Dufferin Elevated Tank | 2025-12-29
WEST | December | Metering chamber flood alarm came in Sump pump was not running in auto Ran in manual to clear alarm Will make work order | King City Dufferin Elevated Tank | 2025-12-19
WEST | December | Onsite for station check and to collect weekly micro sample Tower draining Checked residuals mg/l @1450 Total analyzer 1.74 grab 1.72 Free analyzer 0.03 grab 0.03 Sl1000 Mcl grab 1.72 F nh3 grab 0.04 T nh3 grab 0.38 | King City Dufferin Elevated Tank | 2025-12-22
WEST | December | Restart IFIX (SCADA Software) in order to clear Historian Heartbeat alarm caused by startup/network failure. Verify alarm cleared, contacted ROC to confirm, verify trending all OK, | King City Dufferin Elevated Tank | 2025-12-29
WEST | December | Onsite for station check and to collect weekly micro sample W11454867 Tower draining Checked residuals mg/L @09:47 Total analyzer 1.82 grab 1.86 Free analyzer 0.03 grab 0.04 SL1000 Mcl grab 1.76 F nh3 grab 0.04 T nh3 grab 0.38 No2 grab 0.003 | King City Dufferin Elevated Tank | 2025-12-16
WEST | December | On site for station check and to collect bacti sample wo# w11438533 Residuals@ 13:50colorimeter Total Grab: 1.90mg/L Analyzer Total 1.83mg/L Free Grab: 0.05mg/L Analyzer Free 0.04mg/L Operational Sampling (SL1000) Total Cl: 1.92mg/L Total NH3: 0.42mg/L Free NH3: 0.08mg/L NH2CL: 1.74mg/L NO2: 0.000mg/L Reagents all okay Collected sample for in house lab No other issues on site | King City Fisher Elevated Tank | 2025-12-10
WEST | December | Work orders: #1146671 Lo temp. #11466124 & 11466615 heat trace #11466615 port. gen. #11466183 Hi/Lo level #11466095 valve insp. #11466274 jhs #11466534 Depolox 10:08 Free: Grab 0.03, A 0.04 mg/l Total: Grab 1.73, A 1.79 mg/l | King City Fisher Elevated Tank | 2025-12-11
WEST | December | Restarted the Operator Interface Terminal due to Video Driver Updates. This is being done to fix a memory leak. | King City Fisher Elevated Tank | 2025-12-16
WEST | December | Onsite for station check and to collect weekly micro samples W11419273 Tower draining Checked residuals mg/l @1047 Total analyzer 1.89 grab 1.87 Free analyzer 0.04 grab 0.04 Sl1000 Mcl grab 1.78 No2 grab 0.004 F nh3 grab 0.10 T nh3 grab 0.42 Changed KI solution | King City Fisher Elevated Tank | 2025-12-03
WEST | December | Details: On site for station check and to collect bacti sample wo# w1143604 Residuals@ 13:15colorimeter Total Grab: 1.58mg/L Analyzer Total 1.50mg/L Free Grab: 0.05mg/L Analyzer Free 0.03mg/L Reagents all ok Disconnected generator power site back on utility power | King City Fisher Elevated Tank | 2025-12-29
WEST | December | Onsite for station check and to collect weekly micro sample W11454867 Tower draining Checked residuals mg/L @0915 Total analyzer 2.01 grab 1.88 Free analyzer 0.03 grab 0.05 Adjusted total analyzer Sl1000 Mcl grab 1.88 F nh3 grab 0.02 T nh3 grab 0.39 No2 grab 0.002 | King City Fisher Elevated Tank | 2025-12-16
WEST | December | Onsite for station check and to collect weekly micro sample W11469932 Tower draining Checked residuals mg/l @1409 Total analyzer 1.61 grab 1.67 Free analyzer 0.03 grab 0.05 | King City Fisher Elevated Tank | 2025-12-22
WEST | December | -on site to connect tower to backup power -topped up generator - all ok | King City Fisher Elevated Tank | 2025-12-29
WEST | December | Onsite for station check and to collect weekly micro sample W11438669 Deactivated duty to get sample on down cycle Checked residuals mg/l @1239 Total grab 1.91 Free grab 0.07 Sl1000 Mcl grab 1.94 F nh3 grab 0.04 T nh3 grab 0.42 No2 grab 0.004 | Kleinburg Elevated Tank | 2025-12-10
WEST | December | Onsite for station check and to collect weekly micro sample W11419594 Deactivated duty to get sample on down cycle Checked residuals mg/L @1327 Total grab 2.15 Free grab 0.07 Sl1000 Mcl grab 2.01 No2 grab 0.004 F nh3 grab 0.10 T nh3 grab 0.50 | Kleinburg Elevated Tank | 2025-12-03
WEST | December | Onsite for station check and to collect weekly micro sample W11454984 Deactivated duty to get sample on down cycle Checked residuals mg/l @1353 Total grab 2.15 Free grab 0.02 Sl1000 Mcl grab 1.98 T nh3 grab 0.43 F nh3 grab 0.04 No2 grab 0.004 | Kleinburg Elevated Tank | 2025-12-16
WEST | December | On site for station check and to collect bacti sample wo# w11483730 Residuals@ 09:30 colorimeter Total Grab: 2.19mg/L Free Grab: 0.07mg/L Operational Sampling (SL1000) Total Cl: 2.21mg/L Total NH3: 0.49mg/L Free NH3: 0.10mg/L NH2CL: 1.98mg/L No issues on site | Kleinburg Elevated Tank | 2025-12-29
WEST | December | Onsite for station and to collect weekly micro sample w11470068 Checked residuals mg/l @1318 Total grab 2.05 Free grab 0.05 Sl1000 Mcl grab 2.05 F nh3 grab 0.05 T nh3 grab 0.45 | Kleinburg Elevated Tank | 2025-12-22
WEST | December | Onsite for station check Duty not active Checked residuals mg/l @1343 Total analyzer 2.15 grab 2.08 Free analyzer 0.03 grab 0.06 Reagents ok | Kleinburg HWY 27 Booster Pumping Station | 2025-12-12
WEST | December | Onsite for station check Duty active Checked residuals mg/l @1239 Total analyzer 2.20 grab 2.18 Free analyzer 0.03 grab 0.06 Reagents ok | Kleinburg HWY 27 Booster Pumping Station | 2025-12-01
WEST | December | Onsite for station check Duty not active Checked residuals mg/l @1318 Total analyzer 2.18 grab 2.13 Free analyzer 0.03 grab 0.06 Reagents ok | Kleinburg HWY 27 Booster Pumping Station | 2025-12-08
WEST | December | Station Check (no issues found0 Input data to PWQ 12:30 Verified Depolox (mg/L) Free: Grab 0.05, A 0.03 Total: Grab 2.10, A 2.16 | Kleinburg HWY 27 Booster Pumping Station | 2025-12-04
WEST | December | Onsite for station check Checked residuals mg/l @1252 Total analyzer 2.00 grab 2.01 Free analyzer 0.03 grab 0.03 Reagents ok | Kleinburg HWY 27 Booster Pumping Station | 2025-12-24
WEST | December | On-site for station check Checked residuals Total Analyzer 1.94mg/L Grab 1.98mg/L Free Analyzer 0.02mg/L Grab 0.05mg/L Reagents - all ok No known issues | Kleinburg HWY 27 Booster Pumping Station | 2025-12-29
WEST | December | Onsite for station check Deactivated duty to get Klet sample on down cycle Checked residuals mg/l @1301 Total analyzer 2.03 grab 2.04 Free analyzer 0.03 grab 0.05 | Kleinburg HWY 27 Booster Pumping Station | 2025-12-22
WEST | December | Onsite for station check Duty not active Checked residuals mg/l @1345 Total analyzer 2.16 grab 2.02 Free analyzer 0.03 grab 0.04 Adjusted total analyzer Completed deplox maintenance Grit and electrolyte ok Reagents ok | Kleinburg HWY 27 Booster Pumping Station | 2025-12-19
WEST | December | On site for station check Duty not active Check residuals mg/l @1405 Total analyzer 2.05 Grab 2.03 Free analyzer 0.01 grab 0.04 Jockeyed pumps 1&2 in local | Kleinburg Whisper Lane Booster Pumping Station | 2025-12-12
WEST | December | Onsite for station check Duty not active Checked residuals mg/L @1356 Total analyzer 2.00 grab 2.01 Free analyzer 0.01 grab 0.01 | Kleinburg Whisper Lane Booster Pumping Station | 2025-12-15
WEST | December | Onsite for station check Duty not active Checked residuals mg/l @1333 Total analyzer 1.98 grab 2.01 Free analyzer 0.00 grab 0.03 Reagents ok | Kleinburg Whisper Lane Booster Pumping Station | 2025-12-08
WEST | December | Station Check (no issues found) Input data to PWQ 11:25 Verified Depolox (mg/l) Free: Grab 0.04, A 0.02 Total: Grab 1.99, A 1.98 | Kleinburg Whisper Lane Booster Pumping Station | 2025-12-04
WEST | December | Onsite for station check Checked residuals mg/l @1257 Total analyzer 1.91 grab 1.88 Free analyzer 0.02 grab 0.04 | Kleinburg Whisper Lane Booster Pumping Station | 2025-12-01
WEST | December | Onsite for station check Duty not active Checked residuals mg/l @1425 Total analyzer 2.01 grab 1.99 Free analyzer 0.01 grab 0.03 Reagents ok | Kleinburg Whisper Lane Booster Pumping Station | 2025-12-19
WEST | December | Onsite for station check Duty not active Checked residuals mg/l @1149 Total analyzer 1.95 grab 1.95 Free analyzer 0.01 grab 0.04 Ran pumps 1&2 in local | Kleinburg Whisper Lane Booster Pumping Station | 2025-12-24
WEST | December | Onsite for station check Duty not active Checked residuals mg/l @1208 Total analyzer 1.71 grab 1.76 Free analyzer 0.02 grab 0.02 Topped up acetate solution | Kleinburg Whisper Lane Booster Pumping Station | 2025-12-22
WEST | December | On-site for station check Checked residuals Total Analyzer 1.93mg/L Grab 1.98mg/L Free Analyzer 0.00mg/L Grab 0.03mg/L Reagents all okay Bumped pumps 1 and 2 No issues | Kleinburg Whisper Lane Booster Pumping Station | 2025-12-29
LINEAR | December | Totalizer: 9,811,74 m3 Discharge pressure: 30.91 Kpa Flow Rate: 11.2 l/s Monitoring well: 219.1 masl Well 8 RPM: 2450 AMP: 5.5 %: 42 Level:208.0 masl Well 13 RPM: 2111 AMP: 4.9 %: 21 Level: 205.7 masl | Major MacKenzie and Newkirk Road Dewatering Wells | 2025-12-01
LINEAR | December | Totalizer: 482943 m3 Discharge pressure: 30.68 Kpa Flow Rate: 11.4 l/s Monitoring well: 219.3 masl Well 8 RPM: 2449 AMP: 5.5 %: 42 Level: 208.0 masl Well 13 RPM: 2112 AMP: 4.9 %: 21 Level: 205.8 masl | Major MacKenzie and Newkirk Road Dewatering Wells | 2025-12-19
LINEAR | December | Totalizer: 483217 m3 Discharge pressure: 30.60 Kpa Flow Rate: 11.2l/s Monitoring well: 219.1 masl Well 8 RPM: 2449 AMP: 5.5 %: 42 Level: 207.9 masl Well 13 RPM: 2112 AMP: 4.9 %: 21 Level: 205.7 masl | Major MacKenzie and Newkirk Road Dewatering Wells | 2025-12-22
LINEAR | December | Totalizer: 484109 m3 Discharge pressure: 26.60 Kpa Flow Rate: 11.4 L/s Monitoring well: 219.2 masl Well 8 RPM: 2450 AMP: 5.5 %: 42 Level: 207.8 masl Well 13 RPM: 2111 AMP: 5 %: 21 Level: 205.7 masl | Major MacKenzie and Newkirk Road Dewatering Wells | 2025-12-31
WEST | December | Station Check (no issues found) input data to PWQ Grab Residuals: (mg/L) Free 0.02, Total 1.62, Mono 1.53, FA 0.08, TA 0.38, N 0.000 12:35 #11438655 weekly and operational samples | Maple North Reservoir | 2025-12-10
WEST | December | On site for station check and to collect bacti sample wo# w11419287 Residuals @ 10:30colorimeter *West Cell* Total Grab: 1.81mg/L Free Grab: 0.05mg/L Operational Sampling (SL1000) Total Cl: 1.79mg/L Total NH3: 0.48mg/L Free NH3: 0.14mg/L NH2CL: 1.71mg/L NO2: 0.000mg/L No issues on site | Maple North Reservoir | 2025-12-03
WEST | December | Onsite to complete work orders Completed jhsc with no issues Exercised valves | Maple North Reservoir | 2025-12-19
WEST | December | On site for station check and to collect bacti sample wo# w11454881 Residuals @ 10:30colorimeter *East Cell* Total Grab: 1.64mg/L Free Grab: 0.05mg/L No issues on site | Maple North Reservoir | 2025-12-16
WEST | December | on site to complete station check and collect weekly bacti W11483618 -checked trends: all ok -took chlorine grab east cell 09:00 sampled -free cl: 0.04mg/l -total cl: 1.74mg/l Nitrite. O.00 Monochloramine 1.58 mg/L Free Ammonia. 0.09 mg/L Total Ammoni -took chlorine grab west cell 09:15 -free cl: 0.05mg/l -total cl: 1.73mg/l -equipment all ok | Maple North Reservoir | 2025-12-29
WEST | December | -on site to complete station check and collect weekly bacti W11470054 -checked trends: all ok -entered readings in PWQ -took chlorine grab east cell 09:20 -free cl: 0.03mg/l -total cl: 1.65mg/l -took chlorine grab west cell 09:15 - sampled -free cl: 0.04mg/l -total cl: 1.64mg/l -equipment all ok | Maple North Reservoir | 2025-12-22
WEST | December | On site to Complete Station Check. Residuals PD8 Total Grab: 1.96mg/L, Analyzer: 1.93mg/L PD8 Free Grab: 0.05mg/L, Analyzer: 0.02mg/L PD7 Total Grab: 1.84mg/L, Analyzer: 1.82mg/L PD7 Free Grab: 0.05mg/L, Analyzer: 0.04mg/L No issues on site | Maple Pumping Station | 2025-12-12
WEST | December | Pumping Station Check (no issues found) Input data to PWQ 13:16 Residuals (mg/l): PD7 Free: Grab 0.05, A 0.06 Total: Grab 1.16, A 1.58 PD8 Free: Grab 0.06, A 0.02 Total: Grab 1.78, A 1.70 | Maple Pumping Station | 2025-12-15
WEST | December | Vibration readings | Maple Pumping Station | 2025-12-15
WEST | December | Grease motor and pumps 1 and 2 pd7 | Maple Pumping Station | 2025-12-12
WEST | December | On site to respond to reports of Station power outage. Upon arrival to site found Hydro power not coming into Station and generators running correctly. Called utility company to come in and check the incoming Vista switch and was able to confirm that the Vista switch was tripped. Worked with maintenance supervisor to arrange for Ainsworth high voltage contractor to be dispatched to site to work with on-call electrician towards restoration of site power. Transferred information to on-call electrician who has arrived at site. | Maple Pumping Station | 2025-12-10
WEST | December | 10:00 (approx) power failure & generator operating as should Following pump VFD faulted and re-set: PD7 1&3 PD8 1, 3, 4 (pump 2 left in fault for electricians) Generator test work order closed for the month due to outage | Maple Pumping Station | 2025-12-10
WEST | December | On site to assist Ainsworth with VISTA switch reset. Alectra on site to isolate main power. Ainsworth tested T1 and T2. No issues found. Cause of VISTA switch gear trip unknown. Alectra called back to site to reconnect. Utility power restored at 9:20pm. Reset faults on Scada. Informed ROC. | Maple Pumping Station | 2025-12-10
WEST | December | On site with Tyler Zimmerman-Jones to troubleshoot PD8 pump #2. ROC notified. Found VFD in fault condition. Displaying ?AMC: Class 2? fault. Vfd fault reset completed and returned to ready condition. With assistance of ROC, Pump #2 placed in Manual and tested for 6 minute run time. Vfd started and stopped without incident. Fault could not be replicated. ROC notified of work completion. | Maple Pumping Station | 2025-12-02
WEST | December | On site to Complete Station Check. Residuals PD8 Total Grab: 2.08mg/L, Analyzer: 2.13mg/L PD8 Free Grab: 0.04mg/L, Analyzer: 0.02mg/L PD7 Total Grab: 1.99mg/L, Analyzer: 2.09mg/L PD7 Free Grab: 0.05mg/L, Analyzer: 0.04mg/L No issues on site | Maple Pumping Station | 2025-12-01
WEST | December | On site to Complete Station Check. Residuals PD8 Total Grab: 1.56mg/L, Analyzer: 1.53mg/L PD8 Free Grab: 0.04mg/L, Analyzer: 0.02mg/L PD7 Total Grab: 1.35mg/L, Analyzer: 1.41mg/L PD7 Free Grab: 0.05mg/L, Analyzer: 0.04mg/L No issues on site | Maple Pumping Station | 2025-12-08
WEST | December | On site to check res south high alarm -lit reads 0 no water at sample tap all seems okay - disregard alarms | Maple Pumping Station | 2025-12-01
WEST | December | Started PD8 P1 in remote/man for trouble shooting at AURSBS, informed area OIC Jordan Bloye. | Maple Pumping Station | 2025-12-02
WEST | December | Torbear orientation Vibration testing Got pump 3 done all pumps shut down | Maple Pumping Station | 2025-12-02
WEST | December | -on site for station check -checked trends: all ok -took readings in PWQ: all ok -verified PD7 analyzer 11:15: -analyzer free: 0.04mg/l grab: 0.08mg/l -analyzer total: 1.81mg/l grab: 1.78mg/l -verified PD8 analyzer 11:20: -analyzer free: 0.02mg/l grab: 0.04mg/l -analyzer total: 1.74mg/l grab:1.72mg/l -equipment all ok | Maple Pumping Station | 2025-12-30
WEST | December | On site with Sean Peoples to assist ABB vfd technician performing maintenance on PD8 vfd?s. PD8 Pump #2 breaker opened, racked out and locked out. ROC notified. Pump #2 maintenance completed and VFD reenergized. With ROC assistance, pump #2 run for 5 minutes as test. All work completed, ROC notified. | Maple Pumping Station | 2025-12-17
WEST | December | Oversaw/assisted ABB technical rep performed Annual VFD maintenance. | Maple Pumping Station | 2025-12-19
WEST | December | On site with Sean Peoples to assist ABB vfd technician performing maintenance on PD8 vfd?s. PD8 Pump #3 breaker opened, racked out and locked out. ROC notified. PD8 Pump #3 maintenance completed and reenergized. With assistance from ROC, pump #3 run for 5 minute test. PD8 Pump #1 breaker opened, racked out and locked out. ROC notified. On site with Sean Peoples to assist ABB vfd technician performing maintenance on PD8 vfd?s. PD8 Pump #3 breaker opened, racked out and locked out. ROC notified. PD8 Pump #1 maintenance completed and reenergized. ROC notified. | Maple Pumping Station | 2025-12-18
WEST | December | Station Check (no issues found) Input data to PWQ 11:37 CL2 Residuals (mg/l) PD7 Free: Grab 0.04, A 0.04 Total: Grab 1.82, A 1.86 PD8 Free: Grab 0.04, A 0.02 Total: Grab 1.86, A 1,80 W/O #11450259 screens #11450350 sump #11426995 clean #11450652 flood (gen.) #11450782 fuel panel #11450810 jhs | Maple Pumping Station | 2025-12-18
WEST | December | Station Check (no other issues found) Input data to PWQ w/o#11450308 Depolox maint Verified (mg/L): PD 7(11:26) Free: Grab 0.06, A 0.04 Total: Grab 1.86, A 1.91 PD 8 (11:36) Free: Grab 0.04, A 0.02 Total: Grab 1.60, A 1.56 PD7- pump 3: Generated w/o #11536217 (noisy), placed in manual off, notified ROC | Maple Pumping Station | 2025-12-23
WEST | December | -on site for station check -checked trends: all ok -entered readings in PWQ: all ok -verified PD7 analyzer 09:20 -analyzer free: 0.04mg/l grab: 0.04mg/l -analyzer total: 1.83mg/l grab: 1.81mg/l -verified PD8 analyzer 09:25 -analyzer free: 0.02mg/l grab: 0.03mg/l -analyzer total: 1.70mg/l grab: 1.86mg/l - adjusted -equipment all ok | Maple Pumping Station | 2025-12-24
WEST | December | Chris Iliohan and Tyler Smith into replace flexible fuel line on generators 1 and 2. Ran generators to check for leaks and operation no issues noticed. Also on site to inspect pd7 pump for abnormal noise. After investigation pump has air entrapment due to choked off air valve will install new fitting and replace when scheduled | Maple Pumping Station | 2025-12-24
WEST | December | Station Check (no issues found) Input data to PWQ 10:14 North Cell (mg/L): Grabs: Free: 0.02, Total 1.73, Mono 1.65, FA 0.07, TA 0.39, N 0.000 10:50 #11438655 weekly, operational samples 10:30 Metro (mg/L): Free: Grab 0.04, A 0.01 Total: Grab 1.80, 1.97 (adjusted to match grabs) 10:45 Peele (mg/L): Total: Grab 2.00, A 2.06 Work orders: # 11458671 cl2 analyzers maint. #11456626 dehumidifier #11456894 eyewash sol'n #11456613 sump #11456924 valve box #11456509 hoist Unable to exercise valves as locked out | Maple South Reservoir | 2025-12-10
WEST | December | On site for station check and to collect bacti sample wo#w11419287 Peel Total Grab: 2.10mg/L, Analyzer: 2.14mg/L Metro Total Grab: 2.12mg/L, Analyzer: 2.14mg/L Metro Free Grab: 0.05mg/L, Analyzer: 0.01mg/L Residuals North cell:@ 0825 Free: 0.05mg/L Total 2.18mg/L SL1000 readings Total Cl: 2.16mg/L Total NH3: 0.47mg/L Free NH3: 0.09mg/L NH2Cl: 1.97mg/L NO2: 0.000mg/L Reagents - changed out peel CL17 reagents No issues on site | Maple South Reservoir | 2025-12-03
WEST | December | Made changes to pressure setpoints at ARPS and lolo level setpoint for maple reservoir per PCSCR#223700 and W/OW11508859 | Maple South Reservoir | 2025-12-17
WEST | December | On site for station check and to collect bacti sample wo#w11419287 Peel Total Grab: 1.56mg/L, Analyzer: 1.51mg/L Metro Total Grab: 1.85mg/L, Analyzer: 1.85mg/L Metro Free Grab: 0.05mg/L, Analyzer: 0.01mg/L Residuals North cell:@ 1000 Free: 0.05mg/L Total 1.78mg/L Reagents - all ok No issues on site | Maple South Reservoir | 2025-12-16
WEST | December | Onsite to close Peel feeder main inlet valve res-inlt1_mv1 for trial isolation | Maple South Reservoir | 2025-12-17
WEST | December | Under the supervision of Cole Warnica as per the PCSCR 224346 and 224326 by Cristina Sistilli, Changed the HMA HiHi and LoLo Reservoir Cell 1 Setpoints. New Setpoints are: HiHi - 87% LoLo - 50% | Maple South Reservoir | 2025-12-22
WEST | December | on site for station check and collect weekly bacti W11483618 -check trends: all ok Free ammonia. 0.07mg/l Total ammonia. 0.39mg/l Nitrite. O.001mg/l Monochloramine. 1.63mg/l -verified Peel analyzer 10:00: 1.72mg/l grab: 1.74mg/l -verified metro 10:06 -analyzer free: 0.02mg/l grab: 0.02mg/l -analyzer total: 1.74mg/l grab: 1.75mg/l -north cell grab 09:55 -free cl: 0.02mg/l -total cl: 1.84mg/l -south south offline due to construction | Maple South Reservoir | 2025-12-29
WEST | December | -on site for station check and collect weekly bacti W11470054 -check trends: all ok -enter readings in PWQ: all ok -verified Peel analyzer 08:15: 1.78mg/l grab: 1.74mg/l -verified metro 08:20 -analyzer free: 0mg/l grab: 0.03mg/l - adjusted -analyzer total: 1.93mg/l grab: 1.87mg- adjusted -north cell grab 08:25 -free cl: 0.06mg/l -total cl: 1.75mg/l -south south offline due to construction -reset PD8 pump 4 at MAPS | Maple South Reservoir | 2025-12-22
CENTRAL | December | Onsite for station check/collect sample- WO# W11438473: Sample results (09:10): Free- 0.06, Total- 2.66 * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Newmarket (East) Harry Walker Elevated Tank | 2025-12-10
CENTRAL | December | On-site for ET/altitude valve isolation for Devine (contractor) to complete repairs on Altitude valve. Informed ROC. Changed system controlling ET to QVETQS, QVETQS man/open. Isolated ET from distribution at 07:30 via remote SCADA, doubled isolated ET and altitude valve with hand valves once on-site and confirmed isolation at 08:46 and LOTO appropriate equipment. Powered down depolox analyzer as flow cut off to analyzer for duration of work. Devine began their work on the altitude valve. Devine completed their repairs on the altitude valve and disinfected parts/valve body with >1% hypo solution. Returned Inlet portion of system to the motorized isolation valve to normal operation and cracked motorized isolation valve to charge main and bleed air from altitude valve cover, ET remains isolated from distribution system via BV in mezzanine. Flushed via drain valve with dechlorination measures in place and powered on depolox analyzer, grab sample as follows (mg/L): Free Cl (12:51): 0.05 Total Cl (12:56): 2.38 Confirmed mechanical operation of valve while flow directed to drain. Opened mezzanine BV and continued to commission valve via SCADA commands/setpoints through system conditions with Ian Williams (PCS). Adjusted depolox analyzer once analyzer readings stabilized based on average grab as follows (mg/L): Free Cl (13:42): G: 0.05 A: 0.02 Total Cl (13:46): G: 2.44 A: 2.07 (adjusted to 2.44mg/L) System returned to normal operation as of 14:25, altitude commissioning successful. Informed ROC. No new issues found while on-site. | Newmarket (East) Harry Walker Elevated Tank | 2025-12-04
CENTRAL | December | FYI, Ernie and I came to site this morning for some follow up. In an effort to determine if the temperature?sensing was working correctly we disabled the heat trace and flushed the sense line until the temperature stabilized, around 5C. The temperature was corroborated with an IR camera. Seems like the temperature sensors are working correctly. Heat trace re-enabled. We verified that the temperature sensors are installed properly. As to their location, they are right adjacent to each other, ?not sure this is the best design? If they were separated by a greater distance the system may get a better average reading? However, the sensing line is long, and the temperature sensor only reports the temperature at that one signal spot. And I did not witness the heat trace installation. It is possible there is a cold spot somewhere along the run that the temperature sensors cannot see. We set the set point to 10C. We found the low temp alarm set point at 1C, too low, increased it to 5C. Lastly, there is a small line tapped off the main sensing line in the valve room which goes to the sample sink. We cracked its ball valve so there is a small amount of flow. | Newmarket (East) Harry Walker Elevated Tank | 2025-12-08
CENTRAL | December | Onsite to investigate tower level rising even though duty is off. Temperature outside is -3 degrees Celsius and has been colder all day. Found LIT sample line heat trace 3 off and reading 12 degrees but line is frozen. Set heat trace to heat to 14 degrees. Flushed LIT line. Lit line now matches mainline pressure and is reading accurately. No issues remain. Will have maintenance investigate the temperature reading on thermometer heat heat trace controller on Monday. | Newmarket (East) Harry Walker Elevated Tank | 2025-12-05
CENTRAL | December | On site to complete station check, weekly bacti sampling (W11420073) and monthly fluoride sampling (W11419398). -Topped up depolox acetate buffer reagent -Verified analyzer: Free chlorine @ 11:32 Grab: 0.06 mg/L Analyzer: 0.01 mg/L Total chlorine @ 11:32 Grab: 2.50 mg/L Analyzer: 2.54 mg/L -Topped up depolox KI reagent -Checked trends -Entered data into PD sheet -Placed QVW12 both wells in manual-on | Newmarket (East) Harry Walker Elevated Tank | 2025-12-03
CENTRAL | December | Onsite for station check/collect sample- WO# W11455364: Sample results (10:38): Free- 0.04, Total- 2.84 * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Newmarket (East) Harry Walker Elevated Tank | 2025-12-16
CENTRAL | December | On site to complete work orders and collect sample. COC W11469872. 14:17 Tower level 66% and draining at 5.6 l/s. 14:18 verified chlorine analyzers (mg/l) and collect sample. Free grab 0.05. Analyzer: 0.01. Total grab: 2.66. Analyzer: 2.68. Cracked open LIT drain line to help keep line from freezing. No issues found. | Newmarket (East) Harry Walker Elevated Tank | 2025-12-22
CENTRAL | December | Adjusted duty start from 40 to 50%. Adjusted duty stop from 75 to 80 % | Newmarket (East) Harry Walker Elevated Tank | 2025-12-28
CENTRAL | December | On site to complete work orders and collect sample. COC W11484072. 15:24 Tower level 67% and draining at 45 l/s. 15:26 verified chlorine analyzers (mg/l) and collect sample. Free grab 0.01. Analzyer: 0.00. Total grab: 2.62. Analyzer: 2.63. topped up analzyer acetate reagent. No issues found. | Newmarket (East) Harry Walker Elevated Tank | 2025-12-29
CENTRAL | December | Onsite to complete assigned work orders: H/S inspection Heat trace system inspection Depolox analyzer maintenance Performed station housekeeping Station/equipment- Ok | Newmarket (East) Harry Walker Elevated Tank | 2025-12-17
CENTRAL | December | Onsite to verify analyzers: Grabs (08:10): Free- 0.03, Total- 2.84 Analyzers (08:10): Free- 0.02, Total- 2.87 Depolox reagents- Ok Station/equipment- Ok | Newmarket (East) Harry Walker Elevated Tank | 2025-12-19
CENTRAL | December | Restarted the Operator Interface Terminal due to Video Driver Updates. This is being done to fix a memory leak. | Newmarket (East) Harry Walker Elevated Tank | 2025-12-16
CENTRAL | December | Onsite for station check: Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Chemscan reagents- Ok Station/equipment- Ok | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2025-12-12
CENTRAL | December | On-site for a station and equipment check, no issues found. Chemical levels and systems ok Topped up both Hypo day tanks Verified analyzers while draining All readings and grabs entered into PWQ sheet Pre-injection Free@1322 g:0.04 a:0.02mg/L Pre-injection Total@1329 g:1.86 a:1.81mg/L Post-injection Free@1335 g:0.09 a:0.06mg/L Post-injection Total@1336 g:3.32 a:3.35mg/L | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2025-12-15
CENTRAL | December | Onsite for station check/collect sample- WO# W11438473: Sample results (14:00): Free- 0.02, Total- 1.80 * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Chemscan reagents- Ok Station/equipment- Ok | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2025-12-10
CENTRAL | December | Onsite to complete assigned work order- informed ROC: Completed chemscan outlet/header hot water flush- chemical systems back in auto once completed Station/equipment- Ok | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2025-12-02
CENTRAL | December | Onsite to complete assigned work orders- informed ROC: H/S inspection Low temp test Ventilation inspection CL17 analyzer maintenance Chemscan analyzer maintenance Flood alarm test Chemical storage tank inspections Performed station housekeeping Station/equipment- Ok | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2025-12-04
CENTRAL | December | Onsite for station check: Performed station housekeeping Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Chemscan reagents- Ok Station/equipment- Ok | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2025-12-05
CENTRAL | December | Onsite to complete assigned work orders- informed ROC: Chemscan outlet/header hot water flush Hypo pump inspections Ammonia pump inspections Received hypo delivery Adjusted hypo pump 3 max flow from 480 mL/min to 440 mL/min based on multiple drawdown attempts * Adjusted hypo pump 4 max flow from 480 mL/min to 460 mL/min based on multiple drawdown attempts * Station/equipment- Ok | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2025-12-09
CENTRAL | December | Onsite for station check: Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Chemscan reagents- Ok Performed maintenance/cleaning on hypo injection points #2 and #4- will monitor * Station/equipment- Ok | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2025-12-08
CENTRAL | December | Onsite for station check: Replaced inlet free CL17 reagents * Replaced hypo p#3 and p#4 Watson Marlow tubing * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Chemscan reagents- Ok Station/equipment- Ok Received hypo delivery * | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2025-12-01
CENTRAL | December | On-site for station check, weekly micro sampling (W11420073) and monthly fluoride sampling (W11419398) work orders. Entered station readings into shared PD excel file, duty recently activated. Grab sample taken from Outlet sample tap as follows (mg/L): Outlet Free Cl (08:45): 0.02 Outlet Total Cl (08:45): 1.47 Collected samples from Outlet sample tap. Checked station and equipment, no new issues found. | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2025-12-03
CENTRAL | December | -Performed year-end inventory count -Received 550L of hypo | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2025-12-23
CENTRAL | December | Receive 450 L of hypo (Dec 16 @ 330 pm) | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2025-12-17
CENTRAL | December | On-site for station check and sampling 10:40 Tank 2 at 75% and filling at 80 /s. System in chloramine reformation dosing. Tank 1 offline. Topped up hypo tanks 1 and 2. Topped up ammonia tank 1. 11:54. Verified outlet/preinjection residuals (mg/l). Reservoir now draining at 104 l/s. Collected sample Free grab: 0.05. Analyzer: 0.02. Total grab: 1.85/1.83/1.82 CL17: 1.82 Chemscan: 1.68. adjusted chemscan to match grab. Monochlormaine: 0.56 Chemsca: 0.45. Adjusted chemscan to match grab. Free ammonia: 0.08 Chemscan: 0.17. Adjusted to match grab. Total ammonia: 0.19. Chemscan: 0.20 12:10. Post-Injection (header). Free chlorine: 0.06. CL17: 0.06. Total chlorine: 3.40 CL17: 3.43. Chemscan: 3.29. Monochloramine grab: 2.01. Chemscan: 2.13 Free ammonia: 0.00. Chemscan: 0.05. Total ammonia: 0.36. Chemscan: 0.39. Hypo pump 3 minor leak on discharge tubing fitting. Placed OOS and repaired fitting. Placed back in service with no issues. No issues on site. | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2025-12-22
CENTRAL | December | Onsite for station check/collect sample- WO# W11455364: Sample results (12:38): Free- 0.02, Total- 1.84 * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Chemscan reagents- Ok Station/equipment- Ok | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2025-12-16
CENTRAL | December | On-site for station check and sampling. COC11484072 13:21 Tank 2 at 65% and draining at 95 l/s. System in chloramine boosting mode. Tank 1 offline. Topped up hypo tanks 1 and 2. Topped up ammonia tank 2. Replaced header total cl17 analyzer reagent. Topped up chemscan distilled water and sulphuric acid reagents. 13:52. Verified outlet/preinjection residuals (mg/l). Collected sample Free grab: 0.02. Analyzer: 0.02. Total grab: 1.91 CL17: 1.99 Chemscan: 1.74. Monochlormaine: 0.68 Chemsca: 0.65. Free ammonia: 0.09 Chemscan: 0.13. Total ammonia: 0.23. Chemscan: 0.25 14:15. Post-Injection (header). Free chlorine: 0.09. CL17: 0.05. Total chlorine: CL17: 3.19. Chemscan: 3.29. Monochloramine grab: 2.02. Chemscan: 2.16 Free ammonia: 0.00. Chemscan: 0.05. Total ammonia: 0.42. Chemscan: 0.41. No issues on site. | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2025-12-29
CENTRAL | December | Onsite for station check: Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Depolox reagents- Ok Station/equipment- Ok | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2025-12-19
CENTRAL | December | Onsite for station check: Station/equipment- Ok | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2025-12-19
CENTRAL | December | Station and equipment check Took grabs @ 10:05 am (filling) Inlet Total: 3.08 mg/l Inlet Free: 0.08 mg/l Header Total: 2.56 mg/l Header Free: 0.05 mg/l Chemicals/reagents ok Ops normal | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2025-12-24
CENTRAL | December | Station and equipment check ET OFFLINE Ops normal | Newmarket (London) Yonge Street Elevated Tank | 2025-12-12
CENTRAL | December | Station and equipment check ET OFFLINE as per norm ET ok | Newmarket (London) Yonge Street Elevated Tank | 2025-12-01
CENTRAL | December | Station and equipment check Complete monthly Maximo workorders ET OFFLINE Ops normal | Newmarket (London) Yonge Street Elevated Tank | 2025-12-18
CENTRAL | December | Station and equipment check ET remains OFFLINE as per norm ET ops ok | Newmarket (London) Yonge Street Elevated Tank | 2025-12-23
CENTRAL | December | Site off line. On-site for a visual inspection, perimeter check. All buildings secure. No issues found. | Newmarket (Northeast) Davis Drive Elevated Tank | 2025-12-05
CENTRAL | December | Onsite to complete assigned work orders: Station check completed H/S inspection Station/equipment- Ok | Newmarket (Northeast) Davis Drive Elevated Tank | 2025-12-18
CENTRAL | December | Onsite for station check. Site offline. Buildings secure. No issues found. | Newmarket (Northeast) Davis Drive Elevated Tank | 2025-12-22
CENTRAL | December | Onsite to complete assigned work orders: H/S inspection Heat trace inspection Flood alarm test Depolox analyzer maintenance Portable generator inspection Performed station housekeeping Station/equipment- Ok | Newmarket (Southeast) Ivsbridge Elevated Tank | 2025-12-11
CENTRAL | December | Onsite for station check/collect sample- WO# W11438473: Sample results (10:42): Free- 0.08, Total- 2.76 * Adjusted total analyzer from 2.90 to 2.76 based on multiple grabs Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Newmarket (Southeast) Ivsbridge Elevated Tank | 2025-12-10
CENTRAL | December | On-site to investigate elevated total chlorine reading of 9.99 mg/l. ROC created cmu5 work order at 18:47. 19:35 found sample line blocked and analyzers receiving no flow. Exercised psv and cleared blockage. Analyzer dropped once flow resumed. 19:50 total grab 2.72 /2.70/2.68 mg/l. Analyzer: 2.14. Adjusted analyzer to match grabs. No issues remain. | Newmarket (Southeast) Ivsbridge Elevated Tank | 2025-12-04
CENTRAL | December | On site to complete station check, weekly bacti sampling (W11420073) and monthly fluoride sampling (W11419398). -Verified analyzer: Free chlorine @ 9:10 Grab: 0.02 mg/L Analyzer: 0.03 mg/L Total chlorine @ 9:10 Grab: 2.44 mg/L Analyzer: 2.35 mg/L -Checked trends -Entered data into PD sheet | Newmarket (Southeast) Ivsbridge Elevated Tank | 2025-12-04
CENTRAL | December | -Performed station check - logged station readings into PWQ sheet Grab: treated total=2.92mg/L free=0.06mg/L@16:00 Analyzer: treated total=2.92mg/L free=0.03mg/L -Checked Depolox reagents - OK -Collected weekly BacT sample YD #W11484072 | Newmarket (Southeast) Ivsbridge Elevated Tank | 2025-12-29
CENTRAL | December | Onsite for station check/collect sample- WO# W11455364: Sample results (08:30): Free- 0.07, Total- 2.70 * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Newmarket (Southeast) Ivsbridge Elevated Tank | 2025-12-16
CENTRAL | December | On-site to complete station check and sampling COC W11469872. 07:54. Tank Level: 64% and draining at 73 l/s. 08:27. Collected grab sample and verified analyzers (mg/l). Free grab: 0.06. Analyzer: 0.02. Total chlorine grab: 2.83 Analyzer: 2.80. Station and equipment - no issues identified. | Newmarket (Southeast) Ivsbridge Elevated Tank | 2025-12-22
CENTRAL | December | On site to perform PM on heat trace system. Checked voltage and current, operating in good condition. | Newmarket (Southeast) Ivsbridge Elevated Tank | 2025-12-31
CENTRAL | December | Onsite for station check/collect sample- WO# W11438473: Sample results (12:00): Free- 0.06, Total- 2.80 * Adjusted inlet total analyzer from 2.63 to 2.92 based on multiple grabs Verified analyzers Depolox reagents- Ok Station/equipment- Ok Completed assigned work orders: H/S inspection Puck dispenser inspection Depolox analyzer maintenance Station housekeeping | Newmarket (West) Bathurst Tank | 2025-12-10
CENTRAL | December | Station and equipment check Take weekly BacT sample/fluoride and grabs @ 13:25 pm Total: 2.70 mg/l Free: 0.04 mg/l reagents ok ops normal | Newmarket (West) Bathurst Tank | 2025-12-03
CENTRAL | December | Station Check (no issues found) Input data to PWQ 14:05 Verified Depolox (mg/l) Free: Grab 0.06, A 0.08 Total: Grab 2.82, A 2.90 14:15 #11484072 sample | Newmarket (West) Bathurst Tank | 2025-12-29
CENTRAL | December | On-site to complete station check and collect sample. COC WW11479872. 09:24 Tank Level: 52%. Draining at 105 l/s. 09:25 collected outlet sample and verified analyzer (mg/l): Free grab: 0.09 Analyzer: 0.07 Total grab: 2.70/2.74/2.70 analzyer 2.59. Adjusted total to match grab average. Station and equipment: No known issues. Recorded data into process sheets. | Newmarket (West) Bathurst Tank | 2025-12-22
CENTRAL | December | Onsite for station check/collect sample- WO# W11455364: Sample results (13:55): Free- 0.03, Total- 2.64 * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Newmarket (West) Bathurst Tank | 2025-12-16
CENTRAL | December | On-site for a station and equipment check, no issues found All measurements and readings entered into PWQ sheet | Newmarket Kirby Pumping Station | 2025-12-15
CENTRAL | December | Onsite for station check: Station/equipment- Ok | Newmarket Kirby Pumping Station | 2025-12-12
CENTRAL | December | Onsite for station check: Station/equipment- Ok | Newmarket Kirby Pumping Station | 2025-12-08
CENTRAL | December | Onsite for station check: Station/equipment- Ok | Newmarket Kirby Pumping Station | 2025-12-05
CENTRAL | December | Onsite to complete assigned work orders- informed ROC: H/S inspection Low temp test Ventilation inspection Pump and motor inspection- ran each pump (10 min each) Activated valve exercise/inspection Manual valve exercise/inspection PRV inspection Flow control valve inspection Performed station housekeeping Generator test run: Generator pre test inspection completed- no abnormalities * Start time- 11:42 am Stop time- 12:50 pm Start hours- 29.55 Stop hours- 30.65 Start fuel- 892 L (89.6 cm) Stop fuel- 882 L (88.6 cm) Generator operating stats (under load): 1800 rpm 60 hertz 600 V 10 A Oil pressure 37 psi Coolant temp 168 F No abnormalities during generator test run- placed generator back into auto once test completed. Station back on hydro. Station/equipment- Ok | Newmarket Kirby Pumping Station | 2025-12-02
CENTRAL | December | Onsite for station check: Station/equipment- Ok | Newmarket Kirby Pumping Station | 2025-12-01
CENTRAL | December | On site perform station check. All pumps in standby. Recorded data into process sheets. FCV 1 flow at 0 l/s. No issues on site. | Newmarket Kirby Pumping Station | 2025-12-22
CENTRAL | December | Onsite to assist CPD, consultant, and developer with station isolation for nearby development work. Placed all station pumps and FCV in man/off- informed ROC. At 10:25- discharge valve in driveway fully isolated. | Newmarket Kirby Pumping Station | 2025-12-17
CENTRAL | December | Station and equipment check FCV: 17% Suction pressure: 74 kPa Discharge pressure: 352 kPa Discharge flow: 20 l/s Ops normal | Newmarket Kirby Pumping Station | 2025-12-24
CENTRAL | December | Onsite to return station back to normal operation: @16:40- notified by CPD (Rafi) and Consultant (Jake GEI) that the work has been completed- will begin reverting station back to normal operation @17:00- discharge isolation valve in driveway reopened @17:10- returned all station pumps and FCV back into auto- informed ROC Station back to normal operation- informed oncall operator (Jason Garnett) Station/equipment- Ok | Newmarket Kirby Pumping Station | 2025-12-17
CENTRAL | December | Received call from RO Adam Button regarding effluent free Cl analyzer fault triggered after well start up. Reviewed trends, analyzer fault reset, returned Wells to service and monitored remotely. Influent Free Cl spike on start-up but returned to operating range and cleared hi alarm, CT achieved and effluent analyzer reading normally, informed ROC. | Newmarket Well 1 & 2 | 2025-12-13
CENTRAL | December | Station and equipment check Take weekly BacT sample W11439265 and grabs @ 9:45 am Treated Total: 2.85 mg/l Treated Free: 0.13 mg/l All other readings on PD sheets Topped up ammonia tank 2 Chemicals/reagents ok Ops normal | Newmarket Well 1 & 2 | 2025-12-10
CENTRAL | December | Receive chlorine cylinders x12 Full, return 12 empty | Newmarket Well 1 & 2 | 2025-12-15
CENTRAL | December | Station and equipment check Took grabs @ 9:35 am Treated Total: 2.87 mg/l (standardized analyzer) Treated Free: 0.12 mg/l Chemicals/reagents ok Ops normal | Newmarket Well 1 & 2 | 2025-12-12
CENTRAL | December | Station and equipment check Take in-house operational sample and grabs @ 9:50 am Treated Total: 3.05 mg/l Treated Free: 0.12 mg/l No adjustments required All other readings on PD sheets Chemicals/reagents ok Ops normal | Newmarket Well 1 & 2 | 2025-12-15
CENTRAL | December | Onsite to complete maximo workorders Hot water flush both silicate lines Chemical inspections complete - all ok JHSC inspection no issues General housekeeping duties complete Ops normal | Newmarket Well 1 & 2 | 2025-12-04
CENTRAL | December | Topped up silicate day tanks. | Newmarket Well 1 & 2 | 2025-12-09
CENTRAL | December | Chlorine cylinder change w/ Joe D (right bank) Also pull silicate injection point 1 for cleaning, informed ROC (Christian V) of ongoings Placed all analyzers in CAL mode and wells Manual After cleaning complete returned station to normal ops (auto) both wells ran in auto duty with no issues | Newmarket Well 1 & 2 | 2025-12-09
CENTRAL | December | Station and equipment check Took grabs and in house operational samples @ 9:40 am Treated Toyal: 2.90 mg/l Treated Free: 0.12 mg/l Chemicals/reagents ok No adjustments required Ops normal | Newmarket Well 1 & 2 | 2025-12-01
CENTRAL | December | Station and equipment check Take weekly BacT samples and grabs @ 10:40 am Treated Total: 2.82 mg/l (adjusted analyzer to match) Treated Free: 0.14 mg/l Topped up ammonia tank 1 Chemicals/reagents ok All other readings on PD sheets Ops normal | Newmarket Well 1 & 2 | 2025-12-03
CENTRAL | December | Station and equipment check Took grabs @ 9:15 am (running) Treated Total: 2.90 mg/l Treated Free: 0.12 mg/l All other readings on PD sheets no adjustments required Chemicals/reagents ok Ops normal | Newmarket Well 1 & 2 | 2025-12-05
CENTRAL | December | Onsite to complete maximo workorders Informed ROC (Carter D) of ongoings Placed wells in Manual OFF completed cleaning of ALL analyzers and turbidimeter Returned wells to Auto inspection of chlorine system and took chlorine scrubber media samples to be sent to lab Ammonia system inspection - all ok Station ops normal | Newmarket Well 1 & 2 | 2025-12-02
CENTRAL | December | Station and equipment check Took grabs and in-house operational sample @ 9:20 am (running) Treated Total: 2.87 mg/l Treated Free: 0.14 mg/l No adjustments required All other readings on PD sheets shared online folder Chemicals/reagents OK *Silicate P1 remains OOS, tried another hot flush of lines to no avail, will have to pull injection point to investigate further Ops otherwise normal | Newmarket Well 1 & 2 | 2025-12-08
CENTRAL | December | Topped up silicate day tanks. 704 L 1116 L. No issues remaining. | Newmarket Well 1 & 2 | 2025-12-02
CENTRAL | December | Grease bottom motor bearings | Newmarket Well 1 & 2 | 2025-12-05
CENTRAL | December | Station Check (no issues found) Input data to PWQ 9:50 Verified CL17s (mg/l) Influent: Free Grab 2.70, A 2.71 Effluent: Free Grab 2.60, A 2.54 Treated: Free Grab 0.10, A 0.14 Total Grab 3.00, A 2.97 (new reagents) 10:05 #11483430 samples (raw & treated) | Newmarket Well 1 & 2 | 2025-12-29
CENTRAL | December | Station and equipment check Take weekly BacT sample W1145707 and grabs @ 8:25 am (running) Treated Total: 2.96 mg/l Treated Free: 0.12 mg/l All other readings on PD sheets no adjustments required Topped up well 2 Drip oil Chemicals/reagents ok Ops normal | Newmarket Well 1 & 2 | 2025-12-16
CENTRAL | December | Topped up silicate tanks about 300 L | Newmarket Well 1 & 2 | 2025-12-23
CENTRAL | December | Station and equipment check Take weekly BacT samples W11470548 and grabs @ 9:45 am Treated Total: 2.85 mg/l Treated Free: 0.12 mg/l All other readings on PD sheets shared online folder Chemicals/reagents ok No adjustments Ops normal | Newmarket Well 1 & 2 | 2025-12-22
CENTRAL | December | Onsite to deliver silicate. Topped up tank to 123 cm. Tank lvl out of range triggered and interlocked silicate system. Roc called to inform me. 11:00 Disabled oor alarm for silicate tank and silicate system resumed. Notified team lead that tank fill limits need adjusting. | Newmarket Well 1 & 2 | 2025-12-16
CENTRAL | December | Onsite to complete workorder chlorine leak test, informed ROC (Connor) - all ok Topped up ammonia tank 1 and dropped off ammonia bags Ops normal | Newmarket Well 1 & 2 | 2025-12-17
CENTRAL | December | Change chlorine cylinders w/ Jerry Z (left bank) Ops normal | Newmarket Well 1 & 2 | 2025-12-23
CENTRAL | December | Station and equipment check Took grabs @ 9:00 am (off) Treated Total: 1.68 mg/l Treated Free: 0.05 mg/l Topped up ammonia tank 2 Chemicals/reagents ok Ops normal | Newmarket Well 1 & 2 | 2025-12-24
CENTRAL | December | Topped up silicate day tanks.638 L to 1088L. Adjusted hi flow alarm from 25.5 to 26.1 L/s. Hihi flow alarm remains the same. | Newmarket Well 1 & 2 | 2025-12-30
CENTRAL | December | NMW12- Silicate Tank 1 Level OOR. Interlocked Silicate Pumps. Called Donald M. Requested to disable OOR alarm and clear it. Silicate Pump 1 started up in duty 1. | Newmarket Well 1 & 2 | 2025-12-16
CENTRAL | December | Station and equipment check Took grabs @ 9:30 am (running) Treated Total: 2.98 mg/l Treated Free: 0.14 mg/l Analyzer Treated Total: 2.94 mg/l Analzer Treated Free: 0.14 mg/l All other readings on PD sheets shared online folder Changed CL17 reagents on Influent free analyzer and treated free analyzer Chemicals/reagents ok Ops normal | Newmarket Well 1 & 2 | 2025-12-19
CENTRAL | December | Onsite to complete assigned work orders: Station check completed H/S inspection Station/equipment- Ok | Newmarket Well 14 | 2025-12-18
CENTRAL | December | General housekeeping Ops normal | Newmarket Well 1 & 2 | 2025-12-18
CENTRAL | December | Station and equipment check Took grabs @ 8:30 am Treated Total: 3.40 mg/l Treated Free: 0.15 mg/l Changed CL17 reagent ?treated total/free? Chemicals/reagents ok General housekeeping complete as per workorder Ops ok | Newmarket Well No. 15 | 2025-12-12
CENTRAL | December | Station and equipment check Took in-house operational sample and grabs @ 8:30 am (running) Treated Total: 3.42 mg/l Treated Free: 0.16 mg/l No adjustments required All other readings on PD sheets Placed well in manual ?off? until we get silicate delivery Well can be run as needed Will also need ammonia top up and cylinder change Swapped chlorine injector 2 with new rebuilt (ejector) Ops normal | Newmarket Well No. 15 | 2025-12-15
CENTRAL | December | Accidentally timed into elog, was not on-site at 07:15 on December 14 2025. | Newmarket Well No. 15 | 2025-12-14
CENTRAL | December | Notified by ROC that AMM tk1 ?valve failed to close? on tank rotation. Valve has closed as tank 2 is open and tanks did not equalize. Tried rotating tanks to cycle valves, alarms continue to trigger but tank 2 is open and available. Placed AMM tk1 valve in manual to prevent alarm from continue to trigger. Returned W15 to auto. | Newmarket Well No. 15 | 2025-12-14
CENTRAL | December | Restarted the Operator Interface Terminal at 1435 Hrs. Contacted the Remote Operations Center before restarting. Well was off. Done at 1438 Hrs. | Newmarket Well No. 15 | 2025-12-10
CENTRAL | December | Station and equipment check Take weekly BacT samples W11439265 and grabs @ 10:30 am Treated Total: 3.37 mg/l Treated Free: 0.16 mg/l All other readings on PD sheets, no adjustments required Chemicals/reagents ok Ops normal | Newmarket Well No. 15 | 2025-12-10
CENTRAL | December | Station and equipment check Took grabs @ 8:10 am (running) Treated Total: 3.34 mg/l Treated Free: 0.15 mg/l All other readings on PD sheets Changed chlorine cylinder with Joe D Changed "element" tubing on silicate pump 2 and placed back into auto duty oit screen not working, emailed John D Ops normal | Newmarket Well No. 15 | 2025-12-05
CENTRAL | December | Station and equipment check Take grabs and in-house operational samples at 8:30 am (running) Treated Total: 3.40 mg/l Treated Free: 0.15 mg/l All other readings on PD sheets shared online folder No adjustments required Changed CL17 reagent on Effluent Free analyzer chemicals/reagents ok Ops normal | Newmarket Well No. 15 | 2025-12-08
CENTRAL | December | Station and equipment check Took grabs and in- house operational sample @ 8:40 am Treated Total: 3.38 mg/l Treated Free: 0.14 mg/l All other readings on PD sheets No adjustment needed Ops normal | Newmarket Well No. 15 | 2025-12-01
CENTRAL | December | Top up ammonia tank 2 Yorknet onsite pulling fibre optic cable Station ops normal | Newmarket Well No. 15 | 2025-12-02
CENTRAL | December | Topped up delicate day tank. 196L to 381 L. | Newmarket Well No. 15 | 2025-12-02
CENTRAL | December | Station and equipment check Take weekly BacT sample and grabs @ 8:35 am Treated Total: 3.30 mg/l Treated Free: 0.13 mg/l chemicals/reagents ok Ops normal | Newmarket Well No. 15 | 2025-12-03
CENTRAL | December | Station and equipment check Take weekly BacT sample W11470548 and grabs @ 8:55 am Treated Total: 2.97 mg/l Treated Free: 0.12 mg/l All other readings on PD sheets Changed CL17 reagent ?influent free? analyzer Chemicals/reagents ok Ops normal | Newmarket Well No. 15 | 2025-12-22
CENTRAL | December | Onsite to deliver silicate to day tank and replace right chlorine cylinder with Jason G. No issues. | Newmarket Well No. 15 | 2025-12-16
CENTRAL | December | Informed ROC (Connor S) onsite to assist Lee F and complete Maximo workorders Cleaned ALL analyzers while in Cal mode Readings all returned to normal verified via grabs, will re verify readings at next station check JHSC inspection complete no issues Top up ammonia tank 1 and drop off extra ammonia bags Chemical system inspection ok | Newmarket Well No. 15 | 2025-12-17
CENTRAL | December | Check oil around motor base Logo motor Remove lid found oil under lid ring cleaned wiped down motor and well head Oil right to max point false line on glass reading below min line Operations to keep an eye on in will check back in a week | Newmarket Well No. 15 | 2025-12-17
CENTRAL | December | Station and equipment check Took grabs @ 8:15 am (off) Treated Total: 2.30 mg/l Treated Free: 0.06 mg/l Chemicals/reagents ok Ops normal | Newmarket Well No. 15 | 2025-12-24
CENTRAL | December | Station and equipment check Took grabs @ 8:25 am (off) Treated Total: 2.60 mg/l Treated Free: 0.05 mg/l All other readings on PD sheets Also complete Maximo workorder silicate line flush, air in lines flushed and conducted drawdown - all ok Will monitor at next auto run Chemicals/reagents ok Ops normal | Newmarket Well No. 15 | 2025-12-19
CENTRAL | December | Topped up silicate 251 to 385 L. | Newmarket Well No. 15 | 2025-12-30
CENTRAL | December | Topped up silicate day tank about 140 L. | Newmarket Well No. 15 | 2025-12-23
CENTRAL | December | Adjusted chlorine dosing loop update from 300 seconds to 340 seconds. Influent free chlorine readings seem to be chasing setpoint. | Newmarket Well No. 15 | 2025-12-24
CENTRAL | December | 11:10 Well VFD Fault (9081) reset (auto on) Station Check (no other issues found) Input data to PWQ 12:02 Verified CL17s (mg/l) Influent: Free Grab 2.94, A 2.87 Effluent: Free Grab 2.80, A 2.74 Treated: Free Grab 0.10, A 0.14 Total Grab 3.26, A 3.20 Ammonia Tank #2 (top up) 12:15 #11483430 samples | Newmarket Well No. 15 | 2025-12-29
CENTRAL | December | Station and equipment check Take weekly BacT sample W11454707 and grabs @ 14:10 pm (running) Treated Total: 3.00 mg/l Treated Free: 0.12 mg/l Ran in manual to get sample, turned manual off until maintenance can top up well motor oil Chemicals/reagents All other readings on PD sheets Ops normal | Newmarket Well No. 15 | 2025-12-16
CENTRAL | December | Onsite to change chlorine cylinder w/ Jerry Z Left side Ops normal | Newmarket Well No. 15 | 2025-12-23
CENTRAL | December | Completed work orders, informed ROC (Gluzen) Chlorine inspection - visual only Chlorine leak test verified and reset All ok Ops normal | Newmarket Well No. 15 | 2025-12-18
CENTRAL | December | Station and equipment check Take weekly BacT sample W11439265 and grabs @ 11:20 am Treated Total: 2.68 mg/l Treated Free: 0.12 mg/l All other readings on PD sheets shared online folder Changed CL17 reagent ?effluent free? Chemicals/reagents ok Also complete monthly maximo workorders General housekeeping, removed garbage from site Ops normal | Newmarket Wells 13-16 | 2025-12-10
CENTRAL | December | Station and equipment check Take in-house operational sample and grabs @ 11:50 am (not running) Treated Total: 2.80 mg/l Treated Free: 0.10 mg/l No adjustments required Topped up ammonia tank 2 Chemicals/reagents ok Ops normal | Newmarket Wells 13-16 | 2025-12-15
CENTRAL | December | Station and equipment check Took grabs @ 10:20 am Treated Total: 2.87 mg/l Trreated Free: 0.12 mg/l Chemicals/reagents ok Ops normal | Newmarket Wells 13-16 | 2025-12-12
CENTRAL | December | Informed ROC (Adeela K) will be completing monthly maximo workorders CL2 leak test Analyzer maintenance Chemical system inspection Ops normal | Newmarket Wells 13-16 | 2025-12-11
CENTRAL | December | Grease well 13 motor 16 well is disconnected for pulling well pump | Newmarket Wells 13-16 | 2025-12-05
CENTRAL | December | Station and equipment check all ok Took grabs and in-house operational samples @ 11:05 am Treated Total: 2.74 mg/l Treated Free: 0.10 mg/l No adjustments needed Chemical/reagents ok General housekeeping Ops normal | Newmarket Wells 13-16 | 2025-12-01
CENTRAL | December | Informed ROC. Treated total chlorine analyzer-reading was intermittently dropping. ROC turned off the well. Changed the motor, cam, pinch plates, pinch tubes and optical sensor. Put back in service and reading was stable. ROC run the well. We will observe for couple of days. All alarms were cleared after the job. No other issues encountered. | Newmarket Wells 13-16 | 2025-12-09
CENTRAL | December | Onsite to replace check valve on ammonia pump 2, now back in service Also complete Maximo workorders Instrumentation onsite Wells manual OFF | Newmarket Wells 13-16 | 2025-12-09
CENTRAL | December | Station and equipment check Take weekly BacT samples and grabs @ 9:15 am Treated Total: 2.53 mg/l Treated Free: 0.12 mg/l Raw sample for well 16 was taken at 9:05 am before well disconnected for maintenance LOTO Topped up ammonia tank 1 Chemicals/reagents ok Well 13 changed to Duty 1 Ops normal | Newmarket Wells 13-16 | 2025-12-03
CENTRAL | December | Station and equipment check Took grabs and in-house operational sample @ 11:15 am(running) Treated Total: 2.54 mg/l *adjusted analyzer to match grabs Treated Free: 0.12 mg/l All other readings on PD sheets shared online folder Found broken spring on check valve on Ammonia P2, will be OOS until can be replaced Ammonia P1 duty 1 Chemicals/reagents ok Ops normal | Newmarket Wells 13-16 | 2025-12-08
CENTRAL | December | Delivered silicate to bulk tank. About 100 L | Newmarket Wells 13-16 | 2025-12-02
CENTRAL | December | Grease bottom motor bearings Well not running couldn?t grease | Newmarket Wells 13-16 | 2025-12-02
CENTRAL | December | Station and equipment check Took grabs @ 11:30 am Treated Total: 2.56 mg/l Treated Free: 0.13 mg/l Chemicals/reagents ok Placed nmkt wells 1,2 and 13 in manual for Lee F to grease bearings. All back to auto Ops normal | Newmarket Wells 13-16 | 2025-12-05
CENTRAL | December | On site with Sean Peoples and Jason Garnett to disconnect Well #16 pump motor. Motor starter locked out and motor disconnected. | Newmarket Wells 13-16 | 2025-12-03
CENTRAL | December | Cylinder change w/ Joe D (right bank) Checked for leaks found none Ops normal | Newmarket Wells 13-16 | 2025-12-09
CENTRAL | December | Station and equipment check Take weekly BacT sample W11470548 and grabs @ 10:25 am Treated Total: 2.73 mg/l Treated Free: 0.10 mg/l All other readings on PD sheets shared online folder No adjustments to analyzers required Topped up Ammonia tank 1 Chemicals/reagents ok Trouble shoot silicate pump 1 and found diaphragm is damaged, will replace Silicate pump 1 remains isolated and manual off OOS until repair, informed ROC and team Station ops otherwise normal | Newmarket Wells 13-16 | 2025-12-22
CENTRAL | December | Replace diaphragm on Silicate P1, now back in service Drop off ammonia bags x4 Station ops normal | Newmarket Wells 13-16 | 2025-12-23
CENTRAL | December | Station and equipment check Took grabs @ 10:55 am Treated Total: 2.78 mg/l Treated Free: 0.12 mg/l No adjustments required, all other readings on PD sheets shared online folder Topped up drip oil on both wells Changed CL17 reagent "treated free" Chemicals/reagents ok Ops normal | Newmarket Wells 13-16 | 2025-12-19
CENTRAL | December | Station Check (no issues found) Input data to PWQ 8:30 Verified CL17s (mg/L) Influent: Free Grab 2.86, A 2.86 Effluent: Free Grab 2.38, A 2.41 Treated: Free Grab 0.08, A 0.12 Total Grab 2.84, A 2.78 (new reagents) 8:40 #11483430 samples treated & 16 raw, 9:15 well 13 raw | Newmarket Wells 13-16 | 2025-12-29
CENTRAL | December | Station and equipment check Take weekly BacT sample W11454707 and grabs @ 10:40 am (Running) Treated Total: 2.80 mg/l Treated Free: 0.12 mg/l All other readings on PD sheets, no adjustments required Chemicals/reagents ok *Ran well 13 in manual to get RAW sample, at 10:55 am Influent Free analyzer showed reading of 4.03 mg/l Took garb right away with SL1000 and pocket kit and verified false reading 10:55 am Influent Free grab SL1000 = 2.85 mg/l 10:55 am Influent Free grab pocket kit = 2.74 mg/l Analyzer trended down to normal, no effect on treated Ops normal | Newmarket Wells 13-16 | 2025-12-16
CENTRAL | December | Station and equipment check Took grabs @ 7:30 am (Off) Treated Total: 2.60 mg/l Treated Free: 0.08 mg/l Chemicals/reagents ok Ops normal | Newmarket Wells 13-16 | 2025-12-24
CENTRAL | December | Added 750 L to silicate bulk tank. | Newmarket Wells 13-16 | 2025-12-16
CENTRAL | December | Onsite to drop off silicate. 2699 L to 2821 L. Replaced chlorine cylinder bank 1 with Danielle Z. Topped up well 16 oil reserve from 1/2. | Newmarket Wells 13-16 | 2025-12-30
CENTRAL | December | General housekeeping Ops normal | Newmarket Wells 13-16 | 2025-12-18
WEST | December | -on site for station check -pumps running/chamber dry -JHSC inspection completed | Nobleton Booster Pumping Station | 2025-12-12
WEST | December | -pumps running/ chamber dry | Nobleton Booster Pumping Station | 2025-12-15
WEST | December | Onsite to complete station check. No issues, pump running. | Nobleton Booster Pumping Station | 2025-12-05
WEST | December | -on site for station check -chamber dry/pumps running | Nobleton Booster Pumping Station | 2025-12-08
WEST | December | Onsite to complete station check. No issues, pump running. | Nobleton Booster Pumping Station | 2025-12-01
WEST | December | -on site for station check -pump running/chamber dry | Nobleton Booster Pumping Station | 2025-12-19
WEST | December | Station Check Pump running | Nobleton Booster Pumping Station | 2025-12-24
WEST | December | On-site for station check Did visual inspection of chamber and pump Chamber floor dry, No issues | Nobleton Booster Pumping Station | 2025-12-22
WEST | December | -on site to troubleshoot analyzer -found PRV on unit clogged - unclogged lines and tested - reset analyzer pressure to 50 OPA -topped free electrolyte -took grab at 14:40 -adjusted analyzer free: 1.43mg/l -adjusted analyzer total: 1.67mg/l | Nobleton North Elevated Tank | 2025-12-12
WEST | December | -on site to complete station check and collect weekly bacti W11438418 -checked trends: all ok -took reading in PWQ: all ok -verified analyzer 09:20 -analyzer free: 0.95mg/l grab: 1.45mg/l - adjusted -analyzer total: 1.60mg/l grab: 1.58mg/l -reagents all ok -equipment all ok | Nobleton North Elevated Tank | 2025-12-10
WEST | December | -on site to verify analyzer -took grab 09:15 -analyzer free: 2.24mg/l grab: 1.56mg/l - adjusted -analyzer total: 1.98mg/l grab: 1.94mg/l | Nobleton North Elevated Tank | 2025-12-15
WEST | December | Station Check (no issues found) Input data to PWQ 9:10 Verified Depolox (mg/L) Free: Grab 1.53, A 0.98 (adjusted to match grabs) Total: Grab 1.76, A 1.76 9:20 #11419165 weekly bact. | Nobleton North Elevated Tank | 2025-12-03
WEST | December | -on site to verify analyzer 13:55 -analyzer free: 1.16mg/l grab: 1.43mg/l -analyzer total: 1.76mg/l grab: 1.70mg/l - adjusted -topped up reagents | Nobleton North Elevated Tank | 2025-12-19
WEST | December | -on site for year end inventory and additional housekeeping | Nobleton North Elevated Tank | 2025-12-23
WEST | December | Onsite to troubleshoot flow issues for Chlorine analyzer. Informed ROC. Put the device in Calibration mode. Removed the back pressure valve and found it was dirty. Added inlet valve to free chlorine analyzer to regulate the flow. Put the back pressure valve back in service. Put everything back to service. All the related alarms were cleared. No issues. Informed ROC, armed the building and left the site. | Nobleton North Elevated Tank | 2025-12-16
WEST | December | On site to complete the following WOs: - portable generator run test - H$S inspection - Chlorine analyzer cleaning/maintenance - Heat trace system instruction - Low temp alarm test Notified ROC before starting WOs Cleaned chlorine analyzer (1400 hrs to 1431 hrs) 1436 hrs: Returned analyzer to service Zeroed and calibrated analyzer Adjusted analyzer reading to 1.30 mg/l Tested generator by turning utility off from the breaker and connected generator power to station, no issues Cleared all alarms and returned station to normal. Notified ROC before leaving site | Nobleton North Elevated Tank | 2025-12-18
WEST | December | On site for station check, collection of weekly bacT and samples Reviewed scad, duty not active Visual inspection in and around station Verification of equipment and instrumentation Verified chlorine analyzers readings. Outstanding alarm: None Chlorine residual @ 9:34 hrs Grab Analyzer reading ? FCL = 1.55 mg/l FCL = 1.39 mg/l ? TCL = 1.74 mg/l. TCL = 1.86 mg/l Adjusted total chlorine analyzer reading based on multiple grabs = 1.74 mg/l Adjusted free chlorine analyzer reading based on average of 3 grabs ( 1.60, 1.54,and 1.51 mg/l) = 1.55 mg/l UPS beeping notified PCS on call (Yash), disregard battery replacement in the process. No issues | Nobleton North Elevated Tank | 2025-12-22
WEST | December | -on site for station check and weekly bacti W11483482 -checked trends: all ok -entered readings in PWQ: all ok -verified analyzer 08:50 -analyzer free: 1.26mg/l grab: 1.54mg/l - adjusted -analyzer total: 1.55mg/l grab: 1.74mg/l - adjusted -reagents all ok | Nobleton North Elevated Tank | 2025-12-29
WEST | December | Station Check (no issues found) 12:35 Free: Grab 1.40, A 1.36 Total: Grab 1.76, A 1.81 12:40 #11454759 sample | Nobleton North Elevated Tank | 2025-12-16
WEST | December | -on site responding to temp alarm -heater not running - adjusted thermostat - started -alarm cleared -heat trace also all o | Nobleton South Elevated Tank | 2025-12-12
WEST | December | -on site re-verify analyzer and inspect analyzer -adjusted flow -took chlorine grab 13:15 -analyzer free: 1.96mg/l grab: 1.70mg/l - adjusted -analyzer total: 1.88mg/l grab: 1.91mg/l | Nobleton South Elevated Tank | 2025-12-10
WEST | December | -on site for station check and weekly bacti W11438417 -checked trends: all ok -entered readings in PWQ: all ok -verified analyzer 09:50 -analyzer free: 1.27mg/l grab: 1.50mg/l - adjusted -analyzer total: 1.66mg/l grab: 1.73mg/l - adjusted -reagents all ok -equipment all ok | Nobleton South Elevated Tank | 2025-12-10
WEST | December | Station Check (no issues found) Input data to PWQ 9:50 Verified Depolox (mg/l) Free: Grab 1.45, A 1.33 (adjusted to match grabs) Total: Grab 1.80, A 1.74 10:00 #11419165 weekly bact. | Nobleton South Elevated Tank | 2025-12-03
WEST | December | -on site to drop off distilled and topped up KI reagent -no issues | Nobleton South Elevated Tank | 2025-12-19
WEST | December | On site for station check, collection of weekly bacT and samples Reviewed scad, duty not active Visual inspection in and around station Verification of equipment and instrumentation Verified chlorine analyzers readings. Outstanding alarm: None Chlorine residual @ 11:21 hrs Grab Analyzer reading ? FCL = 1.64 mg/l FCL = 1.51 mg/l ? TCL = 1.90 mg/l. TCL = 1.93 mg/l Adjusted total chlorine analyzer reading based on multiple grabs = 1.90 mg/l Adjusted free chlorine analyzer reading based on average of 3 grabs (1.58, 1.67and 1.63 mg/l) = 1.64 mg/l No issues | Nobleton South Elevated Tank | 2025-12-22
WEST | December | -on site to complete following work orders -generator run: all ok/topped up -JHSC inspection: all ok -low temp alarm: all ok -sump pump inspection: all ok -heat traces inspection: all ok -cleaned and verified analyzer - unit need extensive cleaning -took chlorine grab 14:15 -free grab: 1.70mg/l - adjusted analyzer -total grab: 2.10mg/l analyzer: 2.13mg/l - all ok | Nobleton South Elevated Tank | 2025-12-17
WEST | December | On site to perform PM on heat trace systems. Checked voltage and current on all systems. All operating in good condition. | Nobleton South Elevated Tank | 2025-12-31
WEST | December | -on site for station check and weekly bacti W11483482 -checked trends: all ok -entered readings in PWQ: all ok -verified analyzer 09:20 -analyzer free: 1.52mg/l grab: 1.63mg/l -adjusted -analyzer total: 1.88mg/l grab: 1.86mg/l -reagents all ok -equipment all ok | Nobleton South Elevated Tank | 2025-12-29
WEST | December | -on site for station check -checked trends: all ok | Nobleton Well 2 | 2025-12-12
WEST | December | Station Check (no issues found) Input data to PWQ 13:35 Verified Depolox (mg/l) Free: Grab 1.42, A 1.10 (adjusted to match grabs) Total: Grab 1.75, A 1.68 (adjusted to match grabs) (topped up reagents (KI & acetate) 13:45 #11454759 sample | Nobleton South Elevated Tank | 2025-12-16
WEST | December | -on site for station check and to collect weekly bacti W11438417 -checked trends: all ok -entered readings in PWQ: all ok -well locked out due to influent analyzer crashed -took grab at 10:45: 1.89mg/l -adjusted flow and primed pump -analyzer returned to 1.94mg/l grab- all ok -will return to sample | Nobleton Well 2 | 2025-12-10
WEST | December | Onsite to repair faulty keypad on Influent AIT Informed ROC. Operations onsite and placed duty manual off Repaired keypad Took grabs and adjusted A = 1.87mg/L G = 1.87mg/L Informed ROC and operations Armed building and left site | Nobleton Well 2 | 2025-12-15
WEST | December | -on site to finish station check -enter readings in PWQ: all ok -verified analyzer -influent 13:20: 1.70mg/l grab: 1.71mg/l -effluent 13:25: 1.47mg/l grab: 1.70mg/l - adjusted -total grab: 1.86mg/l -reagents all ok | Nobleton Well 2 | 2025-12-12
WEST | December | -on site for station check -checked trends: all ok -entered readings PWQ: all ok -verified analyzers -influent 10:10: 1.92mg/l grab: 1.90mg/l -effluent 10:15: 1.90mg/l grab: 1.72mg/l - adjusted -total grab: 1.98mg/l -reagents all ok | Nobleton Well 2 | 2025-12-15
WEST | December | -on site to collect weekly bacti W11438417 -verified effluent 12:15 analyzer: 1.69mg/l grab: 1.72mg/l -total grab: 1.99mg/l -reagents all ok | Nobleton Well 2 | 2025-12-10
WEST | December | Station Check (no issues found) Input data to PWQ 11:40 Verified CL17s (mg/l) Influent: Free Grab 1.94, A 1.99 Effluent: Free Grab 1.90, A 1.86 Total Grab 2.18 11:50 #11419165 weekly bact. | Nobleton Well 2 | 2025-12-03
WEST | December | Work orders: #114113397 jhs #11415301 silicate maint #11435045 dechlor #11415349 cl2 sys. maint #11413085 turb. #11413118 scrubber samples #11412929 prv #11413011 Deep well #11413316 cl17 maint. #11413042 cl2 leak 11:50 (after maint) Influent: Free Grab 1.88, A 1.90 mg/l Effluent: Free Grab 1.83, A 1.81 mg/l | Nobleton Well 2 | 2025-12-02
WEST | December | Influent CL17 reagent change | Nobleton Well 2 | 2025-12-09
WEST | December | Onsite for station check Duty not active Checked residuals mg/L Influent @1122 Free analyzer 1.75 grab 1.86 Effluent @1120 Free analyzer 1.47 grab 1.49 Total grab 1.72 Topped up silicate tank | Nobleton Well 2 | 2025-12-05
WEST | December | Onsite for station check Duty active Checked residuals mg/l Effluent @1040 Free analyzer 1.85 grab 1.86 Total grab 2.16 Influent @1044 Free analyzer 1.94 grab 1.99 Stopped well in manual afterwards | Nobleton Well 2 | 2025-12-01
WEST | December | -on site for station check -checked trends: all ok -entered readings in PWQ: all ok -verified analyzers -influent 11:00: 1.83mg/l grab: 1.88mg/l -effluent 11:05: 1.63mg/l grab: 1.68mg/l -total: 2.11mg/l -changed effluent reagents -changed cylinder 63.9kg/ - 132kg -created W11497075 for influent analyzer buttons | Nobleton Well 2 | 2025-12-08
WEST | December | Station Check (no issues found) Input data to PWQ 9:40 Verified CL17s (mg/l) Influent: Free Grab 2.02, A 1.97 Effluent: Free Grab 1.92, A 1.94 Total Grab 2.58 9:45 #11454759 samples | Nobleton Well 2 | 2025-12-16
WEST | December | -on site for station check -checked trends: all ok -entered readings in PWQ: all ok -cleaned NTU analyzer -verified analyzers -influent 12:45: 1.78mg/l grab: 1.75mg/l -effluent 12:50: 1.64mg/l grab: 1.56mg/l - adjusted -total grab: 1.81mg/l -reagents all ok | Nobleton Well 2 | 2025-12-19
WEST | December | Station Check (no issues found) Input data to PWQ 11:45 Verified CL17s (mg/l) Influent: Free Grab 1.89, A 1.88 Treated: Free Grab 1.78, A 1.83 Total Grab 2.20 | Nobleton Well 2 | 2025-12-24
WEST | December | -on site for year end inventory and housekeeping -disturbed NTU sample line - caused spike - NTU returned to normal | Nobleton Well 2 | 2025-12-23
WEST | December | -on site to complete station check and collect weekly bacti W11483482 -checked trends: all ok -entered readings in PWQ: silicate dose low - primed pumps -issue with pump 2 - will leave in man/off -verified analyzer -influent 14:50: 1.92mg/l grab:1.95mg/l -effluent 14:55: 1.85mg/l grab: 1.85mg/l -total grab: 2.18mg/l -reagents all ok -equipment all ok | Nobleton Well 2 | 2025-12-29
WEST | December | On site for station check and collection of weekly bacT sample Reviewed scada, duty active, well running in auto Visual inspection in and around station Verification of equipment and instrumentation. Verified chlorine analyzers readings. Outstanding alarm: none Chlorine residual @ 1242 hrs Influent: Grab: ? FCL= 2.02 mg/l. ? Analyzer: 1.98 mg/l Effluent FCL @ 1250 hrs Grab ? FCL = 1.82 mg/l ? TCL = 2.46 mg/l ? Analyzer = 1.78 mg/l Chemicals: Chlorine System: Duty1: pump1, chlorinator1 Chlorinator1 @ 43% BP2 Discharge Press: 1,420 kpa Dosage factor: 86% Standby: BP1 Chlorinator1 Silicate System: Duty1: Pump2 Pumps speed: 46% Dosage: 55.8 mL/min Disch. Pressure: 650 kpa Pump2 on standby System pressure: 554 kpa Recorded station readings into pwq data sheet No issues | Nobleton Well 2 | 2025-12-22
WEST | December | On site responding to low influent lockout Placed dechlor pucks in chamber started back flushing at 14:56hrs @~11L/s Primed both hypo pumps some air in the line but did not notice any leaks. Stopped back flushing at 15:12 restarted well | Nobleton Wells 3 & 7 | 2025-12-11
WEST | December | -on site for station check and weekly bacti W11438417 -checked trends: all ok -entered readings in PWQ: all ok -verified analyzer -influent 12:35: 2.07mg/l grab: 1.86mg/l - adjusted -effluent 12:45: 1.57mg/l grab: 1.54mg/l -total grab: 1.74mg/l -reagents all ok -found minor leak on pump 1 quick connect- tightened and clean - all ok -equipment all ok | Nobleton Wells 3 & 7 | 2025-12-10
WEST | December | -on site responding to low influent lockout and NTU fault -began backflush/dechlor 09:50 to 10:10 -inspected hypo pump 2 - no visible issue -cleaned NTU flow sensor - all ok -entered readings in PWQ: all ok -verified analyzer -influent 11:05: 1.77/l grab: 1.87mg/l - adjusted -effluent 11:00: 1.92mg/l grab: 1.85mg/l - adjusted -total grab: 2.07mg/l -reagents all ok | Nobleton Wells 3 & 7 | 2025-12-12
WEST | December | On site to reinstall and test chlorine containment flood float switch. | Nobleton Wells 3 & 7 | 2025-12-11
WEST | December | -on site to complete station check -checked trends -primed hypo pump 2 and man/started well - all ok -entered readings in PWQ: all ok -verified analyzer -influent analyzer 13:15: 1.83mg/l grab: 1.80mg/l -effluent analyzer 13:20: 1.34mg/l grab: 1.38mg/l -total grab: 1.58mg/l -reagents all ok -topped up hypo - 158/153 - 224/219L | Nobleton Wells 3 & 7 | 2025-12-15
WEST | December | Onsite to replace faulty flowmeter on turbidity analyzer. Used the calibration mode and replaced flowmeter. Put it back to service. All the related alarms were cleared. No issues. Informed ROC, armed the building and left the site. | Nobleton Wells 3 & 7 | 2025-12-15
WEST | December | Onsite for station check Duty not active Checked residuals mg/L Influent @1121 Free analyzer 1.13 grab 1.13 Effluent @1226 Free analyzer 1.20 grab 1.24 Total grab 1.42 Reagents ok Topped up silicate tanks | Nobleton Wells 3 & 7 | 2025-12-05
WEST | December | Onsite for station check Duty active Checked residuals mg/l @1004 Effluent Free analyzer 1.40 grab 1.43 Total grab 1.64 @1008 Influent Free analyzer 1.85 grab 1.99 Adjusted influent analyzer based an average of multiple grabs Rotated hypo pumps Stopped well and placed in manual off afterwards | Nobleton Wells 3 & 7 | 2025-12-01
WEST | December | -on site to meet maintenance for containment installation -pumped out tanks -Dan B removed LITs -tanks removed, new containment installed -tanks and pumps reconnected -tested system and restarted well -topped up tanks 93/91 L -well interlocked at 12:02 due high effluent -backflushed/dechlorinated at 12:05 - no high residual to system -took effluent free grab at 12:05 - 3.80mg/l analyzer 4.13mg/l - unable to adjust - will monitor -backflushed until 12:35 - 37800m3 -took effluent grab at 13:45: 1.62mg/l - analyzer 1.65mg/l -received hypo top up 90/90L - 237/234L -inspected tanks after top up - all ok | Nobleton Wells 3 & 7 | 2025-12-09
WEST | December | Station Check (no issues found) input data to PWQ 10:40 Verified CL17s (mg/l) Influent: Free Grab 1.69, A 1.70 Effluent: Free Grab 1.55. A 1.53 Total Grab 1.73 10:55 #11419165 weekly bact. samples Hypo day tanks not topped up in preparation for containment work on Tuesday | Nobleton Wells 3 & 7 | 2025-12-03
WEST | December | -on site for station check -checked trends: all ok -entered readings in PWQ: all ok -verified analyzers -influent 12:00: 1.22mg/l grab: 1.27mg/l -effluent 12:05: 1.37mg/l grab: 1.42mg/l -total: 1.59mg/l -reagents all ok -did not top up hypo - drawing tanks down for removal for tomorrow -NTU analyzer flow sensor not working | Nobleton Wells 3 & 7 | 2025-12-08
WEST | December | 10:25 Verified CL17s (mg/l) Influent: Free Grab 1.65, A 2.01 (adjusted to match grabs) Effluent: Free Grab 1.05, A 1.09 | Nobleton Wells 3 & 7 | 2025-12-02
WEST | December | Responded to Low Influent Lock out 10:05 Backflush start at 6 l/s 10:45 Backflush stop 10:55 well manual on (operating normally) will return to auto remotely | Nobleton Wells 3 & 7 | 2025-12-04
WEST | December | Containment for hypo Installed pvc containment tank for hypo tanks | Nobleton Wells 3 & 7 | 2025-12-09
WEST | December | -on site for station check and weekly bacti W11483482 -well interlocked due low low influent -backflushed/dechlorinated 09:50 -found pump 2 discharge fitting cracked - replaces -topped up hypo 144/140 - 225/221 -verified analyzer -influent 10:55: 1.95mg/l grab: 1.92mg/l -effluent 11:00: 1.66mg:l grab: 1.62mg/l -total grab: 1.76mg/l -reagents all ok | Nobleton Wells 3 & 7 | 2025-12-29
WEST | December | Work orders: #11423391 Turb. cal #11423389 silicate #11421685 Generator: Start Hrs.: 368.5 Start Time: 12:10 Start Fuel: 82.9cm/872L End Hrs: 869.6 End Time 13:10 End Fuel: 82.6cm /868L 12:40 (30 min check) eng. temp. 185F, oil pres. 57psi, oil temp. 186F, 600v, 9 amps, 60hz #11422060 CL17 maint 10:15 (mg/l) Influent: Free Grab 1.59, A 1.63 Effluent: Free Grab 1.59, A 1.57 12:15 #11421467 Hypo (pulled lances again (to clear blockage) after low influent lockout and back flush) #11421514 prv #11423251 hi/lo temp #11423297 vent #11423357 jhs | Nobleton Wells 3 & 7 | 2025-12-17
WEST | December | Station Check (no issues found) Input data to PWQ 8:50 Verified CL17s (mg/l): Influent: Free Grab 1.98, A 1.98 Effluent: Free Grab 1.52, A 1.57 Total Grab 1.92 Hypo day tank top up 9:00 #11454759 samples 10:30 bulk hypo delivery | Nobleton Wells 3 & 7 | 2025-12-16
WEST | December | On site for station check and collection of weekly bacT samples Reviewed scada, duty not active, Started well in manual at 45% speed @ 24 l/s Vilsual inspection in and around station Verification of equipment and instrumentation Verified chlorine analyzers readings. Outstanding Alarms: None Chlorine residual @ 1608 hrs Influent: ? FCL= 1.90 mg/l. ? Analyzer: FCL: 1.87 mg/l Effluent FCL @ 1608 hrs Grab ? FCL = 1.21 mg/l ? TCL = 1.42 mg/l ? Analyzer = 1.20 mg/l wet Changed chlorine analyzers reagents Returned well 7 to auto, returned pump speed to auto, stopped well after sample collection Residual stablized ~ inf FCL analyzer at 2.30 and Eff FCL analyzer at 1.88 mg/l. Notified ROC No issues on site. | Nobleton Wells 3 & 7 | 2025-12-22
WEST | December | -on site for station check -checked trends all ok -entered readings in PWQ: all ok -topped up hypo: 199/195L- 234/231L -verified analyzer -influent 11:40: 1.38mg/l grab: 1.40mg/l -effluent 11:45: 1.52mg/l grab: 1.55mg/l -total grab: 1.77mg/l -reagents all ok | Nobleton Wells 3 & 7 | 2025-12-19
WEST | December | -on site for year end inventory and additional housekeeping -noticed significant build around around dice block discharge fitting cleaned/tightened and man/started well to investigate -no issues | Nobleton Wells 3 & 7 | 2025-12-23
WEST | December | On-site for hypo tanks top up ~ 200 L | Nobleton Wells 3 & 7 | 2025-12-22
WEST | December | Station Check (no issues found) Input data to PWQ 8:25 Verified CL17s (mg/l) Influent: Free Grab 1.25. A 1.30 Treated: Free Grab 1.65, A 1.70 Total Grab 1.82 Hypo day tank top up 8:56 Well locked out on low influent, replace discharge tube on hypo pump 2 (pin hole leak), back flushed with dechlor 10:25 Back flush complete, returned well to auto on, operated normally | Nobleton Wells 3 & 7 | 2025-12-24
WEST | December | Filled silicate tank 33.40 to 67.08 cm | Nobleton Wells 3 & 7 | 2025-12-18
WEST | December | On site responding to silicate p1 leak alarm - replaced tubing restarted well | Nobleton Wells 5 & 6 | 2025-12-11
WEST | December | -on site for station check -checked trends: all ok -entered readings in PWQ -verified analyzers -influent 11:20: 1.67mg/l grab: 1.67mg/l -effluent 11:25: 1.62mg/l grab: 1.68mg/l - adjusted -total grab: 2.09mg/l -reagents all ok -equipment all ok | Nobleton Wells 5 & 6 | 2025-12-12
WEST | December | Onsite to repair faulty keypad on Influent AIT Informed ROC. Operations onsite and placed duty manual off Repaired keypad Took grabs and adjusted A = 1.88mg/L G = 1.90mg/L Informed ROC and operations Armed building and left site | Nobleton Wells 5 & 6 | 2025-12-15
WEST | December | -on site for station check and weekly bacti W11438417 -checked trends: all ok -entered readings PWQ: all ok -verified analyzer -influent 11:05: 2.60mg/l grab: 2.60mg/l -effluent 11:10: 1.74mg/l grab: 1.78mg/l -total grab: 2.09mg/l -reagents all ok -equipment all ok | Nobleton Wells 5 & 6 | 2025-12-10
WEST | December | -on site to run chemical lines -connected nasi pump 2 to injection point -tested pump and primed- no leaks, show flowing and healthy pressure -placed in auto and duty 1 - informed ROC and west team | Nobleton Wells 5 & 6 | 2025-12-15
WEST | December | -on site for station check -checked trends: -entered readings in PWQ: all ok -verified analyzers -influent 10:45: 2.67mg/l grab: 2.50mg/l - adjusted -effluent 10:50: 1.93mg/l grab: 1.90mg/l -total grab: 2.26mg/l -reagents all ok -equipment all ok | Nobleton Wells 5 & 6 | 2025-12-15
WEST | December | Onsite for station check Duty active Checked residuals mg/l Effluent @1124 Free analyzer 2.33 grab 2.32 Total grab 2.86 Influent @1129 Free analyzer 2.62 grab 2.99 Adjusted analyzer Deactivated duty afterwards | Nobleton Wells 5 & 6 | 2025-12-01
WEST | December | Work Orders: #11435178 Cl17 maintenance: Generated w/o #11500303 for Influent CL17 keypad repair Verified CL17s after maint. 11:05 Influent Free: Grab 1.92, A 1.97 mg/l Effluent Free: Grab 1.80, A 1.76 mg/l #11434277 dehumidier #11434291 hi/lo temp. #11434344 fuel spill #11433894 cl2 leak #11433914 PRV #11435107 silicate sys. maint. #11433874 CL2 emerg. #11433973 scrubber #11434159 jhs #11434478 Turb. #11433927 Generator Test: Pre-check complete Start Hrs: 256:22 End Hrs: 257:33 Start Time: 12:15 End Time: 13:19 Start Fuel: 93.4/91.0 cm, 973/947L End Fuel : 92.2/89.9 cm, 960/935L 30min. check: (oil pres. 56, temp. 178, 1804 rpm, 345volts, 54, amps, 60hz) | Nobleton Wells 5 & 6 | 2025-12-09
WEST | December | Station Check (no issues found) Input data to PWQ 12:55 Verified CL17s (mg/l) Influent: Free Grab 2.56, A 2.64 Effluent: Free Grab 1.78, A 1.82 Total Grab 2.40 Influent CL17 (new reagents) | Nobleton Wells 5 & 6 | 2025-12-03
WEST | December | -on site for station check -checked trends: all ok -entered readings in PWQ: -verified analyzers -influent 10:20: 1.77mg/l grab: 1.75mg/l -effluent 10:25: 1.73mg/l grab: 1.69mg/l -effluent total: 2.04mg/l -reagents all ok -equipment all ok | Nobleton Wells 5 & 6 | 2025-12-08
WEST | December | Onsite for station check Duty not active Checked residuals mg/L Influent @1319 Free analyzer 1.50 grab 1.45 Effluent @1322 Free analyzer 1.60 grab 1.69 Total grab 1.91 | Nobleton Wells 5 & 6 | 2025-12-05
WEST | December | Chlorine cylinder change with JM (A Side) | Nobleton Wells 5 & 6 | 2025-12-02
WEST | December | Station Check (no issues found) Input data to PWQ 10:50 Verified CL17s (mg/l) Influent: Free Grab 2.62, A 2.70 Effluent: Free Grab 1.87, A 1.90 Total Grab 2.56 11:00 #11454759 samples | Nobleton Wells 5 & 6 | 2025-12-16
WEST | December | Filled silicate tank 34.74 to 65.48 cm | Nobleton Wells 5 & 6 | 2025-12-18
WEST | December | Repaired chlorine room unit heater. | Nobleton Wells 5 & 6 | 2025-12-18
WEST | December | -on site to change cylinder - 60.6kg- 128kg | Nobleton Wells 5 & 6 | 2025-12-17
WEST | December | Station Check (no issues found) Input data to PWQ 11:00 Verified CL17s (mg/L): Influent: Free Grab 2.58, A 2.61 Treated: Free Grab 1.96, A 2.02 Total Grab 2.58 | Nobleton Wells 5 & 6 | 2025-12-24
WEST | December | -on site to complete station check -checked trends: all ok -entered readings in PWQ: all ok -verified analyzer -influent 09:50: 1.59mg/l grab: 1.49mg/l - adjusted -effluent 09:55: 1.75mg/l grab: 1.72mg/l -total grab: 2.06mg -reagents all ok -made followings adjustments to pump 1 to match pump - adjusted pump 2 to rpm display -pump 1 max flow adjust to 100 - 125 -adjusted drawdown on pump 1 90ml/min - 130ml/min -checked displays and rpm all ok - pump 1 has different roller- informed team lead -man/started well -completed additional housekeeping | Nobleton Wells 5 & 6 | 2025-12-19
WEST | December | -completed dosage calculation on Nasi pump 2 - 30mg/l - adjusted max flow to 180ml/min - pump speed 34-32% - placed well back to auto | Nobleton Wells 5 & 6 | 2025-12-19
WEST | December | -on site to clean NTU analyzer, year end inventory and additional housekeeping. | Nobleton Wells 5 & 6 | 2025-12-23
WEST | December | - placed silicate pump to into duty 1 - set max flow from 90ml/min to 170ml/min -will leave well in man/on - for testing | Nobleton Wells 5 & 6 | 2025-12-17
WEST | December | -on site for station check and weekly bacti W11483482 -checked trends: all ok -entered readings in PWQ: increased silicate does 32- 34% -verified analyzer -influent 14:25: 2.64mg/l grab: 2.68mg-l -effluent 14:30: 2.06mg/l grab: 2.09mg/l -total grab: 2.64mg/l -changed effluent reagents | Nobleton Wells 5 & 6 | 2025-12-29
WEST | December | On site for station check and collection of weekly bacT samples Reviewed scada, duty active, well 5 running in auto Visual inspection at site Verification of equipment and instrumentation Outstanding alarm: none Verified chlorine analyzers readings Chlorine residual @ 1352 hrs Influent FCL: Grab: 2.70 mg/l. Analyzer: 2.68mg/l @ 1400 hrs: Effluent FCL = 2.14 mg/l. Analyzer = 2.10 mg/l TCL = 2.74 mg/l Chemicals: Chlorine gas System Duty1: pump2, chlorinator2 Pumps speed: 79% Dosage Factor: 171% Disch. Press: 540 kpa Pump1 and Chlorinator on standby Silicate System: Duty1: Pump2 Pumps speed: 32% Dosage: 57.8 mL/min Disch. Pressure: 540 kpa Pump1 on standby System pressure: 619 kpa Recorded station readings into pwq data shee No issues | Nobleton Wells 5 & 6 | 2025-12-22
CENTRAL | December | On site to complete station check, collect operational samples, and collect weekly bacti sample (W11438487). Verified analyzers: Inlet Free chlorine @ 11:05 Grab: 0.03 mg/L Analyzer: 0.02 mg/L Total chlorine @ 11:05 Grab: 2.76 mg/L Analyzer: 2.71 mg/L Outlet Free chlorine @ 10:45 Grab: 0.05 mg/L Analyzer: 0.05 mg/L Total chlorine @ 10:45 Grab: 2.32 mg/L Analyzer: 2.30 mg/L -Entered data into PD sheet -Checked trends -Placed well 1 in manual off, then placed wells 1 and 2 in manual on | Queensville Elevated Tank | 2025-12-10
CENTRAL | December | On site to complete station check and collect weekly bacti sample (W11419127). Verified analyzers: Inlet Free chlorine @ 14:48 Grab: 0.08 mg/L Analyzer: 0.04 mg/L Total chlorine @ 14:48 Grab: 2.66 mg/L Analyzer: 2.64 mg/L Outlet Free chlorine @ 14:34 Grab: 0.07 mg/L Analyzer: 0.05 mg/L Total chlorine @ 14:43 Grab: 2.30 mg/L Analyzer: 2.23 mg/L -Entered data into PD sheet -Checked trends | Queensville Elevated Tank | 2025-12-03
CENTRAL | December | On site to complete PMs. Notified ROC of relevant alarms. -Completed JHSC inspection. All good -Completed portable generator test. All good -Inspected inlet/outlet heat trace systems: All setpoints are 5 degrees Celsius or above, heaters on as applicable, no alarms, all good -Tested high water level and low water level alarms via SCADA: all good -Inspected altitude valve: all good -Exercised and inspected manual valves: butterfly valve 00052704/TWR_HV2 found only partially open. It is the only valve labeled as opening clockwise in the tower. Tested to make sure valve was labeled correctly by running well 1 and 2 with the tower tie valve manually open in case of mislabeling. Notified ROC before conducting test. Valve is mislabeled, it opens counterclockwise. Returned wells 1/2 and tie valve to auto, notified ROC of end of test. Created a temporary sign to label the valve correctly. Otherwise all good -Performed maintenance on Depolox chlorine analyzers. Cleaned y-screens and flushed sample lines. Verified analyzers after cleaning: Inlet Free chlorine @ 11:49 Grab: 0.03 mg/L Analyzer: 0.02 mg/L Total chlorine @ 11:49 Grab: 2.82 mg/L Analyzer: 2.73 mg/L Outlet Free chlorine @ 11:44 Grab: 0.09 mg/L Analyzer: 0.05 mg/L Total chlorine @ 11:44 Grab: 2.22 mg/L Analyzer: 2.20 mg/L | Queensville Elevated Tank | 2025-12-17
CENTRAL | December | On site to complete station check and collect weekly bacti sample (W11469886). Verified analyzers: Inlet Free chlorine @ 11:46 Grab: 0.08 mg/L Analyzer: 0.04 mg/L Total chlorine @ 11:46 Grab: 2.16 mg/L Analyzer: 2.11 mg/L Outlet Free chlorine @ 11:32 Grab: 0.04 mg/L Analyzer: 0.05 mg/L Total chlorine @ 11:32 Grab: 2.26 mg/L Analyzer: 2.25 mg/L -Entered data into PD sheet -Checked trends | Queensville Elevated Tank | 2025-12-22
CENTRAL | December | On site to complete station check and collect weekly bacti sample (W11454721). -Placed wells 1 and 2 in manual-on Verified analyzers: Inlet Free chlorine @ 9:18 Grab: 0.05 mg/L Analyzer: 0.02 mg/L Total chlorine @ 9:18 Grab: 2.68 mg/L Analyzer: 2.72 mg/L Outlet Free chlorine @ 9:08 Grab: 0.10 mg/L Analyzer: 0.05 mg/L Total chlorine @ 9:08 Grab: 2.28 mg/L Analyzer: 2.25 mg/L -Entered data into PD sheet -Checked trends | Queensville Elevated Tank | 2025-12-16
CENTRAL | December | On-site for station check and collect sample. COC w111483444 Topped upboth inlet and outlet chlorine analyzer Acetate and KI reagents. 10:14 Tower level 83%. Tower filling at 67 l/s and draining at 64 l/s in flow-through mode. Verified analyzers (mg/l): 10:16 hrs. Inlet: Free chlorine grab: 0.02. Analyzer: 0.02. Total chlorine grab: 2.86/2.90/2.74. Analyzer: 2.63. Adjusted analyzer to match grab. 10:25 hrs. Outlet: Free chlorine grab: 0.09. Analyzer: 0.03. Total chlorine grab: 2.52/2.54/2.58. Analyzer: 2.22. Adjusted analyzer to match grab average. Collected sample. No other issues on site. | Queensville Elevated Tank | 2025-12-29
CENTRAL | December | On site to complete station check. Verified analyzers: Influent Free Chlorine @ 10:57 Grab: 2.98 mg/L Analyzer: 2.97 mg/L Effluent Free Chlorine @ 10:51 Grab: 2.80 mg/L Analyzer: 2.84 mg/L Treated Free Chlorine @ 10:31 Grab: 0.22 mg/L Analyzer: 0.23 mg/L Treated Total Chlorine @ 10:54 Grab: 3.34 mg/L Analyzer: 3.34 mg/L -Placed wells in manual-off -Notified ROC of generator test and relevant alarms -Completed monthly generator run test for portable contracted generator: Hours before test: 16565h 31m Test start: 11:13 On load @ 11:16 Off load @ 12:16 Test end: 12:17 Cooldown end: 12:20 Fuel after test: 75% 637L Hours after test: 16566h 39m -Changed reagents for effluent free and total free chlorine analyzers -Returned wells to auto -Topped up silicate day tanks -Entered data into PD sheet -Checked trends | Queensville Wells No. 1 and 2 | 2025-12-12
CENTRAL | December | On site to complete station check and collect operational samples. Placed well 1 in manual for duration of check, returned to auto after. Verified analyzers: Influent Free Chlorine @ 9:20 Grab: 2.86 mg/L Analyzer: 2.90 mg/L Effluent Free Chlorine @ 9:17 Grab: 2.90 mg/L Analyzer: 2.88 mg/L Treated Free Chlorine @ 9:14 Grab: 0.22 mg/L Analyzer: 0.23 mg/L Treated Total Chlorine @ 9:14 Grab: 3.36 mg/L Analyzer: 3.33 mg/L -Topped up ammonia tank 2 -Topped up well 1 and well 2 mineral oil -Topped up silicate day tanks 438L -> 785L -Replaced influent free chlorine analyzer reagents -Upon reviewing trends, increased flow on effluent sample line -Entered data into PD sheet | Queensville Wells No. 1 and 2 | 2025-12-15
CENTRAL | December | Changed chlorine cylinder bank B with Ryan B. Contractors on site. | Queensville Wells No. 1 and 2 | 2025-12-15
CENTRAL | December | On site to complete station check and collect bacti samples (W11438487). Verified analyzers: Influent Free Chlorine @ 12:35 Grab: 2.74 mg/L Analyzer: 2.82 mg/L Effluent Free Chlorine @ 12:32 Grab: 2.52 mg/L Analyzer: 2.58 mg/L Treated Free Chlorine @ 12:29 Grab: 0.19 mg/L Analyzer: 0.22 mg/L Treated Total Chlorine @ 12:29 Grab: 3.30 mg/L Analyzer: 3.22 mg/L -Returned well 2 to auto -Found chlorine cylinders drawing at the same time ? no evidence of overly high draw rate. Appears that bank A regulator was not put on standby properly during recent change. Set to standby. -Entered data into PD sheet -Checked trends -Topped up ammonia tank 1 | Queensville Wells No. 1 and 2 | 2025-12-10
CENTRAL | December | On site to complete station check. Verified analyzers: Influent Free Chlorine @ 13:59 Grab: 2.78 mg/L Analyzer: 2.86 mg/L Effluent Free Chlorine @ 13:43 Grab: 2.78 mg/L Analyzer: 2.82 mg/L Treated Free Chlorine @ 13:28 Grab: 0.19 mg/L Analyzer: 0.22 mg/L Treated Total Chlorine @ 13:30 Grab: 3.24 mg/L Analyzer: 3.35 mg/L -Entered data into PD sheet -Checked trends -Topped up ammonia tank 2 -Topped up silicate day tanks 447L -> 805L | Queensville Wells No. 1 and 2 | 2025-12-01
CENTRAL | December | On site to complete PMs. Notified ROC of relevant alarms. -Contractors on site loadbank testing the generator. This caused the generator fault alarm for the duration of their test. -Placed wells in manual-off then local -Completed chlorine analyzer maintenance. Verified analyzers: Influent Free Chlorine @ 9:28 Grab: 2.50 mg/L Analyzer: 2.71 mg/L Adjusted analyzer based on average of grabs. Analyzer read 2.53 mg/L after adjustment. Effluent Free Chlorine @ 9:30 Grab: 0.11 mg/L Analyzer: 0.14 mg/L Treated Free Chlorine @ 9:32 Grab: 0.05 mg/L Analyzer: 0.10 mg/L Treated Total Chlorine @ 9:38 Grab: 2.88 mg/L Analyzer: 2.69 mg/L Adjusted analyzer based on average of grabs. Analyzer read 2.89 mg/L after adjustment. -Cleaned silicate injection points: Isolated raw main via closing influent valve on contact chamber. Depressurized raw main through waste valve ? dechlor added to waste chamber beforehand. Silicate point 1 drawdown was 570 mL/min on average. Max flow setpoint on SCADA not adjusted. Silicate point 2 drawdown was 585 mL/min on average. Max flow setpoint on SCADA not adjusted. Reprimed silicate lines while wasting before closing waste valve and fully reopening influent valve. -Tested chlorine detection system: all good -Performed maintenance upon well 1 and 2 deep well exhaust valves -Inspected well2 flow control valve -Placed well 1 back in auto, started duty 1. Started well 2 manually to observe operation of the flow control valve: all good. Returned well 2 to manual-off once wells attained normal operational flow. Placed well 2 in auto. -Influent chlorine hi and hihi alarms caused by dosing spike as well 2 turned off and the chlorine system did not ramp down identically, dosing returned to normal shortly and no issues were found once water passed contact chamber. Influent Free Chlorine @ 12:17 Grab: 3.00 mg/L Analyzer: 2.94 mg/L -Switched silicate pumps at 12:53 -Continued monitoring and adjusting chlorine analyzers: Effluent Free Chlorine @ 13:16 Grab: 2.60 mg/L Analyzer: 2.84 mg/L Adjusted analyzer based on average of grabs. Analyzer read 2.71 mg/L after adjustment. Treated Total Chlorine @ 13:06 Grab: 3.20 mg/L Analyzer: 3.51 mg/L Adjusted analyzer based on average of grabs. Analyzer read 3.36 mg/L after adjustment. -Completed JHSC inspection: no issues found | Queensville Wells No. 1 and 2 | 2025-12-02
CENTRAL | December | Received bulk silicate order. 40.5cm -> 90.1cm | Queensville Wells No. 1 and 2 | 2025-12-09
CENTRAL | December | On site to complete station check. Verified analyzers: Influent Free Chlorine @ 13:39 Grab: 3.04 mg/L Analyzer: 2.93 mg/L Effluent Free Chlorine @ 13:37 Grab: 2.82 mg/L Analyzer: 2.86 mg/L Treated Free Chlorine @ 13:24 Grab: 0.23 mg/L Analyzer: 0.23 mg/L Treated Total Chlorine @ 13:33 Grab: 3.44 mg/L Analyzer: 3.48 mg/L -Entered data into PD sheet -Checked trends -Topped up ammonia tank 2 -Topped up silicate day tanks | Queensville Wells No. 1 and 2 | 2025-12-05
CENTRAL | December | Changed chlorine cylinder bank A with J Garnett. | Queensville Wells No. 1 and 2 | 2025-12-08
CENTRAL | December | On site to complete station check and collect weekly bacti samples (W11419127). -Historian heartbeat alarm interlocked wells, contacted PCS who solved the issue. -Changed chlorine cylinder bank B with Ben Hess Verified analyzers: Influent Free Chlorine @ 13:52 Grab: 2.66 mg/L Analyzer: 2.68 mg/L Effluent Free Chlorine @ 13:58 Grab: 1.55 mg/L Analyzer: 1.49 mg/L Treated Free Chlorine @ 14:00 Grab: 0.18 mg/L Analyzer: 0.21 mg/L Treated Total Chlorine @ 14:00 Grab: 3.00 mg/L Analyzer: 3.10 mg/L -Entered data into PD sheet -Checked trends -Topped up ammonia tank 1 -Silicate pump 1 placed in manual-off due to rise in turbidity trend -Placed wells in manual off then returned to auto | Queensville Wells No. 1 and 2 | 2025-12-03
CENTRAL | December | 12:30. Remotely activated well 3 in manual. 12:54 onsite. Well running at 70.1 l/s. Onsite to complete station check. Verified analyzers(mg/l): 13:35 Influent free grab: 2.62. CL17: 2.65. 13:21 Effluent free grab: 2.44. CL17: 2.36. 13:35 Treated free grab: 0.14. CL17: 0.14. 13:39 Treated total grab: 3.02/3.00/3.06. CL17: 3.21. 13:50 Treated total analyzer failed from menu buttons not working while adjusting the reading to match grabs. Analyzer inputed no reading and interlocked the wells. I had collected three grabs with a 3.03 average. No adverse water directed to users. Created work order for instrumentation replace analyyzer board. Was able to adjust readings on secend attempt to match grab. Acknowledged and cleared alarms. Notified ROC. Placed well back into auto. Replaced influent chlorine analyzer reagent. No issues remain on site. | Queensville Wells No. 1 and 2 | 2025-12-05
CENTRAL | December | On site to complete station check and collect operational samples. Verified analyzers: Influent Free Chlorine @ 10:29 Grab: 2.82 mg/L Analyzer: 2.91 mg/L Effluent Free Chlorine @ 10:23 Grab: 2.72 mg/L Analyzer: 2.85 mg/L Treated Free Chlorine @ 10:07 Grab: 0.23 mg/L Analyzer: 0.22 mg/L Treated Total Chlorine @ 10:18 Grab: 3.30 mg/L Analyzer: 3.49 mg/L Adjusted analyzer based on average of grabs. Analyzer read 3.36 mg/L afterwards. -Entered data into PD sheet -Checked trends -Topped up silicate day tanks 505L -> 816L -Placed well 1 back in auto | Queensville Wells No. 1 and 2 | 2025-12-08
CENTRAL | December | Grease motor bearing Well 1 | Queensville Wells No. 1 and 2 | 2025-12-09
CENTRAL | December | On site to troubleshoot well 1 vfd | Queensville Wells No. 1 and 2 | 2025-12-30
CENTRAL | December | On site troubleshooting Vfd further. I brought a test motor from 380 to try on the Vfd. Hooked the motor up and found that the drive runs that one fine with no faults l. Came to the conclusion that the motor needs to be swapped. Talked with Donny M and confirmed it can wait till next week when we have better man power available. Left motor locked out and connected it all back to the original wiring. Under direction of oic. | Queensville Wells No. 1 and 2 | 2025-12-30
CENTRAL | December | Received chlorine delivery. 12 empties exchanged for 12 full. | Queensville Wells No. 1 and 2 | 2025-12-16
CENTRAL | December | Placed both wells in manual-off then manual-on to facilitate taking weekly bacti samples upon arrival to site. | Queensville Wells No. 1 and 2 | 2025-12-22
CENTRAL | December | On site with Jackie S to transfer silicate. ? Start level: 76.69cm Stop level: 69.63cm Cleaned hoses and surrounding areas.? | Queensville Wells No. 1 and 2 | 2025-12-24
CENTRAL | December | Onsite with Satnam M and Chris I to test well 1. Vfd faulted again. 10:54 placed well 2 man off. Found issue likely with the vfd. Maintenance will come back for further investigation at later date. | Queensville Wells No. 1 and 2 | 2025-12-29
CENTRAL | December | On-site for station check, weekly micro sampling (W11483444), Cl2 cylinder change, and to investigate W1 VFD fault alarm. Found W1 had overcurrent alarm outstanding on VFD pad. Changed Cl2 bank A with Donald Moses. Entered station readings into shared PD excel file. Grab/analyzer results as follows (mg/L): Influent Free Cl (07:45): G: 2.96 A: 2.94 Effluent Free Cl (07:47): G: 2.94 A: 3.05 Treated Free Cl (07:52): G: 0.24 A: 0.23 Treated Total Cl (07:53): G: 3.44 A: 3.35 Collected W2 raw and site treated sample. Adjusted effluent Free Cl high alarm from 3.05 to 3.10mg/L, will monitor (Influent Cl normal). Cleared alarms and shutdown W2, attempted to run W1. Heard ?popping? sound when W1 tried to start, VFD faulted. On-call Op Donald Moses to contact on-call CMS regarding W1. Well 1 local/off with emergency stop button pressed. Batched ammonia tank 1 and topped up NaSi day tanks. Returned W2 to auto. No other new issues found while on-site. | Queensville Wells No. 1 and 2 | 2025-12-29
CENTRAL | December | Onsite to respond to well 1 vfd fault. Reset vfd overcurrent fault. Placed well back in auto. No issues remaining. | Queensville Wells No. 1 and 2 | 2025-12-28
CENTRAL | December | On site to troubleshoot silicate pump and injection point 1. Placed wells in manual-off. Notified ROC of relevant alarms. Added dechlor to waste chamber. Isolated raw main from contact chamber and depressurized raw main. Pulled and cleaned injection point 1. Repressurized raw main, ran silicate pump 1 manually to reprime line. Ran well 1 to test if dosing issue for silicate line 1 was resolved. No turbidity issues found, silicate pump 1 now back in auto/in service. Wells returned to auto. | Queensville Wells No. 1 and 2 | 2025-12-19
CENTRAL | December | Responding to chlorine scrubber overload alarm. Generator not running, cycled power to scrubber and reset alarms, no other issues found. Informed ROC. | Queensville Wells No. 1 and 2 | 2025-12-22
CENTRAL | December | On site to complete PMs. Notified ROC of relevant alarms. -Inspected and performed maintenance on ammonia system: -Reworked fittings for pump 1 DICE block (sightglass and tube from pump) -Performed drawdown on pump 1, max flow 205 mL/min. Adjusted setpoint on SCADA from 200 to 205 mL/min. -Performed drawdown on pump 2, max flow 200 mL/min. Did not adjust setpoint on SCADA. -Tested containment flood alarm: all good -Topped up ammonia tank 1 -Inspected chlorine system: -Added dechlor to waste chamber and cracked waste valve slightly to avoid creating a pocket of highly chlorinated water during testing -Tested vacuum, regulators, pumps. No issues found in function -Water found in line from chlorinator 1 to vacuum gauge, created followup work order W11526445 -Placed wells in manual-off -Performed maintenance on turbidimeter: -Placed analyzer in hold output mode -Cleaned vial -Calibrated analyzer using standard. Analyzer read 0.065 NTU afterwards. -Removed analyzer from hold output mode -Returned wells to auto -Topped up silicate day tanks | Queensville Wells No. 1 and 2 | 2025-12-18
CENTRAL | December | 10:00 On-site for station check. Well 1 running at 70 l/s. Topped up silicate day tanks. Topped up ammonia tank 1. Verified analyzers(mg/l): 10:30 Influent free grab: 2.92. CL17: 2.92. 10:38 Effluent free grab: 2.80/2.80/2.84. CL17: 2.65. Adjusted to match grab average. 10:45 Treated free grab: 0.26. CL17: 0.21. 11:14 Treated total grab: 3.32. CL17: 3.25. Monochloramine: 2.78. Free ammonia: 0.09 Total ammonia: 0.64. Adjusted chlorine to ammonia ratio from 4.0 to 4.1. Topped up well 1 oil reservoir from 3/4 full to 4/4. No issues found on site. | Queensville Wells No. 1 and 2 | 2025-12-24
CENTRAL | December | On site to complete station check. -Changed chlorine cylinder bank A with Ryan B. Verified analyzers: Influent Free Chlorine @ 8:26 Grab: 2.92 mg/L Analyzer: 2.91 mg/L Effluent Free Chlorine @ 7:54 Grab: 2.86 mg/L Analyzer: 2.78 mg/L Treated Free Chlorine @ 7:48 Grab: 0.17 mg/L Analyzer: 0.23 mg/L Treated Total Chlorine @ 7:48 Grab: 3.20 mg/L Analyzer: 3.26 mg/L -Entered data into PD sheet -Checked trends -Topped up silicate day tanks -Started QVW34 well 3 in manual | Queensville Wells No. 1 and 2 | 2025-12-19
CENTRAL | December | On site to finish station check. -Changed cylinder bank B with Ryan B. -Started well 1 manually under guidance of Ryan B. Influent lo free chlorine alarms cleared upon well start. Influent free hi and hihi alarms caused by analyzer blip (falsely read 8.77mg/L). Took the following grab: Influent Free Chlorine @ 10:06 Grab: 2.80 mg/L Analyzer returned to normal (2.75mg/L) on next reading. -Changed treated total chlorine analyzer reagents -Topped up well 1 mineral oil -Topped up silicate day tanks 484L -> 795L -Left well 1 manual-on in coordination with Ryan B who will monitor it and return it to auto. | Queensville Wells No. 1 and 2 | 2025-12-22
CENTRAL | December | -Responded forward flow hihi alarm - Well 2 started at 14:10 - forward flow stay around 75L/s which is very close to hihi flow 75.7L/s, the highest flow was at 76.7L/s - reviewed trends well was running above 72L/s recently which is higher than setting, 70L/s - adjusted flow control valve to 69.5L/s at 15:18 | Queensville Wells No. 1 and 2 | 2025-12-31
CENTRAL | December | On site to complete station check and collect weekly bacti samples (W11469886) Verified analyzers: Influent Free Chlorine @ 8:43 Grab: 2.21 mg/L Analyzer: 2.13 mg/L Effluent Free Chlorine @ 8:39 Grab: 2.16 mg/L Analyzer: 2.19 mg/L Treated Free Chlorine @ 8:35 Grab: 0.15 mg/L Analyzer: 0.20 mg/L Treated Total Chlorine @ 8:35 Grab: 2.68 mg/L Analyzer: 2.63 mg/L -Found chlorinator 2 dosing low despite higher calculated SCADA dose, causing low influent chlorine alarm. Returned wells to manual-off. Well 2 returned to auto. -Entered data into PD sheet -Checked trends -Topped up ammonia tank 2 | Queensville Wells No. 1 and 2 | 2025-12-22
CENTRAL | December | On site to complete station check and collect bacti samples (W11454721). Placed well 1 in manual for duration of check. Verified analyzers: Influent Free Chlorine @ 8:34 Grab: 2.96 mg/L Analyzer: 2.98 mg/L Effluent Free Chlorine @ 8:32 Grab: 2.78 mg/L Analyzer: 2.84 mg/L Treated Free Chlorine @ 8:27 Grab: 0.22 mg/L Analyzer: 0.23 mg/L Treated Total Chlorine @ 8:27 Grab: 3.20 mg/L Analyzer: 3.29 mg/L -Entered data into PD sheet -Checked trends -Placed both wells in manual-off | Queensville Wells No. 1 and 2 | 2025-12-16
CENTRAL | December | On site to collect well 2 raw bacti sample. Placed wells back in auto. | Queensville Wells No. 1 and 2 | 2025-12-16
CENTRAL | December | On site to address chlorine leak with Jerry Z. Notified ROC. -Opened cylinders on bank A, left bank B cylinders and regulator closed -Placed well 4 in manual on | Queensville Wells No. 3 and 4 | 2025-12-12
CENTRAL | December | On site to complete station check and collect weekly bacti samples (W11438487). Verified analyzers: Influent Free Chlorine @ 8:39 Grab: 2.60 mg/L Analyzer: 2.71 mg/L Effluent Free Chlorine @ 8:29 Grab: 2.26 mg/L Analyzer: 2.27 mg/L Treated Free Chlorine @ 8:25 Grab: 0.07 mg/L Analyzer: 0.13 mg/L Treated Total Chlorine @ 8:25 Grab: 2.92 mg/L Analyzer: 2.82 mg/L -Completed well 4 deep well exhaust valve maintenance -Switched from well 3 manual-on to well 4 manual-on -Completed well 4 FCV maintenance and addressed intermittent hi flow alarm CMU (W11484310) by adjusting flow pilot valve setting down slightly -Changed well 3 duty to duty 4, well 4 duty to duty 2 -Entered data into PD sheet -Checked trends -Returned wells to auto | Queensville Wells No. 3 and 4 | 2025-12-10
CENTRAL | December | Reviewed Cl2 gas leak trend, Cl2 emergency gas closure system triggered isolating cylinders. Gas level below high alarm, Central OPs will investigate tomorrow. Site interlocked. | Queensville Wells No. 3 and 4 | 2025-12-11
CENTRAL | December | On site with Ben H and Donny M to replace chlorine line 2 ejector. -Placed wells and chlorinators in manual -off -Purged chlorine system -Replaced chlorine ejector #2 -Reprimed chlorine system -Added dechlor to waste chamber and backflushed well slightly to remove excess chlorine from purging/repriming process -Returned wells and chlorinators to auto, chlorinator and chlorine booster pump 2 now back in service | Queensville Wells No. 3 and 4 | 2025-12-10
CENTRAL | December | On site to complete station check. -Verified analyzers: Influent Free Chlorine @ 10:59 Grab: 1.88 mg/L Analyzer: 1.91 mg/L Effluent Free Chlorine @ 10:57 Grab: 0.38 mg/L Analyzer: 0.39 mg/L Treated Free Chlorine @ 10:55 Grab: 0.08 mg/L Analyzer: 0.05 mg/L Treated Total Chlorine @ 10:55 Grab: 2.32 mg/L Analyzer: 2.35 mg/L -Entered data into PD sheet -Checked trends Continued troubleshooting chlorine leak with Donny M. Notified ROC. -Purged system -Replaced right regulator -Reprimed system -Added dechlor to waste chamber and backflushed well slightly to remove excess chlorine from testing -Left wells in manual-off | Queensville Wells No. 3 and 4 | 2025-12-15
CENTRAL | December | On site to run well 3 with Ryan B. Inspected chlorine room ? no issues found. Ran well 3 in manual until contact tank cleared: returned to manual-off once chamber was cleared. -Changed treated total chlorine analyzer reagents | Queensville Wells No. 3 and 4 | 2025-12-15
CENTRAL | December | On-site to assist Alex Bell (OIT under direction of OIC) and Donald Moses with Cl2 leak investigation. Checked for leaks once Alex/Donny made regulator swap and returned system to normal operation. Cleared alarms, site in auto. | Queensville Wells No. 3 and 4 | 2025-12-12
CENTRAL | December | On site to troubleshoot chlorine gas leak with Donny M and Ryan B and complete station check. -Purged system -Replaced left regulator -Reprimed system -Added dechlor to waste chamber and backflushed well slightly to remove excess chlorine from testing -Verified analyzers: Influent Free Chlorine @ 14:20 Grab: 2.64 mg/L Analyzer: 2.59 mg/L Effluent Free Chlorine @ 14:18 Grab: 0.10 mg/L Analyzer: 0.11 mg/L Treated Free Chlorine @ 14:14 Grab: 0.09 mg/L Analyzer: 0.05 mg/L Treated Total Chlorine @ 14:14 Grab: 2.28 mg/L Analyzer: 2.28 mg/L -Entered data into PD sheet -Checked trends -Ryan cleared chlorine alarms and returned sites to auto | Queensville Wells No. 3 and 4 | 2025-12-12
CENTRAL | December | On site to address chlorine leak with Donny M. Notified ROC. -Purged system and adjusted parker fittings -Checked for chlorine leaks -Reprimed chlorine system -Added dechlor to the waste chamber and backflushed well slightly -Cleared alarms -Donny placed well 4 in manual-on at 11:10 | Queensville Wells No. 3 and 4 | 2025-12-11
CENTRAL | December | On site to collect operational samples. -Retested monochloramine, free and total ammonia, written on sample bottle | Queensville Wells No. 3 and 4 | 2025-12-01
CENTRAL | December | On site to continue work on well 4 VFD upgrade project | Queensville Wells No. 3 and 4 | 2025-12-03
CENTRAL | December | On site to investigate chlorine leak alarm with Ben H, complete station check, and collect operational samples. -Topped up ammonia tank 1 -Verified analyzers: Influent Free Chlorine @ 8:43 Grab: 2.06 mg/L Analyzer: 2.08 mg/L Effluent Free Chlorine @ 8:46 Grab: 0.10 mg/L Analyzer: 0.11 mg/L -Tested chlorine system, ran chlorine booster pumps and chlorinators locally. No leak found. Added dechlor to waste chamber and backflushed contact chamber slightly to remove added chlorine from the tests. -Manually started well 3. Influent free chlorine high and hihi alarms are due to leftover chlorine from the testing ? cleared quickly. Treated total lo alarm is due to contact chamber drawing back distribution water while well was interlocked over the weekend. Trend showing recovery. | Queensville Wells No. 3 and 4 | 2025-12-08
CENTRAL | December | On site to continue completing station check and collecting operational samples. Verified other analyzers: Treated Free Chlorine @ 11:41 Grab: 0.19 mg/L Analyzer: 0.15 mg/L Treated Total Chlorine @ 11:46 Grab: 3.00 mg/L Analyzer: 3.03 mg/L -Entered data into PD sheet -Checked trends -In response to slightly high free ammonia grab, switched ammonia pumps -Returned wells to auto | Queensville Wells No. 3 and 4 | 2025-12-08
CENTRAL | December | On site to pick up silicate from bulk tank. 750 L removed. | Queensville Wells No. 3 and 4 | 2025-12-02
CENTRAL | December | On site to respond to influent chlorine lolo interlock, complete station check, and collect weekly bacti samples (W11419127). Influent Total Chlorine @ 7:44 Grab: 1.97 mg/L Influent Total Chlorine @ 7:47 Grab: 1.98 mg/L Influent Free Chlorine @ 7:45 Grab: 0.05 mg/L Analyzer: 0.06 mg/L Based on influent grabs, determined contact tank to have filled with chloraminated distribution water. Reset lock out manually under direction from Ben Hess and manually started well 3 at 8:04. -Switched wells at 9:35. Verified analyzers with well running: Influent Free Chlorine @ 10:01 Grab: 2.58 mg/L Analyzer: 2.61 mg/L Effluent Free Chlorine @ 9:55 Grab: 2.46 mg/L Analyzer: 2.42 mg/L Treated Free Chlorine @ 9:49 Grab: 0.18 mg/L Analyzer: 0.15 mg/L Treated Total Chlorine @ 9:49 Grab: 3.22 mg/L Analyzer: 3.17 mg/L -Entered data into PD sheet -Checked trends -Changed influent analyzer reagents (unrelated to previous alarm) -Created follow up (to station check) work order W11484310 to address intermittent well 4 hi flow alarms. | Queensville Wells No. 3 and 4 | 2025-12-03
CENTRAL | December | On site to complete station check. Verified analyzers: Influent Free Chlorine @ 9:06 Grab: 2.64 mg/L Analyzer: 2.70 mg/L Effluent Free Chlorine @ 9:00 Grab: 2.45 mg/L Analyzer: 2.59 mg/L Adjusted analyzer based on average of grabs. Analyzer read 2.45 mg/L afterwards. Treated Free Chlorine @ 8:47 Grab: 0.15 mg/L Analyzer: 0.15 mg/L Treated Total Chlorine @ 8:47 Grab: 3.28 mg/L Analyzer: 3.32 mg/L -Entered data into PD sheet -Checked trends -Returned well 3 to auto | Queensville Wells No. 3 and 4 | 2025-12-01
CENTRAL | December | On site to complete PMs. Notified ROC of relevant alarms. -Sites placed in manual-off by ROC due to SCADA upgrades at 9:00-9:30 -Completed chlorine leak detection test: sensor functional, all halogens functional, alarms received by SCADA | Queensville Wells No. 3 and 4 | 2025-12-09
CENTRAL | December | Onsite with Stephen Baidy to respond to chlorine leak alarm of 0.49 ppd. Couldn?t find leak. Tightened fittings and tested chlorine vacuum. No issues found. Chlorine detector reading 0. | Queensville Wells No. 3 and 4 | 2025-12-05
CENTRAL | December | Grease bottom bearing motor 3 well | Queensville Wells No. 3 and 4 | 2025-12-09
CENTRAL | December | On site to complete PMs. Notified ROC of relevant alarms. -Received silicate bulk order. 32.1cm -> 69.7cm -Completed turbidimeter monthly maintenance; reading after cleaning and calibrating: 0.040 NTU -Completed CL17 monthly maintenance. All chlorine lo and lolo alarms were caused directly by maintenance and did not reflect water conditions as evidenced by the following verifying grabs. Verified analyzers: Influent Free Chlorine @ 13:15 Grab: 2.52 mg/L Analyzer: 2.63 mg/L Effluent Free Chlorine @ 13:17 Grab: 0.38 mg/L Analyzer: 0.39 mg/L Treated Free Chlorine @ 13:19 Grab: 0.08 mg/L Analyzer: 0.05 mg/L Treated Total Chlorine @ 13:21 Grab: 2.40 mg/L Analyzer: 2.43 mg/L -Topped up well 4 mineral oil -Ran generator: Hours before run: 703h 34m Fuel before run: 1218L Started @ 13:34 On load @ 13:36 Off load @ 14:37 Ended run @ 14:39 Cooldown ended @ 14:45 Hours after run: 704h 45m Fuel after run: 1178L -Returned wells to auto | Queensville Wells No. 3 and 4 | 2025-12-09
CENTRAL | December | Topped up silicate day tanks. Picked up 750 L of silicate from bulk tank. | Queensville Wells No. 3 and 4 | 2025-12-16
CENTRAL | December | Onsite to investigate chlorine leak alarm. Low chlorine Alarm has been tripping for past few weeks without operators finding any leaks. Alarm tripped evening if the 24th and site had been offline with no leaks since then. No obvious sings of leaks. All cylinders properly closed via emergency shutoff. Tightened pig tail to manifold and hihi chlorine alarm tripped reading 1.39 ppm. Purged into chlorine manifold line. Placed dechlore pucks at outfall and briefly backwashed line to remove any excess chlorine sent into system. Will return with second operator tomorrow to further investigate. Notified roc and site to remain offline. | Queensville Wells No. 3 and 4 | 2025-12-28
CENTRAL | December | Assisted Donald Moses replace pigtail gasket on Cl2 bank B. Donald Moses remains on-site, Chlorine system back in operation, Chlorinator 1 man/off. | Queensville Wells No. 3 and 4 | 2025-12-29
CENTRAL | December | On site to pick up silicate from bulk track. Approximately 750L taken. | Queensville Wells No. 3 and 4 | 2025-12-16
CENTRAL | December | On site to complete station check. -Verified analyzers: Influent Free Chlorine @ 9:37 Grab: 2.58 mg/L Analyzer: 2.65 mg/L Effluent Free Chlorine @ 9:35 Grab: 2.38 mg/L Analyzer: 2.40 mg/L Treated Free Chlorine @ 9:20 Grab: 0.10 mg/L Analyzer: 0.14 mg/L Treated Total Chlorine @ 9:20 Grab: 3.11 mg/L Analyzer: 2.96 mg/L -Entered data into PD sheet -Checked trends -Manually triggered chlorinator and chlorine pump rotation 1 -> 2 | Queensville Wells No. 3 and 4 | 2025-12-19
CENTRAL | December | Onsite to troubleshoot chlorine room leak detector Informed ROC Place detector in cal mode on scada Removed Halogen actuators Removed gas sensor , replaced with new and calibrated Replaced Halogen actuators Informed ROC, armed building and left site | Queensville Wells No. 3 and 4 | 2025-12-19
CENTRAL | December | On site to complete PMs. Notified ROC of relevant alarms. -Placed wells in manual-off then local. Placed silicate and chlorine pumps in manual-off. Isolated raw main from contact chamber. Added dechlor to waste chamber. Depressurized raw main. Pulled and cleaned silicate injection points.Reprimed injection points while passing water through waste valve to avoid overdosing silicate. Returned all pumps to auto. Returned wells to manual-off. Ran well 3 manually to test silicate dosage. Switched silicate pumps at 14:33. Returned both wells to auto. | Queensville Wells No. 3 and 4 | 2025-12-17
CENTRAL | December | With Ryan B, returned chlorine cylinder bank B and regulator 2 into service. | Queensville Wells No. 3 and 4 | 2025-12-22
CENTRAL | December | 13:00 Activated duty 2 (well 4) remotely. | Queensville Wells No. 3 and 4 | 2025-12-24
CENTRAL | December | Placed chlorinator 1 and chlorine pump 1 in manual-off. | Queensville Wells No. 3 and 4 | 2025-12-19
CENTRAL | December | On site to collect well 4 raw bacti sample. -Placed well 4 in manual-on -Inspected ammonia system: all good. Past grabs acceptable. Pump 1 drawdown: 205 mL/min. Adjusted max flow setpoint on SCADA from 200mL/min to 205mL/min. Pump 2 drawdown: 205 mL/min. SCADA setpoint not adjusted. Tested containment flood alarm after notifying ROC. | Queensville Wells No. 3 and 4 | 2025-12-16
CENTRAL | December | On site to troubleshoot chlorine leak with J Garnett. -Shut off bank B cylinders and chlorine regulator 2. -Manifold valve also completely shut and must be reopened prior to attempting to use side B chlorine cylinder bank -Returned wells to auto | Queensville Wells No. 3 and 4 | 2025-12-18
CENTRAL | December | On site to complete station check and collect weekly bacti samples (W11469886) -Verified analyzers: Influent Free Chlorine @ 13:55 Grab: 2.70 mg/L Analyzer: 2.72 mg/L Effluent Free Chlorine @ 14:03 Grab: 2.11 mg/L Analyzer: 2.09 mg/L Treated Free Chlorine @ 14:14 Grab: 0.12 mg/L Analyzer: 0.14 mg/L Treated Total Chlorine @ 14:14 Grab: 2.99 mg/L Analyzer: 2.85 mg/L -Entered data into PD sheet -Checked trends -Changed reagents for treated free chlorine analyzer -Swapped which well was manual-on to collect well 4 raw sample -Returned wells to auto | Queensville Wells No. 3 and 4 | 2025-12-22
CENTRAL | December | Grease well 4 bottom motor bearing | Queensville Wells No. 3 and 4 | 2025-12-16
CENTRAL | December | On site to complete station check, collect operational samples, and collect weekly bacti sample (W11454721). -Verified analyzers: Influent Free Chlorine @ 11:01 Grab: 2.56 mg/L Analyzer: 2.66 mg/L Effluent Free Chlorine @ 11:04 Grab: 1.94 mg/L Analyzer: 1.97 mg/L Treated Free Chlorine @ 11:12 Grab: 0.10 mg/L Analyzer: 0.13 mg/L Treated Total Chlorine @ 11:12 Grab: 2.66 mg/L Analyzer: 2.70 mg/L -Entered data into PD sheet -Checked trends -Received chlorine cylinder delivery 12 empties exchanged for 12 full -Placed well 3 in manual-off | Queensville Wells No. 3 and 4 | 2025-12-16
CENTRAL | December | Drain drip oiler and clean refill with clean oil Loto well called control well was being locked out | Queensville Wells No. 3 and 4 | 2025-12-22
CENTRAL | December | Onsite to complete station check. Wells in standby. 07:55 Verified analyzers(mg/l): Influent free grab: 2.32. CL17: 2.33. Effluent free grab: 0.39. CL17: 0.34. Treated free grab: 0.05. CL17: 0.04. Treated total grab: 2.28. CL17: 2.33. Topped up well 4 reservoir oil pot. Chlorinator 1 remains OOS and isolated after possible leaking. No other issues found on site. | Queensville Wells No. 3 and 4 | 2025-12-24
CENTRAL | December | Onsite with Ryan Bewley to investigate chlorine leak alarm. Cylinders closed and gas purged. Replaced chlorine manifold 2 pigtail A gasket as some corrosion found. Opened cylinders and found no leaks. 09:45 Placed dechlore at outback and began to back flush contact tank. Contact tank has not turned over in 5 days. | Queensville Wells No. 3 and 4 | 2025-12-29
CENTRAL | December | On site to pick up silicate for HLW1. Bulk tank level Before filling- 41.05 cm After filling- 37.63 cm | Queensville Wells No. 3 and 4 | 2025-12-22
CENTRAL | December | Onsite to repair treated total and effluent free AITs. Key pads not working Coordinated with ROC and operations. Well duty not active but placed manual off anyway Replaced main circuit boards and a membrane Configured new boards Took preliminary grabs. Asked OIC to the run the well in manual. Waited for contact tank to clear. Too multiple grabs and adjusted Eff Free: A = 2.76mg/L G = 2.73mg/L Treated Tot: A = 3.30mg/L G = 3.30mg/L Monitored for a while. OIC placed duty back to Auto Informed ROC, armed building and left site | Queensville Wells No. 3 and 4 | 2025-12-31
CENTRAL | December | 11:17 Onsite to stop backflushing contact tank and complete station check and sampling. COC W11483444. 11:25 ran well 3 at 50 l/s. Verified analyzers(mg/l): 11:46 verified Influent free grab: 2.90. CL17: 2.80. 12:20 Effluent free grab: 1.24 CL17: 1.21 12:22 Treated free grab: 0.09. CL17: 0.08. 12:22 Treated total grab: 1.74 CL17: 1.74. collected treated sample. 12:28 Rotated to well 4 manual on and well 3 off. Adjusted well 3 flow speed setpoint back to 70 l/s. 12:34 collected well 4 raw sample. Adjusted duty start to 40% and stop to 75% Harry walker level. 12:37 influent hihi chlorine alarm triggered to 3.90 mg/l. Settled back down to typical level of 2.47 mg/l on next reading. Chlorinator 1 remains oos. No other issues on site. | Queensville Wells No. 3 and 4 | 2025-12-29
CENTRAL | December | 11:17 Onsite to stop backflushing contact tank and complete station check and sampling. COC W11483444. 11:25 ran well 3 at 50 l/s. Verified analyzers(mg/l): 11:46 verified Influent free grab: 2.90. CL17: 2.80. 12:20 Effluent free grab: 1.24 CL17: 1.21 12:22 Treated free grab: 0.09. CL17: 0.08. 12:22 Treated total grab: 1.74 CL17: 1.74. collected treated sample. 12:28 Rotated to well 4 manual on and well 3 off. Adjusted well 3 flow speed setpoint back to 70 l/s. 12:34 collected well 4 raw sample. Adjusted duty start to 40% and stop to 75% Harry walker level. 12:37 influent hihi chlorine alarm triggered to 3.90 mg/l. Settled back down to typical level of 2.47 mg/l on next reading. Chlorinator 1 remains oos. No other issues on site. | Queensville Wells No. 3 and 4 | 2025-12-29
WEST | December | Pumping Station Check Chlorine Grab (mg/L): Free: 0.05 Total: 1.68 No issues on site | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2025-12-12
WEST | December | Pumping Station Check (no issues found) input data to PWQ 12:05 Grab Residuals (mg/l) Free 0.04 Total 1.81 | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2025-12-15
WEST | December | Onsite for station check Checked residuals mg/l @1431 Total grab 1.72 Free grab 0.01 | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2025-12-04
WEST | December | On site for station check and to collect weekly sample W11438655 WEST cell @1120 Chlorine Free grab 0.04mg/L Total grab 1.30mg/L Sl1000 Total Chlorine 1.30mg/L FA 0.11mg/L TA 0.33mg/L Mono 1.12mg/L Nitrite 0.002mg/L No issues on site | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2025-12-10
WEST | December | Pumping Station Check Chlorine Grab (mg/L): Free: 0.05 Total: 1.77 No issues on site | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2025-12-08
WEST | December | On site for the following RHPSWA, JHSC Health and Safety Inspection, Woodland Acres Reservoir and WPS (1M) RHPSWA, Ventilation System Inspection, Woodland Acres WPS (1M) RHPSWA, PRV Valve Inspection, Woodland Acres, WPS(1M) RHPSWA, Pump & Motor Inspection, Woodland Acres WPS (1M) RHPSWA, Flood Alarm Test, Woodland Acres WPS (1M) RHPSWA, Discharge Valve & Actuator Exercise & Inspection, Woodland Acres WPS (1M) RHRSWA, Sump Pit System Inspection, Woodland Acres RES (1M) RHRSWA, Flood Alarm Test, Woodland Acres RES (1M) RHRSWA, High/Low Temperature Alarm Test, Woodland Acres RES (1M) RHRSWA, Dehumidifier Inspection & Cleaning, Woodland Acres RES (1M) RHRSWA, Actuated Valve Exercise & Inspection, Woodland Acres RES (1M) RHRSWA, External Venting Screens Inspection, Woodland Acres RES (1M) No issues | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2025-12-02
WEST | December | Pumping Station Check Chlorine Grab (mg/L): Free: 0.05 Total: 1.80 No issues on site | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2025-12-01
WEST | December | -on site to complete station checks -checked trends: all ok -entered reading in PWQ: all ok -took chlorine grab 13:15 -free cl: 0.04mg/l -total cl: 1.50mg/l -equipment all ok | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2025-12-24
WEST | December | Onsite for station check Duty not active Checked residuals mg/l @1148 Total grab 1.63 Free grab 0.02 | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2025-12-23
WEST | December | -on site to complete station check and weekly bacti W11483618. East Cell -checked trends: all ok Free. 0.00 mg/l Total. 1.30 mg/l Nitrite 0.00 mg/l Monochloramine 1.12 mg/l Free Ammonia 0.11 mg/l Total Ammonia 0.33 mg/l -took grab west cell 12:30 -free cl: 0.03mg/l -total cl: 1.27mg/l -equipment all ok | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2025-12-29
WEST | December | Duty not active Checked residuals mg/l @1148 Total grab 1.73 Free grab 0.05 | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2025-12-30
WEST | December | -on site for station check -took readings in PWQ: -checked trends: all ok -took chlorine grab 13:15 -free: 0.03mg/l -total: 1.56mg/l -equipment all ok -exercise pumps 1 & 2 for 10 minutes each | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2025-12-18
WEST | December | -on site to complete station check and weekly bacti W11470054 -checked trends: all ok -entered readings in PWQ: -took grab east cell 12:50 -free cl: 0.07mg/l -total cl: 1.32mg/l -equipment all ok | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2025-12-22
WEST | December | On site for station check and to collect weekly sample W11454881 WEST cell @1245 Chlorine Free grab 0.04mg/L Total grab 1.41mg/L Sl1000 Total Chlorine 1.38mg/L FA 0.11mg/L TA 0.33mg/L Mono 1.12mg/L Nitrite 0.001mg/L No issues on site | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2025-12-16
CENTRAL | December | On-site for a station and equipment check, no issues found. Took weekly bacti sample while draining Took biweekly operational sample while draining Verified analyzers and entered all readings and grabs into PWQ sheet Inlet Free grab@ 0901 0.09mg/L Inlet Total@0903 g: 1.82 a: 1.80mg/L Outlet Free grab@0907 0.03mg/L Outlet Total@0910 g:1.77 a:1.79mg/L | Richmond Hill Bloomington Elevated Tank | 2025-12-10
CENTRAL | December | On-site for station and equipment check, no issues found Took weekly bacti sample WO W11419193 Verified analyzers and entered all readings and grabs into PWQ sheet Will follow up with B Hess on how best to FA inlet and outlet | Richmond Hill Bloomington Elevated Tank | 2025-12-03
CENTRAL | December | Onsite to complete work orders. Notified ROC of work. Altitude valve inspection. Flow control valve inspection. Adjusted setpoint from 100 to 85% on SCADA. Valve deviation alarm triggered and valve did not close. Found valve control ball valve closed. Opened ball valve. Tested by closing valve with no issues but failed again to open on its own. Manually drained valve cover to reopen valve to 100%. Created work order W11526458 for maintenance to repair. Manual valve exercise. 12:30 Chlorine analyzer maintenance. 13:18 verified analyzers: Inlet total: 1.69 analyzer: 1.75 Outlet total: 1.69 analyzer: 1.67 Actuated valve exercise and inspection. JHSC inspection. Inlet/outlet heat trace system inspection. circulation pump test. PRV valve inspection. 12:03 Valve room, electrical room and chlorine room low temmperature alarm test. ventilation system inspection. Site cleaning. Bathroom heater not working. Team lead to create property service work order. No other issues found on site. | Richmond Hill Bloomington Elevated Tank | 2025-12-18
CENTRAL | December | On-site for a station and equipment check No issues found. Changed both sets of reagents Took weekly bacti while draining Verified analyzers and entered all readings and grabs into PWQ sheet Total inlet@0936 G:1.88 A:1.85mg/L Total outlet@0955 G:1.64 A:1.69mg/L | Richmond Hill Bloomington Elevated Tank | 2025-12-29
CENTRAL | December | Switched PD9 controlling ET to RHETBR from RHETCR for work later today on altitude valve @ RHETCR. | Richmond Hill Bloomington Elevated Tank | 2025-12-23
CENTRAL | December | On-site for a station and equipment check. No issues found. Weekly bacti sample taken while draining, W11469830 General housekeeping. Verified analyzers and entered all readings and grabs into PWQ sheet Inlet Total@0842 G:1.79 A:1.86mg/L Outlet Total@0848 G:1.59 A:1.61mg/L | Richmond Hill Bloomington Elevated Tank | 2025-12-22
CENTRAL | December | On-site for a station and equipment check, no issues Washroom and general cleaning Weekly bacti sample taken while draining Verified analyzers, all readings and grabs entered into PWQ sheet Inlet Free@0910 g:0.05mg/L Inlet Total @9010 g:1.72 a:1.80mg/L Outlet Free@0915 g:0.04mg/ Outlet Total @0921 g:1.71 a:1.68mg/L | Richmond Hill Bloomington Elevated Tank | 2025-12-16
CENTRAL | December | On-site for a station and equipment check. One issue found. Work order created for leak at the position transmitter on altitude valve. Verified analyzers and entered all readings and grabs into PWQ sheet Took weekly bacti and biweekly operational samples while draining Higher FA values than expected, will discuss how to better manage these at our morning meeting tomorrow Inlet Free CL2 grab@1000 0.04mg/L Inlet Total CL2 @1000 g:1.81 a:1.89mg/L Outlet Free CL2 grab@1006 0.04mg/L Outlet Total CL2 @1008 g:1.83 a:1.84mg/L | Richmond Hill Coon's Elevated Tank | 2025-12-10
CENTRAL | December | On-site for a station and equipment check, no issues found Took weekly bacti sample while draining WO #W11419193 Will speak to B Hess how best to deal with higher FA grabs. Verified analyzers and entered all readings and grabs into PWQ sheet | Richmond Hill Coon's Elevated Tank | 2025-12-03
CENTRAL | December | On-site for various WO's -JHSC inspection -Inlet Outlet heat trace inspection -Circulation pump test and inspection -Altitude valve inspection, still pending work order for leak at position indicator -Valves exercised -Analyzers cleaned and maintained -Actuated valve exercised -PRV valve inspection completed -Low temp alarm tested, completed -Ventilation system inspected -General housekeeping | Richmond Hill Coon's Elevated Tank | 2025-12-18
CENTRAL | December | On-site for a station and equipment No issues found Changed both sets of reagents in analyzers Weekly bacti sample taken while draining Verified analyzers and entered all readings and grabs into the PWQ sheet Inlet Total@1031 G:1.81 A:1.73mg/L Outlet Total@1046 G:1.73 A:1.73mg/L | Richmond Hill Coon's Elevated Tank | 2025-12-29
CENTRAL | December | On-site with L Ferguson to repair altitude valve. Isolated valve. Confirmed valves hold for future work on check-valve Returned tower to operation and back into controlling tower of PD9 | Richmond Hill Coon's Elevated Tank | 2025-12-23
CENTRAL | December | Repair altitude valve Replace prongs and isolate main to verify check valve repair | Richmond Hill Coon's Elevated Tank | 2025-12-23
CENTRAL | December | On-site for a station and equipment check. No issues found. Weekly bacti sample taken while draining Verified analyzers and entered all readings and grabs into PWQ sheet Inlet total @1315 G:1.68 A:1.60mg/L Outlet Total @1320 G:1.55 A:1.63mg/L | Richmond Hill Coon's Elevated Tank | 2025-12-22
CENTRAL | December | On-site for a station and equipment check, no issues found Weekly bacti sample taken while draining Verified analyzers, entered all readings and grabs into PWQ sheet Inlet Free@0948 0.06mg/L Inlet Total@0950 g:1.63 a:1.57mg/L Outlet Free@0955 0.04mg/L Outlet Total@0956 g:1.67 a:1.70mg/L | Richmond Hill Coon's Elevated Tank | 2025-12-16
EAST | December | On site for station check. Reviewed scada, duty not active. Cell level @ 84 and 84% Visual inspection in and around station. Verification of equipment and instrumentation. Outstanding alarm: None Chlorine residual @ 14:42 hrs Efffluent: FCL= 0.07 mg/l. TCL = 1.42 mg/l P1~ Duty4 P2 ~Duty4 P3 ~ Duty1 P4 ~ Duty1 Station OK, recorded station readings in PWQ sheet. | Richmond Hill Pugsley Pumping Station | 2025-12-12
EAST | December | On site to complete station check. Time: 14:25 Grab (mg/l) Free: 0.03 Total: 1.40 Cleared alarm at 14:15. Checked site and trends. Took grabs all ok. | Richmond Hill Pugsley Pumping Station | 2025-12-05
EAST | December | On site for station check Duty active Visual inspection in and around station Verification of equipment and instrumentation Verified chlorine analyzers readings. Unable to review scada due to password issues. Outstanding alarm: None Effluent FCL @ 16:04 hrs Grab ? FCL = 0.06 mg/l ? TCL = 1.42 mg/l | Richmond Hill Pugsley Pumping Station | 2025-12-01
EAST | December | Attended site for station check - station and equipment okay | Richmond Hill Pugsley Pumping Station | 2025-12-08
EAST | December | On site for preventative maintenance work orders Completed Suction valve exercise Piping and support visual inspection Discharge valve exercise Control panel light inspection Flood alarm test Eye wash cleaning and solution replacement JHSC inspection VFD air filter change Housekeeping Generator test run Generator test: Hours: Start 372.4 Stop 376.1 Fuel: Start 6770 L Stop 6673 L Generator run statistics: Oil pressure 64 PSI Coolant temperature 162 F Engine speed 1798 RPM Frequency 60.0 Hz Voltage 599 V Current 226 A ATS failed to transfer to utility when commanded, Dan Boate attended site and reset PAC card failed and Chris Scott attended site to replace Tested generator and pumps 1 to 3 on new PAC card - okay Station and equipment okay | Richmond Hill Pugsley Pumping Station | 2025-12-09
EAST | December | On site to respond to malfunction during station generator testing. When Station generator test was completed and a retransfer to normal power was initiated, the transfer switch indicated a problem with the source 2 breaker and the station was left without power. Upon arrival I assessed the situation and reset the alarm on the transfer switch controller. At that point the operation of the transfer switch returned to normal. I subsequently tested 4 transfer to generator tests and back to normal power. All 4 tests worked correctly. Could not find any outstanding or persistent issue. Left generator control in automatic mode with no outstanding alarms. | Richmond Hill Pugsley Pumping Station | 2025-12-09
EAST | December | On site for station check Grabs at 14:25 FCl 0.07 mg/L TCl 1.47 mg/L Reviewed station trends Checked station and equipment Recorded observations in the shared PWQ sheet Station on at the time of station check Station and equipment okay | Richmond Hill Pugsley Pumping Station | 2025-12-22
EAST | December | Vibration readings Grease pumps and motors | Richmond Hill Pugsley Pumping Station | 2025-12-19
EAST | December | On site to check station and equipment. P1 and P4 are running in duty 1.? 14:25 grab chlorine residual from discharge header: FCL. = 0.06 mg/l, TCL = 1.53 mg/l. Reviewed trends, station is under normal operation. | Richmond Hill Pugsley Pumping Station | 2025-12-29
WEST | December | Onsite to complete work orders Inspected and tested high lift PRV Inspected and tested Fire pump actuated valve and inspected fire pump Completed JHSC at well 2 Manual and actuated valve exercised well 2 valves | Schomberg Water Treatment Plant & Wells 2-4 | 2025-12-11
WEST | November | Entry to document site power failure on November 1st. No UV alarms. Reviewed trends, dose above 40mj/cm2 while filter discharge flow registered. | Schomberg Water Treatment Plant & Wells 2-4 | 2025-11-01
WEST | December | On site for Station Checks Check trends- All okay Verified Analyzers. Reservoir- Grab Total Cl2:3.80 mg/L, Analyzer- 3.75 mg/L Post filter- Grab Total Cl2:2.36 mg/L, Analyzer- 2.29 mg/L Highlift- Grab Total Cl2:3.40 mg/L, Analyzer- 3.35 mg/L Reagents all good Responded to Filter 2 turbidity spike, noticed debris in vail, cleaned and flushed line, needle valve clogged, adjusted needle valve to get the desired flow. W11449233- High lift turbidity meter analyzer cleaned vail and verified Conducted in house lab analysis. Entered values in PWQ sheet Equipment okay | Schomberg Water Treatment Plant & Wells 2-4 | 2025-12-15
WEST | December | -on site to complete station check - plant duty active and high lift duty active -wells 2 and 4 in duty -filled KMnO4 tank #1 15.6 to 81.0 cm - KMnO4 pump 2 running at 15.7%, 58 psi, 62.7 ml/min - chlorinator 1 54% open, df 140%, 0.54 kg/hr, vac = -700 mbar - chlorinator 2 29% open, df 166%, 0.31 kg/hr, vac = -830 mbar - recorded data in PWQ sheet - checked equipment - CL17 reagents ok - reviewed trends - no issues found -verified analyzers: 09:43 - high lift treated water TCL analyzer = 3.45 mg/L 09:43 - high lift treated water grab: TCL = 3.48 mg/L 09:53 - reservoir TCL analyzer = 3.76 mg/L 09:53 - reservoir grab: TCL = 3.68 mg/L 09:58 - post filter TCL analyzer = 2.26 mg/L 09:58 - post filter grab: TCL = 2.34 mg/L | Schomberg Water Treatment Plant & Wells 2-4 | 2025-12-11
WEST | December | -on site to complete station check, lab and to collect samples -sample work order # W11438617 - plant duty active, high lift duty active 08:40 - collected weekly well #4 raw water micro sample - KMnO4 pump 1 running at 14%, 70 psi, 63.9 ml/min - chlorinator 1 55% open, df 140%, 0.54 kg/hr, vac = -700 mbar - chlorinator 2 32% open, df 164%, 0.32 kg/hr, vac = -830 mbar - recorded data in PWQ sheet - checked equipment - CL17 reagents ok - reviewed trends - no issues found -verified analyzers: 08:59 - high lift treated water TCL analyzer = 3.36 mg/L 08:59 - high lift treated water grab: FCL = 0.04 mg/L TCL = 3.32 mg/L Mono = 3.02 mg/L 09:05 - collected weekly treated water micro sample 09:11 - reservoir TCL analyzer = 3.62 mg/L 09:11 - reservoir grab: TCL = 3.62 mg/L Mono = 3.32 mg/L 09:17 - post filter TCL analyzer = 2.22 mg/L 09:17 - post filter grab: TCL = 2.26 mg/L -completed well #2 station check 09:49 - collected weekly well #2 raw water micro sample 10:47 - collected weekly well #3 raw water micro sample -KMnO4 pump #1 dosage low, completed draw down on pump - max flow = 125 ml/min -replaced pump element and roller, completed drawdown - max flow = 375 ml/min -adjusted SCADA max flow setpoint 455 to 375 ml/min -pump back in service, will monitor -completed lab, results in PWQ sheet -completed High Lift Discharge Check Valves, Service and Inspection -completed High Lift Pumps, Inspection | Schomberg Water Treatment Plant & Wells 2-4 | 2025-12-10
WEST | November | Filter media measurements taken: F1 20.5 / 30.5 F2 21 / 29 F3 21 / 28.5 Previous measurements taken June 26: F1 22 / 30 F2 20 / 28 F3 20 / 28 | Schomberg Water Treatment Plant & Wells 2-4 | 2025-11-25
WEST | December | Onsite to update post filter AIT firmware. Informed ROC and operations Plant already offline Performed update and confirmed setting were unchanged Contacted PCS to return PAC program to original Verified scada alarms during no flow and with flow - all ok Operations started plant All ok, no issues Informed ROC and operations Left site | Schomberg Water Treatment Plant & Wells 2-4 | 2025-12-09
WEST | December | -on site to complete work orders -informed ROC of work -completed Electric Actuated Valves Inspection, Schomberg WTP W3&4 -completed Exhaust Fan Inspection, Schomberg WTP W3&4 -completed Check Valves Inspection, Schomberg WTP W3&4 -completed Dehumidifier Inspection, Schomberg WTP W3&4 -completed Pump and Motor Inspection, Schomberg WTP W3&4 -reduced reservoir residual setpoint 3.75 to 3.70 mg/L -completed UV Reactors, Inlet Isolation Valves Exercise -completed UV Reactors, Sensor Check: -all sensors passed verification -ran UV #2 in local with cooling valves open for verification -site back to normal operation | Schomberg Water Treatment Plant & Wells 2-4 | 2025-12-09
WEST | December | -on site to complete station check and lab - plant duty active and high lift duty active -wells 2 and 4 in duty - KMnO4 pump 1 running at 13.8%, 70 psi, 62.6 ml/min - chlorinator 1 55% open, df 140%, 0.54 kg/hr, vac = -710 mbar - chlorinator 2 27% open, df 152%, 0.27 kg/hr, vac = -900 mbar - recorded data in PWQ sheet - checked equipment - CL17 reagents ok - reviewed trends - no issues found -completed wells 2,3,4 station checks 11:56 - adjusted flow to filter #3 turbidimeter causing turbidity reading spike -verified analyzers: 12:08 - high lift treated water TCL analyzer = 3.51 mg/L 12:08 - high lift treated water grab: FCL = 0.00 mg/L TCL = 3.58 mg/L Mono = 3.22 mg/L 12:12 - reservoir TCL analyzer = 3.83 mg/L 12:12 - reservoir grab: TCL = 3.82 mg/L Mono = 3.59 mg/L 12:21 - post filter TCL analyzer = 2.37 mg/L 12:21 - post filter grab: TCL = 2.38 mg/L -reduced KMnO4 pump #1 max flow setpoint from 460 to 455 ml/min based on dosage calculation -cleaned high lift turbidimeter vial -switched to north reservoir cell, adjusted sample valves accordingly -completed lab, results in PWQ sheet -cleaned UVT lens due to erratic readings over the weekend, no issues observed. Will continue to monitor -contractor on site to replace filters on generator, ran generator for a couple minutes to test - no issues -site back to normal operation | Schomberg Water Treatment Plant & Wells 2-4 | 2025-12-08
WEST | December | -on site to complete station check and lab - plant duty active and high lift duty active -wells 2 and 4 in duty - KMnO4 pump 2 running at 15.8%, 58 psi, 63.0 ml/min - chlorinator 1 54% open, df 140%, 0.54 kg/hr, vac = -710 mbar - chlorinator 2 29% open, df 160%, 0.28 kg/hr, vac = -850 mbar - recorded data in PWQ sheet - checked equipment - CL17 reagents ok - reviewed trends - no issues found -completed wells 2,3,4 station checks -verified analyzers: 10:16 - high lift treated water TCL analyzer = 3.20 mg/L 10:16 - high lift treated water grab: FCL = 0.00 mg/L TCL = 3.32/3.34/3.40 mg/L Mono = 3.06 mg/L 10:33 - adjusted treated water analyzer to 3.35 mg/L based on average of 3 grabs 10:40 - reservoir TCL analyzer = 3.81 mg/L 10:40 - reservoir grab: TCL = 3.76 mg/L Mono = 3.49 mg/L 10:57 - post filter TCL analyzer = 2.35 mg/L 10:57 - post filter grab: TCL = 2.32 mg/L -filled KMnO4 tank #2 19.5 cm to 86.3 cm -completed lab, results in PWQ sheet -received chlorine cylinder delivery, 12 cylinders | Schomberg Water Treatment Plant & Wells 2-4 | 2025-12-05
WEST | December | -on site to complete work orders -informed ROC of work -completed Compressed Air System, Inspection -rotated compressor duties -completed Backwash Sump Tank System, Inspection -completed high lift PRV test -adjusted to 120 PSI and tested with hydrostatic tester -completed UVT Unit Bulb Replacement -replaced UVT analyzer sample lines -completed KMnO4 Injection Point Cleaning -completed Filters 1-3, Turbidity Analyzer TU5300, Maintenance and Calibration -cleaned and verified turbidimeters, all passed verification -replaced sample lines -completed KMNO4 Feed Pumps, Service: -ran pumps into calibration column: Pump #1 max flow = 444 ml/min Pump #2 max flow = 400 ml/min -will continue to monitor dosage calculations -completed CL-17sc Analyzer, Maintenance: -cleaned analyzers, flushed sample lines -verified analyzers after maintenance: 13:36 - high lift treated water TCL analyzer = 3.25 mg/L 13:36 - high lift treated water grab: TCL = 3.26 mg/L 13:44 - reservoir TCL analyzer = 3.82 mg/L 13:44 - reservoir grab: TCL = 3.86 mg/L 13:55 - post filter TCL analyzer = 2.32 mg/L 13:55 - post filter grab: TCL = 2.32 mg/L -in preparation for well #3 rehab testing plant with wells 2 and 4 running -increased well #2 max flow setpoint from 17 to 18 l/s -filled KMnO4 tank #1 15.65 to 82.6 cm -site back to normal operation | Schomberg Water Treatment Plant & Wells 2-4 | 2025-12-02
WEST | December | -on site to complete station check, lab and to collect samples -micro sample work order # W11419315 - plant duty active, high lift duty active - KMnO4 pump 2 running at 15.8%, 58 psi, 62.1 ml/min - chlorinator 4 52% open, df 140%, 0.53 kg/hr, vac = -720 mbar - chlorinator 2 30% open, df 156%, 0.29 kg/hr, vac = -850 mbar - recorded data in PWQ sheet - checked equipment - CL17 reagents ok - reviewed trends - no issues found -verified analyzers: 08:35 - high lift treated water TCL analyzer = 3.23 mg/L 08:35 - high lift treated water grab: FCL = 0.02 mg/L TCL = 3.32 mg/L Mono = 3.01 mg/L 08:36 - collected weekly treated water micro sample 08:48 - reservoir TCL analyzer = 3.76 mg/L 08:48 - reservoir grab: TCL = 3.66 mg/L Mono = 3.46 mg/L 08:54 - post filter TCL analyzer = 2.29 mg/L 08:54 - post filter grab: TCL = 2.32 mg/L -collected monthly raw water iron and manganese sample - W/O # W11377166 -collected monthly filter effluent iron and manganese samples - W/O # W11419426 -completed Transfer Pump and Motor Inspection -completed Transfer Pump Air Relief Valves, Inspection 09:00 - collected weekly well #4 raw water micro sample -completed well #2 station check 09:28 - collected weekly well #2 raw water micro sample 10:40 - collected weekly well #3 raw water micro sample -completed lab, results in PWQ sheet | Schomberg Water Treatment Plant & Wells 2-4 | 2025-12-03
WEST | December | -on site to complete station check and lab -completed chlorine cylinder change - plant duty active and high lift duty active -wells 3 and 4 in duty - KMnO4 pump 1 running at 14.3%, 70 psi, 66.1 ml/min - chlorinator 4 62% open, df 140%, 0.58 kg/hr, vac = -700 mbar - chlorinator 2 29% open, df 164%, 0.28 kg/hr, vac = -860 mbar - recorded data in PWQ sheet - checked equipment - replaced high lift CL17 reagents - reviewed trends - no issues found -completed wells 2,3,4 station checks -verified analyzers: 11:54 - high lift treated water TCL analyzer = 3.33 mg/L 11:54 - high lift treated water grab: FCL = 0.00 mg/L TCL = 3.34 mg/L Mono = 3.10 mg/L 12:03 - reservoir TCL analyzer = 3.82 mg/L 12:03 - reservoir grab: TCL =3.78 mg/L Mono = 3.54 mg/L 12:10 - post filter TCL analyzer = 2.37 mg/L 12:10 - post filter grab: TCL = 2.32 mg/L -completed high lift turbidimeter maintenance: -cleaned and verified turbidimeter, no issues -decreased KMnO4 pump #1 max flow setpoint 465 to 460 ml/min based on dosage calculation -completed lab, results in PWQ sheet | Schomberg Water Treatment Plant & Wells 2-4 | 2025-12-01
WEST | December | -on site to complete work orders -informed ROC of work -completed JHSC Health and Safety Inspection, Schomberg WTP / Wells 3 & 4 -completed Chlorine Cylinder Emergency Repair Kit Inspection -completed Chlorine Scrubber, Media Sampling -completed Chemical System Inspection - Chlorine -vacuum tested chlorine system, no leaks observed -completed Rotate chlorinator #4 duty -chlorinators 1 and 2 now in service -completed Chlorine Leak Detector, Test -completed Chlorine Scrubber, Check -completed Diesel Generator Test Run: -pre inspection ok Start hours = 536.3 Stop hours = 537.7 Run time = 1.4 hours Fuel start = 1716 L / 1711 L Fuel Stop = 1705 L / 1691 L Fuel Used = 11 L / 20 L 11:48 - transfer to generator power -activated plant and high lift duty -transfer back to utility power -no issues with generator test run -site back to normal operation | Schomberg Water Treatment Plant & Wells 2-4 | 2025-12-04
WEST | December | -on site to respond to site power failure -UV1 and UV3 received low UV dose alarms due to power fail -from 13:16 to 13:17 UV dose was zero while flow meter registered flow, less than 10 minute limit -cleared alarms and restarted plant, checked generator and UV system - both operating normally | Schomberg Water Treatment Plant & Wells 2-4 | 2025-12-17
WEST | December | -plant interlock on raw water tank low low alarm -well 2 was in duty 4 - rotated duties and restarted plant | Schomberg Water Treatment Plant & Wells 2-4 | 2025-12-29
WEST | December | On site for Station Checks Check trends- All okay Verified Analyzers. Reservoir- Grab Total Cl2:3.52 mg/L, Analyzer- 3.44 mg/L Post filter- Grab Total Cl2:2.22 mg/L, Analyzer- 2.25 mg/L Highlift- Grab Total Cl2:3.70 mg/L, Analyzer- 3.70 mg/L Reagents all good Conducted in house lab analysis. Entered values in PWQ sheet Equipment okay | Schomberg Water Treatment Plant & Wells 2-4 | 2025-12-31
WEST | December | -on site to complete station check, lab and to collect samples -sample work order # W11483646 -completed chlorine cylinder change 09:09 - collected weekly well #4 raw water micro sample -completed well #2 station check 09:28 - collected weekly well #2 raw water micro sample 10:33 - collected weekly well #3 raw water micro sample - plant duty active, high lift duty active - KMnO4 pump 1 running at 16.5%, 70 psi, 66.6 ml/min - chlorinator 1 57% open, df 144%, 0.56 kg/hr, vac = -720 mbar - chlorinator 2 28% open, df 162%, 0.28 kg/hr, vac = -820 mbar - recorded data in PWQ sheet - checked equipment - replaced high lift CL17 reagents - reviewed trends - no issues found -verified analyzers: 10:58 - high lift treated water TCL analyzer = 3.43 mg/L 10:58 - high lift treated water grab: FCL = 0.03 mg/L TCL = 3.34 mg/L Mono = 3.00 mg/L 11:06 - collected weekly treated water micro sample 11:17 - reservoir TCL analyzer = 3.75 mg/L 11:17 - reservoir grab: TCL = 3.70 mg/L Mono = 3.22 mg/L 11:24 - post filter TCL analyzer = 2.34 mg/L 11:24 - post filter grab: TCL = 2.38 mg/L -filled KMnO4 tank #2 15.7 cm to 84.6 cm -cleaned high lift turbidimeter vial -completed lab, results in PWQ sheet | Schomberg Water Treatment Plant & Wells 2-4 | 2025-12-29
WEST | December | Responded to Compressor 1 fault (E:0821 shortcircuit), reset and cleared alarm | Schomberg Water Treatment Plant & Wells 2-4 | 2025-12-23
WEST | December | -on site to reset air compressors -short circuit alarm cause by power blips from ice storm -restarted plant and monitored air pressure -confirmed with ROC no UV alarms during power dips -checked trends no issues on site | Schomberg Water Treatment Plant & Wells 2-4 | 2025-12-28
WEST | December | Increased permanganate pump #1 max flow 375 to 385 ml/min based on dosage calculations | Schomberg Water Treatment Plant & Wells 2-4 | 2025-12-18
WEST | December | Documenting multiple power failures approx. 0600-0645. SHTP plant production was not active, no UV dosing at time of power failures. Compressor fault, will have it reset on site. | Schomberg Water Treatment Plant & Wells 2-4 | 2025-12-23
WEST | December | -on site to complete station check and lab - plant duty active and high lift duty active -wells 2 and 4 in duty - KMnO4 pump 1 running at 16.7%, 70 psi, 63.9 ml/min - chlorinator 1 56% open, df 144%, 0.55 kg/hr, vac = -760 mbar - chlorinator 2 27% open, df 160%, 0.27 kg/hr, vac = -860 mbar - recorded data in PWQ sheet - checked equipment - CL17 reagents ok - reviewed trends - no issues found -completed wells 2,3,4 station checks -verified analyzers: 08:13 - high lift treated water TCL analyzer = 3.37 mg/L 08:13 - high lift treated water grab: FCL = 0.00 mg/L TCL = 3.38 mg/L Mono = 2.97 mg/L 08:24 - reservoir TCL analyzer = 3.63 mg/L 08:24 - reservoir grab: TCL = 3.58 mg/L Mono = 3.25 mg/L 08:27 - post filter TCL analyzer = 2.38 mg/L 08:27 - post filter grab: TCL = 2.30 mg/L -filled KMnO4 tank #2 15.7 cm to 82.4 cm -filled KMnO4 tank #1 59.4 cm to 82.9 -received UV#3 minor fault due to lamps 2, 3 and 4 reaching 5000 run hours. Replaced UV#3 bulbs 2, 3 and 4 -replaced UV#1 bulbs 1,2,3 and 4 as run hours were close to 5000 -restarted plant, no issues with UV start up -completed lab, results in PWQ sheet | Schomberg Water Treatment Plant & Wells 2-4 | 2025-12-24
WEST | December | -received call at 12:35am - low raw water tank -request plant flow adjusted 34-32l/s | Schomberg Water Treatment Plant & Wells 2-4 | 2025-12-30
WEST | December | -on site to complete station check and lab - plant duty active and high lift duty active -wells 2 and 4 in duty - KMnO4 pump 2 running at 15.8%, 58 psi, 62.8 ml/min - chlorinator 1 56% open, df 142%, 0.54 kg/hr, vac = -720 mbar - chlorinator 2 30% open, df 162%, 0.29 kg/hr, vac = -840 mbar - recorded data in PWQ sheet - checked equipment - CL17 reagents ok - reviewed trends - no issues found -completed wells 2,3,4 station checks -verified analyzers: 08:08 - high lift treated water TCL analyzer = 3.39 mg/L 08:08 - high lift treated water grab: FCL = 0.00 mg/L TCL = 3.34 mg/L Mono = 2.95 mg/L 08:58 - reservoir TCL analyzer = 3.69 mg/L 08:58 - reservoir grab: TCL = 3.66 mg/L Mono = 3.31 mg/L 09:06 - post filter TCL analyzer = 2.27 mg/L 09:06 - post filter grab: TCL = 2.30 mg/L -completed Pressure Relief Valve, Inspection Well #2 -installed check valve on reservoir sample pump #2, will monitor flow -filled KMnO4 tank #1 15.7 cm to 81.2 cm -completed lab, results in PWQ sheet | Schomberg Water Treatment Plant & Wells 2-4 | 2025-12-19
WEST | December | Power failure occurred at 1316, hydro pole taken out from vehicle collision at Hwy27 and Dillane. Plant shutdown normally on power failure, UV system appears to have interlocked normally. Filter discharge flow registered for less than 10 minutes while UV dose below 40mj/cm2. Reset alarms and started plant. Power restored approx 1520. Plant shutdown again during power transfer to utility. UVs appear to have interlocked normally, filter discharge flow registered for less than 10 minutes again while UV dose below 40mj/cm2. | Schomberg Water Treatment Plant & Wells 2-4 | 2025-12-17
WEST | December | -ack and reset phase alarms -power blips caused severe snow storm -no UV alarms -deactivated highlifts to reduce energy use and protect pumps from further outages | Schomberg Water Treatment Plant & Wells 2-4 | 2025-12-29
WEST | December | -on site to complete station check, lab and to collect samples -sample work order # W11454909 - plant duty active, high lift duty active - KMnO4 pump 1 running at 17.7%, 70 psi, 65.8 ml/min - chlorinator 1 62% open, df 140%, 0.61 kg/hr, vac = -700 mbar - chlorinator 2 32% open, df 164%, 0.32 kg/hr, vac = -840 mbar - recorded data in PWQ sheet - checked equipment - replaced reservoir and post filter CL17 reagents - reviewed trends - no issues found -verified analyzers: 09:02 - high lift treated water TCL analyzer = 3.38 mg/L 09:02 - high lift treated water grab: FCL = 0.02 mg/L TCL = 3.42 mg/L Mono = 3.06 mg/L 09:08 - collected weekly treated water micro sample 10:12 - collected weekly well #3 raw water micro sample 10:12 - collected weekly well #4 raw water micro sample 10:29 - reservoir TCL analyzer = 3.84 mg/L 10:29 - reservoir grab: TCL = 3.74 mg/L Mono = 3.60 mg/L 10:44 - post filter TCL analyzer = 2.24 mg/L 10:44 - post filter grab: TCL = 2.22 mg/L -completed well #2 station check 11:27 - collected weekly well #2 raw water micro sample -increased chlorinator #1 DF 140 to 142% -completed lab, results in PWQ sheet -completed cylinder change -filled KMnO4 tank #2 15.7 cm to 82.0 cm | Schomberg Water Treatment Plant & Wells 2-4 | 2025-12-16
WEST | December | Station Check (no issues found) Input data to PWQ Verified Analyzers (mg/L): Pre-Injection Free: Grab 0.01, A 0.00 Total: Grab 1.50, A 1.57 Mono: Grab 1.26, A 1.32 FA: Grab 0.06, A 0.07 TA: Grab 0.31, A 0.28 Post Injection: Free: Grab 0.04, A 0.02 Total: Grab 2.10, A 2.14 Mono: Grab 1.79, A 1.93 FA: Grab 0.05, A 0.02 TA: Grab 0.41, A 0.33 Reagents: Chemscan (grey, distilled & distilled/muratic top ups) Depolox (Acetate top ups) | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2025-12-15
WEST | December | -on site to complete station check, lab and to collect samples -sample work order # W11470016 - plant duty active, high lift duty active - KMnO4 pump 2 running at 15.8%, 58 psi, 62.4 ml/min - chlorinator 1 55% open, df 142%, 0.54 kg/hr, vac = -760 mbar - chlorinator 2 29% open, df 170%, 0.28 kg/hr, vac = -860 mbar - recorded data in PWQ sheet - checked equipment - CL17 reagents ok - reviewed trends - no issues found -verified analyzers: 08:16 - high lift treated water TCL analyzer = 3.46 mg/L 08:16 - high lift treated water grab: FCL = 0.05 mg/L TCL = 3.42 mg/L Mono = 3.10 mg/L 08:26 - collected weekly treated water micro sample 08:31 - reservoir TCL analyzer = 3.68 mg/L 08:31 - reservoir grab: TCL = 3.70 mg/L Mono = 3.29 mg/L 08:41 - post filter TCL analyzer = 2.30 mg/L 08:41 - post filter grab: TCL = 2.28 mg/L 08:50 - collected weekly well #4 raw water micro sample -increased chlorinator #1 DF 142 to 144% -rotated to south reservoir cell, adjusted sample pump valving -installed check valve on sample pump #1 09:38 - collected weekly well #3 raw water micro sample -completed well #2 station check 09:57 - collected weekly well #2 raw water micro sample -cleaned high lift turbidimeter vial -completed lab, results in PWQ sheet | Schomberg Water Treatment Plant & Wells 2-4 | 2025-12-22
WEST | December | On site for station check Rechlor Pre inj (mg/L) Fcl Analyzer: 0.00; Grab: 0.05 TCL Analyzer: 1.52; Grab: 1.49 Fa Analyzer: 0.09; Grab: 0.07 Ta Analyzer: 0.32; Grab: 0.33 Mcl Analyzer: 1.31; Grab: 1.28 Nitrite: 0.001mg/L Post inj Fcl Analyzer: 0.02; Grab: 0.05 TCL Analyzer: 1.95; Grab: 1.97 Fa Analyzer: 0.02; Grab: 0.06 Ta Analyzer: 0.32; Grab: 0.39 Mcl Analyzer: 1.81; Grab: 1.69 Nitrite: 0.001mg/L Topped up ammonia tank 1 from 14-90cm (5 bags) ((75cm/1140L)*1375L=90.461 cm) Reagents all ok | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2025-12-12
WEST | December | On site for station check and to collect weekly back same w11438655 Reservoir @10:00am North Cell Sample Tap: Total: 2.18mg/L Free: 0.06mg/L SL1000 TCL 2.19mg/L FA 0.09mg/L TA 0.47mg/L Mono 1.93mg/L Nitrite 0mg/L West Cell Sample Tap: Total: 2.11mg/L Free: 0.06mg/L South Cell Sample Tap: Total: 2.03mg/L Free: 0.04mg/L Rechlor Pre inj (mg/L) Fcl Analyzer: 0.00; Grab: 0.03 TCL Analyzer: 1.57; Grab: 1.71 Fa Analyzer: 0.04; Grab: 0.07 Ta Analyzer: 0.36; Grab: 0.37 Mcl Analyzer: 1.53; Grab: 1.49 Nitrite: 0.000mg/L Adjusted TCL from 1.57-1.71mg/L after multiple grabs and to match chem scan (1.68mg/L) Adjusted FA offset by 0.03mg/L after multiple grabs and dosages. Post inj Fcl Analyzer: 0.00; Grab: 0.03 TCL Analyzer: 1.67; Grab: 1.72 Fa Analyzer: 0.02; Grab: 0.05 Ta Analyzer: 0.33; Grab: 0.37 Mcl Analyzer: 1.63; Grab: 1.52 Nitrite: 0.000mg/L Changed out pre deploys reagents ki No other issues on site | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2025-12-10
WEST | December | On site for station check Rechlor Pre inj (mg/L) Fcl Analyzer: 0.00; Grab: 0.05 TCL Analyzer: 1.57; Grab: 1.69 Fa Analyzer: 0.05; Grab: 0.07 Ta Analyzer: 0.34; Grab: 0.36 Mcl Analyzer: 1.40; Grab: 1.45 Post inj Fcl Analyzer: 0.02; Grab: 0.04 TCL Analyzer: 2.00; Grab: 2.06 Fa Analyzer: 0.04; Grab: 0.09 Ta Analyzer: 0.40; Grab: 0.44 Mcl Analyzer: 1.87; Grab: 1.80 Reagents all ok | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2025-12-01
WEST | December | On site for station check and to collect weekly back same w11419287 Reservoir @11:15am North Cell Sample Tap: Total: 2.13mg/L Free: 0.03mg/L SL1000 TCL 2.12mg/L FA 0.12mg/L TA 0.49mg/L Mono 1.88mg/L West Cell Sample Tap: Total: 2.07mg/L Free: 0.04mg/L South Cell Sample Tap: Total: 1.99mg/L Free: 0.04mg/L Rechlor Pre inj (mg/L) Fcl Analyzer: 0.00; Grab: 0.05 TCL Analyzer: 1.60; Grab: 1.70 Fa Analyzer: 0.07; Grab: 0.09 Ta Analyzer: 0.37; Grab: 0.39 Mcl Analyzer: 1.50; Grab: 1.48 N02: 0.000mg/L Post inj Fcl Analyzer: 0.02; Grab: 0.05 TCL Analyzer: 2.04; Grab: 2.09 Fa Analyzer: 0.04; Grab: 0.09 Ta Analyzer: 0.43; Grab: 0.48 Mcl Analyzer: 1.96; Grab: 1.82 NO2: 0.000mg/L Reagents all ok Topped up ammonia tank 1 from 14-74cm | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2025-12-03
WEST | December | Receiver delivery for skid of ammonia sulfate. | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2025-12-05
WEST | December | On site for station check Rechlor Pre inj (mg/L) Fcl Analyzer: 0.00; Grab: 0.05 TCL Analyzer: 1.60; Grab: 1.63 Fa Analyzer: 0.03; Grab: 0.05 Ta Analyzer: 0.32; Grab: 0.33 Mcl Analyzer: 1.42; Grab: 1.40 Nitrite: 0.001mg/L Post inj Fcl Analyzer: 0.00; Grab: 0.00 TCL Analyzer: 2.30; Grab: 2.33 Fa Analyzer: 0.04; Grab: 0.11 Ta Analyzer: 0.43; Grab: 0.50 Mcl Analyzer: 2.07; Grab: 1.95 Nitrite: 0.000mg/L Changed chlorine cylinders with Jake Muzzin bank 1 from 0-68kg | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2025-12-09
WEST | December | Onsite for station check duty not active Checked residuals mg/l Pre inj @1323 TCL analyzer 1.68 grab 1.66 Fcl analyzer 0.02 grab 0.03 F nh3 analyzer 0.02 grab 0.09 T nh3 analyzer 0.27 grab 0.38 Mcl analyzer 1.65 grab 1.46 Post @1324 TCL analyzer 2.05 grab 1.97 Fcl analyzer 0.02 grab 0.03 F nh3 analyzer 0.03 grab 0.06 T nh3 analyzer 0.41 grab 0.40 Mcl analyzer 1.97 grab 1.75 Reagents ok | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2025-12-04
WEST | December | On site for station check Rechlor Pre inj (mg/L) Fcl Analyzer: 0.00; Grab: 0.05 TCL Analyzer: 1.52; Grab: 1.54 Fa Analyzer: 0.03; Grab: 0.05 Ta Analyzer: 0.30; Grab: 0.32 Mcl Analyzer: 1.37; Grab: 1.34 Nitrite: 0.000mg/L Post inj Fcl Analyzer: 0.02; Grab: 0.05 TCL Analyzer: 2.27; Grab: 2.31 Fa Analyzer: 0.04; Grab: 0.09 Ta Analyzer: 0.49; Grab: 0.54 Mcl Analyzer: 2.14; Grab: 1.99 Nitrite: 0.001mg/L Topped up ammonia tank 2 from 14-74cm Reagents all ok | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2025-12-08
WEST | December | Onsite for chlorinator rebuilds Co-ordinated with ROC and operations Purged chlorine to waste Rebuilt chlorinators and performed vacuum test. All ok Calibrated chlorinators pushing water to waste. All ok Cleared associated alarms System back to auto and duty active. Monitored for a while. No issues observed Informed ROC and operations Armed building and left site | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2025-12-04
WEST | December | On site for jhsc inspection | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2025-12-02
WEST | December | -on site for station check -checked trends: all ok -entered readings in PWQ: -verified pre-analyzer 13:35 -analyzer free: 0.01mg/l grab: 0.03mg/l -analyzer total: 1.41mg/l grab: 1.39mg/l -reagents all ok -verified post- analyzer 13:40 -analyzer free: 0.02mg/l grab: 0.06mg/l - adjusted -analyzer total: 2.31mg/l grab: 2.30mg/l -reagents all ok -topped up ammonia tank 2 - 241l - 1155L -verified chem scan -adjusted post free ammonia 0.02mg/l to 0.08mg/l (-0.03/0.03 offset) -topped up green/grey/yellow reagents -created spare bottles with fresh reagent and updated labels | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2025-12-30
WEST | December | -on site to complete station check and collect weekly bacti W11483618 -checked trends: all ok Total Ammonia 0.41mg/l Free Ammonia 0.07mg/l Nitrite 0.00mg/l Monochloramine 1.74mg/l - took chlorine grab of north cell 11:35 -free cl: 0.02mg/l -total cl: 1.93mg/l -equipment all ok | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2025-12-29
WEST | December | -on site for station check -Joe w on site to changes cylinders -65.3kg- 133.3kg -verified analyzer -pre injection 09:55 -analyzer free: 0mg/l grabs: 0.02mg/l - cal zero free reading and adjusted -analyzer total: 1.60mg/l grabs: 1.46mg/l - adjusted -post injection 10:15 -analyzer free: 0.02mg/l grab: 0.04mg/l -analyzer total: 2.16mg/l grab: 2.10mg/l - adjusted -topped up reagents -verified chem scan -adjusted pre mono reading 1.37- 1.29 (off set 0.05/ -0.03) -adjusted post total ammonia 0.30 - 0.42 (off set -0.03/0.09 -reagents all ok -switched to ammonia tank 1 and topped up tank 2 23.11cm - 83.11cm | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2025-12-18
WEST | December | On site for station check and to collect weekly back same w11454881 Reservoir @11:30am North Cell Sample Tap: Total: 1.95mg/L Free: 0.06mg/L SL1000 TCL 1.98mg/L FA 0.05mg/L TA 0.39mg/L Mono 1.69mg/L Nitrite 0.001mg/L West Cell Sample Tap: Total: 2.08mg/L Free: 0.05mg/L South Cell Sample Tap: Total: 1.98mg/L Free: 0.04mg/L Rechlor Pre inj (mg/L) Fcl Analyzer: 0.00; Grab: 0.05 TCL Analyzer: 1.81; Grab: 1.76 Fa Analyzer: 0.05; Grab: 0.06 Ta Analyzer: 0.34; Grab: 0.36 Mcl Analyzer: 1.53; Grab: 1.51 Nitrite: 0.002mg/L Post inj Fcl Analyzer: 0.02; Grab: 0.05 TCL Analyzer: 2.02; Grab: 1.95 Fa Analyzer: 0.02; Grab: 0.05 Ta Analyzer: 0.31; Grab: 0.36 Mcl Analyzer: 1.78; Grab: 1.68 Nitrite: 0.000mg/L No issues | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2025-12-16
WEST | December | -on site to complete station check and collect weekly bacti W11470054 -checked trends: all ok -entered readings in PWQ: - took chlorine grab of north cell 10:20 -free cl: 0.10mg/l -total cl: 2.00mg/l -equipment all ok -completed station of re-chlor building -pre injection analyzer 10:50 -free cl: 0.02mg/l grab: 0.03mg/l -total cl: 1.44mg/l grab: 1.44mg/l -reagents all ok -post injection analyzer 11:00 -analyzer free: 0.02mg/l grab: -analyzer total: 2.25mg/l grab: -reagents all ok -equipment all ok | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2025-12-22
LINEAR | December | Replenished dechlorination pucks at McCowan an Stoufville break site. Chlorine residuals Free - 0.00 mg/l Total - 0.00 mg/ | Linear Water System | 2025-12-13
WEST | December | -on site for station check - entered readings in PWQ: all ok -verified pre analyzer 10:45 -analyzer free:0.02mg/l grab: 0.03mg/l -analyzer total: 1.40mg/l grab: 1.37mg/l -reagents all ok -verified post analyzer 10:55 -analyzer free: 0.02mg/l grab: 0.05mg/l -analyzer total: 2.27mg/l grab: 2.22mg/l -reagents all ok -topped ammonia tank 1 17- 78cm -no issues -adjusted post mono 2.11mg/l - 1.94mg/l - (0.16/-0.01) -chem scan reagents all ok | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2025-12-24
LINEAR | December | Replenished dechlorination pucks at McCowan an Stoufville break site. Chlorine residuals Free - 0.00 mg/l Total - 0.00 mg/l | Linear Water System | 2025-12-09
LINEAR | December | Replenished dechlorination pucks at McCowan an Stoufville break site. Chlorine residuals Free - 0.00 mg/l Total - 0.00 mg/l | Linear Water System | 2025-12-10
LINEAR | December | Replenished dechlorination pucks at McCowan an Stoufville break site. Chlorine residuals Free - 0.00 mg/l Total - 0.00 mg/ | Linear Water System | 2025-12-14
LINEAR | December | Replenished dechlorination pucks at McCowan an Stoufville break site. Chlorine residuals Free - 0.00 mg/l Total - 0.00 mg/l | Linear Water System | 2025-12-12
LINEAR | December | Replenished dechlorination pucks at McCowan an Stoufville break site. Chlorine residuals Free - 0.00 mg/l Total - 0.00 mg/l | Linear Water System | 2025-12-06
LINEAR | December | Replenished dechlorination pucks at McCowan an Stoufville break site. Chlorine residuals Free - 0.00 mg/l Total - 0.00 mg/l | Linear Water System | 2025-12-01
LINEAR | December | Replenished dechlorination pucks at McCowan an Stoufville break site. Chlorine residuals Free - 0.00 mg/l Total - 0.00 mg/l | Linear Water System | 2025-12-05
LINEAR | December | Replenished dechlorination pucks at McCowan an Stoufville break site. Chlorine residuals Free - 0.00 mg/l Total - 0.00 mg/l | Linear Water System | 2025-12-08
LINEAR | December | Replenished declorination pucks at leak site on Stouffville Rd east of McCowan Rd. Grab chlorine residual tests as follows, Free- 0.00mg/l Total- 0.00 mg/l | Linear Water System | 2025-12-03
LINEAR | December | Worked with North Rock on the Air Valve Mod project to replace an air valve at the corner of Kennedy and Metro road in Georgina. Once the new air valve was installed we collected a grab chlorine residual test. Free-1.54mg/l Total- 1.87mg/l. All valves are open and the system is back to normal operation. | Linear Water System | 2025-12-09
LINEAR | December | Replenished dechlorination pucks at McCowan an Stoufville break site. Chlorine residuals Free - 0.00 mg/l Total - 0.00 mg/l | Linear Water System | 2025-12-07
LINEAR | December | Replenished dechlorination pucks at McCowan an Stoufville break site. Chlorine residuals Free - 0.00 mg/l Total - 0.00 mg/l | Linear Water System | 2025-12-04
LINEAR | December | Replenished declorination pucks at leak site on Stouffville Road east of McCowan road and took grab chlorine residual tests. Free- 0.00mg/l Total- 0.00 mg/l | Linear Water System | 2025-12-02
LINEAR | December | Replenished the declorination pucks at the break site on Stouffville Road east of McCowan Road. Grab chlorine residual test as follows Free- 0.00mg/l Total- 0.00mg/l | Linear Water System | 2025-12-30
LINEAR | December | The bypass for the Stouffville main break is now in service. The mainline valves have been throttled down to 4 turns open (2 off the seat). Positive pressure is being maintained at a much slower flow rate. Clearway and the consultant will be physically monitoring the bypass for the next 24 hrs round the clock. Dechlor pucks have been replenished. Residuals Free - 0.00 mg/l Total - 0.00 mg/l | Linear Water System | 2025-12-27
LINEAR | December | Replenished the declorination pucks at the break site on Stouffville Road east of McCowan Road. Grab chlorine residual test as follows Free- 0.00mg/l Total- 0.00mg/l | Linear Water System | 2025-12-31
LINEAR | December | Replenished the declorination pucks at the break site on Stouffville Road east of McCowan Road. Grab chlorine residual test as follows Free- 0.00mg/l Total- 0.00mg/l | Linear Water System | 2025-12-26
LINEAR | December | Replenished the declorination pucks at the break site on Stouffville Road east of McCowan Road. Grab chlorine residual test as follows Free- 0.00mg/l Total- 0.00mg/l | Linear Water System | 2025-12-25
LINEAR | December | Replenished the declorination pucks at the break site on Stouffville Road east of McCowan Road. Grab chlorine residual test as follows Free- 0.00mg/l Total- 0.00mg/l | Linear Water System | 2025-12-24
LINEAR | December | Replenished the declorination pucks at the break site on Stouffville Road east of McCowan Road. Grab chlorine residual test as follows Free- 0.00mg/l Total- 0.00mg/l | Linear Water System | 2025-12-20
LINEAR | December | Replenished the declorination pucks at the break site on Stouffville Road east of McCowan Road. Grab chlorine residual test as follows Free- 0.00mg/l Total- 0.00mg/l | Linear Water System | 2025-12-29
LINEAR | December | Replenished dechlorination pucks at McCowan an Stoufville break site. Chlorine residuals Free - 0.00 mg/l Total - 0.00 mg/ | Linear Water System | 2025-12-16
LINEAR | December | Replenished the declorination pucks at the break site on Stouffville Road east of McCowan Road. Grab chlorine residual test as follows Free- 0.00mg/l Total- 0.00mg/l | Linear Water System | 2025-12-28
LINEAR | December | Replenished dechlorination crystals at McCowan an Stoufville break site . Chlorine residuals Free - 0.00 mg/l Total - 0.00 mg/ | Linear Water System | 2025-12-18
LINEAR | December | Replenished the declorination pucks at the break site on Stouffville Road east of McCowan Road. Grab chlorine residual test as follows Free- 0.00mg/l Total- 0.00mg/l | Linear Water System | 2025-12-22
LINEAR | December | Replenished the declorination pucks at the break site on Stouffville Road east of McCowan Road. Grab chlorine residual test as follows Free- 0.00mg/l Total- 0.00mg/l | Linear Water System | 2025-12-21
LINEAR | December | Replenished dechlorination crystals at McCowan an Stoufville break site . Chlorine residuals Free - 0.00 mg/l Total - 0.00 mg/ | Linear Water System | 2025-12-19
LINEAR | December | Replenished the declorination pucks at the break site on Stouffville Road east of McCowan Road. Grab chlorine residual test as follows Free- 0.00mg/l Total- 0.00mg/l | Linear Water System | 2025-12-23
WW-WEST | December | Harie Rajamithiran(OIT) working under the direction of Daniel Hirstwood(OIC) -Supernated sludge thickening tank and transferred to sludge holding tank -Completed lab analysis, no abnormalities found -Started batch wasting process at 10:00 -Wasting from 11:00-13:00 for 25m^3 per train in 6 cycles -Returned RAS pumps back to auto -Completed station check, no abnormalities found - Added 2 bags of soda ash into each aeration tank -Completed aeration solids removal, foam still exists and some solids slip away from reach points -Bled condensation from aeration tank air lines | Nobleton Water Resource Recovery Facility | 2025-12-11
WW-WEST | December | Harie Rajamithiran(OIT) working under the direction of Lance Johnson(OIC) -Transferred sludge from thickening tank directly to holding tank -Completed lab analysis, no abnormalities found -Turned off RAS at 9:06 -Started wasting from 10:00-12:00 in 6 cycles for 15m^3 per train -Returned RAS pumps in auto when completed -Added 2 bags of soda ash in each aeration tank | Nobleton Water Resource Recovery Facility | 2025-12-10
WW-WEST | December | In to Complete Scheduled WO. Process Building Gas Detector Alarm Active Upon Arrival. O2 Readings @ 10.0%, Ventilated Building Whilst On-site. Added Soda Ash to Both Aer. Tanks ?> 2 Bags Each. Salted Aer. Tank Steps and Walkways. | Nobleton Water Resource Recovery Facility | 2025-12-14
WW-WEST | December | Completed work orders with Harie | Nobleton Water Resource Recovery Facility | 2025-12-10
WW-WEST | December | - Received alum delivery at 13:00. Checked certificate of authenticity. Signed all papers. Received from 0.86 m to 3.62 m. No issues while receiving. For payment processing, sent a copy to Adriana Posea - Performed in-house lab and recorded readings on SharePoint - Decanted the sludge thickening tank. Once done, transferred sludge into the holding tank - Added 2 bags of soda ash per each aeration tank - Performed station check and recorded readings on SharePoint - Created work order for process building gas detector alarm and warning - Made sampling bottles for sampling tomorrow | Nobleton Water Resource Recovery Facility | 2025-12-15
WW-WEST | December | Harie Rajamithiran(OIT) working under the direction of Daniel Hirstwood(OIC) -Supernated sludge thickening tank and transferred to sludge holding tank -Completed lab analysis, no abnormalities found -Started batch wasting process at 11:00 -Wasting from 12:00-14:00 for 25m^3 per train in 6 cycles -Completed station check, no abnormalities found - Added 2 bags of soda ash into each aeration tank -Put RAS in auto -Put WAS in manual off | Nobleton Water Resource Recovery Facility | 2025-12-12
WW-WEST | December | Harie Rajamithiran(OIT) working under the direction of Lance Johnson(OIC) -Completed station check and found aeration blower #1 rubber flange leak , created work order for the repair -Inspected aeration blowers -Cleaned aeration inlet/outlet rags -Checked online DO probes | Nobleton Water Resource Recovery Facility | 2025-12-10
WW-WEST | December | Wasted 10 m3 more in 2 cycles from train 2. Set return pumps to auto when complete. | Nobleton Water Resource Recovery Facility | 2025-12-05
WW-WEST | December | Completed work orders with Harie. | Nobleton Water Resource Recovery Facility | 2025-12-08
WW-WEST | December | Supernated STT and released to SHT. Shut RAS off at 8:00. Set auto wasting for 15 m3 per train in three cycles between 9:00 and 11:00. | Nobleton Water Resource Recovery Facility | 2025-12-05
WW-WEST | December | Collected weekly compliance samples. | Nobleton Water Resource Recovery Facility | 2025-12-09
WW-WEST | December | Started supernate pump in STT. Started labs. Collected monthly and weekly compliance samples. | Nobleton Water Resource Recovery Facility | 2025-12-02
WW-WEST | December | Assisted Harie. | Nobleton Water Resource Recovery Facility | 2025-12-09
WW-WEST | December | Completed labs and entered numbers in ace sheet. Added 2 bags soda ash to each train. Opened aeration outlet to clarifier 2. Closed aeration interconnect. Opened clarifier 2 RAS inlet. Enabled 275 minute batch wasting timer at 11:41. Set all RAS pumps and RAS valves to auto. Set pump 3 to standby to train 1. Set auto wasting between 13:00 and 15:00 to waste 40 m3 in 8 cycles. Return pumps in auto when complete. Checked basement sump pumps. ROC received high level alarm. Adjusted RAS system so pump 3 is standby to train 2. (Valves in correct positions, but dashed box is not. Ignore box for now.) Set pumps to flow control, rather than ratio control. Set flow rate to 16 l/sec. | Nobleton Water Resource Recovery Facility | 2025-12-02
WW-WEST | December | Harie Rajamithiran(OIT) working under the direction of Lance Johnson(OIC) -Supernated sludge thickening tank to sludge holding tank -Completed lab analysis, no abnormalities found -Completed station check, no abnormalities found -Added 2 bags soda ash into each aeration tank -Turned off the RAS at 8:35 -Wasted 20m^3 from each train in 8 cycles between 10:00 and 12:00 -Wasted additional 10m^3 from train 2 in 2 cycles -Return pumps in auto when complete. -Adjusted duty 2 Min. DO from 1.15 mg/L to 1.50 mg/L -Inspected grit vortex 1 and 2. -Inspected Debris auger. -Inspected bar screen. -Inspected grit screw. -No issues with any of the above. | Nobleton Water Resource Recovery Facility | 2025-12-08
WW-WEST | December | Harie Rajamithiran(OIT) working under the direction of Lance Johnson(OIC) -Supernated raw sewage -Completed lab analysis, no abnormalities found -Added 2 bags of soda ash into each aeration tank -Completed station check, no abnormalities found -Wasted 40m^3 from 9:00 - 11:37 | Nobleton Water Resource Recovery Facility | 2025-12-05
WW-WEST | December | Remotely Responded to Aer. Tank #2 Lo DO Alarm Communicated by the ROC. Reviewed Previous Days In-House Laboratory Analysis Results and SCADA. Outlet DO Trends Indicate a Gradual Decrease in Concentration, No Obstruction to Aer. Tank Inlet Suspected at Present. Remotely Rotated Duty #2 Blower Control to Aer. Tank #2. DO Recovered and Alarms Cleared. Advised ROC to Continue to Monitor and Notify if Issue Persists. | Nobleton Water Resource Recovery Facility | 2025-12-06
WW-WEST | December | Supernated STT and released to SHT. Shut RAS off at 10:00. Set auto wasting for 40 m3 in 8 cycles between 11:00 and 13:00. Completed labs. Completed station check - no issues found. Added 2 bags of soda ash to each train. Completed JHSC inspection - no issues found. Checked for hazardous waste. Found pail of used oil to go to Newmarket tomorrow. Inspected east and west clarifiers. | Nobleton Water Resource Recovery Facility | 2025-12-01
WW-WEST | December | Completed the station check and daily lab work Removed floating debris from the aeration tank Added 2 bags of soda ash to each aeration tank Decanted then emptied the sludge thickening tank Batch wasted 15m3 from clarifier 1 and 20m3 from clarifier 2 | Nobleton Water Resource Recovery Facility | 2025-12-04
WW-WEST | December | Started supernate pump. Removed floating solids from filtration inlet channel. Removed floating solids from aeration tank surface. Checked for aeration tank air line condensation. None found. Confirmed D O probe operation. Okay. Checked heat trace on headworks building. Not okay. Created work order for repair. | Nobleton Water Resource Recovery Facility | 2025-12-04
WW-WEST | December | Harie Rajamithiran(OIT) working under the direction of Lance Johnson(OIC) -Supernated sludge thickening tank and released to sludge holding tank -Collected weekly compliance samples -Completed lab analysis, no abnormalities found -Started 300 minute wasting process at 10:00 -Set up wasting from 11:00-13:00 in 6 cycles, 15m^3 per each train -Completed station check , no abnormalities found -Added 2 bags of soda ash in each aeration tank | Nobleton Water Resource Recovery Facility | 2025-12-09
WW-WEST | December | In to Complete Scheduled WO. Shovelled and Salted Aer. Tank and Clarifier Walkways and Stairs. Added Soda Ash to Both Aer. Tanks ?> 2 Bags Each. | Nobleton Water Resource Recovery Facility | 2025-12-07
WW-WEST | December | Remotely Responded to Aer. Tank #2 Lo DO Alarm Communicated by the ROC. Reviewed SCADA and Trends. Outlet Analyzer Concentrations Indicate a Gradual Decrease in DO, No Obstruction to Aer. Tank Inlet Suspected at Present. Remotely Rotated Duty #2 Blower Control to Aer. Tank #1. DO Recovered and Alarms Cleared. Advised ROC to Manually Activate a Secondary Blower if Issue Persists. | Nobleton Water Resource Recovery Facility | 2025-12-08
WW-WEST | December | On site to finish N20 wiring temporarily disconnected O2 sensor to replace electrical connection box wiring completed device to be powered up and calibrated | Nobleton Water Resource Recovery Facility | 2025-12-03
WW-WEST | December | Harie Rajamithiran(OIT) working under the direction of Lance Johnson(OIC) -Supernated sludge thickening tank -Completed lab analysis, no abnormalities found -Completed station check, no abnormalities found | Nobleton Water Resource Recovery Facility | 2025-12-17
WW-WEST | December | Supernated STT and released to SHT. Shut RAS off at 9:02. Wasted 15 m3 per train, 30 total, between 10:00 and 11:46 in 6 cycles. Return pumps in auto when complete. Completed labs and entered numbers in ACE sheets. Completed station check. No issues found. Added 2 bags soda ash to each train. Cleaned aeration outlet weirs. | Nobleton Water Resource Recovery Facility | 2025-12-03
WW-WEST | December | Released supernated sludge to thickening tank. Shut RAS pumps off at 9:30. Set auto wasting for 45 m3 in 8 cycles between 11:00 and 13:00. Checked sanitary sewer pumps and high level alarm. ROC received high level alarm. Inspected and confirmed online DO probes. Bled aeration air line condensation. Added 2 bags soda ash to each train. | Nobleton Water Resource Recovery Facility | 2025-12-17
WW-WEST | December | On site to troubleshoot head works screenings press heat trace. Controller display is not functioning correctly but the heat trace is still working. Have to source a replacement controller. | Nobleton Water Resource Recovery Facility | 2025-12-16
WW-WEST | December | Completed labs and entered numbers in ACE sheets. Completed station check. Added 2 bags soda ash to each train. Return pumps in auto when wasting complete. | Nobleton Water Resource Recovery Facility | 2025-12-16
WW-WEST | December | Supernated STT and released to SHT. Completed labs. Final TSS result was a bit high, but i suspect it was scale error. Tested a grab sample and received 2.4 mg/L. Added 2 bags soda ash to each train. Enabled 220 minute ras timer. Set auto wasting for 50 m5 between 11:00 and 13:00 in 8 cycles. Wasted a bonus 5 m3 from tank 1. Completed station check. No issues found. | Nobleton Water Resource Recovery Facility | 2025-12-24
WW-WEST | December | Supernated STT and released to SHT. Added 2 bags soda ash to each train. Completed station check. No issues found. Enabled 200 minute was timer. Set auto wasting for 40 m3 between 14:00 and 16:00 in 8 cycles. Worked on alum pump drawdown work order. | Nobleton Water Resource Recovery Facility | 2025-12-22
WW-WEST | December | Supernated STT and released to SHT. Started labs. Collected weekly compliance samples. Shut RAS pumps off at 9:00. Set auto wasting for 55 m3 between 10:00 and 12:00. | Nobleton Water Resource Recovery Facility | 2025-12-16
WW-WEST | December | Re-enabled ras timer ar 12:18. Set auto wasting for 55 m3 between 13:00 and 15:00 in 8 cycles Completed labs and entered numbers in ACE sheets. Completed station check. No issues found. Added 2 bags soda ash to each train. Unplugged sand washer on filter 4b. | Nobleton Water Resource Recovery Facility | 2025-12-30
WW-WEST | December | Checked with operator and found blower 1 rubber out let is leaking. Measured outlet pipe and will get new outlet rubber to make repairs. | Nobleton Water Resource Recovery Facility | 2025-12-18
WW-WEST | December | Supernated STT. Started labs. Collected weekly compliance samples. | Nobleton Water Resource Recovery Facility | 2025-12-23
WW-WEST | December | Attending site to check oxygen sensor (W11516071). Found O2 sensor has failed. Replaced sensor and calibrated. ROC was notified once sensor was replaced and they were able to clear the alarm. | Nobleton Water Resource Recovery Facility | 2025-12-17
WW-WEST | December | Placed mechanical bar screen in manual on due to high flow | Nobleton Water Resource Recovery Facility | 2025-12-28
WW-WEST | December | Completed labs. Enabled a 220 minute was timer. Set up auto wasting for 45 m4 between 13:00 and 15:00 in 8 cycles. Added 2 bags soda ash to each train. Completed station check. | Nobleton Water Resource Recovery Facility | 2025-12-23
WW-WEST | December | Returned the bar screen to automatic operation | Nobleton Water Resource Recovery Facility | 2025-12-28
WW-WEST | December | Harie Rajamithiran(OIT) working under the direction of Lance Johnson(OIC). -Supernated sludge thickening tank and transferred to sludge holding tank -Completed lab analysis, no abnormalities found -Started batch wasting process at 11:00 for 12:00 - 14:00 in 8 cycles for 27.5m^3 per train -Completed station check, no abnormalities found -Added 2 bags of soda ash into each aeration tank | Nobleton Water Resource Recovery Facility | 2025-12-19
WW-WEST | December | Supernated STT and released to SHT. Enabled 215 minute ras timer. Set auto wasting for 55 m3 in 8 cycles between 12:00 and 14:00. Added 2 bags soda ash to each train. | Nobleton Water Resource Recovery Facility | 2025-12-21
WW-WEST | December | Completed work orders with Harie. | Nobleton Water Resource Recovery Facility | 2025-12-19
WW-WEST | December | Harie Rajamithiran(OIT) working under the direction of Lance Johnson(OIC) -Supernated sludge thickening tank and transferred to sludge holding tank -Completed lab analysis ,no abnormalities found -Completed station check ,no abnormalities found -Started batch wasting process at 10:00 -Set auto wasting for 11:00 - 13:00 for 27.5m^3 per train in 8 cycles -Added 2 bags of soda ash into each aeration tank -Removed rags from aeration outlet weirs -Aeration channel cleaning complete -Aeration floating solids removal complete -Filter inlet channel cleaning complete -Air compressor cleaning completed -UV channel cleaning completed | Nobleton Water Resource Recovery Facility | 2025-12-18
WW-WEST | December | - Added two bags of soda ash into each aeration tank. - Performed in-house lab and recorded readings on Shares point. No issues - Checked station and recorded readings on SharePoint. No new issues - Prepared sample bottles for tomorrow - Did not waste due to sludge holding tank and sludge thickening tank being full | Nobleton Water Resource Recovery Facility | 2025-12-29
WW-WEST | December | Harie Rajamithiran(OIT) working under the direction of Daniel Hirstwood(OIC). -Supernated sludge thickening tank and transferred to sludge holding tank -Completed lab analysis, no abnormalities found -Completed station check, no abnormalities found -Started batch wasting process at 11:00, wasting from 12:00-14:00 for 25m^3 per train in 8 cycles -Added 3 bags of soda ash into each aeration tank -Completed aeration floating solids removal -Completed online DO probe maintenance -Completed aeration outlet weir cleaning -Completed H&S inspection for vehicle#2056-18 -Turned WAS pumps/valves in manuel off -Turned RAS pumps to auto | Nobleton Water Resource Recovery Facility | 2025-12-31
WW-WEST | December | Auto wasting 25m3 from each clarifier Added 2 bags of soda ash to each aeration tank | Nobleton Water Resource Recovery Facility | 2025-12-27
WW-WEST | December | Supernated STT and released to SHT. Started labs. Collected weekly compliance samples. Enabled ras timer at 9:10. . | Nobleton Water Resource Recovery Facility | 2025-12-30
WW-WEST | December | Reset the faulted bar screen Emptied the sludge thickening tank Set up auto wasting from 5-7pm to take 22.5m3 from each clarifier | Nobleton Water Resource Recovery Facility | 2025-12-29
WW-WEST | December | Completed work orders with Harie | Nobleton Water Resource Recovery Facility | 2025-12-18
WW-CEAST | December | P2 VFD PM completed by ABB Tech. | Markham Leslie Pumping Station | 2025-12-15
WW-CEAST | December | Weather today Clear and -4 Celsius -On site to complete work orders W11431335, W11437764, W11444677, W11465031. -Completed station check. -Entered station readings into SharePoint. -Investigated bar screen #2 fault alarm. -Comprehensive Housekeeping. -Pumps 2, 3, 5 and 6 available in timed-auto duty rotation every 4 hours. -Pump 1 out of service for repair and taken off site. -Pump 4 out of service for repair. -All standby power generators available in auto. -Switched sump pump duty. -Drained condensates from the surge tanks air compressors. -Checked dry well, ok. -Checked bar screens. Switched rag bin. Cleaned/hosed down bar screen room. -Bar Screen Bin Removal and Replacement - pushed rag bins back in the screen room after pick up by Miller Waste. | Markham Leslie Pumping Station | 2025-12-12
WW-CEAST | December | Weather today Snow and -7 Celsius -On site to complete work orders W11449182, W11448009. -Completed station check. -Entered station readings into SharePoint. -pump # 2 is currently being work on by centralized maintenance. -Pumps 3, 5 and 6 available in timed-auto duty rotation every 4 hours. -Pump 1 out of service for repair and taken out of site. -Pump 4 out of service for repair. -Tested standby power generator #1 Failed to start alarm from previous generator test run. -Tested standby power generator #1 at 10:20 am and also at 1:00 pm with centralized maintenance electrical. -All standby power generators available in auto. -Switched sump pump duty. -Drained condensates from the surge tanks air compressors. -Checked dry well, ok. -Checked bar screens. Switched rag bin. Cleaned/hosed down bar screen room. | Markham Leslie Pumping Station | 2025-12-15
WW-CEAST | December | Weather today Rain and snow mixed and 2 Celsius -On site to complete work orders W11431335, W11437556, W11437764, W11439401. -Completed station check. -Entered station readings into SharePoint. - Check valve inspection - Dry well flood alarm test - Sump pit inspection - RS pump & motor inspection? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? - BAS check - Seal Water Strainer - Air Compressor Inspection -RS Pumps and Motors Inspection. -Pumps 1 and 4 out of service for repair. -Pump 2 @ 0% speed: 1008 L/s, 470 kPa, 48 Hz, 125 A, 581 RPM, 435 Kw / @ 100% speed: 1824 L/s, 437 kPa, 60 Hz, 173 A, 716 RPM, 894 Kw. -Pump 3 Constant Speed: 1259 L/s. -Pump 5 @ 0% speed: 870.7 L/s, 415 kPa, 49Hz, 125 A, 581 RPM, 423 Kw / @ 100% speed: 1719 L/s, 441 kPa, 60 Hz, 176 A, 716 RPM, 909 Kw. -Pump 6 Constant Speed: 1152 L/s. -Pumps 2, 3, 5 and 6 available in timed-auto duty rotation every 4 hours. -Pump 1 and 4 out of service for repair. -All standby power generators available in auto. -Drained condensates from the surge tanks air compressors. -Checked dry well, ok. -Checked bar screens. Switched rag bin. Cleaned/hosed down bar screen room. -Bar Screen Bin Removal and Replacement - pushed rag bins outside the screen room for pick up by Miller Waste tomorrow. | Markham Leslie Pumping Station | 2025-12-10
WW-CEAST | December | Weather today Clear and -11 Celsius -On site to complete work orders W11409947, W11411376, W11411443. -Completed station check. -Entered station readings into SharePoint. -Two-Way Radio Functional test. -Pumps 2, 3, 5 and 6 available in timed-auto duty rotation every 4 hours. -Pump 1 out of service for repair and taken out of site. -Pump 4 out of service for repair. -All standby power generators available in auto. -Drained condensates from the surge tanks air compressors. -Checked dry well, ok. -Checked bar screens. Switched rag bin. Cleaned/hosed down bar screen room. | Markham Leslie Pumping Station | 2025-12-01
WW-CEAST | November | Brought back screens from Bayview mist elimators and washed them out after bringing bins back in and setting a new bin up for the weekend. After washing out screens I washed down the floor and the screen at the bottom of the auger. Took station readings and entered into SharePoint,, reviewed trends - all looks good. Checked pump floor - no issues,, station running under normal ops- pumps 1 & 4 are OOS. | Markham Leslie Pumping Station | 2025-11-28
WW-CEAST | December | Weather today Overcast and -7 Celsius -On site to complete work order W11426317. -Completed station check. -Entered station readings into SharePoint. -Pumps 2, 3, 5 and 6 available in timed-auto duty rotation every 4 hours. -Pump 1 out of service for repair and taken out of site. -Pump 4 out of service for repair. -All standby power generators available in auto. -Switched sump pump duty. -Drained condensates from the surge tanks air compressors. -Checked dry well, ok. -Checked bar screens. Switched rag bin. Cleaned/hosed down bar screen room. -Bar Screen Bin Removal and Replacement - pushed rag bins back in the screen room after pick up by Miller Waste. | Markham Leslie Pumping Station | 2025-12-05
WW-CEAST | December | On site to look at Generator 1. Tested generator 1 with the help of operations. Ran and transferred load with generator 1 twice. Both times there were no issues. Checked control wiring etc. unable to recreate any problems. Cause of failure to run unknown. | Markham Leslie Pumping Station | 2025-12-08
WW-CEAST | December | Attending site to check bar screen differential level transmitters (W11286763). Devices are not on SCADA yet and do not control other equipment. Adjusted empty distance on both transmitters so that the reading is zero while respective bar screens are running. | Markham Leslie Pumping Station | 2025-12-03
WW-CEAST | December | Weather today Clear and -6 Celsius -On site to complete work order W11431335, W11430091, W11428909, W11431682, W11428992, W11497362. -Completed station check. -Entered station readings into SharePoint. -Hoist Inspection. -Surge tank inspection. -Odour control scrubber system inspection. -Pumps 2, 3, 5 and 6 available in timed-auto duty rotation every 4 hours. -Pump 1 out of service for repair and taken out of site. -Pump 4 out of service for repair. -Tested standby power generator #1 Failed to start alarm from previous generator test run. -Tested standby power generator #1 at 10:20 am and also at 1:00 pm with centralized maintenance electrical. -All standby power generators available in auto. -Switched sump pump duty. -Drained condensates from the surge tanks air compressors. -Checked dry well, ok. -Checked bar screens. Switched rag bin. Cleaned/hosed down bar screen room. | Markham Leslie Pumping Station | 2025-12-08
WW-CEAST | December | Weather today Rain and Snow mixed and 2 Celsius -On site to complete work order W11460249. -Completed station check. -Entered station readings into SharePoint. -Pumps 3, 2, 5, and 6 available in timed-auto duty rotation every 4 hours. -Pumps 1 and 4 out of service. -All standby power generators available in auto. -Drained condensates from the surge tanks air compressors. -Checked dry well, ok. -Checked bar screens. Switched rag bin. Cleaned/hosed down bar screen room. -Bar Screen Bin Removal and Replacement - pushed rag bins back in the screen room after pick up by Miller Waste. | Markham Leslie Pumping Station | 2025-12-19
WW-CEAST | December | -On site to clean Bayview Steeles mist eliminator filters. -Hosed down filters in screen room and left sitting out to dry. -Fixed leak on upper screw press drain line. -Hosed down floors in screen room. -Pumps 1 and 4 OOS. -Crane Tech is on site continuing repairs to lower level hoist. | Markham Leslie Pumping Station | 2025-12-17
WW-CEAST | December | Weather today Partly Cloudy and -5 Celsius -On site to complete work orders W11479427, W11482733, W11482920. -Completed station check. -Entered station readings into SharePoint. -Pumps 3, 2, 5, and 6 available in timed-auto duty rotation every 4 hours. -Pumps 1 and 4 out of service. -All standby power generators available in auto. -Switched sump pump duty. -Drained condensates from the surge tanks air compressors. -Checked dry well, ok. -Checked bar screens. Switched rag bin. Cleaned/hosed down bar screen room. -Bar Screen Bin Removal and Replacement - pushed rag bins out for pick up by Miller Waste. | Markham Leslie Pumping Station | 2025-12-31
WW-CEAST | December | Weather today Clear and -2 Celsius -On site to complete work orders W11469148, W11469335. -Completed station check. -Entered station readings into SharePoint. -Pumps 3, 2, 5, and 6 available in timed-auto duty rotation every 4 hours. -Pumps 1 and 4 out of service. -All standby power generators available in auto. -Switched sump pump duty. -Drained condensates from the surge tanks air compressors. -Checked dry well, ok. -Checked bar screens. Switched rag bin. Cleaned/hosed down bar screen room. -Bar Screen Bin Removal and Replacement - pushed rag bins out for pick up by Miller Waste. | Markham Leslie Pumping Station | 2025-12-24
WW-CEAST | December | On site to complete P5 VFD PM with ABB. Pump back in service running in auto duty 1 Assisted crane tech with site access and trouble shooting bussbar issue they will return at a later date with materials to make repair. | Markham Leslie Pumping Station | 2025-12-16
WW-CEAST | December | On site for Station Check. Pumps 2, 3, 5 and 6 available in timed auto duty rotation every 4 hours. Tung 1 and 4 out of service. All standby power generators available in auto. Switched pump duty of sump pump and ran one sump pump to dewater sump pit or remove old/stagnant water/sewage. Drained surge tanks air compressors. Blew down bubblers. Cleared/reset alarms. Checked bar screens. Switched rag bin. Pushed rag bin back inside the screen room. Flushed screw press drain due to clogging. Checked bar screens 1 for fault as reported by ROC. Cleared/reset alarms. Ran for several cycles, ok. Was able to put it back in service. Too much dirt, rags and big chunks of grease. Cleaned/hosed down bar screens room. Will up door switch broken. It was hit by the rag bin while I?m putting back the bins back inside the screen room. Main gate stuck open, it won?t close. Tried to reset but it won?t. | Markham Leslie Pumping Station | 2025-12-29
WW-CEAST | December | On site to install saddle and live tap discharge pipe in preparation of discharge valve #4 bonnet removal. | Markham Leslie Pumping Station | 2025-12-22
WW-CEAST | December | Rotated bins in screen room Cleaned screen room Inspected site | Markham Leslie Pumping Station | 2025-12-27
WW-CEAST | December | Onsite to configure bar screen LDITs Informed ROC Configured and verified as much as possible PCS to complete scada work Informed ROC, armed building and left site | Markham Leslie Pumping Station | 2025-12-16
WW-CEAST | December | Weather today A few clouds and -4 Celsius -On site to complete work order W11463780. -Completed station check. -Entered station readings into SharePoint. -Pumps 3, 2, 5, and 6 available in timed-auto duty rotation every 4 hours. -Pumps 1 and 4 out of service. -All standby power generators available in auto. -Switched sump pump duty. -Drained condensates from the surge tanks air compressors. -Checked dry well, ok. -Checked bar screens. Switched rag bin. Cleaned/hosed down bar screen room. | Markham Leslie Pumping Station | 2025-12-22
WW-CEAST | December | Bar screen 1 and 2 - Configured both bar screen differential level LIT. Tested with PCS Yash. Everything worked good ( differential level signal and loss of echo ). Put in service. No further issues encountered. | Markham Leslie Pumping Station | 2025-12-23
WW-CEAST | December | Weather today Partly Cloudy and -5 Celsius -On site to complete work orders W11479427, W11482733, W11482920. -Completed station check. -Entered station readings into SharePoint. -Pumps 3, 2, 5, and 6 available in timed-auto duty rotation every 4 hours. -Pumps 1 and 4 out of service. -All standby power generators available in auto. -Switched sump pump duty. -Drained condensates from the surge tanks air compressors. -Checked dry well, ok. -Checked bar screens. Switched rag bin. Cleaned/hosed down bar screen room. -Bar Screen Bin Removal and Replacement - pushed rag bins out for pick up by Miller Waste. | Markham Leslie Pumping Station | 2025-12-31
EAST | December | On site for station check. Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 1.90mg/l FCL Analyzer: 1.96mg/l Effluent Free Cl2 grab residual: 1.68mg/l FCL Analyzer: 1.72mg/l Effluent Total Cl2 grab residual: 1.81mg/l Isolated Hypo Tank 1 for the weekend, it?s almost low enough to drain and repair leaking fitting. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Mount Albert Wells 1 & 2 | 2025-12-12
EAST | December | On site for annual generator PM. Oil changed but unable to do a load test due to the weather. Called the ROC to turn off well. Did a station transfer test. Returned station back to auto. | Mount Albert Wells 1 & 2 | 2025-12-10
EAST | December | On site for station check. Collected weekly micro samples (W11438459). Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 1.88mg/l FCL Analyzer: 1.91mg/l 12:42hrs: Effluent Free Cl2 grab residual: 1.45mg/l FCL Analyzer: 1.49mg/l Effluent Total Cl2 grab residual: 1.74mg/l Ran Well #1 in local to waste (not into distribution) to collect raw samples. Ensured chemical pumps were off and isolated from distribution system while running well. Back to local off when complete. Well used for emergency purposes only. Well #1 raw sample collected @ 13:10hrs. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. Hypo Tank 1 currently feeding to draw down for tank repair. Hypo Tank 2 | Mount Albert Wells 1 & 2 | 2025-12-10
EAST | December | On site for station check. Duty not active, tower level 60% Completed turbidimeter calibration and vial cleaning with well manual off. Placed well back in auto after completed. Verified analyzer readings with grab residuals. Influent taken 9:06 Free Grab: 1.42 mg/L Analyzer: 1.41 mg/L Effluent taken at 9:09 Free Grab: 1.54 mg/L Analyzer: 1.52 mg/L Total Grab: 1.74 mg/L Visual inspection of chemical systems - all ok. Entered station readings in PWQ sheet. Reviewed trends, equipment ok. Station ok | Mount Albert Wells 1 & 2 | 2025-12-05
EAST | December | Onsite to deliver silicate Track level 85 L to 500 L | Mount Albert Wells 1 & 2 | 2025-12-09
EAST | December | On site to provide access to generator for contractor maintenance (John from Total Power). | Mount Albert Wells 1 & 2 | 2025-12-09
EAST | December | On site for station check. Duty active, tower level 78% Verified analyzer readings with grab residuals. Influent taken 12:10 Free Grab: 1.81 mg/L Analyzer: 1.95 mg/L Adjusted influent free analyzer after three grab samples. Effluent taken at 12:13 Free Grab: 1.57 mg/L Analyzer: 1.56 mg/L Total Grab: 1.85 mg/L Took operational sample at 12:18 (W11410888) Chemical systems: Chlorinator open 33%, DF= 50%. Booster P1 DP= 1020 kpa. Hypo p1 speed 24%, DF=88%, DP= 460 kpa. Silicate P2 speed 38%, DP= 510 kpa. Visual inspection of chemical systems - all OK. Entered station readings in PWQ sheet. Reviewed trends, equipment ok. Station ok Completed assigned work orders: MT South Tower station check, JHSC inspections. | Mount Albert Wells 1 & 2 | 2025-12-01
EAST | December | On site for station check, and weekly micro sampling (W11419099), and Manganese sampling (W11420244). Placed all chemical pumps manual off for sampling well 1 raw water. Local started well #1 @ 9:09 for sampling. Flow avg 29 L/s Collected W1 raw micro and manganese samples @ 9:25 Stopped W1 @ 9:28 Put all chemical pumps and well 2 back in auto (re-examined hypo p2, concluded not actively leaking. No issue with running, returned p2 to service). Placed well 2 back in auto. Activated MT system duty - tower level 61% Well 2 running - 22 L/s, discharge pressure 315 kpa Verified analyzer readings with grab residuals: Influent @ 10:16 Grab Free: 1.98 mg/L / Analyzer: 2.00 mg/L Effluent: @ 10:18 Grab free: 1.48 mg/L / Analyzer: 1.48 mg/L Grab total: 1.75 mg/L NTU: 0.059 Collected treated micro and manganese samples @ 10:23 Collected well 2 raw micro and manganese samples @ 10:29 Chemical systems: Hypo pump 1 speed 24%, DF=90%, DP=460 kpa Silicate P1 speed 37%, 70.2 ml/min, DP=510 kpa Recorded station readings in PWQ sheets. Reviewed trends, station OK. | Mount Albert Wells 1 & 2 | 2025-12-03
EAST | December | On site for station check. Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 1.45mg/l FCL Analyzer: 1.36mg/l Effluent Free Cl2 grab residual: 1.50mg/l FCL Analyzer: 1.50mg/l Effluent Total Cl2 grab residual: 1.72mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Mount Albert Wells 1 & 2 | 2025-12-08
EAST | December | On site for monthly work orders, notified ROC of work being done and will be on site all day. Building high/low temperature alarm test - alarm triggered at 9:38, and was cleared. Manual stop well pump 2 at 9:43 Generator test run: Start hours: 201.1 hrs Stop hours:202.55 hrs Start fuel: 12.0 cm Stop fuel: 11.5 cm Start test at 9:48 Manual start well 2 for load test at 9:54 and monitor start up. Running checks: Volts 600 Amp 42 Hertz 60 RPM 1800 Oil pressure 412 kpa Coolant temp 78 C Manual stop well pump 2 at 10:51 Switch ATS back to auto at 10:53 Chlorine analyzer maintenance: Completed cleaning and verified with grab sample. Influent analyzer @ 13:21 Grab: 1.50 mg/L. Analyzer: 1.50 mg/L Effluent analyzer @ 13:24 Grab: 1.67 mg/L. Analyzer: 1.69 mg/L Silicate pumps maintenance. Hypo panel boards inspection. Hypo diaphragm pumps inspection and maintenance. Found a leak on the outlet of hypo pump 2 - placed manual off and disabled duty rotation. Will follow up and repair later this week. Hypo system inspection. General housekeeping. Placed well 2 back in auto. | Mount Albert Wells 1 & 2 | 2025-12-02
EAST | December | On site for station check, and weekly micro sampling (W11483416). Duty active - tower level 69% Well 2 Manual off to sample well 1 first. All chemical pumps in manual off. Local started well #1 @ 13:06 for sampling. Flow 28.8 L/s Collected W1 raw micro sample @ 13:20 Stopped W1 @ 13:21 Placed all chemical pumps and well 2 back in auto. Well 2 back to auto start up at 13:30 Well 2 running - 22.2 L/s, discharge pressure 323 kpa Verified analyzer readings with grab residuals: Influent @ 13:57 Grab Free: 1.93 mg/L / Analyzer: 1.93 mg/L Effluent: @ 14:00 Grab free: 1.43 mg/L / Analyzer: 1.47 mg/L Grab total: 1.67 mg/L NTU: 0.045 Collected treated micro sample and well 2 raw sample @ 14:07 Reviewed trends, station ok. | Mount Albert Wells 1 & 2 | 2025-12-29
EAST | December | On site for station check. Duty not active, tower level 78% Verified analyzer readings with grab residuals. Influent taken 9:07 Free Grab: 1.48 mg/L Analyzer: 1.44 mg/L Effluent taken at 9:10 Free Grab: 1.51 mg/L Analyzer: 1.50 mg/L Total Grab: 1.72 mg/L Visual inspection of chemical systems - all ok. Entered station readings in PWQ sheet. Reviewed trends, equipment ok. Outstanding alarm: Hypo tank 1 level LOLO alarm - tank isolated for drain port replacement. Station ok | Mount Albert Wells 1 & 2 | 2025-12-18
EAST | December | On site with Jackie S to transfer silicate. ? Start level: 68.9 cm Stop level: 110.7 cm.? Performanced station checks and cleaned turbidity meter while on site. Well duty is not active. 10:30 verified chlorine readings with grabs. Influent grab free = 1.50 mg/l, analyzer = 1.44 mg/l. Effluent grab free = 1.50 mg/l, analyzer = 1.49 mg/l. Station readings are in PWQ sheet.? Reviewed trends.? Equipment OOS: Hypo day tank 1. Well 1 local off as normal operations. | Mount Albert Wells 1 & 2 | 2025-12-24
EAST | December | Silicate top up from 61 to 108.3cm | Mount Albert Wells 1 & 2 | 2025-12-17
EAST | December | On site for station check. Collected weekly micro samples (W11469858). Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 1.87mg/l FCL Analyzer: 1.86mg/l 09:20hrs: Effluent Free Cl2 grab residual: 1.45mg/l FCL Analyzer: 1.51mg/l Effluent Total Cl2 grab residual: 1.73mg/l Ran Well #1 in local to waste (not into distribution) to collect raw samples. Ensured chemical pumps were off and isolated from distribution system while running well. Back to local off when complete. Well used for emergency purposes only. Well #1 raw sample collected @ 09:45hrs. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: Hypo Tank #1 offline and emptied for maintenance to repair leaking fitting. | Mount Albert Wells 1 & 2 | 2025-12-22
EAST | December | Check eyewash chlorine room Broken prong on inside of eyewash diffuser, cleaned flushed working properly | Mount Albert Wells 1 & 2 | 2025-12-22
EAST | December | Chris Iliohan Tyler Smith in to replace leaking fitting in hypo tank new fittings installed unable to check for leaks due to tank levels operations to Add hypo and monitor. | Mount Albert Wells 1 & 2 | 2025-12-22
EAST | December | I?m site to transfer the remaining hypo from tank 1 to tank 2. Responding to call from ROC (Ethan) that well 2 and well 3 were faulted. Brief power loss in the system caused alarms, reset well 2 VFD on site. After transfer of hypo tank 1 level change from 13.19 cm to 2.28 cm. Tank 2 change from 78.3 cm to 89.32 cm. Tank 1 isolated for drain port replacement. | Mount Albert Wells 1 & 2 | 2025-12-17
EAST | December | On site for station check, and weekly micro sampling (W1145493). Duty active - tower level 76% Well 2 running - 2 L/s, discharge pressure 324 kpa Verified analyzer readings with grab residuals: Influent @ 13:12 Grab Free: 1.87 mg/L / Analyzer: 1.93 mg/L Effluent: @ 13:16 Grab free: 1.68 mg/L / Analyzer: 1.63 mg/L Grab total: 1.82 mg/L NTU: 0.042 Collected treated micro sample @ 11:02 Collected well 3 raw micro sample @ 11:03 Chemical systems: Hypo pump 1 speed 25%, DF=95%, DP=460 kpa Chlorinator 1 open 33%, DF=51%, Rotameter: 16 ppd, BP1 DP=1020 kpa Silicate P1 speed 37%, 69.81 ml/min, DP=500 kpa Recorded station readings in PWQ sheets. Reviewed trends, station OK. Manual stop well 2 @ 13:46 Placed all chemical pumps manual off for sampling well 1 raw water. Local started well #1 @ 13:48 for sampling. Flow 28.4 L/s Collected W1 raw micro sample @ 14:01 Stopped W1 @ 14:03 Transfer Hypo from tank 1 to tank 2, tank 1 from 20 cm to 13.2 cm, tank 2 from 74.42 cm to 81.08 cm. Tank 1 isolated, tank 2 feeding. Deactivate system duty Tower at 80%. Put all chemical pumps and well 2 back in auto. Placed well 2 back in auto. | Mount Albert Wells 1 & 2 | 2025-12-16
EAST | December | On site for station check. Outstanding VFD bypass alarm when well started up. Was able to clear on SCADA. Collected weekly micro samples (W11438459). Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 1.85mg/l FCL Analyzer: 1.81mg/l 11:50hrs: Effluent Free Cl2 grab residual: 1.73mg/l FCL Analyzer: 170mg/l Effluent Total Cl2 grab residual: 1.91mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Mount Albert Well 3 | 2025-12-10
EAST | December | On site for station check. Collected in house iron samples. Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 1.82mg/l FCL Analyzer: 1.87mg/l Effluent Free Cl2 grab residual: 175mg/l FCL Analyzer: 1.77mg/l Effluent Total Cl2 grab residual: 1.97mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Mount Albert Well 3 | 2025-12-12
EAST | December | On site with Sean Peoples to replace damaged conduit in generator rm. BAS control wiring disconnected, then reconnected as part of repair. ROC notified. | Mount Albert Well 3 | 2025-12-15
EAST | December | On site for monthly work orders, notified ROC of work being done. Generator test run: Completed pre-run checks, Start hours: 375:54 hrs Stop hours: 377:06 hrs Start fuel: tk 1 - 90.7 cm/904.2 L, tk 2 - 90.1 cm/879.6 L Stop fuel: tk 1 - 90.1cm/ 898 L, tk 2 - 89.3 cm/ 889 L Running checks: Amp 43 Hertz 60.1 RPM 1803 Oil pressure 56 psi Coolant temp 181 F Manual start well 3 @ 9:25 Manual stop well 3 @ 10:27 Switch ATS back to auto at 10:27 Exhaust fans check, Supply fans check, Dechlorination puck dispenser inspection and cleaning, Deep well exhaust valve check, Chlorine analyzer maintenance: Completed cleaning and verified with grab sample. Influent analyzer @ 12:01 Grab: 1.72 mg/L. Analyzer: 1.72 mg/L Effluent analyzer @ 12:02 Grab: 1.68 mg/L. Analyzer: 1.70 mg/L Chlorine leak test, Scrubber check, JHSC Inspections, Chlorine system inspection - placed well local off, ran chlorine booster pumps in manual. And put all back to auto after completed. General Housekeeping. Donald M. Delivered sodium silicate: added 6.38 cm to silicate tank. | Mount Albert Well 3 | 2025-12-09
EAST | December | On site for station check, and weekly micro sampling (W11419099), and Manganese sampling (W11420244). Duty active - tower level 68% Well 3 running - 30 L/s, discharge pressure 394 kpa Verified analyzer readings with grab residuals: Influent @ 11:32 Grab Free: 1.79 mg/L / Analyzer: 1.80 mg/L Effluent: @ 11:36 Grab free: 1.72 mg/L / Analyzer: 1.70 mg/L Grab total: 1.95 mg/L NTU: 0.046 Collected treated micro and manganese samples @ 11:41 Collected well 3 raw micro and manganese samples @ 11:42 Chemical systems: Chlorinator 1 open 34%, DF=52%, Rotameter: 16.5 ppd, BP1 DP=1020 kpa Silicate P1 speed 41%, 62.88 ml/min, DP=520 kpa Recorded station readings in PWQ sheets. Reviewed trends, station OK. | Mount Albert Well 3 | 2025-12-03
EAST | December | On site for station check. Collected in house iron samples. Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 1.66mg/l FCL Analyzer: 1.62mg/l Effluent Free Cl2 grab residual: 1.53mg/l FCL Analyzer: 1.59mg/l Effluent Total Cl2 grab residual: 1.80mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Mount Albert Well 3 | 2025-12-08
EAST | December | On site for station check. Duty active, tower level 61% Completed turbidimeter calibration and vial cleaning with well manual off, placed well back to auto after completed. 10:30 Historian Heartbeat alarm interlocked and shut down well, notified ROC to request PCS assistance. Placed well manual off. 10:42 Placed well back in auto after historian heartbeat alarm was cleared. Verified analyzer readings with grab residuals. Influent taken 10:57 Free Grab: 1.83 mg/L Analyzer: 1.83 mg/L Effluent taken at 11:00 Free Grab: 1.82 mg/L Analyzer: 1.85 mg/L Total Grab: 2.04 mg/L Chemical systems: Chlorinator open 34%, DF= 53%. Booster P1 DP= 1040 kpa. Hypo p1 speed 24%, DF=88%, DP= 460 kpa. Silicate P2 speed 41%, DP= 490 kpa. Visual inspection of chemical systems - all ok. Entered station readings in PWQ sheet. Reviewed trends, equipment ok. Station ok Placed well manual off for Chris S. To reboot OIT. 11:53 - placed well back in auto. | Mount Albert Well 3 | 2025-12-05
EAST | December | Outstanding Turbidity fault alarm upon arrival, well interlocked and placed manual off by the ROC. Cleaned vial and adjusted flow through turbidimeter, analyzer returned to service. On site for station check. Activated system duty, tower level 65% Verified analyzer readings with grab residuals - no adjustments needed. Influent taken 10:13 Free Grab: 1.93 mg/L Analyzer: 1.94 mg/L Effluent taken at 10:15 Free Grab: 1.73 mg/L Analyzer: 1.69 mg/L Total Grab: 1.93 mg/L Took operational sample at 10:20 (W11410888) Chemical systems: Chlorinator 1 open 33%, DF= 50%. Booster P1 DP= 1020 kpa. Silicate P1 speed 40%, D P= 510 kpa. Visual inspection of chemical systems - all OK. Entered station readings in PWQ sheet. Reviewed trends, equipment ok. Station ok | Mount Albert Well 3 | 2025-12-01
EAST | December | Effluent CL17 analyzer had a sensor warning alarm active, could not be cleared. 12:07 Manual stop well in order to perform analyzer maintenance. Cleaned analyzer and verified reading with a grab sample. @ 13:11 grab: 1.62 mg/L, analyzer: 1.65 mg/L. Placed well back in auto. | Mount Albert Well 3 | 2025-12-03
EAST | December | Noticed turbidity higher than normal, rotated silicate pump duty to see if that helps. Sodium silicate was delivered right after duty activated - most likely sediment was disturbed in silicate tank. Turbidity trending downward. | Mount Albert Well 3 | 2025-12-09
EAST | December | On site for station check, and weekly micro sampling (W1145493). Duty active - tower level 66% Well 3 running - 30 L/s, discharge pressure 393 kpa Verified analyzer readings with grab residuals: Influent @ 10:54 Grab Free: 1.76 mg/L / Analyzer: 1.74 mg/L Effluent: @ 10:57 Grab free: 1.62 mg/L / Analyzer: 1.65 mg/L Grab total: 1.86 mg/L NTU: 0.123 Collected treated micro sample @ 11:02 Collected well 3 raw micro sample @ 11:03 Chemical systems: Chlorinator 1 open 33%, DF=51%, Rotameter: 16 ppd, BP1 DP=1020 kpa Silicate P2 speed 41%, 62.24 ml/min, DP=500 kpa Recorded station readings in PWQ sheets. Reviewed trends, station OK. Noticed only chlorinator 1 has been running for the past 3 weeks - duty rotate was disabled when a fitting on the injection line broke. Changed chlorine duty rotate back to All Stop. Completed turbidity analyzer maintenance. NTU after cleaning = 0.07 | Mount Albert Well 3 | 2025-12-16
EAST | December | Grease motor bottom bearing | Mount Albert Well 3 | 2025-12-18
EAST | December | On site for station check. Collected weekly micro samples (W11469858). Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 1.68mg/l FCL Analyzer: 1.68mg/l 08:37hrs: Effluent Free Cl2 grab residual: 1.78mg/l FCL Analyzer: 1.79mg/l Effluent Total Cl2 grab residual: 1.98mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Mount Albert Well 3 | 2025-12-22
EAST | December | On site with Jackie S. Performanced station checks. Well duty is not active. 10:50 verified chlorine readings with grabs. Influent grab free = 1.60 mg/l, analyzer = 1.57 mg/l. Effluent grab free = 1.57 mg/l, analyzer = 1.56 mg/l. Station readings are in PWQ sheet.? Reviewed trends.? | Mount Albert Well 3 | 2025-12-24
EAST | December | On site for work orders, notified ROC of work being done. Silicate system inspection, injection point cleaning, Placed well local off for work. Isolate and depressurize water pipe, pull and clean both injection points. Re-pressurized pipe and checked for leaks. Inspected silicate pumps 1 & 2, inspected and cleaned foot valves, performed pump flow test using graduated columns. Returned silicate system to operating conditions. Placed well in remote manual mode and started well pump to test silicate system, 12:35 - Stopped well and placed back in auto after running for 35 mins. Turbidity value remained consistent during run. | Mount Albert Well 3 | 2025-12-23
EAST | December | On site for silicate top up. | Mount Albert Well 3 | 2025-12-17
EAST | December | Got to site motor hatch was open I closed it and put a bolt on the handle to keep it secure. Under direction of oic | Mount Albert Well 3 | 2025-12-30
EAST | December | ROC informed of generator running alarm. Reviewed SCADA, ATS is on utility power. And+reset alarm, alarm cleared and generator stopped. | Mount Albert Well 3 | 2025-12-27
EAST | December | On site for station check. Duty not active, tower level 76% Verified analyzer readings with grab residuals. Influent taken 9:56 Free Grab: 1.68 mg/L Analyzer: 1.68 mg/L Effluent taken at 10:01 Free Grab: 1.66 mg/L Analyzer: 1.68 mg/L Total Grab: 1.91 mg/L Visual inspection of chemical systems - all ok. Entered station readings in PWQ sheet. Reviewed trends, equipment ok. Station ok | Mount Albert Well 3 | 2025-12-18
EAST | December | On site for station check, and weekly micro sampling (W11483416). Duty active - tower level 74% Well running - 30 L/s, discharge pressure 395 kpa Verified analyzer readings with grab residuals: Influent @ 14:42 Grab Free: 1.84 mg/L / Analyzer: 1.84 mg/L Effluent: @ 14:44 Grab free: 1.77 mg/L / Analyzer: 1.73 mg/L Grab total: 1.97 mg/L NTU: 0.051 Collected treated micro sample and well 3 raw sample @ 14:48 Cleaned turbidimeter vial. Turbidity was still high, Flushed sample line and changed turbidimeter vial. Reviewed trends, station ok. | Mount Albert Well 3 | 2025-12-29
EAST | December | On site to check station and equipment. Tower is on a filling cycle. 11:56 grab chlorine residual from outlet, FCL = 1.52 mg/l, TCL = 1.72 mg/l. Analyzer free = 1.52 mg/l. 11:56 collected bac-T sample, YD W11438459. Station readings and chlorine grabs are entered in PWQ sheet.? Reviewed trends, station is under normal operation. | Mount Albert North Elevated Tank | 2025-12-10
EAST | December | On site for monthly work orders, notified ROC of work being done. Building low temperature alarm test - alarm triggered at 9:58, and was cleared. Sump pit system inspection, Heat trace inlet/outlet inspection, Chlorine analyzer maintenance: Completed cleaning and verified with grab sample. Outlet @ 10:51 Grab: 1.33 mg/L. Analyzer: 1.37 mg/L Manual valve exercise Portable generator test run. JHSC inspections, General housekeeping. | Mount Albert North Elevated Tank | 2025-12-04
EAST | December | On site for station check, and weekly micro sampling (W11419099), and Manganese sampling (W11420244). Tower level - 63% and draining at 12.5 L/s Recorded station readings in PWQ sheets Verified analyzer reading: Outlet @ 8:36 Free Grab: 1.34 mg/L Analyzer: 1.38 mg/L Total Grab: 1.52 mg/L Collected micro and manganese sample @ 8:40 from outlet. Reviewed trends, equipment ok Station ok | Mount Albert North Elevated Tank | 2025-12-03
EAST | December | On site for station check. Collected weekly micro samples (W11469858). Verification of HACH CL17 Chlorine Analyzers: 10:10hrs: Free CL2 grab residual: 1.34mg/l FCL Analyzer: 1.36mg/l Total Cl2 grab residual: 1.58mg/l Changed HACH Cl17 Analyzer reagents Checked station readings and verified Cl2 analyzer. All information in PWQ sheet. Checked site and equipment. Equipment out of service: None. | Mount Albert North Elevated Tank | 2025-12-22
EAST | December | On site for station check, and weekly micro sampling (W11454693), and operational sampling (W11419562) Tower level - 63% and draining at 11.5 L/s Recorded station readings in PWQ sheets Verified analyzer reading: Outlet @ 9:39 Free Grab: 1.346 mg/L Analyzer: 1.44 mg/L Total Grab: 1.57 mg/L Adjusted analyzer after three grab residuals. Collected micro and manganese sample @ 9:45 from outlet. Reviewed trends, equipment ok Station ok Activated system duty at 9:57 | Mount Albert North Elevated Tank | 2025-12-16
EAST | December | Under direction of OIC, Danielle Zhou. Notified ROC. Worked with contractors to calibrate new diesel tank LIT. | Stouffville Zone 1 Booster Pumping Station | 2025-12-11
EAST | December | Placed P1 and P2 to auto | Stouffville Zone 1 Booster Pumping Station | 2025-12-15
EAST | December | Activate duty. Zone 1 ET = 61%. | Stouffville Zone 1 Booster Pumping Station | 2025-12-10
EAST | December | ROC called for STETTL draining while duty is active. STETBR duty is also active. Deactivated STETBR duty @10:45 - tower level is 67%. Placed P1/P2 in man/off. Will drain STETBR to approx 50% to allow STETTL to recover the tower level. ROC will continue to monitor system | Stouffville Zone 1 Booster Pumping Station | 2025-12-14
EAST | December | Placed STPSTL pumps back to auto - STETBR level is 57%. Pump 1 started, duty is active | Stouffville Zone 1 Booster Pumping Station | 2025-12-14
EAST | December | On Site for; - Comprehensive Housekeeping - Manual Valve Exercise (BFV 1,2,3,4 - FCV) @ 13:24 set FCV to 50 L/s to exercise open (18.6 %) @ 13:33 set FCV to 0 L/s to close | Stouffville Zone 1 Booster Pumping Station | 2025-12-15
EAST | December | Under Direction of OIC (Dan Zhou) On Site for; - Station Checks Data in PWQ Excel Workbook Grabs @ 09:49 hrs. FCl: 1.73 mg/L TCL: 1.99 mg/L Equipment OOS: station generator for TSSA upgrades, mobile generator hooked up. Facility OK | Stouffville Zone 1 Booster Pumping Station | 2025-12-12
EAST | December | Placed pumps man/off and changed Zone 1 ET tower low alarm from 60% to 40%. Informed ROC. | Stouffville Zone 1 Booster Pumping Station | 2025-12-15
EAST | December | On site to complete station check. Time: 10:30 Grab (mg/l) Free: 1.76 Total: 1.96 Checked site. Duty is currently active. | Stouffville Zone 1 Booster Pumping Station | 2025-12-01
EAST | December | Closed FCV and placed pumps back to auto. | Stouffville Zone 1 Booster Pumping Station | 2025-12-03
EAST | December | Under Direction of OIC (Dan Zhou) @ 09:41 Deactivated duty to maintain flow to zone 2 tower, while doing PM?s at STW12. | Stouffville Zone 1 Booster Pumping Station | 2025-12-04
EAST | December | On site to complete station check. Time: 13:13 Grab (mg/l) Free: 1.59 Total: 1.77 Checked site. Duty is not active. | Stouffville Zone 1 Booster Pumping Station | 2025-12-08
EAST | December | Manual stopped pumps. Opened FCV to deep cycle Zone 1 ET. | Stouffville Zone 1 Booster Pumping Station | 2025-12-03
EAST | December | Onsite to respond to pumps fault alarm. Asked ROC to place both pumps in manual off while I drive to site. Upon arrival, found both pumps VFDs in power overload alarm. Cleared and reset. Requested ROC to run pump1 in manual, pump1 ok, discharge flow was 57 L/s. Asked ROC to stop pump1 and start pump2 in manual, discharge flow for pimp2 was 56 L/s. Both pumps ran ok no issue. Directed ROC to return pumps to auto, duty was active. Places pump2 in lead duty. Notified ROC before leaving site. | Stouffville Zone 1 Booster Pumping Station | 2025-12-09
EAST | December | Under direction of OIC, Danielle Zhou. Notified ROC of the TSSA work and temp generator disconnection. Worked with operator Travis Wyatt, Electrician Sean Peoples and contractors from Ferguson electric. Disconnected temp IO from PAC panel. Updated SCADA displays and OIT screens. Tested all new device alarms. Tested station on station generator via ATS transfer. No outstanding issues. | Stouffville Zone 1 Booster Pumping Station | 2025-12-16
EAST | December | Under Direction for OIC (Dan Zhou) On Site for; - Operational assistance for Ferguson post TSSA upgrade and generator load test - Station Checks FCL: 1.68 mg/L TCL: 1.91 mg/L @ 11:06 placed STW3 well pump in manual off @ 11:09 placed STPSTL pumps 1 and 2 in manual off Generator Test Run; Start Time: 11:22 hrs. Stop Time: 12:27 hrs. Start Hours: 512.1 Stop Hours: 513.3 Pre run checks; Battery Cell Levels: Ok Battery Terminals and Cables: Ok Oil Level: Ok Coolant Level: Ok Fluid Leaks: Ok Coolant Recirculating pump: Ok Faulty Gauges: Ok @ 11:34 hrs. Put BP1 in manual on, activated zone 1 tower duty @ 11:37 put STW3 well pump in Manual ON *under station load, well pump 3 and BP1 at STPSTL Operating Current: 116 Amps Operating Frequency: 60.1 Hz Operating Voltage: 600 Volts, Engine speed: 1802 RPM Water/coolant Temp: 590 C Oil Pressure: 56 psi Engine temp 100 f Oil temp: 225 f @ 12:10 - switched from station generator to main power supply (station generator tested and hooked back up to station back up power supply) - Deactivated zone 1 tower duty - Manually turned off STPSTL BP2 - Manually turned off STW3 well pump 3 @ 12:27 - main power supplying facility - Placed STW3 well pump 3 in auto zone 2 duty active (pump activated) - Placed STPSTL BP1/2 in auto Equipment out of Service: None Facility OK | Stouffville Zone 1 Booster Pumping Station | 2025-12-16
EAST | December | Under Direction of OIC (Dan Zhou) On Site for; - Station Checks Data in PWQ Excel Workbook Grabs @ 12:33 hrs. FCl: 1.69 mg/L TCL: 1.86 mg/L @ 11:36 hrs. Glusen from ROC called about diesel tank vacuum alarm, called Tyler from maintenance and is aware of the minor leak. Ferguson in charge of TSSA upgrades is also aware of the issue and is going to be fixing it. Gauge on tank reads -30 Kpa, no fluctuations while idle @ 12:50 hrs. Drew from Ferguson came and made a temporary fix to vacuum switch until later date, alarm cleared Equipment OOS: none Facility OK | Stouffville Zone 1 Booster Pumping Station | 2025-12-18
EAST | December | On-site for station check Visual inspection of equipment and instrumentation Verified analyzer reading Grab residual at 1133 hrs: FCL = 1.53 mg/l TCL = 1.75 mg/l Recorded station reading into pwq data sheet No issues | Stouffville Zone 1 Booster Pumping Station | 2025-12-29
EAST | December | Closed FCV. Placed pumps back to auto. P1 started in duty 1. STETBR level = 41%. | Stouffville Zone 1 Booster Pumping Station | 2025-12-30
EAST | December | On?site to check station and equipment. Pump duty is not active upon arrival. Opened FCV while on site.? Station readings are in PWQ sheet.? Reviewed trends, station is under normal operation. No outstanding alarms. | Stouffville Zone 1 Booster Pumping Station | 2025-12-22
EAST | December | Grease motors and pumps All pumps are off | Stouffville Zone 1 Booster Pumping Station | 2025-12-18
EAST | December | On site with Jack Palmer to replace Cl2 regulator #1. Tested its function. No issues. Received a high Cl2 Treated free alarm on startup which quickly dissipated on shutdown and was able to restart with no issue. | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-12-15
EAST | December | 11:39 - 14:27 Opened FCV to draw down Zone 1 ET. Placed the pumps back to auto afterwards and P2 started in duty 1. Zone 1 ET is 50%. | Stouffville Zone 1 Booster Pumping Station | 2025-12-17
EAST | December | Opened FCV to 50 l/s. Man/off pumps. | Stouffville Zone 1 Booster Pumping Station | 2025-12-30
EAST | December | On site for station check Recorded observations in the shared PWQ sheet Verified chlorine analyzers, 8:47, in mg/L Influent total Cl - G 1.36; A 1.41 Effluent free Cl - G 2.09; A 2.10 Effluent total Cl - G >4.40; A 4.80 Simulated free Cl - G 2.02; A 1.99 Station and equipment okay | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-12-10
EAST | December | Assigned pump 1 and pump 2 to duty 1. Flow set point changed from 95 l/s to 110 l/s. | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-12-15
EAST | December | On site for station check. Reviewed scada, duty active, controlling tower @ 55%, system pressure: 633 kpa. Visual inspection in and around station Verification of equipment and instrumentation. Verified chlorine analyzers readings. Recorded Station readings in PWQ sheet No issues Outstanding alarm: None Grab Residuals @0944-0956 hrs Residual Grab Analyzer Influent TCL 1.42 mg/l. 1.41 mg/l FCL 2.10 mg/l. 2.09 mg/l TCL. 4.60 mg/l 4.75 mg/l Sim. FCL 2.01 mg/l. 1.99 mg/l Chemical system: Chlorinator 1 open at 31%, DF: 78%, Cl booster P1 DP= 1600 kpa Rotated Pump duty (HL) to #2 in duty 1, P3 in duty 2, P1 in duty 3 Changed chlorine cylinders bank 1 with Joe M. | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-12-12
EAST | December | Reset outstanding P3 VFD fault. | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-12-02
EAST | December | On site for chlorine cylinder change on bank 1 Reviewed scada, duty active Purged cylinders, chlorine leak alarm triggered during cylinder isolations Duty shutdown during leak alarm, causing effluent free chlorine to drop to 0.05 mg/l, grab was 0.08 mg/l Switched cylinders tested for leaks, nothing found Tested vacuum switchover, work ok, but bank 1 will not stay on stand by, placed it bank 1 in service for the weekend 1430 hrs: Started backflushing @ 31 l/s to bring effluent free residual chlorine back up, 1438 hrs: Effluent free chlorine analyzer reading @ 1.78 mg/l. Stopped backflushing 1445 hrs: did grab on effluent free chlorine when analyzer was reading 1.83 mg/l. Grab was 1.82 mg/l Cleared all alarms and returned system to auto. Pumps started right away, no issues Did a final check for leaks while duty was active before leaving site no issues. Notified ROC ROC issued a CMU | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-12-05
EAST | December | On site for station check Reviewed scada, duty active, controlling tower @ 58% Visual inspection in and around station Verification of equipment and instrumentation. Verified chlorine analyzers readings. Outstanding alarm: Free chlorine total analyzer reading a little higher, made adjustment on the water sample line to the analyzer and will continue to monitor. Grab Residuals @ 1052 hrs Residual Grab Analyzer FCL 2.03 mg/l. 2.09 mg/l TCL. 4.79 mg/l 4.79 mg/l Sim. FCL 2.00 mg/l. 1.98 mg/l Influent TCL 1.34 mg/l. 1.35 mg/l Chemicals: Chlorinator1 opened @ 41 dosing at 54 kgd Chlorine BP1 pressure @ 240 psi Booster pumps (HL) #1 and 3 in duty1 System pressure: 667 kpa Recorded station readings into PWQ data sheet No issues | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-12-03
EAST | December | Vibration testing | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-12-03
EAST | December | Switched pump duty for Lee F's vibration test. Tested Pump 3 with 90 l/s flow setpoint. Placed P1 and P3 in duty 1 and flow setpoint is changed back to 140 l/s. | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-12-03
EAST | December | On site for station check Reviewed scada, duty active, controlling tower @ 62% Visual inspection in and around station Verification of equipment and instrumentation. Verified chlorine analyzers readings. Outstanding alarm: None Grab Residuals @ 1220 hrs Residual Grab Analyzer FCL 2.06 mg/l. 2.08 mg/l TCL. 4.68 mg/l 4.77 mg/l Sim. FCL 1.65 mg/l. 1.65 mg/l Influent TCL 1.37 mg/l. 1.37mg/l Chemicals: Chlorinator2 opened @ 36 dosing at 50 kgd Chlorine BP2 pressure @ 240 psi Booster pumps (HL) #1 and 2 in duty1 System pressure: 677 kpa Recorded station readings into PWQ data sheet No issues | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-12-01
EAST | December | On site for station check and chlorine cylinder delivery Recorded observations in the shared PWQ sheet Station and equipment okay | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-12-08
EAST | December | Changed duty so that only pump 3 is running in duty 1. Flow setpoint changed from 140 l/s to 90 l/s. | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-12-08
EAST | December | On site for station check Shut down station to verify chlorine analyzers, 9:31, in mg/L Influent total Cl - G 1.39; A 1.36 Effluent free Cl - G 2.05; A 2.06 Effluent total Cl - G 2.88; A 2.90 Simulated free Cl - G 2.04; A 1.96 Recorded observations in the shared PWQ sheet Turned unit heaters on in generator room - was cold Station back in service, station and equipment okay | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-12-16
EAST | December | On site to change chlorine cylinders with Joe Mazza for the left bank. Duty is active. Tested vacuum switches, no issue.? | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-12-23
EAST | December | On site to change chlorine cylinders with Stephen Baidy. Duty is not active.? Purged the system with chlorine #?2.? After changing, tested vacuum switches, no issues.? Re-assigned pump duties, P2 and P3 are in duty 1.? | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-12-29
EAST | December | Grease pumps and motors Chlorine leak facility shut down | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-12-18
EAST | December | On site for preventative maintenance Completed Chlorine analyzer maintenance Chlorine leak detector test Chlorine cylinder emergency kit inspection JHSC inspection Chlorine scrubber check Chemical system inspection - chlorine Air valve flush and inspection Pump and motor inspection Housekeeping Generator test run Generator test run: Fuel Start 2987/2496 L Stop 2987/2410 L Hours Start 457.6 Stop 459.3 Statistics Oil pressure 60 PSI Oil temperature 182 F Coolant temperature 173 F Speed 1799 RPM Exhaust temperature 700 F Current 176 A Voltage 600 V Power 175 kW Frequency 59.9 Hz Station and equipment okay | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-12-17
EAST | December | On site for station check Verified chlorine analyzers, 8:24, mg/L Influent TCl - G 1.43; A 1.44 Effluent FCl - G 2.12; A 2.11 Effluent TCl - G >4.40; A 4.87 Simulated FCl - G 1.97; A 1.87 Recorded observations in the shared PWQ sheet Replaced effluent FCl analyzer reagent Station and equipment okay | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-12-29
EAST | December | On site for station check Verified chlorine analyzers, 9:15, mg/L Influent TCl - G 1.40; A 1.43 Effluent FCl - G 2.20; A 2.17 Effluent TCl - G >4.40; A 4.89 Simulated FCl - G 1.90; A 1.83 Recorded observations in the shared PWQ sheet and reviewed SCADA Station and equipment okay | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-12-22
EAST | December | Under Direction of OIC (Dan Zhou) On Site for monthly PM work orders; - JHSC Health and Safety Inspections - Inlet/Outlet Heat Trace System Inspection - Sump Pit System Inspection - Manual valve exercise - General Housekeeping - AIT Analyzer maintenance/clean Analyzer Maintenance/Clean Start Clean @ 11:13 hrs Tower filling-water not being sent to distribution Stop Clean @ 11:43 Post maintenance/clean verification Grab @ 11:59 FCl: 2.44 mg/L Analyzer: 2.42 mg/L Equipment OOS: None Facility OK | Stouffville Zone 2 Elevated Tank | 2025-12-15
EAST | December | On site with Travis Wyatt for chlorine cylinder change Purged lines and Changed right side bank. After switching, and opening cylinders, the chlorine leak alarm came in. Scrubber started, and emergency valves activated. Once the PPM got below 1.0, entered with SCBA. Checked for leaks, none found, suspect that the leak was from regulator vents. Will continue to monitor, reset emergency valves Station ok | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2025-12-18
EAST | December | On site for station check, and weekly micro sampling (W11438547) Tower level - 82% and draining at 35 L/s Recorded station readings in PWQ sheets Verified analyzer reading: Outlet @ 12:31 Free Grab: 1.85 mg/L Analyzer: 1.89 mg/L Total Grab: 2.00 mg/L Collected micro sample @ 12:36 from outlet. Reviewed trends, equipment ok Station ok | Stouffville Zone 2 Elevated Tank | 2025-12-10
EAST | December | Under Direction of OIC (Dan Zhou) On site for; - Station Checks - Regulatory Sampling, Micro (W11419179) Regulatory samples taken @ 13:01 hrs. Data in PWQ Excel Workbook Grabs @ 13:01 hrs. FCl: 1.48 mg/L TCL: 1.68 mg/L Analyzer FCl: 1.54 mg/L Tower Draining Equipment out of Service: None | Stouffville Zone 2 Elevated Tank | 2025-12-03
EAST | December | On-site for station check and weekly bacT samples collection Reviewed scada, et @ 90% and filling @ 80 l/s Visual inspection of equipment and instrumentation Verified analyzer reading Grab residual at 0805 hrs: FCL = 1.77 mg/l Analyzer: 1.81 mg/l TCL = 1.95 mg/l Recorded station reading into pwq data sheet No issues Returned to site to replace CL17 analyzer reagents as there was none on site | Stouffville Zone 2 Elevated Tank | 2025-12-29
EAST | December | Under Direction of OIC (Dan Zhou) On site for; - Station Checks - Regulatory Sampling, Micro (W11454773) Regulatory samples taken @ 13:45 hrs. Data in PWQ Excel Workbook Grabs @ 13:45 hrs. FCl: 1.83 mg/L TCL: 2.09 mg/L Analyzer FCl: 1.92 mg/L Tower Draining Equipment out of Service: None | Stouffville Zone 2 Elevated Tank | 2025-12-16
EAST | December | On site to check station and equipment. Well duty is active upon arrival, but tower is draining at 15 l/s.? 12:58 grab chlorine residual from riser tap: FC: = 1.72 mg/l, TCL = 1.96 mg/l. Analyzer free = 1.80 mg/l. 12:58 Collected Bac-T sample, YD W11469946. Station readings are in PWQ sheet.? Reviewed trends, station is under normal operation. No outstanding alarms. | Stouffville Zone 2 Elevated Tank | 2025-12-22
EAST | December | On site for station check, and weekly micro sampling (W11438547) Tower level - 64% and draining at 34.7 L/s Recorded station readings in PWQ sheets Verified analyzer reading: Outlet @ 13:18 Free Grab: 1.25 mg/L Analyzer: 1.27 mg/L Total Grab: 1.43 mg/L Collected micro sample @ 13:21 from outlet. Reviewed trends, equipment ok Station ok | Stouffville Zone 1 Elevated Tank | 2025-12-10
EAST | December | Under Direction of OIC (Dan Zhou) On site for; - Station Checks - Regulatory Sampling, Micro (W11419179) - Flouride for blended systems sampling (W11419412) Reg. Samples taken @ 10:54 hrs. Data in PWQ Excel Workbook Grabs @ 10:54 hrs. FCl: 1.06 mg/L TCl: 1.22 mg/L Analyzer: FCl: 1.05 mg/L Tower draining (currently deep cycling) Equipment OOS: None Facility OK | Stouffville Zone 1 Elevated Tank | 2025-12-03
EAST | December | On site to check station and equipment. Tower is on a down cycle at 75%. 10:25 grab chlorine residual from header: FC: = 1.52 mg/l, TCL = 1.69 mg/l. Analyzer free = 1.47 mg/l. 10:25 Collected Bac-T sample, YD W11469946. Station readings are in PWQ sheet.? Reviewed trends, station is under normal operation. No outstanding alarms. | Stouffville Zone 1 Elevated Tank | 2025-12-22
EAST | December | Under Direction of OIC (Dan Zhou) On site for; - Station Checks - Regulatory Sampling, Micro (W11454773) Reg. Samples taken @ 13:11 hrs. Data in PWQ Excel Workbook Grabs @ 13:11 hrs. FCl: 1.45 mg/L TCl: 1.62 mg/L Analyzer: FCl: 1.48 mg/L Equipment OOS: None Facility OK | Stouffville Zone 1 Elevated Tank | 2025-12-16
EAST | December | In relation to load test @ STPSTL @ 11:34 hrs. Remotely activated duty tower filling @ 12:10 hrs. deactivated duty tower draining | Stouffville Zone 1 Elevated Tank | 2025-12-16
EAST | December | On-site for station check and weekly bacT samples collection Reviewed scada, et @ 72% and filling @ 36.4 l/s Visual inspection of equipment and instrumentation Verified analyzer reading Grab residual at 0805 hrs: FCL = 1.35 mg/l Analyzer: 1.34 mg/l TCL = 1.59 mg/l Recorded station reading into pwq data sheet No issues | Stouffville Zone 1 Elevated Tank | 2025-12-29
EAST | December | On site for monthly maintenance: Flushed Air valves Dehumidifier inspection, could not get to turn on, WO issued. Flood alarm test. No issues. High/Low alarm test. No issues. JHSC inspection. Sump pump inspection 13:15hrs: Cleaned Total Hach Cl17 Chlorine Analyzer. Verified Analyzer after cleaning: TCL Grab residual: 1.52mg/l Analyzer: 1.47mg/l Eyewash solution replacement Overhead crane inspections complete. No issues. Hatch/vent inspection complete. | Markham PD6 Reservoir | 2025-12-15
EAST | December | On site for monthly work orders, notified ROC of work being done. JHSC Inspections - Eyewash flow alarm triggered and cleared, Heat Trace System Inspection, Portable Generator Test Run, General housekeeping, Chlorine analyzer maintenance: Completed cleaning and verified with grab sample. Outlet analyzer @ 14:25 Grab: 1.42 mg/L. Analyzer: 1.52 mg/L Adjusted analyzer after three grab samples. | Stouffville Zone 1 Elevated Tank | 2025-12-17
EAST | December | On site for station check and sampling W11438575 Recorded observations in the shared PWQ sheet Collected samples from North cell while draining, 9:50, mg/L South cell Grabs: FCl 0.07; TCl 1.54 North cell Grabs: FCl 0.08; TCl 1.41 Analyzer: TCl 1.46 Station and equipment okay | Markham PD6 Reservoir | 2025-12-10
EAST | December | On site for station check and collection weekly bacT sample. Reviewed scada, reservoir level @ 43% and draining 691 l/s Visual inspection in and around station Verification of equipment and instrumentation. Verified chlorine analyzers readings. Performed nitrification monitoring tests Outstanding alarm: None Residual: Cell #1(south). Cell #2 (North). Analyzer Time (HR) FCL. 0.05 0.08 0.08 TCL. 1.44 1.52 0.05 1210 hrs Mono. 1.16 Total Amm. 0.32 Free Amm. 0.09 Nitrite 0.001 Temperature. 6.8C Res level. 43% pH. 8.03 Samples collected from north cell (2) Recorded station readings into pwq data sheet No issues | Markham PD6 Reservoir | 2025-12-03
EAST | December | Received a call from ROC regarding hi and hi hi flow alarms from pd6 during supplying. ROC verified CoT is not pumping 2115 hrs: During scada investigation, noticed erratic flow from flowmeter on MV6 (supplying) header ranging from 700 to 1035 L/s causing hi flow alarms. Reservoir was in supply in mode. 2130 hrs: placed MV1 in manual and open to 100% When MV1 was fully opened, placed MV6 in manual and fully closed (0%), this is to confirm if this is a flowmeter issue or its actual demand flow. MV1 was pretty consistent hovering around 950 l/s for about 45 mins, no alarms triggered. Flowmeter on MV6 while fully closed at 0%, was still reading flows between 10 and 114 L/s. Directed ROC to return valves to normal operations for the night. Further investigation will needed with Instrumentation team. | Markham PD6 Reservoir | 2025-12-07
EAST | December | On site for station check and BacT sampling W11454801 Collected samples from North cell while draining, 10:10 Chlorine residuals as follows, in mg/L North cell FCl - G 0.01 TCl - G 1.37; A 1.42 South cell FCl - G 0.05 TCl - G 1.50 Recorded observations in the shared PWQ sheet, including nitrification monitoring Station and equipment okay | Markham PD6 Reservoir | 2025-12-16
EAST | December | On site for station check and sampling W11469974 Collected sample from north cell and verified analyzer, 9:45, in mg/L North cell: FCl G 0.11 TCl G 1.47; A 1.48 South cell: FCl G 0.10 TCl G 1.56 Recorded observations in the shared PWQ sheet Station and equipment okay | Markham PD6 Reservoir | 2025-12-22
EAST | December | On site for station check and sampling W11483524 Collected samples from North cell while draining and verified North cell TCl analyzer, 9:10, mg/L South cell FCl: G 0.09; TCl: G 1.56 North cell FCl: G 0.05; TCl: G 1.41; A 1.49 Recorded observations in the shared PWQ sheet Station and equipment okay | Markham PD6 Reservoir | 2025-12-29
CENTRAL | December | Cleared lolo co2 adjusted alarm and monitored fill of conduit/filters remotely. Returned HLPs to auto. | Keswick Water Treatment Plant | 2025-12-10
CENTRAL | December | KSTP on-site for station check/lab. Activated D1 to observe plant operation while on-site. Treated grab/analyzer results as follows (09:20): Free Cl (mg/L): G: 1.46 A: 1.45 Total Cl (mg/L): G: 1.79 A: 1.85 Turbidity (NTU): G: 0.075 A: 0.081 pH: G: 7.4 A: 7.33 Fluoride (mg/L): G: 0.82 A: 0.80 Temperature (?C): G: 3 A: 1.2 Clearwell Influent Free Cl grab/analyzer at 09:20 (mg/L): G: 1.68 A: 1.67 Entered station readings into shared PWQ/lab excel files. Topped up PACl wash/day tanks. No new issues found while on-site. | Keswick Water Treatment Plant | 2025-12-15
CENTRAL | December | On-site for station check. Reviewed previous elog entry by Patrick Forbert, reviewed trends, appears that low lift ramp speed may be impacting CO2 dose (ramp too quickly causing flow variation impacting CO2 dosing). Alarms cleared, started duty to observe plant in operation. CO2 adjusted pH grab at 09:29 of 7.09, analyzer reading 7.14, target setpoint 7.1. Adjusted CO2 adjusted target setpoint from 7.1 to 7.3 to try and minimize lolo pH lock out on low lift pumps, and will create WO for PCS/electrical to adjusted ramp speed on low lift pumps. Will monitor filter performance and coagulation. Informed on-call operator (Patrick F). Adjusted Treated pH analyzer from 6.97 to 7.30 at 09:44 to match grab samples (7.30). Adjusted treated fluoride analyzer from 0.66mg/L to 0.76mg/L at 09:44 based on grab samples and calculated dosage (0.76mg/L). Entered station readings into shared PWQ/lab excel files. No other new issues found while on-site. Completed daily filter performance review at 11:34, both filters 100%. | Keswick Water Treatment Plant | 2025-12-12
CENTRAL | December | Completed daily filter performance review, both filters 100% for the month. | Keswick Water Treatment Plant | 2025-12-15
CENTRAL | December | @17:41 - ROC called for CO2 adjusted PH Lolo alarm, interlocking the low lift pumps. Reviewed SCADA trends, analyzer experienced a sudden drop from 7.1 to 6.2. There is also filter #2 currently in backwash. @17:55 - placed high lift pumps to manual off, and closed the effluent valve on filter #1, as there is no flow going to the pre treatment as low lifts are interlocked. @17:55 - settled water conduit low alarm also came in. Will monitor CO2 adjusted pH for now, and see if it recovers. Plant is in manual off. @18:11 - CO2 adjusted PH is 6.7. Cleared alarm, and low lift pumps restarted. Monitoring plant while the pretreatment is filling again and the backwash finished. Placed filter #1 effluent valve back to auto @18:34. Filter back to production. Duty is almost to stop setpoint, will leave the plant off for the night so central team can investigate tomorrow on site if there are further issues. Informed ROC, alarms cleared, plant in manual off for the night | Keswick Water Treatment Plant | 2025-12-11
CENTRAL | December | On-site with Donald Moses for station check, weekly micro sampling (W11438603) and weekly GLIP sampling work orders. CO2 adjusted pH at 08:50: G: 8.05 A: 7.1 (adjusted to 8.05 to better reflect grab samples) Topped up PACl day/wash water tanks. Collected raw water and treated water samples. Treated Grab residuals at 09:17 as follows (mg/L): Free Cl: 1.47 Total Cl: 1.77 CO2 adjusted pH at 10:20: G: 6.97 A: 7.48 (adjusted to 6.97 to better reflect grab samples) CO2 adjusted pH at 10:35: G: 7.14 A: 7.13 Checked station and equipment, will monitor CO2 adjusted pH analyzer/CO2 dose. Daily filter performance review at 10:48, both filters 100% for the month. Adjusted PACl dose from 8 to 7mg/L based on visual/lab analysis of filters, will continue to monitor. Changed Pre-chlorine cylinder A with Donald Moses. | Keswick Water Treatment Plant | 2025-12-10
CENTRAL | December | Completed daily filter performance check via remote SCADA, both filters 100% for the month. | Keswick Water Treatment Plant | 2025-12-11
CENTRAL | December | 09:02 filter turbidity performance. Both filters at 100%. | Keswick Water Treatment Plant | 2025-12-10
CENTRAL | December | Completed filter performance check: filter 1- 100%, filter 2- 100% | Keswick Water Treatment Plant | 2025-12-02
CENTRAL | December | On-site for station check. Ran HLP4 in remote/man to bring down clearwell level and initiated manual start of backwash for filter 1 to achieve greater offset between filter run times (F1 current 22hr, F2 current 17hr). Placed HLPs man/off while backwash sequence continues. Adjusted PACl dose from 10mg/L to 9mg/L based on visual observations of Filters and runtime hours, will monitor. Back wash on Filter 1 completed, filter ran to raw water well following backwash as per sequence, at 13/15minute mark I placed effluent valve FILT_FIT1_MV2 in manual/0% to accommodate site shutdown for PCS to replace PAC switch and this caused Filter 1 backwash is out of service alarm. Reset run hours on filter 1 as backwash was completed but operator adjustable filter to waste runtime did not lapse prior to me placing effluent valve in manual. 09:20 PCS replacing PAC switch, plant off. 09:35 returned site to service following PCS switch replacement and cleared alarms, activated D1. Treated water lab/analyzed results (10:16) as follows: Free Cl G: 1.54mg/L A: 1.58mg/L Total Cl G: 1.88mg/L A: 1.94mg/L Turbidity G: 0.065NTU A: 0.068NTU pH G: 7.23 A: 7.05 Fluoride G: 0.64mg/L A: 0.67mg/L Temperature G: 4?C A: 2.6?C Topped up PACl BW and Day tanks. Checked station and equipment, no other new issues found, site running in duty. | Keswick Water Treatment Plant | 2025-12-05
CENTRAL | December | Onsite to complete work orders. 09:04 station running at 80 l/s. 09:09 kstp daily filter turbidity review. Both filters at 100%. Chlorine emergency kit A inspection. 09:20 notified ROC placed high lift pumps in manual off. Filter top sample pump maintenance. Cleaned settled water lit, turbidity and chlorine analyzer. 09:47 Verified analyzers: Free chlorine grab 0.02 mg/l. Analyzer: 0.02 Turbidity. 0.278 ntu. Analyzer: 0.269 10:04 tested chlorine leak detection and evcs system. No issues. Reset alarms. Tested chlorine gas system and vacuum leak. No issues. Flushed raw water sample line. Triggered low raw ph and low settled water channel level alarms. Cleared when with complete. Placed all pumps back to auto with no further issues on site. | Keswick Water Treatment Plant | 2025-12-04
CENTRAL | December | Monthly filter performance check, both filters 100% for the month November. | Keswick Water Treatment Plant | 2025-12-01
CENTRAL | December | Put pumps back to auto and activated duty at 11:55. | Keswick Water Treatment Plant | 2025-12-02
CENTRAL | December | Filter performance turbidity review. Both filters 100% No issues. | Keswick Water Treatment Plant | 2025-12-05
CENTRAL | December | Put hi lift pumps in manual at 08:15 due to deer park ET isolation and drain. | Keswick Water Treatment Plant | 2025-12-02
CENTRAL | December | Filter turbidity performance review. Both filters 100% and no issues found. | Keswick Water Treatment Plant | 2025-12-08
CENTRAL | December | Remotely assisted Inst with fluoride analyzer alarm troubleshooting. Ran HLP manually with fluoride pump off to trigger Lo alarms on analyzer. Once troubleshooting complete put system back to auto | Keswick Water Treatment Plant | 2025-12-08
CENTRAL | December | Onsite for diesal gen test with total power. 09:30 notified roc. Ran generator in manual. 09:34 shut down generator. 09:35 initiated a gen transfer test. Filter backwash faults triggered, raw sample pump and chlorine evc system faulted due to power transfer. Reset with no issues. 09:45 placed low lifts back in auto. 10:35 completed generator run. Fuel at 1862. Run meter at 917.8 to 918.9. No issues found. | Keswick Water Treatment Plant | 2025-12-02
CENTRAL | December | Onsite for station check and sampling. W11419235 and W11419057. Completed filter performance review. Both filters at 100%. 10:16 initiated filter backwash. Run hours at 24.2. Topped up pacl and fluoride day tanks. Station now running in duty 1 at 80 l/s. 11:00 collected raw water samples and verified analyzers. 11:46 collected pre filtration sample. 11:36 collected backwash effluent raw sample. 11:50 collected post filtration sample. 12:00 collected treated water samples and verified analyzers(mg/l): Chlorine free grab: 1.69. A 1.70. Chlorine total grab: 2.00 A 2.06. Fluoride grab 0.654: A 0.70. Turbidity grab: 0.062 A 0.055 NTU 12:10 collected backwash effluent treated sample. Completed station rounds and lab work. Entered readings into pwq sheets. 13:47 placed hi lift p4 in auto. 14:01 completed shoreline observation. | Keswick Water Treatment Plant | 2025-12-03
CENTRAL | December | On-site for station check. Topped up PACl day/BW tanks. Noticed HLP2/3 VFDs? setpoints constantly adjusting and varying flow when duty activated, reviewed trends. Appears that when 2 pumps running the VFDs are too sensitive to each other and cannot find stable output. Reduced flow setpoint to 80L/s and adjusted pump duties so 1 pump is running in D1. Adjusted filter flow setpoint (40L/s) to match HLP setpoint. Will create WO for CMS and/or PCS to adjust VFDs to operate more efficiently while maintaining target flow setpoint. Adjust raw water sample pump flow to reduce air entrapment in sample lines. No other new issues found. | Keswick Water Treatment Plant | 2025-12-01
CENTRAL | December | On-site for station check. Activated D1 for plant to run while taking grabs/lab analysis. Found raw water turbidimeter being starved of water, adjusted flow and raw turbidity fault cleared. CO2 adjusted pH analyzer reading not reflective of grab samples (G: 8.05, A: 6.58 @10:01) and analyzer providing message ?CH1: M125 Sensor Glass?, informed Instrumentation Parth Patel who will come to site to replace sensor. Verified analyzers. Treated grab/analyzer results as follows (10:20): Free Cl: G: 1.68mg/L A: 1.70mg/L Total Cl: G: 2.04mg/L A: 2.14mg/L Turbidity: G: 0.068NTU A: 0.062NTU pH: G: 7.13 A: 6.91 Fluoride: G: 0.76mg/L A: 0.70mg/L Temperature: G: 2.9?C A: 2.6?C Clear Well Influent Free Cl Grab/analyzer (10:17): G: 1.77mg/L A: 1.77mg/L Entered station readings into shared PWQ/Lab excel files. Path Patel and Ricardo Locatelli on-site for CO2 adjusted pH probe replacement, I placed site man/off and placed the pH meter in calibration mode via SCADA. Enabled pH lolo alarm for CO2_AIT1. Changed post chlorine cylinder with Alex Bell (OIT/under direction of OIC), weigh scale lolo alarm triggered while changing cylinders, reading correctly again and cleared alarm. Returned site to normal operation following instrumentations replacement of pH probe, ran low lifts/settling tank valve 1 to move water across sensor to test operation, appears to be operating normally. No other new issues found while on-site. | Keswick Water Treatment Plant | 2025-12-08
CENTRAL | December | Completed filter performance check: filter 1- 100%, filter 2- 100% | Keswick Water Treatment Plant | 2025-12-01
CENTRAL | December | Onsite to troubleshoot CO2 pH issues Informed ROC and operations. Plant off line Removed pH probe. Calibrated new pH probe and installed -all ok Also troubleshooting nuisance AIT alarm that is triggered when Fluoride drops below 0.2 Informed Ben Hess of of our observations Cleared associated alarms . Low fluoride alarm will clear when plant back online Informed ROC, armed building and left site | Keswick Water Treatment Plant | 2025-12-08
CENTRAL | December | Accidentally signed into elog, was not on-site from 13:08 to 13:09 December 5 2025. | Keswick Water Treatment Plant | 2025-12-05
CENTRAL | December | Filter turbidity performance review. Both filters are 100% | Keswick Water Treatment Plant | 2025-12-09
CENTRAL | December | On-site for assigned work orders, informed ROC. Placed raw water turb/pH/temp/Chlorine analyzers in cal mode and flushed raw water sample intake line with plant off. Returned system to normal operation. Replaced eyewash station solution in fluoride room. Completed general housekeeping. No new issues found while on-site. | Keswick Water Treatment Plant | 2025-12-09
CENTRAL | December | -Performed filter turbidity performance check - 100% | Keswick Water Treatment Plant | 2025-12-31
CENTRAL | December | -on site to investigate the dampers in the generator room. Sean and my self found that the exhaust fan timer has failed. Looking to get a replacement and installed. We also found the combustion damper fins have broken from their track we will need to return in the spring to investigate repairing them from above. Placed system back to auto and original set points. Under direction of oic. | Keswick Water Treatment Plant | 2025-12-23
CENTRAL | December | Filter performance review via scada @ 15:25 F1 and F2 100% all ok Ops normal | Keswick Water Treatment Plant | 2025-12-18
CENTRAL | December | At 08:21 put hi lift pumps in manual to activate duty for GWTP. | Keswick Water Treatment Plant | 2025-12-18
CENTRAL | December | On-site for station check and lab. Found backwash P1 valve powered down via switch, turned back on and cleared modbus alarm, WO created for PCS to adjust interlock on pump when valve unavailable. Contractors on-site for generator upgrades. Completed daily filter performance review, both filters 100% for the month. Verified analyzers, adjusted CO2 adjusted pH analyzer at 11:40 from 7.30 to 7.05 based on average grab sample, adjusted again at 12:55 from 7.30 to 7.72 based on average grab sample. Will monitor CO2 adjusted pH analyzer. CO2 adjusted pH at 13:40 G: 7.26, A: 7.32. Checked station and equipment, no other new issues found. Topped up PACl day/wash tanks, and fluoride day tank. | Keswick Water Treatment Plant | 2025-12-19
CENTRAL | December | Onsite to replace chlorine cylinder. Completed filter turbidity performance check. Both filters at 100%. No issues found. | Keswick Water Treatment Plant | 2025-12-24
CENTRAL | December | Filter performance review via scada @ 15:25 Both F1 and F2 100% - All ok | Keswick Water Treatment Plant | 2025-12-17
CENTRAL | December | Reviewed filter turbidity performance. Both filters 100% performance. No issues found. | Keswick Water Treatment Plant | 2025-12-29
CENTRAL | December | Reviewed filter turbidity performance. I filters 100%. No issues found. | Keswick Water Treatment Plant | 2025-12-30
CENTRAL | December | On-site for station check/lab, weekly micro sampling (W11483552) and GLIP sampling work orders. ROC Carter called to inform power blips have caused site to interlock shortly before I arrived onsite. Reviewed trends and placed Fluoride pumps man/off as analyzer seems to drift high while site not running. Reset Cl2 emergency closure fault alarm and cleared interlocks on site. Site started, fluoride pumps remain man/off. HLPs interlocked on fin water fluoride res hihi alarm at 10:56. Analyzer read fluoride residual of 1.50 from 10:56:15 to 10:56:30. Immediately took grab sample at 10:57 and noticed air bubble on analyzer - removed air bubble from analyzer, fin water fluoride grab result of 0.42mg/L, analyzer now reading 0.5mg/L. No reportable adverse event as fluoride pumps were not running at time of alarm, air bubble on analyzer caused false reading and grab results are not adverse. Reset alarms and monitored HLP start up with fluoride pumps remaining man/off. Informed ORO Dan Zhou. 11:36 returned fluoride pumps to remote/auto and monitored fluoride analyzer residual. Topped up PACl day/wash tanks and fluoride day tank. Entered station readings into shared PWQ/lab excel files. Collected raw/treated samples, treated grabs/analyzer results at 13:03 as follows: Free Cl (mg/L): G: 1.54 A: 1.54 Total Cl (mg/L): G: 1.88 A: 1.94 Turbidity (NTU): G: 0.075 A: 0.066 pH: G: 7.20 A: 7.12 Fluoride (mg/L): G: 0.82 A: 0.76 No other new issues found while on-site. Informed ROC. | Keswick Water Treatment Plant | 2025-12-29
CENTRAL | December | On-site for station check, lab, weekly micro sampling (W11454829), and weekly GLIP sampling WOs. Plant running in duty upon arrival. Treated water grab residuals as follows (mg/L): Free Cl (10:41): 1.51 Total Cl (10:41): 1.96 Collected samples. Verified analyzers. Checked station and equipment, no new issues found. Deactivated duty for storage sampling later today. | Keswick Water Treatment Plant | 2025-12-16
CENTRAL | December | Daily filter performance review via scada @ 15:12 (as directed) F1 and F2 100% - All OK | Keswick Water Treatment Plant | 2025-12-19
CENTRAL | December | ROC informed of KSTP post CO2 PH lolo. Reviewed SCADA, LLP interlocked due to the alarm. Man/stopped settling tank draining. Post CO2 PH recovered to 6.8, reset alarm.? LLPs resumed operation.? Filter 2 is going through a backwash.? As of 13:00, post CO2 PH is stabilized to 7.2. Returned plant to auto operation.? | Keswick Water Treatment Plant | 2025-12-25
CENTRAL | December | Attempt to grease bottom motor bearings All pumps off plant is off | Keswick Water Treatment Plant | 2025-12-16
CENTRAL | December | Daily filter performance review via scada @ 15:35 F1 and F2 100% - all ok | Keswick Water Treatment Plant | 2025-12-22
CENTRAL | December | Reviewed daily and monthly filter performances. They are all 100%. Activated duty, KSTKWP = 55%. | Keswick Water Treatment Plant | 2025-12-26
CENTRAL | December | On-site for assigned work orders, informed ROC. Placed all processes man/off for chlorine/turbidimeter maintenance: Settled (10:00): Free Cl: G: 0.01mg/L A: 0.01mg/L Turbidity: G: 0.133NTU A: 0.080NTU Filter 1 (10:20): Turbidity: G: 0.069NTU A: 0.055NTU Filter 2 (10:20): Turbidity: G: 0.066NTU A: 0.054NTU 10:31 tested filter1/2 turbidimeter flow faults by isolating flow to analyzers, reset alarms once triggered and flow returned. 10:37 tested filter 1 turbidity CCP with 20NTU standard vial, alarms/trends at this time due to 20NTU standard as followed by assigned WO job plan. 10:40 began cleaning of Treated water Free CL17 analyzer. 10:45 tested hi/hihi turbidity alarms for settled water - alarms triggered at 10:59. 10:57 tested filter 2 turbidity CCP with 20NTU standard vial, alarms/trends at this time due to 20NTU standard as followed by assigned WO job plan. 11:00 Finished cleaning/maintenance of depolox treated total Cl, treated free Cl CL17, and Clearwell Influent free Cl CL17sc analyzers and verified as follows (mg/L): Clearwell Influent Free Cl (11:05): G: 1.54 A: 1.52 Treated Free Cl (11:05): G: 1.54 A: 1.50 Treated Total Cl (11:05): G: 1.83 A: 1.88 Treated turbidity (11:20): G: 0.072A: 0.069NTU 11:21 tested treated water turbidity CCP with 20NTU standard vial, alarms/trends at this time due to 20NTU standard as followed by assigned WO job plan. 11:30 tested Clearwell Influent Free Cl and Treated Free/Total Cl hi/low alarm setpoints. Completed fluoride analyzer maintenance. 11:50 completed cl17 maintenance for wet well total/free Cl CL17 analyzers, verified as follows at 12:13: Free Cl: G: 0.02mg/L A: 0.02mg/L Total Cl G: 0.19mg/L A: 0.20mg/L 11:55 11:21 tested raw water turbidity CCP with 20NTU standard vial, alarms/trends at this time due to 20NTU standard as followed by assigned WO job plan. Raw water turbidity analyzer grab/analyzer at 12:13: G: 0.125NTU A: 0.100NTU Reset all alarms and returned system to normal operation (auto). Rotated HLP2 to D1 to test/inspect FCV, duty active. Completed JHSC inspection. Completed wash pump inspection. No new issues found while on-site. Site running in auto. | Keswick Water Treatment Plant | 2025-12-18
CENTRAL | December | Completed daily filter performance review, both filters 100% for the month. | Keswick Water Treatment Plant | 2025-12-16
CENTRAL | December | Daily filter performance review via scada @ 15:30 F1 and F2 100% - All ok | Keswick Water Treatment Plant | 2025-12-23
CENTRAL | December | On-site for assigned work orders. Completed general housekeeping, cleaned bathrooms and signed off on posted sign off forms. Completed settling tube maintenance with Donald Moses. Completed PRV inspection and blower inspections. Noticed small amount of water pooling in corner of high lift room, 2?C current outdoor temp, water seems to be slowly dripping from behind sound dampening panels. Will notify Supervisor so property services can investigate. No other new issues found while on-site. Site in auto. | Keswick Water Treatment Plant | 2025-12-17
CENTRAL | December | On-site for station check, lab and Cl2 cylinder change. Changed Post-Inj Cylinder bank A with Donald Moses. Replaced Settled Free Cl and Raw Free/Total Cl CL17 analyzer reagents. Topped up PACl Day/BW tanks. Entered station/lab readings into shared PWQ/Lab excel files. Verified analyzers. Treated Cl grab/analyzer results as follows at 10:28 (mg/L): Free Cl: G: 1.48 A: 1.48 Total Cl: G: 1.85 A: 1.87 Checked station and equipment, no new issues found while on-site. Filter performance check, both filters 100% for the month. | Keswick Water Treatment Plant | 2025-12-24
CENTRAL | December | Reviewed daily and monthly filter performances. They are all 100%. Activated duty, KSTKWP = 58%. | Keswick Water Treatment Plant | 2025-12-25
CENTRAL | December | On-site for station check/lab, weekly GLIP sampling and weekly micro (W11470002) work orders. Treated grab/analyzer results as follows (10:42): Free Cl (mg/L): G: 1.58 A: 1.57 Total Cl (mg/L): G: 1.88 A: 1.96 Turbidity (NTU): G: 0.070 A: 0.065 pH: G: 7.23 A: 7.40 (adjusted offset from 0.33 to 0.15 to better reflect grab, analyzer now reading 7.23) Fluoride (mg/L): G: 0.68 A: 0.77 Temperature (?C): G: 1.6 A: 1.5 Clearwell Influent Grab/analyzer (10:42): Free Cl (mg/L): G: 1.64 A: 1.71 Collected samples. Completed filter performance review, both filters 100% for the month, no issues. Checked station and equipment, no new issues found while on-site, Ferguson electric contractors on-site for generator upgrades. Entered station readings into shared PD excel file. Topped up PACl day/WW tanks. | Keswick Water Treatment Plant | 2025-12-22
EAST | December | On site to complete station check. Collecting weekly Bac-t Samples. W11439302 Weekly Bac-t Sample. Time: 10:58 Grab (mg/l) Analyzer (mg/l) Free: 1.71 1.64 Total: 1.94 Verified analyzers with grabs. Checked site and trends. While on site informed ROC at 11:05 of work orders being completed. Completing a few work orders as in: Chlorine analyzer maintenance, low temp alarm test, manual valve exercise, JHSC, generator test, house keeping. All alarms from 11:07 to 11:20 and changes in trends are due to work orders being completed. Chlorine analyzer has been verified from grabs completed earlier. No issues with work orders on site. | Sutton Elevated Tank | 2025-12-10
EAST | December | On site to complete station check. Collecting weekly Bac-t Sample. Collecting monthly THM samples. W11420163 Weekly Bac-t Sample. W11420135 THM Samples. Time: 09:40 Grab (mg/l) Analyzer (mg/l) Free: 1.45 1.45 Total: 1.73 Verified analyzer with grabs. Checked site and trends. | Sutton Elevated Tank | 2025-12-03
EAST | December | On site for station check and weekly micro sampling (W11484117) Tower level - 73% and draining at 30 L/s Recorded station readings in PWQ sheets Verified analyzer reading @09:14 Grab free: 1.53 mg/L / Analyzer: 1.48 mg/L Grab total: 1.81 mg/L Collected micro sample @09:17 Reviewed trends Equipment OOS: None Reagents ok Station ok | Sutton Elevated Tank | 2025-12-29
EAST | December | On site to complete station check. Collecting weekly sample. W11470585 Weekly Bac-t Sample. Time: 11:05 Grab (mg/l) Analyzer (mg/l) Free: 1.74 1.73 Total: 1.98 Verified analyzer with grabs all ok. Checked site and trends. No outstanding alarms on site. No OOS equipment. Changed reagents for the free CL-17 analyzer on site at 11:12. | Sutton Elevated Tank | 2025-12-22
EAST | December | On site to complete station check and sampling W11455409 Weekly Bac-t Sample. Time: 09:20 Grab (mg/l) Analyzer (mg/l) Free: 1.99 1.97 Total: 2.46 No outstanding alarms on site. No OOS equipment. | Sutton Elevated Tank | 2025-12-16
EAST | December | On site with Sean Peoples to begin replacement of altitude valve. Disconnected altitude valve solenoid and limit switch at valve. Installed junction boxes to capture wiring. Disconnected and capped conductors in pac panel. | Keswick Deer Park Elevated Tank | 2025-12-03
EAST | December | On site for site meeting with contractor to go over site project and needs. No issues on site. | Keswick Deer Park Elevated Tank | 2025-12-08
EAST | December | On site to collect micro sample and VOC samples. ET is isolated from the system. Outlet header has no water via sample tap. Inlet header has water through sample tap. 17:30 collected VOC samples from inlet. 17:35 collected micro samples from inlet. 17:35 chlorine grab from inlet: FCL = 1.61 mg/l, TCL = 1.95 mg/l.? Inlet analyzer reading at the same time: FC: = 1.58 mg/l, TCL = 1.83 mg/l.? Checked outfall, there is no more water draining through it. The ET remains isolated from the system. | Keswick Deer Park Elevated Tank | 2025-12-02
EAST | December | On site to open inlet valve for contractor so that they can use water for the cleaning of the bowl. At 09:00 cracked inlet valve by a couple turns to allow for water for the contractor to use. No other issues on site. | Keswick Deer Park Elevated Tank | 2025-12-04
EAST | December | On site closing outlet valves to drain and isolate tower. Work was being completed for this task between 09:00 and 09:27. Due to the design of the tower we are draining through the inlet which does not record flow values on SCADA. We are currently draining at 41l/s from the FIT on site. Closing chemical systems at 09:30 in anticipation for ET shut down. Informed ROC of work being completed at 09:33. While on site completing work orders that have been assigned. Time: 09:40 Inlet Grab (mg/l) Analyzer (mg/l) Free: 1.71 1.65 Total: 2.00 2.14-2.00 At 09:43 adjusted the inlet chlorine total reading from 2.14mg/l to 2.00mg/l after multiple grabs were taken. Time: 09:45 Outlet Grab (mg/l) Analyzer (mg/l) Free: 1.50 1.47 Total: 1.98 2.25-1.98 At 09:50 adjusted the outlet total from 2.25mg/l to 1.98mg/l after multiple grabs were taken. Both outlet and inlet chlorine alarms were ack and reset. At 10:52 ET is now isolated from system. At 10:55 started draining tower to waste at 25l/s sodium thiosulphate is being used to neutralize any chlorine residual. Ignore lolo tower alarms for this site due to isolation and drain. Flow was lowered to 18l/s. No other issues during work orders or isolation. | Keswick Deer Park Elevated Tank | 2025-12-02
EAST | December | On site for station check. Site secure contractors working no issues. | Keswick Deer Park Elevated Tank | 2025-12-22
CENTRAL | December | On-site for station check. Tank filling upon arrival. Adjusted manual chlorine dosage factor from 95 to 75%, will continue to monitor. Spoke with East area OP Patrick Forbert to discuss target FCl while draining, Patrick informed me typically target while draining in winter months FCl of 1.5mg/L, and areas can work together to adjust targets at WTPs accordingly to help achieve. Grab/analyzer results as follows at 13:05 (mg/L): Free Cl: G: 1.73 A: 1.63 (adjusted to 1.73mg/L based on average of 3 grabs) Total Cl: G: 2.02 A: 1.92 (adjusted to 2.02mg/L based on average of 3 grabs) No new issues found while on-site. Entered station readings into shared PD excel file. | Keswick West Park Reservoir | 2025-12-12
CENTRAL | December | On-site for station checks. Reviewed trends, adjusted manual chlorine dosage factor from 75 to 65% to target seasonal drain free Cl residual of 1.5mg/L. Will continue to monitor. Tank filling while on-site. Grab/analyzer results as follows (mg/L): Free Cl (12:46): G: 1.45 A: 1.43 Total Cl (12:46): G: 1.75 A: 1.73 Checked station and equipment, no new issues found. | Keswick West Park Reservoir | 2025-12-15
CENTRAL | December | On-site for station check and weekly micro sampling (W11439510) work orders. Grab/analyzer results as follows (mg/L): Free Cl (13:16): G: 1.72 A: 1.88 (adjusted to 1.72mg/L based on average of 3 grabs) Total Cl (13:16): G: 2.00 A: 2.16 (adjusted to 2.00 based on average of 3 grabs) Collected micro sample. Adjusted manual chlorine dosage factor from 105 to 95% for both chlorinators to better target FCl residual of 1.3mg/L, will continue to monitor. Checked station and equipment, outstanding tank level hi alarm as East OPs had d1 stop at 90% while sampling at WTPs occurred, D1 returned to 85% and tank draining, alarm should be able to be cleared soon (current 86%). No other new issues found while on-site. | Keswick West Park Reservoir | 2025-12-10
CENTRAL | December | On-site for station check. Grab/analyzer results as follows (mg/L): Free Cl (14:31): G: 1.79 A: 1.85 Total Cl (14:31): G: 2.13 A: 2.13 Adjusted manual dosage factor for chlorine system from 118% to 105% for both chlorinators to better meet target FCl setpoint of 1.3mg/L, will monitor and adjust further if required. No new issues found while on-site. Entered station readings into shared PD excel file. | Keswick West Park Reservoir | 2025-12-08
CENTRAL | December | On-site for station check. Entered station readings into shared PD excel file. Replaced CL17 analyzer reagents. Grab/analyzer results as follows (mg/L): Free Cl (13:20): G: 1.51 A: 1.45 Total Cl (13:20): G: 1.80 A: 1.77 Checked site and equipment, no new issues found. | Keswick West Park Reservoir | 2025-12-05
CENTRAL | December | Reopened tower inlet mainline valve MV1 @11:02. Tower has resumed draining to distribution system. | Keswick West Park Reservoir | 2025-12-02
CENTRAL | December | Closed main line valve for tower due to isolation and drain of Deer Park ET. This happened at 08:17. | Keswick West Park Reservoir | 2025-12-02
CENTRAL | December | Onsite to complete station check and sampling. VOC - W11420583 MBDW - W11420597 08:25 Reservoir level at 75% and draining at 58 l/s. 08:32 Verified analyzer (mg/l). Collected samples. Free chlorine grab: 1.67. Analyzer: 1.71. Total Chlorine grab: 1.97. Analyzer: 2.01 No issues found. | Keswick West Park Reservoir | 2025-12-03
CENTRAL | December | On site to complete station check. -Verified analyzers: Free Chlorine @ 13:24 Grab: 1.47 mg/L Analyzer: 1.50 mg/L Total Chlorine @ 13:24 Grab: 1.87 mg/L Analyzer: 1.80 mg/L -Entered data into PD sheet -Checked trends | Keswick West Park Reservoir | 2025-12-19
CENTRAL | December | On-site for station check. Entered station readings in shared PD excel file. Grab/analyzer results as follows (mg/L): Free Cl (14:18): G: 1.44 A: 1.43 Total Cl (14:18): G: 1.74 A: 1.74 No new issues found while on-site. | Keswick West Park Reservoir | 2025-12-01
CENTRAL | December | On-site for station check and weekly micro sampling (W11484201) work orders. Grab/analyzer results as follows (mg/L): Free Cl (10:09): G: 1.41 A: 1.36 Total Cl (10:09): G: 1.69 A: 1.67 Chlorinator 1 remains man/off, no new issues found while on-site. Adjusted Chlorine manual dosage factor from 55 to 65%, will monitor, targeting 1.5mg/L FCl while draining. | Keswick West Park Reservoir | 2025-12-29
CENTRAL | December | On-site for station check. Created WO for Instrumentation to investigate chlorinator 1 fail to close alarm. Exercised chlorinator 1 and cleared fail to close alarm but left chlorinator man/off, can be used if needed but alarm is likely to trigger on shutdown until INST can take a look at it. Grab/analyzer results as follows (mg/L): Free Cl (07:36): G: 1.46 A: 1.44 Total Cl (07:36): G: 1.77 A: 1.74 Checked station and equipment, no other new issues found. Entered station readings into shared PD excel file. | Keswick West Park Reservoir | 2025-12-24
CENTRAL | December | On-site for station check and to collect weekly micro sample (W11470835). Grab/analyzer results as follows (mg/L): Free Cl (08:54): G: 1.47 A: 1.49 Total Cl (08:54): G: 1.80 A: 1.79 Entered station readings into shared PD excel file and collected micro sample while tank draining. No new issues found while on-site. | Keswick West Park Reservoir | 2025-12-22
CENTRAL | December | On-site for station check, weekly micro sampling (W11455538) and to investigate chlorinator 1 failed to close alarm. Site draining upon arrival. Exercised chlorinator (cl2 pump not running, not dosing to system) and cleared alarm. Will monitor. Grab/analyzer results as follows (mg/L): Free Cl (13:23): G: 1.66 A: 1.66 Total Cl (13:23): G: 1.99 A: 1.95 Collected samples. Local SCADA OIT experiencing memory issues, notified on-call PCS for correction. No other new issues found while on-site. Adjusted manual chlorine dosage factor from 65 to 55% for both chlorinators, will continue to monitor drain free Cl residual. | Keswick West Park Reservoir | 2025-12-16
CENTRAL | December | Onsite to complete work orders. 08:00 Portable gas generator test run. 08:23 chlorine analyzer maintenance. Placed free and total chlorine readings in calibration mode. Cleaned analyzer. 08:58 verified chlorine Free grab: 1.61. Analyzer 1.61. Total grab: 1.91. Analyzer: 1.96. 09:14 tested chlorine leak detection system. Triggered alarm. Reset with no issues. Tested chlorine dosing system. No issues found Completed Jhsc inspection. No issues found. | Keswick West Park Reservoir | 2025-12-17
EAST | December | On site for station check. Collected weekly micro samples (W11438445). Verification of HACH CL17 Chlorine Analyzer: 10:30hrs: Free CL2 grab residual: 1.13mg/l FCL Analyzer: 1.09mg/l Total Cl2 grab residual: 1.25mg/l Checked station readings and verified Cl2 analyzer. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None | Musselman's Lake Elevated Tank | 2025-12-10
EAST | December | On site for monthly work orders, notified ROC of work being done. Building low temperature alarm test - alarm triggered at 13:12, and was cleared. Heat trace inlet/outlet inspection, Chlorine analyzer maintenance: Completed cleaning and verified with grab sample. Outlet @ 14:11 Grab: 1.06 mg/L. Analyzer: 1.08 mg/L Portable generator test run. JHSC inspections, General housekeeping. | Musselman's Lake Elevated Tank | 2025-12-04
EAST | December | On site for station check. Collected weekly micro samples (W11419085). Verification of HACH CL17 Chlorine Analyzer: 08:55hrs: Free CL2 grab residual: 1.09mg/l FCL Analyzer: 1.10mg/l Total Cl2 grab residual: 1.24mg/l Checked station readings and verified Cl2 analyzer. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None | Musselman's Lake Elevated Tank | 2025-12-03
EAST | December | On site for station check. Collected weekly micro samples (W11469844). Verification of HACH CL17 Chlorine Analyzer: 12:50hrs: Free CL2 grab residual: 1.32mg/l FCL Analyzer: 1.30mg/l Total Cl2 grab residual: 1.50mg/l Checked station readings and verified Cl2 analyzer. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None | Musselman's Lake Elevated Tank | 2025-12-22
EAST | December | On site for station check, and weekly micro sampling (W11483402) Tower level - 91% and draining at 13.2 L/s Recorded station readings in PWQ sheets Verified analyzer reading: Outlet @ 11:18 Free Grab: 1.34 mg/L Analyzer: 1.35 mg/L Total Grab: 1.48 mg/L Adjusted analyzer after three grab residuals. Collected micro and manganese sample @ 11:22 from outlet. Reviewed trends, equipment ok Station ok | Musselman's Lake Elevated Tank | 2025-12-29
EAST | December | On site for station check. Collected weekly micro samples (W11454679). Verification of HACH CL17 Chlorine Analyzers: 08:30hrs: Free CL2 grab residual: 1.24mg/l FCL Analyzer: 1.22mg/l Total Cl2 grab residual: 1.40mg/l Checked station readings and verified Cl2 analyzer. All information in PWQ sheet. Checked site and equipment. Equipment out of service: None. | Musselman's Lake Elevated Tank | 2025-12-16
EAST | December | On site to complete station check. Collecting weekly Bac-t Sample. W11439316 Weekly Bac-t Sample. Header Time: 09:50 Grab (mg/l) Analyzer (mg/l) Free: 1.84 1.88 Total: 2.28 2.29 Inlet Time: 09:52 Grab (mg/l) Analyzer (mg/l) Free: 1.90 1.82 Total: 2.22 2.17 Outlet Time: 09:55 Grab (mg/l) Analyzer (mg/l) Free: 1.70 1.75 Total: 2.02 2.11 Verified analyzers with grabs. Checked site and trends. No OOS equipment. No Outstanding alarms. | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2025-12-10
EAST | December | On site to complete the following work orders: W11417152 Chlorine Gas Detector Test W11417377 Manual Valve Exercise W11417559 JHSC Inspection W11418069 Inlet Outlet Heat Trace System Insp. W11418078 Depolox CL2 Analyzer Maint. W11418319 Ventilation System Insp. W11418369 Actuated Valve Exercise W11417405 Standby Power Generator Test W11418382 Dehumidifier Cleaning/Insp. W11420039 Chemical System Insp. W11418725 Chlorine Scrubber Check W11418459 Drain Valve Exercise W11442491 Housekeeping Completing grabs on analyzers. Calibration has been done on pocket colorimetre. Time: 13:50 Header Grab (mg/l) Analyzer (mg/l) Free: 1.89 1.85 Total: 2.32 2.33 Time: 13:55 Inlet Grab (mg/l) Analyzer (mg/l) Free: 1.90 1.71-1.90 Total: 2.16 2.21 At 13:56 adjusted the inlet free from 1.71mg/l to 1.90mg/l after multiple grabs were taken. Time: 14:02 Outlet Grab (mg/l) Analyzer (mg/l) Free: 1.78 1.61-1.78 Total: 2.07 2.14 At 14:02 adjusted the Outlet free from 1.61mg/l to 1.78mg/l after multiple grabs were taken. Informed ROC of work being done on site. Alarms coming in from 12:00 to 14:00 were because of work orders being completed. Any changes in trends are also due to work orders being completed. | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2025-12-15
EAST | December | At 09:03 started closing ET to 50% to help with the draining and isolation of Deer Park ET. Closed the outlet to 25% at 09:05. Closed valve to 10% at 09:06. Closed valve to 7% at 09:08. Closed valve to 5% at 09:12. | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2025-12-02
EAST | December | On site to complete station check. Collecting weekly Bac-t Samples. Collecting THM Samples. W11420177 Bac-t Samples. W11420149 THM Samples. Header Time: 10:45 Grab (mg/l) Analyzer (mg/l) Free: 1.61 1.57 Total: 1.90 1.95 Inlet Time: 10:49 Grab (mg/l) Analyzer (mg/l) Free: 1.48 1.53 Total: 2.13 2.26-2.13 after multiple grabs were taken adjusted the inlet total from 2.26mg/l to 2.13mg/l at 10:53. Outlet Time: 10:55 Grab (mg/l) Analyzer (mg/l) Free: 1.50 1.56 Total: 1.91 1.97 Verified analyzers with grabs all ok. Checked site and trends. No outstanding alarms. No OOS equipment. | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2025-12-03
EAST | December | On site to complete station check. Collecting weekly Bac-t Sample. W11470599 Weekly Bac-t Sample. Time: 09:30 Header Grab (mg/l) Analyzer (mg/l) Free: 1.59 1.60 Total: 1.96 1.99 Time: 09:32 Inlet Grab (mg/l) Analyzer (mg/l) Free: 1.60 1.58 Total: 2.10 2.10 Time: 09:40 Outlet Grab (mg/l) Analyzer (mg/l) Free: 1.58 1.51 Total: 1.93 1.99 Verified analyzers with grabs all ok. Checked site and trends. No outstanding alarms on site. No OOS equipment. | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2025-12-22
EAST | December | On site for station check and weekly micro sampling (W11484131) Tower level - 79% and draining at 35 L/s Recorded station readings in PWQ sheets Verified chlorine analyzer readings with grab residuals: Inlet: @08:25 Grab free: 1.76 mg/L / Analyzer: 1.75 mg/L Grab total: 2.10 mg/L / Analyzer: 2.06 mg/L Outlet: @08:28 Grab free: 1.56 mg/L / Analyzer: 1.40 mg/L - Adjusted to 1.56 mg/L based on grabs Grab total: 1.88 mg/L / Analyzer: 1.87 mg/L Header: @08:31 Grab free: 1.55 mg/L / Analyzer: 1.70 mg/L Grab total: 1.90 mg/L / Analyzer: 1.88 mg/L Collected micro sample @08:35 from header Reviewed trends, equipment OOS: None Station ok | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2025-12-29
EAST | December | On site to complete station check. W11455423 Weekly Bac-t Sample. Time: 10:00 Header Grab (mg/l) Analyzer (mg/l) Free: 1.61 1.55 Total: 1.92 1.93 Time: 10:02 Inlet Grab (mg/l) Analyzer (mg/l) Free: 1.63 1.55 Total: 2.01 1.99 Time: 10:05 Outlet Grab (mg/l) Analyzer (mg/l) Free: 1.62 1.55 Total: 1.92 1.93 Verified analyzers with grabs all ok. No outstanding alarms on site. Checked site and trends. | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2025-12-16
EAST | December | On site to complete some general work orders. No issues on site. | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2025-12-17
EAST | December | On site for station check. Reviewed scada, Reservoir cells 37% and 37% Visual inspection in and around station Verification of equipment and instrumentation. Outstanding alarms: None Verified chlorine analyzers readings Chlorine residual @ 1158 hrs Effluent: FCL= 0.12 mg/l. TCL = 1.39 mg/l Analyzer: FCL: 0.10 mg/l. TCL: 1.40 mg/l Station OK, recorded station readings in PWQ sheet. BP1~ Duty2 BP2 ~Duty1 BP3 ~ Duty1 | Markham Pumping Station | 2025-12-12
EAST | December | On site for preventative maintenance work orders Completed: Generator test run Flood alarm test Dehumidifier inspection and cleaning JHSC inspection Housekeeping Generator test run Hours Start 583.2 Stop 584.9 Fuel Start 695/696 L Stop 650/646 L Statistics Oil pressure 59 PSI Oil temperature 196 F Coolant temperature 185 F Voltage 600 V Current 199 A Power 177 kW Frequency 60 Hz Speed 1800 RPM Exhaust temperature 672 F Station and equipment okay | Markham Pumping Station | 2025-12-15
EAST | December | Attended site for station check Snowplow attended site to plow the driveway Zero and span calibrated the free chlorine analyzer to match grabs Swept garage Station and equipment okay | Markham Pumping Station | 2025-12-10
EAST | December | On site for station check Reviewed scada, duty active Visual inspection in and around station Verification of equipment and instrumentation. Verified chlorine analyzers readings. Recorded station readings into pwq data sheet | Markham Pumping Station | 2025-12-01
EAST | December | On site for station check Verified analyzers, 11:19, mg/L FCl - G 0.07; A 0.11 TCl - G 1.45; A 1.52 Recorded observations in the shared PWQ sheet Station and equipment okay | Markham Pumping Station | 2025-12-29
EAST | December | On site for station check Verified chlorine analyzers, 12:44, in mg/L Free Cl - G 0.05; A 0.13 Total Cl - G 1.47; A 1.48 Recorded observations in the shared PWQ sheet Station and equipment okay | Markham Pumping Station | 2025-12-16
EAST | December | On site for station check Verified chlorine analyzers, 11:05, mg/L FCl - G 0.07; A 0.17 Adjusted to match average of grabs TCl - G 1.44; A 1.46 Recorded observations in the shared PWQ sheet Station and equipment okay | Markham Pumping Station | 2025-12-22
EAST | December | On site for station check and sampling W11438575 Collected samples while tower draining, 13:05, in mg/L FCl - G 0.13; A 0.04 TCl - G 1.67; A 1.62 Performed nitrification monitoring and recorded SL1000 observations in the shared PWQ sheet Reviewed station trends Station and equipment okay | Markham Milliken Elevated Tank | 2025-12-10
EAST | December | On site for work orders. Called ROC to request for Toronto to place pump in manual off in order to perform actuated valve exercise. Completed valve exercise when Toronto pump stopped, and notified ROC work completed. Completed following work orders: Water high/low level alarm tests - Alarms triggered at 9:54 and 9:55 respectively, then cleared. Building low temperature alarm - alarm triggered at 10:23 and cleared. Sump pit inspection and maintenance, Dehumidifier cleaning and inspection, Heat Trace System inspection, Depolox 5 maintenance - chlorine analyzer screen is blank, no input or output available, power is on, SCADA residuals visible. Notified Dan Z. To make work order for Instrumentation. Grab at 10:41 - Free 0.03 mg/L TCL 1.57 mg/L Health and safety inspections, And general housekeeping. | Markham Milliken Elevated Tank | 2025-12-11
EAST | December | On site for station check and collection of bacT samples. Reviewed scada, trends OK, ET level @ 69%, and filling@ 153 l/s Visual inspection in and around station Verification of equipment and instrumentation. Verified chlorine analyzers readings. Recorded station readings into pwq data sheet Outstanding alarm: none Grabs: Residual: Grab Time (HR). Analyzer FCL. 0.05 mg/l 1433 hrs 0.06 mg/l TCL. 1.53 mg/l 1.55 mg/l Mono. 1.32 mg/l Total Amm. 0.35 mg/l Free Amm. 0.09 mg/l Nitrite 0.000 mg/l Temperature. 6.7 C PH. | Markham Milliken Elevated Tank | 2025-12-03
EAST | December | Informed ROC. Onsite to troubleshoot chlorine analyzer display issue. Switched off the power to analyzer. Replaced the analyzer display. Turned on the power. No issues. Put it back in service. Display readings and SCADA matches. Informed ROC, armed the building and left the site. | Markham Milliken Elevated Tank | 2025-12-23
EAST | December | On site for station check and sampling W11469974 Collected sample and verified analyzers, 11:56, mg/L FCl - G 0.05; A 0.02 TCl - G 1.72; A 1.75 Recorded observations in the shared PWQ sheet Reviewed SCADA Checked station and equipment All okay | Markham Milliken Elevated Tank | 2025-12-22
EAST | December | On site for station check and sampling W11483524 Collected sample while draining and verified chlorine analyzers, 12:00, mg/L FCl - G 0.07; A 0.04 TCl - G 1.68; A 1.73 Recorded observations in the shared PWQ sheet Reviewed station trends Deplox analyzer control screen okay since Instrumentation service Station and equipment okay | Markham Milliken Elevated Tank | 2025-12-29
EAST | December | On site for station check and BacT sampling, W11454801 Collected samples and verified analyzers, 14:00, in mg/L FCl - G 0.03; A 0.03 TCl - G 1.60; A 1.73 Recorded observations in the shared PWQ sheet Deplox analyzer LED screen is dead - created W11519938 for instrumentation | Markham Milliken Elevated Tank | 2025-12-16
EAST | December | On site for station check and sampling W11438575 Collected samples from West cell while draining, 10:30, in mg/L FCl - G 0.02; A 0.05 TCl - G 1.25; A 1.42 Adjusted analyzer to match average of grabs West cell is out of service for capital project Collected nitrification monitoring samples and recorded SL1000 grab sample results in the shared PWQ sheet Station and equipment okay, contractor on site | Markham PD5 Reservoir | 2025-12-10
EAST | December | On site for station check and bacT sample collection Reviewed scada, trends OK Visual inspection in and around station Verification of equipment and instrumentation Verified chlorine analyzers readings. Recorded station readings into pwq data sheet Outstanding alarm: Grabs: Residual: Cell #1(West). Cell #2 (East). Time (HR) Analyzer FCL. 0.08 mg/l OOS 1220 0.07 mg/l TCL. 1.31 mg/l 1.36 mg/l Mono. 0.99 mg/l Total Amm. 0.28 mg/l Free Amm. 0.09 mg/l Nitrite 0.00 mg/l Temperature. 8.3 C pH. 7.99 Res level. 47% Collected samples from west cell East cell OOS Recorded station readings into pwq data sheet No issues | Markham PD5 Reservoir | 2025-12-03
EAST | December | On site for work orders, Notified ROC. Hi/low water level alarm tests - adjusted alarm set points for res 1, received alarms at 13:29 and 13:32, and reverted changes. Chlorine analyzer maintenance: @ 14:05 Grab West Cell Free: 0.08 mg/L Analyzer: 0.08 mg/L Total: 1.35 mg/L Analyzer: 1.38 mg/L General housekeeping, JHSC inspections, And external venting screen inspections. | Markham PD5 Reservoir | 2025-12-18
EAST | December | On site for station check and BacT sampling W11454801 Collected samples from West cell while draining, 10:50, East cell OOS for rehab Verified West cell chlorine analyzers, 10:50, in mg/L Free Cl - G 0.05; A 0.08 Total Cl - G 1.35; A 1.36 Recorded observations in the shared PWQ, nitrification monitoring results recorded Very strong organic vapor odour detected in the valve house, inquired with Team Lead who contacted the Contractor/ Site Superintendent | Markham PD5 Reservoir | 2025-12-16
EAST | December | On site for station check and sampling W11469974 Collected sample from west cell and verified analyzers, 10:25, mg/L Free Cl - G 0.06; A 0.06 Total Cl - G 1.36; A 1.36 East cell offline Recorded observations in the shared PWQ sheet Station and equipment okay | Markham PD5 Reservoir | 2025-12-22
EAST | December | On site for station check and sampling W11483524 Collected sample from West cell while draining and verified chlorine analyzers, 10:40, in mg/L FCl - G 0.06; A 0.06 TCl - G 1.32; A 1.39 East cell is out of service for rehabilitation Attended STW12 to validate ekey - was unable to open station door Recorded observations in the shared PWQ sheet Station is in contractor custody, Brook is on site Station and equipment okay | Markham PD5 Reservoir | 2025-12-29
EAST | December | Under direction of OIC (Dan Zhou) On site for; - Chlorine analyzer Maintenance and cleaning (influent and Effluent AIT) - Turbidity analyzer maintenance/cleaning/calibration - Chemical system inspection (chlorine) @ 09:51 place well pump 3 in manual off for PM?s Started chlorine analyzer maintenance on AIT 1 and 2 Start Clean @ 09:52 hrs. Exited Clean @ 10:53 hrs. Effluent (Treated Water) AIT verification Grab @ 11:08 hrs. FCl: 2.44 mg/L Analyzer FCl: 2.51 mg/L Influent AIT verification Grab @ 11:10 hrs. FCl: 2.52 mg/L Analyzer FCl: 2.59 mg/L Y screen and tubing for influent line compromised, red from instrumentation replaced line with 1/4 inch tubing and fittings. Exited Clean @ 10:53 hrs. Turbidity meter clean and calibration; Start @ 10:54 hrs. Stop @ 11:03 hrs. @ 11: 16 hrs. Returned well pump 3 to auto (well pump 3 active) - tower mode During chlorine chemical system inspection noticed GC 2 and GC 1 position indicator trending upward. Instrumentation already on-site to rebuild chlorinators. Equipment OOS: None | Stouffville Well 3 | 2025-12-11
EAST | December | On site for station check and weekly micro sampling (W11438547) Duty active, tower level 84%. Verified analyzer readings with grab residuals. Influent @ 10:42 Free Grab: 2.72 mg/L Analyzer: 2.64 mg/L Effluent @ at 10:46 Free Grab: 2.56 mg/L Analyzer: 2.51 mg/L Total Grab: 2.84 mg/L Took treated sample at 10:50. Visual inspection of chemical systems - all ok. Entered station readings in PWQ sheet. Reviewed trends, equipment ok. Station ok | Stouffville Well 3 | 2025-12-10
EAST | December | Onsite to perform annual chlorinator rebuild. Due to conflict with contractors onsite unable to perform work. Will reschedule for next week. Armed the building and left the site. | Stouffville Well 3 | 2025-12-11
EAST | December | Under direction of OIC (Dan Zhou) On-site for; - station checks - Silicate system inspection Data in PWQ excel Workbook Influent Water Grab @ 08:47 hrs. FCl: 2.64 mg/L Analyzer FCl: 2.70 mg/L Effluent (Treated Water) Grab @ 08:47 hrs. FCl: 2.52 mg/L TCL: 2.74 mg/L Analyzer: FCl: 2.56 mg/L Equipment OOS: None Facility?s OK | Stouffville Well 3 | 2025-12-12
EAST | December | Man/start well3 since Zone 1 is filling. | Stouffville Well 3 | 2025-12-15
EAST | December | Under direction of OIC (Dan Zhou) @ 09:41 placed well pump 3 in auto | Stouffville Well 3 | 2025-12-04
EAST | December | Under direction of OIC (Dan Zhou) On-site for; - station checks - Regulatory Sampling (W11419179) Data in PWQ excel Workbook Regulatory samples taken @ 12:12 Influent Water Grab @ 12:12 hrs. FCl: 2.86 mg/L Analyzer FCl: 2.77 mg/L Effluent (Treated Water) Grab @ 12:12 hrs. FCl: 2.74 mg/L TCL: 3.28 mg/L Analyzer: FCl: 2.75 mg/L Equipment OOS: None Facility?s OK | Stouffville Well 3 | 2025-12-03
EAST | December | On site for silicate top up. | Stouffville Well 3 | 2025-12-09
EAST | December | On site for station check with Dan Z. Duty active, tower level 72%. Changed chlorine cylinder on right bank. Verified analyzer readings with grab residuals. Influent @ 11:54 Free Grab: 2.84 mg/L Analyzer: 2.74 mg/L Adjusted analyzer after three grab samples Effluent @ at 11:54 Free Grab: 2.70 mg/L Analyzer: 2.72 mg/L Total Grab: 3.10 mg/L Visual inspection of chemical systems - all ok. Entered station readings in PWQ sheet. Turbidity high - manual shut down well and clean turbidity vial. Place well back in auto afterwards. Reviewed SCADA trends, station ok. Adjusted station flow from 21L/s to 24L/s, chlorinator 1 running at 8 ppd. | Stouffville Well 3 | 2025-12-08
EAST | December | Received 8 full chlorine cylinders, removed 8 empty chlorine cylinders. | Stouffville Well 3 | 2025-12-08
EAST | December | On site to complete station check. Well is currently active in manual. Time: 11:10 Influent Grab (mg/l) Analyzer (mg/l) Free: 2.70 2.78 Time: 11:15 Effluent Grab (mg/l) Analyzer (mg/l) Free: 2.78. 2.76 Total: 2.90 Checked site and trends. Verified analyzers with grabs. No outstanding alarms. No OOS equipment. | Stouffville Well 3 | 2025-12-01
EAST | December | On site for station check and collection of weekly bacT samples Reviewed scada, duty not active ET at 88% Visual inspection in and around station, no issues Verification of equipment, analyzers and instrumentation Chlorine residual Grabs @: 0829 hrs Influent FCL = 2.80 mg/l. Analyzer = 2.77 mg/l Effluent FCL = 2.70 mg/l. Analyzer = 2.66 mg/l TCL = 3.02 mg/l Chemicals: Cl2 System Duty1: pump1 Disch. Press: 750 kpa Pump2 on standby Silicate System: Duty1: Pump2 Pumps speed: 69% Dosage: 69.70mL/min Disch. Pressure: 500 kpa Pump1 on standby System pressure: 328 kpa Recorded station readings into pwq data sheet - Did a chlorine cylinder change turn Danielle on site. - Cleaned turbidity analyzer and replaced vial No issues | Stouffville Well 3 | 2025-12-29
EAST | December | Grease motor bottom bearing | Stouffville Well 3 | 2025-12-18
EAST | December | Man/Start well 3 to assist Zone 1 filling. | Stouffville Well 3 | 2025-12-17
EAST | December | Worked with Joe Mazza ON site to change chlorine cylinder from bank 1 (left side) | Stouffville Well 3 | 2025-12-16
EAST | December | Man/Start well 3 to aid zone 1 filling. | Stouffville Well 3 | 2025-12-26
EAST | December | Remotely put well pump 3 in manual off at 11:06 hrs. For generator load test @ STPSTL @ 11:37 put well pump 3 in manual on for ATS @ 12:10 put well pump 3 in manual off for ATS @ 12:27 put well pump 3 in Auto (duty active, pump active) | Stouffville Well 3 | 2025-12-16
EAST | December | Under direction of OIC (Dan Zhou) On-site for; - station checks Data in PWQ excel Workbook Influent Water Grab @ 11:31 hrs. FCl: 2.66 mg/L Analyzer FCl: 2.73 mg/L Effluent (Treated Water) Grab @ 11:31 hrs. FCl: 2.72 mg/L TCL: 3.06 mg/L Analyzer: FCl: 2.62 mg/L Equipment OOS: None Facility?s OK | Stouffville Well 3 | 2025-12-18
EAST | December | On site to complete chlorination swap out on chlorine system 1. Putting well in manual at 09:46 and stopping well. At 09:30 informed ROC of work to be done. At 09:47 running booster pump 1 in local to purge system. At 10:00 ran booster pump in local to test chlorine system. System is working normally no leaks were detected. Weigh scale is now reading 68/13kg. At 10:05 ack and reset alarms on site. Put well back to auto at 10:06 and activated it. After seeing the system activate no issues to record. All health and safety measures were used during this work. | Stouffville Well 3 | 2025-12-23
EAST | December | Informed ROC. Onsite to perform annual maintenance on Chlorinators. Dan placed pump duty in manual mode. We isolated gas cylinders and purged the lines. We rebuilt chlorinators #1. Chlorinator# 2 rotameter glass cracked and placed out of service currently. Informed Dan Zhou about it. performed vacuum test. leak found. Performed further troubleshooting and found left side of vaccum regulator leaking. Informed Dan Zhou about it and bypassed it until it gets replaced. Booster pump#2 currently off. Performed leak test again on right side of vaccum regulator only. No leak found. Vaccum holding. Put the right side of gas cylinder in service connected directly to chlorinator#1. Performed gas calibration on chlorinator #1 and Performed verification and Put it back in service. No issues. Dan backflushed the lines. Informed ROC and left the site. | Stouffville Well 3 | 2025-12-22
EAST | December | Under direction of OIC (Dan Zhou) On-site for; - station checks - Regulatory sampling, Micro (W11454773) - Operational sampling, iron, temp, turbidity Data in PWQ excel Workbook Influent Water Grab @ 09:02 hrs. FCl: 2.68 mg/L Analyzer FCl: 2.67 mg/L Effluent (Treated Water) Grab @ 09:02 hrs. FCl: 2.80 mg/L TCL: 3.04 mg/L Analyzer: FCl: 2.78 mg/L Equipment OOS: None Facility?s OK | Stouffville Well 3 | 2025-12-16
EAST | December | On?site to check station and equipment. Instrumentation are on site to calibrate the chlorinators. After their work, backflushed the well for about 5 minutes. Man/Start well 3. 14:25 collected well 3 raw, YD # W11469946. 14:26 collected well 3 treated sample. 14:26 effluent free grab = 2.64 mg/l, total = 2.76 mg/l. Effluent analyzer free = 2.63 mg/l. 14:30 Influent free grab = 2.90 mg/l, influent analyzer free = 2.99 mg/l. Station readings are in PWQ sheet.? Chlorine residual high and turbidity high is outstanding due to well start-up. They are trending downwards. Reviewed trends, station is under normal operation. Equipment OOS: Chlorinator 2 and chlorine booster #2. Chlorine regulator on left side. Left side of chlorine cylinder is full, however, it is Teared to 0 kg due to leaky regulator. It is isolated from the system.? | Stouffville Well 3 | 2025-12-22
EAST | December | Man/start wells 1 and 2 since Zone 1 is filling. | Stouffville Well 1 & 2 | 2025-12-15
EAST | December | Under direction of OIC (Dan Zhou) On-site for; - Station checks Data in PWQ excel Workbook Influent Water Grab @ 10:45 hrs. Grab FCl: 3.66 mg/L Analyzer FCl: 3.67 mg/L Treated Water (Effluent) Grabs @ 10:45 hrs. Grabs FCl: 2.22 mg/L TCl: 2.86 mg/L Analyzer FCl: 2.27 mg/L Equipment OOS: None Facility OK | Stouffville Well 1 & 2 | 2025-12-12
EAST | December | Placed well 1&2 man/on for Heather (IAM)? testing of strap on flow meter. At 15:03 Activated Zone 2 duty. Zone 2 ET = 65%. | Stouffville Well 1 & 2 | 2025-12-10
EAST | December | ON site to repair bulk tank fill cap. | Stouffville Well 1 & 2 | 2025-12-12
EAST | December | On site for station check and weekly micro sampling (W11438547) Duty active, tower level 79%. Well 1 running 22.8 L/s and well 2 running 22.6 L/s. Verified analyzer readings with grab residuals. Influent @ 9:30 Free Grab: 3.62 mg/L Analyzer: 3.66 mg/L Effluent @ at 9:40 Free Grab: 2.26 mg/L Analyzer: 2.30 mg/L Total Grab: 2.90 mg/L Took treated sample at 9:45. Visual inspection of chemical systems - all ok. Entered station readings in PWQ sheet. Reviewed trends, equipment ok. Station ok | Stouffville Well 1 & 2 | 2025-12-10
EAST | December | On site to open up discharge valve for well 1 since rehab is being pushed off. Also switching well from local back to auto so it can run in duty. | Stouffville Well 1 & 2 | 2025-12-03
EAST | December | -on site to disconnect well 1. 0900 locked out Vfd and disconnected motor and well level probe. Left electrical team lock and tag on Vfd till work is complete.under direction of oic. | Stouffville Well 1 & 2 | 2025-12-01
EAST | December | On site to check station and equipment. Duty is active upon arrival. Chlorine grabs and station readings are entered in PWQ sheet. Run silicate pump 2 into cal column. Switched silicate P2 into duty 1. Will monitor its performance remotely.? Reviewed trends, no issues.? | Stouffville Well 1 & 2 | 2025-12-08
EAST | December | Lowered silicate dose from 18 mg/l to 15 mg/l. Increased well flow set point from 21 l/s to 23 l/s. | Stouffville Well 1 & 2 | 2025-12-09
EAST | December | Under direction of OIC (Dan Zhou) On-site for; - Station checks - Regulatory Sampling, micro, (W11419179) Data in PWQ excel Workbook @ 08:20 put well 1 in manual ON Turbidity spike due to partial airlock on silicate pump 2. Released prv attempt releasing air lock (failed), toggled pump pressure from 425 psi to 475 psi and pump resumed proper action, turbidity dropped to normal levels. @ 08:51 ROC called after putting well pump 2 in auto on. I turned well pump 2 off to have single operation of well 1 on for sampling. @ 09:30 took regulatory samples for well 1 raw and treated @ 09:44 manually shut off well pump 1 @ 09:57 manually started well pump 2. @ 10:22 hrs. regulatory sample for well 2 raw taken @ 10:24 hrs. Returned well pumps 1 and 2 in auto. Well pumps remain off due to deep cycle on zone 1 tower. Influent Water Grab @ 09:30 hrs. Grab FCl: 3.70 mg/L Analyzer FCl: 3.73 mg/L Treated Water (Effluent) Grabs @ 09:30 hrs. Grabs FCl: 2.54 mg/L TCl: 3.98 mg/L Analyzer FCl: 2.55 mg/L Equipment OOS: None Facility OK | Stouffville Well 1 & 2 | 2025-12-03
EAST | December | Placed both well 1 and 2 in duty 1. Changed flow setpoint for each well from 27 l/s to 21 l/s. | Stouffville Well 1 & 2 | 2025-12-08
EAST | December | On site with Tyler Zimmerman-Jones to reconnect Well #1 pump motor. Motor reconnected and vfd energized. Correct motor rotation verified. Motor controls placed in local. | Stouffville Well 1 & 2 | 2025-12-02
EAST | December | On site to complete station check. Isolating well 1 from the system, so that it can start its rehab process. Informed ROC of work to be complete and any alarms that will be created. Electricians shut down main power to well 1 at 09:00. At 09:04 closed butterfly valve on the discharge side of the well to isolate it from the system. At 09:17 placed well 1 in local. Time: 09:52 Influent Grab (mg/l) Analyzer (mg/l) Free: 4.40 4.73 Time: 09:55 Effluent Grab (mg/l) Analyzer (mg/l) Free: 2.05 2.10 Total: 2.44 Receiving hypo on site Start: 83.9cm/82.9cm 552L/546L Stop: 176.7cm/175.6cm 1161L/1155L Created work order for leak found on hypo tank 1 around the welded section. Checked trends and site. | Stouffville Well 1 & 2 | 2025-12-01
EAST | December | On site to receive hypo delivery: 1400L. | Stouffville Well 1 & 2 | 2025-12-09
EAST | December | On site for silicate tank top up from 29.53cm to 102cm. | Stouffville Well 1 & 2 | 2025-12-09
EAST | December | Onsite to respond to pump hi discharge pressure shut down. ROC rotated duties when lead pump shut down on hi pressure and pump 2 shut down as well. System duty was active and controlling tower level was @ 47% and still draining. Directed ROC to deactivate zone1 duty which was at 61%, to allow zone2 tower to recover. Until wells 1/2 shutdown issue can be investigated. Upon arrival found the distribution isolation valve closed. Opened isolation valve. Also found leak from injector lance 2 when header was pressurized. Closed isolation valve again removed injection lance2 replaced check valve, tested in manual no issues. Place hypo p2 in lead duty, open isolation valve and returned both pumps to auto. Pump1 in lead duty started with no issues. Observed system operation for few minutes, AOK. Notified ROC before leaving site. | Stouffville Well 1 & 2 | 2025-12-04
EAST | December | Under direction of OIC (Dan Zhou) On site for: - Sodium Silicate system inspection and maintenance, injection quill cleaning and hot water flush - Chlorine analyzer Maintenance and cleaning (influent and Effluent AIT) - Turbidity analyzer maintenance/cleaning/calibration - Chemical system inspection and maintenance (chlorine) - Bore Hole inspection - JHSC Health and Safety Checks - Generator Test Run - Sodium Hypochlorite Receiving @ 09:41called ROC to inform them of PM?s on site @ 09:41 hrs. Put Wells 1 and 2 in manual off for PM?s, deactivated zone 1 tower duty at Zone 1 PS, placed Stouffville well 3 in auto Started chlorine analyzer maintenance on AIT 1 and 2 Start Clean @ 09:49 hrs. Exited Clean @ 10:11 hrs. Effluent (Treated Water) AIT verification Grab @ 10:45 hrs. FCl: 1.66 mg/L Analyzer FCl: 1.67 mg/L Influent AIT verification Grab @ 09:43 hrs. FCl: 2.06 mg/L Analyzer FCl: 2.08 mg/L Turbidity Analyzer Maintenance and clean: Clean start @ 10:33 hrs. Exited Clean @ 10:46 hrs. Generator Test Run: Start Fuel: 1034 L Stop Fuel: 1019 L Start Hours: 658.5 Stop Hours: Start Time: 12:51 hrs. Pre run checks; Battery Cell Levels: Ok Battery Terminals and Cables: Ok Oil Level: Ok Coolant Level: Ok Fluid Leaks: NO Coolant Recirculating pump: Ok Faulty Gauges: NO @ 12:59 hrs. Switched ATS to Test for generator power @ 13:11 hrs. Placed generator under facility load Well pump 2 in Manual ON Start Fuel: 1017 L Stop Fuel: 997 L Start Hours: 658.5 Stop Hours: 650.1 Start Time: 13:11 hrs. *under load* Operating Current: 58 Amps Operating Frequency: 60 Hz Operating Voltage: 570 Volts Engine speed: 1750 RPM Water/coolant Temp: 148 f Oil Pressure: 25 psi Oil Temperature: 175 f @ 14:10 Toggled ATS off test to normal @ 14:25 power switched to station power @ 14:26 put well pump @ 13:20 hypo pump 2 fault alarm, tested pump at calibration column and pump fills to column, pulled injection quill, quill is clear and check valve works. May be a blockage mid line. Further investigation next day on chemical board. Hypo pump 2 in local. Equipment OOS: Hypo Pump 2 (in local) Facility OK | Stouffville Well 1 & 2 | 2025-12-04
EAST | December | Under direction of OIC (Dan Zhou) On-site for; - Station checks - Regulatory sampling (W11454773) - Operational sampling; iron, temp, turbidity Data in PWQ excel Workbook Well pumps 1 and 2 ON Influent Water Grab @ 10:02 hrs. Grab FCl: 3.70 mg/L Analyzer FCl: 3.74 mg/L Treated Water (Effluent) Grabs @ 10:02 hrs. Grabs FCl: 2.36 mg/L TCl: 3.76 mg/L Analyzer FCl: 2.33 mg/L Equipment OOS: None Facility OK | Stouffville Well 1 & 2 | 2025-12-16
EAST | December | Under direction of OIC (Dan Zhou) On-site for; - Station checks Data in PWQ excel Workbook Well pumps 1 and 2 ON Influent Water Grab @ 10:46 hrs. Grab FCl: 3.80 mg/L Analyzer FCl: 3.75 mg/L Treated Water (Effluent) Grabs @ 10:46 hrs. Grabs FCl: 2.37 mg/L TCl: 3.02 mg/L Analyzer FCl: 2.32 mg/L Changed buffer and analyzer reagents for AIT 1 and 2. Equipment OOS: None Facility OK | Stouffville Well 1 & 2 | 2025-12-18
EAST | December | Received Hypo delivery: Start level 0.82 m Stop level 1.45 m | Stouffville Well 1 & 2 | 2025-12-17
EAST | December | Received Sodium hypo delivery - approx 1000L Start: 52.9 / 52.1 cm (349/342L) Stop: 131.3 / 130.5 cm (863/859L) | Stouffville Well 1 & 2 | 2025-12-23
EAST | December | Grease bottom motor bearing | Stouffville Well 1 & 2 | 2025-12-18
EAST | December | Manual start well 1 and 2 to assist zone 1 filling. | Stouffville Well 1 & 2 | 2025-12-17
EAST | December | Man/off well 1 due to hypo volume. Well 2 is in duty 1. Requested ROC to leave STW12 out of Zone 1 filling interim memo. | Stouffville Well 1 & 2 | 2025-12-26
EAST | December | On site to check station and equipment. Well duty is active upon arrival. 10:56 Collected well 1 and 2 raw Bac T sample, YD# W11469946. 11:03 grab chlorine residual from treated tap: FC: = 2.20 mg/l, TCL = 2.88 mg/l. Effluent Analyzer free = 2.25 mg/l. 11:03 Collected Treated Bac-T sample, YD W11469946. 11:05 Grab influent free = 3.62 mg/l, analyzer free = 3.65 mg/l.? Station readings are in PWQ sheet.? Reviewed trends, station is under normal operation. No outstanding alarms. | Stouffville Well 1 & 2 | 2025-12-22
EAST | December | Outstanding Turbidity fault alarm on site. Noticed no flow to analyzer. Noticed buildup in sediment in orange flow control valve feeding analyzer, was able to flush it out and this solved the flow issue. Reset fault alarm on Scada and placed well back in duty. On site for station check. Collected weekly micro samples (W11438445). Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 2.06mg/l FCL Analyzer: 2.09mg/l 09:18hrs: Effluent Free Cl2 grab residual: 1.69mg/l FCL Analyzer: 1.71mg/l Effluent Total Cl2 grab residual: 1.86mg/l Collected Well 1 Raw sample @ 09:18hrs. Collected Well 2 Raw sample @ 09:35hrs. Changed Well Duties: W2 to D1, W1 to D2. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Site currently undergoing Construction upgrades by Torbear. Equipment out of service: None. | Ballantrae Well 1 & 2 | 2025-12-10
EAST | December | On site for station check and collection of weekly bacT samples Reviewed scada, duty not active ET at 84% Visual inspection in and around station, no issues Verification of equipment, analyzers and instrumentation Chlorine residual Grabs @:0958 hrs Influent FCL = 3.74mg/l. Analyzer = 3.79 mg/l Effluent FCL = 2.12mg/l. Analyzer = 2.13 mg/l TCL = 3.52 mg/l Chemicals: Hypo System Duty1: pump2 Pumps speed :13% Dosage: 80.25 mL/min Disch. Press: 460 kpa Pump1 on standby Silicate System: Duty1: Pump1 Pumps speed: 39% Dosage: 38.49mL/min Disch. Pressure: 460 kpa Pump2 on standby System pressure: 407 kpa 1020 hrs: started well 1 pump in manual for raw water bacT sample collection. Shut well 2 pump down in manual Recorded station readings into pwq data sheet No issues | Stouffville Well 1 & 2 | 2025-12-29
EAST | December | On site for station check. Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 1.95mg/l FCL Analyzer: 1.98mg/l Effluent Free Cl2 grab residual: 1.93mg/l FCL Analyzer: 1.95mg/l Effluent Total Cl2 grab residual: 2.18mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Site currently undergoing Construction upgrades by Torbear. Equipment out of service: None. | Ballantrae Well 1 & 2 | 2025-12-12
EAST | December | Removal of Hypo equipment as part of an ongoing CPD Project. 6.1.1 Rack 0, Slot 10, Point 3, HYPO_TK1_LIT1_AI ? Hypo Tank 1 Level Indication 6.1.2 Rack 0, Slot 11, Point 3, HYPO_TK2_LIT1_AI ? Hypo Tank 2 Level Indication 6.1.3 Rack 1, Slot 1, Point 11, HYPO_TK1_LIT1_FLT_DI Hypo Tank 1 Loss of Echo 6.1.4 Rack 1, Slot 1, Point 12, HYPO_TK2_LIT1_FLT_DI Hypo Tank 2 Loss of Echo 6.2 Eyewash/shower flow switch 6.2.1 Rack 0, Slot 4, Point 12, HS_EYEW1_STAT_DI Eyewash Status 6.3 Containment float 6.3.1 Rack 1, Slot 2, Point 11, HYPO_LSHH1_DI Hypo Tank Containment Flood Float | Ballantrae Well 1 & 2 | 2025-12-15
EAST | December | On site to remove hypo from bulk tank and into carboy jugs. | Ballantrae Well 1 & 2 | 2025-12-11
EAST | December | Placed both well 1 and 2 in duty 1 to test new chlorine contact tanks and pipings. Lowered the flow setpoint from 30 to 25 l/s. Activate duty, tower level = 81%. Increased flow to 30 l/s for each well. As of 10:48, discharge pressure = 770 kpa, tower level = 89%. | Ballantrae Well 1 & 2 | 2025-12-11
EAST | December | Changed hypo day tank low level alarm from 30 cm to 40 cm. | Ballantrae Well 1 & 2 | 2025-12-15
EAST | December | On site for new Contact Tank 1 and 2 Tie in to the station being conducted by Torbear. This will involve disconnecting and decommissioning of the old Contact tank. This will be a 48 hours shutdown in order to complete. Work also includes electrical work within the station which requires trying off main power to the station. Stand by Generator will be placed in local off during this time. 07:00hrs: In preparation of the new Contact Tank tie in work today, Wells 1 and 2 were placed into manual off and locked out and Tagged out at MCC. ROC informed of all work. Also locked out and tagged out discharge valve leaving the station in the Hypo/Silicate room. Closed new yard valve on Post discharge side of Contact tanks to depressurize all pipes leading into the station. 07:30hrs: Turned off both HACH CL17 Chlorine Analyzers as the pipes/contact tank to be depressurized. Monitored disconnection of existing contact tank and tie in of well facility to upstream side of new contact tanks. Contractors were unable to complete tie in today, will be completed tomorrow between facility and Contact tanks. | Ballantrae Well 1 & 2 | 2025-12-03
EAST | December | On site to assist in commissioning of new Contact Tank 1 and Contact Tank 2. 10:00hrs: Assisted in providing pressure test for new Tie in from new Contact Tanks to distribution system (Tie in #2) by opening main distribution valve and pressurizing new tie in to VC2. Pressure test successful. Next step will be to backflush new contact tanks after contractor has finished backfilling Tie in #2 and finishing tying in new effluent and influent lines from new contact tanks. | Ballantrae Well 1 & 2 | 2025-12-06
EAST | December | 09:05hrs: Outstanding Turbidity Fault alarm on site. Noticed no flow to Analyzer. Had to adjust flow at the effluent line to restore flow to the Analyzer. Reset fault alarm. On site for station check. Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 1.73mg/l FCL Analyzer: 1.76mg/l Effluent Free Cl2 grab residual: 2.18mg/l FCL Analyzer: 2.27mg/l Effluent Total Cl2 grab residual: 2.38mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Site currently undergoing Construction upgrades by Torbear. Equipment out of service: None. | Ballantrae Well 1 & 2 | 2025-12-08
EAST | December | On site for station check and to collect weekly micro samples (W11471393) as this facility will be offline tomorrow for Facility Construction upgrades. Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 1.95mg/l FCL Analyzer: 2.04mg/l 08:17hrs: Effluent Free Cl2 grab residual: 1.72mg/l FCL Analyzer: 1.73mg/l Effluent Total Cl2 grab residual: 1.97mg/l Collected Well 1 Raw sample @ 08:40hrs. Collected Well 2 Raw sample @ 08:17hrs. Changed Well Duties: W2 to D2, W1 to D1. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Site currently undergoing Construction upgrades by Torbear. Equipment out of service: None. Conducted Monthly maintenance on site: Conducted Generator Test Run (08:50hrs): Diesel Generator Run Monthly Test: Start Runtime: 08:50hrs (Run hrs: 1006.3) Fuel Start: 81.7cm/808L Stop Runtime: 09:50hrs (Run hrs: 1007.5) Fuel Stop: 80.1cm/791L Generator Performance Data recorded below: Battery Cell Levels: OK Battery Terminals/Cables: Ok Oil and Coolant: Ok Amps: 75 Volts: 600 Hertz: 60 RPM: 1550 Oil Pressure: 55 Water temp: 160 No issues during generator run test. Ran Well 1 in auto during run test. 09:45hrs: HACH CL17 Influent and Effluent Analyzer cleaning. Verified Analyzer after cleaning: Influent: 1.91mg/l, Analyzer: 1.92mg/l Effluent: 1.71mg/l, Analyzer: 1.69mg/l 10:25hrs:Turbidimeter maintenance and calibration completed Conducted Silicate and Hypo Chemical system inspection including injection point inspection and cleaning. Housekeeping on site. Construction activities occurring on site. Contact Tank and Valve chamber upgrades including electrical upgrades within the facility. | Ballantrae Well 1 & 2 | 2025-12-02
EAST | December | On site for station check. Collected in house iron samples. Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 1.85mg/l FCL Analyzer: 1.93mg/l Effluent Free Cl2 grab residual: 1.65mg/l FCL Analyzer: 1.69mg/l Effluent Total Cl2 grab residual: 1.94mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Site currently undergoing Construction upgrades by Torbear. Equipment out of service: None. | Ballantrae Well 1 & 2 | 2025-12-01
EAST | December | On site to assist in opening distribution valve to pressure test tie in #2 which ties in new Contact tanks 1 and 2 to the distribution. Wells still locked out and off. Brought distribution water back to test tie in. Pressure test passed @ 10:10hrs. Drained tie in pipe after pressure test passed through VC 2 drain valve to allow contractors to finish backfilling and tying in water service line. 14:10hrs: Contractor completed backfilling of tie in #2. Work has been completed and station and CT contact tanks will be pressurized and back flushed and well to be put back online this afternoon. 14:20hrs: Called ROC to activate duty in Ballantrae. 14:25hrs: Opened all valves in yard for both contact tanks now that tie in # 2 is complete. Pressure testing complete. 14:30hrs: Began Back flushing both contact tanks through Well 2 back flush valve bringing back distribution water. Estimated flow rate of 12l/s. Placed sodium thiosulfate pucks in soak away chamber to dechlorinate. 14:50hrs: Opened and Flushed influent and effluent lines and service line. 15:15hrs: Turned on Influent and effluent CL2 Analyzers. 15:18hrs: Removed lock and tags on Well 1 and 2 and energized both wells. Enabled Contact 2 in service on SCADA. Wells still off at this time. Monitored Cl2 influent and effluent, and turbidity values while back flushing. Current values @ 15:50hrs is Influent: 1.54mg/l, Effluent: 1.22mg/l and Turbidity: 0.483ntu. Verified Influent and effluent CL2 Analyzers: Influent CL2 grab residual: 1.53mg/l, Analyzer: 1.50mg/l, Effluent Cl2 grab residual: 1.23mg/l, Analyzers: 1.23mg/l. 16:01hrs: Called on call PCS Chris Scott to log in and ensure new CT Tank SCADA information is up to date and working correctly while running well into system. Conducted manual CT calculation as well to ensure contact time is met when starting up well. Looking for minimum free residual of 0.12mg/l based on 30L/s. Effective contact time = 82.4m3 contact tank volume x 0.7 baffle factor x 1000 divided by 30L/S flow rate x 60s = 32.04min Minimum free residual required = 4.00mg/L/min divided by 32.04min = 0.12mg/L 16:10hrs: Completed back flushing. 16:15hrs: Placed Well 2 into manual on. Monitored start up and Cl2 and turbidity. Collected micro samples (W11475764). 17:25hrs: Effluent Free Cl2 grab residual: 1.63mg/l FCL Analyzer: 1.65mg/l Effluent Total Cl2 grab residual: 1.82mg/l Collected Well 2 Raw sample @ 17:25hrs: Collected Well 1 Raw sample @ 18:05hrs Samples to be dropped off at YD lab. Well 1 in auto, duty 1. | Ballantrae Well 1 & 2 | 2025-12-06
EAST | December | On site for continued operational support during 48 hours shutdown of facility for switchover to new CT1 and CT2 contact tank tie in. Contractors working on Tie in #2 from new contact tanks to distribution. Conducted visual station check on site. Unable to verify HACH Cl17 Analyzers as they are off at the moment for upgrades. I?ll have to return for Tie in #2, as the pressure test did not pass. Will return to site to continue tie in to distribution | Ballantrae Well 1 & 2 | 2025-12-05
EAST | December | -on site 0900 to assist with the electrical shut down of site. With endeavour we placed the generator into off state and pulled battery cables off to stop a start up at 0930. We then plugged the pac panel ups into the generator and confirmed that it was charging. At 0945 endeavour shut site hydro off and commenced work. I called roc to warn them of alarms coming from the work being done. At 1130 endeavour completed work and we returned site back to hydro. We then tested the rotation of the generator cables to confirm operation. I placed the generator back to auto and connected the ups back to proper power feed. Under direction of oic. | Ballantrae Well 1 & 2 | 2025-12-03
EAST | December | On site to provide OP support for new chlorine contact tank tie in. The facility is LOTO from the system. Witness local disinfection of new connection pipe spraying with 12% hypo, as well as new couplings and connection points.? Reviewed SCADA, set hypo P2 local speed of 44 strokes/min, which is 22%.? Set silicate P2 local speed of 52 strokes/min, which is 43% Well 1 FIT 1075671 m3 at start. 13:44 - 13:49 Run well 1 locally to waste via flanged connection and flex hose. Placed dechlor pucks at discharge.? Informed ROC.? 16:43 Started well 1 in local to run to waste with chemical pumps in local.? 17:20 grab chlorine residual from VC2 discharge line: FCL = 1.05 mg/l, TCL = 1.12 mg/l.? Adjusted the BVs so that the discharge pressure is at 442 kpa, discharge flow = 15.3 l/s. Hypo P2 is 25 stroke/min or 12%.? Silicate P2 is 30 stroke/min, or 25%. 17:50 chlorine grab from influent sample line (VC1), FCL> 2.20 mg/l? 17:53 Stopped Well 1 and chemical pumps. Readjusted the discharge hose.? 18:09 Started well 1 again in local. Flow rate = 18 l/s, Hypo P2 = 29 strokes/min, Silicate P2 = 35 stroke/min. 18:33 chlorine grab from influent: FCL > 2.20 mg/l. 18:43 chlorine grab from effluent: FCL = 2.09 mg/l, TCL = 2.22 mg/l.? 18:43 collected micro sample, YD W11475760. 18:48 collected well 1 raw. 18:48 stopped well 1 and chemical pumps.? LOTO well 1 via MCC panel.? Returned hypo and silicate pumps back to remote operation.? Well 1 FIT 1075782 m3, total wasted 111 m3.? Facility remains offline and isolated from the system.? | Ballantrae Well 1 & 2 | 2025-12-04
EAST | December | Disabled software routine in PAC that processes volume for older existing Contact Tank. Enabled software routines for dual contact tank control, allowing new volumes to be processed in CT logic. Operations can select the tanks as required based on yard piping setup. Site works did not go as anticipated, therefore no actual well startup has occurred with the new calculations. To be monitored via SCADA. | Ballantrae Well 1 & 2 | 2025-12-05
EAST | December | On site for hypo delivery top up. 200L . | Ballantrae Well 1 & 2 | 2025-12-17
EAST | December | Dropped off 1459 L of silicate to bulk tank. | Ballantrae Well 1 & 2 | 2025-12-23
EAST | December | On site to set up day tank for silicate and suction lines. Will be filling silicate day tank tomorrow. | Ballantrae Well 1 & 2 | 2025-12-22
EAST | December | Torbear contractor was able to pump out Silicate bulk tank this morning. Donald Moses on site to refill up Silicate bulk tank with silicate. Day tank not required. Re-primed silicate pumps and manually started Well 1 to collect raw sample. 11:11hrs: Collected Well #1 raw sample. 11:11hrs: Collected Treated Cl2 grab residuals: Cl2 Influent Free: 2.10mg/l, Analyzer: 2.11mg/l Cl2 Effluent Free: 1.85mg/l, Analyzer: 1.76mg/l Adjusted Effluent HACH Cl17 Analyzer from 1.76mg/l to 1.85mg/l based on multiple CL2 grab residuals. Checked site and equipment. Torbear on site continuing Facility upgrades. Wells back in to auto. | Ballantrae Well 1 & 2 | 2025-12-23
EAST | December | Enabled silicate tank level hi, lo and lolo alarm. | Ballantrae Well 1 & 2 | 2025-12-22
EAST | December | Switched well duty so that well 2 is duty 1 and well 1 is duty 2. | Ballantrae Well 1 & 2 | 2025-12-18
EAST | December | Back on site to look at silicate room and to plan out setting up a silicate day tank on site while waiting to have bulk tank pumped down. | Ballantrae Well 1 & 2 | 2025-12-22
EAST | December | On site for station check. Collected weekly micro samples (W11469844). 11:40hrs: Noticed Silicate bulk tank reading much higher than normal. Checked bulk tank and noticed bulk tank is full of water. Placed Silicate Pumps off for now. Informed Team Lead and contractor. Grabbed Well 2 Samples and placed wells to manual off for now until Silicate tank overflow can be dealt with. ?Spoke with contractor, said potable water line that feeds silicate Dice block was broken when they came in this morning and spraying water. Contractor fixed the line this morning. Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 2.15mg/l FCL Analyzer: 2.09mg/l 11:48hrs: Effluent Free Cl2 grab residual: 1.99mg/l FCL Analyzer: 2.09mg/l Effluent Total Cl2 grab residual: 2.34mg/l Made adjustment to effluent HACH Cl17 Analyzer from 2.09mg/l to 1.99mg/l based on multiple Cl2 grab residuals. Will return to collect Well #1 samples. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Site currently undergoing Construction upgrades by Torbear. Equipment out of service: Silicate system. | Ballantrae Well 1 & 2 | 2025-12-22
EAST | December | On site with Jackie S to transfer silicate. ? Start level: 23.3 cm Stop level: 31.9 cm Performed station checks while on site. Well duty is not active. 11:54 verified chlorine readings with grabs. Influent grab free = 1.69 mg/l, analyzer = 1.68 mg/l. Effluent grab free = 1.78 mg/l, analyzer = 1.82 mg/l. Station readings are in PWQ sheet.? The block heater on generator is not working, will issue a work order.? Station turbidity is higher than normal. Found grit in the sample vial, performed sample line flushing. Turbidity reading is trending down after flushing. Reviewed trends. Hypo pump 2 is hunting, will investigate later.? | Ballantrae Well 1 & 2 | 2025-12-24
EAST | December | On site for station check and for service request for isolating ball valve for contractors to work on moving the existing hot water tank. - Ball valve controls the water supply line to well pump #1 cooling supply. Well 1 is already in manual off, and well 2 is running, which does not use the cooling water Duty is active - Tower level is 79% Recorded station readings in PWQ sheets Verified analyzer readings @11:05 - Adjusted effluent free analyzer from 2.03 to 2.18 mg/L based on multiple grabs Reviewed trends, equipment ok Contractors currently on site working in former bulk hypo tank room Station ok | Ballantrae Well 1 & 2 | 2025-12-18
EAST | December | On site for station check and weekly micro sampling (W11483402) Duty is active - tower level - 89% Well 2 is running at 30 L/s, 681 kpa Generator is currently running. Traffic lights at Aurora Rd-McCowan Rd intersection not working at time of arrival. Hydro One trucks in the area. Recorded station readings in PWQ sheets Reviewed SCADA trends, station ok. Chemical systems: Hypo pump 1 is running at 24%, DF = 65%. DP= 760 kpa Silicate P1 running at 43%, 76.44 mL/min, DP= 740 kpa Verified analyzer readings with grab residuals Influent: @ 9:44 Free Grab: 1.99 mg/L Analyzer: 1.98 mg/L Effluent: @ 9:48 Free Grab: 1.99 mg/L / Analyzer: 2.00 mg/L Total Grab: 2.30 mg/L NTU: 0.058 Collected TW sample and well 2 raw sample at 9:53 Manual stop well 2 at 9:57 Hydro power came back at 10:11 Manual start well 1 at 10:12 Generator shut down at 10:17 Hours: 1016.7 hrs Fuel: 700 L Brief loss of power at 10:27 - well 1 shut down. Well 1 VFD Fault and VFD Not Ready alarms triggered at 10:27. Manual start well 1 at 10:30. Running at 30 L/s. Collected well 1 raw sample at 10:40 Manual stop well 1 at 10:45 and put both pumps back in auto. | Ballantrae Well 1 & 2 | 2025-12-29
EAST | December | On site for station check. Collected weekly micro samples (W11454679). Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 2.00mg/l FCL Analyzer: 2.03mg/l 11:00hrs: Effluent Free Cl2 grab residual: 1.98mg/l FCL Analyzer: 1.94mg/l Effluent Total Cl2 grab residual: 2.16mg/l Collected Well 1 Raw sample @ 11:30hrs. Collected Well 2 Raw sample @ 11:00hrs. Changed Well Duties: W2 to D2, W1 to D1. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Site currently undergoing Construction upgrades by Torbear. Equipment out of service: None. | Ballantrae Well 1 & 2 | 2025-12-16
EAST | December | On site for station check. Collected weekly micro samples (W11438445). Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 2.12mg/l FCL Analyzer: 2.19mg/l 09:55hrs: Effluent Free Cl2 grab residual: 1.44mg/l FCL Analyzer: 1.47mg/l Effluent Total Cl2 grab residual: 1.73mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Site currently undergoing Construction upgrades by Torbear. Equipment out of service: None. | Ballantrae Well 3 | 2025-12-10
EAST | December | On site for station check. Collected in house iron samples. Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 2.07mg/l FCL Analyzer: 2.14mg/l Effluent Free Cl2 grab residual: 1.47mg/l FCL Analyzer: 1.53mg/l Effluent Total Cl2 grab residual: 1.74mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Site currently undergoing Construction upgrades by Torbear. Equipment out of service: None. | Ballantrae Well 3 | 2025-12-12
EAST | December | On site for station check. Collected weekly micro samples (W11419085). Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 2.07mg/l FCL Analyzer: 2.14mg/l 08:26hrs: Effluent Free Cl2 grab residual: 1.44mg/l FCL Analyzer: 1.51mg/l Effluent Total Cl2 grab residual: 1.68mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Site currently undergoing Construction upgrades by Torbear. Equipment out of service: None. | Ballantrae Well 3 | 2025-12-03
EAST | December | On site for station check. Collected in house iron samples. Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 2.20mg/l FCL Analyzer: 2.23mg/l Effluent Free Cl2 grab residual: 1.41mg/l FCL Analyzer: 1.44mg/l Effluent Total Cl2 grab residual: 1.61mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Site currently undergoing Construction upgrades by Torbear. Equipment out of service: None. | Ballantrae Well 3 | 2025-12-01
EAST | December | On site for station check. Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 1.50mg/l FCL Analyzer: 1.51mg/l Effluent Free Cl2 grab residual: 1.36mg/l FCL Analyzer: 1.45mg/l Effluent Total Cl2 grab residual: 1.54mg/l Adjusted Effluent FCL Analyzer from 1.45mg/l to 1.35mg/l based on multiple Cl2 grab residuals. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Site currently undergoing Construction upgrades by Torbear. Equipment out of service: None. | Ballantrae Well 3 | 2025-12-05
EAST | December | On site for monthly maintenance: 10:45hrs: HACH CL17 Influent and Effluent Analyzer cleaning. Verified Analyzer after cleaning: Influent: 1.60mg/l, Analyzer: 1.58mg/l Effluent: 1.61mg/l, Analyzer: 1.61mg/l Turbidimeter maintenance and calibration completed Conducted Generator Test Run (13:10hrs): Diesel Generator Run Monthly Test: Start Runtime: 13:10hrs (Run hrs: 406hrs, 51min) Fuel Start: 90.7/84.6cm Stop Runtime: 14:15hrs (Run hrs: 407hr, 57min Fuel Stop: Generator Performance Data recorded below: Battery Cell Levels: OK Battery Terminals/Cables: Ok Oil and Coolant: Ok Amps: 25amps Volts: 600 Hertz: 60 RPM: 1801RPM Oil Pressure: 57psi Water temp: 169 F No issues during generator run test. Ran Well 3 during run test. Conducted Silicate and Chlorine inspection. Ran hot water through silicate system. Tested low building temp alarm and Cl2 leak detector test, no issues. | Ballantrae Well 3 | 2025-12-09
EAST | December | On site for station check. Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 2.16mg/l FCL Analyzer: 2.20mg/l Effluent Free Cl2 grab residual: 1.53mg/l FCL Analyzer: 1.60mg/l Effluent Total Cl2 grab residual: 1.85mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Site currently undergoing Construction upgrades by Torbear. Equipment out of service: None. | Ballantrae Well 3 | 2025-12-08
EAST | December | On site top up Silicate day tank from 150 to 200L. | Ballantrae Well 3 | 2025-12-17
EAST | December | At 07:30 deactivated well and put it in manual for the contractors on site. | Ballantrae Well 3 | 2025-12-19
EAST | December | On site for station check. Collected weekly micro samples (W11454679). Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 2.15mg/l FCL Analyzer: 2.20mg/l 09:55hrs: Effluent Free Cl2 grab residual: 1.45mg/l FCL Analyzer: 1.51mg/l Effluent Total Cl2 grab residual: 1.74mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Site currently undergoing Construction upgrades by Torbear. Equipment out of service: None. | Ballantrae Well 3 | 2025-12-16
EAST | December | On site for station check and equipment verifications Duty is active - 82% Recorded station readings in PWQ sheets Verified analyzer readings @11:30 - no adjustments needed Visual inspection of chemical systems - all okay Reviewed trends, equipment OOS: none Station ok | Ballantrae Well 3 | 2025-12-18
EAST | December | On site for station check and weekly micro sampling (W11483402) Duty is active - tower level - 82% Well is running at 30 L/s, 653 kpa Recorded station readings in PWQ sheets Reviewed SCADA trends, station ok. Chemical systems: Chlorinator 1 is open at 52%, DF = 69%. BP1 DP= 1460 kpa Silicate P1 running at 28%, 27.60 mL/min, DP= 740 kpa Verified analyzer readings with grab residuals Influent: @ 8:24 Free Grab: 2.11 mg/L Analyzer: 2.16 mg/L Effluent: @ 8:27 Free Grab: 1.55 mg/L / Analyzer: 1.55 mg/L Total Grab: 1.80 mg/L NTU: 0.040 Collected W3 Raw and TW at 8:33 | Ballantrae Well 3 | 2025-12-29
EAST | December | On site for station check. Collected weekly micro samples (W11469844). Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 2.15mg/l FCL Analyzer: 2.18mg/l 10:55hrs: Effluent Free Cl2 grab residual: 1.48mg/l FCL Analyzer: 1.50mg/l Effluent Total Cl2 grab residual: 1.72mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Site currently undergoing Construction upgrades by Torbear. Equipment out of service: None. | Ballantrae Well 3 | 2025-12-22
EAST | December | Under direction of OIC (Dan Zhou) On-site for; - Station Checks Data in PWQ excel Workbook (Influent) Grabs @ 12:39 hrs. FCl: 1.98 mg/L Analyzer: 1.97 mg/L Effluent (Treated Water) Grabs @ 12:39 hrs. FCl: 1.98 mg/L TCL: 2.10 mg/L Analyzer: 2.04 mg/L Equipment OOS: none Facility OK | Stouffville Reservoir and Wells 5 & 6 | 2025-12-12
EAST | December | Conducted CL2 cylinder change with Dan Zhou. Conducted monthly maintenance: - JHSC inspection - Exhaust and supply fan check - Chlorine chemical system inspection | Ballantrae Well 3 | 2025-12-23
EAST | December | On site with Jackie S to transfer silicate. ? Start level: 145 L Stop level: 210 L Performed station checks while on site. Well duty is not active. 11:25 verified chlorine readings with grabs. Influent grab free = 1.54 mg/l, analyzer = 1.53 mg/l. Effluent grab free = 1.52 mg/l, analyzer = 1.59 mg/l. Station readings are in PWQ sheet.? Reviewed trends.? | Ballantrae Well 3 | 2025-12-24
EAST | December | On site to check station and sample collections. Well duty and high lift duty are active. 09:27 collected well 6 raw. YD W11438547. 09:31 collected well 5 raw. 09:45 grab chlorine residual from treated tap: FCL = 2.04 mg/l, TCL = 2.18 mg/l. Analyzer free = 2.07 mg/l. 09:45 Collected treated sample. HLP2 was running in duty 1. Switched duty to run HLP1.? At UV building, sample pump 2 was running in duty 1.? Chlorine booster pump 1 and chlorinator 1 is in duty 1. Reviewed trends, station is under normal operation. | Stouffville Reservoir and Wells 5 & 6 | 2025-12-10
EAST | December | On site to complete station check. Activated wells at 13:07. Switched feeding cell from East to west. Opened corresponding valve for sample pump. Time: 13:25 Influent Grab (mg/l) Analyzer (mg/l) Free: 2.12 2.09 Time: 13:30 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.94 1.99 Total: 2.10 Verified analyzers with grabs. Checked site and trends. No outstanding alarms. | Stouffville Reservoir and Wells 5 & 6 | 2025-12-01
EAST | December | On site for station check. Duty active, tower level 62%. Well 5 running 27.3 L/s and well 6 running 18.4 L/s. Verified analyzer readings with grab residuals. Influent @ 13:12 Free Grab: 2.10 mg/L Analyzer: 2.11 mg/L Effluent @ at 13:26 Free Grab: 1.95 mg/L Analyzer: 2.00 mg/L Total Grab: 2.07 mg/L Visual inspection of chemical systems - all ok. Entered station readings in PWQ sheet. Reviewed trends, equipment ok. Station ok | Stouffville Reservoir and Wells 5 & 6 | 2025-12-05
EAST | December | On site for station check. Duty active, tower level 87%. Changed chlorine cylinder bank 1 with Dan Z. Switched feeding cell from east to west. Well 5 running 27.4 L/s and well 6 running 18.5 L/s. Verified analyzer readings with grab residuals. Influent @ 14:43 Free Grab: 2.16 mg/L Analyzer: 2.14 mg/L Effluent @ at 14:55 Free Grab: 1.92 mg/L Analyzer: 1.96 mg/L Total Grab: 2.03 mg/L Visual inspection of chemical systems - all ok. Entered station readings in PWQ sheet. Reviewed trends, equipment ok. Station ok | Stouffville Reservoir and Wells 5 & 6 | 2025-12-08
EAST | December | Under direction of OIC (Dan Zhou) On-site for; - Station Checks - Regulatory sampling (W11419179) Data in PWQ excel Workbook @ 13:39 started well pump5 manually for sampling Regulatory samples taken @ 14:15 hrs. (Influent) Grabs @ 14:15 hrs. FCl: 1.98 mg/L Analyzer: 1.97 mg/L Effluent (Treated Water) Grabs @ 14:15 hrs. FCl: 1.91 mg/L TCL: 2.05 mg/L Analyzer: 1.98 mg/L @ 14:29 returned well pumps to auto Equipment OOS: none Facility OK | Stouffville Reservoir and Wells 5 & 6 | 2025-12-03
EAST | December | On site for station check. Collected weekly micro samples (W11454773). Verification of HACH CL17 Chlorine Analyzers: Influent Free CL2 grab residual: 2.00mg/l FCL Analyzer: 2.03mg/l 12:30hrs: High Lift Effluent Free Cl2 grab residual: 1.99mg/l FCL Analyzer: 2.03mg/l Effluent Total Cl2 grab residual: 2.08mg/l Collected Well 5 Raw sample @ 12:05hrs. Collected Well 6 Raw sample @ 11:55hrs. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Stouffville Reservoir and Wells 5 & 6 | 2025-12-16
EAST | December | Well 5 and 6 were interlocked due to influent chlorine lolo alarm. Upon arrival, there is no flow from sample pump 2 while it is running. Sample pump 1 had faulted earlier.? Cycled power on sample pump 1, it resumed operation. Replaced tubing and roller (spare used one) on sample pump 2, primed it , it is in standby.? Switched sample line and corresponding discharge line from West Cell to East Cell. 09:45 grab influent chlorine = 1.32 mg/l, analyzer free = 1.33 mg/l.? Placed HLP1 Man/on and activate well duty.? Switched high lift pump duty so that HLP1 is duty 1.? 10:25 Collected well 5 and 6 raw micro samples. YD #W11483496. 11:02 treated water grab chlorine residual: FCL = 1.78 mg/l, TCL = 1.95 mg/l. Analyzer free = 1.82 mg/l. 11:02 collected treated water micro sample.? Placed HLP1 back to auto and it stopped. Station readings entered in PWQ sheet. Reviewed trends, no issues.? | Stouffville Reservoir and Wells 5 & 6 | 2025-12-29
EAST | December | Under direction of OIC (Dan Zhou) On-site for; - Station Checks - Switch influent sample line and corresponding flow path to reservoir Data in PWQ excel Workbook (Influent) Grabs @ 13:57 hrs. FCl: 2.18 mg/L, 2.19 mg/L, 2.16 mg/L Analyzer: 2.02 mg/L Adjusted analyzer to 2.17 mg/L Effluent (Treated Water) Grabs @ 14:14 hrs. FCl: 2.03 mg/L TCL: 2.19 mg/L Analyzer: 2.07 mg/L @ 14:23 switched influent sample line and corresponding flow path from east to west Equipment OOS: none Facility OK | Stouffville Reservoir and Wells 5 & 6 | 2025-12-18
EAST | December | On site to check station and equipment. High lift duty and well duty are active. 08:50 grab chlorine residual from treated tap:? FCL = 1.91 mg/l, TCL = 2.09 mg/l. Analyzer free = 1.93 mg/l. 08:50 Collected treated bac-T sample, YD W11469946. Switched high lift pump duty from P1 to P2.? Tighten the packing for pump 2. 09:22 Collected well 5 raw. 09:25 Collected well 6 raw. 09:34 influent chlorine grab free = 2.04 mg/l, analyzer free = 2.11 mg/l.? Sample pump 1 fault from Dec. 21. It lost power. Cycled the power on sample pump 1. Placed it in duty 1.? Switched influence sample line and corresponding flow path from West to East cell. Reviewed trends, station is under normal operations. | Stouffville Reservoir and Wells 5 & 6 | 2025-12-22
EAST | December | Grease bottom motor bearing Well 5 and 6 has oil bath bearing motors | Stouffville Reservoir and Wells 5 & 6 | 2025-12-18
EAST | December | Changed left side chlorine cylinder with Joe Mazza. Tested vacuum switch, no issues., | Stouffville Reservoir and Wells 5 & 6 | 2025-12-23
EAST | December | Under direction of OIC (Dan Zhou) On-site for; - Preventative Maintenance; UV building Chlorine Analyzer Maintenance and Verification, High lift Building Chlorine Analyzer Maintenance and Verification, Turbidity Analyzer maintenance and verification - JHSC Health and Safety Checks - Monthly Generator Test Run - Chlorine Emergency Repair kit Inspection - Comprehensive housekeeping - Chlorine leak detector test - Chlorine scrubber check - Chlorine chemical system inspection @ 10:31 hrs. Put wells 5,6 in manual off for pm?s Changed chlorine cylinder with OIC Jackie Performed chlorine leak detector test, scrubber check and chemical system inspection @ 11:29 placed high lifts 1 and 2 in manual off for pm?s UV Building Chlorine Analyzer Start Clean @ 11:30 hrs. Stop Clean @ 11:52 hrs. Influent Water Grab @ 12:10 hrs Grab FCl: 2.04 mg/L Analyzer FCl: 2.01 mg/L High lift Building AIT Maintenance Start Clean @ 11:33 hrs. Exit/Stop Clean @ 11:59 hrs. Treated Water (Effluent) Grab @ 12:18 AM Grabs FCl: 1.96 mg/L Analyzer FCl: 1.98 mg/L Turbidity Analyzer Maintenance and calibration Start @ 11:59 hrs. Stop @ 12:05 hrs. Generator Test Run: Start hours: 10.95 Start time: 12:28 hrs. Stop Hours: 12.12 Stop Time: 13:42 Run Time hours: 1.17 Start Fuel: 3183 L Stop Fuel: 3143 L Pre run checks; Battery Cell Levels: Ok Battery Terminals and Cables: Ok Oil Level: Ok Coolant Level: Ok Fluid Leaks: NO Coolant Recirculating pump: Ok Faulty Gauges: NO *under facility load* @ 12;39 put well pump 5 in manual on @ 12:42 put high lift 1 in manual on Operating Current: 64 Amps Operating Frequency: 60 Hz Operating Voltage: 599.37 Volts Engine speed: 1800.5 RPM Water/coolant Temp: 170.6 f Oil Pressure: 37.13 psi Oil Temperature: not on screen, cannot locate oil temp monitoring on OIT screen @ 13:36 put high lift pump1 in manual off, and put well pump 5 in manual off @ 13:36 flipped ATS switch @ 13;48 put well pumps 5 and 6, high lift pumps 1 and 2 in auto Equipment OOS: none Facility OK | Stouffville Reservoir and Wells 5 & 6 | 2025-12-17
EAST | December | Under direction of OIC (Dan Zhou) On Site for; - Station Checks Data in PWQ Workbook Grabs @ 13:28 FCl: 1.79 mg/L TCL: 1.95 mg/L Analyzer: FCl: 1.84 mg/L Turbidity spike due running air compressor. Equipment out of Service: None Facility OK | Stouffville Highway 48 Booster Pumping Station | 2025-12-12
EAST | December | On site for station check. Verified analyzer reading with grab residuals. Effluent @ at 13:47 Free Grab: 2.00 mg/L Analyzer: 2.12 mg/L Total Grab: 2.11 mg/L Adjusted analyzer with the average of three grab samples Entered station readings in PWQ sheet. Station ok | Stouffville Highway 48 Booster Pumping Station | 2025-12-05
EAST | December | Ran air compressor while on site. Flushed the surge tank via drain port. The water level is between the taped range. | Stouffville Highway 48 Booster Pumping Station | 2025-12-08
EAST | December | On site for station check. Verified analyzer reading with grab residuals. Effluent @ at 13:56 Free Grab: 2.02 mg/L Analyzer: 1.97 mg/L Total Grab: 2.06 mg/L Entered station readings in PWQ sheet. Station ok | Stouffville Highway 48 Booster Pumping Station | 2025-12-08
EAST | December | On site to complete station check. Time: 14:07 Grab (mg/l) Analyzer (mg/l) Free: 1.89 1.95 Total: 1.98 Verified analyzer with grabs. Checked site. No outstanding alarms on site. | Stouffville Highway 48 Booster Pumping Station | 2025-12-01
EAST | December | Under Direction of OIC (Dan Zhou) On site for Preventative maintenance; - Chlorine analyzer maintenance and verification - Comprehensive Housekeeping - Clean portable eye wash and change eye wash solution Chlorine Analyzer Maintenance and verification Start Clean @ 14:09 Exit/Stop Clean @ 14:20 Chlorine low alarm due to not priming AIT long enough Grab @ 14:35 FCl:1.85 mg/L Analyzer FCl: 1.89 Equipment OOS: None Station OK | Stouffville Highway 48 Booster Pumping Station | 2025-12-17
EAST | December | On site to check station and equipment. P2 is running in duty1.? Ran air compressor while on site. There is a pin hole leak on the copper line of the PRV, issued work order to maintenance .? 10:48 Verified chlorine residual with grabs: FCL = 1.70 mg/l. Analyzer free = 1.72 mg/l.? Station readings entered in PWQ sheet. Reviewed trends, no issues.? | Stouffville Highway 48 Booster Pumping Station | 2025-12-29
EAST | December | On site to reset Pump #2 VFD fault Performed visual inspection on site. Pinhole leak on the station PRV is outstanding, WO is created Station operation normal | Stouffville Highway 48 Booster Pumping Station | 2025-12-31
EAST | December | On site to check station and equipment. Pump 1 is running in duty 1.? Ran air compressor while on site. 09:17 grab chlorine free = 1.84 mg/l, total = 2.04 mg/l. Analyzer free = 1.91 mg/l. Reviewed trends, station is under normal operation. No outstanding alarms. | Stouffville Highway 48 Booster Pumping Station | 2025-12-22
EAST | December | On site for station check. Verified Cl2 Analyzers, checked reagent levels. Station readings, residuals and dosages in PWQ sheet. Equipment Out of Service: None. | Stouffville Highway 48 Booster Pumping Station | 2025-12-16
EAST | December | Under direction of OIC (Dan Zhou) On Site for; - Station Checks Data in PWQ Workbook Grabs @ 13:40 FCl: 1.84 mg/L TCL: 1.98 mg/L Analyzer: FCl: 1.84 mg/L Turbidity spike due running air compressor. Equipment out of Service: None Facility OK | Stouffville Highway 48 Booster Pumping Station | 2025-12-18
WEST | December | Station Check (secure & off line) | King City Wells 3 & 4 | 2025-12-04
WEST | December | Onsite were station check Site secure Site offline with no power | King City Wells 3 & 4 | 2025-12-24
WEST | December | Onsite were station check Site secure Site offline with no power Completed jhsc | King City Wells 3 & 4 | 2025-12-12
WEST | December | Onsite were station check Site secure Site offline with no power | King City Wells 3 & 4 | 2025-12-19
WEST | December | Onsite for station check and to collect weekly micro sample W11438669 Ran wells 3&4 in local to waste Checked treated residuals mg/L @1348 Total analyzer 1.91 grab 1.88 Free analyzer 0.01 grab 0.02 | Kleinburg Wells 3 and 4 | 2025-12-10
WEST | December | Changed potassium iodide solution | Kleinburg Wells 3 and 4 | 2025-12-12
WEST | December | Onsite for station check and to collect weekly micro sample W1149594 Ran wells 3&4 in local to waste Checked treated residuals mg/l @1428 Total analyzer 1.96 grab 1.97 Free analyzer 0.01 grab 0.03 | Kleinburg Wells 3 and 4 | 2025-12-03
WEST | December | Onsite to complete work orders Generator test Start Fuel 38.7 cm/ 1998L Hrs 413.4 Ran whisper lane pumps to put load on generator Stop Fuel 37.8 cm / 1953 L Hrs 414.9 Tested cl2 leak with no issues Calibrated ntu analyzer with 20 ntu vail Inspected silicate and ammonia systems Did maintenance on treated cl2 analyzer Topped up electrolyte Grit ok | Kleinburg Wells 3 and 4 | 2025-12-02
WEST | December | Onsite for station check and to collect weekly micro sample W11470068 Ran wells 3&4 in local to waste Checked treated residuals mg/l @1137 Total analyzer 1.91 grab 1.93 Free analyzer 0.00 grab 0.05 Adjusted free analyzer Reagents ok | Kleinburg Wells 3 and 4 | 2025-12-22
WEST | December | On site for station check and to collect bacti sample w11483730 ran wells to waste - distribution valve locked out. Checked residuals Total Analyzer 1.85mg/L Grab 1.90mg/L Free Analyzer 0.00mg/L Grab 0.03mg/L Reagents all okay Wells back offline after sampling No known issues | Kleinburg Wells 3 and 4 | 2025-12-29
WEST | December | Onsite for station check and to collect weekly micro sample W11454984 Ran wells 3&4 in local to waste Checked treated residuals mg/l @2442 Total analyzer 1.88 grab 1.94 Free analyzer 0.00 grab 0.00 Reagents ok | Kleinburg Wells 3 and 4 | 2025-12-16
WEST | December | W11419265- SWO - ON-CALL Consultation - WEST 06:50-ROC called for Hypo pump failed to start alarm. Decided to leave it off until someone attend site as Directed by Team lead. Informed ROC the same. | Schomberg Elevated Tank | 2025-12-08
WEST | December | on site for station check Check trends- All okay Verified analyzers Tower Filling Post injection- Total CL2 Grab: 3.70 mg/L: Analyzer: 3.61 mg/L Deactivated Duty Common inlet/outlet- Total CL2 Grab: 3.54 mg/L: Analyzer: 3.47 mg/L Reagents All good in house lab Sample taken while tower draining entered values in PWQ sheet Equipment all okay | Schomberg Elevated Tank | 2025-12-15
WEST | December | -on site to complete station check and to collect samples - tower draining at 24.0 l/s, level = 42 % - reviewed trends - CL17 reagents ok - checked equipment -recorded readings in PWQ sheet - no issues found -hypo pump #2 OOS -reduced chlorine residual target setpoint 3.70 to 3.65 mg/L -verified analyzers: 10:16 - common inlet/outlet TCL analyzer = 3.60 mg/L 10:16 - common inlet/ outlet grab: FCL = 0.06 mg/L TCL = 3.64 mg/L Mono = 3.14 mg/L 10:22 - collected weekly micro sample - W/O # W11438617 10:24 - post injection TCL analyzer = 4.32 mg/L 10:24 - post injection grab: TCL = 4.32 mg/L | Schomberg Elevated Tank | 2025-12-10
WEST | December | -on site to complete station check - tower filling - reviewed trends - CL17 reagents ok - checked equipment -recorded readings in PWQ sheet - no issues found -hypo pump #2 OOS -hypo pump #1 running at 12%, DF = 117% -verified analyzers: 08:20 - common inlet/outlet TCL analyzer = 3.20 mg/L 08:20 - common inlet/ outlet grab: TCL = 3.20 mg/L 08:26 - post injection TCL analyzer = 3.68 mg/L 08:26 - post injection grab: TCL = 3.72 mg/L | Schomberg Elevated Tank | 2025-12-11
WEST | December | -on site to complete station check and to collect samples - tower draining at 27.2 l/s, level = 43 % - reviewed trends - CL17 reagents ok - checked equipment -recorded readings in PWQ sheet - no issues found -verified analyzers: 10:02 - common inlet/outlet TCL analyzer = 3.62 mg/L 10:02 - common inlet/ outlet grab: FCL = 0.03 mg/L TCL = 3.62 mg/L Mono = 3.16 mg/L 10:07 - collected weekly micro sample - W/O # W11419315 10:09 - post injection TCL analyzer = 4.44 mg/L 10:09 - post injection grab: TCL = 4.36 mg/L | Schomberg Elevated Tank | 2025-12-03
WEST | December | Filled hypo tank 25 to 45 cm | Schomberg Elevated Tank | 2025-12-03
WEST | December | Attending site to check Hypo Pumps not working (W11497043). Found both pumps not able to run. Tightened all terminations in local electrical panel and was able to get pump#1 to run. Pump#2 will not function and remains out-of-service. I have requested a quotation for 2 replacement pumps. Will return to install and configure once they arrive. ROC was notified before and after maintenance work. Associated SCADA alarms were cleared. | Schomberg Elevated Tank | 2025-12-08
WEST | December | -on site to complete station check and to collect sample for in house lab analysis -hypo pump #2 OOS due to fail to start alarms -ran pump in local to calibration column - no issues -ran pump in manual - no issues -returned pump to service, will monitor - tower draining at 26.4 l/s, level = 43% - reviewed trends - CL17 reagents ok - checked equipment -recorded readings in PWQ sheet -verified analyzers: 10:25 - common inlet/outlet TCL analyzer = 3.58 mg/L 10:25 - common inlet/ outlet grab: FCL = 0.02 mg/L TCL = 3.48 mg/L Mono = 3.13 mg/L 10:31 - post injection TCL analyzer = 3.57 mg/L 10:31 - post injection grab: TCL = 3.50 mg/L -noticed sample flow through post injection chlorine analyzer was low -flushed sample lines and analyzer flow meter -no further issues | Schomberg Elevated Tank | 2025-12-01
WEST | December | -on site to complete station check and to collect sample for in house lab analysis - tower draining at 18.0 l/s, level = 18% - reviewed trends - CL17 reagents ok - checked equipment -recorded readings in PWQ sheet - no issues found -verified analyzers: 08:42 - common inlet/outlet TCL analyzer = 3.51 mg/L 08:42 - common inlet/ outlet grab: FCL = 0.00 mg/L TCL = 3.46 mg/L Mono = 2.95 mg/L -activated high lift duty 09:01 - post injection TCL analyzer = 3.50 mg/L 09:01 - post injection grab: TCL = 3.54 mg/L | Schomberg Elevated Tank | 2025-12-05
WEST | December | -on site to complete station check and to collect sample for in house lab analysis -both hypo pumps receiving uncommanded stop and fail to start alarms. Attempted to run pumps in manual and local - pumps will not run. Instrumentation attending site to troubleshoot. - tower draining at 29.2 l/s, level = 33% - reviewed trends -replaced common inlet/outlet CL17 reagents - checked equipment -recorded readings in PWQ sheet -verified analyzers: 11:20 - common inlet/outlet TCL analyzer = 3.50 mg/L 11:20 - common inlet/ outlet grab: FCL = 0.00 mg/L TCL = 3.58 mg/L Mono = 2.97 mg/L 11:26 - post injection TCL analyzer = 3.90 mg/L 11:26 - post injection grab: TCL = 3.82 mg/L | Schomberg Elevated Tank | 2025-12-08
WEST | December | -on site to complete station check and to collect sample for in house lab analysis -filled hypo tank 78 to 142 L -hypo pump DF = 116% -hypo pump #2 OOS - tower draining at 26.9 l/s, level = 39% - reviewed trends - CL17 reagents ok - checked equipment -recorded readings in PWQ sheet - no issues found -verified analyzers: 10:43 - common inlet/outlet TCL analyzer = 3.57 mg/L 10:43 - common inlet/ outlet grab: FCL = 0.00 mg/L TCL = 3.58 mg/L Mono = 3.00 mg/L 10:48 - post injection TCL analyzer = 3.07 mg/L 10:49 - post injection grab: TCL = 3.10 mg/L | Schomberg Elevated Tank | 2025-12-24
WEST | December | -on site to complete station check and to collect samples -hypo pump DF = 113% -hypo pump #2 OOS - tower draining at 27.8 l/s, level = 33 % - reviewed trends - CL17 reagents ok - checked equipment -recorded readings in PWQ sheet - no issues found -verified analyzers: 09:49 - common inlet/outlet TCL analyzer = 3.51 mg/L 09:49 - common inlet/ outlet grab: FCL = 0.05 mg/L TCL = 3.44 mg/L Mono = 2.97 mg/L 09:55 - collected weekly micro sample - W/O # W11483646 09:58 - post injection TCL analyzer = 3.63 mg/L 09:58 - post injection grab: TCL = 3.70 mg/L | Schomberg Elevated Tank | 2025-12-29
WEST | December | -on site to complete station check and to collect samples - tower draining at 28.5 l/s, level = 41 % - reviewed trends - CL17 reagents ok - checked equipment -recorded readings in PWQ sheet - no issues found -verified analyzers: 11:55 - common inlet/outlet TCL analyzer = 3.49 mg/L 11:55 - common inlet/ outlet grab: FCL = 0.06 mg/L TCL = 3.42 mg/L Mono = 2.91 mg/L 12:08 - collected weekly micro sample - W/O # W11454909 12:11 - post injection TCL analyzer = 3.72 mg/L 12:11 - post injection grab: TCL = 3.70 mg/L | Schomberg Elevated Tank | 2025-12-16
WEST | December | Respond to site to continue monitoring of ET while running on mobile generator (site power failure). Power restored approx 1520, returned Generator Panel to utility power. | Schomberg Elevated Tank | 2025-12-17
WEST | December | Vent hypo tank Can?t vent currently until openings are sealed up | Schomberg Elevated Tank | 2025-12-23
WEST | December | -on site to complete work orders -informed ROC of work -filled hypo tank 58 L to 126 L -completed Sodium Hypochlorite Injection Points, Cleaning: -opened bypass valve and isolated inlet/outlet header to remove injection points -common inlet/outlet analyzer lost flow from 10:16 to 11:35 causing total chlorine LO, LOLO, OOR and fault alarms 11:01 - collected grab from outlet, total chlorine = 3.56 mg/L -cleaned and flushed injection points -disinfected, reinstalled and returned system to normal operation -completed CL-17sc Analyzer, Maintenance: 11:57 - 12:19 - analyzers in clean mode -cleaned analyzer cells, flushed sample lines -verified analyzers after maintenance: 12:35 - common inlet/outlet TCL analyzer = 3.49 mg/L 12:35 - common inlet/ outlet grab: TCL = 3.50 mg/L 12:39 - post injection TCL analyzer =3.81 mg/L 12:39 - post injection grab: TCL = 3.74 mg/L -completed Sodium Hypochlorite Pump, Maintenance: -pump #2 OOS -completed drawdown on pump #1 - max flow = 133 ml/min -completed Low Temperature Alarm, Test -completed Inlet/Outlet Heat Trace System, Inspection -completed Outlet Heat Trace System, Inspection -completed Gasoline Generator, Test Run -completed JHSC Health and Safety Inspection -no issues, site back to normal operation -while on site hydro power fail occurred, transferred site to generator power | Schomberg Elevated Tank | 2025-12-17
WEST | December | -on site to complete station check and to collect samples - tower draining at 27.7 l/s, level = 32 % -hypo pump #2 OOS - reviewed trends - CL17 reagents ok - checked equipment -recorded readings in PWQ sheet - no issues found -verified analyzers: 10:40 - common inlet/outlet TCL analyzer = 3.58 mg/L 10:40 - common inlet/ outlet grab: FCL = 0.06 mg/L TCL = 3.54 mg/L Mono = 2.95 mg/L 10:47 - collected weekly micro sample - W/O # W11470016 10:49 - post injection TCL analyzer = 4.55 mg/L 10:49 - post injection grab: TCL = 4.48mg/L | Schomberg Elevated Tank | 2025-12-22
WEST | December | -on site to complete station check and to collect sample for in house lab analysis -hypo pump #2 OOS - tower draining at 27.7 l/s, level = 42% - reviewed trends - CL17 reagents ok - checked equipment -recorded readings in PWQ sheet - no issues found -verified analyzers: 10:00 - post injection TCL analyzer = 3.51 mg/L 10:00 - post injection grab: TCL = 3.60 mg/L 10:10 - common inlet/outlet TCL analyzer = 3.56 mg/L 10:10 - common inlet/ outlet grab: FCL = 0.00 mg/L TCL = 3.58 mg/L Mono = 3.07 mg/L | Schomberg Elevated Tank | 2025-12-19
EAST | December | Under the supervision of Patrick Fobert, Restarted the GWTP Local server to add tags for High lift pump 4 at 10 AM. ROC was informed about the work and all high lifts were put in manual off. Historian Hrbt alarm was generated due to this and High lifts were interlocked. Need to restart iFix for few times to check all the modified screens and networked sites. After the work, Alarms were cleared and High lift were put back in Auto around 11 AM. | Georgina Water Treatment Plant | 2025-12-15
EAST | December | On site for monthly maintenance: Informed ROC of work to be done Reviewed MIT and daily failter performance on all trains - all passed and within range, recorded readings in PWQ sheets Yash from PCs needs to do a GWTP local server updtae for high lift pump #4 (new) Deactivated system duty @10:06 for him to complete his work. Reactivated duty 1 @11:10, after Yash completed his work - Completed chlorine Tonner change with Phil DeGroot - changed right chlorine tonner. Tested for leaks after change, no issues. (Caused chlorinator 5 high vacuum alarms GAC 3 Manual backwash: - Placed GAC 3 OOS @11:39 - Closed inlet valve and began draining filter to clearwell (Caused GAC 3 lo and lolo level alarms, as well as GAC 1 / 4 high alarms as a result of the Inlet channel going high with GAC 3 OOS) - @12:40 started backwash pump #2 in manual - While the GAC was filling to 4.75 m after backwash. There was a comms fail on SCADA. Locally stopped backwash pump, and closed GAC3 backwash inlet valve. Comms restored @13:04. Placed equipment back to remote manual - Stopped filter to waste @15:00, placed GAC back into service - NTU is 0.223 - Backwash complete Adjusted Chlorinator #5 dosage factor from 56 to 54% to lower treated chlorine residuals a bit Reviewed trends, station ok | Georgina Water Treatment Plant | 2025-12-15
EAST | December | On site for station check and weekly micro sampling (W11438589) Duty is active - KSTKWP level - 81% - Temporarily increased duty stop from 85 to 90% to allow more time for station check and sampling Reviewed MIT and daily filter performance on all membrane trains - all passed and within range - readings in PWQ sheets Verified analyzer readings with grab chlorine residuals: Keswick Treated: @10:27 Grab free: 1.93 mg/L / Analyzer: 1.90 mg/L Grab total: 2.24 mg/L / Analyzer: 2.23 mg/L Sutton Treated @10:30 Grab free: 1.93 mg/L / Analyzer: 1.93 mg/L Grab total: 2.22 mg/L / Analyzer: 2.37 mg/L - adjusted based on grab residual Made the following other adjustments to chlorine analyzers: CC #1 adjusted from 1.80 mg/L to 1.97 mg/L CW #1 adjusted from 1.83 mg/L to 1.93 mg/L CW #2 adjusted from 1.88 mg/L to 2.04 mg/L Post clearwell adjusted from 1.85 to 1.99 mg/L Collected Micro samples @10:38 (Raw and treated) Collected weekly GLIP samples Complated in-house lab analysis on raw, permeate, and treated waters - see Lab data sheets @11:56 - Duty rotated post chlorinators (Clearwell) Placed chlorinator #5 to ON and chlorinator #6 to OFF @11:58 - Duty rotated Raw water sampling pumps - Placed P3 to D1, @12:01 - Swapped clearwell chlorine ejectors (Swapped from the right ejector to the left one) Observed chlorinator operation after ejector swap - all okay Duty rotated air compressors - placed BOGE to lead duty Duty deactivated @12:25 - tower level reached 90%. Reverted duty stop setpoint back to 85% Enabled M-cleans on trains #6,7,8 - they were disabled last week for maintenances work on the SBS system Reviewed trends, equipment OOS: Sludge P3 Low lift: Raw water chlorine analyzers - old and new analyzers running concurrently Station ok | Georgina Water Treatment Plant | 2025-12-10
EAST | December | Checked low lift station's operation. Station readings are in PWQ sheet. Changed LLP dut2 band from 190-210 l/s to 230-250 l/s. After the change, only LLP2 is running in duty. Will monitor LLP performance. 10:53 keswick header grab chlorine residual FCL = 1.60 mg/l, analyzer = 1.60 mg/l TCL = 1.88 mg/l, analyzer = 1.84 mg/l. 10:56 Sutton header grab chlorine residual FCL = 1.60 mg/l, analyzer = 1.59 mg/l TCL = 1.85 mg/l, analyzer = 1.83 mg/l. 11:09 post clear well grab chlorine FCL = 1.66 mg/l, analyzer = 1.55 mg/l. 11:12 standardized analyzer reading according to 3 grabs' average. Tested the redundant SV on post chlorination with each SV service to its own ejector. No issues observed. | Georgina Water Treatment Plant | 2025-12-12
EAST | December | Increased plant flow from 200 to 220 L/s as KSTP is off for the night. | Georgina Water Treatment Plant | 2025-12-11
EAST | December | ZW7 - CIP inlet valve failed to open @10:40 - ack / reset alarm and the valve opened. No further issues | Georgina Water Treatment Plant | 2025-12-14
EAST | December | On site for station check and equipment verifications Reviewed MIT and daily filter performance on all membrane trains - all passed and within range - recorded station readings in PWQ sheets GAC #4 manual backwash - Closed inlet valve to GAC4 @10:07, and placed GAC OOS on the filtration page - Manually drained filter to clearwell to 3.0 m - @10:35 closed effluent valve, GAC level is 3.04 m. Opened drain valve and backwash inlet valve - @10:37 started backwash pump #1 - Backwash completed, started filter to waste @11:11 - Stopped filter to waste @11:46, placed GAC 4 back in service - NTU is 0.093 - Recieved Sodium Bisulfite delivery Start: 0.27 cm Stop: 0.93 cm @13:50 - adjusted chlorinator #5 dosage factor from 57 to 56% - will monitor clearwell resiudal Conducted testing the Dan Z on the clearwell chlorine solenoid valves (1 and 2). Valved the chlorine lines so that all of the ball valves on the gas lines / service water lines are open. Except for the interconnect valve between the two service water lines. Chlorine solenoid valves are valved to individual ejectors now, Valve 1 to ejector 1, valve 2 to ejector 2. Can now swap chlorine trains remotely, with all valving in place. Monitored rotameter during the testing and observed no changes in chlorine dosing. Will continue to monitor Reviewed trends, equipment OOS: None Station ok | Georgina Water Treatment Plant | 2025-12-12
EAST | December | On site for monthly maintenance PM's - Informed ROC we are on site and work to be done Duty is active while on site - plant flow is 180 L/s Reviewed MIT and daily filter performance on all membrane trains - all passed and within range - readings in PWQ sheets Low lift station: - Turbidimeter maintenance from 08:55 to 09:15 - Chlorine analyzer maintenance from 08:55 to 09:15 - JHSC Health and safety inspection - Chlorine leak test in low lift basement - Low lift pump FCV's inspections - Sampling pumps greased - Mussel plate inspection - Ran travelling screen sequence - no issues Main Plant: - Flood alarms / Chemical containment leak alarms (Hypo, SBS) - SO2 / SBS room gas leak alarms test - Chlorine leak alarms test - chemical room @09:25, tonner / chlorinator rooms @09:30 - Chlorine scrubber inspection - SO2 emergency kit inspection - JHSC Health and safety inspection - Chemical system inspection chlorine @11:10 - Increased plant flow from 180 to 200 L/s Station operation normal | Georgina Water Treatment Plant | 2025-12-11
EAST | December | On site for station check, lab analysis and data collection Reviewed MIT and daily filter performance on all trains - all passed and within range Assisted ETO / Lexsan with isolating clearwell #2 / suction well for high lift pumps, by closing the interconnect valve between HL pumps 2 and 3 @09:40. No work ended up occuring in the clearwell for the HL pump 4 installation. Only piping work above the clearwell was completed today. Reopened interconnect valve @14:35. Will be isolating the interconnect valve again tomorrow Completed PWQ sheets and data collection - Duty rotated air compressors - placed KAESER compressor to D1 - Duty rotated low lift sampling pumps - placed P3 to D1 - Completed Low lift station check and analyzer verifications Equipment OOS: Sludge P3 Station ok | Georgina Water Treatment Plant | 2025-12-01
EAST | December | On site for maintenance Supervised contractor ETO and Lexan install high lift pump 3 impeller and riser with clearwell isolation valve closed. Witnessed adequate disinfection of equipment Performed loaded generator test run, recorded observations in logbook Performed review of MIT log, verified MIT and membrane met required specifications Station and equipment okay | Georgina Water Treatment Plant | 2025-12-02
EAST | December | On site for station check and lab 08:08 Completed MIT review - all trains passed 08:10 Reviewed filter membrane performance - all meet specified requirements 08:30 Began recording observations in the station PWQ sheet 10:29 Activated plant duty 10:35 Hi lifts activated 11:37 Completed lab Verified chlorine analyzers (Grab/Analyzer, in mg/L) Contact tank 1, 11:45, 2.19/2.17 Contact tank 2, 11:46, 2.50/2.09 - adjusted Clearwell 1, 11:49, 1.58/1.56 Clearwell 2, 11:50, 1.42/1.35 Post clearwell, 11:53, 1.99/1.79 - adjusted East sedimentation tank, 12:01, 0.02/0.06 West sedimentation tank, 12:01, 0.01/0.01 Keswick header free Cl, 12:06, 1.96/2.02 Keswick header total Cl, 12:06, 2.30/2.27 Sutton header free Cl, 12:14, 1.88/1.92 Sutton header total Cl, 12:14, 2.16/2.26 Washwater to lake, 12:20, 0.02/0.03 12:23 Completed station PWQ sheet and reviewed SCADA 13:55 ZW3 M-Clean insufficient chemical alarm - informed PCS on call Chris Scott, he will attend SCADA 14:03 Test running M-Clean on ZW3 with Chris Scott 14:30 Appears M-Clean insufficient chemical alarm was caused by an interruption in communication - will monitor, cleared alarm Station and equipment okay | Georgina Water Treatment Plant | 2025-12-05
EAST | December | Out hi lift pumps in manual at 08:10 due to deer park ET isolation and drain. | Georgina Water Treatment Plant | 2025-12-02
EAST | December | Reviewed November monthly filtration results. All trains within monthly critieria. | Georgina Water Treatment Plant | 2025-12-01
EAST | December | Reviewed MIT and daily filter performance on all trains - all passed. Low lift analyzers both new and old are running concurrently. At 08:25 opened backwash clear well permeate valve to fill the backwash clear well tank. At 08:40 closed the back wash clear well permeate valve due to GAC inlet being at 1.01m. Back wash clear well is currently at 4.11m. At 09:21 put UVs and hi lift pumps in manual off in preperation for UV calibration. At 09:27 opened up drain valve on the UV lines and also put all valves to local closed. Informed ROC at 09:29 of work being performed. At 09:58 turned power off to the UV system. At 11:04 turned power back on to both UV systems. At 11:22 receiving hypo delivery for hypo tank top up. Beginning UV calibration at 11:31. UV1 and 2 calibrations passed and UV system back to normal at 13:00. All the valves for the UV system have also been put back to normal. Starting Train and GAC NTU calibration and maintenance at 13:25. No issues with work that was complete and everything has been put back to normal. | Georgina Water Treatment Plant | 2025-12-09
EAST | December | On site to complete station check and in house lab analysis. Reviewed MIT and daily filter performance on all trains - all passed. Low lift analyzers both new and old are running concurrently. At 11:00 informed TL that the plant needs a Sodium Bisulphate order. At 11:10 cleared low lift surge relief valve alarm will inform team this alarm is still coming in. Time: 12:28 Keswick Grab (mg/l) Analyzer (mg/l) Free: 1.81 1.89 Total: 2.15 2.22 Time: 12:30 Sutton Grab (mg/l) Analyzer (mg/l) Free: 1.90 1.90 Total: 2.18 2.20 Time: 12:20 Hi Lift Grab (mg/l) Analyzer (mg/l) Free: 1.90 1.81 Time: 12:34 Out to Lake Grab (mg/l) Analyzer (mg/l) Free: 0.03. 0.05-0.03 at 12:34 adjusted the pitfall to lake analyzer free reading, from 0.05mg/l to 0.03mg/l after multiple grabs were taken. Entered data into PWQ sheet for lab and station check. | Georgina Water Treatment Plant | 2025-12-08
EAST | December | On site for monthly maintenance: Informed ROC of work to be completed - UV system maintenance and cleaning - removed sleeves and lamps for cleaning and inspections. No issues - UV system calibrations - calibrated UV 1 and UV2 with Phil Degroot. No issues with calibrations. - Placed UV valves back to auto - UV reactors remain in remote manual while other plant maintenance is being completed - Permeate and membrane trains turbidity analyzer maintenance and calibrations - cleaned trains 1 thru 8 and permeate common header analyzers - Calibrated GAC turbidimeters (1 thru 4) - Placed UVs and High lifts back to auto @14:40 - cleared all alarms associated with PM's completed today - Plant operation is normal, duty is currently not active | Georgina Water Treatment Plant | 2025-12-09
EAST | December | On site with Patrick Fobert for station check Completed lab work and recorded results in the shared spreadsheet Verified chlorine and fluoride analyzers and recorded grabs in the shared spreadsheet Reviewed MIT log and verified all trains meet requirements Station and equipment okay | Georgina Water Treatment Plant | 2025-12-01
EAST | December | On site for station check, lab analysis and data collection: And to collect weekly micro samples (W11419221), monthly algae samples (W11419356), and monthly THM samples (W11419043). Reviewed MIT and daily filter performance on all trains - all passed and within range. Recorded readings in PWQ sheets Troubleshooted with train #5 backpulse valve - causing higher than normal MIT values. Adjusted close limit and close speed. Ran multiple backpulses on the train after adjustment. Initiated MIT @09:57 to test. Slightly improved numbers than this morning, but all passed. Will troubleshoot more another day Observed small air leak on BOGE air compressor near the oil separators Completed PWQ plant rounds and Lab data sheets Collected samples @11:06 - Micro, monthly algae and VOC samples Collected weekly GLIP samples Verification of chlorine analyzers: Treated Residuals (Keswick) @11:06 Free grab: 1.64 mg/L / Analyzer: 1.61 mg/L Total grab: 1.94 mg/L / Analyzer: 1.86 mg/L Sutton: @11:10 Free grab: 1.70 mg/L / Analyzer: 1.60 mg/L - adjusted based on grab residual Total grab: 1.91 mg/L / Analyzer: 1.98 mg/L Made the following other adjustments to analyzers: Contact #1 @11:22: Adjusted from 2.74 to 2.86 mg/L based on multiple grabs Contact #2 @11:26: Adjusted from 1.41 to 1.51 mg/L based on multiple grabs Clearwell #1 @11:37: Adjusted from 1.94 to 2.08 mg/L based on multiple grabs Washwater chlorine analyzer maintenance - between 11:35 - 12:00. Generator washwater cl2 residual high alarms (ROC called to inform) Alarm was generated during cleaning. Tested generator / transfer @13:55 to 14:11 - had issues starting yesterday for monthly test, electricans advised to run again today to make sure everything starts okay - no issues. Ack/Res alarms generated from generator transfer. Reviewed trends, equipment OOS: Sludge P3 Station ok | Georgina Water Treatment Plant | 2025-12-03
EAST | December | On site for station check, lab analysis and data collection Reviewed MIT and daily filter performance on all trains - all passed and within range Assisted ETO / Lexsan with isolating clearwell #2 / suction well for high lift pumps, by closing the interconnect valve between HL pumps 2 and 3 @09:40. No work ended up occuring in the clearwell for the HL pump 4 installation. Only piping work above the clearwell was completed today. Reopened interconnect valve @14:35. Will be isolating the interconnect valve again tomorrow Completed PWQ sheets and data collection - Duty rotated air compressors - placed KAESER compressor to D1 - Duty rotated low lift sampling pumps - placed P3 to D1 - Completed Low lift station check and analyzer verifications Equipment OOS: Sludge P3 Station ok | Georgina Water Treatment Plant | 2025-12-01
EAST | December | Will be working on SBS line to get it ready for new dice block to be installed. Generator activated and alarms cleared at 11:58. SBS is not being completed today other work needs to be completed before lines are flushed on site. No other issues. | Georgina Water Treatment Plant | 2025-12-02
EAST | December | Reviewed MIT and daily filter performance on all trains - all passed. Low lift analyzers both new and old are running concurrently. At 10:28 opened GAC back wash clearwell tank to fill for back wash on GAC next week. At 10:41 closed backwash clear well valve to allow for inlet channel to recover. Completing the following work orders: W11418922 Citric Acid Feed System Inspection. W11419694 Visual Inspection Chemical Lines. W11440532 CL2 Emergency Repair Kit Inspection. W11442012 Clear well Drain Pump Inspection. W11442021 Clear well Drain Valve Exercise. W11448032 SO2, NH3 Leak Detector Test. W11415274 Hi lift Pump and Motor Inspection. W11416935 CL2 Analyzer Maintenance Clear well/CT Tanks. W11416810 CL2 Analyzer Maintenance Permeate/CIP. Deactivating both Keswick and Sutton duties at 10:50 to complete the above work orders. At 10:52 put all hi lift pumps and UVs in manual off. From 10:55-11:00 initiated alarms on clear well chlorine analyzers. Deactivating m-clean for train 4 at 12:09 due to hypo level not reading which means, hypo cannot be dosed for the m-clean to occur. Created work order for instrumentation to come take a look at it. Worked with PCS from 12:44 to 13:08 to correct issue, m-clean for train 4 is back in service at 13:09. Work order for instrumentation has been cancelled. Completed analyzer maintenance, verified analyzers. Time: 13:16 CT1 Grab (mg/l) Analyzer (mg/l) Free: 1.98. 2.39-1.98 after multiple grabs were taken adjusted the CT1 from 2.39mg/l to 1.98mg/l at 13:16. Time: 13:18 CW1 Grab (mg/l) Analyzer (mg/l) Free: 2.20 2.25 Time: 13:19 CT2 Grab (mg/l) Analyzer (mg/l) Free: 1.39 1.42 Time: 13:21 CW2 Grab (mg/l) Analyzer (mg/l) Free: 1.20 1.21 Time: 13:23 Hi Lift Grab (mg/l) Analyzer (mg/l) Free: 1.76 1.78 Reactivated duty for Keswick and Sutton at 13:34. At 13:52 switched hi lift pump duty 1 from pump 1 to pump 3. No issues with work orders being completed. | Georgina Water Treatment Plant | 2025-12-04
EAST | December | On site to assist with station check and lab. Ran through how to drain SBS line when completing the SBS chemical board transfer. At 13:55 transferred to test generator if it would transfer no issues with transfer and generator is operating normally. Generator switched back to utility without issue at 14:11. | Georgina Water Treatment Plant | 2025-12-03
EAST | December | train 5 shut down on header isolation valve fail to open. Reset the alarm, place the train in standby. Train 7 and 8 shut down alarm came in. Cleared the alarm, place the trains in standby. Test Sutton header free chlorine hi alarm. | Georgina Water Treatment Plant | 2025-12-17
EAST | December | Exercised train #1 backpulse valve in manual. It was left off overnight. Still failed to open. Placed train #1 to on and initiated MIT | Georgina Water Treatment Plant | 2025-12-18
EAST | December | On site for station check, lab analysis and weekly micro sampling (W11483538) Reviewed MIT and daily filter performance on all membrane trains - all passed and within range - recorded readings in PWQ sheets Attempted to exercise backpulse tank #1 fill valve @10:39 - it failed to open. On call Op had experienced issues with it over the holiday break. Duty rotated clearwell chlorinators @11:30, placed chlorinator #5 to D1. Switched clearwell solenoid valve from #2 to #1 Duty rotated raw water sampling pumps - placed P3 to D1 Completed washwater and water to lake analyzer maintenance - cleaned cl2 analyzers and TSS probe - no issues Verified analyzers in basement: Contact tanks, clearwells, treated, residual management Grab / Analyzer (Mg/L) @12:13 CT#1: 2.01 / 1.94 @12:15 CT#2: 2.13 / 2.19 @12:18 CW#1: 1.77 / 1.66 - Adjusted to 1.77 based on grab residuals @12:20 CW#2: 1.54 / 1.50 @12:24 Post CW: 1.85 / 1.63 - Adjusted to 1.85 based on grabs @12:33 Keswick Free: 1.81 / 1.86 @12:33 Keswick Total: 2.06 / 2.06 @12:30 Sutton Free: 1.79 / 1.75 @12:30 Sutton Total: 2.09 / 2.08 Collected weekly micro samples @12:40 (Raw and Treated) Completed PWQ sheets, data collection and lab data sheets Exercised backpulse tank fill vlave #2 again. Found that the actuator body itself was moving while the valve was trying to open. Found that the bolts holding the actuator on the valve were loose. Tightened bolts, exercised valve locally and on SCADA, opened and closed okay. Placed vlave back to auto, in duty 2 Reviewed trends Equipment OOS: Sludge P3, Bisulfite P2 Station ok | Georgina Water Treatment Plant | 2025-12-29
EAST | December | On site for station check, equipment verifications Reviewed MIT and daily filter performance on all membrane trains - all passed and within range, recorded data in PWQ sheets Reviewed trends on membranes, UV, treated - no abnormalities @10:00 - Placed Train #2 to OFF and initiated Acid Recovery clean - Had to manually injection portion of the citric acid due to a ball valve left closed on the citric acid board. All okay Keswick / Sutton Header fluoride Lolo alarms came in @10:15 - Low fluoride caused by train #2 tank filling from treated water for Acid Clean @11:51 - Particle counter 1/2 alarms - disregard, units not used anymore. Cleared alarms Verifification of basement analyzers - Contact tanks, Clearwells, Treated and Residual management: - Adjusted CT #2 from 1.63 to 1.75 mg/L FCL - Adjusted Post Clearwell from 1.99 to 1.89 mg/L FCL - Completed Treated Header (Keswick and sutton analyzer maintenance and verifications: Keswick: @12:04 FCL: Grab: 1.82 mg/L / Analyzer: 1.83 mg/L TCL: Grab: 2.08 mg/L / Analyzer: 2.06 mg/L Sutton: @12:09 FCL: Grab: 1.81 mg/L / Analyzer: 1.76 mg/L TCL: Grab: 2.07 mg/L / AnalyzerL 2.07 mg/L @13:00 - Verified Citric acid concentration for Train #2 acid clean is within range - pH = 3.28 Equipment OOS: Sludge P3, Bisulfite P2 Station operation normal | Georgina Water Treatment Plant | 2025-12-24
EAST | December | Grease motors | Georgina Water Treatment Plant | 2025-12-16
EAST | December | ROC informed of train 7 PSW fill valve (PV1B) fail to open. Reviewed SCADA and reset alarm, the valve opened. Train 7 is going through a M clean, step 8. | Georgina Water Treatment Plant | 2025-12-30
EAST | December | Reviewed MIT and daily filter performance on all membrane trains - all passed and within range. Recorded readings into PWQ sheets - Activated system duty @09:02, controlling ET @64% | Georgina Water Treatment Plant | 2025-12-31
EAST | December | Reviewed daily and monthly filter performances. Recorded results in PWQ, no issues. Activated plant duty. Controlling ET is 58%. | Georgina Water Treatment Plant | 2025-12-25
EAST | December | ROC informed train 7 M-Clean aborted and ?backpulse flow lolo alarm. Noticed the back pulse tank level is low at 0.6m. Tank 1 was in lead duty. Tested tank 1 fill valve, it failed to open. Leave it in man/off.? Switch to tank 2. Topped up the back pulse tank.? Initiated train 1 backwash to test the system. Initiated train 7 m-clean.? Train 7 CIP fill valve (PV1B) failed to open, exercised it a few times and it opened.? | Georgina Water Treatment Plant | 2025-12-26
EAST | December | On site for station check, lab analysis and to collect weekly micro samples (W11469988) Reviewed MIT and daily / monthly filter performance on all membrane trains - all passed and within range - recorded readings into PWQ sheets Initiated Recovery Clean Hypo on Train #2 @09:00 - it has the highest TMP numbers of all trains, and has had reoccuring TMP alarms recently - Observed that Keswick head fluoride is reading higher than normal at 0.97 mg/L. Duty was just activated @09:02, plant will start soon. Placed Fluoride pumps 1/2 to manual off while the plant starts, will place pumps back to auto once fluoride level drops. Placed fluoride pumps back to auto @09:18. P1 started. - Completed Low lift station check and mussel plate inspection. Verified low lift analyzers. Duty rotated raw water sampling pumps - placed P1 to D1. @09:45 - Activated Sutton ET duty - tower level is 69%. Cleared fluoride low alarm - Duty rotated clearwell chlorinators @10:12 - Placed Chlorinator #6 in D1. Also rotated Clearwell Solenoid valve from #1 to #2. Inspected Rotameter / Ejector performance. No issues observed - Duty rotated air compressors - placed BOGE compressor in lead duty - Collected first grab sample from train #2 recovery clean @10:40: Cl2 = 440 mg/L, pH = 9.98 Verifications of basement chlorine analyzers: (Grab / Analyzer reading) @11:42 Contact #1: 2.09 mg/L / 2.01 mg/L @11:45 Contact #2: 2.04 mg/L / 1.96 mg/L @11:47 Clearwell #1: 1.83 mg/L / 1.71 mg/L - Adjusted based on grab residual @11:52 Clearwell #2: 2.52 mg/L / 2.44 mg/L Post Clearwell: 2.00 mg/L / 1.52 mg/L - Adjusted based on grab residual @12:12 Keswick Free: 1.97 mg/L / 2.01 mg/L @12:12 Keswick Total: 2.20 mg/L / 2.25 mg/L @12:18 Sutton Free: 2.01 mg/L / 1.94 mg/L @12:18 Sutton Total: 2.34 mg/L / 2.29 mg/L Collected Raw and Treated micro samples @12:26 (YD #W11469988) - Collected second grab sample from train #2 recovery clean @12:30: Cl2 = 450 mg/L, pH = 9.70 - @12:40: Adjusted Keswick Header fluoride from 0.77 mg/L to 0.63 mg/L - Completed Plant PWQ sheets and data collected, chemical dosages all okay - Completed Lab data sheets for Raw and Treated headers - Cleaned citric acid tank and containment area to prepare for citric acid recovery cleans. Prepared citric acid solution for R-clean tomorrow Reviewed trends, no abnormalities observed Equipment OOS: Bisulfite P2, Sludge P3 Station ok | Georgina Water Treatment Plant | 2025-12-22
EAST | December | Reviewed daily and monthly filter performances. No Conerns. Activated plant duty. Controlling ET is 54%. | Georgina Water Treatment Plant | 2025-12-30
EAST | December | Initiated MIT on train #2 @07:58. MIT passed: High: 10.87 kpa, Low: 3.72 kpa | Georgina Water Treatment Plant | 2025-12-23
EAST | December | Received call from ROC at 11:10 about Back Pulse valve failing. Was able to clear the alarm and put train off then on again between 11:20 and 11:55. No other issues noticed. | Georgina Water Treatment Plant | 2025-12-20
EAST | December | On site responding to back pulse system issue. CMU5 W11529194 Back Pulse System Lock Out After duty had started and plant was running back pulse system seems to have corrected itself. At 14:11 put train 3 into neutralization mode due to it soaking with hypo during maintenance clean. Disabled all maintenance cleans for all trains for the rest of the weekend. At 14:12 turned train 4 off than on again due to issues with back pulse system train 4 is back in standby. Also there were NTU fault alarms that came in on trains 1-4 was able to clear those alarms. Also changed the back pulse control level selection from tank 2 to tank 1. Will monitor while off site. | Georgina Water Treatment Plant | 2025-12-20
EAST | December | On site for station check, weekly micro sampling (W11454815) and in-house lab analysis Reviewed MIT and daily filter performance on all trains - all passed and within range - recorded readings into PWQ sheets Reviewed trends, no abnormalities observed Operational adjustments: Adjusted Clearwell dosage factors to reduce chlorine residuals for winter: - Chlorinator #5 = 54% - Chlorinator #6 = 55% - Duty rotated air compressors - placed Kaeser compressor to lead duty - Duty rotated sampling pumps at Low lift - placed P2 to D1 @11:58 - Completed washwater / water to lake analyzer cleanings Recieved Sodium Hydroxide delivery - 32 full containers, 30 empty returned Topped up Sodium hydroxide day tank Completed plant PWQ sheets and data collection Assisted Mechanical (Lee) with rotating low lift and high lift pump duties so he can grease the pumps while they are running (Between 10:00 and 10:32) Verification of chlorine analyzers: Contact tanks, clearwells, treated, wash/waste. See Lab data sheets for full grabs/analyzers. Made the following adjustments: @11:02 - Adjusted Post clearwell free from 1.78 to 1.93 mg/L Keswick Treated @11:12 (Grab/Analyzer) Free: 1.88 mg/L / 1.91 mg/L Total: 2.18 mg/L / 2.20 mg/L Sutton Treated @11:18 (Grab/Analyzer) Free: 1.89 mg/L / 1.89 mg/L Total: 2.17 mg/L / 2.17 mg/L Collected raw and treated samples @11:33 (YD# W11454815) Collected weekly GLIP samples Train #7 Recirculation inlet valve / CIP valve failed to open @10:55, Caused M-clean exceed duration alarms @11:50. Ack/reset alarm and the valve opened. Will investigate valve after m-clean is done System duty deactivated @12:40 Worked with maintenance to drain Sodium Bisulfite line for their tie in of the new chemical board tomorrow. Placed SBS pumps and SV to manual off and drained chemical fully from the lines. Caused SBS pump not available alarms. Informed ROC Activated duty again @15:22 - KSTKWP level - 58% Equipment OOS: Sludge Pump 3 Station ok | Georgina Water Treatment Plant | 2025-12-16
EAST | December | Boge air compressor Replace all 3 1/4 inch tubing and 1/4 inch fitting Tested no leaks | Georgina Water Treatment Plant | 2025-12-17
EAST | December | Increased fluoride pump 1 dosage factor from 1.09 to 1.14. ? | Georgina Water Treatment Plant | 2025-12-30
EAST | December | On site for monthly maintenance - Informed ROC of work to be completed Manual backwash of GAC #2: - Closed inlet valve and began draining GAC 2 to clearwell @08:35 - Placed GAC 2 OOS on the filtration page - Started backwash P1 @09:18. Opened Backwash clearwell fill valve MV1 to fill backwash clearwell. - Backwash P1 stopped @09:41 - backwash complete - @09:44 UV and filters started to fill GAC inlet channel again, placed Train 1 and 2 to demand override to help fill the backwash clearwell / inlet channel - Opened inlet gate valve and started filter to waste (FTW) @10:16. Placed Train 3 to demand override to keep up with filling BW clearwell and inlet channel during FTW - Closed BW clearwell MV1 @10:55 once the clearwell was to 6.0 m - Stopped FTW @11:07 - NTU is 0.161 - Placed GAC 2 back in service @14:59 UVT analyzer dehumidifier change out @09:24 - Caused UVT hi, UV 1/2 minor fault and warning alarms. Alarms cleared, no further issues Worked on compressed air small leak near BOGE compressor with Lee from maintenance. Caused air pressure low and lolo alarms, and various alarms on the membrane trains. Leak was fixed. - Compressed air system inspection - Air compressor maintenance - Air dryer checks - Aeration blower maintenance - Permeate / Backpulse pumps maintenance / inspection. CMS greased the pumps yesterday, performed visual / audible inspection only - Housekeeping / floor cleaning in basement Disabled M-cleans for trains 1-4 tomorrow to allow the new SBS board and piping to cure overnight. Will test and prime chemical system tomorrow morning Observed a small air leak on train #5 permeate valve - exercised valve in local and manual, no further issues and air leak stopped Reviewed trends, equipment ok Station ok | Georgina Water Treatment Plant | 2025-12-17
EAST | December | Reviewed daily and monthly filter performances. Recorded results in PWQ, no issues. Activated plant duty. Controlling ET is 55%. | Georgina Water Treatment Plant | 2025-12-26
EAST | December | eviewed MIT and daily filter performance on all trains - all passed. Low lift analyzers both new and old are running concurrently. Completing in house lab analysis. No issues with the lab. Alarms are from the hi lift 4 commissioning. Will be purging the SBS line to make sure it is safe for the mechanics to work on. SBS board is fully drained and ready for mechanics to work on it. | Georgina Water Treatment Plant | 2025-12-16
EAST | December | Reviewed MIT and daily filter performance on all trains - all passed. Low lift analyzers both new and old are running concurrently At 11:14 Ack and Reset CIP valve failed to open alarm, M clean is able to finish. At 11:55 hypo is being topped up start: 0.74m stop: 1.21m At 12:05 turned train 2 back on, which cleared outstanding alarms on the train. Air Unit 1 alarm came in was able to ack and reset on air panel by the chemical room. Topped up caustic tank Start: 60L Stop: 100L Replaced hypo pump 1 discharge coupling due to it being broken and leaking. | Georgina Water Treatment Plant | 2025-12-23
EAST | December | Reviewed MIT and daily filter performance on all trains - all passed. Low lift analyzers both new and old are running concurrently. At 08:21 put hi lift pumps in manual at KWTP. At 08:25 cleared NTU faults on GAC 3 and 4. At 08:26 activated duty for Sutton and Keswick. At 09:09 back pulse valve for train 1 failed to open causing train to shut down, train has been switched off and valve is in manual at 09:10. This is an ongoing issue that will be investigated. Time: 10:13 Keswick Grab (mg/l) Analyzer (mg/l) Free: 1.79 1.83 Total: 2.06 2.03 Time: 10:15 Sutton Grab (mg/l) Analyzer (mg/l) Free: 1.71 1.75 Total: 2.04 2.06 Time: 10:05 Hi Lift Grab (mg/l) Analyzer (mg/l) Free: 1.70 1.77 Time: 09:54 CW1 Grab (mg/l) Analyzer (mg/l) Free: 1.98. 2.32-1.98 after multiple grabs were taken adjusted the CW1 free analyzer from 2.32mg/l to 1.98mg/l at 09:58. At 13:58 SBS pumps have been primed 3 and 3/4 turn for the PRV and 2 1/2 turn for the discharge pressure. Discharge pressures have been set to 20psi and the PRVs have been set to 50psi for both pumps. Pump 2 is OOS due to over pressurizing the system while running to drain that was at 14:45. Initiating m clean to see how system reacts at 14:47. At 15:43 enabled trains 1-4 m cleans. | Georgina Water Treatment Plant | 2025-12-18
EAST | December | Train 2 finished acid r clean. Initiated MIT, it passed. Pressure decays are: 10.67kpa (hi) and 2.53kpa(low). Placed train 2 in standby. | Georgina Water Treatment Plant | 2025-12-24
EAST | December | -on site to move the SBS chemical board and pumps to the new location. Operations isolated system and was aware of our work starting at 0900. Electrical finished the removal of old wiring and placing pumps into their new location. Mechanical finished the piping installation. My self and Ernesto completed the wiring and confirmed that the pumps turn on. Ops will monitor tomorrow when they do their tests. Under direction of oic. | Georgina Water Treatment Plant | 2025-12-17
EAST | December | On site to complete following work orders: W11436979 Spectrophotometer Verification W11408674 Lab Reagents Inventory Replace W11410695 Hypo Pump Insp. W11410708 SBS Pump Insp. W11410721 NAOH Pump Insp. W11416901 Cl2 Sed Tank and Outfall to lake analyzer maintenance. W11470664 GAC2 Backwash Alarms coming in throughout the day are due to VFD commissioning for pump 4. At 11:18 cleared low lift pump 2 uncommanded open alarm. At 11:21 maintenance is working on compressed air system fixing a leak alarms are coming in these can be disregarded. Compressors are fixed and back up and running at 11:34. At 11:42 started NTU verification on Keswick and Sutton lines. ROC has been informed of work being completed here today. Activated duty at 14:31. | Georgina Water Treatment Plant | 2025-12-17
EAST | December | Train #2 and 8 TMP alarms are active - Cause is that there is only 4 trains available. Train #1 and 4 were off overnight, and train #6 in M-clean. Reduced Plant flow to 150 L/s @10:45 Placed train #4 to MIT @10:42 - it was left off after M-clean last night Exercised Train #1 backpulse valve (Its been off for a few days) Increased the open speed setting - was able to open in in manual a few times. Placed train into MIT, it pended Train #4 - Passed: 4.49 kpa / 1.34 kpa Train #1 - Passed: 2.27 kpa / 1.34 kpa Trains 1 and 4 placed back to ON Increased plant flow to 180 L/s @12:34 | Georgina Water Treatment Plant | 2025-12-19
WW-CEAST | December | On site completed work orders. Station Check (See details on SharePoint). All pumps available in all-stop auto duty rotation. Pump 1 currently running in auto as duty 1 with 51 L/s flow at 331 kPa. Standby power generator available in auto. Station operations normal. Air Relief Valves Inspection RS Pumps Inspection Pump 1 - @ 0% speed, 35 L/s, 312 kPa, 46 A, 527 V, 55 Hz, 1639 RPM: @ 50% speed, 51 L/s, 331 kPa, 57 A, 551 V, 58 Hz, 1711 RPM Pump 2 - @ 0% speed, 40 L/s, 317 kPa, 48 A, 527 V, 55 Hz, 1639 RPM: @ 50% speed, 55 L/s, 338 kPa, 59 A, 551 V, 58 Hz, 1710 RPM Pump 3 - @ 0% speed, 40 L/s, 318 kPa, 49 A, 527 V, 55 Hz, 1639 RPM: @ 50% speed, 55 L/s, 338 kPa, 57 A, 550 V, 58 Hz, 1711 RPM Pump 4 - @ 0% speed, 40 L/s, 316 kPa, 48 A, 527 V, 55 Hz, 1639 RPM: @ 50% speed, 55 L/s, 338 kPa, 58 A, 551 V, 58 Hz, 1711 RPM Check Valves Inspection | Aurora Henderson Sewage Pumping Station | 2025-12-12
WW-CEAST | December | -On site to perform a station check. -Entered station readings into SharePoint. -Checked generator and valve room. -Station in PAC mode due to LIT1 fluctuations. -FM interconnect valve fault outstanding. | Aurora Henderson Sewage Pumping Station | 2025-12-15
WW-CEAST | December | On site completed work orders. RS Pump Discharge Valves Actuator Inspection and Exercise Manual Valves Exercise Comprehensive Housekeeping - cleaned/vacuumed/mopped floors. Sanitized/disinfected washroom. Collected garbage. | Aurora Henderson Sewage Pumping Station | 2025-12-02
WW-CEAST | December | On site completed Station Check (See details on SharePoint). All pumps available in all-stop auto duty rotation. Pump 2 currently running in auto as duty 1 with 55 L/s flow at 341 kPa. Standby power generator available in auto. Station operations normal. | Aurora Henderson Sewage Pumping Station | 2025-12-08
WW-CEAST | December | Weather: -6 C Cloudy Wind: 4 km/h from N On site completed work orders. Station Check (See details on SharePoint). All pumps available in all-stop auto duty rotation. Pump 3 currently running in auto as duty 1 with 55 L/s flow at 336 kPa. Station operations normal. JHSC Health and Safety Inspection - all eye wash stations alarms received by ROC. Dry Well Flood Alarm Test - alarm received by ROC. High/Low Temperature Alarm Test - all alarms for INFO. Hazardous Waste Collection and Removal Standby Power Generator Test Run - pre-test checked, ok. Generator started and stopped running without problem. Cleared/reset all alarms. Generator back in auto and available. After generator test ran, the Interconnect Valve (RSP_FM1_MV2) faulted in an open position (normally open valve) that won?t clear/reset. On SCADA, valve is showing in auto but in actual, the actuator is in local mode with no power. Switch breaker at the Lighting Panel 1 is ON. Created work order #W11479996 for CMS to check power source. | Aurora Henderson Sewage Pumping Station | 2025-12-01
WW-CEAST | December | On site completed Station Check (See details on SharePoint). All pumps available in all-stop auto duty rotation. Pump 2 currently running in auto as duty 1 with 57 L/s flow at 341 kPa. Standby power generator available in auto. Station operations normal. | Aurora Henderson Sewage Pumping Station | 2025-12-05
WW-CEAST | December | Restarted the Operator Interface Terminal due to Video Driver updates. this is being done to fix a memory leak. | Aurora Henderson Sewage Pumping Station | 2025-12-16
WW-CEAST | December | On site for Station Check (See details on SharePoint). All pumps available in all-stop auto duty rotation. Pump 1 currently running in auto as duty 1 with 52.9 L/s flow at 339 kPa. Standby power generator available in auto. Checked valve room/dry well. Station operations normal. No outstanding alarms. | Aurora Henderson Sewage Pumping Station | 2025-12-22
WW-CEAST | December | On site completed work orders. Wet Well High Level Alarm Test - received and confirmed by ROC (Christian V.B.) Wet Well Inspection and Cleaning Wet Well Valves Exercised | Aurora Henderson Sewage Pumping Station | 2025-12-18
WW-CEAST | December | -on site to address boiler fault, causing multiple low pressure alarms and low temp alarms on the glycol system -boiler had a few faults on the control panel/display -was able to reset these alarms and get the boiler running again in auto -monitoring SCADA to watch system run before leaving -temps are increasing and low pressure alarms have cleared -glycol reservoir seems low -station okay | Aurora Henderson Sewage Pumping Station | 2025-12-20
WW-CEAST | December | On site completed work orders. Station Check (See details on SharePoint). All pumps available in all-stop auto duty rotation. Pump 2 currently running in auto as duty 1 with 55.6 L/s flow at 336 kPa. Standby power generator available in auto. Station operations normal. Odour Control Scrubber System Inspection - mist eliminator filter and 12? x 24? x 1? filter clean. | Aurora Henderson Sewage Pumping Station | 2025-12-19
WW-CEAST | December | On site for Station Check (See details on SharePoint). All pumps available in all-stop auto duty rotation. Pump 4 currently running in auto as duty 1 with 50.8 L/s flow at 333 kPa. Standby power generator available in auto. Checked valve room/dry well. Station operations normal. | Aurora Henderson Sewage Pumping Station | 2025-12-29
WW-CEAST | December | -Remotely assisting NAC with Recirculation Pump and bubble damper testing. Aecom, Promation, and EB Air also on site for testing. -1224 - Placed Fan 2 in manual off and Train 2 OOS. -Contractors repaired Damper 2 and 4 deficiencies and functionality was tested, including during power loss scenarios. -1327 - Placed Fan in manual off, Train 1 OOS. -Contractors repaired Damper 1 and 3 deficiencies and functionality was tested, including during power loss scenarios. -Damper 3 would not open in auto with Fan 1 running in manual, or even if Fan 1 was in auto, but the Speed Control Setpoint was in manual. -Dampers 1-4 all working normally when dampers and fans are in auto. Dampers 1 and 2 now failing closed and fully closing following a power loss or fault. -1452 - Also tested entire facility during power loss and transfer to generator power. Confirmed alarms must be cleared before Fans will turn back on under generator power. Specifically the Fan VFD Faults and Inlet Damper Faults must be cleared. -1504 - Station back on utility power. -Remote testing completed for the day, contractors remaining on site to work on Electrical/Mechanical room dampers and air flow, as well as makeup air unit. Contractors also working on Process Room Exhaust Fan 2. | Oak Ridges Air Management Facility | 2025-12-10
WW-CEAST | December | On site for Station Check (See details on SharePoint). Fans 1 and 2 both running in auto. Recirculation pump 2 at Bioscrubber System Unit 2 out of service and taken out of site by contractor for repair. Nutrient tank batch mixing - tank filled up to 3/4 and added nutrient. Standby power generator available in auto. | Oak Ridges Air Management Facility | 2025-12-15
WW-CEAST | December | -Remotely assisting NAC and air technician with MAU troubleshooting. Cycled power and tested various speed Setpoints. -Discovered timer for Failed to Start Alarm is far too short, with the MAU faulting out before it can heat up enough to turn on. | Oak Ridges Air Management Facility | 2025-12-12
WW-CEAST | December | On site with NAC (Jamie) to troubleshoot train 1 recirc pump no flow/low pressure alarm. Found recirc pumps interlock/OFF on above alarms and alarm would not clear on scada. Ran recirc pumps in local to overcome the alarm setpoint -> clear the alarm. Tested both recirc pumps and they are producing 3.2 l/s. Both train 1 recirc pumps still make rattling noise while running. Biorem is aware and repair in progress. Found 2 sensor/gauge not working. CARBSYSPDIT2 and manual gauge after Fan 2. Reported to NAC and CD team. | Oak Ridges Air Management Facility | 2025-12-03
WW-CEAST | December | -On site to assist with damper testing with Promation, NAC, CPD, and PCS remotely. -Train 2 turned off for damper testing. Damper 2 and 4 testing and inspection revealed that all damper actuators were missing capacitor require for function following a power loss. Actuators will all need to be repaired or replaced. -Placed dampers 2 and 4 back into service and returned Fan 2/Train 2 to service. | Oak Ridges Air Management Facility | 2025-12-04
WW-CEAST | December | At around 10:07am, remotely assisted contractors (NAC/Biorem). They will check/inspect recirculation pumps for Bioscrubber Unit 1. Fan 1 at Bioscrubber Unit 1 has been put in manual/off at 10:10am. At 13:05pm, put fan 1 back in auto and running. Recirculation pump 1 at Bioscrubber Unit 1 ran in auto. Facility back to normal operations. | Oak Ridges Air Management Facility | 2025-12-02
WW-CEAST | December | On site for Station Check (See details on SharePoint). Fans 1 and 2 both running in auto. Recirculation pump 2 at Bioscrubber System Unit 2 out of service and taken out of site by contractor for repair. Nutrient tank batch mixing - tank filled up to 3/4 and added nutrient. Standby power generator available in auto. | Oak Ridges Air Management Facility | 2025-12-08
WW-CEAST | December | On site for Station Check (See details on SharePoint). Fans 1 and 2 both running in auto. Damper 1 in auto. Damper 2 in local mode but 100% open. Recirculation pump 2 at Bioscrubber unit 2 out of service and taken out of site by contractor for repair. Nutrient tank at 1/2 full - filled up to 3/4 and added 1.5 bags of nutrient as per recommended. Standby power generator available in auto. | Oak Ridges Air Management Facility | 2025-12-01
WW-CEAST | December | Shut off Fan 2 @ 10:11am remotely as requested by NAC to troubleshoot issues on site Tested train 2 damper 2 without the fan running. Damper failed to modulate to set % open in manual. Jamie from NAC tested the power-fail scenario with train 2 damper 2. Damper failed to close on powerfail and no alarm outstanding on SCADA about this damper. Issue need to be further looked at by NAC. Jamie from NAC noted significant rattling sound coming from train 1 recirc pump 1. I placed it OOS so the issue can be looked at, and put pump 2 in lead duty instead. NAC informed me that the building exhaust fan 1 has been fixed, I placed it back it auto and NAC reported that it is now running as intended | Oak Ridges Air Management Facility | 2025-12-01
WW-CEAST | December | -called by Jose Oliviera to test recirculation system on fan 2 -air locking issues with pumps causing low flow interlocks -eventually found an air leak on suction side of pumps, tightened valves and fixed issue -both recirculation pumps on system 2 are working now -had to run pumps local on multiple times to fix issues -tested system multiple times and it is okay -reviewed scada before leaving -both fans are running and recirculating pumps are working -station okay | Oak Ridges Air Management Facility | 2025-12-22
WW-CEAST | December | On site for Station Check (See details on SharePoint). Fans 1 and 2 running in auto. Nutrient tank batch mixing - tank filled up to desired level. Standby power generator available in auto. | Oak Ridges Air Management Facility | 2025-12-29
WW-CEAST | December | On site for Station Check (See details on SharePoint). Fan 1 running in auto. Put Fan 2 in local/out of service. CPD (Joe Oliveira) and contractor re-piping the lines for recirculation pumps on Train 2 (Bioscrubber Unit 2) due to high vibration. Also, put Recirculation Pumps 1 and 2 in local/out of service. Nutrient tank batch mixing - tank filled up from 5/8 to 3/4 level. Standby power generator available in auto. | Oak Ridges Air Management Facility | 2025-12-22