## Operational Issues
PERSONGROUP | LOGBOOK_MONTH | LDTEXT | DESCRIPTION | EVENTDATE
WW-NORTH | January | Onsite for daily operations Review scada/trends Decant stt 1 and 3 plus transfer Collect in lab samples Collect weekly regulatory samples Complete lab enter data in sharepoint Check station Hose membranes 3 and 5 Turbidimeter maintenance Switch barscreen duty. Screen 1 in duty 1 | Keswick Water Resource Recovery Facility | 2026-01-21
WW-NORTH | January | on site 0700hrs sludge handling. WAS now feeding STT3. station checks lab and readings. tightened leaky flange going to aeration tank 1. pumped down scum tanks. work table set up in membrane area. | Keswick Water Resource Recovery Facility | 2026-01-23
WW-NORTH | January | Switched WAS feed to sludge thickening tank 1. | Keswick Water Resource Recovery Facility | 2026-01-31
WW-NORTH | January | Program hypo and acid clean on train 1 Looking into CIP neutralization issue Complete lab and enter data into SharePoint Plant checks completed Level grit bin and rake bar screens Re set channel blower and clean intake Reset sludge heat trace pad | Keswick Water Resource Recovery Facility | 2026-01-26
WW-NORTH | January | Restarted the KSSP Local SCADA server due to Windows updates. Notified the Remote Operations Center. | Keswick Water Resource Recovery Facility | 2026-01-22
WW-NORTH | January | plant checks completed level grit bin rake bar screen tidy up membrane room completed lab and enter data into SharePoint pumped down scum tanks OCU checks sludge handling completed | Keswick Water Resource Recovery Facility | 2026-01-29
WW-NORTH | January | on site 0700hrs sludge handling. Batch waste into STT1. WAS now feeding STT3 station checks lab and readings. | Keswick Water Resource Recovery Facility | 2026-01-19
WW-NORTH | January | Performed sludge handling | Keswick Water Resource Recovery Facility | 2026-01-18
WW-NORTH | January | Complete lab and enter data into SharePoint Grease and inspect bar screen 2 Hypo and acid clean schedule tonight @ 7pm Top up NaOH day tank 5 car boys Plant checks Level grit bin Sludge hanging completed | Keswick Water Resource Recovery Facility | 2026-01-16
WW-NORTH | January | Onsite for daily operations Review scada/trends Decant stt 3 plus transfer Top up hypo tank Collect in house lab samples Complete lab Data in sharepoint UV janitorial Check station Level grit bin | Keswick Water Resource Recovery Facility | 2026-01-30
WW-NORTH | January | Onsite for daily operations Review scada/trends Decant stt 1 and 2 plus transfer Check station Rake and level bin Collect in house lab samples Complete lab Enter data in sharepoint Diesel test run Pump down both scum tanks during sludge transfer | Keswick Water Resource Recovery Facility | 2026-01-20
WW-NORTH | January | on site 0700hrs sludge handling. WAS now feeding STT3 station checks lab and readings DO verification topped up caustic soda, hypochlorite, and Hydrochloric acid tanks jockeyed Hydrochloric acid jugs into containment area. SCADA review | Keswick Water Resource Recovery Facility | 2026-01-27
WW-NORTH | January | on site 0700hrs sludge handling. Batch waste into STT1. WAS now feeding STT2 station checks lab and readings ocu maintenance turbidmeters inspections/maintenance Poor plowing on site, as per usual from contractor. topped up Hypo | Keswick Water Resource Recovery Facility | 2026-01-15
WW-NORTH | January | on site at 0700hrs sludge handling. WAS now feeding STT2 station check lab and readings weekly samples collected and delivered to Harry Walker Headworks screen room cleaned Tss probe maintenance Investigated chemical room for CIP neutralization not working properly due to freezing in room. Heaters added with extension chords running in room. Property services looking into it. Uv rotation alum board exercised. | Keswick Water Resource Recovery Facility | 2026-01-28
WW-NORTH | January | On site to look at permeate valve leaking air. Operated the valve and found no issues. Also changed the actuators on train 4-5 air scour lines. Line 1 has a small leak but we need to order a replacement | Keswick Water Resource Recovery Facility | 2026-01-30
WW-NORTH | January | continue hosing membranes clear duck from microscreen top up Cl2 day tank received Alum delivery plant checks completed complete lab and enter data into SharePoint verified DO probes hosed membrane room floor check air compressors clean TSS check OCU level grit bin rake bar screen Received captor delivery | Keswick Water Resource Recovery Facility | 2026-01-22
WW-NORTH | January | Onsite for sludge handling Receive call at 07:10hrs regarding train 2 shutdown and membrane blower 2 shutdown on lolo airflow. Reset train alarms - check trends and prime train 2 Monitor backwash sequence with no issues. Train 2 and membrane blower 2 back in service | Keswick Water Resource Recovery Facility | 2026-01-25
WW-NORTH | January | on site -0700hrs sludge handling. Batch waste into STT1. WAS feeding STT3 station checks lab and readings collected weekly samples and delivered to Harry Walker Headworks Grit vortex, dewatering press and screenings presses inspection Headworks gas detectors tested topped up Hydrochloric Acid tank | Keswick Water Resource Recovery Facility | 2026-01-14
WW-NORTH | January | batch waste into tank 1 decant and transfer sludge tank 3 complete lab and enter data into SharePoint check hoists clean TSS probe collect samples and deliver to Harry Walker check RAS,WAS and scum pumps hypo transfer | Keswick Water Resource Recovery Facility | 2026-01-07
WW-NORTH | January | on site 0700hrs sludge handling. Batch waste into STT1. transferred and now feeding STT2 station checks lab and readings. Drillers on site. blower inspections. | Keswick Water Resource Recovery Facility | 2026-01-13
WW-NORTH | January | Onsite for annual calibrations Informed operations Used cal mode on scada during the work Instruments calibrated: Sludge FIT, Hypo FIT, collection box LIT, plant effluent FIT and inlet channel TSS Cleared associated alarms Informed operations and left site | Keswick Water Resource Recovery Facility | 2026-01-12
WW-NORTH | January | Onsite for annual calibrations Informed operations and ROC Used cal mode on scada during the work Coordinated with operations for train availability Completed train 4 and most of train 2 only turbidity left to do Cleared associated alarms Informed ROC and operations Left site | Keswick Water Resource Recovery Facility | 2026-01-07
WEST | January | Onsite for station check Check trends- All okay Station duty active; pump 2 running. 10:00-verified analyzers Grab free Cl2-0.04 mg/L Analyzer free Cl2- 0.05 mg/L Grab Total Cl2- 1.53 mg/L Analyzer Total Cl2-1.59 mg/L Entered values in PWQ sheet Equipment okay. | Woodbridge East Booster Pumping Station | 2026-01-30
WW-NORTH | January | Started decanting S.T.T 2 and 3 Cleared fault on collection blower 1 Finished decanting S.T.T 2 and 3 Started transfer to S.T.T 2 and 3 Switch WAS feed to S.T.T 2 | Keswick Water Resource Recovery Facility | 2026-01-11
WW-NORTH | January | on site 0700hrs sludge handling. Batch waste into STT1 lab and readings station checks lowered alum dosage on pumps 1 and 2 from 65 to 60 mg/l programmed R-cleans Train #4 and #2 Exercised UV gate valves. Admin and odour control sumps inspected. sludge transfer pumps inspected. Reset Headworks collection box blower #2. OCU maintenance Generator building and membrane building compressor maintenance | Keswick Water Resource Recovery Facility | 2026-01-12
WW-NORTH | January | plant checks completed sludge handling completed batch waste into tank 1 completed lab and enter data into SharePoint flush Alum board with hot water Sump pump checks sludge loading pumps cleaned up around UV OCU check JH@S checks NAOH pump 1 operation ok create WO to change fuses in CIP heater | Keswick Water Resource Recovery Facility | 2026-01-08
WW-NORTH | January | Onsite for annual calibrations Informed operations and ROC Coordinated with operations for available membrane trains Used cal mode on scada Calibrated train 2 turbidity, train 5 instruments, backpulse LIT, CIP AITs Cleared associated alarms Informed operations and ROC Left site | Keswick Water Resource Recovery Facility | 2026-01-08
WW-NORTH | January | on site 0700hrs sludge handling station checks lab and readings citric system replumbed hypo topped up scum tanks pumped down membrane micro screens inspected | Keswick Water Resource Recovery Facility | 2026-01-09
WW-NORTH | January | Onsite for annual calibrations Informed operations and ROC Coordinated train availability with operations Used cal mode on scada during the work Completed train 3 instruments Completed Headworks Influent FITs Replaced aeration basin inlet DO air clean/purge hose Cleared associated alarms Informed operations and ROC Left site No issues | Keswick Water Resource Recovery Facility | 2026-01-09
WW-NORTH | January | Onsite for daily operations Review scada/trends Decant stt 2 and 3 Collect in house lab samples Compressor and dryer maintenance Conplete lab -data in sharepoint Check station Rake and level bin DO probe maintenance Chemical containment float checks Ran portable generator Hose trains 2,3,4 Chlorine analyzer maintenance Membrane sump inspection | Keswick Water Resource Recovery Facility | 2026-01-06
WW-NORTH | January | Onsite for annual calibrations Informed operations. Informed operations and ROC Used cal mode on scada during the work Instruments calibrated: Chemical LITs and Odour control gas detectors Cleared associated alarms Informed ROC and operations Left site | Keswick Water Resource Recovery Facility | 2026-01-06
WW-NORTH | January | Switched WAS feed to sludge thickening tank 1 Restarted membrane train 2 after it shutdown overnight. | Keswick Water Resource Recovery Facility | 2026-01-01
WW-NORTH | January | Received call from ROC regarding membrane train 3 shutdown - no available blowers Restarted train 3 and cleared blower alarms. | Keswick Water Resource Recovery Facility | 2026-01-01
WW-NORTH | January | Received call from ROC regarding membrane train 3 shutdown - membrane blower 2 went OOS on low air flow resulting in no available blowers Restarted train 3 and observed it complete a backwash. | Keswick Water Resource Recovery Facility | 2026-01-01
WW-NORTH | January | Adjusted pH fine injection setpoint from 6.5 to 6.3. | Keswick Water Resource Recovery Facility | 2026-01-05
WW-NORTH | January | Onsite for annual calibrations Informed operations and ROC Used cal mode on scada during the calibrations Instruments calibrated: Diesel fuel LITs and Headworks and Grit room Gas detectors. Could not get in to the odour control room. Neither door would open Informed operations and ROC then left site | Keswick Water Resource Recovery Facility | 2026-01-05
WW-NORTH | January | Onsite for daily operations Review scada/trends Decant stt 1 and 2 plus transfer Collect in house lab samples Complete lab - data in sharepoint Check station Rake and level bin Lowered alum dosage on both tanks from 70mg/L down to 65mg/L Maintenance adjust limits on aeration inlet valve for train 3 Clean caustic injection point | Keswick Water Resource Recovery Facility | 2026-01-05
WW-NORTH | January | Performed station check Decanted and transferred STT 1 and 2 Completed lab analysis and entered readings into SharePoint Checked head works building - cleared bar screen and checked bins Received Hypo delivery - Large temporary tank and day tank were topped up Cleared ice off of blower exhaust vents - Reset channel blower fault Manually closed damper in membrane blower room. Programmed recovery cleans on membranes 2, 4 and 5 | Keswick Water Resource Recovery Facility | 2026-01-02
WW-NORTH | January | Reset train 3 shutdown. | Keswick Water Resource Recovery Facility | 2026-01-02
WW-NORTH | January | Received call from ROC regarding CIP neutralization taking too long alarm Aborted neutralization and restarted the process but that did not solve issue Adjusted fine injection pH setpoint from 6.5 to 6.4 - it appeared that pH was the parameter preventing neutralization from completing (stationary at 6.5) Monitored neutralization - after another cycle, the solution was discharged to the drain tank Returned pH setpoint back to 6.5. | Keswick Water Resource Recovery Facility | 2026-01-02
WW-NORTH | January | Onsite for annual calibrations Informed ROC and operations Operations placed train 1 to OFF for me Performed maintenance on NIT and calibrated Calibrated FIT and PIT. PIT reconfigured to show PV in kPa Calibrated UVD FIT 1 and 2 as well as CIP FIT PEFF_FIT1 has electronic issues. Will create follow up w/o. Informed operations Cleared associated alarms Informed operation and ROC Left site | Keswick Water Resource Recovery Facility | 2026-01-02
WW-NORTH | January | Switched WAS feed to sludge thickening tank 1 Restarted train 3 (to complete its backwash) which had shut down over night, then returned to off Noticed during SCADA check that CIP neutralization is still taking too long - the chlorine residual is adequate but pH is not reaching the setpoint. Tried increasing the caustic injection time but no change in pH occurred. Changed the medium injection from 6.0 to 5.8 and fine injection from 6.5 to 5.9 so the remaining R-cleans could proceed. | Keswick Water Resource Recovery Facility | 2026-01-03
WW-NORTH | January | Attended for sludge handling Decanted/transferred sludge thickening tanks Switched WAS feed to sludge thickening tank 2 Checked bar screen and raked bin Ran train 3 for a cycle and membrane blower 2 faulted during backwash, returned train status to off and notified ROC Switched active NaOH pump to p.2 (pump on the right) and returned pH setpoints to 6.0 and 6.5 (medium and fine injection). | Keswick Water Resource Recovery Facility | 2026-01-04
WEST | January | Onsite for station check Check trends- All okay Station duty not active 09:30-verified analyzers Grab free Cl2-0.03 mg/L Analyzer free Cl2- 0.04 mg/L Grab Total Cl2- 1.36 mg/L Analyzer Total Cl2-1.39 mg/L Entered values in PWQ sheet W11585377- Washroom light cleaning & supplies check complete. Equipment okay. | Woodbridge East Booster Pumping Station | 2026-01-26
WEST | January | Onsite for station check Check trends- All okay 08:45-verified analyzers Grab free Cl2-0.04 mg/L Analyzer free Cl2- 0.04 mg/L Grab Total Cl2- 1.45 mg/L Analyzer Total Cl2-1.43 mg/L Entered values in PWQ sheet Equipment okay. | Woodbridge East Booster Pumping Station | 2026-01-23
WEST | January | Onsite for scheduled PM workorders below.informed ROC about the works being done. W11517655 VNPSAP, JHSC Health and Safety Inspection W11516691 VNPSAP, Sump Pit System, Inspection W11518328 VNPSAP, Check Valve Service & Inspection W11518345 VNPSAP, Flood Alarm, Test W11518366 VNPSAP, Low Temperature Alarm, Test W11516634 VNPSAP, Hoist System, Inspection W11516848 VNPSAP, Siemens Depolox 5 Maintenance 13:55-verified analyzers Grab free Cl2-0.02 mg/L Analyzer free Cl2- 0.06 mg/L Grab Total Cl2- 1.51 mg/L Analyzer Total Cl2-1.54 mg/L | Woodbridge East Booster Pumping Station | 2026-01-20
WEST | January | Onsite for station check Check trends- All okay 10:05-verified analyzers Grab free Cl2-0.02 mg/L Analyzer free Cl2- 0.04 mg/L Grab Total Cl2- 1.53 mg/L Analyzer Total Cl2-1.49 mg/L Entered values in PWQ sheet Equipment okay. | Woodbridge East Booster Pumping Station | 2026-01-12
WEST | January | Onsite for station check Check trends- All okay 10:25-verified analyzers Grab free Cl2-0.01 mg/L Analyzer free Cl2- 0.04 mg/L Grab Total Cl2- 1.40 mg/L Analyzer Total Cl2-1.45 mg/L Entered values in PWQ sheet Equipment okay. | Woodbridge East Booster Pumping Station | 2026-01-19
WEST | January | Checked/troubleshoot sump pump and flood alarm float switches. Found faulty flood alarm float switch, changed/replaced float switch. Tested ok | Woodbridge East Booster Pumping Station | 2026-01-12
WEST | January | Details: Onsite for station check Check trends- All okay 11:05-verified analyzers Grab free Cl2-0.05 mg/L Analyzer free Cl2- 0.04 mg/L Grab Total Cl2- 1.54 mg/L Analyzer Total Cl2-1.54 mg/L Entered values in PWQ sheet Equipment okay. | Woodbridge East Booster Pumping Station | 2026-01-15
WEST | January | Onsite for station check Check trends- All okay 09:40-verified analyzers Grab free Cl2-0.02 mg/L Analyzer free Cl2- 0.06 mg/L Grab Total Cl2- 1.49 mg/L Analyzer Total Cl2-1.54 mg/L Entered values in PWQ sheet Equipment okay. | Woodbridge East Booster Pumping Station | 2026-01-09
WEST | January | Onsite for station check Check trends- All okay 13:20-verified analyzers Grab free Cl2-0 mg/L Analyzer free Cl2- 0.05 mg/L Grab Total Cl2- 1.68 mg/L Analyzer Total Cl2-1.59 mg/L Entered values in PWQ sheet Equipment okay. | Woodbridge East Booster Pumping Station | 2026-01-05
WEST | January | On site for station check. Pumps in auto Verified analyzer readings Free 0.04mg/L Total 1.37mg/L Grab Free 0.05mg/L Total 1.42mg/L No issues on site | Woodbridge East Booster Pumping Station | 2026-01-02
WEST | January | On site for Station Check, W11539194 Micro Sampling Check Trends: All Okay Tower Draining (65%) 13:10- Grabs Taken FCL- 0.01 mg/L TCL- 1.64 mg/L Samples Taken. Entered Values in PWQ sheet. Equipment Okay | Woodbridge East Elevated Tank | 2026-01-21
WEST | January | Onsite for scheduled PM workorders below.informed ROC about the works being done. W11517665 VNETAG,JHSC Health and Safety Inspection W11516621 VNETAG, Sump Pit System, Inspection W11516660 VNETAG, Manual Valve, Exercise W11517903 VNETAG, Actuated Valve, Exercise & Inspection W11518218 VNETAG, Low Temperature Alarm, Test W11518628 VNETAG, Portable Gasoline Generator, Test W11516610 VNETAG, Dehumidifier, Inspection & Cleaning | Woodbridge East Elevated Tank | 2026-01-20
WEST | January | On site for Station Check, W11551636 Micro Sampling Check Trends: All Okay Tower Draining (40%) 08:20- Grabs Taken FCL- 0.02 mg/L TCL- 1.83 mg/L Samples Taken. Entered Values in PWQ sheet. Equipment Okay | Woodbridge East Elevated Tank | 2026-01-28
WEST | January | On site for Station Check, W11504620 Micro Sampling & W11503287 VAUGHAN WATER, YWS Nitrification and Corrosion Control Operational Monitoring. Check Trends: All Okay Tower Draining (53%) 09:45- Grabs Taken FCL- 0.01 mg/L TCL- 1.52 mg/L Samples Taken. Entered Values in PWQ sheet. Equipment Okay. | Woodbridge East Elevated Tank | 2026-01-07
WEST | January | Onsite for annual calibrations Informed ROC Used cal mode on scada during the work Instruments calibrated: FIT, PIT and LIT Cleared associated alarms Informed ROC, armed building and left site | Woodbridge West Elevated Tank | 2026-01-28
WEST | January | On site for Station Check, W11523629 Micro Sampling & W11476022 Q1 water samples - YWS west east wood bridge ET Check Trends: All Okay Tower Draining (53%) 09:40- Grabs Taken FCL- 0.04 mg/L TCL- 1.69 mg/L Samples Taken. Entered Values in PWQ sheet. Equipment Okay. | Woodbridge East Elevated Tank | 2026-01-14
WEST | January | On site for Station Check, W11539194 Micro Sampling VAUGHAN WATER, YWS Nitrification and Corrosion Control Operational Monitoring. Check Trends: All Okay Tower Filling 14:25- Grabs Taken FCL- 0.02 mg/L TCL- 1.55 mg/L Samples Taken. Entered Values in PWQ sheet. Equipment Okay. | Woodbridge West Elevated Tank | 2026-01-21
WEST | January | On site for the following workorders with T. Hudson Informed ROC about the works being done W11539749 VNETFD, JHSC Health and Safety Inspection Inspection Complete, nothing to report W11539684 VNETFD, High & Low Water Level Alarm, Test Alarms tested, Test passed, cleared alarm W11539692 VNETFD, Actuated Valve, Exercise Valve exercised, working fine. W11539708 VNETFD, Sump Pit System Inspection Inspection Complete, nothing to report W11540035 VNETFD, Low Temperature Alarm, Test Alarms tested, Test passed, cleared alarm W11540452 VNETFD, Manual Valve, Exercise Valve exercised, working fine. W11540544 VNETFD, Portable Gasoline Generator Ran generator. Topped up fuel. W11540501 VNETFD, Inspection Form Air release valve, flood alarm, tower isolation valve and sump pump all working and in good condition | Woodbridge West Elevated Tank | 2026-01-22
WEST | January | On site for Station Check, W11504620 Micro Sampling & W11503287 VAUGHAN WATER, YWS Nitrification and Corrosion Control Operational Monitoring. Check Trends: All Okay Tower Filling (73%) 11:05- Grabs Taken FCL- 0.01 mg/L TCL- 1.42 mg/L Samples Taken. Entered Values in PWQ sheet. Equipment Okay. | Woodbridge West Elevated Tank | 2026-01-07
WEST | January | On site for Station Check, W11551636 Micro Sampling Check Trends: All Okay Tower Draining (57%) 09:40- Grabs Taken FCL- 0.04 mg/L TCL- 1.50 mg/L Samples Taken. Entered Values in PWQ sheet. Equipment Okay. | Woodbridge West Elevated Tank | 2026-01-28
WEST | January | On site for Station Check, W11523629 Micro Sampling & W11476078 Q1 water sample - YWS West west woodbridge Check Trends: All Okay Tower Filling (54%) 10:45- Grabs Taken FCL- 0.09 mg/L TCL- 1.47 mg/L Samples Taken. Entered Values in PWQ sheet. Equipment Okay. | Woodbridge West Elevated Tank | 2026-01-14
WW-CEAST | January | Onsite for CMU5. Screen room frozen, water pipe burst and sprayed water on surge tank LITs. LITs not responding Accompanied OIC into screen room. Used some heat to defrost LIT impulse lines. Flushed impulse lines. LITs reading back to normal. Cleared associated alarms. Removed surge tanks from maintenance mode. Placed RSP?s duties back to auto. Monitored for a short time. All ok Informed ROC and left site This is the second year in a row that this issue has occurred. System should be reviewed | Newmarket Sewage Pumping Station & Equalization Tank | 2026-01-18
WW-CEAST | January | On site completed consolidated monthly dry well pump floor inspection. Auto Dialer Alarm Test - still not received by ROC. Reported to Supervisor/Team Lead. At around 11:30am, Bell technician on site to check the phone line. At 12:40pm, Bell technician fixed the dialer. He found the issue at the Bell pedestal. Tested - alarm received and confirmed by ROC. Dry Well Flood Alarm Test - received and confirmed by ROC. Sump Pit Inspection High Low Temp Alarm Test - currently on alarm due to cold air going inside the building. Air Compressor Inspection Check Valve Inspection RS Pump and Motor Inspection Pump 1 - @ 0% speed 150 L/s, 137 kPa, 118 A, 625 V, 39 Hz; @ 25% speed 226 L/s, 166 kPa, 134 A, 625 V, 44 Hz; @ 35% speed 279 L/s, 166 kPa, 170 A, 624 V, 46 Hz Pump 2 - @ 0% speed 237 L/s, 116 kPa, 123 A, 384 V, 798 RPM, 40 Hz; @ 25% speed 246 L/s, 170 kPa, 143 A, 431 V, 896 RPM, 45 Hz; @ 100% speed 538 L/s, 164 kPa, 251 A, 573 V, 1192 RPM, 60 Hz Pump 3 - @ 0% speed 142 L/s, 137 kPa, 115 A, 371 V, 769 RPM, 39 Hz; @ 25% speed 232 L/s, 140 kPa, 156 A, 424 V, 878 RPM, 44 Hz; @ 35% speed 256 L/s, 165 kPa, 174 A, 445 V, 921 RPM, 46 Hz. Pump 4 - @ 0% speed 223 L/s, 131 kPa, 130 A, 624 V, 39 Hz; @ 25% speed 192 L/s, 204 kPa, 173 A, 624 V, 44 Hz; @ 35% speed 379 L/s, 140 kPa, 204 A, 623 V, 46 Hz. | Newmarket Sewage Pumping Station & Equalization Tank | 2026-01-20
WW-CEAST | January | On site completed Station Check (See details on SharePoint). All pumps available in timed auto duty rotation every 3 hours. Currently, pump 3 is running in auto as duty 1, with a flow of 277.7 L/s at 35% auto speed minimum setpoint and at 142 kPa. Standby power generator available in auto. Checked dry well, ok. Checked bar screens. Levelled rags from the bin. Switched rag bin. Cleaned screen room of rags. Building Hi/Lo Temperature Alarm outstanding due to cold weather. HVAC BAS System General Alarm still outstanding. Station operations normal, as intended. | Newmarket Sewage Pumping Station & Equalization Tank | 2026-01-26
WW-CEAST | January | Onsite for annual calibrations Informed ROC Used cal mode on scada during the work Instruments calibrated: Wet well LITs Bar screen LITs NMS 1 LIT Issues resetting the dialer panel. Seems to have cleared for now Informed ROC and left site | Newmarket Sewage Pumping Station & Equalization Tank | 2026-01-21
WW-CEAST | January | On site completed Station Check (See details on SharePoint). All pumps available in timed auto duty rotation every 3 hours. Currently, pump 3 is running in auto as duty 1, with a flow of 246.7 L/s at 35% auto speed minimum setpoint and at 147 kPa. Standby power generator available in auto. Checked dry well, ok. Checked bar screens. Levelled rags from the bin. Cleaned screen room of rags. Pushed rag bins back inside the screen room after picked up by Miller Waste yesterday, with the help of K. Shaji and C. Rodie. HVAC BAS System General Alarm still outstanding. Station operations normal, as intended. | Newmarket Sewage Pumping Station & Equalization Tank | 2026-01-23
WW-CEAST | January | On site assisted Property Services Staffs with the Wet Well Audible Fire Alarm Test. | Newmarket Sewage Pumping Station & Equalization Tank | 2026-01-16
WW-CEAST | January | On site completed work orders. Station Check (See details on SharePoint). All pumps available in timed auto duty rotation every 3 hours. Standby power generator available in auto. Checked dry well, ok. Checked bar screens. Levelled rags from the bin. Switched rag bin. Bar screen bin removal and replacement- pushed out rag bins, with the help of D. Kim. Miller Waste will pick up tomorrow. Cleaned screen room. Air compressors cleaning and inspection. | Newmarket Sewage Pumping Station & Equalization Tank | 2026-01-21
WW-CEAST | January | On site to check pump 1 RTD fault. Found RTD 6 for motor windings failed high. Turned off fault for RTD 6 on multilin relay. Fault has been reset, test ran pump 1 with the help of operations, pump ran without fault. Pump 1 is to be left off but is available to run if needed in an emergency. After checking all the wiring connections, RTD 6 reading returned to normal. Enabled RTD 6 faults on multilin. Asked operations to put pump1 back in auto duty for testing. If RTD 6 fault happens again we will come back and disable fault and leave pump 1 in off and for emergency use only. | Newmarket Sewage Pumping Station & Equalization Tank | 2026-01-28
WW-CEAST | January | On site completed Station Check (See details on SharePoint). All pumps available in timed auto duty rotation every 3 hours. Standby power generator available in auto. Checked dry well, ok. Checked bar screens, ok. | Newmarket Sewage Pumping Station & Equalization Tank | 2026-01-16
WW-CEAST | January | on site in response to surge tank hihi/lolo alarms, all pumps unavailable due to inhibit. Upon arrival, found wet well emergency ventilation running along with the normal ventilation which caused cold outside air to blow into the screen room. Also found water pipe burst next to the bay door which sprayed over the surge tank level sensors and froze them. Immediately shut off emergency ventilation fan. Put both surge tanks in maintenance bypass mode to clear the inhibits on the pumps. Placed the pump back in auto and monitoring the surge tank level to see if level sensors would come back to life. Called ROC to call INST on-call as these sensors need to be checked. Rick (INST) on-site to take a look at the sensor down in the wet well. Flushed out debris/ice from the sensor flushing port and sensors now reading normal values. Put both surge tanks back in service. Put all pumps back in service/auto. OFF/LOTO breaker switch for wet well emergency ventilation to prevent it from coming on again. | Newmarket Sewage Pumping Station & Equalization Tank | 2026-01-18
WW-CEAST | January | Onsite to complete remaining instrument calibrations Informed ROC Used cal mode on scada during the work Instruments calibrated: Discharge FIT and PIT Surge Tank LITs Gas detectors Generator LIT Cleared associated alarms Informed ROC and left site No issues upon leaving | Newmarket Sewage Pumping Station & Equalization Tank | 2026-01-22
WW-CEAST | January | Station Check completed (See details on SharePoint). All pumps available in auto duty rotation. Standby power generator available in auto. Checked dry well, ok. checked screen room. Switched rag bins out. | Newmarket Sewage Pumping Station & Equalization Tank | 2026-01-19
WW-CEAST | January | LOTO bar screen 1 Weld broken stationary bars back in place. Test run. Okay. | Newmarket Sewage Pumping Station & Equalization Tank | 2026-01-16
WW-CEAST | January | Station Check completed (See details on SharePoint). All pumps available in auto duty rotation. Standby power generator available in auto. Checked dry well, ok. Changed screen bins and flushed the drain screen and drain hose. Placed the bar screen bin outside for removal. Air compressors inspection completed. Everything looks normal | Newmarket Sewage Pumping Station & Equalization Tank | 2026-01-07
WW-CEAST | January | On site for Station Check (See entries on SharePoint). All pumps are available in timed-auto duty rotation every 3 hours. Standby power generator available in auto. Checked dry well, ok. Checked bar screens. Levelled rags from the bin. Cleaned screen room of rags. HVAC BAS System General Alarm still outstanding. Station operations normal, as intended. | Newmarket Sewage Pumping Station & Equalization Tank | 2026-01-30
WW-CEAST | January | On site checked Pump 1 multilin trip fault alarm reported by ROC, which happened at 2:24 am today. Found Pump 1 with RTD #6 temperature of 249 C before it tripped. Created work order request to CMS to check the problem. Left alarm as it is so that CMS will see the cause of multilin trip. | Newmarket Sewage Pumping Station & Equalization Tank | 2026-01-27
WW-CEAST | January | On site completed work orders. Station Check (See entries on SharePoint). Put pump 1 back in service after CMS troubleshoot the problem. Currently, pump 1 is running in auto as duty 1, with a flow of 253.1 L/s at 32% auto speed minimum setpoint and at 149 kPa. All pumps now are available in timed-auto duty rotation every 3 hours. Standby power generator available in auto. Checked dry well, ok. Checked bar screens. Levelled rags from the bin. Switched rag bin. Cleaned screen room of rags. Bar Screen Bin Removal and Replacement - rag bins pushed out for pick up by Miller Waste tomorrow. Air Compressors Cleaning and Inspection HVAC BAS System General Alarm still outstanding. Station operations normal, as intended. | Newmarket Sewage Pumping Station & Equalization Tank | 2026-01-28
WW-CEAST | January | On site completed work orders. Consolidated Wet Well Inspection: Wet Well High Level Alarm Test - received and confirmed by ROC. Facility Overflow Inspection Tipping Bucket Operational Checked - dewatered eq tanks afterwards. Sluice Gate Valve/Actuator Exercised Wet Well Valve Exercised Wet Well Inspection and Cleaning Bar Screen Cleaning/Lubrication Screw Conveyor Cleaning/Lubrication Consolidated monthly Surge Tank Inspection Surge Tank and System Inspection Surge Tank Drain Valve Inspection Transmission Lines Flushing Surge Tank Valve and Actuator Exercise and Inspection | Newmarket Sewage Pumping Station & Equalization Tank | 2026-01-13
WW-CEAST | January | Station Check completed(See details on SharePoint). All pumps available in auto duty rotation. Standby power generator available in auto. reset bar screen #2. tripped on over torque alarm. adjusted the torque sensor with Daniel. Checked dry well, ok. | Newmarket Sewage Pumping Station & Equalization Tank | 2026-01-09
WW-CEAST | January | On site completed Station Check (See details on SharePoint). All pumps available in timed auto duty rotation every 3 hours. Standby power generator available in auto. Checked dry well, ok. Checked bar screens, ok. | Newmarket Sewage Pumping Station & Equalization Tank | 2026-01-12
WW-CEAST | January | On in response to mech screen 1 overtorque alarm. Cleared the alarm, tightened the torque sensor arm and the nuts on the gearbox tension rod as it was found slightly loose. Ran it in L for 45 min, no issues observed. Mech screen 1 back in service | Newmarket Sewage Pumping Station & Equalization Tank | 2026-01-15
WW-CEAST | January | Weather today Overcast and -3 Celsius -On site to complete work order W11488939, W11489094, W11491214, W11491065, W11472967. -Completed station check. -Entered station readings into SharePoint. -Generator Test run completed and reset the alarms generated by generator test. -JHSC Health and Safety Inspection completed. -Hazardous Waste collection and removal. -Comprehensive Housekeeping. -Checked drywell, okay. -Checked screen room, changed out rag bin, cleaned floor and conveyor, bar screen oil full. -SCADA Review. | Newmarket Sewage Pumping Station & Equalization Tank | 2026-01-06
WW-CEAST | January | On site to put barscreen 1 back in service after the troubleshoot by CMS. Open the inlet gate and placed the unit back in service. Observed 3 cycles, no issue. | Newmarket Sewage Pumping Station & Equalization Tank | 2026-01-05
WW-CEAST | January | Checked barscreen 1 and found barscreen 1 is overtorqueing at top of travel checked drive chains and adjusted greased upper bearings ran barscreen, motor and gear box still move slightly but didn't trip the overtorque Still recommend repairing broken stationary bars at the bottom of the barscreen. | Newmarket Sewage Pumping Station & Equalization Tank | 2026-01-02
WW-CEAST | January | Station Check completed(See details on SharePoint). All pumps available in auto duty rotation. Standby power generator available in auto. Checked dry well, ok. inlet gate for Bar screen 1 closed, for maintenance to fix bar screen issues. | Newmarket Sewage Pumping Station & Equalization Tank | 2026-01-02
WW-CEAST | January | On site to replace the flow meter on pump 3. We will return in the morning to finish | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-01-19
WW-CEAST | January | Weather today Mostly cloudy and -6 Celsius -On site to complete work order W11527342. -Completed station check. -Entered station readings into SharePoint. -Pumps 2, 4, 5, and 6 available in timed auto duty rotation every 3 hours. -Pump 1 out of service due to discharge valve issue. -Pump 3 still in manual/duty 7 but has been primed and available if needed and can be ran remotely. -Standby power generators available in auto. -Checked dry well, Ok. -All lines available in auto at the dump pad for the haulers. -Checked bar screens and Rotated bin. -Cleaned bar screen room of rags and bar screen oil full. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-01-16
WW-CEAST | January | -On site to complete work orders W11515567, W11515567. -Diesel Generator 2 Annual Maintenance and load test. -Dump Pad Heat trace system Inspection. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-01-21
WW-CEAST | January | On site to assist contractor Total Power with Diesel Generator PM and load test on Generator 3. All alarms reset and all generators back in auto service. Notified ROC of work completed for the night. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-01-20
WW-CEAST | January | Weather today Partly Cloudy and -9 Celsius -On site to complete work order W11546438, W11549708, W11599777. -Completed station check. -Entered station readings into SharePoint. -Pumps 2, 3, 4, 5, and 6 available in timed auto duty rotation every 3 hours. -Pump 1 out of service due to discharge valve issue. -Standby power generators available in auto. -Checked dry well, Ok. -All lines available in auto at the dump pad for the haulers. -Checked bar screens and Rotated bin. -Cleaned bar screen room of rags and bar screen oil full. -Aurora East Forcemain trial isolation shutdown. -Closing and LOTO of valves to east forcemain to begin the trial isolation. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-01-28
WW-CEAST | January | On site to continue work with contractor Total Power on diesel generators. PM and Load Test on Generator 2. Informed ROC of work. Work completed for the day. Cleared all alarms and confirmed all generators back in auto service. Informed ROC work is done for the day. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-01-21
WW-CEAST | January | -on site for Aurora East Forcemain trial isolation shutdown -closing and LOTO of valves to east forcemain to begin the trial isolation -all pumps 1-6 east forcemain valves are closed and in local, both east forcemain surge valves are local closed and LOTO, common header east forcemain discharge valve is closed, and LOTO, east forcemain ISS discharge valve is closed and LOTO. -no flow is leaving AUSS from the east forcemain -points on SCADA also have east forcemain disabled | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-01-28
WW-CEAST | January | Weather today Overcast and -15 Celsius -On site to complete work orders W11545317, W11485176, W11485336, W11382000, W11549017, W11617770. -Diesel Generator 3 Annual Maintenance and load test. -Air compressors inspection and cleaning. -Air Dryer inspection and cleaning. -Hoist system inspection. -Odour control scrubber system inspection. -Dump Pad Lane 2 and Line 3 valved overtorque alarms W11617770. -Back flushed receiving lines #2 and #3 and cleared outstanding alarms. -All receiving lines available currently. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-01-27
WW-CEAST | January | Weather today Heavy Snow and -9 Celsius -On site to complete work order W11537204, W11381728, W11606515, W11536558, W11537666, W11552848, W11552833. -Completed station check. -Entered station readings into SharePoint. -Diesel Generator 2 Annual Maintenance and load test. -Replenish Sale bin at dump Pad. -Air Compressors inspection and cleaning. -Pumps 2, 4, 5, and 6 available in timed auto duty rotation every 3 hours. -Pump 1 out of service due to discharge valve issue. -Pump 3 still in manual/duty 7 but has been primed and available if needed and can be ran remotely. -Checked dry well, Ok. -All lines available in auto at the dump pad for the haulers. -Checked bar screens and Rotated bin. -Cleaned bar screen room of rags and bar screen oil full. -Bar Screen Bin Removal and Replacement - pushed rag bins out for pick up by Miller Waste. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-01-22
WW-CEAST | January | On site to replace the the flow tube on pump 3. Finish installing the tube and flooded the pump and left it in manual but is available to run if needed. The wiring needs to be completed by the electricians | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-01-20
WW-CEAST | January | Weather today Mostly Cloudy and -16 Celsius -On site to complete work order W11553698, W11599965. -Completed station check. -Entered station readings into SharePoint. -East Forcemain trial isolation is now back in service. -East and West Forcemainare now in timed auto duty rotation every 4 hours. -Pumps 2, 3, 4, 5, and 6 available in timed auto duty rotation every 3 hours. -Pump 1 out of service due to discharge valve issue. -Standby power generators available in auto. -Checked dry well, Ok. -All lines available in auto at the dump pad for the haulers. -Checked bar screens and Rotated bin. -Cleaned bar screen room of rags and bar screen oil full. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-01-30
WW-CEAST | January | Weather today Overcast and -17 Celsius -On site to complete work order W11546438, W11544685, W11382000. -Completed station check. -Entered station readings into SharePoint. -Diesel Generator 3 Annual Maintenance and load test. -Pump 3 is now back in service in auto/duty 5. -Pumps 2, 3, 4, 5, and 6 available in timed auto duty rotation every 3 hours. -Pump 1 out of service due to discharge valve issue. -Standby power generators available in auto. -Checked dry well, Ok. -All lines available in auto at the dump pad for the haulers. -Checked bar screens and Rotated bin. -Cleaned bar screen room of rags and bar screen oil full. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-01-26
WW-CEAST | January | Weather today Snow and -13 Celsius -On site to complete work order W11532227, W11537666, W11541418. -Completed station check. -Entered station readings into SharePoint. -Pumps 2, 4, 5, and 6 available in timed auto duty rotation every 3 hours. -Pump 1 out of service due to discharge valve issue. -Pump 3 still in manual/duty 7 but has been primed and available if needed and can be ran remotely. -Standby power generators available in auto. -Checked dry well, Ok. -All lines available in auto at the dump pad for the haulers. -Checked bar screens and Rotated bin. -Cleaned bar screen room of rags and bar screen oil full. -Bar Screen Bin Removal and Replacement - pushed rag bins back in after being picked up by Miller Waste. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-01-23
WW-CEAST | January | Weather today Snow and -14 Celsius -On site to complete work order W11526108. -Completed consolidated monthly surge tank inspection. - Surge tank and system inspection. - Surge tank valve and actuator exercise and inspection. - Surge tank drain valve inspection. - Transmission Line Flushing. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-01-15
WW-CEAST | January | Weather today Clear and -11 Celsius -On site to complete work orders W11535621, W11534613, W11603349, W11552848, W11552833. -Dump Pad Inspection & Cleaning. -Comprehensive Housekeeping. -Code of Conduct Training. -Fire Safety Training. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-01-20
WW-CEAST | January | On site to assist contractor Total Power with Diesel Generator maintenance and Load Test. Informed ROC of work. Work completed. All alarms cleared and all generators back in auto service. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-01-26
WW-CEAST | January | On site for Station Check, and Standby Power Generators Annual Maintenance and Load Test with CMS and Contractor (Total Power). Station Check (See details on SharePoint) Pumps 2, 4, 5 and 6 available in timed auto duty rotation every 3 hours. Pump 1 out of service and in manual/duty 7. Ran pump 3 to remove old sewage inside the pump before CMS will work on it. Afterwards, put Pump 3 out of service/manual/duty 7. Standby power generators available in auto. Checked dry well, ok. Checked bar screens. Levelled rags from the bin. Rotated rag bin. Added oil on the chain reservoir tank. Cleaned/hosed down screen room. Flushed screw press drain. All lines available in auto at the dump pad for the haulers to use. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-01-19
WW-CEAST | January | Reset RSP_PMP1 Runtime Hours and Statistics. Completed. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-01-29
WW-CEAST | January | Here to flush out Line 2 and reset Line 2 at the dump pad - CMU# W11611762. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-01-23
WW-CEAST | January | On site to replace pump 1 with a rebuild with a new bowl. Pump is installed but not in service due to the discharge valve actuator has failed and we are waiting for delivery. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-01-21
WW-CEAST | January | On site completed Station Check. Pumps 2, 4 and 6 available in timed auto duty rotation every 3 hours. Pump 1 out of service due to discharge valve issue. Pump 3 still in manual/duty 7 but has been primed and available if needed and can be ran remotely. Pump 5, while on site developed leakage alarm. It is now in manual/duty 7. Created work order request for CMS to check the problem ( W11581590). All standby power generators available in auto. Checked dry well, ok. Checked bar screens. Rotated rag bin. Cleaned bar screen room of rags. All lines available in auto at the dump pad for the haulers to be used. As per Team Lead?s instruction, put pump 3 in duty 1 and ran. It is not registering any flow reading in its discharge flow FIT due to fault and also at the combined flow FIT. It seems, there is flows coming out since the wet well level is not really going up. It, somewhat, maintaining the wet well level. Pump 5 back in service. CMS fixed the problem. See eLogbook entry of CMS above. Aurora is now back to 4 pumps in auto. Pump 3 is available when needed. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-01-12
WW-CEAST | January | Electricians reset leakage alarm. Drained 5 Litres of coolant from pump 5 Refilled coolant. Tested operation of pump 5. Complete. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-01-12
WW-CEAST | January | On site in response to dump pad line 2 fault alarm. Cleared the alarm by backflushing the line/value. Put line 2 back in service | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-01-13
WW-CEAST | January | Weather today Rain and 3 Celsius -On site to complete work orders W11521389, W11520430, W11519498. -Completed station check. -Entered station readings into SharePoint. - Check valve inspection. - Dry well flood alarm test. - Sump pit inspection. - High low temp alarm test.? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? ? - Autodialer test. - Air Compressor Inspection and cleaning. -Pumps 2, 4, 5, and 6 available in timed auto duty rotation every 3 hours. -Pump 1 out of service due to discharge valve issue. -Pump 3 still in manual/duty 7 but has been primed and available if needed and can be ran remotely. -Standby power generators available in auto. -Checked dry well, Ok. -All lines available in auto at the dump pad for the haulers. -Checked bar screens and Rotated bin. -Cleaned bar screen room of rags and bar screen oil full. - RS pump & motor instead. -Pump 1 (VFD) - Out of service. -Pump 2 (VFD) - @ 0% speed, 290.6 L/s, 768 kPa, 384 A, 517 V, 54 Hz, 1077 Rpm; 40% speed, 364.6 L/s, 784 kPa, 465 A, 536 V, 56 Hz, 1116 Rpm. -Pump 3 (Constant) - Out of service. -Pump 4 (Constant) - 472.4 L/s, 780 kPa, 462 A, 601 V, 60 Hz. -Pump 5 (VFD) - @ 0% speed, 329.8 L/s, 787 kPa, 378 A, 517 V, 54 Hz, 1077 Rpm; 40% speed, 412.9 L/s, 780 kPa, 463 A, 536 V, 55 Hz, 1115 Rpm. -Pump 6 (VFD) - @ 0% speed, 318.8 L/s, 775 kPa, 387 A, 517 V, 54 Hz, 1077 Rpm; 40% speed, 412.3 L/s, 776 kPa, 463 A, 536 V, 55 Hz, 1115 Rpm. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-01-14
WW-CEAST | January | Weather today Overcast and 1 Celsius -On site to complete work order W11501989, W11489032, W11489032, W11500942, W11502470, W11491164, W11489432. -Completed station check. -Entered station and generator readings into SharePoint. -Bar screen bin removal and replacement. -Air compressor inspection and cleaning. -Standby Power Generators 1, 2, and 3 test run. -Hazardous waste collection and removal. -JHSC Health and Safety Inspection. -Pumps 2, 4, 5 and 6 available in timed auto duty rotation every 3 hours. -Pump 3, which is in manual/duty 7, out of service due to discharge flow fault. -Pump 1 is in manual/duty 7. -Standby power generators available in auto. -Checked dry well, Ok. -All lines available in auto at the dump pad for the haulers. -Checked bar screens. Rotated bin. Cleaned bar screen room of rags. -Bar Screen Bin Removal and Replacement - pushed rag bins out for pick up by Miller Waste. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-01-07
WW-CEAST | January | Weather today Overcast and 5 Celsius -On site to complete work orders W11565192, W11509779. -Completed station check. -Entered station readings into SharePoint. -Unit Heater replacement and MCC 5 Shutdown. -Unit Heater in screen room have been replaced. -Pumps 2, 4, 5 and 6 available in timed auto duty rotation every 3 hours. -Pump 3, which is in manual/duty 7, out of service due to discharge flow fault. -Pump 1 is in manual/duty 7. -Standby power generators available in auto. -Checked dry well, Ok. -All lines available in auto at the dump pad for the haulers. -Checked bar screens. Rotated bin. Cleaned bar screen room of rags. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-01-09
WW-CEAST | January | On site for pump 1 discharge valve. Found the actuator to be faulty we will source a replacement. Will on site we found bar screen 2 to be tripped on overload. Adjusted the rake on both screens and preformed a pm on both. Screens are in service | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-01-09
WW-CEAST | January | Station readings taken and updated on sharepoint. Reviewed trends, ok. both pumps available in all stop auto duty rotation station ok, no issues. | Newmarket Green Lane Pumping Station | 2026-01-19
WW-CEAST | January | Weather today Clear and -9 Celsius -On site to complete work order W11489844. -Completed station check. -Entered station readings into SharePoint. -Pumps 2, 4, 5 and 6 available in timed auto duty rotation every 3 hours. -Pump 3, which is in manual/duty 7, out of service due to discharge flow fault. -Pump 1 is in manual/duty 7. -Standby power generators available in auto. -Checked dry well, Ok. -All lines available in auto at the dump pad for the haulers. -Checked bar screens. Rotated bin. Cleaned bar screen room of rags. -Two rag bins pushed outside last week not pick up by Miller Waste. | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-01-02
WW-CEAST | January | Weather today Overcast and -3 Celsius -On site to complete work orders W11493907, W11472962. -Completed station check. -Entered station readings into SharePoint. -Pumps 2, 4, 5 and 6 available in timed auto duty rotation every 3 hours. -Pump 3, which is in manual/duty 7, out of service due to discharge flow fault. -Pump 1 is in manual/duty 7. -Standby power generators available in auto. -Checked dry well, Ok. -All lines available in auto at the dump pad for the haulers. -Checked bar screens. Rotated bin. Cleaned bar screen room of rags. -SCADA Review. ? | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-01-05
WW-CEAST | January | On site for station check. Both pumps available in all stop auto duty rotation. SCADA is trending. Station has normal operations. No outstanding alarm. | Newmarket Green Lane Pumping Station | 2026-01-16
WW-CEAST | January | On site checked station (See details on SharePoint). Both pumps available in all-stop auto duty rotation. Currently, pump 1 is running in auto as duty 1, with a flow of 265.6 L/s at 40% auto speed setpoint. No outstanding alarms. Station operations normal. SCADA is trending. | Newmarket Green Lane Pumping Station | 2026-01-30
WW-CEAST | January | On site checked station (See details on SharePoint). Both pumps available in all-stop auto duty rotation. Currently, pump 2 is running in auto as duty 1, with a flow of 194.4 L/s at 40% auto speed setpoint. No outstanding alarms. Station operations normal. SCADA is trending. | Newmarket Green Lane Pumping Station | 2026-01-26
WW-CEAST | January | On site checked station (See details on SharePoint). Both pumps available in all-stop auto duty rotation. Currently, pump 1 is running in auto as duty 1, with a flow of 262.4 L/s at 40% auto speed setpoint. No outstanding alarms. Station operations normal. SCADA is trending. | Newmarket Green Lane Pumping Station | 2026-01-23
WW-CEAST | January | On site for station check. Both pumps available in all stop auto duty rotation. SCADA is trending. Station has normal operations. No outstanding alarm. | Newmarket Green Lane Pumping Station | 2026-01-12
WW-CEAST | January | Station readings taken and updated on sharepoint. both pumps available in all stop auto duty rotation station ok, no issues. Reviewed trends, ok. | Newmarket Green Lane Pumping Station | 2026-01-09
WW-CEAST | January | Station readings taken and updated on SharePoint. Reviewed trends, ok. both pumps available in all stop auto duty rotation station ok, no issues. | Newmarket Green Lane Pumping Station | 2026-01-02
WW-CEAST | January | -On site to perform a station check and to assist CPD/contractors with air compressor repairs. -Readings entered into SharePoint. -Verified alum dosing and sand filter operation. -Contractors able to make repairs to both air compressors 1 and 2, both air compressors back in auto duty rotation. -OCU remains OOS. | Mount Albert Water Resource Recovery Facility | 2026-01-22
WW-CEAST | January | -On site to perform a station check. -Entered station readings into SharePoint. -Verified sand filter operation and alum dosing. -OCU remains OOS. | Mount Albert Water Resource Recovery Facility | 2026-01-28
WW-CEAST | January | On site completed work orders. Station Check (See entries on SharePoint) Checked DO Probes. Removed dangling rags from the probes. Checked Alum dosing injection points at pre-filter and post aeration. Sand Filter Filter-Reject Drain Line Flushed Process Building and Garages Comprehensive Housekeeping Also, operational support for Black and MacDonald to replace the faulty components in the OCU disconnect parts. | Mount Albert Water Resource Recovery Facility | 2026-01-27
WW-CEAST | January | Completed Lab work and sludge processing and entered results of the Lab into Sharepoint. DID NOT waste today and added 4 bags of soda ash. Washed down UV channel and also checked the sand filter operation while there - all good. Station running under normal ops - no new issues were observed. | Mount Albert Water Resource Recovery Facility | 2026-01-29
WW-CEAST | January | Restarted the Local SCADA server due to windows updates. Notified the Remote Operations Center and the OIC. | Mount Albert Water Resource Recovery Facility | 2026-01-22
WW-CEAST | January | Completed Lab work and collected weekly samples for the Lab,, entered results into Sharepoint after completing the Lab. Wasted 20m3 and added 4 bags of soda ash. cleaned the clarifier sludge trough. Phil created a work order for air compressor 1 - OOS but the rest of the station is running as per normal. | Mount Albert Water Resource Recovery Facility | 2026-01-21
WW-CEAST | January | -On site to collect weekly samples, W11538364. | Mount Albert Water Resource Recovery Facility | 2026-01-21
WW-CEAST | January | -On site to complete work orders. -Hoist system inspections completed for aeration blower room and sand filter room. -Sand filter reject drain line flushes completed. -Station check completed, readings entered into SharePoint. -Verified sand filter operation and alum dosing. -Work order completed for pumping out water in influent flowmeter chamber, not enough water to pump out of bottom of chamber. -OCU OOS. | Mount Albert Water Resource Recovery Facility | 2026-01-20
WW-CEAST | January | Completed Lab work and entered results into Sharepoint,, also completed sludge processing. Wasted 10m3 and added 4 bags of soda ash. went through the station and all systems are working well. station running under normal ops - no new issues observed. | Mount Albert Water Resource Recovery Facility | 2026-01-20
WW-CEAST | January | -On site to complete work orders. -RAS inlet chamber and post aeration alum chambers cleaned out. -Station check completed, readings entered into SharePoint. -Verified alum dosing and sand filter operation. -OCU OOS. -Compressor 1 Motor Overload Alarm came in this afternoon, found drain line on air compressor 2 tank continually blowing out air. Isolated drain line with ball valve on line. Unable to reset motor overload alarm on compressor 1 despite attempt to reset on panel and cycle power at breaker. Work request created for maintenance team. Compressor 1 currently OOS, Compressor 2 running in auto. | Mount Albert Water Resource Recovery Facility | 2026-01-21
WW-CEAST | January | -On site to complete work orders. -Station check completed, readings entered into SharePoint. -Verified alum dosing and sand filter operation. -UV Bank 1B inspection and cleaning completed. Verified Bank 1B was working properly following cleaning. -ROC called about Aeration Tank 2 DO Lo Alarm this afternoon. Changed controlling tank for DO level from Aeration Tank 1 to Tank 2. Previously only one blower had been running. Second aeration blowing immediately began running in auto and alarm was able to be cleared within a few minutes. -OCU remains OOS. | Mount Albert Water Resource Recovery Facility | 2026-01-23
WW-CEAST | January | Completed Lab work and entered results into Sharepoint,, also completed sludge processing, Wasted 20m3 and added 4 bags of soda ash. Cleaned UV bank 1B bulbs with Phil - all look good. Station running under normal ops - no new issues were found. | Mount Albert Water Resource Recovery Facility | 2026-01-23
WW-CEAST | January | Completed Lab work and sludge processing,, entered results of the lab into Sharepoint. Wasted 10m3 and added 4 bags of soda ash. Went through the station - all is good, valves for the blow offs on the compressors are still closed. Station running under normal ops - no new issues were found. | Mount Albert Water Resource Recovery Facility | 2026-01-27
WW-CEAST | January | -On site to perform a station check. -Entered station readings into SharePoint. -Verified sand filter operating and alum dosing. -Shoveled and salted stairs and walkways. -Manually rotated Sludge Blower 1 into duty and UV Bank 1A into duty. -At approximately 14:00, GFL sludge hauler reported small spill of sludge at end of driveway, where driveway connects to Doanne Rd. GFL is arranging hydrovac truck to attend site and clean up spilled sludge on driveway. | Mount Albert Water Resource Recovery Facility | 2026-01-16
WW-CEAST | January | -Station check completed, readings entered into SharePoint. -Verified alum dosing and sand filter operation. -Added two bags of soda ash to each aeration tank. -Worked on cleaning up process building. -OCU remains OOS. | Mount Albert Water Resource Recovery Facility | 2026-01-30
WW-CEAST | January | Completed Lab work and sludge processing,, entered results from Lab into Sharepoint. Wasted 20m3 and added 4 bags of soda ash. Went quickly through the station and everything is working properly, blow-off valves for air release are still closed. | Mount Albert Water Resource Recovery Facility | 2026-01-25
WW-CEAST | January | Weather today Snow and -17 Celsius -On site for call out MTSP - Air Compressor Pressure LoLo W11611787. -On arrival found that air pressure had returned to normal operating pressure. -Checked trends and did see where the air pressure level dipped. -Suspecting that it may be the same issue with the automatic drain valves malfunctioning. -I manual valved both automatic drain valves closed for now and will investigate more next week. | Mount Albert Water Resource Recovery Facility | 2026-01-23
WW-CEAST | January | Completed Lab work and entered results into Sharepoint,, also completed sludge processing. Phil wasted 20m3 and we added 4 bags of soda ash. went through the station and everything is working fine. Crew here fixing hatches on the clarifier. | Mount Albert Water Resource Recovery Facility | 2026-01-19
WW-CEAST | January | Station check/lab complete and the readings have been entered into the sharepoint. Batch wasted 14m3, added 4 bags of soda ash into the aeration. | Mount Albert Water Resource Recovery Facility | 2026-01-18
WW-CEAST | January | Completed Lab work and entered results into Sharepoint,, completed sludge processing as well. Collected weekly samples at 08:45, wasted 10m3 and added 4 bags of soda ash. Station running under normal ops - no new issues observed. | Mount Albert Water Resource Recovery Facility | 2026-01-28
WW-CEAST | January | -On site to perform a station check and to assist contractors with air compressor repairs. | Mount Albert Water Resource Recovery Facility | 2026-01-03
WW-CEAST | January | Completed Lab work and entered results into Sharepoint,, also completed sludge processing. Shovelled a bunch of snow as well. Went through the station - all good. Station running under normal ops - no issues observed. | Mount Albert Water Resource Recovery Facility | 2026-01-16
WW-CEAST | January | -On site to complete work orders. -Lab analysis completed, results entered into SharePoint. -STT decanted to headworks, then emptied into SHT. -Batch wasted 20m3, ran RAS pumps at 100% speed when returning to service. -Station check completed, readings entered into SharePoint. -Verified sand filter operation and alum dosing. -Two bags of soda ash added to each aeration tank. -Cleaned out RAS inlet chamber and post aeration alum chamber. -OCU remains OOS. | Mount Albert Water Resource Recovery Facility | 2026-01-19
WW-CEAST | January | Completed Lab work and entered results into Sharepoint,, completed sludge processing as well. Wasted 10m3 today and added 4 bags of soda ash. Company is here to work on air compressor 1. Washed down UV channel while RAZ pumps were off. | Mount Albert Water Resource Recovery Facility | 2026-01-22
WW-CEAST | January | Completeds Lab work and entered results into Sharepoint,, also the sludge processing. went through the station and checked equipment - all good. Station running under normal ops - no issues were found. | Mount Albert Water Resource Recovery Facility | 2026-01-14
WW-CEAST | January | -On site to complete work orders. -Shoveled and salted stairs and walkways. -Hosed down clarifier scum troughs to remove large amount of ice buildup. -RAS inlet chamber and post aeration alum chamber cleaned out. -Station check completed, readings entered into SharePoint. -Verified alum dosing and sand filter operation. -OCU remains OOS. | Mount Albert Water Resource Recovery Facility | 2026-01-29
WW-CEAST | January | -On site to complete work orders. -Grit bin out for pickup tomorrow. -Shoveled and salted stairs and walkways. -Station check completed, readings entered into SharePoint. -Verified alum dosing and sand filter operation. -OCU remains OOS. -Air compressor drain lines manually closed until drain line solenoids can be repaired. | Mount Albert Water Resource Recovery Facility | 2026-01-26
WW-CEAST | January | Completed Lab work and sampling for the week,, entered results from the lab into SharePoint. Completed sludge processing and wasted 20m3 and added 4 bags of soda ash. Drained water from the clarifier gear box and did not need to add oil. Station running under normal ops - no issues were found. | Mount Albert Water Resource Recovery Facility | 2026-01-07
WW-CEAST | January | Completed Lab work and sludge processing and entered results into Sharepoint,, wasted 10m3 and added 4 bags of soda ash. cleaned out post aeration tank and washed down UV channel. Washed down inlet channel and cleaned up rags and also went through the station and completed the station check. Station running under normal ops - no issues found. | Mount Albert Water Resource Recovery Facility | 2026-01-15
WW-CEAST | January | Completed Lab work and sludge processing,,entered the results from the Lab into Sharepoint,, wasted 20m3 today and added 4 bags of soda ash. Cleaned out the post aeration tank as well as at the inlet gates - no much again in the post aeration tank. Shovelled some snow but Phil shovelled most of it. By-pass valves for the drain on the air tanks are still closed but the rest of the station is running fine. | Mount Albert Water Resource Recovery Facility | 2026-01-26
WW-CEAST | January | Completed Lab work and entered results into SharePoint,, completed sludge processing and wasted 20m3 and added 4 bags of soda ash. Checked both clarifiers and just had to grease the motors - oil level OK. Station running under normal ops - no issues were found. | Mount Albert Water Resource Recovery Facility | 2026-01-09
WW-CEAST | January | Completed Lab work and entered results into SharePoint,, completed sludge processing and wasted 20m3 and added 4 bags of soda ash. Washed down UV bank bulbs on A bank and washed down the channel. Station running under normal ops - no issues found. | Mount Albert Water Resource Recovery Facility | 2026-01-08
WW-CEAST | January | -On site to complete work orders. -Station check completed, readings entered into SharePoint. -Verified alum dosing and sand filter operation. -Air compressors 1-2 cleaning and inspection completed. -Consolidated headworks inspection completed. -Greased travelling screen and cleaned out back compartment . -Screw press inspection completed. -Grit screw press inspection completed and unit greased. -Vortex 1-2 inspections completed. -Black and McDonald on site for electrical investigation regarding OCU motor. OCU remains OOS. | Mount Albert Water Resource Recovery Facility | 2026-01-07
WW-CEAST | January | Onsite to review why effluent pump #1 is the only pump working Upon inspection found pump alternator relay faulty Parts no longer available waiting for new replacement parts | Mount Albert Water Resource Recovery Facility | 2026-01-09
WW-CEAST | January | -On site to complete work orders. -Weekly samples collected, W11522761. -Sand filter drain line flushing completed. -Station check completed, readings entered into SharePoint. -Verified sand filter operation and alum dosing. -Rotated grit bins. | Mount Albert Water Resource Recovery Facility | 2026-01-14
WW-CEAST | January | Completed Lab work and entered results into SharePoint,, also sludge processing and the station check. Wasted 20m3 and added 4 bags of soda ash,, flushed both sand filter recycling drain lines as well as checked both blowers and also checked both sludge blowers - oil/belts both are good. Votes are both working good as well. Station running under normal ops - no issues were found. | Mount Albert Water Resource Recovery Facility | 2026-01-13
WW-CEAST | January | -On site to complete work orders. -Collected weekly/monthly samples: W11503347, W11488403, W11488389, W11481414. | Mount Albert Water Resource Recovery Facility | 2026-01-07
WW-CEAST | January | -On site to complete work orders. -Received alum delivery. Alum tank: 87cm -> 381cm. -Cleaned out RAS inlet chamber and post aeration alum chamber. -Cleaned DO probes and aeration inlet gates. -UV 1A cleaning and inspection completed. -Station check completed, readings entered into SharePoint. -Verified sand filter operation and alum dosing. | Mount Albert Water Resource Recovery Facility | 2026-01-08
WW-CEAST | January | -on site for lab analysis and sludge handling -reviewed SCADA -inspected site -entered data into SharePoint -added 4 bags of soda ash to aeration tanks -wasted 20 m3 of sludge from clarifiers to sludge thickening tank -completed Sunday lab analysis -ran RAS pumps manual speed 100% to clear debris, back to auto speed after -station okay | Mount Albert Water Resource Recovery Facility | 2026-01-11
WW-CEAST | January | -On site to complete work orders. -Decanted STT to headworks. -Added two bags of soda ash to each aeration tank. -Completed lab analysis, entered results into SharePoint. -RAS inlet chamber and post aeration alum chambers cleaned out. -Soda ash delivery of 120 50lb bags received. -Station check completed, readings entered into SharePoint. -Verified alum dosing and sand filter operation. | Mount Albert Water Resource Recovery Facility | 2026-01-12
WW-CEAST | January | -On site to complete work orders. -Inspected headworks Flowmeter chamber, found only a couple inches of water on chamber floor, not enough to pump out. -Station check completed, readings entered into SharePoint. -Verified alum dosing and sand filter operation. -OCU remains OOS. | Mount Albert Water Resource Recovery Facility | 2026-01-09
WW-CEAST | January | Attending site to check oxygen sensor (W11555069). Sensor has failed. Replaced failed sensor and calibrated, ROC was notified after sensor was replaced and SCADA alarms were cleared. | Mount Albert Water Resource Recovery Facility | 2026-01-05
WW-CEAST | January | Lab and station check complete. All the readings have been entered into the sharepoint. Batch wasted 20m3 in total. Dosed 4 bags of soda ash into the aeration tank. Created CMU3 for headworks O2 sensor as it is currently reading around 9% | Mount Albert Water Resource Recovery Facility | 2026-01-02
WW-CEAST | January | Weather today Overcast and -9 Celsius -On site to complete work order W11492100. -completed lab analysis and sludge handling. -Entered station readings into SharePoint. -Decanted STT to headworks, then emptied tank into SHT. -Batch wasted 20m3, ran RAS pumps at 100% speed when returning to service. -Headworks O2 LoLo alarm outstanding. | Mount Albert Water Resource Recovery Facility | 2026-01-04
WW-CEAST | January | Completed lab work and entered results into SharePoint,, wasted 20m3 and added 4 bags of soda ash. Did not get any clarifier sample , Phil showed me the trap door when he showed up after his WO?s at the pumping station. Completed Diesel test run and entered results into SharePoint,, also H & S completed - no issues. Cleaned out post aeration tank as well as the influent gates. Shovelled snow all around the station - all walkways and entrances are cleared. Station running under normal ops - no issues to report. | Mount Albert Water Resource Recovery Facility | 2026-01-05
WW-CEAST | January | -On site to complete work orders. -RAS pumps 1-3 inspections completed. -WAS pumps 1-2 inspections completed. -Scum pumps 1-2 inspections completed. -Sump pumps maintenance completed, inspected all pumps and sump pits. -Station check completed, readings entered into SharePoint. -Verified sand filter operation and alum dosing. | Mount Albert Water Resource Recovery Facility | 2026-01-06
WW-CEAST | January | -On site to complete work orders. -Station check completed, readings entered into SharePoint. -Verified sand filter operation and alum dosing. -Lab reagent inventory completed. -Grit bin outside for pickup. -Shovelled walkways and stairs. | Mount Albert Water Resource Recovery Facility | 2026-01-05
WW-CEAST | January | -On site to collect weekly samples - W11550827. -Collected samples, flushed sample jug with hot water, reset composite sampler for 0700 Feb. 3, 2026. | Mount Albert Pumping Station | 2026-01-28
WW-CEAST | January | -On site to complete work orders. -Station check completed, readings entered into SharePoint. -Checked drywell. -Unable to open e-lock to generator. -Comprehensive housekeeping tasks completed. -Shoveled snow around walkways and doors. | Mount Albert Pumping Station | 2026-01-26
WW-CEAST | January | Completed Lab work and entered results into SharePoint,, wasted 20m3 and added 4 bags of soda ash. There was no hazardous waste to dispose of and cleaned out post aeration tank as well as the inlet gate. Verified DO probes in the aeration tanks, tried flushing the drain lines for the sand filters but not much flow coming from the water line(not sure if it did much). | Mount Albert Water Resource Recovery Facility | 2026-01-06
WW-CEAST | January | -On site to perform a station check. -Entered station readings into SharePoint. -Checked drywell and diesel generator. | Mount Albert Pumping Station | 2026-01-19
WW-CEAST | January | Onsite for annual calibration Informed ROC Used cal mode in scada during the work Instruments calibrated: Wwel LITs Diesel LIT Will return for FIT Cleared associated alarms Informed ROC, armed building and left site No issues upon leaving | Mount Albert Pumping Station | 2026-01-27
WW-CEAST | January | -On site to collect weekly samples, W11538364. -Collected samples, flushed sample jug with hot water, reset composite sampler for 0700 January 27. | Mount Albert Pumping Station | 2026-01-21
WW-CEAST | January | -On site to perform a station check. -Entered station readings into SharePoint. -Checked drywell. -Unable to open e-lock on generator door due to cold temperatures. | Mount Albert Pumping Station | 2026-01-16
WW-CEAST | January | -On site to complete work orders. -Station check completed, readings entered into SharePoint. -Checked drywell, unable to open e-lock to check generator due to cold temperatures. -Raw sampler inspection and cleaning completed. | Mount Albert Pumping Station | 2026-01-23
WW-CEAST | January | -On site to perform a station check. -Entered station readings into SharePoint. -Checked drywell and diesel generator. | Mount Albert Pumping Station | 2026-01-30
WW-CEAST | January | Onsite to continue annual calibrations Informed ROC Used cal mode on scada during the process Calibrated RSP Discharge FIT Cleared associated alarms Verified one pump cycle Informed ROC, armed building and left site No issues up on leaving | Mount Albert Pumping Station | 2026-01-28
WW-CEAST | January | -On site to collect weekly/monthly samples: W11503347, W11488389. -Collected samples, flushed sample jug with hot water, reset composite sampler for 0700 on Jan. 13. -Shovelled walkways and dropped off extra bag of ice melter on site. | Mount Albert Pumping Station | 2026-01-07
WW-CEAST | January | -On site to collect weekly samples, W11522761. -Collected samples, flushed sample jug with hot water, reset composite sampler for 0700 Jan. 20. | Mount Albert Pumping Station | 2026-01-14
WW-CEAST | January | -On site to complete work orders. -Station check completed, readings entered into SharePoint. -Checked drywell. -Monthly JHSC H&S inspection completed, no issues noted. -Hazardous waste collection and removal completed, no items removed from site this month. -Monthly diesel generator test run completed, readings entered into SharePoint. -0907 - Transferred site to generator power. -1023 - Transferred site back to utility power. -Generator start hours: 616.7, stop hours: 618.2, run time: 1.5hrs. | Mount Albert Pumping Station | 2026-01-05
WW-CEAST | January | Took station readings and entered into SharePoint,, reviewed trends - all good, pumps in all stop Duty rotate. Checked pump floor - no issues and checked Diesel room - no leaks or alarms. Station running under normal ops - no issues were found. | Mount Albert Pumping Station | 2026-01-12
WW-CEAST | January | -On site to complete work orders. -Station check completed, readings entered into SharePoint. -Checked drywell and generator. -Hoist system inspection completed, hoist locked out my maintenance team. -Consolidated dry well inspection completed. -RS pump inspection completed, greased both pumps. -Pump 1: 44L/s at 50% speed. -Pump 2: 38L/s at 50% speed. -Autodialer test completed. -Dry well flood alarm test completed and confirmed by ROC. -Sump pit system inspection completed. Functionally tested float and pump with no issues. -Placed station back to Auto wet well backup control mode from PAC mode. No LIT2 fluctuations in trends since Dec. 26. | Mount Albert Pumping Station | 2026-01-09
WW-CEAST | January | Station Check (See details on SharePoint). Both pumps available in all-stop auto duty rotation. Standby power generator available in auto. Checked dry well, ok. | Mount Albert Pumping Station | 2026-01-02
WW-CEAST | January | On site to troubleshoot O2 sensor alarms that have caused facility shutdown alarm. System was remotely turned back on yesterday following the facility shutdown alarm by opening main inlet gate in manual. Tried out new O2 sensor puck that INST left onsite and did not work. Notified ROC/INST TL and created CMU3. | SEC Fairport Air Handling Facility (Shaft 4) | 2026-01-16
WW-CEAST | January | On site for comprehensive housekeeping. Cleaned/vacuumed/swept facility. Sanitized/disinfected toilet/bathroom. Supplies replenished and available. Collected and disposed of garbage and waste in appropriate locations. Organized document storage. | SEC Fairport Air Handling Facility (Shaft 4) | 2026-01-22
WW-CEAST | January | -exercised rotork actuators for both fans -rotated fan duties, fan 1 switched to duty 1, fan 2 duty 2 -switched duties back, fan 1 duty 2, fan 2 duty 1 -reviewed SCADA -station okay | SEC Fairport Air Handling Facility (Shaft 4) | 2026-01-23
WW-CEAST | January | Onsite to troubleshoot fan room O2 sensor Informed ROC Replaced faulty O2 sensor and calibrated Cleared associated alarms Left site Contractors working on site (electrical room) | SEC Fairport Air Handling Facility (Shaft 4) | 2026-01-29
WW-CEAST | January | -station check of site -reviewed SCADA -entered data into sharepoint -inspected site -station okay | SEC Fairport Air Handling Facility (Shaft 4) | 2026-01-21
WW-CEAST | January | On site for station check. Entered station readings to sharepoint. Inspect site, reviewed Scada. No issues found. Station Ok. | SEC Fairport Air Handling Facility (Shaft 4) | 2026-01-27
WW-CEAST | January | -station check of site -reviewed SCADA -inspected site -entered data into SharePoint -JHSC Inspection -Heat Trace Controller Inspection -Crane Hoist Inspection -monthly generator test run -started generator at 09:40 -stopped generator at 10:47 Generator Start Hours: 253.4 Generator Stop Hours: 254.6 Run Time: 1.2 hrs Fuel Start: 2131L Fuel Stop: 2088L Fuel Used: 43 -generator test run successful, back on utility power -station okay | SEC Fairport Air Handling Facility (Shaft 4) | 2026-01-14
WW-CEAST | January | At 09:32am, fans interlocked due to issue with O2 monitor alarm that caused the inlet gate MV1 closing. At 11:10am, remotely put inlet gate MV1 in manual and opened the gate. Fan 2 ran in auto as duty 1. Fan 1 is in auto standby. Inlet gate MV1 will remain in manual open until O2 monitor 1 is fixed. | SEC Fairport Air Handling Facility (Shaft 4) | 2026-01-15
WW-CEAST | January | On site for Station Check (See details on SharePoint). All pumps available in timed-auto duty rotation every 4 hours. Standby power generator available in auto. Checked dry well, ok. Ran pump 2 for several minutes, with a flow of 196.6 L/s at 103 kPa. Cleared/reset intrusion alarm. No more outstanding alarms. Station operations normal. | Newmarket Bogart Creek Sewage Pumping Station | 2026-01-26
WW-CEAST | January | -station check of site -reviewed SCADA -inspected site -entered data into SharePoint -station okay | SEC Fairport Air Handling Facility (Shaft 4) | 2026-01-07
WW-CEAST | January | On site completed work orders. Station Check (See details on SharePoint). All pumps available in timed auto duty rotation every 4 hours. Standby power generator available in auto. Checked dry well, ok. No outstanding alarms. Ran pump 2 for several minutes with a flow of 196 L/s at 117 kPa. Currently, pump 1 is running in auto at 15% speed as duty 1, with a flow of 77.7 L/s at 86 kPa. Consolidated Wet Well Inspection Wet Well High Level Alarm Test - received and confirmed by ROC. Wet Well Inspection and Cleaning Wet Well Valve Exercise Facility Outfall Inspection Channel Grinder Inspection and Cleaning Overflow Sluice Gate Exercise | Newmarket Bogart Creek Sewage Pumping Station | 2026-01-16
WW-CEAST | January | Station readings taken. Data entered on sharepoint. Reviewed SCADA, trends. Checked basement. ok Station running normal. | Newmarket Bogart Creek Sewage Pumping Station | 2026-01-19
WW-CEAST | January | On site for Station Check (See details on SharePoint). All pumps available in timed-auto duty rotation every 4 hours. Currently, pump 4 is running in auto as duty 1 with a flow of 82.1 L/s at 83 kPa and 15% minimum auto speed setpoint. Standby power generator available in auto. Checked dry well, ok. No outstanding alarms. Station operations normal. | Newmarket Bogart Creek Sewage Pumping Station | 2026-01-30
WW-CEAST | January | Onsite for failed O2 sensor Informed ROC Replaced sensor with new and calibrated Cleared associated alarms Informed ROC Unable to arm building. Spoke with security. They armed the building remotely and arranged for someone to investigate on-site within the next 15min. Left site | Newmarket Bogart Creek Sewage Pumping Station | 2026-01-15
WW-CEAST | January | Onsite to adjust O2 sensor Informed ROC Adjusted sensor and verified on scada All ok Informed ROC, armed building and left site | Newmarket Bogart Creek Sewage Pumping Station | 2026-01-16
WW-CEAST | January | On site for Station Check (See details on SharePoint). All pumps available in timed-auto duty rotation every 4 hours. Standby power generator available in auto. Checked dry well, ok. Ran pump 2 for several minutes, with a flow of 198.6 L/s at 117 kPa. No outstanding alarms. Station operations normal. | Newmarket Bogart Creek Sewage Pumping Station | 2026-01-23
WW-CEAST | January | -on site for work orders -manual valve exercise -discharge valve exercise/inspection -Housekeeping -Crane/Hoist Inspection -station okay | Newmarket Bogart Creek Sewage Pumping Station | 2026-01-15
WW-CEAST | January | Station check complete and the readings have been entered into the sharepoint Created CMU3 for INST to investigate oxygen lolo | Newmarket Bogart Creek Sewage Pumping Station | 2026-01-12
WW-CEAST | January | Check right sump pump not pumping. Removed check valve and found check valve flap is seized. Installed new check valve assembly. Ran pump through a few cycles and sump is pumping down fully. Complete. | Newmarket Bogart Creek Sewage Pumping Station | 2026-01-07
WW-CEAST | January | Weather today Overcast and 5 Celsius. -On site to complete work order W11509710. -On site to perform a station check. -Entered station readings into SharePoint. -Checked drywell. -OCU running, supply fan off. -All pumps in auto and available. | Newmarket Bogart Creek Sewage Pumping Station | 2026-01-09
WW-CEAST | January | Station readings taken. Data entered on sharepoint. Reviewed SCADA, trends. Checked basement. ok Station running normal. | Newmarket Bogart Creek Sewage Pumping Station | 2026-01-02
WW-CEAST | January | Onsite to troubleshoot building O2 sensors Informed ROC Calibrated both east and west building O2 sensors Cleared associated alarms There is a slight burning odour from the electrical heat in the office and in the chemical storage area. Everything appears to be working as it should. Will inform property services. Informed ROC, armed building and left site | SEC Boxgove Corrosion Control Facility | 2026-01-29
WW-CEAST | January | Station check and generator test run complete and the readings have been entered into the sharepoint JHSC inspection complete for this month Consolidated dry well inspection complete Pump test run result: P1 pushed out 88.9 l/s @ 16%, P2 pushed out 193.5 l/s, P3 pushed out 97.2 l/s @ 16%, P4 pushed out 85.8 l/s @ 16% | Newmarket Bogart Creek Sewage Pumping Station | 2026-01-05
WW-CEAST | January | -station check of site and work orders -reviewed SCADA -inspected site -entered data into sharepoint -Tank Maintenance -Chemical Pump Inspection -HVAC Inspection -Sump Pump Inspection -station okay | SEC Boxgove Corrosion Control Facility | 2026-01-19
WW-CEAST | January | On site to clear O2 monitor alarm and HVAC general alarm. Was able to acknowledge and reset the alarms from the gas monitor panel found outside of the chemical room. Checked for any other HVAC issues and none found in the building . Cleared the alarms on scada and station running normal. | SEC Boxgove Corrosion Control Facility | 2026-01-27
WW-CEAST | January | Shut off water going into H2O2 tank 1 in response to tank level hi/hihi Tank 1 @ 4.79m of water Tank 2 has 0.5m of 50% H2O2 chemical solution | SEC Boxgove Corrosion Control Facility | 2026-01-08
WW-CEAST | January | -On site to respond to General HVAC Alarm and O2 Monitor Alarm. -Upon arrival to site, ODOR-GO22 (North Wall) was reading 20.7% on the Gas Monitor Panel and 20.8% on the O2 sensor. Reset alarm on Gas Monitor Panel. Reset O2 and HVAC alarms on SCADA. MAU Fan did not appear to have speed ramped up when O2 alarm was active. Upon arrival to site, fan was running at 60.0Hz/5600CFM. Reset fan aft6er clearing O2 and HVAC alarms, but speed did not change. Alarms appeared to have been caused by O2 sensor (north wall) fluctuations between 1-2am this morning. Readings are now stable. Building temp currently at 16.8C in chemical tank room, no further issues on site. | SEC Boxgove Corrosion Control Facility | 2026-01-31
WW-CEAST | January | -station check of site -reviewed SCADA -entered data into SharePoint -inspected site -Housekeeping -station okay | SEC Boxgove Corrosion Control Facility | 2026-01-26
WW-CEAST | January | -station check of site -reviewed SCADA -inspected site -entered data into SharePoint -station okay | SEC Boxgove Corrosion Control Facility | 2026-01-12
WW-CEAST | January | -tank 1 is filled with water 1.28 meters -tank 2 with 50% hydrogen peroxide 0.50 meters -tank 2 is interlocked on low level, waiting on delivery/procurement contract -began filling tank 1 with more water to keep pumps supplied with water until site receives more peroxide, tank 1 was at 1.28 meters before adding water began | SEC Boxgove Corrosion Control Facility | 2026-01-06
WW-CEAST | January | -station check of site -reviewed SCADA -inspected site -entered data into SharePoint -Nutrient Tank Inspection -Impellor Bearing Lubrication -station okay | SEC Markham Odour Control Facility | 2026-01-19
WW-CEAST | January | -station check of site and work orders -reviewed SCADA -inspected site -entered data into SharePoint -chemical pump inspection work order -JHSC Inspection -station okay | SEC Boxgove Corrosion Control Facility | 2026-01-05
WW-CEAST | January | -station check of site -reviewed SCADA -inspected site -entered data into SharePoint -Nutrient Tank Batching -Fan Impeller Lubrication -Activated Carbon Filter 1,2 Maintenance | SEC Markham Odour Control Facility | 2026-01-26
WW-CEAST | January | -topped up nutrient tank 2 with water -reviewed SCADA, reset nutrient tank 2 low level alarm | SEC Markham Odour Control Facility | 2026-01-27
WW-CEAST | January | -station check of site -reviewed SCADA -inspected site -entered data into SharePoint -Alectra on site to change hydrometer -station okay | SEC Markham Odour Control Facility | 2026-01-12
WW-CEAST | January | -on site for alarm management and investigation with Kevin Shaji -was looking into below alarms: 1. Damper station flood alarm, outstanding alarm, WO created for maintenance, needs new floats 2. S2 Humid Chamber LOLO LVL Switch Alarm, outstanding alarm, WO created for maintenance, new float required 3. Knife Gate Fault Alarm, was able to reset 4. O2 sensor alarms, created WO for instrumentation | SEC Markham Odour Control Facility | 2026-01-13
WW-CEAST | January | -station check of site and monthly work orders -reviewed SCADA -inspected site -entered data into SharePoint -monthly generator test run, notified ROC -JHSC Inspection -Nutrient Tank Batch Mixing/Inspection -Fan Bearing Lubrication -Recirculation Pump and Strainer Inspection -Booster Pump/Solenoid Valve/Media Spray Checks Inspection Generator Start Hours: 254.4 hrs Generator Stop Hours: 255.4 Run Time: 1.0 hrs Fuel Start: 11848L/73% Fuel Stop: 11801.8 L Fuel Used: 47 L -generator started at 10:32 -generator stopped at 11:34 -back on utility power, generator test run successful -topped up nutrient tank 2, reset low level alarm -creating WO for outstanding alarms, OCF Damper O2 sensor -station okay | SEC Markham Odour Control Facility | 2026-01-06
WW-CEAST | January | -exercised rotork actuators for both fans -rotated fan duties, fan 1 switched to duty 2, fan 2 duty 1 -switched duties back, fan 1 duty 1, fan 2 duty 2 -reviewed SCADA -station okay | SEC Altona Air Handling Facility (Shaft 6/7) | 2026-01-23
WW-CEAST | January | -station check of site -reviewed SCADA -inspected site -entered data into Sharepoint -Fan 1 back to auto from local, will not interlock because inlet gate is manual open now -O2 monitor 1 reading low, O2 monitor 2 reading 20.7%, work order in for instrumentation, this is interlocking the inlet gate which interlocks the fans -with inlet gate manual open we can bypass the interlock and still run the fans -station okay | SEC Altona Air Handling Facility (Shaft 6/7) | 2026-01-27
WW-CEAST | January | -station check of site -reviewed SCADA -inspected site -entered data into sharepoint -Ventilation System Inspection -Heat Trace Inspection -station okay | SEC Altona Air Handling Facility (Shaft 6/7) | 2026-01-21
WW-CEAST | January | Attending site to check oxygen sensors in fan room (W11615729). Both sensors were replaced and calibrated. ROC was notified before and after maintenance was performed. | SEC Altona Air Handling Facility (Shaft 6/7) | 2026-01-28
WW-CEAST | January | -station check of site and monthly work orders -reviewed SCADA -inspected site -entered data into SharePoint -monthly generator test run, notified ROC -JHSC Inspection -generator started at 11:15 -generator stopped at 12:25 Generator Start Hours: 218.6 hrs Generator Stop Hours: 219.8 hrs Run Time: 1.2 hrs Fuel Start: 3651 L Fuel Stop: 3640 L Fuel Used: 11 L -generator test run successful, reset alarms, fans back to auto -station okay | SEC Altona Air Handling Facility (Shaft 6/7) | 2026-01-07
WW-CEAST | January | Weather today Partly Cloudy and -30 Celsius -On site for call out SEOC SHAFT 6/7, Gas High Facility Shutdown Alarm, Fans Stopped Running W11611843. -On arrival found that Fans 1 and 2 not running. -O2 monitor #1 low low alarm, interlocking fans. -Unable to open door to ventilate room E-lock not working. -I placed fan one in local left running for the weekend. -Will investigate O2 monitor #1 low low alarm early next week. | SEC Altona Air Handling Facility (Shaft 6/7) | 2026-01-24
WW-CEAST | January | -station check of site -reviewed SCADA -inspected site -entered data into sharepoint -station okay | SEC Altona Air Handling Facility (Shaft 6/7) | 2026-01-14
WW-WEST | January | Harie Rajamithiran(OIT) working under the direction of Daniel Hirstwood(OIC) -Completed station check, no abnormalities found -Granted access to Embridge for metering | Nobleton Janet St. Sewage Pumping Station | 2026-01-16
WW-WEST | January | Collected weekly compliance samples | Nobleton Janet St. Sewage Pumping Station | 2026-01-28
WW-WEST | January | Harie Rajamithiran(OIT) working under the direction of Daniel Hirstwood(OIC). -Completed washroom cleaning and housekeeping -Completed station check, no issues found | Nobleton Janet St. Sewage Pumping Station | 2026-01-30
WW-WEST | January | Harie Rajamithiran(OIT) working under the direction of Gavin Walker(OIC). -Completed station check, no abnormalities found | Nobleton Janet St. Sewage Pumping Station | 2026-01-20
WW-WEST | January | Harie Rajamithiran(OIT) working under the direction of Gavin Walker(OIC). -Completed station check, no issues found -Completed valve exercises, no issues found | Nobleton Janet St. Sewage Pumping Station | 2026-01-27
WW-WEST | January | Harie Rajamithiran(OIT) working under the direction of Gavin Walker(OIC). -Completed station check, no abnormalities found -Completed consolidated wet well inspection, no abnormalities found -Tested wet well overflow alarm, no abnormalities found -Tested automated crane hoist, no abnormalities found -Conducted wet well valve exercise | Nobleton Janet St. Sewage Pumping Station | 2026-01-09
WW-WEST | January | Harie Rajamithiran(OIT) working under the direction of Gavin Walker(OIC) . -Completed station check , no abnormalities found | Nobleton Janet St. Sewage Pumping Station | 2026-01-13
WW-WEST | January | Isolated suction and discharge piping Drained piping and opened victaulic to have dry pipe Welded crack Reassembled and flooded piping. Rotated through pumps to run pump 1. Pump one operating correctly. Complete. | Nobleton Janet St. Sewage Pumping Station | 2026-01-12
WW-WEST | January | Collected weekly sewage samples | Nobleton Janet St. Sewage Pumping Station | 2026-01-07
WW-WEST | January | Rotated pump duty to pump 2 Locked out Pump 1 to make piping repairs | Nobleton Janet St. Sewage Pumping Station | 2026-01-12
WW-WEST | January | Harie Rajamithiran(OIT) working under the direction of Gavin Walker(OIC). -Collected weekly compliance samples | Nobleton Janet St. Sewage Pumping Station | 2026-01-14
WW-WEST | January | Harie Rajamithiran(OIT) working under the direction of Daniel Hirstwood(OIC). -Completed station check, no abnormalities found. | Nobleton Janet St. Sewage Pumping Station | 2026-01-02
WW-WEST | January | Harie Rajamithiran(OIT) working under the direction of Gavin Walker(OIC). -Tested autodialer alarm -Tested, Inspected and ran generator -Tested Hi/Low temperature -Tested dry well flood alarm -Tested sump pit floats -Inspected pumps/air relief valve -Inspected RS sampler -Conducted station check -Conducted JH&S inspected | Nobleton Janet St. Sewage Pumping Station | 2026-01-06
WW-CEAST | January | on-site to perform station check and work orders Heater element: 77.6F hydro meter: 273475 odour control scrubber inspection, filter cleaning completed JHSC Health & Safety Inspection completed Fan running, condensate is draining, no foul odour detected. | Bayview & Steeles Air Management Facility | 2026-01-08
WW-CEAST | January | on-site to perform station check Heater element: 90.1F hydro meter: 276410 kWh Fan running, condensate is draining, no foul odour detected. | Bayview & Steeles Air Management Facility | 2026-01-23
WW-CEAST | January | -station check of site -fan running -inspected site -Heater Element: 78F -no odour detected -station okay | Bayview & Steeles Air Management Facility | 2026-01-30
WW-CEAST | January | on-site to perform station check and work orders Heater element: 94.2F hydro meter: 274257 kWh Mist eliminator filter, clean and replace completed. Fan running, condensate is draining, no foul odour detected. | Bayview & Steeles Air Management Facility | 2026-01-12
WW-CEAST | January | -station check of site -reviewed SCADA -inspected site -entered data into Sharepoint -Nutrient Tank Inspection -Recirculation Pump Inspection -Booster pumps/solenoid inspection -station okay | SEC Pickering Odour Control Facility (York/Durham) | 2026-01-21
WW-CEAST | January | On site for station check. Entered station readings to sharepoint. Inspect site, reviewed Scada. No issues found. Station Ok. | SEC Pickering Odour Control Facility (York/Durham) | 2026-01-27
WW-CEAST | January | -on site for Housekeeping -reviewed SCADA -inspected site -station okay | SEC Pickering Odour Control Facility (York/Durham) | 2026-01-23
WW-CEAST | January | -station check of site and monthly work orders -reviewed SCADA -inspected site -entered data into SharePoint -monthly generator test run, notified ROC -JHSC inspection -Nutrient Tank Batch Mixing -started generator at 09:34 -stopped generator at 10:37 Generator Start Hours: 261:45 Generator Stop Hours: 262:48 Run Time: 1:03 Fuel Start: 1.98m/3640L Fuel Stop: 1.96/3611L Fuel Used: 29L -generator test run successful, back on utility power, fan 2 and fan 1 back to auto, fan 2 running, bypass knife gate open -work orders complete -station okay | SEC Pickering Odour Control Facility (York/Durham) | 2026-01-07
WW-CEAST | January | -station check of site -inspected site -reviewed SCADA -entered data into sharepoint -nutrient tank inspection -station okay | SEC Pickering Odour Control Facility (York/Durham) | 2026-01-14
WW-WEST | January | - Raked bin and cleaned area. Pushed bin back in - Checked screen, oil is good - Performed weekly pump test. Ran each pumps 1-4 manually, one at a time, and recorded readings. Check valve for pump 3 not closing. Work order already created. Pump 5 OOS Pump 1: 581 L/s, pressure 289 kPa Pump 2: 453.4 L/s at 100%, pressure 262 kPa Pump 3: 133.4 L/s at 100% speed, pressure 215 kPa Pump 4: 467 L/s at 100% speed, pressure 273 kPa - Checked station and recorded readings on SharePoint. No new issues found | Vaughan Black Creek Pumping Station | 2026-01-23
WW-WEST | January | Onsite for station check and weekly pump run test. Station check complete - no new issues. Reviewed trends and entered data into SharePoint. Ran pump test: Pump1 - 583.9L/s at285kpa Pump 2 - 465.5L/s at 260kpa at 100% Pump 3 130.2L/s at 214kpa at 100% Pump4 - 460.8L/s at 269kpa at 100% Pump 5 -OOS | Vaughan Black Creek Pumping Station | 2026-01-16
WW-CEAST | January | completed inspection and media replacement of passive odour control scrubbers at the following locations: Leslie & Major Mackenzie Warden & Enterprise Woodbine Ave & 16th Ave VC Milne Park Tuclor Lane / Hwy 48 | Central-East Wastewater Linear System | 2026-01-14
WW-WEST | January | Checked out diesel 2 pink fluid. Fluid is not diesel. Leak appears to have come from petcock on block heater. Currently not leaking. Cleaned up liquid underneath generator. | Vaughan Black Creek Pumping Station | 2026-01-15
WW-WEST | January | - Checked station and trends. Recorded readings on SharePoint. No new issues - Created work order for screen room oxygen Lolo alarm. | Vaughan Black Creek Pumping Station | 2026-01-20
WW-WEST | January | Checked water line which is dry currently. Followed line to main floor and floor is not sealed where water line comes through. Suspect water from wash down/garden hose ran through insulation to opening on B1. Took multiple photos of sanitary line as cast pipe and fittings are cracked. Multiple fittings and pipe will be required. | Vaughan Black Creek Pumping Station | 2026-01-15
WW-WEST | January | - Checked screen, oil is good - Performed weekly pump test. Ran each pumps 1-4 manually, one at a time, and recorded readings. Check valve for pump 3 not closing. Work order already created. Pump 5 OOS Pump 1: 589 L/s, pressure 294 kPa Pump 2: 471 L/s at 100%, pressure 268 kPa Pump 3: 131.7 L/s at 100% speed, pressure 214 kPa Pump 4: 462.7 L/s at 100% speed, pressure 277 kPa - Checked station and recorded readings on SharePoint. Found leak coming through the clean out of the sanitary drain line on B5. Seems the screw is loose or the the line is plugged. Ladder is not tall enough and cannot reach the ceiling safely to remedy the issue. Notified TL | Vaughan Black Creek Pumping Station | 2026-01-27
WW-WEST | January | Checked station and trends, and recorded readings on SharePoint. No new issues | Vaughan Black Creek Pumping Station | 2026-01-30
WW-WEST | January | Took garbage out and cleaned washroom | Vaughan Black Creek Pumping Station | 2026-01-20
WW-WEST | January | Completed the comprehensive cleaning work order | Vaughan Black Creek Pumping Station | 2026-01-26
WW-WEST | January | On site to replace cracked floor drain pipes on B1. | Vaughan Black Creek Pumping Station | 2026-01-22
WW-WEST | January | Called ROC to inform of work being done Completed dry well inspection. Inspected check valves. Tested dry well flood alarm and checked sump pit operation. Tested dialer alarm - alarm received by ROC. Tested hi/lo temp alarm. Inspected RS pumps and ran pumps in manual Pump 1 - 581.9L/s at 290KPa Pump 2 - 469L/s at 262kpa at 100% Pump 3 - 126.4L/s at 212kpa at 100% Pump 4 - 453.5L/s at 207kpa at 100% Pump 5 - OOS Actuated suction valves and inspected RS valves. Flushed and inspected air relief valves Completed wet well inspection Cleaned and lubricated the bar screen | Vaughan Black Creek Pumping Station | 2026-01-12
WW-WEST | January | - Checked station and trends, and recorded readings on SharePoint. No new issues found. Levelled bin | Vaughan Black Creek Pumping Station | 2026-01-13
WW-WEST | January | - Levelled and pushed bin out for pick up. Cleaned up the general area - Performed JHSC inspection. No issues - Performed station check and recorded readings on SharePoint. No new issues. - Contractor onsite for the semi annual diesel generator testing. Notified ROC of the work being performed - Performed monthly generator testing. Inspected the generators and fuel level. Started the generator at 9:58. Recorded readings on SharePoint after 30 minutes, no issues. Ran for approximately one hour. Runtime for generator 1 from 477.9 hrs to 479.0 hrs - Started generator 2 at 11:07. Recorded readings after 30 minutes. Run time for generator 2 from 490.6 hrs to 491.6 hrs. No issues with readings. - Fuel level readings before: 97 cm (6173 L). After gen test 95 cm (6053 L) - Reset alarms caused by generator test. - Checked for hazardous waste. None found - Inspected the odour control unit. No issues. Filters below 2.5 inch and does not need cleaning - Inspected the hoist system. No issues Update: pump 4 check valve not closing. Will monitor and create a work order | Vaughan Black Creek Pumping Station | 2026-01-06
WW-WEST | January | Onsite for station check and pump run tests Station check completed reviewed trends and added data into SharePoint. Empty bin pushed back in, bar screen ok. Pump1 582.5 at 299kpa Pump 2 460.8 at 264kpa at 100% Pump 3 136.7L/s at 215kpa at 100% Pump4 444.2 at 268kpa at 100% Pump 5 tripped on overcurrent causing pump 5 uncommanded stop alarm, pump 5 multiplying trip ALRM and pump 5 disc valve uncommanded close alarm. Upon checking pump 5 in B4 there?s seem to be a leak in the pump. Unsure if this is related to the pump not running. Team lead informed and WO created Left pump 5 in manual off and OOS | Vaughan Black Creek Pumping Station | 2026-01-09
WW-WEST | January | Power blip caused some alarms requiring reaetting: Reset fault on pump 1. Reset bar screen. Reset pump 3. Reset pump 3 to duty 1 and activated. Running okay now. | Vaughan Black Creek Pumping Station | 2026-01-09
WW-WEST | January | Performed Argo maintenance | Vaughan Humber Pumping Station | 2026-01-26
WW-WEST | January | Onsite for wet well work with Young Jung. ROC informed of wet well high level float alarms being triggered. Triggered wet well high level float alarms successfully and cleared. Greased bar screens and cleaned debris from wet well. - oil levels good. Lubricated wet well valves. Completed station check and added data into SharePoint. | Vaughan Humber Pumping Station | 2026-01-16
WW-WEST | January | Checked station and trends, and recorded readings on SharePoint Due to the cold weather, doors and screen roll up door are all frozen. The screen door over torqued when I attempted to open it. Eventually I got in through the side door and noticed large amounts of ice build up on all the doors and screen door. Duct inside the screen room has ice build up as well. Notified team and asked for some heaters to be brought inside the screen room. Archibus work order created | Vaughan Humber Pumping Station | 2026-01-30
WW-WEST | January | On site for scheduled work. Raked and levelled bin | Vaughan Humber Pumping Station | 2026-01-31
WW-WEST | January | Onsite to rake bins | Vaughan Humber Pumping Station | 2026-01-17
WW-WEST | January | Completed the station check Pushed the rag bins back inside Assisted miller in replacing a broken wheel on one of the bins Everything operating as intended | Vaughan Humber Pumping Station | 2026-01-23
WW-WEST | January | Reenabled RS pump duty rotate. | Vaughan Humber Pumping Station | 2026-01-16
WW-WEST | January | Disabled duty rotation leaving pump 3 in duty 1. Peel Region attempting to adjust chemicals and requested steady incoming flow until approx 11:30am. | Vaughan Humber Pumping Station | 2026-01-16
WW-WEST | January | Levelled screen room bins. | Vaughan Humber Pumping Station | 2026-01-24
WW-WEST | January | Checked station and recorded readings on SharePoint. No new issues Humber bin doors were frozen. Eventually removed enough ice to get the door moving. Levelled bin and pushed bin out for pick up | Vaughan Humber Pumping Station | 2026-01-27
WW-WEST | January | Onsite for station check - no new issues, reviewed trends and added data into SharePoint. Property services inside to fixed bar screen rollup door - rolled up door fixed and operating normally. Pushed bins out for pick up. Completed comprehensive housekeeping - swept and mopped office and diesel/Pump motor room Cleaned bathroom. | Vaughan Humber Pumping Station | 2026-01-20
WW-WEST | January | Level screen room rag bins and shift for better weight distribution. | Vaughan Humber Pumping Station | 2026-01-04
WW-WEST | January | - Levelled bin and pushed bin out for pick up. Cleaned general area - Checked screen oil level. All okay - Checked station and recorded readings on SharePoint - Finished lubricating all pumps and motors. Lubricated pump upper and lower bearing, frame bearing. Lubricated shaft bearing. Lubricated the motor upper 80g and lower bearing 60g. Removed excess grease | Vaughan Humber Pumping Station | 2026-01-13
WW-WEST | January | - Upon arrival, historian heartbeat alarm was present on local SCADA and occurred yesterday on January 8, 2026. A small gap in the trend occurred between 3:55~4:03. Issue did not occur again after this time. Spoke to PCS on call and confirmed that this was due to an update being performed - Pushed empty bins back in. Cleaned general area and levelled bin - Checked station and trends, and recorded readings on SharePoint. Upon vibrational trend check, noticed that pump 3 B3 lower vibrational reading spiked briefly past the high high setpoints to 26.03 mm/s and upper vibrational to 18.10 mm/s. The issue does not persist anymore. Will continue to monitor - Notified ROC of the work being performed - Inspected forcemain diversion chamber. All okay. Remade the pole to be able to flip the switch. High level audible alarm heard and valve chamber high alarm on scada received - Greased pump 1 motor upper bearing. In progress | Vaughan Humber Pumping Station | 2026-01-09
WW-WEST | January | Raked bins. | Vaughan Humber Pumping Station | 2026-01-11
WW-WEST | January | Onsite for station check and work orders. Station check ok - no new issues added data into SharePoint. Check valves all appear good, leak on check valve 2 fixed and still good. Called ROC to inform of generator run test and alarm testing. Transferred power to generator at 9am. Collected data before transferring back to hydro at 10am. Both transfers went well. Transfer back to hydro caused exhaust fan VFDs to fault - reset and back to normal. inspected heat exchanger radiator - no issues. Tested dialler alarm Tested high/low level alarm - set back to normal range when finished. Tested dry well floor alarm. Inspected drywall sump pit - operated normally pumps and floats ok. Placed bins outside and replaced with empty bins. Completed JHSC inspection and checked site for hazardous waste. | Vaughan Humber Pumping Station | 2026-01-06
WW-WEST | January | In to Complete Scheduled WOs. Enabled Batch Waste Set-point. RAS Pumps Auto Off in Preparation for Wasting @ 09:00. GFL On-site for Sludge Load. Sludge Thickening Tank #2 Outlet Valve Manual Open, Transferred Thickened Sludge. Outlet Valve Returned to Manual Closed. WAS Pump #1 and 2 Manual On and Off Intermittently and Sequentially for Wasting. Wasting Complete, Reset Batch Wasting Set-point. RAS Pumps #2 and 4 Running in Auto. Wasted 10 m3 from Each Clarifier. Topped Up Soda Ash Hopper ?> 12 Bags. Completed HWs and Tertiary Building Sump Inspections. Tested Hi Level Alarms and Confirmed Reception by the ROC. Returned to Service. Cleared Associated Alarms. | Kleinburg Water Resource Recovery Facility | 2026-01-16
WW-WEST | January | Remotely Placed Scum Pump #1 in Manual On for Scum Tank Drawdown. Drawdown Complete, Returned Pump to Auto and Service. | Kleinburg Water Resource Recovery Facility | 2026-01-28
WW-WEST | January | There's a gap in the effluent flow trend on January 27 from 8:42 until 20:32. Gap likely due to faulty effluent flow transmitter. Created work order to instrumentation and notified PCS on call about the gap on January 31, 2026 at 10:30. Also notified TL | Kleinburg Water Resource Recovery Facility | 2026-01-27
WW-WEST | January | In to Complete Scheduled WOs. Notified ROC. Contractor On-site for Compressor Deficiency Repair Work. Enabled Batch Waste Set-point. RAS Pumps Auto Off in Preparation for Wasting @ 08:50. Lowered Sludge Thickening Tank #2 Decant Slip Tube. WAS Pump #1 and 2 Manual On and Off Intermittently and Sequentially for Wasting. Decant Complete, Raised Decant Slip Tube. Sludge Thickening Tank #2 Outlet Valve Manual Open, Transferred Thickened Sludge. Outlet Valve Returned to Manual Closed. UV Channel #1 Bank B Lamp Failure Alarm Outstanding. Manually Rotated UV Channel Duty, Channel #2 in Duty #1. Rotated Active Sludge Thickening Tank. WAS Valve #1 Manual Closed, WAS Valve #2 Manual Open. Wasting Complete, Reset Batch Wasting Set-point. RAS Pumps #2 and 4 Running in Auto. Wasted 15 m3 from Clarifier #1 and 10 m3 from Clarifier #2. Placed UV Channel #1 in Manual Off. Replaced Burnt Bulb and Tested Unit with No Issues. Returned to Service. Cleared Associated Alarms. Topped Up Soda Ash Hopper ?> 17 Bags. Placed Clarifier Helical Skimmers in Manual On for Scum Tank Flushing. Placed Scum Pump #1 in Manual On. Scum Tank Flushing and Drawdown Complete. Returned All to Auto and Service. | Kleinburg Water Resource Recovery Facility | 2026-01-26
WW-WEST | January | In to Complete Reg. Sampling and Scheduled WOs. Notified ROC. Enabled Batch Waste Set-point. RAS Pumps Auto Off in Preparation for Wasting @ 08:00. Contractors On-site for TSSA Upgrade Testing. Activated Generators in Manual Individually for Fuel Line Testing. WAS Pump #1 and 2 Manual On and Off Intermittently and Sequentially for Wasting. Topped Up Soda Ash Hopper ?> 8 Bags. TSSA Upgrade Fuel Line Testing Complete. Identified Fuel Leak and Completed Repairs. Returned Both Generators to Service. Cleared Associated Alarms. Completed Generator Load Testing Post TSSA Fuel Line Testing. Rotated UV Systems Accordingly for Proper Transfer and Generator Power Source Allocation. Transferred Station to Generator Power Twice with No Issues. Acknowledged Associated Alarms. Transferred Station Back to Utility Power Twice with No Issues. Cleared Associated Alarms. Wasting Complete, Reset Batch Wasting Set-point. RAS Pumps #1 and 3 Running in Auto. Wasted 15 m3 from Each Clarifier. Completed UV System Inspection and Maintenance. No Issues Found. Returned to Service. Cleared Associated Alarms. | Kleinburg Water Resource Recovery Facility | 2026-01-21
WW-WEST | January | In to Complete Scheduled WOs. Enabled Batch Waste Set-point. RAS Pumps Auto Off in Preparation for Wasting @ 10:00. Sludge Room Access Door Locking Mechanism Experiencing Issues, Notified Appropriate Staff. Lowered Sludge Thickening Tank #2 Decant Slip Tube. WAS Pump #1 and 2 Manual On and Off Intermittently and Sequentially for Wasting. Decant Complete, Raised Decant Slip Tube. Sludge Thickening Tank #2 Outlet Valve Manual Open, Transferred Thickened Sludge. Outlet Valve Returned to Manual Closed. Topped Up Soda Ash Hopper ?> 9 Bags. Wasting Complete, Reset Batch Wasting Set-point. RAS Pumps #1 and 4 Running in Auto. Wasted 12 m3 from Each Clarifier. Completed RAS Pump #2 Inspection. Notified ROC. Driveshaft and Coupling OK, Pump Free Spinning. Returned to Service and Duty. No Recurrence of Previous VFD Fault. Cleared Associated Alarms. | Kleinburg Water Resource Recovery Facility | 2026-01-30
WW-WEST | January | In to Complete Scheduled WOs. WAS Pump #1 and 2 Manual On and Off Intermittently and Sequentially for Wasting. Topped Up Soda Ash Hopper ?> 9 Bags. Wasting Complete, Reset Batch Wasting Set-point. RAS Pumps #1 and 3 Running in Auto. Wasted 17 m3 from Clarifier #1 and 19 m3 from Clarifier #2. TSSA Upgrade Contractors On-site Found Slight Glycol Leak on Generator #1. Notified Appropriate Project Staff for Investigation. | Kleinburg Water Resource Recovery Facility | 2026-01-23
WW-WEST | January | Under direction of OIC, Marcus Remonde. Worked with contractor electrician to disconnect generator fuel tanks IO from the PAC CP. under TSSA there is a new fuel tank that will have LIT and digital inputs installed at a later date. No outstanding alarms on SCADA for this system. | Kleinburg Water Resource Recovery Facility | 2026-01-21
WW-WEST | January | Checked station and recorded readings on SharePoint. No new issues | Kleinburg Water Resource Recovery Facility | 2026-01-29
WW-WEST | January | In to Complete Scheduled WOs. Enabled Batch Waste Set-point. RAS Pumps Auto Off in Preparation for Wasting @ 09:00. Topped Up Soda Ash Hopper ?> 8 Bags. WAS Pump #1 and 2 Manual On and Off Intermittently and Sequentially for Wasting. Wasting Complete, Reset Batch Wasting Set-point. RAS Pumps #1 and 3 Running in Auto. Wasted 15 m3 from Clarifier #1 and 10 m3 from Clarifier #2. Completed Air Compressors Maintenance. Flagged Potential Condensate Drainage Issue, Notified Appropriate Staff. Oil Levels, Air Filters and Belts OK. Returned to Service. Cleared Associated Alarms. Notified by ROC of Filter #4 Inlet Gate Valve Failed to Open. Inspected and Tested Unit in Local. No Issues Found. Returned to Service. Cleared Associated Alarms. Completed Biorem Odour Control Unit Inspection. No Issues Found. | Kleinburg Water Resource Recovery Facility | 2026-01-20
WW-WEST | January | Added 9 x 25kg bags of soda ash to the auto dispenser hopper | Kleinburg Water Resource Recovery Facility | 2026-01-24
WW-WEST | January | In to Complete Scheduled WOs. Enabled Batch Waste Set-point. RAS Pumps Auto Off in Preparation for Wasting @ 08:40. WAS Pump #1 and 2 Manual On and Off Intermittently and Sequentially for Wasting. Wasting Complete, Reset Batch Wasting Set-point. RAS Pumps #2 and 4 Running in Auto. Wasted 15 m3 from Each Clarifier. Topped Up Soda Ash Hopper ?> 14 Bags. Received Soda Ash Delivery with No Issues. Reviewed and Signed Documentation. Completed Aer. Tank Diffuser Line Condensate Flushing with No Issues. Returned to Service. | Kleinburg Water Resource Recovery Facility | 2026-01-19
WW-WEST | January | - performed station check and recorded readings on SharePoint. No new issues created - Cleaned alum stains from alum containment area - Notified ROC and tested plant 2 influent chamber float alarm - Pumped down influent chamber | Kleinburg Water Resource Recovery Facility | 2026-01-28
WW-WEST | January | Remotely turned on batch wasting mode at 17:05. Set up to auto waste from 18~19, 12 m^3 from aeration tank 1 and 12 m^3 from aeration tank 2. Turned WAS pumps 1 and 2 to auto. | Kleinburg Water Resource Recovery Facility | 2026-01-31
WW-WEST | January | Onsite for work orders. Added 8 bags of soda ash to hopper. Assisted Marcus with UV channel clean out and UV maintenance. Assisted with UVT wiper replacement and maintenance. | Kleinburg Water Resource Recovery Facility | 2026-01-15
WW-WEST | January | Completed daily lab and station check - no new issues added data into SharePoint Decanted sludge thickening tank 1 and transferred remaining sludge to holding. Enabled batch wasting at 9am and set auto waste for 20m3 from 10am to 11am. After auto wasting completed manually wasted an additional 5m3 from each tank, total wasted 30m3. WAS pumps placed back into manual and RAS placed back into operation. Added 8 bags of soda ash to hopper. Cleared rags from bar screen and confirmed operation. | Kleinburg Water Resource Recovery Facility | 2026-01-22
WW-WEST | January | Remotely Placed Clarifier Helical Skimmers in Manual On for Scum Tank Flushing. Returned to Auto and Service. | Kleinburg Water Resource Recovery Facility | 2026-01-22
WW-WEST | January | Onsite to provide Panel access to consultants, ETO. | Kleinburg Water Resource Recovery Facility | 2026-01-29
WW-WEST | January | Enabled batch wasting mode Put WAS pumps in auto and programed auto wasting to begin at 10:00. Batch wasting completed Side 1: 11.15m3 Side 2: 10m3 Put was pumps in manual off and restored RAS FLOW. | Kleinburg Water Resource Recovery Facility | 2026-01-24
WW-WEST | January | Completed station check - no new issues added data into SharePoint. Cleaned and verified aeration tank DO probes. Placed UV 2 bank b into duty 1 and placed UV 1 into local off. Assisted Marcus with UV service of channel 1 bank B. When completed placed UV 1 bank b service placed Uv 1 back into remote and into duty rotation | Kleinburg Water Resource Recovery Facility | 2026-01-21
WW-WEST | January | In to Complete Scheduled WOs. Notified ROC. Contractor On-site for Generator #1 Exhaust Inspection. Placed Unit in Manual Off and Activated E-Stop. Generator #2 Remains in Service and Available In the Case of a Power Loss Event. Exhaust Inspection Complete with No Issues. Returned Generator #1 to Service. Cleared Associated Alarm. | Kleinburg Water Resource Recovery Facility | 2026-01-22
WW-WEST | January | In to Complete Scheduled WOs. Provided Access to York Regional Staff On-site for Facility Site Assessments. Enabled Batch Waste Set-point. RAS Pumps Auto Off in Preparation for Wasting @ 08:25. WAS Pump #1 and 2 Manual On and Off Intermittently and Sequentially for Wasting. Received Alum Delivery. Reviewed and Signed Documentation. Alum Tank Level: 0.91 ?> 2.66m. Wasting Complete, Reset Batch Wasting Set-point. RAS Pumps #2 and 4 Running in Auto. Wasted 12 m3 from Each Clarifier. Topped Up Soda Ash Hopper ?> 7 Bags. RAS Pump #2 VFD Fault Alarm Activated. Cleared Fault and Returned to Service, Fault Returned. Placed RAS Pump #2 in Manual Off Until Investigation Conducted, RAS Pump #1 Running in Auto. Cleared Outstanding Fault, Notified ROC and On-Call Staff Member. | Kleinburg Water Resource Recovery Facility | 2026-01-29
WW-WEST | January | Collected weekly regulatory samples | Kleinburg Water Resource Recovery Facility | 2026-01-28
WW-WEST | January | Restarted the Local SCADA server. Notified the OIC and the Remote Operations Center. | Kleinburg Water Resource Recovery Facility | 2026-01-22
WW-WEST | January | Assisted with RSHW blower oil changes, sludge loading pipe blockage and created CMUs for the WAS Motorized valves faulting and also for the oil lines to be replaced on the RSHW blower # 1 | Kleinburg Water Resource Recovery Facility | 2026-01-07
WW-WEST | January | Finished auto wasting at 19:22. Reset RAS batch wasting mode and turned WAS pumps to manual off | Kleinburg Water Resource Recovery Facility | 2026-01-31
WW-WEST | January | In to Complete Scheduled WOs. Notified ROC. Enabled Batch Waste Set-point. RAS Pumps Auto Off in Preparation for Wasting @ 08:55. WAS Pump #1 and 2 Manual On and Off Intermittently and Sequentially for Wasting. Wasting Complete, Reset Batch Wasting Set-point. RAS Pumps #2 and 4 Running in Auto. Wasted 8 m3 from Clarifier #1 and 12 m3 from Clarifier #2. Topped Up Soda Ash Hopper ?> 8 Bags. Completed Aer. DO Sensor Maintenance. Placed Probes in Calibration Mode. Cleaned and Inspected Units, No Issues Found. Returned to Service. | Kleinburg Water Resource Recovery Facility | 2026-01-28
WW-WEST | January | Enabled batch wasting mode at 9am and set Wasting to auto waste 20m3 (10m3 per side) from 10am-11am Wasting completed at 11am - WAS pumps placed back in manual and RAS pumps placed back in operation. Added 8 bags of soda ash to hopper. | Kleinburg Water Resource Recovery Facility | 2026-01-17
WW-WEST | January | In to Complete Scheduled WOs. Notified ROC. Enabled Batch Waste Set-point. RAS Pumps Auto Off in Preparation for Wasting @ 09:00. Lowered Sludge Thickening Tank #1 Decant Slip Tube. WAS Pump #1 and 2 Manual On and Off Intermittently and Sequentially for Wasting. Decant Complete, Raised Decant Slip Tube. Sludge Thickening Tank #1 Outlet Valve Manual Open, Transferred Thickened Sludge. Outlet Valve Returned to Manual Closed. Wasting Complete, Reset Batch Wasting Set-point. RAS Pumps #2 and 4 Running in Auto. Wasted 10 m3 from Clarifier #1 and 13 m3 from Clarifier #2. Topped Up Soda Ash Hopper ?> 7 Bags. Completed Biorem Odour Control Unit Inspection. Replaced Driveshaft Belts and Greased Bearings. No Other Issues Found. Returned to Service. Completed Filter Bypass Float Alarm Test. Confirmed Reception by the ROC. Returned to Service. Cleared Associated Alarm. | Kleinburg Water Resource Recovery Facility | 2026-01-27
WW-WEST | January | Notified by ROC of a trend issue of plant effluent flow. There's a gap in the effluent flow trend from January 27 at 8:42 until 20:32. In addition, the trend flatlines on Jan 29 10:36 at 11.64 L/s and the readings doesn't fluctuate as it should. Likely faulty flow indicating transmitter. Created a work order to instrumentation and notified PCS on call of the gap. Also notified TL | Kleinburg Water Resource Recovery Facility | 2026-01-31
WW-WEST | January | Added 9 bags of soda ash into the hopper. Moved hose in aeration tank 2 outlet for foam control to aeration tank 1 outlet | Kleinburg Water Resource Recovery Facility | 2026-01-31
WW-WEST | January | Remotely Enabled Batch Waste Set-point. RAS Pumps Auto Off in Preparation for Wasting @ 09:55. | Kleinburg Water Resource Recovery Facility | 2026-01-23
WW-WEST | January | Set valves to wast to tank 2. Added 16 bags to soda ash hopper. | Kleinburg Water Resource Recovery Facility | 2026-01-11
WW-WEST | January | Onsite for work orders - called ROC to inform of work being done on compressors. Placed air compressor 1 into off and activated E stop generating e stop fault alarm. Checked filters and belts. All ok. Changed oil and placed compressor 1 back into service. Confirmed operation. Placed air compressor 2 into off and activated E stop generating e stop fault alarm. Checked filters and belts. All ok. Changed oil and placed compressor back into service. Confirmed operation. Exercised aeration header butterfly valves and placed all valves back into original positions. Cleaned rags from bar screen and confirmed operation. Pulled rags from diversion chamber valve stem and checked for rag build up on DO probes. | Kleinburg Water Resource Recovery Facility | 2026-01-13
WW-WEST | January | Onsite to perform work orders and maintenance on blowers. Called ROC to inform of of work being done onsite. Placed SLDG blower 1 in LOTO - generated E stop alarm. Changed oil. Belts and filter ok. Placed back in service and cleared alarms. Rotated duty to SLDG blower 1 and placed SLDG blower 2 in LOTO - generated E stop alarm. Changed oil. Belts and filter ok. Placed back in service and cleared alarms. Placed RSHW blower 2 in LOTO generated e stop alarm- changed oil with Dan. Filter ok. Returned to service and cleared alarms and rotated duty to RSHW blower 2 to place RSHW blower 1 on LOTO, generated E stop alarms. Could not change oil - Dan created WO Filter ok. Placed back in service and cleared alarms. Placed aeration blower 1 in LOTO generated E stop alarms. Oil levels, belt and filter all ok. Placed back in service and rotated duty to aeration blower 1 to place aeration blower 2 in LOTO, e stop alarm generation. Oil levels belts and filter ok. Placed back in service and cleared alarms Placed diversion tank blower 1 and 2 in LOTO both oil levels belts and filters ok. Placed both blowers back online. Placed grit blowers 1 and 2 in LOTO generated e stop alarms, classifier and vortex alarms. Both oil levels, belts and filters good. Placed back in service and cleared all alarms. Exercised scum tank 3 valve. | Kleinburg Water Resource Recovery Facility | 2026-01-07
WW-WEST | January | In to Complete Scheduled WOs. Enabled Batch Waste Set-point. RAS Pumps Auto Off in Preparation for Wasting @ 08:35. Lowered Sludge Thickening Tank #2 Decant Slip Tube. WAS Pump #1 and 2 Manual On and Off Intermittently and Sequentially for Wasting. Decant Complete, Raised Decant Slip Tube. Sludge Thickening Tank #2 Outlet Valve Manual Open, Transferred Thickened Sludge. Outlet Valve Returned to Manual Closed. Topped Up Soda Ash Hopper ?> 9 Bags. Rotated Active Sludge Thickening Tank. WAS Valve #1 Manual Closed, WAS Valve #2 Manual Open. Wasting Complete, Reset Batch Wasting Set-point. RAS Pumps #2 and 4 Running in Auto. Wasted 10 m3 from Clarifier #1 and 15 m3 from Clarifier #2. Completed Distribution Chamber Butterfly Valve Manual Exercise with No Issues. Returned to Service. Completed HWs Building Heat Trace Inspections with No Issues. Completed Raw Sewage and Final Effluent Composite Sampler Inspections. Replaced FE Sampler Tubing, Tested Unit and Returned to Service. No Other Issues Found. | Kleinburg Water Resource Recovery Facility | 2026-01-13
WW-WEST | January | In to Complete Scheduled WOs. Enabled Batch Waste Set-point. RAS Pumps Auto Off in Preparation for Wasting @ 09:00. Adjusted Soda Ash Conveyor Dosage Timer Based on In-House Laboratory Results: 7.0 ?> 6.5 s. WAS Pump #1 and 2 Manual On and Off Intermittently and Sequentially for Wasting. Wasting Complete, Reset Batch Wasting Set-point. RAS Pumps #2 and 4 Running in Auto. Wasted 5 m3 from Each Clarifier. Completed UVT Inspection and Profile Replacement, UV Channel #1, Bank A Service and UV Channel Clean Out with No Issues. Returned to Service. | Kleinburg Water Resource Recovery Facility | 2026-01-15
WW-WEST | January | In to Complete Scheduled WOs. Enabled Batch Waste Set-point. RAS Pumps Auto Off in Preparation for Wasting @ 08:30. WAS Pump #1 and 2 Manual On and Off Intermittently and Sequentially for Wasting. Rotated Active Sludge Thickening Tank. WAS Valve #2 Manual Closed, WAS Valve #1 Manual Open. Topped Up Soda Ash Hopper ?> 8 Bags. Wasting Complete, Reset Batch Wasting Set-point. RAS Pumps #2 and 4 Running in Auto. Wasted 15 m3 from Each Clarifier. Placed Clarifier Helical Skimmers in Manual On for Scum Tank Flushing. Returned to Auto and Service. Hosed and Flushed Scum Tank. Scum Pump #1 Manual On for Scum Tank Drawdown. Drawdown Complete, Returned Pump #1 to Auto and Duty. Completed Aer. Tank Diffuser Line Condensate Flushing with No Issues. Returned to Service. | Kleinburg Water Resource Recovery Facility | 2026-01-12
WW-WEST | January | Remotely Returned WAS Pumps #1 and 2 to Manual Off. Adjusted Batch Wasting Timeframe: 200 --> 240 mins. | Kleinburg Water Resource Recovery Facility | 2026-01-12
WW-WEST | January | - Decanted the sludge thickening tank then transferred sludge into the holding tank - Inspected WAS and RAS pumps. No issues found. Couplings and check valves are all good - Exercised WAS and RAS valves - Inspected sand filter hose. No issues | Kleinburg Water Resource Recovery Facility | 2026-01-14
WW-WEST | January | In to Complete Scheduled WOs. Enabled Batch Waste Set-point. RAS Pumps Auto Off in Preparation for Wasting @ 08:45. Lowered Sludge Thickening Tank #2 Decant Slip Tube. WAS Pump #1 and 2 Manual On and Off Intermittently and Sequentially for Wasting. Decant Complete, Raised Decant Slip Tube. Sludge Thickening Tank #2 Outlet Valve Manual Open, Transferred Thickened Sludge. Outlet Valve Returned to Manual Closed. Wasting Complete, Reset Batch Wasting Set-point. RAS Pumps #1 and 3 Running in Auto. Wasted 10 m3 from Clarifier #1 and 15 m3 from Clarifier #2. Found Soda Ash Conveyor Disch. Ducting Detached from Conveyor Housing. Soda Ash Dosing Affected. Returned Discharge. Ducting to Service. Topped Up Soda Ash Hopper ?> 8 Bags. Reject Sump Pump #1 Fault Alarm Outstanding. Reset Fault and Cleared Alarm. Returned Pump to Service. | Kleinburg Water Resource Recovery Facility | 2026-01-09
WW-WEST | January | In to Complete Reg. Sampling and Scheduled WOs. Adjusted Soda Ash Conveyor Dosage Timer Based on In-House Laboratory Results: 8.5 --> 7.00 s. Enabled Batch Waste Set-point. RAS Pumps Auto Off in Preparation for Wasting @ 10:00. Sludge Loading Pumps Experienced Several Hi Disch. Pressure Interlocks. Cleared and Reset Alarms. WAS Pump #1 and 2 Manual On and Off Intermittently and Sequentially for Wasting. Topped Up Soda Ash Hopper ?> 10 Bags. Wasting Complete, Reset Batch Wasting Set-point. RAS Pumps #1 and 3 Running in Auto. Wasted 10 m3 from Clarifier #1 and 15 m3 from Clarifier #2. Reject Sump Pump #1 Fault Alarm Outstanding. Reset Fault and Cleared Alarm. Returned Pump to Service. Known Issue, WO Previously Made and Pending for Maintenance. UV #1 Major Fault Alarm Active Upon Testing of Cassette B, Rack #2 Testing. Ballast Fault Remains Outstanding. Returned Unit to Service, Cleared Associated Alarms. Completed DO Sensor Maintenance and Inspection. Removed Debris and Cleaned Sensor Heads. No Other Issues Found. Returned to Service. Created Follow Up WO for Outstanding Scum Pump Disch. Heat Trace #1 Fault Alarm Generated by Previous PCS/PAC Panel Investigation --> W11570211. | Kleinburg Water Resource Recovery Facility | 2026-01-07
WW-WEST | January | Enabled 200 minute ras timer. Set auto wasting for 40 m3 between 10 and 12 in 8 cycles. Set was pumps to auto. | Kleinburg Water Resource Recovery Facility | 2026-01-11
WW-WEST | January | In to Complete Scheduled WOs. Enabled Batch Waste Set-point. RAS Pumps Auto Off in Preparation for Wasting @ 08:50. WAS Pump #1 and 2 Manual On and Off Intermittently and Sequentially for Wasting. Wasting Complete, Reset Batch Wasting Set-point. RAS Pumps #1 and 3 Running in Auto. Wasted 10 m3 from Clarifier #1 and 12 m3 from Clarifier #2. Rotated Active Sludge Thickening Tank. WAS Valve #2 Manual Closed, WAS Valve #1 Manual Open. Placed Clarifier Helical Skimmers in Manual On for Scum Tank Flushing. Returned to Auto and Service. Hosed and Flushed Scum Tank. Removed Floating Debris. Scum Pump #1 and 2 in Manual On Independently for Tank Drawdown. Drawdown Complete, Returned Pumps to Auto and Duty. Topped Up Soda Ash Hopper ?> 10 Bags. Reject Sump Pump #1 Fault Alarm Outstanding. Reset Fault and Cleared Alarm. Returned Pump to Service. | Kleinburg Water Resource Recovery Facility | 2026-01-08
WW-WEST | January | Onsite to complete work orders in headworks building. Contacted ROC to inform of work being done in headworks. Performed LOTO on vortex 1 and 2. Greased and checked oil levels - both ok. Cleaned rags from vortex blades. Returned both vortex 1 and 2 back into operation - confirmed operation. Greased and checked oil level on grit classifier and screw. Confirmed operation. Performed LOTO on traveling bar screen and auger. Checked oil levels and greased nipples. Cleaned rags from bar screen and flushed with hose to clean. Placed back into service and confirmed operation. Opened WAS_MV4 valve to clear interlock on WAS pumps 3 and 4 for inspection. Checked oil levels and condition of WAS pumps 3 and 4, both ok. Placed WAS pumps 3 and 4 in service and ran manually to confirm operation. After inspection placed both pumps back into OOS and returned WAS_MV4 valve to closed position the place WAS pumps 3 and 4 in interlock. Picked rags from diversion valve stem and aeration inlet valve stems. Checked aeration outlet for rags. UV #2 display panel not reading dosage and not showing the channel as in operation, UV channel 2 currently on and in operation. Reset display panel causing UV channel 2 system alarms and showing a gap in UV treatment - UV display panel does not control actual power to the UV and UV channel 2 remained on and in operation throughout. Alarms due to connection being lost to scada After panel reset UV channel 2 display now reading accurately. | Kleinburg Water Resource Recovery Facility | 2026-01-08
WW-WEST | January | Collected regulatory weekly samples. Completed daily lab and station check - no new issues. Added data into SharePoint. Enabled batch wasting mode at 9am and set auto waste for 20m3 from 10am to 11am. Upon wasting completion set WAS pumps back into manual and RAS back in operation. Added 8 bags of soda ash to hopper. Raked rags from bar screen and confirmed bar screen operation. Cleared rags from diversion chamber valve stem and pulled rags from aeration tank outlet. Cleaned and verified DO probes. | Kleinburg Water Resource Recovery Facility | 2026-01-14
WW-WEST | January | Onsite for sludge loading pumps not working. Checked and found exterior pipe below 0. Used tiger torch to heat up exterior piping. Test ran pump into bin. Okay. Complete. | Kleinburg Water Resource Recovery Facility | 2026-01-07
WW-WEST | January | In to Complete Scheduled WOs. Enabled Batch Waste Set-point. RAS Pumps Auto Off in Preparation for Wasting @ 08:40. PCS On-site to Perform PAC Investigative Work Post Generator Run from Previous Day. Lowered Sludge Thickening Tank #1 Decant Slip Tube. WAS Pump #1 and 2 Manual On and Off Intermittently and Sequentially for Wasting. Decant Complete, Raised Decant Slip Tube. Sludge Thickening Tank #1 Outlet Valve Manual Open, Transferred Thickened Sludge. Outlet Valve Returned to Manual Closed. Wasting Complete, Reset Batch Wasting Set-point. RAS Pumps #1 and 3 Running in Auto. Wasted 5 m3 from Clarifier #1 and 10 m3 from Clarifier #2. Topped Up Soda Ash Hopper ?> 12 Bags. Completed Biorem Odour Control Unit Inspection. No Issues Found. Scum Pump Disch. Heat Trace #1 Fault Alarm Remains Outstanding Post PCS Work. Unable to Locate Deriving Issue. Scum Tank Heat Trace Remains Active. | Kleinburg Water Resource Recovery Facility | 2026-01-06
WW-WEST | January | Notified by PCS John DiMarco that today Ian and Kevin from PCS were following up on an incident that occurred Jan 05 (multiple PAC fail alarms). During their testing a 23 minute data gap was produced from 10:21 to 10:44. No operation issues occurred as a result. | Kleinburg Water Resource Recovery Facility | 2026-01-06
WW-WEST | January | Onsite to investigate pac minor faults caused by network and power issues yesterday. Fail power at headworks pac UPS stayed up for expected period of time then system lost power. Restored power and switch came back up. Local computer did not restart correctly. Data gap from 10:21 am to 10:45. | Kleinburg Water Resource Recovery Facility | 2026-01-06
WW-WEST | January | In to Complete Scheduled WOs. Enabled Batch Waste Set-point. RAS Pumps Auto Off in Preparation for Wasting @ 09:00. Placed Clarifier Helical Skimmers in Manual On for Scum Tank Flushing. Returned to Auto and Service. Sludge Loading Pumps Experienced Several Hi Disch. Pressure Interlocks. Cleared and Reset Alarms. Topped Up Soda Ash Hopper ?> 13 Bags. WAS Pump #1 and 2 Manual On and Off Intermittently and Sequentially for Wasting. Rotated Active Sludge Thickening Tank. WAS Valve #1 Manual Closed, WAS Valve #2 Manual Open. Wasting Complete, Reset Batch Wasting Set-point. RAS Pumps #1 and 3 Running in Auto. Wasted 10 m3 from Each Clarifier. | Kleinburg Water Resource Recovery Facility | 2026-01-05
WW-WEST | January | Activated batch wasting mode and programmed wasting to begin at 8am. | Kleinburg Water Resource Recovery Facility | 2026-01-04
WW-WEST | January | Decanted sludge thickening tank and transferred remaining sludge to holding tank. Completed daily lab and station check - no new issues. Added data into SharePoint. Enabled batch wasting at 10am and set auto waste for 40m3 from 11am to 1pm. WAS pumps placed back in manual and RAS back in operation upon wasting completion. Added 17 bags of soda ash to hopper. | Kleinburg Water Resource Recovery Facility | 2026-01-02
WW-WEST | January | Called ROC to inform of generator run tests and work being done Inspected circular plant aeration blowers 1-4. All oil levels ok and belts ok. Noticed some cracking in the coupling of blower #1 but ran in manual fine with no leakage. Ran all in manual and all ran ok. Inspected circular clarifier drive - chain okay and oil levels good. Reset filter reject sump pump 1 estop alarm. Estop alarm came back In shortly after reset. Started generator run test of Stella at 9:12am and ran until 10:30am. Both Power transfers smooth. Started generator run test of Bertha at 10:43am and finished at 11:43am. Both Power transfers smooth. Inspected rectangular plant clarifier drives 1 and 2 - oil levels good, chains good and sheer pins good. EStop alarms reset and placed back into operation. Alum delivery onsite at 9:50am. Tank level at 0.71m. Delivery complete at 10:15am, tank level now at 3.43m. All paperwork signed and reviewed certificate of analysis. Alum tank hi level alarm currently active. | Kleinburg Water Resource Recovery Facility | 2026-01-05
WW-WEST | January | Wasting completed 20m3 per side. Switch alternate ras pump duties and put back in service. Confirmed flow. Was pumps in manual off. Added 9 bags of soda ash to the auto dispenser. | Kleinburg Water Resource Recovery Facility | 2026-01-04
WW-WEST | January | On site with David D and Dan H to investigate power loss After arriving on site and having voltage confirmed from Hydro over night found there was good utility voltage Found phase module in ats in fault mode calling for generator to run Phase sensing module in ats was set between 450-600VAC Incoming voltage was between 608-612VAC Found phase module interrupting contact wired backwards, reversed contacts and increased high voltage sensing module to 640VAC Now when incoming utility is between 450-640VAC there should be no power interruption to switch to generator power Why this problem just became more prevalent is not understood. Will continue to monitor station for power loss We will be coming back to do a voltage coordination between soft starts and low voltage setpoints on ats module when scheduled. | King City Pumping Station | 2026-01-16
WW-WEST | January | Checked station and trends, and recorded readings on SharePoint. No new issues | King City Pumping Station | 2026-01-27
WW-WEST | January | - Checked station and trends. Recorded readings on SharePoint - Notified ROC. Flushed inlet and outlet pressure transmitter on pump 1 and 3. Bled air out. - Mopped floor | King City Pumping Station | 2026-01-20
WW-WEST | January | On site to meet electrical to troubleshoot hydro supply issue. Shovelled snow from entrances. Diesel generator continues to run. Electrical investigating cause. Ran pumps manually during testing. Dropped the wet well down and site power shut off for periods of time during testing. Ordered 1000L of fuel for generator. Delivery TBD. Cause of diesel run found and corrected- see entry by electrical. All systems returned to normal operation with pumps in auto. Rotated offline duty pump 1 to 2. Station checks, SharePoint readings and review of continuous monitoring data. Level rag bin and check equipment/flush drains. | King City Pumping Station | 2026-01-16
WW-WEST | January | Checked station and recorded readings on SharePoint. No new issues | King City Pumping Station | 2026-01-30
WW-WEST | January | Pushed bin out for pick up | King City Pumping Station | 2026-01-22
WW-WEST | January | Onsite for diesel delivery - delivery onsite at 1:18pm. Diesel tank 1 at 54.7cm and 513L filled to 94.7cm and 939L Diesel tank 2 at 54.0 and 505L filled to 93.0cm and 920L. Total volume delivered 894.5Litres. Delivery completed at 1:40pm. | King City Pumping Station | 2026-01-17
WW-WEST | January | Remote entry - Hydro 1 onsite confirmed no issue on hydros end. Possible phase issue with our generator. Called and notified on call electrician Sean Peoples to meet and troubleshoot first thing in the morning. | King City Pumping Station | 2026-01-15
WW-WEST | January | Onsite for generator running for majority of the day - upon arrival generator had stopped and station transferred back to hydro. Cleared alarms and checked station. | King City Pumping Station | 2026-01-15
WW-WEST | January | On site to inspect pump 3 suction pressure Turned the pumps to manual and ran p3 while trying to release air in the line. Cycled it twice, did not get much out of the line. Flows are good, suction pressure does still fluctuate and drop when running but flows are good | King City Pumping Station | 2026-01-19
WW-WEST | January | - Notified ROC of the work being performed - Performed station check and recorded readings on SharePoint - Performed bar screen cleaning. Applied grease to the z fittings. Topped up oil to the hopper. Cleaned general area and flushed drain line. No issues found - Dampers in the generator room was not closing once again and no information was being displayed on the interface. Upon inspection, noticed that the breaker BR3 was tripped. Reset breaker and restarted the system. The readings came back up on the interface and dampers closed - Inspected the generator and fuel level, all okay. Started the generator at 10:02. Recorded readings on SharePoint after 30 minutes, no issues. Ran for approximately one hour. Runtime for generator 1 from 667.1 hrs to 668.1 hrs. Fuel level for tank 1 from 76.3 cm (743 L) to 75.8 cm (737 L). Fuel level for tank 2 from 75.7 cm (736 L) to 74.8 cm (727 L) - Tested sump pit operation and manually lifted float. Sump pump turned on, no issues - Tested dry well flood alarm, alarm received. No issues - Tested diesel containment flood alarm. Alarm received - Performed JHSC inspection. All okay. Tested eyewash, no issues - Tested building Hi and Low temperature alarm. Alarm received - Checked for hazardous waste, none found - Tested and inspected pump, motor and check valves. All okay. - Assisted maintenance with replacing exhaust fan 1 in the screen room. Successfully replaced the fan and test successful. Placed exhaust fan 1 back in auto | King City Pumping Station | 2026-01-08
WW-WEST | January | Checked station and trends, and recorded readings on SharePoint. No new issues found Pushed bin back in and tidied the area. Flushed drain lines and checked screen. Screen oil level is good | King City Pumping Station | 2026-01-23
WW-WEST | January | Onsite for station check - no new issues. Added data into SharePoint. Checked bar screen room - oil levels ok and bar screen in operation. | King City Pumping Station | 2026-01-09
WW-WEST | January | Checked station and trends, and recorded readings on SharePoint. No new issues. Rotated OOS pump duty | King City Pumping Station | 2026-01-13
WW-WEST | January | Reset pump 1 breaker and fault alarm. Reset dewatering press fault. Alarms caused by power blip caused by very windy afternoon. | King City Pumping Station | 2026-01-09
WW-WEST | January | Harie Rajamithiran(OIT) working under the direction of Gavin Walker(OIC) -Completed wet well cleaning | King City Pumping Station | 2026-01-12
WW-WEST | January | Assisted Young with bar screen cleaning and inspection, flushed and cleared rags from barscreen | King City Pumping Station | 2026-01-08
WW-WEST | January | Hosed down and cleaned the wet well | King City Pumping Station | 2026-01-12
WW-WEST | January | Onsite for wetwell cleaning with Gavin and Harie | King City Pumping Station | 2026-01-12
WW-WEST | January | Rotate offline pump from pump 3 to pump 1. Test pump 3 in auto and pump 1 is now duty 4/OOS. | King City Pumping Station | 2026-01-02
WW-WEST | January | Checked screen room and station. No new issues | King City Pumping Station | 2026-01-06
WW-WEST | January | Did not inspect facility outfall due to safety. Cannot see the path towards the outfall due to heavy amounts of snow. Will inspect another time | Vaughan Pine Valley Pumping Station | 2026-01-16
WW-WEST | January | Completed the station check Entered data into SharePoint Cleaned up around the site Everything operating as intended | Vaughan Pine Valley Pumping Station | 2026-01-23
WW-WEST | January | Checked station and trends. Recorded readings on SharePoint. No new issues Cleared path towards odour control unit. No issues | Vaughan Pine Valley Pumping Station | 2026-01-27
WW-WEST | January | Onsite for station check - no new issues. Reviewed trends and added data into SharePoint. | Vaughan Pine Valley Pumping Station | 2026-01-20
WW-WEST | January | Attending site to replace H2S sensor in wetwell. Could not open door to wetwell. Suspect door is iced up. Will return for another attempt once weather warms up. ROC notified before and after unsuccessful maintenance attempt. | Vaughan Pine Valley Pumping Station | 2026-01-23
WW-WEST | January | Onsite with Young Jung for wetwell work order and station check. Upon arrival pump 1 ultrasonic alarm on scada and high temp alarm active on pump 1 VFD. Cleared alarms and placed pump 1 in duty and watched it run a cycle - no alarms triggered and ultrasonic level sensor operating normally. Will continue to monitor. Completed station check, reviewed trends and added data to SharePoint. Completed wetwell inspection - triggered hi level alarms on scada by adjusting set points. Greased channel grinder and exercised gate valves. | Vaughan Pine Valley Pumping Station | 2026-01-16
WW-WEST | January | Checked station and trends, and recorded readings on SharePoint. No new issues | Vaughan Pine Valley Pumping Station | 2026-01-30
WW-WEST | January | - Checked station and trends, and recorded readings on SharePoint - Cleared snow to make path to the odour control unit. No issues with the odour control unit. Belt is good - Notified ROC of the work being performed - H2S out of range alarm outstanding. Ventilated the wet well to try and clear the alarm. Did not help lower the H2S levels. Seems to be faulty. Checked log entry and work order is already created - Tested sump pump operation. Sump pump works well in hand and also when using the float. Tested sump pump high level float. Sump pump high level alarm received on SCADA. No issues - Tested the dry well flood float. Received dry well flood float alarm on scada and dialer - Performed JHSC inspection. Tested eyewash. No issues found - Tested high and low temperature alarm. Pipe gallery temperature alarm received. Gallery room temperature alarm received - Checked mist eliminator. All okay and does not need cleaning - Checked air handling unit. Replaced dirty filter. Belt is all okay - Inspected the generator, oil level is good, coolant is good, and battery is good. Started the generator test at approximately 9:55 and ran for an hour. Took readings after 30 minutes and recorded on SharePoint. No issues. Generator hours from 513.2 hrs to 514.4 hrs. Fuel level from 102.6 cm (2277 L) to 101.2 cm (2238 L) - Tested wet well high level alarm via SCADA. Alarm received - Inspected pump and check valve, no issue - Tested air relief valve, all good - Exercised valves - Took out garbage | Vaughan Pine Valley Pumping Station | 2026-01-07
WW-WEST | January | - Upon arrival, historian heartbeat alarm was present on local SCADA and occurred yesterday on January 8, 2026. Cleared alarm. Checked trends and found no issues or gaps - Checked station and recorded readings on SharePoint Update: PCS on call confirmed that the heartbeat alarm was due to update | Vaughan Pine Valley Pumping Station | 2026-01-09
WW-WEST | January | - Upon arrival, noticed that the front building security camera was cut off and busted up. Notified TL and will create a work order - Checked station and trends. Recorded readings on SharePoint | Vaughan Pine Valley Pumping Station | 2026-01-13
CENTRAL | January | On-site for station check. Dan Boate and Kyle Rae on-site for generator ATS repairs, pumps man/off and ROC informed. Entered station readings in shared PD excel file. Increased air pressure from 27 to 30psi for P4 check valve, will monitor air pressure. Need new chain/lock for entry gate, informed Supervisor, building otherwise secure. No other new issues found. | Aurora (East) Wellington Pumping Station | 2026-01-23
WW-WEST | January | Onsite for station check - reviewed trends and added data into SharePoint. H2S out of range alarm present on arrival - alarm would not clear. Created work order W11565040. No new issues otherwise. | Vaughan Pine Valley Pumping Station | 2026-01-06
CENTRAL | January | On site to complete PMs. Notified ROC of relevant alarms. -Completed pump and motor inspection for pump 4 -Placed all pumps in manual-off -Ran generator run test: Hours before run: 368h 38m Fuel before run: 97.1 cm / 953 L and 97.3 cm / 955 L Run start @ 9:32 Run end @ 10:02 -When activating generator test, ATS malfunctioned. Site would not connect to generator or utility power. Contacted Tyler Z, Ben H, and ROC. Placed Poppy Lane valve in manual-closed (0L/s) to limit flow out of pressure zone. -Tyler Z arrived on site and brought it back on to utility power. Activated pump 4 to replenish tower levels before continuing troubleshooting. -Tested generator again at 10:56. Generator ran normally, but ATS did not automatically transfer again. -Tyler tested the ATS again at 11:48. Generator hours after all the tests: 369h 31m -Returned pump 5 to auto -Returned Poppy Lane FCV to auto. -Completed pump and motor inspection for pump 5 -Completed low temp alarm test: all good -Completed flood alarm test: all good -Exercised pump bypass valves -Exercised surge relief valves -Inspected and flushed air relief valve -Returned pump 4 to auto | Aurora (East) Wellington Pumping Station | 2026-01-22
CENTRAL | January | Vibration readings Got panel to start pump 5 kept shutting down and pump 4 started 3 times Called team lead and notified him of the issue | Aurora (East) Wellington Pumping Station | 2026-01-26
CENTRAL | January | On site to troubleshoot and repair transfer switch. Found missing brush holder and subsequent loose brush on transfer switch drive motor. Disassembled and repaired. Reassembled and tested. All good now. | Aurora (East) Wellington Pumping Station | 2026-01-23
CENTRAL | January | Station Check (no other issues found) Input data to PWQ w/o#11615948 generated for the Ventilation system in generator room (open) | Aurora (East) Wellington Pumping Station | 2026-01-26
CENTRAL | January | On-site for station check and to meet Alectra for power meter replacement. Alectra tech?s replaced power meter. Checked station and equipment, no new issues found. | Aurora (East) Wellington Pumping Station | 2026-01-19
CENTRAL | January | On site for station check. 08:25 45Pump 4 and 5 in standby. Found pump 4 shaft spinning in reverse direction. Discharge checkvalve likely passing. LOTO P4. Isolated discharge and shaft stopped spinning. Pump 5 activated in duty. Reoponed p4 discharge and check valve seated. Removed LOTO for P4. Ran p4 to test if CV continues to seat. No issues further observed. Notified Ben Hess. ROC, and Tyler zimmerman of work. 742 m3 of reverse flow recorded. Entered data into process sheets. No issues found. | Aurora (East) Wellington Pumping Station | 2026-01-16
CENTRAL | January | On site to complete PMs. Notified ROC of relevant alarms. -Placed pumps in manual-off -Ran generator run test: Hours before run: 369h 50m Fuel before run: 95.0 cm / 931 L and 95.0 cm / 932 L Run start @ 8:45 On load @ 8:52 Run end @ 9:55 ATS switchover @ 9:59 Generator cooldown ended @ 10:05 Hours after run: 371h 10m Fuel after run: 92.4 cm / 904 L and 92.5 cm / 905 L -Found pump 4 check valve passing, created W11617650 for maintenance -Completed pump and motor inspections for pumps 1, 2, and 3 by running them locally individually -Pumps returned to auto | Aurora (East) Wellington Pumping Station | 2026-01-27
CENTRAL | January | On site for station check. 13:21 Pump 4 and 5 in standby. Entered data into process sheets. No issues found. | Aurora (East) Wellington Pumping Station | 2026-01-12
CENTRAL |  | On site for station check. 10:29. Reservoir inlet filling at 47 l/s. Zone 3 Pump 1 running at 70.1 l/s. Chemical boosting not active. Reservoir level at 60%. Replaced outlet total anlayzer reagent. Replaced chemscan sulphuric acid reagent. Verified analyzer residuals (mg/l): Pre-injection grabs: 10:49 Monchloramine grab: 2.06 Chemscan: 2.04 Free ammonia: 0.08. Chemscan: 0.02. Adjusted to match grab average. Total ammonia: 0.49. Chemscan: 0.48. 11:00 Free chlorine grab: 0.04. Analyzer: 0.04. Total Chlorine grab: 1.73 CL17 Analyzer: 1.77 Chemscan: 1.71. 11:12 Post-injection grabs: Free chlorine grab: 0.10. Analyzer: 0.05. Total Chlorine grab: 2.58 CL17: 2.53. Chemscan: 2.64 Monchloramine grab: 2.11 Chemscan: 2.07. Free ammonia: 0.07. Chemscan: 0.04. Total ammonia: 0.49. Chemscan: 0.53. 11:20 Reservoir outlet chlorine grab: Free grab: 0.02. Analyzer: 0.04. Total grab: 2.34 Analyzer: 2.30. 11:25 Zone 3 grabs: Free chlorine grab: 0.02. Analyzer: 0.04. Total chlorine grab: 2.34 Analyzer: 2.30. Station and equipment ok. No issues found. Entered readings into process sheets. | Aurora (East) Wellington Pumping Station | 2026-01-12
CENTRAL | January | On site for station check. 08:45. Pump 4 running in duty at 165 l/s. Entered data into process sheets. No issues found. | Aurora (East) Wellington Pumping Station | 2026-01-05
CENTRAL | January | Vibration testing | Aurora (East) Wellington Pumping Station | 2026-01-15
CENTRAL | January | On site for station check. 08:23. Pump 4 and 5 in standby. Entered data into process sheets. No issues found. | Aurora (East) Wellington Pumping Station | 2026-01-09
CENTRAL | January | High vibration readings reported on Pump 4. Upon closer inspection it was found that 2 of the feet had loose hardware and missing shims. Re- levelled pump, installed new coupling and re-align pump & motor set. Greased motor and ran for approximately 1hr before returning to service, no other issues to report and will monitor it?s condition. | Aurora (East) Wellington Pumping Station | 2026-01-06
WW-WEST | January | Supernated STT and released to SHT. Completed labs and entered data in ACE sheets. Completed station check. No issues found. | Schomberg Water Resource Recovery Facility | 2026-01-23
CENTRAL | January | On-site for station and equipment check No issues found. Entered all readings and measurements into PWQ sheet General tidy for new operator next week. | Aurora (East) Wellington Pumping Station | 2026-01-02
WW-WEST | January | Restarted the Local SCADA server due to Windows updates. Notified the Remote Operations Center. | Schomberg Water Resource Recovery Facility | 2026-01-22
WW-WEST | January | On site to provide panel access to consultants, ETO for future plant upgrades. | Schomberg Water Resource Recovery Facility | 2026-01-29
WW-WEST | January | Attending site to replace Alum Pumps 6 & 7 flowmeter (W11523891). While setting up the replacement flowmeter, I noticed that the low-flow cutoff was set to 20mL/minute on the existing flowmeter. I have now changed the low-flow cutoff to 5mL/minute in the existing flowmeter to see if this corrects the issue. Also, replaced Screen Room Oxygen sensor (W11526277). ROC was notified before and after maintenance activities. | Schomberg Water Resource Recovery Facility | 2026-01-27
WW-WEST | January | Completed labs and entered data in ACE sheets. Completed station check. No issues found. Completed blower building and aeration tank comprehensive housekeeping. | Schomberg Water Resource Recovery Facility | 2026-01-27
WW-WEST | January | Completed labs and entered data in spreadsheet. Completed station check. No issues found. Assisted contractors with compressor deficiency repairs. Reset alarms Pumped ground water from sodium hydroxide containment. | Schomberg Water Resource Recovery Facility | 2026-01-20
WW-WEST | January | Supernated STT and released to SHT. Completed labs and entered numbers in ACE sheet. Completed station check. No issues found. Comprehensively house cleaned process building. Adjusted wasting window from 16:00 to 23:00 to 16:00 to 22:00 to bring solids up. | Schomberg Water Resource Recovery Facility | 2026-01-26
WW-WEST | January | On site to troubleshoot VFD for effluent pump 3. Unable to repair VFD. Found suitable, used replacement at Harry Walker. Installed and powered up. Have to come back next week to program and test VFD. Please leave effluent pump 3 in manual off for time being. | Schomberg Water Resource Recovery Facility | 2026-01-30
WW-WEST | January | Transferred sludge thickening tank to sludge holding tank. Collect samples and complete in house labs Enter lab results and flow data into SharePoint spreadsheet Complete station checks, SharePoint readings and review of continuous monitoring data. Salted stairs to aeration tank and broke up some ice General Housekeeping in various spots through facility | Schomberg Water Resource Recovery Facility | 2026-01-30
WW-WEST | January | Received load of alum, filling tanks from 0.88m/0.88m to 2.73m/2.73m. Set WAS pump 2 back in auto to resume wasting. Set sludge blower 2 to auto/duty 1. Completed labs and entered data in ace sheet. Completed station check. No issues found. Cleaned TSS probe. Completed comprehensive housekeeping around clarifiers. | Schomberg Water Resource Recovery Facility | 2026-01-29
WW-WEST | January | Released STT to SHT. Completed labs and entered data in ACE sheet. Completed station check. No issues found. Set WAS P2 to manual/stop to eliminate a night of wasting to increase solids. Maintained online DO probes. Checked headworks building heat trace - ok. | Schomberg Water Resource Recovery Facility | 2026-01-28
WW-WEST | January | Started supernate pump. Started labs. Collected weekly compliance samples. | Schomberg Water Resource Recovery Facility | 2026-01-21
WW-WEST | January | Supernated STT and released to SHT. Completed labs and entered numbers in ACE sheets. Completed station check. No issues found. Inspected filter reject pumps. ROC received high level alarm. Changed UV bulb on bank B, rack 3, bulb 3. | Schomberg Water Resource Recovery Facility | 2026-01-19
WW-WEST | January | Installed new vacuum gauge for air filter on blower 3. Checked for oil leak on blower 1 No leak found, oil level is good. Operator will monitor and advise if issue returns. | Schomberg Water Resource Recovery Facility | 2026-01-29
WW-WEST | January | - Notified ROC of the work being performed - Inspected WAS pumps 1-2. Coupling for WAS pump 1 is good. Coupling for WAS pump 2 had some movement between the joint but is satisfactory. Greased fittings - Tested filter drain sump pumps. Ran okay when float was flipped. Tested alarm. Filter drain sump high float alarm received - Tested RAS/WAS drain sump high float. Tested sump pump operation in local. Both pumps okay. Tested alarm. Received RAS/WAS drain sump high float - Shut off effluent pumps to divert to the lagoon for UV maintenance and UV channel cleaning. Started diverting at 12:54 - Cleaned UV 1 and 2 and inspected UV. No issues - Cleaned UV channel and filter effluent channel. No issues - Stopped diverting at 13:58. Roughly 21 m^3 or 21000 L diverted. Notified ENV Incidence about the diversion due to UV and cleaning maintenance work - Once done, turned back on Effluent pumps 1-3, and reassigned duties. Cleared alarms associated to UV and effluent pumps | Schomberg Water Resource Recovery Facility | 2026-01-15
WW-WEST | January | Started supernate pump. Started labs. Collected weekly compliance samples. | Schomberg Water Resource Recovery Facility | 2026-01-28
WW-WEST | January | Shut off supernate pump. Released STT to SHT. Completed labs and entered data in ACE sheet. Completed station check, finding no issues. Maintained online DO probes. Cleaned online TSS probe. | Schomberg Water Resource Recovery Facility | 2026-01-21
WW-WEST | January | Completed labs and entered data in ACE sheets. Completed station check. No issues found. Final effluent has been a bit cloudy lately, so: Increased final pass of aeration alum dosage from 110 mg/L to 115 mg/L. Increased clarifier effluent alum dosage from 18 mg/L to 20 mg/L. Created W11609267 (low priority work order)for vortex digital readouts that are not reading correctly. | Schomberg Water Resource Recovery Facility | 2026-01-22
WW-WEST | January | Supernated STT and released to SHT. Completed labs and entered data in ACE sheets. Completed station check. No issues found. Cleaned TSS probe. Created work order for effluent pump 3 that faulted yesterday. | Schomberg Water Resource Recovery Facility | 2026-01-16
WW-WEST | January | Completed labs and entered numbers in ACE sheet. Adjusted wasting window from 16:00 - 24:00 to 16:00 - 23:00. Completed station check. No issues found. Assisted Young with UV work order. | Schomberg Water Resource Recovery Facility | 2026-01-15
WW-WEST | January | Started supernating STT. Started labs. Collected weekly compliance samples. Inspected position or raw sample intake. Found it worked its way a bit lower. Raised up from bottom of chamber. | Schomberg Water Resource Recovery Facility | 2026-01-14
WW-WEST | January | Completed labs and entered numbers in ACE sheets. Created work order for Sludge Blower 2 fan overload alarm (W11570169) Completed D.O. probe maintenance. | Schomberg Water Resource Recovery Facility | 2026-01-07
WW-WEST | January | Check on blower 3 vacuum gauge not working. Measured at 2.5? body with 1/4? npt thread off back of gauge. Will source replacement, supplier unable to provide new gauge. | Schomberg Water Resource Recovery Facility | 2026-01-07
WW-WEST | January | Released supernated STT to SHT. Completed labs and entered numbers in ACE sheet. Completed station check. No issues found. Maintained DO probes. Completed consolidated clarifier maintenance. | Schomberg Water Resource Recovery Facility | 2026-01-14
WW-WEST | January | On site to investigate raw sub exceedances. Found nothing obvious as the cause. Adjusted sample draw location hose. Instructed OiC to clean the sidewall of the tank it draws from. Investigated the water infiltration into RAS basement. Do not suspect aeration as source. Likely travelling through the conduit holes. Completed the clarifier TP: 0.064mg/L. | Schomberg Water Resource Recovery Facility | 2026-01-14
WW-WEST | January | Supernated SHT and released to SHT. Completed labs and entered data in spreadsheet. Completed station check. No issues found. Cleaned TSS probe. Exercised SHT overflow valve. Tested SHT high level float. ROC received alarm. Power blip caused alarms and clarifier rake drive cutout. Reset alarms and duties. Reset clarifier. No more outstanding alarms. | Schomberg Water Resource Recovery Facility | 2026-01-09
WW-WEST | January | Supernated STT and released to SHT. Completed labs and entered numbers in ACE sheets. Completed station check. No issues found. Completed consolidated headworks work order. ROC received alarms. Completed debris auger inspection. ROC received alarms. | Schomberg Water Resource Recovery Facility | 2026-01-12
WW-WEST | January | Collected weekly and monthly compliance samples. Suoernated STT and released to SHT. Started labs. Completed station check. No issues found. | Schomberg Water Resource Recovery Facility | 2026-01-07
WW-WEST | January | On site for clarifier rake drive cut CMU # W11565272. Reset rake drive and review scada for all duty setpoints check. Power blip was cause of disruption. | Schomberg Water Resource Recovery Facility | 2026-01-06
WW-WEST | January | Completed labs and entered data in ace sheets. Completed station check. No issues found. Inspected aeration blowers. Blower 1 leaked oil out of the drive side. Wiped up oil. Topped up oil. Created a work order (W11573836). Inspected sludge blowers. No issues. Inspected vortex blowers. No issues. Cleaned and inspected new air compressors. No new issues found. Replaced sludge blower room supply fan filter. | Schomberg Water Resource Recovery Facility | 2026-01-08
WW-WEST | January | Completed labs and entered numbers in ACE sheet. Completed station check. No issues found. Inspected RAS pumps 1-3. No issues found. Inspected scum pumps 1 and 2. No issues found. | Schomberg Water Resource Recovery Facility | 2026-01-13
WW-WEST | January | Collect samples and complete in house labs. Input labs and data into ace spreadsheet Decant sludge thickening tank and transfer to sludge holding tank. Station checks, SharePoint readings and review of continuous monitoring data. | Schomberg Water Resource Recovery Facility | 2026-01-02
WW-WEST | January | On site to replace UV1 Rack 5 relay board. Replaced. Tested with help of operations. UV1 Rack 5 back in service. | Schomberg Water Resource Recovery Facility | 2026-01-05
WW-WEST | January | Supernated STT and released to SHT. Assisted electricians with UV system. Electricians assisted with changing blown bulbs. Bank A, rack 2 lamp 7 and bank b, rack 5, lamp 7. Returned duty rotation to daily. Completed labs and entered data in ace sheets. Test ran diesel generator. Start hours: 550.5, fuel level: 0.75 m. Stop hours: 551.6, fuel level: 0.75 m. Completed station check. No issues found. Completed JHSC inspection. No issues found. Collected spent UV bulbs for hazardous waste. Will deliver to Newmarket on Wednesday. | Schomberg Water Resource Recovery Facility | 2026-01-05
WW-WEST | January | On site to reset clarifier rake drive for cmu W11556971. Caused by power blip. Rake drive reset and running. Review SCADA and check duty selection on all equipment. | Schomberg Water Resource Recovery Facility | 2026-01-04
WW-WEST | January | Completed station check. Entered data in spreadsheet. No issues found. | Schomberg Dr. Kay Pumping Station | 2026-01-20
WW-WEST | January | Completed labs and entered numbers in ACE sheet. Completed station check. No issues found. Sludge blower 2 fan overloaded twice. Set blower to manual off and will investigate further. | Schomberg Water Resource Recovery Facility | 2026-01-06
WW-WEST | January | On site for effluent pump uncommanded start and stops. All three pumps keep started and then shutting off. Check float system and see that level is at the start float and the stop float is just below the start float. The miltronics level is flatlined at 1.52m no alarms on display. With the guidance of Rick from Instrumentation, reset the power to the endless hauser unit in the basement. Level reading restored on miltronics. Pump 3 continued to run and would not stop/reset. Fail to stop alarms. Lifted the low level float to stop the pump and restored pump duty to all 3 effluent pumps. Everything back into remote auto and ROC notified. Cmu W11552910 | Schomberg Water Resource Recovery Facility | 2026-01-01
WW-WEST | January | Completed station check and entered data in spreadsheet. No issues found. | Schomberg Dr. Kay Pumping Station | 2026-01-27
WW-WEST | January | Remote entry - noticed faulty ultrasonic reading in the trend earlier in the day. Controlling LIT is currently ultrasonic. Switched controlling LIT to hydrostatic | Schomberg Dr. Kay Pumping Station | 2026-01-16
WW-WEST | January | Completed station check. Entered data in spreadsheet. No issues found. | Schomberg Dr. Kay Pumping Station | 2026-01-16
WW-WEST | January | Completed station check. No issues found. Completed comprehensive house keeping work order. | Schomberg Dr. Kay Pumping Station | 2026-01-23
WW-WEST | January | Station checks, SharePoint readings and review of continuous monitoring data. | Schomberg Dr. Kay Pumping Station | 2026-01-30
WW-WEST | January | Completed station check. Entered data in spreadsheet. No issues found. | Schomberg Dr. Kay Pumping Station | 2026-01-13
WW-WEST | January | Checking station after temporary bad readings from ultrasonic sensor. Readings returned to normal without intervention. Checked wetwell. Nothing unusual through-out pump cycle. Cleared alarms. All okay at this time. | Schomberg Dr. Kay Pumping Station | 2026-01-16
WW-WEST | January | Completed station check. Entered data in spreadsheet. No issues found. | Schomberg Dr. Kay Pumping Station | 2026-01-09
WW-WEST | January | Completed station check. No issues found. Completed JHSC inspection. No issues found. Test ran generator: Start hours: 557, fuel 3/4 full. Stop hours: Tested hi and low temperature alarms. ROC received alarms. No hazardous waste on site. | Schomberg Dr. Kay Pumping Station | 2026-01-06
ROC | January | KLET27 - Terry from Property services on site. | ROC General | 2026-01-26
ROC | January | Adam Button signing out | ROC General | 2026-01-18
ROC | January | Carter Dunn Signing In, -13D/Clear | ROC General | 2026-01-18
ROC | January | Adeela Khan signing out | ROC General | 2026-01-23
ROC | January | KSSP - Ben Han from property services on site to work on the heating system in the chemical room. | ROC General | 2026-01-28
ROC | January | Adam Button signing out | ROC General | 2026-01-24
ROC | January | MKTKKC- Jamie from ETO Engineering onsite for construction upgrades. | ROC General | 2026-01-27
ROC | January | Christian Van Beek signing in. Weather: -10C and clear. | ROC General | 2026-01-19
ROC | January | Adeela Khan signing out | ROC General | 2026-01-19
ROC | January | HLSSBS- Ken from IT onsite. | ROC General | 2026-01-20
ROC | January | STETBR- Phil from AB on site | ROC General | 2026-01-21
ROC | January | KBSP, NBSP, KLET27/KLPS27, KLW34/KLPSWL - Pesticon Pest control visiting these sites today. Pesticon operator will be attending NBSP and KBSP after hours for spray application. | ROC General | 2026-01-23
ROC | January | KBSP- Drew from Ferguson Electric is on site | ROC General | 2026-01-21
ROC | January | Adam Button signing out | ROC General | 2026-01-25
ROC | January | Carter D signing Out | ROC General | 2026-01-18
ROC | January | MARS - Courtney from Torbear is on site | ROC General | 2026-01-17
ROC | January | Ethan Ullalkar signing out. | ROC General | 2026-01-17
ROC | January | NMTKKC, Khalid from ETO engineering is on site | ROC General | 2026-01-16
ROC | January | MTW3- Dominique from Honeywell is done on site | ROC General | 2026-01-15
ROC | January | Adam Button signing out | ROC General | 2026-01-21
ROC | January | SEOC6/7 Theodore from ABPMC leaving site. | ROC General | 2026-01-22
ROC | January | NRETBR - Terry from property services leaving site. | ROC General | 2026-01-23
ROC | January | KSSP, Franko from property services is leaving site | ROC General | 2026-01-16
ROC | January | Adeela Khan signing out | ROC General | 2026-01-17
ROC | January | Angelica Chepiga signing out | ROC General | 2026-01-20
ROC | January | NMTKKC - Jamie from ETO engineering is on site with Kingdom construction | ROC General | 2026-01-26
ROC | January | KSTP - Drew from Ferguson electric on site. | ROC General | 2026-01-26
ROC | January | Christian Van Beek signing in. Weather: -18C and clear. | ROC General | 2026-01-30
ROC | January | Connor Smith signing out | ROC General | 2026-01-30
ROC | January | QVW12 - Drew from Ferguson Electric leaving site. | ROC General | 2026-01-30
ROC | January | KCSSKR - Terry G from property services leaving site. | ROC General | 2026-01-20
ROC | January | Carter D Signing Out | ROC General | 2026-01-16
ROC | January | QVW12, QVETQS, QVW34, MTSS, MTSP, MTETNL, MTW12, MTW3 - Imtiaz from Pesticon will be attending these sites today | ROC General | 2026-01-22
ROC | January | Adam Button signing in -13 Clear | ROC General | 2026-01-26
ROC | January | Adeela Khan signing in | ROC General | 2026-01-23
ROC | January | QVW12 - Garrick from Ferguson Electric on site to complete pipe work. | ROC General | 2026-01-28
ROC | January | Christian Van Beek signing in. Weather: -14C and clear. | ROC General | 2026-01-20
ROC | January | NMTKKC - Jon C. from Kingdom Construction is on site | ROC General | 2026-01-22
ROC | January | KSSP - Franco from Property Services is finished on site and headed to HMSS | ROC General | 2026-01-30
ROC | January | KSTP - Drew from Ferguson Electric on site to pull cable today. | ROC General | 2026-01-19
ROC | January | Angelica Chepiga signing out | ROC General | 2026-01-30
ROC | January | Adeela Khan signing in. | ROC General | 2026-01-26
ROC | January | Connor Smith signing in -10C Cloudy | ROC General | 2026-01-22
ROC | January | Adeela Khan Signing out | ROC General | 2026-01-21
ROC | January | VNPS - Jonathan from property services on site to test the sprinkler system. Jonathan will call back to confirm the signal was received. | ROC General | 2026-01-23
ROC | January | Christian Van Beek signing in. | ROC General | 2026-01-29
ROC | January | QVW12- Phil from AB is on site | ROC General | 2026-01-21
ROC | January | SEOC SHAFT 6/7, Phil from AB is on site, if fire alarm goes off, give him a call Phil: 2898390704 | ROC General | 2026-01-22
ROC | January | NMTKKC - Jamie from ETO engineering is on site with Kingdom construction | ROC General | 2026-01-23
ROC | January | Connor Smith signing out | ROC General | 2026-01-28
ROC | January | KSTP - Drew from Ferguson electric leaving site. Hamid from ETO engineering still on site. | ROC General | 2026-01-28
ROC | January | Carter Dunn Signing In, -4D/Clear | ROC General | 2026-01-22
ROC | January | STETBR - Johnny from ETO Engineering is finished on site | ROC General | 2026-01-22
ROC | January | SEOC 6/7 - Theodore from ABPMC leaving site. | ROC General | 2026-01-23
ROC | January | KBSP- Drew from Ferguson onsite. | ROC General | 2026-01-20
ROC | January | AUSS - William from CHUBB is on site | ROC General | 2026-01-21
ROC | January | Adam Button signing out | ROC General | 2026-01-28
ROC | January | Angelica Chepiga signing out | ROC General | 2026-01-27
ROC | January | Adam Button signing out | ROC General | 2026-01-27
ROC | January | QVW12, Phil from AB is on site, doing some welding, fire alarm may come in, directed to disregard but to give him a call if it does come in 2898390704 | ROC General | 2026-01-16
ROC | January | Christian Van Beek signing in. | ROC General | 2026-01-28
ROC | January | SUSSWB - Ben Han from property services on site to complete maintenance on the heating system. | ROC General | 2026-01-20
ROC | January | Adeela Khan signing in. Weather: -17C and Cloudy | ROC General | 2026-01-29
ROC | January | GWTP - Terry G from Property services leaving site, placed heaters and left some of the storage doors open. Not able to clear HL intrusion alarm. HL doors secured. | ROC General | 2026-01-29
ROC | January | GWTP- Ben H from Property Services onsite. 13:44- Offsite. | ROC General | 2026-01-27
ROC | January | NMTKKC - Jamie from ETO engineering on site to enter the chemical disinfection area to work with Kingdom Construction. | ROC General | 2026-01-28
ROC | January | Angelica Chepiga signing out | ROC General | 2026-01-29
ROC | January | SEOC4 - Theodore from AB Project Management is on site and will be cleaning up in the generator room | ROC General | 2026-01-30
ROC | January | STETBR - Johnny from ETO engineering on site to complete an inspection for upcoming work. | ROC General | 2026-01-22
ROC | January | KSTP - Drew from Ferguson electric on site to continue work on the generator. | ROC General | 2026-01-23
ROC | January | Angelica Chepiga signing out | ROC General | 2026-01-21
ROC | January | AUW14 - William from CHUBB is on site for a service call 18:00 - William is finished on site | ROC General | 2026-01-22
ROC | January | KSTP - Drew from Ferguson Electric leaving site. | ROC General | 2026-01-19
ROC | January | Christian Van Beek signing out. | ROC General | 2026-01-19
ROC | January | NMPSKC - Caden from Ferguson Electric is on site 18:02 - Caden is finished on site SEOC4 - Theodore from AB Project Management is finished on site. Instructed to no longer disregard smoke alarms and fire alarms | ROC General | 2026-01-29
ROC | January | SEOC6- Theo from AB done on site | ROC General | 2026-01-30
ROC | January | KSSP - Franco from Property services called to inform that he is on site | ROC General | 2026-01-16
ROC | January | Carter Dunn Signing In, -5D/Clear | ROC General | 2026-01-16
ROC | January | Angelica Chepiga signing out | ROC General | 2026-01-26
ROC | January | KSTP - Drew from Ferguson Electric leaving site. | ROC General | 2026-01-30
ROC | January | KSTP - Drew from Ferguson Electric is finished on site | ROC General | 2026-01-26
ROC | January | QVW12 - Phil from ABPMC leaving site. | ROC General | 2026-01-28
ROC | January | GWTP - Mark from Process Optimization is finished on site and headed to KSTP | ROC General | 2026-01-30
ROC | January | MTSP - Steven from CPD leaving site. | ROC General | 2026-01-22
ROC | January | Christian Van Beek signing in. Weather: -17C and clear. | ROC General | 2026-01-31
ROC | January | SEOC4- Phil from AB onsite. | ROC General | 2026-01-28
ROC | January | NMSSBP- Tony from Property Services finished onsite. | ROC General | 2026-01-30
ROC | January | QVW34, Gerrick from Ferguson Electric is on site | ROC General | 2026-01-16
ROC | January | STPSTL - Drew from Ferguson Electric leaving site. Phil from Ferguson is still on site. | ROC General | 2026-01-20
ROC | January | STPSTL - Drew from Ferguson Electric on site to complete work on the generator fuel system. | ROC General | 2026-01-20
ROC | January | KSTP- Gerrick from Ferguson offsite. | ROC General | 2026-01-20
ROC | January | Connor Smith signing out | ROC General | 2026-01-23
ROC | January | SHSP - Phil from AB onsite | ROC General | 2026-01-19
ROC | January | Adam Button signing out | ROC General | 2026-01-30
ROC | January | Christian Van Beek signing out | ROC General | 2026-01-23
ROC | January | SUSSWB - Ben Han leaving site. Headed to NMSSBP. | ROC General | 2026-01-20
ROC | January | Angelica Chepiga signing in, weather -15C | ROC General | 2026-01-20
ROC | January | NMTKKC, John from Kingdom Construction is on site | ROC General | 2026-01-29
ROC | January | KCETFS - Zack from Bell is on site. | ROC General | 2026-01-29
ROC | January | KCW34, Kevin N from York net is on site | ROC General | 2026-01-29
ROC | January | Carter Dunn Signing In | ROC General | 2026-01-29
ROC | January | KBSP - Terry from Property Services is on site and will be working on the emergency lights | ROC General | 2026-01-22
ROC | January | GWTP- Mark from Process optimization on site for a tour | ROC General | 2026-01-30
ROC | January | NMPSKC - Drew from Ferguson electric on site. | ROC General | 2026-01-27
ROC | January | GWTP- Ben from Property services on site | ROC General | 2026-01-27
ROC | January | NMTKKC- Jamie from ETO Engineering offsite. | ROC General | 2026-01-27
ROC | January | NMETYS - York Regional Police operator on site for their monthly site visit. | ROC General | 2026-01-22
ROC | January | Adam Button signing -24 C clear | ROC General | 2026-01-24
ROC | January | QVW12 - Drew from Ferguson Electric on site. | ROC General | 2026-01-30
ROC | January | Connor Smith signing out | ROC General | 2026-01-29
ROC | January | KSTP, Drew from Ferguson Electric is on site | ROC General | 2026-01-29
ROC | January | NBW3- Jason from Paladine leaving site. Issue arming building, transferred to security | ROC General | 2026-01-30
ROC | January | HMSS - Franco from Property services leaving site. | ROC General | 2026-01-30
ROC | January | SUSP- Scott from IAM leaving site. | ROC General | 2026-01-30
ROC | January | SEOC4 - Stephen from AB working on site (dusty work). Requested disregard fire/smoke alarm for the duration of the work. | ROC General | 2026-01-27
ROC | January | MTSS- Domonique from Honey well is done on site and heading to MTW3 | ROC General | 2026-01-15
ROC | January | Adam Button signing in -4 Clear | ROC General | 2026-01-17
ROC | January | Adam Button signing out | ROC General | 2026-01-15
ROC | January | KLET27 - Steven from ABPMC on site. | ROC General | 2026-01-20
ROC | January | Christian Van Beek signing out. | ROC General | 2026-01-28
ROC | January | STW12-Dominic from Honeywell on site 14:03-STW12-Dominic from Honeywell done on site STW3-Dominic from Honeywell on site | ROC General | 2026-01-30
ROC | January | Adeela Khan signing in. Weather: -10 and partly cloudy | ROC General | 2026-01-18
ROC | January | Angelica Chepiga signing in, weather -16C | ROC General | 2026-01-26
ROC | January | Connor Smith signing in -13C Clear | ROC General | 2026-01-29
ROC | January | Angelica Chepiga signing in, weather -19C | ROC General | 2026-01-29
ROC | January | Angelica Chepiga signing in | ROC General | 2026-01-27
ROC | January | QVW12 - Garrick from Ferguson electric leaving site. | ROC General | 2026-01-27
ROC | January | Adam Button signing in | ROC General | 2026-01-21
ROC | January | Adeela Khan signing in | ROC General | 2026-01-30
ROC | January | KSSP- Franco from Property services is on site to work on MUAs | ROC General | 2026-01-30
ROC | January | KBSP - Phil from ABPMC on site for the day. | ROC General | 2026-01-22
ROC | January | Adeela Khan signing out | ROC General | 2026-01-30
ROC | January | Christian Van Beek signing out. | ROC General | 2026-01-20
ROC | January | KSSP- Ben H from Property Services finished onsite. | ROC General | 2026-01-28
ROC | January | AUW14- Rob from Chubb is on site | ROC General | 2026-01-21
ROC | January | NMTKKC - Jamie from ETO engineering leaving site. | ROC General | 2026-01-28
ROC | January | KSSSQW - Joe O. called to inform that he is on site with a contractor to take a look at the boiler | ROC General | 2026-01-26
ROC | January | Connor Smith signing in -12C Clear | ROC General | 2026-01-28
ROC | January | Pesticon visiting following sites; BLW12, NMETIB, NMETHW, NMETDD, NMSSBP, NMSSHS, NMW12, NMW15, NMETYS, NMTKKC, NMW136, NMTKBS, ANW23 | ROC General | 2026-01-28
ROC | January | KBSP- Hamid from ETO onsite for inspection. | ROC General | 2026-01-27
ROC | January | LSSS- Franco from Property Services onsite working on card readers. | ROC General | 2026-01-27
ROC | January | Christian Van Beek signing out. | ROC General | 2026-01-22
ROC | January | NMTKKC - Drew from Ferguson Electric leaving site. | ROC General | 2026-01-28
ROC | January | Connor Smith signing in -20C Clear | ROC General | 2026-01-30
ROC | January | Carter Dunn Signing In, -15D/Snowing | ROC General | 2026-01-24
ROC | January | Adeela Khan signing out | ROC General | 2026-01-22
ROC | January | NMPSKC- Drew from Ferguson Electric done on site | ROC General | 2026-01-27
ROC | January | Adeela Khan signing in. Weather: -3 and cloudy | ROC General | 2026-01-17
ROC | January | Adam Button signing in -15 Clear | ROC General | 2026-01-27
ROC | January | Connor Smith signing out | ROC General | 2026-01-22
ROC | January | SEOC6- Phil from AB finished onsite. | ROC General | 2026-01-27
ROC | January | Pest control visiting sites: MKRSMR, MKPSSA, STW12, STETTL, STW3, 56, BLETNL, BLW3. | ROC General | 2026-01-26
ROC | January | KBSP - Terry G from property services on site to check emergency lights | ROC General | 2026-01-20
ROC | January | SUSP - Scott from IAM is on site KSTP - Natalie P. and Mark S. are on site NBW3 - Jason from Palladin is on site | ROC General | 2026-01-30
ROC | January | Adeela Khan signing in. Weather: -6 and sunny | ROC General | 2026-01-22
ROC | January | Adeela Khan signing in | ROC General | 2026-01-16
ROC | January | Christian Van Beek signing out. | ROC General | 2026-01-29
ROC | January | LSSS - Franco from Property services leaving site. | ROC General | 2026-01-27
ROC | January | SEOC 6/7 - Theodore from ABPMC on site. | ROC General | 2026-01-23
ROC | January | GWTP, Jeff/Greg from property services are on site testing the fire alarm | ROC General | 2026-01-29
ROC | January | Garrick from Ferguson Electric on site. | ROC General | 2026-01-22
ROC | January | ANW23 - Terry G from property services on site for a short visit to inspect emergency lights. Pesticon Pest control attending these sites: NRETCR, NRETBR, RHAMF, JFRS, RHPSPA, Bayview OCF. | ROC General | 2026-01-19
ROC | January | KSSP - Ben Han from property services on site to inspect an office heating system. | ROC General | 2026-01-19
ROC | January | Carter D Signing In, -13D/Snowing | ROC General | 2026-01-25
ROC | January | Adeela Khan signing out | ROC General | 2026-01-26
ROC | January | SEOC67- Hamid from ETO onsite for inspection. | ROC General | 2026-01-27
ROC | January | Angelica Chepiga signing in, weather -11C | ROC General | 2026-01-28
ROC | January | Christian Van Beek signing out. | ROC General | 2026-01-31
ROC | January | KSTP- Drew from Ferguson onsite for generator work. | ROC General | 2026-01-28
ROC | January | QVW12- Drew from Ferguson onsite. | ROC General | 2026-01-30
ROC | January | QVW12 - Drew from Ferguson Electric is finished on site | ROC General | 2026-01-30
ROC | January | STPSTL- Phil from AB finished onsite | ROC General | 2026-01-20
ROC | January | Connor Smith signing in -4C Snowy | ROC General | 2026-01-21
ROC | January | KBSP - Steven from ABPMC on site. | ROC General | 2026-01-23
ROC | January | NMPSKC - Theodore from AB Project management and Construction is on site | ROC General | 2026-01-16
ROC | January | NMSSBP, Property Services is on site, testing fire alarm 08:32, Patrick from Property services is finished on site | ROC General | 2026-01-16
ROC | January | KSTP - Drew from Ferguson electric on site. | ROC General | 2026-01-27
ROC | January | KSETDP - Thomas from IAM/Landmark leaving site | ROC General | 2026-01-19
ROC | January | KSTP- Mark from IAM done on site | ROC General | 2026-01-30
ROC | January | EGSSSC - Dominic from Honeywell is on site | ROC General | 2026-01-21
ROC | January | SEOC Shaft4, Phil from AB is on site, disregard fire alarms on site as drilling is happening. if alarm goes off, call Phil Phil: 2898390704 | ROC General | 2026-01-29
ROC | January | Angelica Chepiga signing in, weather -9C | ROC General | 2026-01-19
ROC | January | KSTP- Gerrick from Ferguson onsite. | ROC General | 2026-01-20
ROC | January | SEOC67- Hamid from ETO off site. | ROC General | 2026-01-27
ROC | January | KSTP - Drew from Ferguson Electric leaving site. STRS48 - Drew from Ferguson Electric off site. | ROC General | 2026-01-22
ROC | January | STETBR - Tower level hi alarm. Placed STW1 and STW3 in auto mode. | ROC General | 2026-01-30
ROC | January | KCSSKR - Terry G on site to complete work on the emergency light system. | ROC General | 2026-01-20
ROC | January | NMTKKC - Garrick from Ferguson Electric on site for epoxy work. | ROC General | 2026-01-28
ROC | January | KLPS27 - Chris from property services on site to remove a fire extinguisher for recharge. | ROC General | 2026-01-20
ROC | January | GWTP - Terry G. is on site placing heaters Adeela Khan signing out | ROC General | 2026-01-29
ROC | January | KSTP - Drew from Ferguson electric leaving site. | ROC General | 2026-01-29
ROC | January | SEOC67- Teodore from AB on site. 12:10 Teodore off site. | ROC General | 2026-01-26
ROC | January | Ethan U signing in | ROC General | 2026-01-16
ROC | January | Pest Control attending following sites- AUSS, AUSSYS,AUW14,AUW57,AUPSRR,AUPSOH,AUETOH,AURSOH,AURSBSAUETFC,AUPSWS | ROC General | 2026-01-21
ROC | January | KLET27 - Steven from ABPMC leaving site. | ROC General | 2026-01-19
ROC | January | Connor Smith signing out | ROC General | 2026-01-27
ROC | January | Adam Button signing in -18 C clear | ROC General | 2026-01-25
ROC | January | AUETFC - Dominic from Honeywell is on site 13:13 - Dominic is finished on site | ROC General | 2026-01-30
ROC | January | Connor Smith signing in -14C Clear | ROC General | 2026-01-27
ROC | January | GRSSWA, Franco from Property services is on site | ROC General | 2026-01-29
ROC | January | MTW3 - Dominick from Honeywell on site. | ROC General | 2026-01-22
ROC | January | SHSP - Phil from AB informed they are done at site YDOC - Phil and contractor entering site 11:35 - Leaving site | ROC General | 2026-01-19
ROC | January | Christian Van Beek signing in. Weather: -13C and clear. | ROC General | 2026-01-23
ROC | January | Adam Button signing in | ROC General | 2026-01-30
ROC | January | Carter Dunn Signing In, -21D/Clear | ROC General | 2026-01-31
ROC | January | Connor Smith signing in | ROC General | 2026-01-20
ROC | January | KBSP- Terry from Property Services leaving site. | ROC General | 2026-01-20
ROC | January | NMTKKC - Jamie from ETO engineering leaving site. | ROC General | 2026-01-23
ROC | January | Carter Dunn Signing In, -14D/Clear | ROC General | 2026-01-23
ROC | January | KSSP - Ben Han leaving site. | ROC General | 2026-01-19
ROC | January | Ethan U signing in | ROC General | 2026-01-16
ROC | January | Ethan U signing in Weather -10. | ROC General | 2026-01-15
ROC | January | Carter Dunn Signing Out | ROC General | 2026-01-25
ROC | January | EGSSSC- Joe O done on site | ROC General | 2026-01-15
ROC | January | KBSP- Drew from Ferguson offsite Connor Smith signing out | ROC General | 2026-01-20
ROC | January | AUETFC- Dominic from Honeywell onsite. 09:26- Offsite. | ROC General | 2026-01-20
ROC | January | VNPS, Natalie from Process Engineering is on site | ROC General | 2026-01-07
ROC | January | MARS- Courney from Torbear is leaving site | ROC General | 2026-01-17
ROC | January | Adeela Khan signing in. Weather: -14 and clear | ROC General | 2026-01-21
ROC | January | Carter Dunn Signing Out | ROC General | 2026-01-07
ROC | January | Adeela Khan signing out | ROC General | 2026-01-14
ROC | January | Adam Button signing in | ROC General | 2026-01-08
ROC | January | Connor Smith signing out | ROC General | 2026-01-09
ROC | January | Connor Smith signing in 3C Rainy | ROC General | 2026-01-09
ROC | January | KSETDP- Tony from Landmark on site | ROC General | 2026-01-08
ROC | January | Angelica Chepiga signing out | ROC General | 2026-01-08
ROC | January | Adam Button signing in | ROC General | 2026-01-09
ROC | January | Carter Dunn Signing In, -13D/Blizzard | ROC General | 2026-01-15
ROC | January | Adam Button signing in | ROC General | 2026-01-15
ROC | January | VNPS, Natalie from Process Engineering is off site | ROC General | 2026-01-07
ROC | January | Christian Van Beek signing out. | ROC General | 2026-01-15
ROC | January | KSTP, Gerrick from Ferguson Electric is leaving site | ROC General | 2026-01-07
ROC | January | YDOC, YDOC9, OCF, shaft 4, SEOC 8/9 - Johnathan from PS testing fire alarm | ROC General | 2026-01-14
ROC | January | HMSS - Ryan from Capital on site. | ROC General | 2026-01-08
ROC | January | KSSP - Ben from Property services leaving site. | ROC General | 2026-01-08
ROC | January | Adeela Khan signing in KBSP - Drew from Ferguson Electric is on site | ROC General | 2026-01-14
ROC | January | AURSBS - Dom from Honeywell leaving site | ROC General | 2026-01-12
ROC | January | EGSSSC- Joe O on site | ROC General | 2026-01-15
ROC | January | Angelica Chepiga signing in, weather +2C | ROC General | 2026-01-08
ROC | January | KSETDP, Junji from IAM is on site with landmark, once they are finished he will give a call back | ROC General | 2026-01-07
ROC | January | Ethan U signing in | ROC General | 2026-01-07
ROC | January | Christian Van Beek signing in. Weather: -3C and clear. | ROC General | 2026-01-12
ROC | January | Angelica Chepiga signing in, weather +2C | ROC General | 2026-01-10
ROC | January | STPS48 - Dom from Honeywell onsite | ROC General | 2026-01-14
ROC | January | NBSP, KCSSKR, KCETFS, KCETDS - Imtiaz from Pesticon will be attending these sites | ROC General | 2026-01-14
ROC | January | MKETFA- Meghan from YRP onsite | ROC General | 2026-01-09
ROC | January | KSSP - Ben from Property Services is finished on site | ROC General | 2026-01-14
ROC | January | Angelica Chepiga signing out | ROC General | 2026-01-07
ROC | January | AUSS - Teodore from AB on site. | ROC General | 2026-01-08
ROC | January | GRSSWA - Dom from Honeywell finished at site | ROC General | 2026-01-13
ROC | January | Adam Button signing out | ROC General | 2026-01-08
ROC | January | KLET27, Presley from West Power/Rogers is on site, working on the fibre cables | ROC General | 2026-01-13
ROC | January | KSTP- Garrick from Ferguson Electric is done on site | ROC General | 2026-01-08
ROC | January | KSSP- Drew from Ferguson onsite. 11:36- Offsite | ROC General | 2026-01-09
ROC | January | KSTP- Gerrick from Ferguson onsite. | ROC General | 2026-01-09
ROC | January | KSETDP- Tony from Landmark is on site | ROC General | 2026-01-09
ROC | January | KSTP - Garrick from Ferguson Electric on site to pull some pipe. | ROC General | 2026-01-12
ROC | January | KSETDP - Junjie from IAM visiting site. 14:44 Junjie off site. | ROC General | 2026-01-08
ROC | January | GWTP - Ben from PS onsite to work on heating system in generator and chemical room | ROC General | 2026-01-12
ROC | January | MTSP, Dominic from Honeywell is on site MTSS, Dominic from Honeywell is on site | ROC General | 2026-01-15
ROC | January | KSETDP - Junjie with Landmark off site. | ROC General | 2026-01-07
ROC | January | GWTP- Ben from property services is on site to work on generator heater | ROC General | 2026-01-09
ROC | January | Adeela Khan signing out | ROC General | 2026-01-12
ROC | January | Christian Van Beek signing out. | ROC General | 2026-01-12
ROC | January | Angelica Chepiga signing in,weather +2C | ROC General | 2026-01-09
ROC | January | KSETDP - Tony from Landmark onsite for mechanical work | ROC General | 2026-01-12
ROC | January | QVW12 - Theodore from AB working on site 9:04 - Will be doing grinding work, disregard fire alarm. Will notify Theodore onsite if alarm is triggered. 289-839-0704 | ROC General | 2026-01-12
ROC | January | Carter D Signing Out | ROC General | 2026-01-09
ROC | January | Pest control visiting sites: NBSP,SHSP, SHSSDK,SHTP,SHW2, SHETCS. | ROC General | 2026-01-08
ROC | January | KBSP, Drew from Ferguson Electric is leaving site | ROC General | 2026-01-13
ROC | January | Carter Dunn Signing Out | ROC General | 2026-01-13
ROC | January | QVW12- Stephen from AB done on site | ROC General | 2026-01-08
ROC | January | Carter D Signing In, 1D/Clear | ROC General | 2026-01-13
ROC | January | VNETAG- Mehgel from YRP is on site | ROC General | 2026-01-09
ROC | January | SUSP - Dominic from Honeywell on site. | ROC General | 2026-01-08
ROC | January | STPS48 - Drew from Ferguson electric on site. 09:03 Off site. | ROC General | 2026-01-08
ROC | January | KSSP, ETO Enginnering consultant on site | ROC General | 2026-01-13
ROC | January | Carter Dunn Signing In, 1D/Clear | ROC General | 2026-01-08
ROC | January | KSSP - Ben from Property services on site. | ROC General | 2026-01-08
ROC | January | QVW12 - Theodore from ABPMC leaving site. | ROC General | 2026-01-12
ROC | January | Ethan Ullalkar signing out. | ROC General | 2026-01-13
ROC | January | Ethan Ullalkar signing out. | ROC General | 2026-01-07
ROC | January | Adeela Khan signing in. Weather: -5 and Windy | ROC General | 2026-01-11
ROC | January | Ethan U signing in Weather 4. | ROC General | 2026-01-14
ROC | January | Ethan Ullalkar signing out. | ROC General | 2026-01-14
ROC | January | Christian Van Beek signing in. Weather: -3C and clear. | ROC General | 2026-01-14
ROC | January | Adeela Khan signing in. Weather: -1C and Cloudy | ROC General | 2026-01-12
ROC | January | Ethan Ullalkar signing out. | ROC General | 2026-01-08
ROC | January | KSTP - Garick from Ferguson onsite for pipe work | ROC General | 2026-01-13
ROC | January | GRSSWA, Dominic from Honeywell is on site | ROC General | 2026-01-13
ROC | January | Christian Van Beek signing in. Weather: 1C and clear. | ROC General | 2026-01-13
ROC | January | Christian Van Beek signing out. | ROC General | 2026-01-14
ROC | January | MKRSMR - Ben from PS leaving site | ROC General | 2026-01-13
ROC | January | Carter Dunn Signing In | ROC General | 2026-01-07
ROC | January | Angelica Chepiga signing out | ROC General | 2026-01-10
ROC | January | STRSMR - Travis W testing flood alarm , eyewash alarm and cleaning chlorine analyzers. | ROC General | 2026-01-08
ROC | January | NMTKKC - Cody from Kingdom construction on site. | ROC General | 2026-01-08
ROC | January | KSSP - Drew from Ferguson electric on site. | ROC General | 2026-01-08
ROC | January | Ethan Ullalkar signing out. | ROC General | 2026-01-12
ROC | January | Adam Button signing out | ROC General | 2026-01-09
ROC | January | KBSP - Drew from Ferguson onsite for conduit work | ROC General | 2026-01-12
ROC | January | Angelica Chepiga signing in, weather 0C | ROC General | 2026-01-07
ROC | January | GWTP- Ben from property services offsite. | ROC General | 2026-01-09
ROC | January | Angelica Chepiga signing out | ROC General | 2026-01-11
ROC | January | Pesticon Pest control visiting the following locations today: MARS, VNRSKS, RHRSTR, RHRSWA. | ROC General | 2026-01-12
ROC | January | Christian Van Beek signing in. Weather: -2C and clear. | ROC General | 2026-01-11
ROC | January | Christian Van Beek signing out. | ROC General | 2026-01-11
ROC | January | VNETFD/PVSS/VNETAG/VNPSAP/BLSS/HMSS, PCO Operator on site | ROC General | 2026-01-13
ROC | January | NMTKKC- Kody from Kingdom Construction is done on site | ROC General | 2026-01-08
ROC | January | MKPSMR - Drew from Ferguson electric leaving site, not able to arm the building. Corp security will take care of it. | ROC General | 2026-01-07
ROC | January | KSTP - Garrick from Ferguson Electric leaving site. | ROC General | 2026-01-12
ROC | January | KBSP - Drew from Ferguson Electric leaving site. | ROC General | 2026-01-12
ROC | January | KSTP - Drew from Ferguson onsite running conduit | ROC General | 2026-01-05
ROC | January | KSSP - PS onsite | ROC General | 2026-01-05
ROC | January | Ethan. U Signing the in Weather: 0 freezing rain | ROC General | 2026-01-06
ROC | January | Christian Van Beek signing in. Weather: -9 and clear. | ROC General | 2026-01-05
ROC | January | Christian Van Beek signing out. | ROC General | 2026-01-06
ROC | January | NMW12, Jeff from Keyshack is on site 13:43, Jeff left site | ROC General | 2026-01-05
ROC | January | Connor Smith signing out | ROC General | 2026-01-01
ROC | January | AUSSHS, Jeff from Keyshack is on site | ROC General | 2026-01-06
ROC | January | Adam Button signing out | ROC General | 2026-01-02
ROC | January | Christian Van Beek signing in. | ROC General | 2026-01-02
ROC | January | Christian Van Beek signing in. Weather: -11 and clear. | ROC General | 2026-01-04
ROC | January | KSETDP - Tony from Landmark entering site to retrieve tools 12:23 - Leaving site | ROC General | 2026-01-05
ROC | January | Carter Signing Out | ROC General | 2026-01-06
ROC | January | KSTP- Garrick from Ferguson Electric iso n site | ROC General | 2026-01-06
ROC | January | GWTP, Property services is on site | ROC General | 2026-01-05
ROC | January | QVW12, Drew from Ferguson Electric is on site | ROC General | 2026-01-06
ROC | January | GWTP - PS leaving site | ROC General | 2026-01-05
ROC | January | Adam Button signing out | ROC General | 2026-01-06
ROC | January | Christian Van Beek signing out. | ROC General | 2026-01-03
ROC | January | Connor Smith signing out | ROC General | 2026-01-03
ROC | January | KSTP- Garrick from Ferguson electric is done on site | ROC General | 2026-01-06
ROC | January | Adeela Khan signing out | ROC General | 2026-01-02
ROC | January | Keswick/Sutton, Derek from Aquazition is doing flushing | ROC General | 2026-01-05
ROC | January | Connor Smith signing in -19 Cloudy | ROC General | 2026-01-01
ROC | January | KSTP, Drew from Ferguson Electric is leaving site | ROC General | 2026-01-05
ROC | January | Adam Button signing in -1 Clear | ROC General | 2026-01-06
ROC | January | Connor Smith signing in -8C Cloudy | ROC General | 2026-01-03
ROC | January | Adam Button signing in -10 clear | ROC General | 2026-01-01
ROC | January | Christian Van Beek signing out. | ROC General | 2026-01-02
ROC | January | Ethan Ullalkar signing out. | ROC General | 2026-01-04
ROC | January | Ethan U signing in | ROC General | 2026-01-05
ROC | January | Connor Smith signing out | ROC General | 2026-01-04
ROC | January | Christian Van Beek signing out. | ROC General | 2026-01-05
ROC | January | Adeela Khan signing in. Weather: -11 and clear | ROC General | 2026-01-02
ROC | January | Adeela Khan signing out | ROC General | 2026-01-01
ROC | January | NBSSJA - Ben Han from property services on site to check the discharge air system. | ROC General | 2026-01-02
ROC | January | Connor Smith signing in -6C Cloudy | ROC General | 2026-01-02
ROC | January | Ethan U signing in | ROC General | 2026-01-04
ROC | January | Christian Van Beek signing in. Weather: -10C and clear. | ROC General | 2026-01-03
ROC | January | KLET27 - Terry G leaving site. | ROC General | 2026-01-02
ROC | January | STETBR/STETTL - Andrew from OCWA will be flushing in zone 1 and zone 2 in Stouffville today. | ROC General | 2026-01-02
ROC | January | Ethan Ullalkar signing out. | ROC General | 2026-01-05
ROC | January | NMW136, Treated Free Cl2 hihi, Rotated Ammonia pumps so ammonia pump 1 is D1 and ammonia pump 2 is in D2 | All Water System ROC General | 2026-01-18
ROC | January | NMETIB, Activated D1 to have towers offset | All Water System ROC General | 2026-01-18
ROC | January | YWS+NYWS normal Adam Button signing out | All Water System ROC General | 2026-01-18
ROC | January | STETTL - Joe M on site for health and safety inspection. Disregard eyewash alarm. | All Water System ROC General | 2026-01-26
ROC | January | YWS+NYWS normal ARPS- ROYKS to ROPKS commfail alarm came in Alarm cleared trends okay | All Water System ROC General | 2026-01-26
ROC | January | NMPSKC - Dan B on site to complete pump testing. Dan will be running each pump in manual to obtain electrical motor stats. | All Water System ROC General | 2026-01-23
ROC | January | NMVCBA - Placed valve in manual/open at 40L/s to prolong the drain cycle of NMETIB to keep its level offset from NMETHW. | All Water System ROC General | 2026-01-23
ROC | January | NBW3, Influent Free Cl2 lolo, Tower still fill normally, no issues. If another well fails, will notify operator RHRSTR, Deactivated D1 VNPS PD7, Placed pump 1 man/off MAPS PD7, Placed pumps 3 back to auto | All Water System ROC General | 2026-01-23
ROC | January | YWS+NYWS normal | All Water System ROC General | 2026-01-27
ROC | January | AUPSRR - Ryan B. is on site for a JHS inspection. May trigger an eyewash alarm. | All Water System ROC General | 2026-01-23
ROC | January | VNPS - Lee F on site and has requested that pump 2 and 3 be deactivated and pump 1 and 4 be activated for testing. KLW34 - Benson S on site to complete a chlorine leak detection test. | All Water System ROC General | 2026-01-19
ROC | January | NMW15- Station turbidity hi alarm came in. Rotated D1 to silicate pump 2 and placed P1 in man/off and disabled all stop rotation | All Water System ROC General | 2026-01-24
ROC | January | STETTL- Notified Phil D about heat trace fault alarm. Will head to site. Informed Ernie H of situation and let him know they may be needed later to resolve issue. Created CMU5 W11611871 QVW12- Treated total Cl2 hi alarm came in. Recovered after 3 mins. Reset alarm #CMU5 | All Water System ROC General | 2026-01-24
ROC | January | AURSOH, Deactivated D1 MAPS PD8. Placed pumps man/off VNPS PD8, Placed pumps man/off Preparing for Maple to Jefferson | All Water System ROC General | 2026-01-24
ROC | January | Maple to Jefferson Feed complete | All Water System ROC General | 2026-01-25
ROC | January | AUETAD, Total Cl2 lolo alarm, Trends show an abnormal dip that occurred on the analyzer, both downstream and upstream analyzers are reading find. Activated D1 on tower for extra precautions. Notified Donald M of the drop in the analyzer, he is heading to site. 16:52, Combined Cl2 lolo, Donald M on site working on the analyzer 16:54, Donald M called to inform that he does need Instrumentation on call, contacted Rick L, he will head to site to assist Donald M. 17:05, Donald M is leaving site, Took a grab sample for site. Rick L is heading to site as per the phone call from Donald M 18:29, Rick L on site, working on the analyzer 19:31, Rick L is finished on site CMU5: W11596027 (Donald M) CMU5: W11596036 (Rick L) | All Water System ROC General | 2026-01-16
ROC | January | AUETAD, Historian Heartbeat, Notified Chris S, he will look into it | All Water System ROC General | 2026-01-16
ROC | January | MKRSEM - Request TO (Zhoran) to run 2 pumps | All Water System ROC General | 2026-01-15
ROC | January | KSTP- Ryan B on site working back wash pumps | All Water System ROC General | 2026-01-15
ROC | January | MKPSSA - Travis W. on site exercising pump 3 | All Water System ROC General | 2026-01-16
ROC | January | NBW5 - Discharge Pressure LoLo alarm came in. Checked site. Noticed well is Local/off. Called Dave T. who informed he is on site and triggered the alarm. | All Water System ROC General | 2026-01-23
ROC | January | NMETIB - Deactivated duty 1 to help offset with NMETHW | All Water System ROC General | 2026-01-23
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-16
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-17
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-15
ROC | January | NMW136 - Alex B. is on site and will be completing a chlorine leak detection test, inspecting chlorine system, analyzer maintenece, and JHS which may trigger an eyewash alarm | All Water System ROC General | 2026-01-16
ROC | January | MTW12/MTW3 - Kingsley M. called to inform that he will be restarting the OIT at both sites. Tower is draining and 2% away from duty activation. Placed MTW2 and MTW3 into man/off. Will get a historian heartbeat 10:10 - Kingsley called back to inform that he is finished restarting the OITs. Placed MTW2 and MTW3 back to auto | All Water System ROC General | 2026-01-26
ROC | January | NMVCBA- Placed valve in manual at 40L/s | All Water System ROC General | 2026-01-26
ROC | January | MAPS PD8 P1 Discharge valve 1 failed to open and P1 failed to start alarms. P3 restarted on duty 1. Cleared alarms, will monitor next cycle. | All Water System ROC General | 2026-01-19
ROC | January | YWS + NYWS Normal Adeela Khan Signing out | All Water System ROC General | 2026-01-21
ROC | January | Angelica Chepiga signing in, weather -9C | All Water System ROC General | 2026-01-19
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-28
ROC | January | GWTP - Train 5 shutdown and permeate turbidity hihi alarm came in. Checked site. Called Jackie S. who informed she is looking into it | All Water System ROC General | 2026-01-16
ROC | January | QVW12 - Theodore from AB project management and construction is finished on site. Any smoke detector alarms from now on are real and will need to be escalated | All Water System ROC General | 2026-01-16
ROC | January | VNRSKS- Activated D1 at 74% | All Water System ROC General | 2026-01-27
ROC | January | Adeela Khan signing in. Weather: -3 and cloudy | All Water System ROC General | 2026-01-17
ROC | January | STETTL to STW12 Communication loss alarm came in. Checked site. Noticed communications are back and alarm cleared. Trending is okay | All Water System ROC General | 2026-01-17
ROC | January | NMETHW, Activated D1 to have towers offset 13:04, QVW2, uncommanded stop alarm, reset alarm and waited for pump to start on its own, pump wouldn't start, placed well 2 man/on 13:08, Placed well back to auto, will send email to ops about it failing to start up. RO has noticed that the first start up when it comes to duty start usually fails but then will start after the first fail attempt | All Water System ROC General | 2026-01-18
ROC | January | STW3 - Joe M. is on site and will be completing a chlorine leak detection test | All Water System ROC General | 2026-01-16
ROC | January | VNETAG - Benson S finished on site. VNPSAP - Benson S headed to site to complete work orders including chlorine analyzer maintenance, JHSC checks and hi/low temp alarm tests. | All Water System ROC General | 2026-01-20
ROC | January | GWTP - Jack P. called to request a CMU5 for Sean P. and Daniel B. for Emergency Generator Maintenance from yesterday. CMU5 created W11606577 #CMU5 | All Water System ROC General | 2026-01-21
ROC | January | GWTP- Jack P called about Train 5 in R clean will neutralize and go back into service. Train 5 may shutdown after neutralization. Jack P directed to disregard if it does | All Water System ROC General | 2026-01-21
ROC | January | STW12/3, Placed wells back to auto | All Water System ROC General | 2026-01-18
ROC | January | Angelica Chepiga signing in, weather -11C | All Water System ROC General | 2026-01-28
ROC | January | KSETDP - Jackie S on site to complete work orders including hi/low temp alarm test and chlorine leak detection test. | All Water System ROC General | 2026-01-20
ROC | January | KLW34 - David T. is on site for PM's. This includes Chlorine Analyzer maintenance, Turbidimeter maintenance, and chlorine scrubber maintenance. | All Water System ROC General | 2026-01-21
ROC | January | SHETCS- Outlet flow hi alarm. Tower level lo alarm almost reached . Notifed Jake M. Req to call King township to inquire about flushing in system. Called Town of King spoke with Tyler. King is flushing in system and they called Cole W beforehand. Notified Jake M . Jake M req to stop flushing. Called Tyler from King township to stop flushing operations. Updated Jake M of situation | All Water System ROC General | 2026-01-21
ROC | January | VNPS PD8- Placed P4 man/off STETBR- Tower level hi alarm. Placed STW12/3 in auto as perinterim | All Water System ROC General | 2026-01-21
ROC | January | QVW12 - Donald M and Will M have fixed the chlorine gas leak and placed QVW1 into duty 1 to run to system. Operations normal. | All Water System ROC General | 2026-01-23
ROC | January | GWTP, UV Reactor 1 Dosage Hi Alarm, Notified Dan Z, she will look into it | All Water System ROC General | 2026-01-16
ROC | January | MAPS PD8 - Kyle Rae and Ernie H. are finished on site | All Water System ROC General | 2026-01-21
ROC | January | HLETYS - Stephen is headed to site | All Water System ROC General | 2026-01-22
ROC | January | KSTP - Kingsley called and said all the server resets are done and says that it is okay to put the Low Lifts and Hi Lifts back to auto. Called Donald M . who directed to place them back to auto | All Water System ROC General | 2026-01-22
ROC | January | NMW15- Combined Chlorine LoLo Alarm. Interlocked well while running in middle of cycle. Trends show some brief flow with combined chlorine below 0.25mg/L however the treated free chlorine remained above 0.05mg/L during this time. Placed well into manual and notified Ben H. CONSULT | All Water System ROC General | 2026-01-22
ROC | January | Adeela Khan signing in. | All Water System ROC General | 2026-01-26
ROC | January | STETBR - Tower Level Hi alarm came in. Placed STW12 and STW3 into auto, as per interim | All Water System ROC General | 2026-01-26
ROC | January | NMTKBS - Jason G on site to test the high level alarm. | All Water System ROC General | 2026-01-22
ROC | January | HLETYS - Tower Level Hi alarm came in. Checked site. Noticed the HLW1 was in manual as well as the HLW2 VC FCV2. Called Stephen B. who informed he is still on site 11:46 - Stephen B. called back and directed to place HLW1 and HLW2 VC FCV2 back to auto. | All Water System ROC General | 2026-01-21
ROC | January | NBW5 Turbidity hi alarm came in disregard on shift report | All Water System ROC General | 2026-01-21
ROC | January | KSETDP - Building Smoke Detector Alarm came in. Tower is offline. Called Jackie S. who informed that contractors are on site welding. Jackie also informed she is headed to site to investigate further 12:02 - Jackie S. called back to inform that there is a YR personnel on site. There are also UPS offline and PAC Control Panel DC power Fault alarms outstanding. Jackie will investigate further 12:06 - Jackie informed that Sean P. is on site | All Water System ROC General | 2026-01-23
ROC | January | NMW136- Treated total and combined Cl2 lo alarms came in. Wells not active no water directed to users reset after 6 mins | All Water System ROC General | 2026-01-27
ROC | January | YWS+NYWS normal | All Water System ROC General | 2026-01-27
ROC | January | VNETAG- VNETAG to VNPSAP comm fail MLPSSA- MKPSSA to MKRSMR comm alarm NMETIB- NMETIB to NMW136 comm alarm Reset all alarms trends okay | All Water System ROC General | 2026-01-27
ROC | January | MKRSEM- Called Metro spoke with Paul to stop pumping to reservoir GWTP- Sutton header pH high alarm came in. Spike in reading slowly coming down. Duty not active and no water being supplied to SUETDR. Will monitor for changes and clear alarm once back in normal range | All Water System ROC General | 2026-01-27
ROC | January | Leslie St. and Doane Road - Ryan from Town of East Gwillimbury called to inform that there is lots of water at this intersection. Ryan informed that an operator went out and noticed a trail through the snow. Ryan wanted to know if any flushing occurred near this intersection. Will speak to ops and give Ryan a call back once more information is known Close to QVW34. Gave Will M. a call. Will informed that he was backflushing but it went directly to the storm sewer. Will M. will investigate 12:20 - Called William M. for an update. Will informed the pooling of water found was from them backflushing. 12:25 - Called Ryan from Town of East Gwillimbury back and let him know about the backflushing | All Water System ROC General | 2026-01-29
ROC | January | NBW2 - David T leaving site, well 2 man/off for the night. | All Water System ROC General | 2026-01-29
ROC | January | KSETDP, Building Smoke Detector Alarm, notified Jack P, he will go to site to investigate CMU5: W11595753 | All Water System ROC General | 2026-01-16
ROC | January | NMVCBA- Placed valve back in auto | All Water System ROC General | 2026-01-27
ROC | January | KSETWB - Eric s leaving site. | All Water System ROC General | 2026-01-28
ROC | January | VNETFD - Rick L leaving site. | All Water System ROC General | 2026-01-28
ROC | January | Adam Button signing in -13 Clear VNPS PD7- Place P1/4 in man/off MAPS PD7 -Placed P2/4 in auto | All Water System ROC General | 2026-01-26
ROC | January | YWS+NYWS normal | All Water System ROC General | 2026-01-27
ROC | January | Adeela Khan signing out | All Water System ROC General | 2026-01-19
ROC | January | AUETFC - Joe D. called to inform that he is headed to site. Joe informed he may deactivate duty early for sampling | All Water System ROC General | 2026-01-21
ROC | January | Connor Smith signing in -14C Clear | All Water System ROC General | 2026-01-27
ROC | January | NMW15- Influent free Cl2 lo alarm came in. Checked trends. Dip in influent and started to recover slowly. Continued to monitor and cleared alarm after 10 mins | All Water System ROC General | 2026-01-17
ROC | January | GWTP- Sutton header free Cl2 hi alarm came in. Notified Phil D. Directed to disregard alarm. While on the phone notified Phil D that controlling tower is currently losing with D1 active while SUETDR D1 also active. Phil D directed to placed KSTP hi lifts in auto an monitor Fluoride residuals on start up. KSTP- Placed highlifts 1-3 in auto #consult | All Water System ROC General | 2026-01-25
ROC | January | NMVCBA - Placed back to auto. | All Water System ROC General | 2026-01-29
ROC | January | STETTL- STETTL to STW12 comm alarm. Reset alarm trends okay KSTP- Fin water Fluoride hi alarm came in. Notified Phil D. Directed to place KSTP high lifts in man/off. Phil D directed to increase GWTP output from 180L/s to 200L/s #consult | All Water System ROC General | 2026-01-25
ROC | January | MAPS PD7, Placed pumps 1/3 back to auto VNPS PD7, pLACED PUMPS 1/4 MAN/OFF | All Water System ROC General | 2026-01-25
ROC | January | BLW3- Cl2 leak alarm and generator running. No spike in Cl2 notified Jackie S. Will investigate issued cleared Cl2 leak alarm. Power loss on site no time for restoration STETTL- Eric S on site to work on Cl2 analyzer. Placed it in calibration mode for work. GWTP- Patrick F on site to work on train 7 inlet valve VNRSKS- Deactivated D1 VNPS PD7- Placed P1/4 in manual MAPS PD7- Placed P 1-4 in auto | All Water System ROC General | 2026-01-30
ROC | January | VNETAG - Tower level low alarm. Checked site, tower low alarm setpoint is the same value as the duty 1 start setpoint. Duty is active and flow is entering the tower. reset alarm. | All Water System ROC General | 2026-01-30
ROC | January | NBW3 - Effluent Free Chlorine Lo alarm came in. Checked site. Wells are not running and water is not being directed to users | All Water System ROC General | 2026-01-30
ROC | January | Connor Smith signing out | All Water System ROC General | 2026-01-29
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-31
ROC | January | HLW1- Eric S onsite working on silicate pump 2. Pump is OOS. Can disregard related alarms that come in. | All Water System ROC General | 2026-01-29
ROC | January | AURSBS - Chlorine GCLR 1 Vlv Fail to Open Alarm at duty stop. Alarm cleared. | All Water System ROC General | 2026-01-29
ROC | January | YWS + NYWS NORMAL | All Water System ROC General | 2026-01-30
ROC | January | YWS+NYWS normal | All Water System ROC General | 2026-01-17
ROC | January | Adeela Khan signing in. Weather: -14 and clear | All Water System ROC General | 2026-01-21
ROC | January | RHRSTR - Tim H on site to inspect the rechlorination system. Tim H directed toa activate duty 1 for RHRSTR. | All Water System ROC General | 2026-01-23
ROC | January | MAPS PD7 - Placed all pumps at VNPS PD7 back to man/closed and placed all pumps at MAPS PD7 back to auto | All Water System ROC General | 2026-01-22
ROC | January | YWS + NYWS Normal Adeela Khan signing out | All Water System ROC General | 2026-01-22
ROC | January | Angelica Chepiga signing out | All Water System ROC General | 2026-01-30
ROC | January | Adeela Khan signing out | All Water System ROC General | 2026-01-29
ROC | January | HLW1 - Treated Free chlorine Hi alarm at duty start. Value back to normal, cleared alarm. | All Water System ROC General | 2026-01-29
ROC | January | YWS+NYWS normal | All Water System ROC General | 2026-01-18
ROC | January | JFPS- Placed P1 back in auto Reverting JFRS to MARS run as per procedure GWTP- Lowlift P2 uncommanded stop/ hydraulic valve uncommanded close alarm came in reset as per shift report KLET27- Activated D1 QVW34- Well 3 control room hi lo temp alarm came in. Emailed Central water team. | All Water System ROC General | 2026-01-18
ROC | January | GWTP- Chris S onsite working on low lift chlorine pumps. Can disregard related alarm. | All Water System ROC General | 2026-01-28
ROC | January | VNRSKS - Deactivated Duty 1. | All Water System ROC General | 2026-01-28
ROC | January | NBW37- David T onsite working on hypo lines. Well is local off. | All Water System ROC General | 2026-01-20
ROC | January | MAPS PD7- Placed P2-4 in manual and stopped P3 VNPS PD7- Placed P1 in auto | All Water System ROC General | 2026-01-25
ROC | January | NBW2- Cl2 booster uncommanded start and stop and gas chlorinator failed to close. Booster pump 1 running okay reset alarms as chlorinator 2 closed | All Water System ROC General | 2026-01-25
ROC | January | VNRSKS- Deactivated D1 | All Water System ROC General | 2026-01-25
ROC | January | Connor Smith signing out | All Water System ROC General | 2026-01-28
ROC | January | MARS- Reservoir Valve House Flood Alarm. Called Tim H. No answer. Will try again. 09:46- Notified Tim H. He will look into it. 09:57- Tim spoke with contractor who had tripped alarm. Can disregard. | All Water System ROC General | 2026-01-27
ROC | January | RHRSTR - Activated D1 to help with MARS level. | All Water System ROC General | 2026-01-27
ROC | January | AUVCBS- Yash S onsite for network maintenance. Will lose comms for 15-20 mins. Duty is active. Placed valve in manual to prevent it from closing during work. 10:35- Yash S finished with work. Placed valve back into auto. | All Water System ROC General | 2026-01-27
ROC | January | RHRSTR- Deactivated duty | All Water System ROC General | 2026-01-23
ROC | January | AUPSRR - Ricardo L. is on site for annual calibrations. Placed the pumps manual/off and will monitor tower level and call Rick once levels are low. 11:50 - Called Ricardo L. informing that the tower is nearing duty start. 12:05 - Deactivated duty 1 at Aurora West 12:10 - Ricardo L. called back that he is done on site for the day. Placed AUPSRR back to auto | All Water System ROC General | 2026-01-29
ROC | January | YWS + NYWS NORMAL | All Water System ROC General | 2026-01-29
ROC | January | VNPS PD7 - Pumps 1&4 man/off MAPS PD7 - Pumps 1&3 to auto. | All Water System ROC General | 2026-01-29
ROC | January | Christian Van Beek signing in. | All Water System ROC General | 2026-01-29
ROC | January | YWS+NYWS normal | All Water System ROC General | 2026-01-24
ROC | January | STETTL- Tower level lo alarm came in. STW12/3- Placed P1/2/3 in man/on as per interim | All Water System ROC General | 2026-01-24
ROC | January | KSTP - Generator not in auto alarm outstanding. Called Artour L. who is still on site and will talk to contractors 16:50 - Artour L. called back and informed that the generator is now back to auto and alarm cleared | All Water System ROC General | 2026-01-29
ROC | January | MARS - Called Toronto water (Brett) and requested increase flow to Res. | All Water System ROC General | 2026-01-28
ROC | January | MKETFA- Travis W onsite testing low temp alarm. Will also be exercising gate valve and opening bypass. | All Water System ROC General | 2026-01-20
ROC | January | AUPSWS - Alex B called to inform the ATS at AUPSWS will not transfer power during the generator test. Alex B has contacted electricians and is waiting for assistance. Alex B ahs closed the Poppy Lane valve to conserve water in AUETFC. 10:14: AUPSWS - Alex B called and requested a CMU% for themself and Tyler ZJ. Made CMU5#W11609054 #CMU5 | All Water System ROC General | 2026-01-22
ROC | January | KSTP - Drew from Ferguson Electric is on site and will be testing the generator 08:40 - Artour L. is on site to assist in the generator transfer. Will wait for an operator to head to site 13:15 - KSTP - Generator Enclosure Smoke alarm came in. Called Artour L. who informed they are starting the testing for the generator now and alarms can be disregarded until testing is complete | All Water System ROC General | 2026-01-30
ROC | January | BLW12- Joe W onsite cleaning injection points. Disregard Low pressure alarms. | All Water System ROC General | 2026-01-20
ROC | January | KCETDS - Metering Chamber Flood alarm came in. Called David T. who informed that he will head to site to manually run a pump. CMU5 Created W11625636 #CMU5 | All Water System ROC General | 2026-01-30
ROC | January | NBW2 - CHlorine gas valve 2 fail to close alarm. Checked site, well recently deactivated. Chlorine valve 2 showing as half open. Reset alarm and watched valve close. Operations normal. | All Water System ROC General | 2026-01-30
ROC | January | NMTKKC - Donald M finished and leaving site. | All Water System ROC General | 2026-01-30
ROC | January | YWS + NYWS NORMAL | All Water System ROC General | 2026-01-29
ROC | January | ANW23- Stephen B directed to activate D1 | All Water System ROC General | 2026-01-30
ROC | January | GWTP - GAC 2 Inlet Valve Fault Alarm came in. Jack P. called to inform that he is backwashing GAC 1 and directed to disregard alarm | All Water System ROC General | 2026-01-22
ROC | January | RHRSTR, Deactivated D1 so more flow can move from MARS to RHRSTR | All Water System ROC General | 2026-01-26
ROC | January | YWS + NYWS NORMAL | All Water System ROC General | 2026-01-20
ROC | January | MKRSEM - Called Toronto water (Brett) and requested to stop filling Res. | All Water System ROC General | 2026-01-29
ROC | January | VNRSKS, Mike P from the City of Vaughan called, he has some guys heading to the North MAPS Area (Not directly on site). Was called for a main break in that area, Looking at trends, everything is normal on our end. He will keep the ROC informed on whats happening at that area | All Water System ROC General | 2026-01-25
ROC | January | GWTP - Jack P. is on site and will be backwashing GAC4 | All Water System ROC General | 2026-01-26
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-30
ROC | January | GWTP, Make Up Air Unit 1 Coil Low Temp Alarm, Critical Alarm, Notified Phil D as it is very cold out at this time with the polar vortex moving through the system, he will look into it 19:00, directed to disregard Consult | All Water System ROC General | 2026-01-23
ROC | January | GWTP - ZW7 Feed Valve Failed to Open CLP alarm came in. Checked site. Called Jack P. who directed to ack/reset alarm and ack/reset again if it comes in during neutralization 12:08 - Alarm came back during neutralization. Ack/reset as per Jack P | All Water System ROC General | 2026-01-30
ROC | January | MKPSSA - Building flood alarm. Dan Z has requested a CMU5 to respond to site. Created CMU5#W11611731 #CMU5 | All Water System ROC General | 2026-01-23
ROC | January | STW12/3, Placed wells back to auto | All Water System ROC General | 2026-01-25
ROC | January | Carter Dunn Signing In, -15D/Snowing | All Water System ROC General | 2026-01-24
ROC | January | MARS, Notified toronto operator Zoran to go back to lo flow | All Water System ROC General | 2026-01-24
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-25
ROC | January | NMVCIB, Placed valve manual and set to 40L/sec NMVCBP, Placed back to auto | All Water System ROC General | 2026-01-23
ROC | January | Carter Dunn Signing In, -4D/Clear | All Water System ROC General | 2026-01-22
ROC | January | NMW136 - Well 16 forward flow hi alarm. Checked site, well recently activated to fill the system. Well forward flowmeter reading a high flow value. Will monitor site. | All Water System ROC General | 2026-01-22
ROC | January | Kingsley M is doing window server updates, SCADA/Remote SCADA/Dialer/Vaughan Server updates, directed to disregard | All Water System ROC General | 2026-01-22
ROC | January | VNRKS - Placed pump 3 at MAPS PD7 man/off and place pump 1 at VNPS PD7 into auto | All Water System ROC General | 2026-01-26
ROC | January | BLW12/BLW3 - Kingsley M. called to inform he will be working on the OIT. Tower is currently draining. May get a historian heartbeat alarm | All Water System ROC General | 2026-01-26
ROC | January | STETBR - Tower Level Lo alarm came in. Placed STW12 and STW3 in man/on as per interim | All Water System ROC General | 2026-01-26
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-26
ROC | January | GWTP- Jack P onsite working on turbidimeters. Disregard related alarms. | All Water System ROC General | 2026-01-27
ROC | January | AUVCBS, Placed valve back to auto | All Water System ROC General | 2026-01-15
ROC | January | MAPS PD8 - Pump 1 discharge valve failed to open, P1 failed to start alarms came again. Placed P1 man/off. Duty 1 rotated to P3. Emailed area about outstanding alarm. MARS - Res High level alarm, activated VNRSKS @ 68%. | All Water System ROC General | 2026-01-20
ROC | January | MARS - High level. Deactivated RHRSTR Duty 1 @ 80%. | All Water System ROC General | 2026-01-21
ROC | January | GWTP- Train 2 TMP lo alarm came in again. Alarm is coming in more often the longer the plant is running. Notified Phil D. Directed to disregard for the night #consult | All Water System ROC General | 2026-01-28
ROC | January | QVW12 - Jason G running temporary generator and testing chlorine leak test. | All Water System ROC General | 2026-01-27
ROC | January | NMW136 - Alex B requested pumps back to auto. | All Water System ROC General | 2026-01-27
ROC | January | NMVCBA - Placed valve in manual at 40 L/s | All Water System ROC General | 2026-01-21
ROC | January | GWTP- UV Reactor 1 Failed To Stop Alarm, UV Reactor 1 Start/Stop Seq Fault Alarm. Notified Dan Z. She is looking into it. | All Water System ROC General | 2026-01-28
ROC | January | HLETPR - Stephen B running portable generator and performing health and safety check. HLW1 - Stephen B requested to activate Duty 1. | All Water System ROC General | 2026-01-26
ROC | January | GWTP - Sutton header fluoride hi. SUETDR just deactivated no flow to site. | All Water System ROC General | 2026-01-17
ROC | January | MARS - Res hi level BVPS - Deactivate duty 1 AURSBS - Activate duty 1 | All Water System ROC General | 2026-01-17
ROC | January | NBW5- Placed well 5 in auto as per interim 18:14-NBW5- Placed well 5 back in man/off as interim states if needed can be placed in auto. Nobleton system cycling okay without well | All Water System ROC General | 2026-01-17
ROC | January | JFRS- Deactivated D1/2 AURSBS- Activated D1 NMETIB- Activated D1 | All Water System ROC General | 2026-01-18
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-21
ROC | January | SCADA Room - Carter D. entered site to confirm access with pin and key card for Dominic from Honeywell | All Water System ROC General | 2026-01-16
ROC | January | MAPS PD7, Placed pumps 1/3 in auto VNPS PD7, Placed pumps 2/3 man/off | All Water System ROC General | 2026-01-16
ROC | January | STETBR - Duty just activated. Placed STW12 and STW3 into man/on, as per interim | All Water System ROC General | 2026-01-17
ROC | January | NMVCBA - Placed valve back to auto | All Water System ROC General | 2026-01-17
ROC | January | KSTP - Finished Water Residual LoLo, Finished Water Fluoride Residual Fault, and Total Chlorine Residual Fault alarms came in. Disregarded as per shift report | All Water System ROC General | 2026-01-19
ROC | January | KSTKWP - Jerry Z. called to inform that he is on site and will be testing the chlorine leak alarm | All Water System ROC General | 2026-01-16
ROC | January | ARPS - Martin from OCWA called to inform that he is doing a pump change. Switching from pump 1 to pump 4. | All Water System ROC General | 2026-01-29
ROC | January | ARPS - Checked site. Pump 2 is now running. Also noticed that the analyzers are back within range and cleared alarms. Called OCWA (Bineesh) who informed that the anlalyzer is no longer in maintenance mode. Will give a call back when all the work is complete 16:25 - Peel Ammonia Analyzer A (AIT4A)- Airport Rd Discharge Free Ammonia (AIT34330) Fault and Peel Ammonia Analyzer A (AIT5A)- Airport Rd Discharge Free Ammonia (AIT34330) Fault alarms came in. No issues are found through trends and the reading is within optimal range. Called OCWA (Bineesh) who informed this is due to calculation mistakes that caused the initial combined chlorine hi alarms. Bineesh informed that the miscalculation has been resolved and alarms can be cleared 17:19 - Bineesh from OCWA called to inform that the work with the analyzer is now complete and ARPS is back to normal operation | All Water System ROC General | 2026-01-29
ROC | January | NMETIB- Deactivated D1 at 61% to offset from NMETHW as per shift report. NMVCIB- changed flow setpoint from 40L/s to 80L/s NMVCBA- changed flow set point from 80L/s to 40L/s | All Water System ROC General | 2026-01-17
ROC | January | BLW12 - Hypo day tank containment flood alarm. Checked site, well is active. Trending shows the hypo day tank level dropping. Informed area operations. 08:23 - BLW12 - Created CMU5#W11608957 for Phil Degroot. #CMU5 | All Water System ROC General | 2026-01-22
ROC | January | MAPSN1 - Kyle C. is restarting the server. Should take no more than 5 mins | All Water System ROC General | 2026-01-23
ROC | January | BVPS - Deactivated duty 1 | All Water System ROC General | 2026-01-19
ROC | January | YWS+NYWS normal | All Water System ROC General | 2026-01-28
ROC | January | Adam Button signing out | All Water System ROC General | 2026-01-28
ROC | January | RHRSTR - deactivated D1. | All Water System ROC General | 2026-01-27
ROC | January | HLETYS- Post injection combined Cl2 lo alarm came in Stephen B on site and will investigate | All Water System ROC General | 2026-01-15
ROC | January | VNRSKS - Swapped supply pumps to one MAPS one VNPS pump. | All Water System ROC General | 2026-01-20
ROC | January | HLW2 - Treated free chlorine HiHi alarm at duty start. Value back to normal in 2 readings. Cleared alarm. | All Water System ROC General | 2026-01-29
ROC | January | NMVCBA - Placed to auto, flow setpoint 80l/s NMVCIB - flow setpoint to 40l/s | All Water System ROC General | 2026-01-29
ROC | January | STW12- Influent Free Chlorine LoLo Alarm. Interlocked well after duty deactivated. Recovered after a few minutes. Cleared alarms and interlocked cleared. | All Water System ROC General | 2026-01-28
ROC | January | QVW34- Comm Fail. Alarm cleared. QVW34- Dan B called. He is onsite running well 4 to waste. During this time noticed that the contact tank is halfway through cycle. Dan B is going to call Ben H and William M to inform. 14:51- Dan B spoke with Operations. William M is heading to site to backflush. | All Water System ROC General | 2026-01-28
ROC | January | VNRSKS - Swapped supply pumps to two MAPS pumps. | All Water System ROC General | 2026-01-20
ROC | January | SHETCS - Hypo Pump 1 Failed to stop alarm came in. Checked site. Called Jacob M. who is on site and primed the pump. Reset alarm as per Jacob M. | All Water System ROC General | 2026-01-21
ROC | January | MAPS PD8 - Pump 1 failed to start and discharge valve failed to open alarms. Checked site, Duty 1 rotated to pump 3. Monitored start and reset alarms. | All Water System ROC General | 2026-01-19
ROC | January | KCETFS - Ricardo L. is on site for annual calibrations 14:35 - Ricardo is finished on site | All Water System ROC General | 2026-01-26
ROC | January | SHTP- Well 2 uncommanded stop alarm at duty stop. Reset alarm, well not running, duty not active. | All Water System ROC General | 2026-01-20
ROC | January | GRTPLL - Low lift discharge total chlorine res fault alarm, disregard as per Scada review. | All Water System ROC General | 2026-01-28
ROC | January | AURSBS - Activated D1. | All Water System ROC General | 2026-01-29
ROC | January | ARPS- Martin from OCWA Called. Comm fail caused pump 2 to shut down. He is working on getting another pump going. | All Water System ROC General | 2026-01-28
ROC | January | Connor Smith signing in -12C Clear | All Water System ROC General | 2026-01-28
ROC | January | YWS + NYWS NORMAL | All Water System ROC General | 2026-01-28
ROC | January | MARS - Called Toronto water (Brett) and requested decrease flow. | All Water System ROC General | 2026-01-28
ROC | January | AURSBS - Chlorine GCLR 1 Vlv Fail to Open Alarm at duty stop. Alarm cleared. | All Water System ROC General | 2026-01-28
ROC | January | Adeela Khan signing in. Weather: -17C and Cloudy | All Water System ROC General | 2026-01-29
ROC | January | VNRSKS - Placed pump 3 man/off at MAPS PD7 and Placed Pump 4 into auto at VNPS PD7 | All Water System ROC General | 2026-01-29
ROC | January | Angelica Chepiga signing out | All Water System ROC General | 2026-01-29
ROC | January | KSTP- Artour L onsite commissioning new generator with contractors. Disregard any generator related alarms. | All Water System ROC General | 2026-01-28
ROC | January | YWS + NYWS NORMAL | All Water System ROC General | 2026-01-28
ROC | January | GWTPLL - low lift discharge total chlorine residual fault alarm. Disregard as per shift report | All Water System ROC General | 2026-01-31
ROC | January | NMW136- Alex B requested CMU5 for Silicate Pump 1 Uncommanded Stop. W11603151 CMU5 | All Water System ROC General | 2026-01-20
ROC | January | AUPSRR- Donald M onsite for Cl leak detection, Cl analyzer maintenance and ammonia pump inspection. | All Water System ROC General | 2026-01-20
ROC | January | STRS48 - Lee F on site to complete a leak inspection and repairs on the high lift pump 2 line. Lee requested that duty 1 be changed to pump 2 so he can identify the leak location. Made the necessary change. 10:42 - STRS48 - Lee F found the leak and would like duty 1 assigned to pump 1 while repairs are made. Made the necessary change. | All Water System ROC General | 2026-01-22
ROC | January | SHETCS - Jacob M. called to inform that he is on site and will be cleaning the chlorine analyzers. Jacob also informed that Jordan B. and Dave T. are also on site to work on the hypo system 12:35 - Jacob M. called to inform that he is deep cycling tower down to 5% | All Water System ROC General | 2026-01-22
ROC | January | VNPS - Kingsley called to inform that he will be resetting the local OIT. Kingsley informed this will not affect operations 11:01 - Kingsley is finished resetting the OIT and the heartbeat alarm has cleared | All Water System ROC General | 2026-01-22
ROC | January | GWTP - Jack P and Joe M on site to complete a chlorine leak detection test. | All Water System ROC General | 2026-01-22
ROC | January | GWTP - ZW2 34.5 KPa MIT - Press Decay Test Failed and ZW2 Shutdown alarms came in. Checked site and shift report. Called Dan Z. who directed to leave it off for the night #CONSULT | All Water System ROC General | 2026-01-19
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-17
ROC | January | MAPS - Tim H headed to site for a station check. | All Water System ROC General | 2026-01-23
ROC | January | Connor Smith signing in -10C Cloudy | All Water System ROC General | 2026-01-22
ROC | January | KBSP - UV channel 1 common minor alarm and lamp fail alarm. Checked site, UV channel 1 bank is active and trending shows normal level of dosage and flow. Unable to clear alarms but minor alarms are a disregard on the shift report as long as one bank is running. | All Water System ROC General | 2026-01-23
ROC | January | KSETWB - Eric S on site to work on the outlet analyzer. May see associated alarms. | All Water System ROC General | 2026-01-28
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-17
ROC | January | MKRSEM - Request TO (Peter) to stop pump | All Water System ROC General | 2026-01-17
ROC | January | Connor Smith signing in -13C Clear | All Water System ROC General | 2026-01-29
ROC | January | Adeela Khan signing out | All Water System ROC General | 2026-01-17
ROC | January | NMTKKC- Sanitary Pump Station High Level Alarm. Donald M is onsite working on it. | All Water System ROC General | 2026-01-30
ROC | January | MKRSEM - Reservoir low level alarm. Called Toronto Water (Mehdi) and requested flow to MKRSEM. | All Water System ROC General | 2026-01-30
ROC | January | NMW15 - Treated Free Chlorine HiHi alarm came in. This occurred on well startup. Rotated ammonia pumps so that ammonia pump 1 is in duty 1. Will continue to monitor 07:37 - Relayed this information to Alex B. who will take a look today | All Water System ROC General | 2026-01-21
ROC | January | HLW2 - Downstream Pressure Hi alarm came in. Checked site. Both wells active and sharon valve open. Switched to FCV HLW2. Will monitor | All Water System ROC General | 2026-01-30
ROC | January | Christian Van Beek signing in. Weather: -18C and clear. | All Water System ROC General | 2026-01-30
ROC | January | HLW2 - Combined Chlorine Hi alarm came in. Checked site. Well is running. Combined levels are rising. Called Stephen B. who will take a look | All Water System ROC General | 2026-01-30
ROC | January | VNMCYS - Forward flow HiHi alarm , flow to RH, notified Harch P, he will check first thing in the morning. # Consult | All Water System ROC General | 2026-01-29
ROC | January | QVETQS- System pressure lo alarm came in as D1 deactivated. Cleared alarm as system pressure recovered right away | All Water System ROC General | 2026-01-28
ROC | January | NMETIB - Activated duty 1 to keep level offset from NMETHW. | All Water System ROC General | 2026-01-28
ROC | January | GWTP - Low lift discharge pH and water temp lolo alarms. Jack P informed that Lexsan contractors are on site working on low lift systems. Chris S also on site working on low lift chlorine and chemical systems. | All Water System ROC General | 2026-01-28
ROC | January | KSTP, Fin Water Fluoride Res Hi Alarm, Duty just activated, if residual doesn't come down after 15 minutes, will contact operator 22:41, contacted Phil D, directed to place high lift pumps man/off for the night, he will look into it tomorrow morning consult | All Water System ROC General | 2026-01-23
ROC | January | YWS+NYWS Normal Adam Button signing out | All Water System ROC General | 2026-01-24
ROC | January | NMETIB - activated D1 to offset with NMETHW | All Water System ROC General | 2026-01-30
ROC | January | QVW34- Dan B on site to work on well 4. PCS is also on site for commissioning. Placed Well 3 in man/off | All Water System ROC General | 2026-01-30
ROC | January | HLW1- Treated free hi alarm came in exceeding hihi. P1 man/off. Notified Benson S will take a look on SCADA 15:30- HLW1- Benson called back treated free slowly coming down. Cleared alarm. Directed to call if to comes back in #consult | All Water System ROC General | 2026-01-24
ROC | January | MTW12 - Gen tank 1 level HiHi alarm, disregard as per SCADA review. | All Water System ROC General | 2026-01-30
ROC | January | YWS + NYWS NORMAL | All Water System ROC General | 2026-01-30
ROC | January | YWS + NYWS NORMAL | All Water System ROC General | 2026-01-29
ROC | January | GWTP, Train 2 - Transmembrane Pressure lo alarm, alarm has been coming in consistently then clearing, notified Phil D, directed to disregard for the night and to deactivate KSTKWP/SUETDR Duties consult | All Water System ROC General | 2026-01-25
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-21
ROC | January | MKRSEM - Called Toronto water (Brett) and requested to stop pumps. | All Water System ROC General | 2026-01-30
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-22
ROC | January | HLW2 - Downstream pressure HiHi alarm, Sharon VC on duty 1. Placed Sharon VC man/close. Rotated D1 to FCV2 and lowered flow setpoint from 30 to 20l/s | All Water System ROC General | 2026-01-30
ROC | January | BLW3- Generator running alarm came in. Site on utility power. Generator shut down in auto. Alarm cleared on its own | All Water System ROC General | 2026-01-30
ROC | January | MKRSEM, Notified Toronto operator Zoran to start filling the res | All Water System ROC General | 2026-01-25
ROC | January | QVW12 - Generator fault alarm. Checked site, generator is not running and ATS is pointing to town hydro indicating normal operations. Unable to clear alarm, Shoft report strates that there is a temporary generator set up on site. Contractors likely working on permanent generator, will monitor site. | All Water System ROC General | 2026-01-28
ROC | January | Adam Button signing out | All Water System ROC General | 2026-01-27
ROC | January | KCETFS - Rick L finished on site. | All Water System ROC General | 2026-01-27
ROC | January | SHTP, Reservoir Total Cl2 lolo/Fault, notified David T, he will look into it consult | All Water System ROC General | 2026-01-31
ROC | January | AURSBS - Activated duty 1 to drawdown MARS level. | All Water System ROC General | 2026-01-31
ROC | January | RHRSTR - Deactivated duty 1. | All Water System ROC General | 2026-01-31
ROC | January | STETBR - Tower level low alarm. Activated STW1 and STW3 in manual mode as per the interim procedure. | All Water System ROC General | 2026-01-31
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-31
ROC | January | YWS + NYWS Normal Christian Van Beek signing out. | All Water System ROC General | 2026-01-31
ROC | January | KSTP - Jerry Z on site to complete chlorine analyzer maintenance. | All Water System ROC General | 2026-01-23
ROC | January | NMETIB - Activated duty 1 to keep level offset from NMETHW. | All Water System ROC General | 2026-01-23
ROC | January | KSTP - Both Fluoride Pumps Not Available alarm came in. Called Jerry Z who informed he is on site and placed the pumps man/off due to the generator work. Jerry will let the ROC know when work is complete | All Water System ROC General | 2026-01-30
ROC | January | NMETIB - Heat Trace Controller 2 Fault Alarm came in last night. Alex B. is headed to site and requested a CMU5. CMU5 Created W11625127 #CMU5 | All Water System ROC General | 2026-01-30
ROC | January | NMTKKC- Header Free CL2 HiHi Alarm. Notified Alex B at NMW13 running well. Requested to contact Joe D. Joe D requested to place Hypo Pumps 3,4 and Ammonia pumps 1,2 in manual off until Alex B completed work. 14:55- Alex B finished with work. Placed hypo and ammonia pumps back into auto | All Water System ROC General | 2026-01-29
ROC | January | GWTP - Jack P. is headed to site | All Water System ROC General | 2026-01-30
ROC | January | AUW57 - Sean P. is on site and will be placing a motor in well 5 | All Water System ROC General | 2026-01-30
ROC | January | BVPS - Deactivated duty 1 | All Water System ROC General | 2026-01-30
ROC | January | ANW23 - Activated duty 1 as per Stephen B | All Water System ROC General | 2026-01-26
ROC | January | MTW12 /MTETNL - site to site communication fail between MTW12 and MTETNL. Checked site, MTW12 was running when the comm failure triggered which shut down the well. Placed well in manual/off to let it rest for 15 minutes for placing in auto and clearing alarms. 14:58 - MTW12 / MTETNL - Duty 1 is close to finished, if MTW12 activates it may not have enough time to clear the contact tank. Deactivated duty 1 instead and placed MTW12 in auto mode. | All Water System ROC General | 2026-01-23
ROC | January | BLW12- Site back on utility. Generator shutdown AURSBS- Activated D1 AUW14- Placed wells back in auto | All Water System ROC General | 2026-01-28
ROC | January | MAPS PD7, Placed pump 3 back to auto VNPS PD7, Placed pump 1 man/off | All Water System ROC General | 2026-01-31
ROC | January | Carter D Signing Out | All Water System ROC General | 2026-01-31
ROC | January | NBW2- Had complaint from contractor on about beeping panel on site saying communication error. Notified Jordan B. Jordan B thinks it may be due to Cl2 leak alarm earlier in the day and to disregard. No Issues with trends on alarms on site | All Water System ROC General | 2026-01-30
ROC | January | HLW2 - Jacob M running well 2 pump to waste. | All Water System ROC General | 2026-01-27
ROC | January | AUVCBS- Comm Fail. Interlocked Valve. Cleared alarm and valve remained open. | All Water System ROC General | 2026-01-28
ROC | January | VNPS - Tim H on site for station check, requested to activate BVPS. | All Water System ROC General | 2026-01-26
ROC | January | AURSOH- Activated D1 VNRSKS- Activated D1 | All Water System ROC General | 2026-01-18
ROC | January | YWS+NYWS normal | All Water System ROC General | 2026-01-24
ROC | January | YDSS+YNSS normal | All Water System ROC General | 2026-01-24
ROC | January | NMVCBA - Place back in auto YWS + NYWS Normal | All Water System ROC General | 2026-01-16
ROC | January | Adam Button signing in -18 C clear | All Water System ROC General | 2026-01-25
ROC | January | YWS+NYWS normal | All Water System ROC General | 2026-01-25
ROC | January | YWS+NYWS normal 12:20-NMETHW- Deactivated at 73% to offset from NMETIB as per shift report | All Water System ROC General | 2026-01-25
ROC | January | ARPS - Sam from Region of Peel called to inform that he is rotating from pump 7 to pump 8 | All Water System ROC General | 2026-01-26
ROC | January | VNPS PD7 - Tim H. called to inform that he is on site and has reset pump 4 due to issues with the pump yesterday. Tim informed he will run the pump for 5-10 mins to try to simulate the issues from yesterday | All Water System ROC General | 2026-01-22
ROC | January | NBW3- Influent free CL2 lolo alarm came in on well start up interlocking well. Recovered after 3 mins reset alarms. KSTP- Both pre-chlors not available alarm came in. Pre-chlor 2 running okay | All Water System ROC General | 2026-01-15
ROC | January | KSTP- Both pre cholrs off. Notified Ryan B. On site replacing regulator and testing for leaks will placed back in auto when done work | All Water System ROC General | 2026-01-15
ROC | January | Carter Dunn Signing In, -5D/Clear | All Water System ROC General | 2026-01-16
ROC | January | YWS + NYWS normal | All Water System ROC General | 2026-01-19
ROC | January | NBW5- Turbidity hi alarm came in. Disregard on shift report | All Water System ROC General | 2026-01-24
ROC | January | YWS+NYWS normal | All Water System ROC General | 2026-01-24
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-25
ROC | January | KSETWB - Dan Z on site and noticed the trendlines have flatlined recently. Dan Z contacted Eric S who will attend site. The header analyzer is still operating correctly. | All Water System ROC General | 2026-01-28
ROC | January | HLETYS, Stephen B leaving site. placed hypo pump 2 man/off for the night as per Stephens request | All Water System ROC General | 2026-01-15
ROC | January | GWTP- Sutton Header Free Chlorine Hi Alarm. Notified Jack P. He will look into it. | All Water System ROC General | 2026-01-27
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-31
ROC | January | QVW4 - Placed well man/on to help the filling of NMETHW | All Water System ROC General | 2026-01-17
ROC | January | MKRSEM - Reservoir 1 Level Lo alarm came in. Called Toronto Water (Paul) and requested two pumps on at reservoir 02:43 - Called Toronto Water (Paul) and requested to stop pumping to reservoir | All Water System ROC General | 2026-01-18
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-19
ROC | January | GRTPLL - Low lift P4 Hydraulic vlv uncommanded close alarm. Reset alarm as per shift report. | All Water System ROC General | 2026-01-20
ROC | January | NMVCBA- Adjusted from 40L/s to 80L/s NMVCIB- Adjusted from 80L/s to 40L/s | All Water System ROC General | 2026-01-21
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-16
ROC | January | ARPS - Peter from OCWA called back to inform that the technician is done filing reagents and the ammonia analyzers are back up and running. Alarms have cleared | All Water System ROC General | 2026-01-16
ROC | January | GWTP - Jack P. called to inform that he is on site and will be performing a backwash and GAC. Jack directed to disregard alarms until backwash is complete | All Water System ROC General | 2026-01-23
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-18
ROC | January | AUPSWS - Alex B on site to complete a generator test. Alex will be placing the pumps in manual mode. Alex B will also be placing the AUETFC system in pressure mode to complete the pump and valve inspection work orders. | All Water System ROC General | 2026-01-22
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-16
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-16
ROC | January | KCETDS- Activated D1 in preparation for MARs to JFRS | All Water System ROC General | 2026-01-17
ROC | January | QVW34- Treated total Cl2 hi alarm. Checked trends dosing looks normal. Trends recovered after 3 mins. Cleared alarm NMVCBA- Changed flow set point from 40L/s to 80L/s NMVCIB- Changed Flow set points from 80L/s to 40L/s | All Water System ROC General | 2026-01-17
ROC | January | Initiating MARS to JFRS as per procedure | All Water System ROC General | 2026-01-18
ROC | January | KSTP- Donald M, Joe D, and Jerry Z onsite working on pre chlorination lines. | All Water System ROC General | 2026-01-27
ROC | January | NMETIB- Deactivated duty | All Water System ROC General | 2026-01-27
ROC | January | YWS+NYWS normal GWTP- Train 1 TMP lo alarm came in but cleared upon acknowledgment. Similar issue came in for trains 2/4 earlier during plant run. Trends are okay dips only last seconds. | All Water System ROC General | 2026-01-27
ROC | January | MKRSEM, Contacted Toronto operator paul to start 2 pumps Carter D Signing Out | All Water System ROC General | 2026-01-16
ROC | January | TMC317 - Noticed higher flows from Toronto Water at about 30 MLD. Called Toronto Water (Paul) and requested that he throttle the pump as higher than normal flow. Paul informed he will switch to a smaller pump | All Water System ROC General | 2026-01-19
ROC | January | Ethan U signing in Weather -3 snow | All Water System ROC General | 2026-01-16
ROC | January | YWS+NYWS normal | All Water System ROC General | 2026-01-18
ROC | January | NMVCIB - Placed valve back to auto | All Water System ROC General | 2026-01-19
ROC | January | KSETWB- Ian W testing chlorine lockout alarms. Can disregard. | All Water System ROC General | 2026-01-27
ROC | January | Carter D signing out, Ethan U on site signing in | All Water System ROC General | 2026-01-15
ROC | January | NMW15- Ryan B heading to site to set up space heater. W11603441 CMU5 | All Water System ROC General | 2026-01-20
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-20
ROC | January | Angelica Chepiga signing in, weather -15C | All Water System ROC General | 2026-01-20
ROC | January | NMTKKC - Ammonia Pump 1 Failed to start alarm came in. Checked site. Pump 2 rotated to duty 1. Ack/reset and alarm cleared. Will monitor to see if this occurs again As this was a higher priority alarm, spoke to Donald M. who directed to wait until the duty rotates back to see if it will start up again #CONSULT | All Water System ROC General | 2026-01-17
ROC | January | QVW12 - Donald M. called to inform that the chlorine gas leak is unable to be pinpointed at this moment. Donald informed that the wells will remain interlocked until the gas leak can be found. Donald directed to rotate duties. Placed Well 4 into duty 1. | All Water System ROC General | 2026-01-23
ROC | January | AUETAD, Rick L is leaving site | All Water System ROC General | 2026-01-15
ROC | January | YWS + NYWS NORMAL | All Water System ROC General | 2026-01-29
ROC | January | AURSBS, Post Injection combined/total/free Cl2 hihi alarm, contacted Donald M, he is still working on site, directed to place AUVCBS in the man/closed position so no water is sent out from the res | All Water System ROC General | 2026-01-15
ROC | January | Ethan U signing in Weather -10. | All Water System ROC General | 2026-01-15
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-15
ROC | January | GWTP - Low lift Pump 1 Uncommanded stop alarm, alarm cleared. | All Water System ROC General | 2026-01-20
ROC | January | YWS+NYWs normal GWTP- ZW2 MIT failed alarm came in. Notified Phil D. Directed to place train offline #consult | All Water System ROC General | 2026-01-28
ROC | January | YWS + NYWS NORMAL | All Water System ROC General | 2026-01-21
ROC | January | VNRSKS - Deactivate duty 1 VNP7 - Place pumps man/off MAP7 - Place pumps back in auto | All Water System ROC General | 2026-01-19
ROC | January | NMETIB - Deactivated D1 to offset with NMETHW. NMVCBA - flow setpoint back to 40l/s NMVCIB- flow setpoint back to 80l/s | All Water System ROC General | 2026-01-30
ROC | January | VNETFD - Tim H. and Benson S. are on site testing the building Hi/lo temp, Tower level hi/low, Building flood alarm and eyewash alarm | All Water System ROC General | 2026-01-22
ROC | January | AUPSRR - Post-inj comb & free chlorine lolo, Spike in reading before coming back down within range. Able to clear right away | All Water System ROC General | 2026-01-19
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-23
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-23
ROC | January | BVPS - Deactivated duty 1 | All Water System ROC General | 2026-01-30
ROC | January | VNPS PD7 - Pumps 1&4 man/off MAPS PD7 - Pumps 1&3 to auto. | All Water System ROC General | 2026-01-30
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-24
ROC | January | Adam Button signing -24 C clear | All Water System ROC General | 2026-01-24
ROC | January | STETTL- Heatrace fault alarm came in emailed east water team about outstanding alarm and will monitor LITs NMETIB- Deactivated D1 at 65% to offset from NMETHW as per shift report MTW12- Gen tank 1 level hihi alarm. Disregard on shift report | All Water System ROC General | 2026-01-24
ROC | January | GWTP - ZW6 Shutdown and ZW6 Permeate Turbidity HiHi alarms came in. Called Joe M. who will take a look 12:53 - Patrick F. called to inform that he is also on site and will be taking a look at train 4. | All Water System ROC General | 2026-01-29
ROC | January | STW12, STW3 - man/on fir STETBR fill cycle | All Water System ROC General | 2026-01-30
ROC | January | YWS + NYWS NORMAL | All Water System ROC General | 2026-01-30
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-16
ROC | January | Carter D Signing Out | All Water System ROC General | 2026-01-26
ROC | January | GWTP - ZW2 Recovery - Exceeded recovery setpoint. Alarm changed to normal status shortly after triggering and reset upon acknowledgment. | All Water System ROC General | 2026-01-31
ROC | January | AUW14- Placed 1/4 back in auto | All Water System ROC General | 2026-01-24
ROC | January | AURSBS- Deactivated D1 | All Water System ROC General | 2026-01-24
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-29
ROC | January | ARPS - Martin from OCWA called to inform that he is rotating pumps. Testing with PCS, trying to run Pump 3 . | All Water System ROC General | 2026-01-27
ROC | January | ARPS -Martin from OCWA called to inform that he is rotating pumps from P6 to P7. | All Water System ROC General | 2026-01-27
ROC | January | QVW34- Influent free Cl2 hihi alarm came in. Checked trends. Looks like a drop in well flow causing excess Cl2 to be dosed. trend recovered after 3 mins alarms cleared. Will monitor effluent and treated Cl2 residuals during scheduled well runtime | All Water System ROC General | 2026-01-25
ROC | January | YWS+NYWS normal | All Water System ROC General | 2026-01-25
ROC | January | NMETHW, Activated D1, NMETIB has finished filling, making sure towers are offset | All Water System ROC General | 2026-01-25
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-25
ROC | January | STPSTL - Communication alarm to STETBR. Checked site, pumps interlocked. Able to reset alarms. Monitored pump start up. | All Water System ROC General | 2026-01-22
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-23
ROC | January | NMW15- Combined Cl2 lo alarm came in. Reset alarm after 6 mins as trends recovered. Treated total hi alarm came in once trends spiked back up and recovered after 3 mins. Cleared alarm | All Water System ROC General | 2026-01-27
ROC | January | Adeela Khan signing out | All Water System ROC General | 2026-01-23
ROC | January | AUW14- influent free Cl2 hi alarm came in on well start up. Trends recovered after 3 mins alarm cleared HLW1- Combined CL2 lo alarm. Well not active trends recovered after 3 mins alarm cleared | All Water System ROC General | 2026-01-25
ROC | January | YWS+NYWS normal | All Water System ROC General | 2026-01-25
ROC | January | NMETHW - Deactivated duty 1. | All Water System ROC General | 2026-01-19
ROC | January | YWS + NYWS Normal AURSBS, Activated D1, Preparing for MARS to JFRS AUW14, Placed wells 1/4 in manual/on to help slow down the drain for mars to Jefferson | All Water System ROC General | 2026-01-24
ROC | January | Christian Van Beek signing in. | All Water System ROC General | 2026-01-22
ROC | January | QVW12 - Noted the duty 1 well is manual off and there is a station turbidity interlock on site. Contacted Will M who stated he is on site with Jerry Z attempting to fix the station turbidity issues. Also informed Will M that Alex B has closed the Poppy Lane valve while they work through issues with the AUPSWS generator. | All Water System ROC General | 2026-01-22
ROC | January | YWS + NYWS NORMAL Angelica Chepiga signing out | All Water System ROC General | 2026-01-27
ROC | January | Connor Smith signing out | All Water System ROC General | 2026-01-27
ROC | January | NMETIB, Heat Trace Controller 2 Fault, Currently -22D out, contacted Ben H do to the extreme cold weather, asked to monitor it for the night, will look into it in the morning consult | All Water System ROC General | 2026-01-24
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-24
ROC | January | RHRSTR- Activated D1 at 71% | All Water System ROC General | 2026-01-24
ROC | January | AUSSSR - Lin 2 valve overtorque and line 2 valve fail to close alarms. Checked site, line 2 valve shows as travelling, likely stuck. Unable to clear the overtorque alarm. Contacted Barry M who will discuss with On call operator Daniel K. | All Water System ROC General | 2026-01-23
ROC | January | YWS + NYWS Normal Ethan Ullalkar signing out. | All Water System ROC General | 2026-01-19
ROC | January | Adam Button signing in | All Water System ROC General | 2026-01-30
ROC | January | ARPS - Martin from OCWA called to inform he will be rotating the pumps. Will be shutting down pump 2 and starting pump 5 | All Water System ROC General | 2026-01-30
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-26
ROC | January | NMVCBA- Placed valve in man/open at 40L/s | All Water System ROC General | 2026-01-27
ROC | January | AUVCBS - Multiple communication alarms came in. Checked site. Interlocked the valve which was open. Alarm cleared right away. Likely a blip. Will monitor | All Water System ROC General | 2026-01-30
ROC | January | NBW3- Influent Free Chlorine LoLo Alarm. Well interlocked on startup. Will restart after a few minutes if it recovers. 09:20- Cleared alarm and well started back up | All Water System ROC General | 2026-01-28
ROC | January | NMW12 - Influent free chlorine hihi alarm. Checked site, well recently activated. Trending shows a spike of the influent free chlorine reading which returned to normal range within two reading intervals. Reset the alarm. | All Water System ROC General | 2026-01-28
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-18
ROC | January | KCETFS- Ric L onsite for analyzer calibrations. | All Water System ROC General | 2026-01-27
ROC | January | MTW3 - Jackie S. is on site and will be placing the well man/off to work on the turbidimeter | All Water System ROC General | 2026-01-30
ROC | January | MARS- Reservoir lo alarm came in. Called Metro spoke with Peter to Increase flow to reservoir 13:50- MARS- Level still not recovering. 13:50- VNRSKS- Deactivated D1 13:50- MAPS- Placed P1-4 in manual/off 13:50- VNPS- Placed P1/4 in auto | All Water System ROC General | 2026-01-24
ROC | January | MARS- Still not recovering called Metro spoke to Peter and requested max flow | All Water System ROC General | 2026-01-24
ROC | January | YWS+NYWS normal MKRSEM- Reservoir lo alarm came in. Called Metro spoke with Paul to start 2 pumps | All Water System ROC General | 2026-01-27
ROC | January | YDSS+YNSS normal **WRONG BOOK** | All Water System ROC General | 2026-01-25
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-18
ROC | January | YWS + NYWS NORMAL | All Water System ROC General | 2026-01-19
ROC | January | NMETIB, Activated D1 to have towers offset | All Water System ROC General | 2026-01-31
ROC | January | NMETHW - Deactivated duty 1. | All Water System ROC General | 2026-01-20
ROC | January | MARS - Hi levels. Activated duty 1 at AURSBS | All Water System ROC General | 2026-01-19
ROC | January | YWS + NYWS NORMAL | All Water System ROC General | 2026-01-19
ROC | January | YWS + NYWS NORMAL | All Water System ROC General | 2026-01-20
ROC | January | NMETIB - Deactivated duty 1. | All Water System ROC General | 2026-01-30
ROC | January | QVW34 - Well Pumps and booster pumps not available alarms came in. Called Will M. who informed he will be wasting for about an hour to take a sample. | All Water System ROC General | 2026-01-29
ROC | January | KSTP - Jerry Z exercising Pressure relive valve. | All Water System ROC General | 2026-01-27
ROC | January | VNPS PD8 - Activated D2 VNPS PD7 - Pumps 1 & 4 to auto MAPS - Pumps 1&3 man/off | All Water System ROC General | 2026-01-27
ROC | January | VNRSKS - Swapped supply pumps to two MAPS pumps. | All Water System ROC General | 2026-01-31
ROC | January | ARPS - Peel/OCWA (Martin) called to inform that they are activating one ARPS pump. Martin informed that Peel/OCWA will be completing pump rotations every morning around 08:00. | All Water System ROC General | 2026-01-28
ROC | January | KSTP - Raw water turbidity fault alarm. Disregard as per the shift report. | All Water System ROC General | 2026-01-31
ROC | January | ANW23 - Stephen B. is headed to site to clean the chlorine analyzers | All Water System ROC General | 2026-01-22
ROC | January | AUPSWS - Dan B. called to inform that he is finished working on site and the generator is back to normal operations. Dan B. informed that the pumps and ANVCPL can go back to auto. Called Ryan B. to confirm. Placed pump 3 and 5 back to auto and placed ANVC back to auto | All Water System ROC General | 2026-01-23
ROC | January | NBW5 - Turbidity hi alarm. Checked site, well is active. Trending shows a spike of the turbidity reading. Rotated silicate pump. Monitor site. | All Water System ROC General | 2026-01-31
ROC | January | ANMCBL - Security Intrusion and PAC Control Panel door open alarms came in. Matt H. is on site with Dwayne L. | All Water System ROC General | 2026-01-30
ROC | January | YWS + NYWS Normal Adeela Khan signing out | All Water System ROC General | 2026-01-16
ROC | January | MARS - Noted that Toronto is pushing more flow than normal. Called Toronto Water (Mehdi) and requested they drop one pump. MKRSEM - Called Toronto Water (Mehdi) and requested they activate two pumps to push flow to MKRSEM. | All Water System ROC General | 2026-01-31
ROC | January | GWTP - ZW4 membrane air valve failed, membrane set B air valve fail to close alarm and ZW shutdown alarm. Checked site. The air valve is showing as closed on SCADA and the filter is filling. Contact Jack P to inform. Jack directed to clear alarms and place the filter back in service. Made the necessary changes. #consult | All Water System ROC General | 2026-01-31
ROC | January | NMW15 - Rick L and Eric S on site for annual calibrations VNRSKS - Swapped supply pumps to one MAPS and one VNPS pump. | All Water System ROC General | 2026-01-19
ROC | January | VNRSKS- Eye wash alarm came in. Called Tim H. on site testing eyewash | All Water System ROC General | 2026-01-15
ROC | January | YWS + NYWS normal | All Water System ROC General | 2026-01-17
ROC | January | STW12- Placed wells back into auto STW3- Placed well back into auto | All Water System ROC General | 2026-01-27
ROC | January | ARPS, Airport Rd Total Ammonia lo/lolo alarm, contacted OCWA operator Peter about the alarms, they are changing the reagents in the analyzers, should be back up and running in 15 minutes | All Water System ROC General | 2026-01-16
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-17
ROC | January | AUW14- Joe D called and req silicate dosing setpoint to be changed from 15 to 16mg/L | All Water System ROC General | 2026-01-21
ROC | January | HLETYS- Post injection Combined Cl2 hi alarm. Cleared upon acknowledgment 19:39- HLETYS- Post injection Combined Cl2 hi alarm came in again. Deactivated D1 as per Jordan B | All Water System ROC General | 2026-01-17
ROC | January | AUPSWS - Lee F performing vibration test, requested to reassign P5 to Duty 1, Pump 4 to Duty 2. P5 started in D1 and switched to D2 immediately, no alarms. P4 restarted in D1. Lee F. requested to reassign P5 to Duty 1 one more time, he will contact OP if it fails. | All Water System ROC General | 2026-01-26
ROC | January | MAPS PD8 - Placed P4 man/off , VNPS PD8 - P4 to Duty 1/auto. | All Water System ROC General | 2026-01-26
ROC | January | Angelica Chepiga signing in | All Water System ROC General | 2026-01-27
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-17
ROC | January | ROYKS to ROPKS Communication alarm came in. Checked site and trending is okay. Alarm cleared | All Water System ROC General | 2026-01-17
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-18
ROC | January | RHRSTR, Activated D1 MARS, Cell1 (North) lvl lo alarm, notified Toronto operator to increase the flow alittle, Peter will put on another small pump, will continue to monitor till its at a higher level | All Water System ROC General | 2026-01-18
ROC | January | YWS + NYWS NORMAL | All Water System ROC General | 2026-01-20
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-17
ROC | January | Adam Button signing in -4 Clear | All Water System ROC General | 2026-01-17
ROC | January | STRS48- High lift P1 failed to stop alarm. Hi lift P1 stopped. Reset alarm | All Water System ROC General | 2026-01-17
ROC | January | KSTP, Cl2 Gas Detector Alarm, contacted Jerry Z, him and Ryan B are good, testing the leak alarms | All Water System ROC General | 2026-01-16
ROC | January | STPSMR- Travis W on site to work on Cl2 analyzers rotating pump inspections. AUETAD-Rick working on tower LIT. Placed pumps 1/2 at AUPSRR in man/off HLETYS- Stephen B on site to work on Cl2 analyzers and testing low temp alarm. Will be running diesel generator at HLPSYS as well | All Water System ROC General | 2026-01-15
ROC | January | AUPSRR/VNRSKS - Kingsley M restating OIT, disregard heartbeat alarm | All Water System ROC General | 2026-01-19
ROC | January | SHETCS - Tower Level Lo alarm came in. Checked site. Hi lifts are not running and tower is draining. Called Jacob M. who informed he is completing a deep cycle of the tower down to 5% | All Water System ROC General | 2026-01-16
ROC | January | GWTP - Sutton and Keswick header fluoride hi alarms. Checked site, plant is active to fill the system. Fluoride levels are dropping to normal range. Alarms cleared themselves. | All Water System ROC General | 2026-01-19
ROC | January | STETBR - Joe M on site to complete work orders including low temperature alarm test, chlorine analyzer maintenance and JHSC checks. | All Water System ROC General | 2026-01-20
ROC | January | AUPSWS - Kyle R and Dan B on site to complete maintenance on the generator ATS. | All Water System ROC General | 2026-01-23
ROC | January | QVW34- Total Cl2 hi alarm came in. Placed well back in auto. Combined Cl2 hi alarm came in. Trends recovered after 3 mins alarms cleared combined CL2 hi alarm will monitor total hi | All Water System ROC General | 2026-01-17
ROC | January | KSTP- Fin water Fluoride res hi alarm came in. Looks like spike on start up. Notified Dan Z. Directed to monitor and clear alarm within 10 mins GWTP- ZW8 memb tank lolo switch alarm came in. Cleared upon acknowledgment #consult | All Water System ROC General | 2026-01-17
ROC | January | GRTPLL - Low lift P3 Hydraulic vlv uncommanded close alarm. Reset alarm as per shift report. | All Water System ROC General | 2026-01-20
ROC | January | STRS48- Joe M cleaning chlorine analyzers and performing health and safety check. | All Water System ROC General | 2026-01-26
ROC | January | AUMCBS- Yash S onsite for switch replacement. Will lose comms for 15-20 mins. | All Water System ROC General | 2026-01-27
ROC | January | VNETAG - Benson S on site to complete work orders including high/low temperature alarm test and valve exercising GWTP - Jackie S on site to complete a generator test. | All Water System ROC General | 2026-01-20
ROC | January | VNPS - Tim H with Lee F onsite putting PD8 pumps back in normal operation. Requested to run VNP7 as well, placed MAP8 pumps man/off and VNP7 pump 2 & 3 auto BVPS - Activate duty 1 at request of Tim H | All Water System ROC General | 2026-01-19
ROC | January | STW12 + STW3 - Place wells back in auto | All Water System ROC General | 2026-01-16
ROC | January | NMW15 - Erick finished at site. Place well back in auto | All Water System ROC General | 2026-01-19
ROC | January | AUVCBS - PAC Communication Failure Alarm came in. Called Kyle C. who will investigate 10:00 - Kyle C. cleared alarm and trending is okay | All Water System ROC General | 2026-01-29
ROC | January | HLW2 - Tim H. directed to change the chlorine residual setpoint from 3.40 mg/L to 3.30 mg/L | All Water System ROC General | 2026-01-29
ROC | January | KLMCIA - Meter chamber flood & Intrusion alarm. Informed Gary P confirming no one at site. Will pump down site tomorrow as known issue with site and hi level caused trigger. Disregard for the night QVW34 - Yash S rebooting OIT, disregard heartbeat alarm. Wells man/off | All Water System ROC General | 2026-01-19
ROC | January | GRTPLL - Low Lift Surge Relief Valve Open Alarm came at plant shut down and cleared right away. | All Water System ROC General | 2026-01-21
ROC | January | VNRSKS - Swapped supply pumps to one MAPS and one VNPS pumps. | All Water System ROC General | 2026-01-28
ROC | January | YWS + NYWS NORMAL | All Water System ROC General | 2026-01-20
ROC | January | NMVCBA - back to auto, flow setpoint from 50 to 80l/s. NMVCIB - flow setpoint from 80 to 40l/s. | All Water System ROC General | 2026-01-20
ROC | January | STW12, STW3 - man/on for STETBR fill cycle. | All Water System ROC General | 2026-01-20
ROC | January | YWS + NYWS NORMAL | All Water System ROC General | 2026-01-21
ROC | January | NMETIB- John D working on OIT. Disregard Heartbeat alarm. | All Water System ROC General | 2026-01-28
ROC | January | KSTP - Arthur L leaving site. | All Water System ROC General | 2026-01-28
ROC | January | NMVCBA- placed back in auto | All Water System ROC General | 2026-01-28
ROC | January | MKRSEM- Called Metro spoke with Paul to stop pumping to reservoir | All Water System ROC General | 2026-01-28
ROC | January | VNETFD - Rick L on site to complete annual calibrations. | All Water System ROC General | 2026-01-28
ROC | January | AURSBS - Deactivated D1 to help with MARS level. | All Water System ROC General | 2026-01-29
ROC | January | QVW12 - Chlorine Room Gas Level HiHi alarm came in. Checked site. Will M. and Donald M. are on site completing a cylinder change and a bit of gas was released. Will informed that these alarms can be disregarded for the time being | All Water System ROC General | 2026-01-23
ROC | January | YWS + NYWS Normal Christian Van Beek signing out. | All Water System ROC General | 2026-01-23
ROC | January | MKRSEM - Called Toronto water (Brett) and requested start filling Res with 2 pumps. | All Water System ROC General | 2026-01-28
ROC | January | YWS + NYWS NORMAL | All Water System ROC General | 2026-01-29
ROC | January | Connor Smith signing in | All Water System ROC General | 2026-01-20
ROC | January | Adam Button signing in QVW34- Well 3 waste valve open alarm came in with well running. Did not clear contact tank. Placed well 3 in man/off. Notified Will M will head to site. Created CMU5 W11606521 #CMU5 | All Water System ROC General | 2026-01-21
ROC | January | NBW5- Turbidity hi alarm came in. Disregard on shift report MKRSEM- Reservoir level hi alarm called metro and spoke with Peter to stop pumping to reservoir | All Water System ROC General | 2026-01-25
ROC | January | MAPS PD7- Placed P1 in manual VNPS PD7- Placed P1 in auto | All Water System ROC General | 2026-01-25
ROC | January | STETBR- Tower level lo alarm STETTL- Activated D1 at 64% STW12/3- Placed P1,2 and 3 in man/on as per interim | All Water System ROC General | 2026-01-25
ROC | January | Carter Dunn Signing In, -14D/Clear | All Water System ROC General | 2026-01-23
ROC | January | Adeela Khan signing in | All Water System ROC General | 2026-01-30
ROC | January | YWS + NYWS Normal BLETNL, Activated D1 | All Water System ROC General | 2026-01-31
ROC | January | STW12- Placed well 1 back into auto STW3- Placed well 3 back into auto | All Water System ROC General | 2026-01-29
ROC | January | QVW12- Influent free Cl2 hi alarm came in on well start up | All Water System ROC General | 2026-01-30
ROC | January | AUETFC, Inlet Line Standby Heat Trace Alarm, notified Jerry Z, directed to disregard, if tower stops trending properly he would like a call. At this time i also notified Jerry that the water temp at NMTKBS is getting very low, directed to disregard. If temperature gets to around 0.5D then he would want a call consult | All Water System ROC General | 2026-01-31
ROC | January | YWS+NYWS normal STETBR- Tower level lo alarm came in STW12/3- Placed P1/3 in man/on as interim | All Water System ROC General | 2026-01-27
ROC | January | GWTP, Low llift discharge total cl2 residual fault, as per shift report, directed to disregard | All Water System ROC General | 2026-01-31
ROC | January | YWS + NYWS Normal MAPS PD7, Placed pumps 1/3 man/off VNPS PD7, Placed pumps 1/4 in auto | All Water System ROC General | 2026-01-31
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-26
ROC | January | MARS- Level lo alarm came in. BVPS starting up in D1 and PD8 D1 deactivating will monitor | All Water System ROC General | 2026-01-25
ROC | January | YWS+NYWS normal | All Water System ROC General | 2026-01-25
ROC | January | Carter D Signing In, -13D/Snowing | All Water System ROC General | 2026-01-25
ROC | January | AUW14, Placed wells 1/4 man/off to draw more water from AURSBS | All Water System ROC General | 2026-01-26
ROC | January | MKRSEM, notified Toronto operator Zoran to stop pumping to the res | All Water System ROC General | 2026-01-26
ROC | January | MKRSEM - Requested Toronto water (Puria) to stop pumps. | All Water System ROC General | 2026-01-20
ROC | January | GWTP- Truck Bay Gas Leak Alarm. Notified Jack P. Can disregard alarm. | All Water System ROC General | 2026-01-20
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-22
ROC | January | MTW3 - Phil D. is on site cleaning the turbidimeters | All Water System ROC General | 2026-01-23
ROC | January | NMW136- Treated total and combined Cl2 lo alarm came in. Wells are not active no water directed to users. Will clear when residuals recover | All Water System ROC General | 2026-01-25
ROC | January | STRS48 - High Lift Pump 1 Failed to stop alarm came in. Checked site. Alarm cleared but came back in. Spoke to Lee F. who informed that pump 1 would not shut down even in manual. Lee placed the pump in local and placed pump 2 man/off. Both pumps shut down. Rotated duties so that pump 1 is in duty 1 and pump 2 in duty 2. Rotated back to check if pump 1 would shut down. Pump 2 started before pump 1 fully shut down. Spoke to Joe M. who will continue to monitor situation and may conduct testing soon. | All Water System ROC General | 2026-01-22
ROC | January | GWTP - ZW7 CIP Feed inlet Valve failed to open. Notified Jack P, requested to clear alarm. | All Water System ROC General | 2026-01-27
ROC | January | Connor Smith signing out | All Water System ROC General | 2026-01-20
ROC | January | SHTP - Well 2 pump uncomm start alarm. Was able to clear alarm. Well 2 pump restarted ok. | All Water System ROC General | 2026-01-20
ROC | January | AUPSWS - Alex B and Christian B running generator. Will run pumps 1,2,3 in manual mode after to check motors. | All Water System ROC General | 2026-01-27
ROC | January | NMTKKC - Sanitary Pump Failed To stop alarm came in. Called Jerry Z. who directed to call Donald M. Called Donald M. who is still on site and will take a look #CONSULT | All Water System ROC General | 2026-01-30
ROC | January | YWS + NYWS Normal Adeela Khan signing out | All Water System ROC General | 2026-01-30
ROC | January | RHRSTR - Activated duty 1. | All Water System ROC General | 2026-01-28
ROC | January | YWS+NYWS normal | All Water System ROC General | 2026-01-28
ROC | January | NMW136 - Alex B. is on site and will be placing the wells in local and will be isolating the contact tank. Alex also informed she will be working on the silicate system | All Water System ROC General | 2026-01-29
ROC | January | Christian Van Beek signing in. | All Water System ROC General | 2026-01-28
ROC | January | YWS + NYWS Normal Christian Van Beek signing out. | All Water System ROC General | 2026-01-28
ROC | January | HLW2 - Combined Chlorine HiHi alarm came in. After checking trends, noticed that the well was still active when the combined hihi alarm came in. Spoke to Tim H. who informed that this is okay to disregard. The well is no longer running. | All Water System ROC General | 2026-01-29
ROC | January | NMVCBA - Placed valve back to auto | All Water System ROC General | 2026-01-20
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-26
ROC | January | TMC317, Noticed Toronto was pumping higher flows than normal for most of the day, contacted Medhi from Toronto to drop the flow back to a low flow condition. MARS has been hovering around the 60-70% range which has been optimal for the day | All Water System ROC General | 2026-01-31
ROC | January | BLW3, Placed well back to auto | All Water System ROC General | 2026-01-31
ROC | January | Christian Van Beek signing in. Weather: -17C and clear. | All Water System ROC General | 2026-01-31
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-30
ROC | January | Carter D Signing Out | All Water System ROC General | 2026-01-29
ROC | January | NMETIB - Activated duty 1 to keep level offset from NMETHW. | All Water System ROC General | 2026-01-22
ROC | January | NMW15 - Combine chlorine Low alarm, value recovered in two readings. Alarm cleared. | All Water System ROC General | 2026-01-26
ROC | January | VNPS- Tim H on site to work on rechlor. Req RHRSTR D1 to be activated. RHRSTR- Activated D1 MAPS PD7 - Placed all pumps in man/off VNPS PD7- Placed P1/4 in auto | All Water System ROC General | 2026-01-30
ROC | January | HLETYS - Stephen B has adjusted the duty start setpoint to deep cycle the tower. | All Water System ROC General | 2026-01-23
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-24
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-25
ROC | January | BLW12- Generator running alarm came in. Site on hydro. Generator shutdown after a few mins cleared alarm | All Water System ROC General | 2026-01-27
ROC | January | MKRSEM, Notified Toronto operator Peter to stop pumping to the res | All Water System ROC General | 2026-01-18
ROC | January | MAPS PD7, Placed pumps 1/3 man/off VNPS PD7, Placed pumps 2/3 in auto 16:40, reverted back to normal operation | All Water System ROC General | 2026-01-18
ROC | January | ARPS - Martin from OCWA called, switching P7 to P2. | All Water System ROC General | 2026-01-27
ROC | January | STW12 - Influent Free chlorine residual low/low at duty stop. Value recovered, cleared alarm. | All Water System ROC General | 2026-01-27
ROC | January | NMETDD/NMETHW- Comm alarm to QVW34. Comms returned in 2 mins cleared alarms wells were not active at this time | All Water System ROC General | 2026-01-27
ROC | January | AUPSWS - Alex B. called to inform that ANVCPL is back open in auto, Tyler Z is offsite and that there is currently 1 pump in auto. Alex informed that the motor on the ATS is not operational and if there is a power outage, immediate call out to the on call electrician. Alex also informed that she will be testing the temperature alar, and will be completing valve exercising | All Water System ROC General | 2026-01-22
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-23
ROC | January | NMVCIB, Placed valve in manual and set flow to 40L/sec | All Water System ROC General | 2026-01-18
ROC | January | STETBR - Tower Level Lo alarm came in. Placed STW12 and STW3 into manual as per interim | All Water System ROC General | 2026-01-18
ROC | January | AUPSOH- Discharge flow lolo alarm came in. Flow within range alarm cleared upon acknowledgment VNRSKS- Deactivated D1 VNPS PD7 - Placed P1/4 in man/off MAPS PD7- Placed P1/3 in auto | All Water System ROC General | 2026-01-27
ROC | January | HLETYS- Sean P onsite disconnecting power to mixer. Will not impact operations. 10:55- Finished onsite | All Water System ROC General | 2026-01-28
ROC | January | AUETAD- Rick L done work on LIT. Placed P1/2 at AUPSRR in auto | All Water System ROC General | 2026-01-15
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-18
ROC | January | Adam Button signing in -15 Clear | All Water System ROC General | 2026-01-27
ROC | January | GWTP- Sutton header free Cl2 hi alarm outstanding with D1 active. Called Phil D. Directed to disregard #consult | All Water System ROC General | 2026-01-27
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-19
ROC | January | MARS- Cell1 (North) Lvl HiHi Alarm. VNRSKS- Activated duty | All Water System ROC General | 2026-01-22
ROC | January | STRS48 - Joe W. is on site and will be running the generator, placed the hi lifts man/off and will be cleaning the chlorine analyzers | All Water System ROC General | 2026-01-22
ROC | January | VNMCYS - Yash S. is on site for radio upgrades | All Water System ROC General | 2026-01-21
ROC | January | NRETBR - Lee F finished on site. Lee is reverting valves to normal operations. | All Water System ROC General | 2026-01-20
ROC | January | MKRSEM - Request TO (Peter) to drop both pumps | All Water System ROC General | 2026-01-16
ROC | January | MKRSMR - Toronto Water (Andrew) called to inform that they may have an energy curtailment later today. Andrew would like to start pumping to the reservoir earlier if the energy curtailment is confirmed. Andrew will give the ROC a call back when he needs to start pumping earlier | All Water System ROC General | 2026-01-29
ROC | January | STW12- Placed wells man/on STW3- Placed well man/on | All Water System ROC General | 2026-01-22
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-15
ROC | January | NMVCBA- Placed in man/open at 40L/s | All Water System ROC General | 2026-01-19
ROC | January | NMVCIB - flow setpoint from 80 to 40l/s NMVCBA - flow setpoint from 40 to 80l/s. | All Water System ROC General | 2026-01-20
ROC | January | STPSTL- Drew from Ferguson requested to clear Diesel Tank 1 Low Vacuum Alarm. Requested a call if it comes back in. | All Water System ROC General | 2026-01-20
ROC | January | NRETBR- Flow Control Vlv Position Deviation Alarm. Outstanding from earlier maintenance work performed. Ryan B requested a CMU5 W11603378 CMU5 | All Water System ROC General | 2026-01-20
ROC | January | YWS + NYWS Normal Christian Van Beek signing out. | All Water System ROC General | 2026-01-20
ROC | January | RHPSWA - Tim informed that he will be running pump 3. Tim also informed that he has placed all VNPS PD8 pumps man/off 14:01 - Tim informed that he is done testing pump 3 at RHPSWA and VNPS PD8 is back to normal operations | All Water System ROC General | 2026-01-22
ROC | January | AUPSWS - Donald M. is on site and working on pump 4. Will be checking the check valve | All Water System ROC General | 2026-01-16
ROC | January | MARS- Reservoir Valve House Flood Alarm. Called Tim H. No answer. Will try again. 08:53- Tim H called back. Contractors triggered alarm. Can disregard. | All Water System ROC General | 2026-01-28
ROC | January | BLW12 - Joe W on site to complete a generator test run. | All Water System ROC General | 2026-01-20
ROC | January | GWTP - Backpulse tank fill valve failed to open alarm. Checked site, SCADA showed the backpulse tank 1 fill valve travelling and then close in auto mode. Trending shows that the tank level did increase before the alarm came in, indicating the valve was open and allowing flow. Able to reset alarm, will call out if it returns. 16:43 - GWTP - Noticed the backpulse tank levels were increasing despite the valve showing as closed. Called Dan Z who directed to manually exercise the valve. The valve opened and closed and then triggered a fail to close alarm and hihi tank level alarms. Dan Z directed to monitor the tank level and call out if the tank level does not drop within one hour. 16:57 - GWTP - Monitored site during a filter backwash, saw the backpulse pumps activate, drawdown the backpulse tanks and the watched the backpulse level increase while the backpulse tank inlet valves remained closed and interlocked. Called Dan Z who will check SCADA. 17:09 - GWTP - Dan Z attending site. Created CMU5#W11603466 #consult #CMU5 | All Water System ROC General | 2026-01-20
ROC | January | NRETBR - Lee F on site to complete work on the valve systems. Lee has stated he needs to close the altitude valve on site. Contacted West and Central operations to inform. Deactivated duty, will attempt to float system on the NRETCR tower. If issues arise with supply, will inform area ops and make necessary adjustments. | All Water System ROC General | 2026-01-20
ROC | January | KSTP - Eric S. is on site working on the Raw Water pH 10:19 - Eric is finished on site | All Water System ROC General | 2026-01-21
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-31
ROC | January | KSTP- Settl Water Turbidity HiHi Alarm. Analyzer shows quick spike up and then down. Plant has been off for the night. Will notify Ops. | All Water System ROC General | 2026-01-28
ROC | January | STW12 well 1 pump, STW3 - Placed man/on for STETBR fill cycle. | All Water System ROC General | 2026-01-28
ROC | January | AUETAD - Ricardo L. and Eric S. are on site to work on the Total Chlorine Analyzer | All Water System ROC General | 2026-01-16
ROC | January | STPSMR - Travis W & Joe M onsite cylinder cahnge, shutting down pumps an purging lines as well | All Water System ROC General | 2026-01-19
ROC | January | NMETIB- Heat trace controller 2 fault alarm came in . Notified Alex B. Heat trace system working at 100% and is struggling to keep up with cold temperatures. Directed to disregard for now and ALex B will notify OCO of outstanding issue | All Water System ROC General | 2026-01-30
ROC | January | MKMCSA - Yash S. called to inform he is on site replacing a radio. May lose communication 12:30 - Yash is finished on site | All Water System ROC General | 2026-01-21
ROC | January | NMW15 - Donald M on site to complete maintenance on silicate pump 1. | All Water System ROC General | 2026-01-22
ROC | January | MKRSEM - Called Toronto water(Brett) and requested to start filling Res with 2 pumps. | All Water System ROC General | 2026-01-29
ROC | January | MAPS PD7 - Pump 1 man/off VNPS PD7 - Pump 1 to duty 1. | All Water System ROC General | 2026-01-29
ROC | January | HLW2 - Combine chlorine Hi alarm. Dave T will check SCADA # Consult NBW2 - Chlorine Gas Leak Hi alarm, Scrubber not running, reading 0,6 ppm. David T will check SCADA and attend site. # CMU5 W11623098 | All Water System ROC General | 2026-01-29
ROC | January | VNPS PD7- Placed P1 in man/off MAPS PD7- Placed P1 in auto | All Water System ROC General | 2026-01-24
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-25
ROC | January | MKRSEM- Called Toronto (Brett) and requested to place pumps off | All Water System ROC General | 2026-01-23
ROC | January | YWS + NYWS Normal Connor Smith signing out | All Water System ROC General | 2026-01-23
ROC | January | AUPSOH- Joe D onsite for generator run. 11:09- Joe D leaving. Site back to normal | All Water System ROC General | 2026-01-20
ROC | January | MKETFA- Pouria from Toronto called. They will switch pump 3 over to pump 2 for testing. | All Water System ROC General | 2026-01-20
ROC | January | NMW136 - Combine chlorine low alarm, quick drop. Value recovered. Alarm cleared. | All Water System ROC General | 2026-01-29
ROC | January | NMVCIB, Placed valve manual and set flow to 40L/sec | All Water System ROC General | 2026-01-24
ROC | January | STRS48 - Lee F has completed his repairs on the pump 2 system and requested the duty 1 be assigned to pump 2 so he can test the repair. Made the change. | All Water System ROC General | 2026-01-22
ROC | January | KSETDP - Post Injection Free Chlorine LoLo switch alarm came in. Checked site. Site is offline and water is not being directed to users | All Water System ROC General | 2026-01-21
ROC | January | HLW1 - Treated Free Chlorine Hi alarm came in. Monitored site. Called Stephen B. who directed to wait 5 mins 14:18 - Treated Free Level came back to optimal range and alarm has been cleared | All Water System ROC General | 2026-01-26
ROC | January | NMETHW - Riser Pipe Heat Trace Controller 1 Fault alarm came in. Checked site. Controller 1 has faulted but controller 2 is on and normal. Informed William M. who is heading to site. CMU5 Created W11615954 #CMU5 | All Water System ROC General | 2026-01-26
ROC | January | MKRSEM- Called Metro spoke to Paul to start 2 pumps to fill reservoir | All Water System ROC General | 2026-01-26
ROC | January | AURSBS- Activated D1 | All Water System ROC General | 2026-01-30
ROC | January | JFPS - Tim H running generator. | All Water System ROC General | 2026-01-27
ROC | January | GWTP- Sutton Header Free Chlorine Hi Alarm. Disregard as per SCADA Report. | All Water System ROC General | 2026-01-28
ROC | January | BLW3, Influent Free Cl2 Res lolo, Jack P is heading to site CMU5: W11625836 | All Water System ROC General | 2026-01-31
ROC | January | Adam Button signing out | All Water System ROC General | 2026-01-30
ROC | January | NMW12 - Silicate pumps not available alarm. Joe W called to inform he is on site and topped up the silicate level. The level sensor in the silicate tank is not reading correctly and it interlocked the silicate pumps. Joe W contacting on call PCS operator to remove the interlock. | All Water System ROC General | 2026-01-28
ROC | January | GWTP LL - Pre-chlorination booster pump 1 overload alarm. Jack P called to inform that a contractor, Lexsan, is working on the low lift pump system today. Jack stated that low lift alarms can be disregarded. Jack is working at the GWTP today. | All Water System ROC General | 2026-01-28
ROC | January | HLW2- Downstream pressure hihi came in. Stephen B. Cole W on site at HLETYS adjusting flow to tower. Cole W will make adjustments and clear alarms | All Water System ROC General | 2026-01-30
ROC | January | NMVCBA- Placed valve in manual 50L/s | All Water System ROC General | 2026-01-20
ROC | January | VNRSKS - Swapped supply pumps to one MAPs one VNPS pump. | All Water System ROC General | 2026-01-23
ROC | January | GWTP - Sulfur Dioxide Room gas level hihi and chemical room gas level fault alarms came in. Jack P. informed he is testing the alarm | All Water System ROC General | 2026-01-23
ROC | January | NBW2 - Pressure Relief Valve Open Alarm came in. Called Dave T. who will take a look | All Water System ROC General | 2026-01-29
ROC | January | Adeela Khan signing out | All Water System ROC General | 2026-01-26
ROC | January | QVW12- Influent free Cl2 lo alarm came in on well start up. Recovered after 3 minas cleared alarm | All Water System ROC General | 2026-01-26
ROC | January | NBET27- Outlet temp lolo alarm came in. Due to low outdoor temperatures. Should recover when duty activates instruments on outlet analyzer seem to be working okay. | All Water System ROC General | 2026-01-26
ROC | January | AURSBS - Chlorine GCLR 1 Vlv Fail to Open Alarm at duty stop. Alarm cleared. | All Water System ROC General | 2026-01-29
ROC | January | KLET27- Activated D1 at 72% | All Water System ROC General | 2026-01-27
ROC | January | KCETDS - Chlorine Room Low Temperature alarm came in. No chlorine on site. Dave T. is on site and informed that this alarm comes from a storage room and can be disregarded | All Water System ROC General | 2026-01-30
ROC | January | KSTP - Jerry Z. called to inform that he is finished on site and the diesel test run is complete. Site is back to normal operations | All Water System ROC General | 2026-01-30
ROC | January | MAPS PD8 - Deactivated D1 to help MARS level recover. | All Water System ROC General | 2026-01-28
ROC | January | SHTP- Well 2 uncomm start alarm. Reset alarm well not being called for | All Water System ROC General | 2026-01-26
ROC | January | AURSOH, Activated D1 AUW14, Placed wells 1/4 man/off | All Water System ROC General | 2026-01-18
ROC | January | NMVCBA - Placed valve in man at 30% | All Water System ROC General | 2026-01-29
ROC | January | Connor Smith signing in -20C Clear | All Water System ROC General | 2026-01-30
ROC | January | NBW2 - Chlorine Gas Leak Hi alarm came in. Called Jordan B. who informed that he has just found the leak that occurred last night and that triggered the alarm 11:27 - Chlorine Gas Leak alarm came in. Cole W. called to inform that he is on site and triggered this alarm. Will clear the alarm. | All Water System ROC General | 2026-01-30
ROC | January | NMETHW, While reviewing trends, noticed that the towers trend started to escalate up quickly, Duty then deactivated and the tower still continued to rise, an issue must have occurred with the LIT, notified Ben H, he is heading to site. Ben H also directed to change the controlling tower to QVETQS CMU5: W11611819 // W11611826 | All Water System ROC General | 2026-01-23
ROC | January | STETBR - Tower level hi alarm. Placed STW12 and STW3 in auto mode. | All Water System ROC General | 2026-01-19
ROC | January | NMVCBA- Placed valve in man/open at 40L/s. | All Water System ROC General | 2026-01-28
ROC | January | GWTP - Sutton Header Fluoride Hi alarm came in. Checked site. SUETDR recently deactivated. Will monitor 05:17 - Sent an email to the east team | All Water System ROC General | 2026-01-19
ROC | January | KSTP - Raw water pH HiHi alarm. Checked site, pH reading is very high and outside of actual pH range limits. Contacted Jerry Z who will check the analyzer. | All Water System ROC General | 2026-01-19
ROC | January | KSTP- Noticed High Lift Pump 4 running in manual. Called Jerry Z. He is finished onsite. Placed high lift back in auto. | All Water System ROC General | 2026-01-20
ROC | January | VNPS- Noticed only duty 1 was active. Activated duty 2. | All Water System ROC General | 2026-01-27
ROC | January | KSETWB - Talha H rebooting OIT, disregard Historian Heartbeat alarm. | All Water System ROC General | 2026-01-27
ROC | January | SHTP, Reservoir Total Cl2 Fault, David T is heading to site CMU5: W11625844 | All Water System ROC General | 2026-01-31
ROC | January | HLW2, Kyle R on site, working on the wells, need the system man/off till he can make the fixes that are needed 11:45, Kyle R is finished on site | All Water System ROC General | 2026-01-29
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-23
ROC | January | VNRSKS - Deactivated D1 @ 81% to help with MARS level. | All Water System ROC General | 2026-01-29
ROC | January | HLW1- Stephen B onsite with Lee F for valve work. Disregard pressure alarms. | All Water System ROC General | 2026-01-27
ROC | January | STETTL- Eric S finished onsite. | All Water System ROC General | 2026-01-30
ROC | January | NMVCIB - Reverted valve setpoint change from 40L/s to 80L/s NMVCBA - Reverted setpoint change from 40L/s to 80L/s. | All Water System ROC General | 2026-01-20
ROC | January | YWS + NYWS NORMAL | All Water System ROC General | 2026-01-29
ROC | January | YWS + NYWS Normal Connor Smith signing out | All Water System ROC General | 2026-01-22
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-22
ROC | January | VNPS PD8 - Tim H requested the duty be activated for the VNPS PD8 pumps. Activated duty 1 and then duty 2. | All Water System ROC General | 2026-01-28
ROC | January | MAPS PD7- Placed pump 3 in manual VNPS PD7- Placed pump 4 in auto as second duty 1 pump | All Water System ROC General | 2026-01-28
ROC | January | GWTP - Make up air unit 1 Coil Low temp alarm. Jack P requested disregard alarm. w/o created with Property services. # Consult | All Water System ROC General | 2026-01-29
ROC | January | STW12, STW3- Placed wells man/on | All Water System ROC General | 2026-01-23
ROC | January | MARS - Level Hi and increasing. AURSBS activated Duty 1. | All Water System ROC General | 2026-01-21
ROC | January | NMW15, Station Turbidity hi alarm, rotated ammonia pumps so pump 2 is in D1 and pump 1 is in D2 | All Water System ROC General | 2026-01-31
ROC | January | Carter Dunn Signing In | All Water System ROC General | 2026-01-29
ROC | January | YWS+NYWS normal Adam Button signing out | All Water System ROC General | 2026-01-15
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-31
ROC | January | KSTP- Settl Water Cond Level LoLo. Plant is offline for the night. | All Water System ROC General | 2026-01-27
ROC | January | KLET27- Activated D1 | All Water System ROC General | 2026-01-28
ROC | January | BLW12- Generator running alarm came in. Utility not available. Will continue to monitor for change AUETOH- Activated D1 | All Water System ROC General | 2026-01-28
ROC | January | Aurora Water System- Received a call from Roads Dispatch. Informed that there is a large amount of water pooling at 301 St Johns Sideroad. Possible water main break. All Pipes shows all infrastructure in the area belongs to the Town of Aurora. Dispatch will follow up with Town of Aurora. | All Water System ROC General | 2026-01-30
ROC | January | Angelica Chepiga signing in, weather -19C | All Water System ROC General | 2026-01-29
ROC | January | Connor Smith signing in -4C Snowy | All Water System ROC General | 2026-01-21
ROC | January | YWS + NYWS NORMAL Angelica Chepiga signing out | All Water System ROC General | 2026-01-26
ROC | January | NMVCBA- Change flow setpoint from 40L/s to 20L/s | All Water System ROC General | 2026-01-27
ROC | January | ARPS- Peel Ammonia Analyzer A- Airport Rd Discharge. Alarm cleared. | All Water System ROC General | 2026-01-28
ROC | January | HLW1 - Eric S. is on site and will be working on silicate pump 2 11:20 - Eric is finished on site | All Water System ROC General | 2026-01-30
ROC | January | HLW2 - Combined Chlorine Lo and Treated Total Chlorine Lo alarms came in. Checked site. Well is not running and water is not being directed to users | All Water System ROC General | 2026-01-30
ROC | January | YWS + NYWS NORMAL | All Water System ROC General | 2026-01-19
ROC | January | STW3 - Effluent free chlorine residual Hi alarm. Influent chlorine residual higher than normal after chlorine cylinders rotated. Will monitor. 19:53 Effluent free chlorine residual back to normal, cleared alarm. | All Water System ROC General | 2026-01-19
ROC | January | MAPSs1 - Ian W. informed that he is working on the server. Directed to disregard heartbeat alarm until further notice 16:38 - Ian informed that he is finished working on the server and the alarm has cleared | All Water System ROC General | 2026-01-23
ROC | January | KCETDS - Chlorine room low temperature alarm. Checked site, no chemical dosing is used on site. No concern for frozen chemical lines. | All Water System ROC General | 2026-01-23
ROC | January | NMETIB- Deactivated D1 at 73% as NMETHW D1 activated as per shift report | All Water System ROC General | 2026-01-26
ROC | January | QVW34 - Yash S. is on site commissioning well 4. Yash informed that the ROC may lose communications to site | All Water System ROC General | 2026-01-30
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-17
ROC | January | STETBR - Tower level low alarm. Placed STW3, STW12 man/on MKRSEM - Requested Toronto water (Brett) to start filling RES with 2 pumps. | All Water System ROC General | 2026-01-19
ROC | January | Ethan U signing out | All Water System ROC General | 2026-01-16
ROC | January | YWS+NYWS normal | All Water System ROC General | 2026-01-26
ROC | January | STETBR - Tower level hi alarm. Placed STW1 and STW3 in auto mode. | All Water System ROC General | 2026-01-28
ROC | January | AUPSRR - Post-inj free chlorine hihi, sudden spike in reading before coming down back within range | All Water System ROC General | 2026-01-17
ROC | January | Ethan Ullalkar signing out. | All Water System ROC General | 2026-01-17
ROC | January | NMETHW- Deactivated D1 at 72% to offset from NMETHW as per shift report | All Water System ROC General | 2026-01-24
ROC | January | NMETIB, Activated D1 to offset tower | All Water System ROC General | 2026-01-16
ROC | January | YWS+NYWS normal STETTL- Phil D done on site was able to reset heat trace fault alarm and site looks okay. Leaving site | All Water System ROC General | 2026-01-24
ROC | January | VNRSKS - Swapped supply pumps to one MAPS pump and one VNPS pump. | All Water System ROC General | 2026-01-22
ROC | January | QVW12- Treated total hi alarm came in. Continued to monitor for 20 mins did not recover. Notified Ben H. Directed to change Influent free target from 2.9 mg/L to 2.8mg/L. ARPS- ROYKS to ROPKs comm alarm came in again comms okay trends okay cleared alarm will contact ROP or PCS oncall if alarm comes back in #consult | All Water System ROC General | 2026-01-26
ROC | January | MTETNL- MTETNL to MTW12 comm alarm cleared alarm as trends were okay | All Water System ROC General | 2026-01-27
ROC | January | YWS+NYWS normal | All Water System ROC General | 2026-01-27
ROC | January | NMVCBA- Changed flow set point from 40l/s to 30L/s AUW14- Placed wells in man/off | All Water System ROC General | 2026-01-27
ROC | January | STW12 and STW3 - Noticed STETBR is not filling. Tower level hi alarm did not come in. Duty is not active. Placed all wells man/off | All Water System ROC General | 2026-01-17
ROC | January | GWTP - Chlorine Tank 1 Weight Lo alarm came in. Checked site. Will send an email to the East Water Team | All Water System ROC General | 2026-01-18
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-19
ROC | January | NMW15 - Eric S on site to complete annual calibrations. Eric has requested the well be deactivated while he completes this task. Confirmed with Alex B that the well can be shut down. Placed the well manual/off. | All Water System ROC General | 2026-01-20
ROC | January | VNRSKS - Placed all pumps at MAPS PD7 into man/off but kept pump 3 in auto. Placed pump 3 at VNPS PD7 into auto 12:32 - Placed all pumps man/off at MAPS PD7 and placed pump 2 in auto at VNPS PD7 16:01 - Placed all pumps man/off at VNPS PD7 and placed all pumps back to auto at MAPS PD7 | All Water System ROC General | 2026-01-17
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-17
ROC | January | MARS - Lo level alarm came in. Checked site. Called Toronto Water (Zoran) and requested to increase flow to reservoir | All Water System ROC General | 2026-01-21
ROC | January | MKRSEM- Called Toronto (Pouria) and requested two pumps on MARS- Called Toronto (Pouria) and requested to lower flow to Maple | All Water System ROC General | 2026-01-21
ROC | January | NMVCBA - Increased flow setpoint to 40l/s | All Water System ROC General | 2026-01-29
ROC | January | NMETHW - Deactivated duty 1 to help offset with NMETIB. | All Water System ROC General | 2026-01-26
ROC | January | YWS + NYWS NORMAL | All Water System ROC General | 2026-01-27
ROC | January | ARPS - Airport Road Total Ammonia LoLo alarm came in. Analyzer is reading 0. Called Peel Water (Sam) who informed their instrumentation team is on site changing reagents. Will call back once they are finished | All Water System ROC General | 2026-01-26
ROC | January | Angelica Chepiga signing in, weather -16C | All Water System ROC General | 2026-01-26
ROC | January | MAP8 - Ernie H onsite working on Pump 4 VFD | All Water System ROC General | 2026-01-19
ROC | January | QVETQS - System Pressure LoLo alarm came in. Reoccurring issue. Pressure hits LoLo level and comes back to optimal range right away. | All Water System ROC General | 2026-01-23
ROC | January | ROC SCADA Room, Franco from Property services showed up to test his key card, card didn't work. never entered the SCADA room | All Water System ROC General | 2026-01-15
ROC | January | YWS + NYWS NORMAL | All Water System ROC General | 2026-01-20
ROC | January | NMW15 - Station turbidity Hi alarm/ value increasing. Rotated silicate pumps will monitor. | All Water System ROC General | 2026-01-20
ROC | January | HLW2, Tim H on site, placing well back in operation, will be taking samples on site | All Water System ROC General | 2026-01-29
ROC | January | Christian Van Beek signing in. Weather: -14C and clear. | All Water System ROC General | 2026-01-20
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-21
ROC | January | NMETHW- Deactivated duty NMVCBA- Adjusted to 40L/s NMVCIB- Adjusted to 80L/s | All Water System ROC General | 2026-01-21
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-22
ROC | January | GWTP- ZW6 shutdown/ Neutralization aborted/ Back pulse not available. notified Jack P. Jack P on site at KSETDP with Patrick F and linear team to charge main but will take a look issues at GWTP | All Water System ROC General | 2026-01-30
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-30
ROC | January | NMETBR - Joe W. is on site for Analyzer Maintenance and testing Hi/Low temp and building temp alarm | All Water System ROC General | 2026-01-16
ROC | January | MAPSN1 Server - Communication alarm. Called Yash S. who is looking into this 08:44 - Yash S. informed he will be restarting HUB 3 server 08:55 - Yash S. is finished restarting the server | All Water System ROC General | 2026-01-26
ROC | January | HLW1- Silicate Pump 2 Leak Alarm. Called Stephen B. Tyler ZJ is onsite troubleshooting HLW2- Stephen B will be heading to site for work orders. Can disregard all alarms while onsite. | All Water System ROC General | 2026-01-20
ROC | January | QVW34 - Activated well 4 in manual mode while QVW12 is being worked on by Will M and Jerry Z. Duty 1 start setpoint has been reached. | All Water System ROC General | 2026-01-22
ROC | January | AUETOH - Joe D. informed that he is finished on siye | All Water System ROC General | 2026-01-22
ROC | January | STW12- Placed wells back into auto STW3- Placed well back into auto | All Water System ROC General | 2026-01-20
ROC | January | MAPS- Control panel door open contact Kyle R. On site with Ernie H troubleshooting P4 | All Water System ROC General | 2026-01-21
ROC | January | RHPSPA - Generator warning alarm and generator not in auto alarm. Checked site, generator is showing in auto. Dan Z signed into site through log book. Able to clear alarms. | All Water System ROC General | 2026-01-23
ROC | January | BLW3 - Generator 1 Running Status alarm came in. Checked site. Site is still connected to hydro power. Possible power blip. Will continue to monitor 17:26 - Generator is no longer running and alarm cleared | All Water System ROC General | 2026-01-22
ROC | January | Connor Smith signing out | All Water System ROC General | 2026-01-30
ROC | January | VNETFD, Kingsley M resetting OIT 11:54, Kingsley M is finished on site MKRSMR, Talha is resetting oit on site | All Water System ROC General | 2026-01-16
ROC | January | VNPSCD - Tim H. is on site and is looking into a power blip that occurred on site | All Water System ROC General | 2026-01-16
ROC | January | NMETIB - Activated Duty 1 to offset with NMETHW. | All Water System ROC General | 2026-01-21
ROC | January | MKRSEM- Called Toronto water (Zoran) and requested stop filling Res. | All Water System ROC General | 2026-01-21
ROC | January | MKPSSA - Phil D. and Travis W. are on site to complete work orders. These include the chlorine analyzers, surge relief valve exercising, generator test, and flood alarm test. Phil informed they will also be running pump 1. Directed to disregard all alarms until work is complete. | All Water System ROC General | 2026-01-22
ROC | January | QVW34- Dan B, Yash S and Will M finished onsite. Well 4 will remain local off. | All Water System ROC General | 2026-01-30
ROC | January | MKRSEM - Called Toronto Water 9Mehdi) and requested they stop flow to MKRSEM. | All Water System ROC General | 2026-01-31
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-31
ROC | January | KSTP - Raw water turbidity fault alarm. Checked site, plant is off. Disregard as per the shift report. BLW3 - Influent free chlorine lolo alarm. Checked site, well was active when alarm triggered. Trending shows a sudden drop of the influent free chlorine reading. No chlorine leak alarm present. No abnormal trends identified. System still filling with BLW1, and tower is nearly full. Well is interlocked, placed the well into manual/mode until it can be inspected. Sent email to OCO and will follow up with a consult later this morning. | All Water System ROC General | 2026-01-31
ROC | January | SHTP - Yash S on site working on control panels. | All Water System ROC General | 2026-01-22
ROC | January | NMW15 - Influent free chlorine hihi and treated free chlorine hihi alarm. Checked site, well recently activated. Trending shows an increase of the treated free chlorine reading that coincides with a drop of the combined chlorine reading. Rotated ammonia pumps to ensure ammonia is being dosed. Monitored site to determine if treated free chlorine reading will drop. 18:02 - NMW15 - Treated free chlorine reading is dropping after rotating the ammonia pump. Angelica C will monitor site to ensure values return to normal range. May see high free chlorine readings at NMTKKC and NMETIB. | All Water System ROC General | 2026-01-20
ROC | January | STPSMR - Dan Z on site to complete a generator test. | All Water System ROC General | 2026-01-23
ROC | January | MKRSEM, Notified Toronto operator Zoran to start filling the res | All Water System ROC General | 2026-01-23
ROC | January | KLET27- Deactivated D1 to help MARS recover | All Water System ROC General | 2026-01-24
ROC | January | Angelica Chepiga signing out | All Water System ROC General | 2026-01-21
ROC | January | Adeela Khan signing in | All Water System ROC General | 2026-01-23
ROC | January | YWS + NYWS NORMAL | All Water System ROC General | 2026-01-20
ROC | January | YWS + NYWS NORMAL | All Water System ROC General | 2026-01-21
ROC | January | YWS + NYWS NORMAL | All Water System ROC General | 2026-01-21
ROC | January | ARPS, Jerry from OCWA called, at 08:00, he will be rotating the pumps at his station | All Water System ROC General | 2026-01-31
ROC | January | KSTP - Both Fluoride Pumps not available alarm came in. Checked site. Hi/lifts are manual/off. Called Ben H. who informed that he placed fluoride pumps off as they were reading higher throughout the weekend. Ben H. also informed that he is topping up chemicals. Ben also informed he will be placing fluoride pumps man/off upon plant startup. Informed to disregard fluoride lolo alarm but call for a fluoride hihi/hi | All Water System ROC General | 2026-01-26
ROC | January | YWSS+ NYWS Normal | All Water System ROC General | 2026-01-31
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-31
ROC | January | QVW34 = Will M on site to complete chlorine and turbidity analyzer maintenance. | All Water System ROC General | 2026-01-28
ROC | January | STETBR - Tower Level Hi alarm came in. Placed STW12 and STW3 back to auto as per interim | All Water System ROC General | 2026-01-22
ROC | January | NMW136- Combined Cl2 lo alarm came in. Looks like analyzer dropped out. Continued to monitor residual recovered after 6 mins cleared alarms | All Water System ROC General | 2026-01-24
ROC | January | Ethan U signing in | All Water System ROC General | 2026-01-19
ROC | January | GWTP - Sutton header fluoride low alarm. Checked site, Sutton system is drawing water to fill the tower. Trending shows that the fluoride value dipped and is recovering. Jack P on site. | All Water System ROC General | 2026-01-28
ROC | January | NMW136 - Well 16 flow hi for a couple minutes. Came back within range shortly after. Will monitor STPSMR - Travis W informed to disregard gas detector hihi. KSTP - Jerry Z onsite with Donald M onsite, manual backwash on filter 1, calibration mode on raw water | All Water System ROC General | 2026-01-19
ROC | January | HLW2, Combined Cl2 hi, Notified Tim H who just left site, he deactivated the duty, residuals should go back to normal range | All Water System ROC General | 2026-01-29
ROC | January | ARPS- Martin from OCWA called. They have placed Total Chlorine Analyzer in maintenance mode for work. They will be taking grabs every 30 minutes to confirm residuals. ARPS- Airport Rd Combined Chlorine Hi Alarm. Called Peel. Confirmed this was not a real reading and residual is 2.33mg/L. Airport transfer pump also shut down due to this analyzer work. Currently working on getting pump started back up. They will call when back to normal operations. | All Water System ROC General | 2026-01-29
ROC | January | Christian Van Beek signing in. Weather: -13C and clear. | All Water System ROC General | 2026-01-23
ROC | January | NMW15 - Eric S. called to inform that he is on site replacing the colourimeter in the total chlorine analyzer 11:05 - Eric called back to inform that he is finished on site but Alex B. is now on site running the well in manual | All Water System ROC General | 2026-01-23
ROC | January | Carter Dunn Signing In, -21D/Clear | All Water System ROC General | 2026-01-31
ROC | January | GRTPLL - Low lift discharge total chlorine res fault alarm, disregard as per Scada review. | All Water System ROC General | 2026-01-29
ROC | January | YWS + NYWS NORMAL | All Water System ROC General | 2026-01-30
ROC | January | NBW3 - Generator not in Auto alarm came in. Checked site. Noticed that the site is still connected to generator power. Generator is showing that its in Local. Called Jordan B. who informed no one is on site. Jordan informed he will check site later today 08:34 - Generator went back to auto and alarm cleared | All Water System ROC General | 2026-01-30
ROC | January | KSTP - Raw water turbidity fault alarm, disregard as per SCADA review. | All Water System ROC General | 2026-01-30
ROC | January | NMTKBS, Activated D1 | All Water System ROC General | 2026-01-31
ROC | January | Carter Dunn Signing Out | All Water System ROC General | 2026-01-25
ROC | January | GWTP - Backpulse Tank 1 and 2 Level HiHi alarms. Dan Z on site. # Consult | All Water System ROC General | 2026-01-20
ROC | January | MKRSEM- Requested Toronto water(Brett) to start filling res with 2 pumps. | All Water System ROC General | 2026-01-20
ROC | January | GWTP - Backpulse tank fill V man/off until further notice. Dan Z leaving site. | All Water System ROC General | 2026-01-20
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-22
ROC | January | Christian Van Beek signing out. | All Water System ROC General | 2026-01-22
ROC | January | Carter Dunn Signing Out | All Water System ROC General | 2026-01-24
ROC | January | NMPSKC - Changed FCV1 from auto17% to manual 0 % to help NMTKBS fill | All Water System ROC General | 2026-01-25
ROC | January | HLETYS - Post injection Combined Chlorine hi alarm came in multiple times. Tower is filling. Alarms were clearing on their own due to fluctuating values. Increased hypo pump 1 max flow to 190 mL/min to decrease dosing setpoint. After five mins, combined levels came back down and alarm cleared 17:48 - Alarm came back in. Called Jordan B. who directed to rotate hypo pumps. Hypo pump 2 is now in duty 1. Jordan directed to deactivate duty if alarm comes back in. #CONSULT | All Water System ROC General | 2026-01-17
ROC | January | KSTP - Both Pre Chlorinators Not Avalible alarm came in. Donald M. called to inform that he and Jerry Z. are on site for raw water samples and needed to turn the pre chlorination system off. Will place it back online in an hour | All Water System ROC General | 2026-01-29
ROC | January | Christian Van Beek signing out. | All Water System ROC General | 2026-01-29
ROC | January | STW56, STRS48- Joe M testing chlorine leak alarm. | All Water System ROC General | 2026-01-27
ROC | January | Adeela Khan signing in. Weather: -6 and sunny | All Water System ROC General | 2026-01-22
ROC | January | RHRSTR - Activated duty 1. | All Water System ROC General | 2026-01-22
ROC | January | KSTP - Donald M. and Jerry Z. are on site and will be working on the chlorine system. | All Water System ROC General | 2026-01-21
ROC | January | ARPS - Martin from OCWA called to inform that he is rotating from pump 8 to pump 1. 08:20 Martin from OCWA called to inform that Pump 5 is running in auto/duty 1. | All Water System ROC General | 2026-01-27
ROC | January | KSETWB- Ian W working on OIT. Disregard Heartbeat Alarm. | All Water System ROC General | 2026-01-27
ROC | January | QVW34 - Influent free chlorine hihi. Checked site, well is running in manual mode for sampling. Trending shows a spike of the influent free chlorine which returned to normal range within two reading intervals. Reset alarm. | All Water System ROC General | 2026-01-28
ROC | January | HLW2- Stephen B leaving site. | All Water System ROC General | 2026-01-20
ROC | January | Adam Button signing out | All Water System ROC General | 2026-01-21
ROC | January | YWS+NYWS normal Adam button signing out | All Water System ROC General | 2026-01-25
ROC | January | Gluzen Ramos Ong signing in STETBR - Adjusted Hi/Lo level alarms from 80/60 to 79/61 to ensure alarm triggered for ROC action as per interim | All Water System ROC General | 2026-01-19
ROC | January | YWS + NYWS Normal Carter D signing Out | All Water System ROC General | 2026-01-18
ROC | January | MARS - Called Toronto Water (Paul) and requested to go back to normal flow | All Water System ROC General | 2026-01-18
ROC | January | Christian Van Beek signing in. Weather: -10C and clear. | All Water System ROC General | 2026-01-19
ROC | January | MKRSEM- Called Metro spoke with Paul to start 2 pumps | All Water System ROC General | 2026-01-17
ROC | January | Adeela Khan signing in. Weather: -10 and partly cloudy | All Water System ROC General | 2026-01-18
ROC | January | STRS48 - Travis W. and Joe M. are on site for a cylinder change | All Water System ROC General | 2026-01-16
ROC | January | JFPS- Placed P1 in man/on KCPSDS- Placed P1/2 in man/off | All Water System ROC General | 2026-01-18
ROC | January | Angelica Chepiga signing out | All Water System ROC General | 2026-01-20
ROC | January | YWS+NYWS normal | All Water System ROC General | 2026-01-18
ROC | January | Adeela Khan signing in | All Water System ROC General | 2026-01-16
ROC | January | RHPSPA - Gen warning, unable to clear, nothing mentioned on shift report. Called Ryan B. Disregard for night Consult | All Water System ROC General | 2026-01-16
ROC | January | GWTP - Make up air unit 1 coil low temp. Critical alarm, informed Dan Z as nothing noted on shift report. Disregard for the night Consult | All Water System ROC General | 2026-01-16
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-18
ROC | January | KSTP - Fin Water Fluoride Residual Hi alarm came in. Checked site. Duty recently activated. Fluoride levels went back to optimal levels | All Water System ROC General | 2026-01-18
ROC | January | AUW14, Placed wells 1/4 man/off to take more water from AURSBS | All Water System ROC General | 2026-01-23
ROC | January | QVETQS - System pressure low and low low alarm. Checked site, trending shows a sudden dip of the system pressure reading which recovered within one reading interval. Area operators making system changes as QVW12 is manual/off and the Poppy lane valve is manual/closed. Will monitor system. | All Water System ROC General | 2026-01-22
ROC | January | NMVCBA - Opened valve in manual mode to 40L/s to slow the drain cycle of NMETIB. NMETHW is not filling due to operational issues, opening NMVCBA to help keep the tower levels offset. | All Water System ROC General | 2026-01-22
ROC | January | NMVCBA - Placed valve in manual at 40 L/s | All Water System ROC General | 2026-01-17
ROC | January | Christian Van Beek signing out. | All Water System ROC General | 2026-01-19
ROC | January | GWTP- Jackie S onsite performing GAC Backwash | All Water System ROC General | 2026-01-20
ROC | January | MKRSEM- Called Toronto (Pouria) and requested two pumps on. | All Water System ROC General | 2026-01-22
ROC | January | GWTP - ZW5 Neutralization Exceeded Duration alarm came in. Disregarded as train 5 is going through an R-Clean, as per Jack P | All Water System ROC General | 2026-01-21
ROC | January | NMETIB - Deactivated Duty 1 to offset with NMETHW. NMETBA - Flow setpoint from 80 to 40l/s NMVCIB - Flow setpoint from 40 to 80l/s | All Water System ROC General | 2026-01-21
ROC | January | VNPS PD8- P4 VFD fault/ uncommanded stop and P$ valve fail to open alarm came in. Placed P3 in D1. Running okay. Notified Tim H. Direct to try and clear alarms as they may be related to D1 deactivation for sampling of JFRS. VFD fault did not clear Let Tim H know about outstanding issue | All Water System ROC General | 2026-01-21
ROC | January | VNRSKS - Placed all MAPS PD7 pumps man/off and placed pump 2 and 3 at VNPS PD7 into auto | All Water System ROC General | 2026-01-16
ROC | January | Carter Dunn Signing In, -13D/Clear | All Water System ROC General | 2026-01-18
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-23
ROC | January | KSETDP- Chris S working on PAC. Will lose communications onsite. | All Water System ROC General | 2026-01-20
ROC | January | STRS48- High Lift Pump 1 Failed to Stop Alarm. Alarm cleared and went back into duty 1. | All Water System ROC General | 2026-01-22
ROC | January | NMW15 - Eric S leaving site after annual calibrations. Alex B on site still. | All Water System ROC General | 2026-01-20
ROC | January | QVETQS- system pressure lo alarm came in. Came in as wells shutdown. Notified Will M as this is a continuing issue and Will will follow up with Ben H about issue | All Water System ROC General | 2026-01-21
ROC | January | MKRSEM- Called Toronto (Pouria) and requested pumps off. | All Water System ROC General | 2026-01-22
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-22
ROC | January | QVETQS- Comm fail on site interlocking QVW12/34. Notified Will M heading to site to hook up temporary generator | All Water System ROC General | 2026-01-15
ROC | January | YWS + NYWS NORMAL | All Water System ROC General | 2026-01-11
ROC | January | NMVCBA - Placed valve man/open at 40 L/s to help slow the drain of NMETIB 02:49 - Placed valve back to auto | All Water System ROC General | 2026-01-11
ROC | January | TMC317 - Noticed Toronto Water was pushing max flow but it was not requested by the ROC. Called Toronto Water (Brett) to see if they were moving water around or if something happened. Brett informed this was by mistake and will place back to normal flow | All Water System ROC General | 2026-01-11
ROC | January | STETTL - STETTL to STW12 Comm alarm came in. Checked site. Communications are back and trending is okay. Alarm has cleared | All Water System ROC General | 2026-01-12
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-15
ROC | January | Carter Dunn Signing In, -13D/Blizzard | All Water System ROC General | 2026-01-15
ROC | January | AUETAD. Rick L is on site doing annual calibrations | All Water System ROC General | 2026-01-15
ROC | January | JFPS, David T on site, testing Generator/Temp/Flood and health and safety alarms. David T will also be testing the flood and health and safety alarms at JFRS | All Water System ROC General | 2026-01-07
ROC | January | AURSBS- Cl2 GCLR valve failed to open. Reset alarm. Chem system not being called for | All Water System ROC General | 2026-01-08
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-13
ROC | January | VNP7 - Place pump 2 man/off MAP7 - Place pump 1 auto | All Water System ROC General | 2026-01-13
ROC | January | GWTP - Make up air unit 1 coil; low temp alarm. All previous instances of this alarm have been a disregard from on call operators. Disregard until Monday at 09:00. 17:55 - GWTP - Decided to contact Stephen B to ensure this alarm can be disregarded. No answer, Adeela K will call him again. | All Water System ROC General | 2026-01-11
ROC | January | Ethan U signing in | All Water System ROC General | 2026-01-12
ROC | January | YWS + NYWS NORMAL | All Water System ROC General | 2026-01-07
ROC | January | ANW23, Stephen B directed to place well 3 back to auto, well will not run tonight Well 3 is in D1 but isn't able to run 15:29, Inlet Free CL2 lolo alarm came in, notified Stephen B, he believes that when well 3 turned off, air got into the pipe that caused the inlet to drop. within 5 minutes, residual came back to normal. Cole W making a work order for well 3 to be looked at | All Water System ROC General | 2026-01-07
ROC | January | Angelica Chepiga signing out | All Water System ROC General | 2026-01-07
ROC | January | Adam Button signing in | All Water System ROC General | 2026-01-08
ROC | January | MTW3- Kingsley M called. Evgeny S will be attending site to look into Historian Heartbeat alarm outstanding. 14:38- Kingsley M called. Issue has been resolved. Placed well into auto. | All Water System ROC General | 2026-01-09
ROC | January | ANW23 - Stephen B attending site. Activate duty for wells at request of operator | All Water System ROC General | 2026-01-14
ROC | January | AUETAD- Eric S onsite to troubleshoot Cl analyzer 15:24- Finished onsite. | All Water System ROC General | 2026-01-09
ROC | January | JFPS - Discharge pressure Lo and Low low alarms/ cleared right away. Will monitor. | All Water System ROC General | 2026-01-08
ROC | January | KSTP - Fin water fluoride res Hi alarm, duty recently activated, notified Jerry Z. He is on site, will check. | All Water System ROC General | 2026-01-08
ROC | January | KSTKWP, Generator Running Alarm, notified Ryan B, he will look into it | All Water System ROC General | 2026-01-15
ROC | January | VNP7 - Place pumps man/off MAP7 - Place all pumps back in auto | All Water System ROC General | 2026-01-07
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-08
ROC | January | Ethan Ullalkar signing out. | All Water System ROC General | 2026-01-08
ROC | January | RHRSTR - Deactivated D1 @ 83 % to maintain MARS level. | All Water System ROC General | 2026-01-08
ROC | January | VNPS PD7 - pump 2 man/off, MARS PD7- Pump 1 to auto. | All Water System ROC General | 2026-01-10
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-13
ROC | January | NMTKKC - Kingsley M. called to inform that he will be restarting the OIT and will receive a historian heartbeat alarm. Kingsley inform this will not interlock the system 08:00 - Kingsley called back to inform that the restart is complete and the historian has been cleared | All Water System ROC General | 2026-01-14
ROC | January | KSTP - Jerry Z and Ryan B running generator and testing chlorine leak alarm. | All Water System ROC General | 2026-01-08
ROC | January | QVW34 - William M running generator. | All Water System ROC General | 2026-01-08
ROC | January | VNRSKS - Swapped supply pumps to one MAPS pump and one VNPS pump. | All Water System ROC General | 2026-01-14
ROC | January | RHRSTR - Deactivate duty 1. | All Water System ROC General | 2026-01-15
ROC | January | Christian Van Beek signing out. | All Water System ROC General | 2026-01-15
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-13
ROC | January | NBW3 - Influent Free Chlorine LoLo alarm came in. Checked site. Influent levels were still low after 10 mins. Called Jordan B. who directed to place hypo pump 2 man/off. If the influent levels increase within the next 2 mins, Jordan directed to start the well | All Water System ROC General | 2026-01-14
ROC | January | QVW12 - Effluent free chlorine hihi, well locked out well. Informed Joe W who is onsite. Is looking into issue | All Water System ROC General | 2026-01-13
ROC | January | GWTP - Sutton Header fluoride Hi alarm. SUETDR duty not active, no flow. Will monitor. | All Water System ROC General | 2026-01-08
ROC | January | AUW57- Joe D on site to test Cl2 leak alarm | All Water System ROC General | 2026-01-15
ROC | January | AURSBS - Post -inj free ammonia HiHi alarm. Duty deactivated recently. Will monitor. | All Water System ROC General | 2026-01-10
ROC | January | GWTP - Backpulse flow lolo, ZW7 shutdown and maintenance clean aborted. Able to reset all alarms except the train shutdown and backpulse pumps not available alarm. Called Stephen B who will check SCADA. #consult | All Water System ROC General | 2026-01-11
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-13
ROC | January | AUW14 - Lee F working on pump 4, Joe D placed pump 4 man/off. | All Water System ROC General | 2026-01-07
ROC | January | RHPSPA, Gen Warning Alarm, Notified Travis W, he will investigate further | All Water System ROC General | 2026-01-15
ROC | January | MKRSEM - Free Chlorine Residual Fault alarm came in. Critical alarm. Called Travis W. but no answer. Will try again 11:33 - Called Travis W. who informed he is on site and just took a grab. Directed to disregard alarm | All Water System ROC General | 2026-01-14
ROC | January | MARS- Cell1 (North) Lvl Hi Alarm RHRSTR- Deactivated duty | All Water System ROC General | 2026-01-09
ROC | January | NMW136 - Silicate Pump 1 Fault and Uncommanded stop alarms came in. Checked site. Called Ryan B. who informed he will place silicate pump 1 man/off for the night | All Water System ROC General | 2026-01-14
ROC | January | GWTP, Sutton Header Fluoride Hi alarm, no water going through the header, Was talking with Stephen B and directed to disregard at this time | All Water System ROC General | 2026-01-07
ROC | January | MKRSEM - Request Paul (TO) to run 2 pumps | All Water System ROC General | 2026-01-07
ROC | January | NMW15 - Combined Chlorine Lo alarm came in. Well is not running and water is not being directed to users | All Water System ROC General | 2026-01-12
ROC | January | KSTP - Fin water fluoride hi. informed Jerry Z. Is heading to site | All Water System ROC General | 2026-01-13
ROC | January | YWS +NYWS Normal | All Water System ROC General | 2026-01-14
ROC | January | YWS + NYWS NORMAL | All Water System ROC General | 2026-01-08
ROC | January | KLPS27- Talha working on OIT. Disregard heartbeat alarm. | All Water System ROC General | 2026-01-09
ROC | January | MAPS PD8 - Pump 1 fail to start and discharge valve fail to open alarms. Second time these alarms have triggered. Placed pump 1 manual off and sent email to area ops to have pump and valve inspected. Duty rotated to pump 3. Monitoring operation. | All Water System ROC General | 2026-01-15
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-14
ROC | January | VNRSKS - Swapped supply pumps to one MAPS pump and one VNPS pump. | All Water System ROC General | 2026-01-13
ROC | January | GWTP - Sutton Header Fluoride hi alarm. Checked site, the duty for SUETDR recently stopped. Trending shows that when this flow stops the fluoride reading spikes at the GWTP. Known issue in operations. Will monitor value. | All Water System ROC General | 2026-01-13
ROC | January | MTW3- Phil D on site to work on NTU analyzers. Well in man/off Will be heading to MTW12 to do the same thing. Phil D will Place well back in auto when done and MTW12 in man/off for work | All Water System ROC General | 2026-01-09
ROC | January | QVW34 - Joe W. called to inform that he is on site and will be testing the chlorine leak alarm | All Water System ROC General | 2026-01-14
ROC | January | MKRSEM - Request TO (Zhoran) to run 2 pumps | All Water System ROC General | 2026-01-14
ROC | January | STETBR, Placed VC_FCV1 man/closed and placed pumps 1/2 back to auto MAPS PD7, Placed pumps 1-4 man/off VNPS PD7, Placed umps 2/3 back to auto | All Water System ROC General | 2026-01-13
ROC | January | GWTP - Wash water tank 2 Chl residual fault/hi. Called Patrick F, disregard | All Water System ROC General | 2026-01-14
ROC | January | VNETFD- Talha H Rebooting OIT. Disregard historian heartbeat deactivated D1 VNETAG- Talha H Rebooting OIT. Disregard historian heartbeat HLW1- Dave T and Stephen B on site to work on Cl2 and NTU analyzers, to test Cl2 leak alarm and work on ammonia system | All Water System ROC General | 2026-01-08
ROC | January | QVW4, Dan B on site, turning the power off for well 4, they will be working on the electrical system for the well | All Water System ROC General | 2026-01-15
ROC | January | YWS + NYWS Normal STRS48 - High Lift Pump 1 failed to stop alarm came in. Checked site. Noticed that the pump was shutting down but interlocked. After about a minute, pump fully shut down and alarm cleared | All Water System ROC General | 2026-01-12
ROC | January | MAPS PD7, Placed pumps 1/2 man/off VNPS PD7. Placed pumps 2/3 in auto 22:52, Reverted Changes | All Water System ROC General | 2026-01-08
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-12
ROC | January | KLET27- Talha H rebooting OIT disregard historian heartbeat until done 10:50- KLET27- Talha done reboot alarm cleared | All Water System ROC General | 2026-01-15
ROC | January | YWS + NYWS Normal VNRSKS - Deactivated duty 1 | All Water System ROC General | 2026-01-10
ROC | January | NMETIB - Deactivated duty 1. | All Water System ROC General | 2026-01-14
ROC | January | AUETAD - Water system fire storage volume low alarm. Shift report states that the duty band has been changed to cycle from 40% to 75%. Duty 1 will activate shortly. | All Water System ROC General | 2026-01-14
ROC | January | AUPSRR - Post injection free chlorine hihi and post injection combined chlorine lolo. Checked site, trending shows a short spike of the free chlorine reading and a small dip of the combined chlorine reading. Both values returned to normal range within one reading interval. reset alarms. | All Water System ROC General | 2026-01-14
ROC | January | SHETCS- Kingsley M rebooting OIT. No comm loss expected QVETQS- Tie valve failed to open alarm came in. Tie valve not usually open reset alarm QVW12- Influent free Cl2 hihi alarm came in on well start up cleared after 3 mins as trends returned to normal 8:41-SHETCS- Kingsley M done reboot alarms cleared trends okay | All Water System ROC General | 2026-01-15
ROC | January | AUPSWS- Lee F done on site NMVCBA- Placed in man/open at 40L/s STETTL- Joe M on site to test eye wash and clean Cl2 analyzer | All Water System ROC General | 2026-01-15
ROC | January | NBW5, Jordan B on site, running generator and testing cl2 analyzers, directed to disregard alarms from site till he is finished | All Water System ROC General | 2026-01-15
ROC | January | RHPSPA- Travis W notified ROC that gen warning alarm is a temperature related issue. Will try to get another heater n the room to help the block heater keep up | All Water System ROC General | 2026-01-15
ROC | January | GWTP- Patrick F working on waste wash pumps. Disregard related alarms. | All Water System ROC General | 2026-01-09
ROC | January | NMPSKC- Jay g on site to run generator and test hi lo temp | All Water System ROC General | 2026-01-15
ROC | January | STW3- Joe M on site to run generator MTW3- Phil D on site to run generator, work on all analyzers and inspect all chemical systems on site AURSBS- Donald M. on site testing Chem system and no alarms coming in. Eye wash alarm came in after a few mins. Donald M will test Cl2 leak alarm again o see if alarm is triggered HLETYS- Post injection combined lo alarm came in. Notified Stephen B will take a look GWTP- Patrick F on site to clean treated and membrane NTU analyzers as well as place train 5 in a hypo clean | All Water System ROC General | 2026-01-15
ROC | January | KLET27, Activated D1, MARS on the high end | All Water System ROC General | 2026-01-15
ROC | January | YWS + NYWS NORMAL | All Water System ROC General | 2026-01-10
ROC | January | Adam Button signing in | All Water System ROC General | 2026-01-09
ROC | January | VNPSAP- Historian Heartbeat Alarm. Artour L is working on it. | All Water System ROC General | 2026-01-09
ROC | January | NBET- Talha H rebooting OIT. Disregard historian heartbeat alarm until done 10:14-NBET- Talha H done reboot reset historian heartbeat alarm | All Water System ROC General | 2026-01-09
ROC | January | STRS48 - Influent free chlorine lolo. Informed Dan Z, will attend site later. CMU = 11589909 | All Water System ROC General | 2026-01-14
ROC | January | AURSBS, Donald M on site, testing Sump/CL2 leak, working on the chemical systems on site and the humidifiers and the health and safety alarms, directed to disregard alarms till he is finished on site | All Water System ROC General | 2026-01-15
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-09
ROC | January | VNRSKS - switched feed to MAPS PD7 | All Water System ROC General | 2026-01-09
ROC | January | YWS + NYWS NORMAL | All Water System ROC General | 2026-01-09
ROC | January | STW12/3, Placed wells man/on | All Water System ROC General | 2026-01-15
ROC | January | Adam Button signing in | All Water System ROC General | 2026-01-15
ROC | January | KSTKWP, Ryan B called, site is operating with the portable generator however the Cl2 room is not having any lights or heat in the area, requests Electrician on call, contacted Sean P, he will give Ryan B a call | All Water System ROC General | 2026-01-15
ROC | January | HLETYS, Post Injection Combined Cl2 lo, Notified Stephen B, he is going to look into it CMU5: W11593334 | All Water System ROC General | 2026-01-15
ROC | January | AUPSWS, Lee F on site doing pump vibration testing, rotated so pump 4 is in D1 MARS, Tim H on site working on the Cl2 analyzers, directed to disregard analyzer alarms till he is finished | All Water System ROC General | 2026-01-15
ROC | January | KSTKWP- Comm fail on site as UPS died. Ryan B already heading to site to hook up generator | All Water System ROC General | 2026-01-15
ROC | January | KSETWP, Tower Power outage, Ryan B is heading to site CMU5: W11593298 | All Water System ROC General | 2026-01-15
ROC | January | NMW12, Alex B on site, working on the silicate system, wells will be man/off till they are finished on site | All Water System ROC General | 2026-01-15
ROC | January | NMETIB - Jason G on site to clean the chlorine analyzer. VNRSKS - Swapped supply pumps to one MAPS and one VNPS pump. | All Water System ROC General | 2026-01-12
ROC | January | KLPS27/KLET27, David T on site running the generator/temp alarms/flood alarms and doing health and safety alarms | All Water System ROC General | 2026-01-15
ROC | January | NMTKKC- Jay G on site to flush sample lines with hot water. Chem system is off and analyzers in calibration mode | All Water System ROC General | 2026-01-09
ROC | January | NRETCR - Lee F working on outlet check valve , switched controlling tower assignment to NRETBR. Will notify Ben H. | All Water System ROC General | 2026-01-08
ROC | January | MKETFA - Kingsley M restarting OIT, disregard historian heartbeat alarm. 10:01 Kingsley M completed work. | All Water System ROC General | 2026-01-08
ROC | January | GWTP Low lift - Jackie S testing eyewash alarm and cleaning turbidity meter. | All Water System ROC General | 2026-01-08
ROC | January | KCETFS - Benson S onsite for PM work on PRV, health N safety, chlorine analyzer & temp | All Water System ROC General | 2026-01-13
ROC | January | Possible Main Break, 7601 Bathurst, Vaughan, Bonnie from Transit Corp Contact Centre called, they have a resident call about a suspected main break, after checking all pipes, the main in that area belongs to Vaughan, notified them to contact the City of Vaughan. | All Water System ROC General | 2026-01-13
ROC | January | BVPS, Dan Z on site testing flood alarm on site QVW1, Joe W/Tyler Z on site running well 1 to waste | All Water System ROC General | 2026-01-13
ROC | January | AURSBS - Activated duty 1 to help lower levels at MARS | All Water System ROC General | 2026-01-13
ROC | January | MTETNL - Phil D called and directed to activate duty 1 at MTETNL. | All Water System ROC General | 2026-01-12
ROC | January | GWTP- Patrick F onsite commissioning high lift pump 4 and doing an acid clean on train 3. | All Water System ROC General | 2026-01-09
ROC | January | Zone 2 - Town of Stouffville (Travis) flushing area | All Water System ROC General | 2026-01-13
ROC | January | NMETIB - Deactivate duty 1 | All Water System ROC General | 2026-01-13
ROC | January | NMW136 - Alex B onsite for maintenance work on ammonia system and valve work | All Water System ROC General | 2026-01-13
ROC | January | JFRS - Deactivated Duty | All Water System ROC General | 2026-01-11
ROC | January | YWS + NYWS NORMAL | All Water System ROC General | 2026-01-11
ROC | January | Carter Dunn Signing Out | All Water System ROC General | 2026-01-13
ROC | January | KLPSWL, KLW34 - Benson S running generator, testing chlorine leak , temperature flood alarms, checking PRV. | All Water System ROC General | 2026-01-08
ROC | January | MKRSEM, Notified Toronto operator Paul to start filling the res YWS + NYWS Normal | All Water System ROC General | 2026-01-08
ROC | January | SHETCSn1, KLPSWLn1, VNETFDs1 and VNRSKSn- Evgeny S working on OITs. Disregard Heartbeat alarms. | All Water System ROC General | 2026-01-09
ROC | January | MKRSEM, Dan Z on site doing analyzer maint and flood alarms | All Water System ROC General | 2026-01-07
ROC | January | Connor Smith signing out | All Water System ROC General | 2026-01-09
ROC | January | RHRSTR - Deactivated D1. | All Water System ROC General | 2026-01-10
ROC | January | MKRSMR, Junji from property services is on site MAPS PD7/PD8, Tim H is having issues with the pumps on site, they wont reset from the faults, requests Dan B, notified Dan B, he will give Tim H a call BVPS, Dan Z is finished on site | All Water System ROC General | 2026-01-13
ROC | January | KCETDS - Outlet total chlorine residual lolo. Checked site, trending shows a sudden dip of the total chlorine which recovered within two reading intervals. | All Water System ROC General | 2026-01-13
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-14
ROC | January | MKRSEM - Called Toronto Water (Peter) and requested they deactivate the pumps pushing flow to MKRSEM. | All Water System ROC General | 2026-01-14
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-07
ROC | January | NBW3, Influent Free Cl2 lolo, Wells are interlocked, notified Cole W, he will get someone to look into this today | All Water System ROC General | 2026-01-07
ROC | January | NMPSKC - Kingsley M rebooting the OIT and directed to disregard the Historian Heartbeat alarm. | All Water System ROC General | 2026-01-12
ROC | January | STETBR - Tower level hi alarm. Placed STW12 and STW3 in auto mode. | All Water System ROC General | 2026-01-11
ROC | January | KSETWB - Jackie S testing chlorine gas leak alrm | All Water System ROC General | 2026-01-07
ROC | January | NMMCAD- Comm alarms came in. Reset alarms | All Water System ROC General | 2026-01-08
ROC | January | AUW14- Joe D and Donald M onsite working on Chlorine System and changing cylinders. | All Water System ROC General | 2026-01-09
ROC | January | AUW14- Donald M requested CMU5 for chlorine repair. W11576189 CMU5 AUETAD- Donald M requested CMU5 for analyzer issue. W11576212 for Donald M W11576219 for Eric S CMU5 | All Water System ROC General | 2026-01-09
ROC | January | MARS - Cell 1 level hi alarm. Activated VNRSKS duty 1 to drawdown MARS. | All Water System ROC General | 2026-01-11
ROC | January | QVW12 - Tyler ZJ working on pump 1 VFD. Disregard alarms for the duration of the work. | All Water System ROC General | 2026-01-07
ROC | January | Adeela Khan signing out | All Water System ROC General | 2026-01-12
ROC | January | MKRSEM- Talha done work on OIT historian heartbeat alarm cleared QVW12- Influent free Cl2 hi alarm alarm cleared after 3 mins | All Water System ROC General | 2026-01-08
ROC | January | BVPS- Tyler S on site to rebuild P2. NBW3- Influent free Cl2 lo alarm came in on well start up. Recovered after 3 mins alarm cleared NMETIB- Activated D1 | All Water System ROC General | 2026-01-08
ROC | January | NMVCBA - Placed valve in manual at 40 L/s 00:20 - Placed valve back to auto | All Water System ROC General | 2026-01-12
ROC | January | ARPS- Martin from OCWA called. He will be switching pumps over from Pump 3 to pump 7. | All Water System ROC General | 2026-01-09
ROC | January | STW3 - Placed well in auto mode. | All Water System ROC General | 2026-01-12
ROC | January | VNRSKS/KLPSWL/SHETCS/VNETFD- Historian heart beat alarms came in on all sites. Notified Artour L created CMU5 W11577145 #CMU5 | All Water System ROC General | 2026-01-09
ROC | January | AUW14, Placed wells 1/2/3/4 man/on for Joe D as he is heading to site and will be taking samples | All Water System ROC General | 2026-01-07
ROC | January | BLETNL - Sean from town of Stouffville flushing in Ballantrae | All Water System ROC General | 2026-01-07
ROC | January | BVPS - Electrical crew from Toronto water on site to replace UPS, notified Tyler CS, he is on site. | All Water System ROC General | 2026-01-08
ROC | January | NMW12 - Alex B cleaning turbidity meter and chlorine analyzers. | All Water System ROC General | 2026-01-08
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-09
ROC | January | STW12- Kingsley M working on OIT. Disregard historian heartbeat alarm until done 11:08- STW12- Kingsley M done working on OIT | All Water System ROC General | 2026-01-09
ROC | January | MTW3- Placed well 3 in man/off for PCS work | All Water System ROC General | 2026-01-09
ROC | January | RHPSPA, Travis W/Dan Z on site, running gen and doing pump tests with health and safety alarm tests KSTKWP, Jerry Z on site cleaning Cl2 analyzers | All Water System ROC General | 2026-01-13
ROC | January | STETBR/STETTL- Travis from town of Stouffville is flushing in zone 1,2 and 3 | All Water System ROC General | 2026-01-09
ROC | January | KSSP - Collection blower 2 high diff pressure alarm. Checked site, collection blower duty rotated to blower 1, operations appear normal. Unable to reset alarm. Sent email to OCO to check the blower today during their site visit. *Wrong book* | All Water System ROC General | 2026-01-11
ROC | January | NMETIB - Combined chlorine hi. Checked site, tower is draining. Trending shows that the combined chlorine is higher than normal. Will monitor system. | All Water System ROC General | 2026-01-11
ROC | January | Adeela Khan signing in. Weather: -1C and Cloudy | All Water System ROC General | 2026-01-12
ROC | January | GWTP - Make up Air unit 1 Coil Low temp alarm. Stephen B requested disregard alarm until Monday. # Consult | All Water System ROC General | 2026-01-10
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-11
ROC | January | NMW136 - Station Turbidity Hi alarm came in. Checked site. Well is not running and water is not being directed to users. | All Water System ROC General | 2026-01-12
ROC | January | KLW34 - Evgeny S restarting OIT. disregard heartbeat alarm | All Water System ROC General | 2026-01-13
ROC | January | ANW23 - Two High lift pumps assigned to duty 2, reassigned duty. | All Water System ROC General | 2026-01-09
ROC | January | HLPSYS - Outstanding Generator Fault alarm from last night. Spoke to Jacob M. who directed to call Dan B. Called Dan B. and explained that Jacob M. went to site last night but was unable to fix the generator fault alarm. Dan B will speak to Jacob M and will head to site. 09:21 - Dan called to inform that he is headed to site. CMU5 Created W11577243 12:10 - Dan B. called to inform that he is finished on site and that he was able to complete a successful transfer test and the fault has cleared #CONSULT #CMU5 | All Water System ROC General | 2026-01-10
ROC | January | GWTP - Permeate turbidity fault on multiple trains. Informed Patrick F, is aware of work on those lines and will follow-up. Disregard for now | All Water System ROC General | 2026-01-12
ROC | January | YWS + NYWS normal | All Water System ROC General | 2026-01-12
ROC | January | NBET - Talha rebooting the OIT. Placed the active wells in manual mode to prevent well deactivation while the reboot is completed. | All Water System ROC General | 2026-01-12
ROC | January | STW3- Joe M on site to work on NTU and Cl2 analyzers | All Water System ROC General | 2026-01-08
ROC | January | SHTP- Power loss on site. OPs ack all alarms and cleared SHETCS- UP power supply loss alarm came in OPs cleared alarms | All Water System ROC General | 2026-01-09
ROC | January | STETBR - Dan Z deep cycling tower to 40% FCV manual 20%. Dan Z. Man close FCV and put pumps back in auto after deep cycle | All Water System ROC General | 2026-01-13
ROC | January | QVW12, Joe W on site, working on the CL17 analyzers | All Water System ROC General | 2026-01-13
ROC | January | YWS+NYWS normal Adam Button signing out | All Water System ROC General | 2026-01-09
ROC | January | ANW23 - Power restored. | All Water System ROC General | 2026-01-10
ROC | January | Jefferson to AURSBS, Placed MV3 in manual and slowly opened the valve. opened valve from 10% to 30%. Mainly doing this to fill AURSBS and not have to rely on MARS as it is currently quite low at the moment MAPS PD8, Placed pumps 1-4 man/off so they don't start up | All Water System ROC General | 2026-01-08
ROC | January | Angelica Chepiga signing in, weather +2C | All Water System ROC General | 2026-01-08
ROC | January | NBW5 - Pump 5 uncommanded stop alarm. Duty activated recently, well 5 pump was running for 10 minutes. Cleared alarm and restarted well 5. Will monitor. | All Water System ROC General | 2026-01-09
ROC | January | VNPS- Tim H heading to site to run generator under load work on analyzers NBET- Talha H working on OIT disregard historian heartbeat until done 9:00- NBET- Talha H done working on OIT | All Water System ROC General | 2026-01-08
ROC | January | VNPS PD8- P3 valve failed to open alarm came in as pump tried to start up while placing in auto but was in D3 status with D3 not active. alarm cleared as acknowledged | All Water System ROC General | 2026-01-08
ROC | January | VNETAG/VNPSAP - Talha H working on the OIT at . Please disregard HRBT alarm | All Water System ROC General | 2026-01-08
ROC | January | MTW12 - Sean P onsite for generator load test | All Water System ROC General | 2026-01-12
ROC | January | NMVCBA- back to auto. | All Water System ROC General | 2026-01-10
ROC | January | NMETIB - Activated D 1 to offset with NMETHW | All Water System ROC General | 2026-01-10
ROC | January | MKRSEM - Request TO (Peter) to run 2 pumps | All Water System ROC General | 2026-01-13
ROC | January | VNPS- Tim H req PD7 pumps to run. Placed P2/3 in auto MAPS PD7- Placed P1-4 in man/off VNRSKS/JFRS- Activated D1 | All Water System ROC General | 2026-01-08
ROC | January | Adeela Khan signing out | All Water System ROC General | 2026-01-13
ROC | January | MKRSEM - Requested Toronto water (Brett) to stop pumps. | All Water System ROC General | 2026-01-10
ROC | January | VNRSKS - Activated duty 1 | All Water System ROC General | 2026-01-10
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-10
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-10
ROC | January | VNRSKS - Swapped supply pumps to two MAPS pumps. | All Water System ROC General | 2026-01-12
ROC | January | GWTP - Activated duty 1 as per Stephen B. | All Water System ROC General | 2026-01-11
ROC | January | KSTP - FIn water fluoride res hi alarm. Checked site, plant recently activated to fill the system. Trending shows a spike on start up that returned to normal range. Reset alarm. | All Water System ROC General | 2026-01-11
ROC | January | Ethan Ullalkar signing out. | All Water System ROC General | 2026-01-13
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-13
ROC | January | NMETIB - Deactivated duty 1. NMVCBA/NMVCIB - Reverted setpoint changes made previously. | All Water System ROC General | 2026-01-13
ROC | January | GWTP - Sulphonator 5 solenoid valve fail to close alarm. Checked site, all sulphonators in auto are showing as not active. Able to clear alarm. | All Water System ROC General | 2026-01-14
ROC | January | MARS - Valve house free Cl2 resi hi. Notified Tim H. a grab was taking earlier today already will look into issue but disregard for now | All Water System ROC General | 2026-01-14
ROC | January | MKRSEM - Request TO (Peter) to put 2 pumps on | All Water System ROC General | 2026-01-12
ROC | January | Carter Dunn Signing In | All Water System ROC General | 2026-01-07
ROC | January | STETTL, Activated D1, Joe M doing sampling for the area | All Water System ROC General | 2026-01-07
ROC | January | YWS + NYWS Normal AURSBS - Deactivated duty 1 | All Water System ROC General | 2026-01-10
ROC | January | MARS - Low levels. deactivated duty 1 at MAPS PD8 17:35 - Due to low levels at MARS, placed MAPS PD7 pump 1 in manual and placed pump 3 at VNPS PD7 into auto to help slow the drain of MARS | All Water System ROC General | 2026-01-10
ROC | January | NMVCBA - back to auto. | All Water System ROC General | 2026-01-11
ROC | January | KSTP - Raw water turbidity fault , disregard as per shift report. | All Water System ROC General | 2026-01-11
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-12
ROC | January | YWS + NYWS Normal Christian Van Beek signing out. | All Water System ROC General | 2026-01-11
ROC | January | AURSBS - Post Injection Free Ammonia HiHi alarm came in. Checked site. Chemical system is not running and duty deactivated recently. Will continue to monitor site 00:35 - Free ammonia level went back to optimal range and alarm cleared | All Water System ROC General | 2026-01-12
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-14
ROC | January | GWTP - Makeup Air Unit 1 Coil Low temp and Chemical Room Gas Level fault alarms came in. Spoke to Patrick F. who informed the chemical fault is because of the sodium bisulfite delivery and the makeup air unit alarm is because a door was left open. GWTP - Multiple communication alarms came in for the low lift building for pumps 1,2,3. Patrick F. called to inform that contractors are on site and they depowered pumps 3 and 4. Patrick will try to clear alarms | All Water System ROC General | 2026-01-14
ROC | January | MARS - High level alarm. Activated VNRSKS duty 1. | All Water System ROC General | 2026-01-14
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-09
ROC | January | BVPS - Deactivated duty 1 | All Water System ROC General | 2026-01-12
ROC | January | Christian Van Beek signing in. Weather: -3C and clear. | All Water System ROC General | 2026-01-12
ROC | January | Ethan U signing in Weather 2. | All Water System ROC General | 2026-01-07
ROC | January | Carter Dunn Signing Out | All Water System ROC General | 2026-01-07
ROC | January | STW12 - Place wells man/on STW3 - Place well man/on | All Water System ROC General | 2026-01-07
ROC | January | YWS + NYWS NORMAL | All Water System ROC General | 2026-01-09
ROC | January | MAPS PD7- P3 discharge valve 1 uncm close alarm on pump start up reset alarm | All Water System ROC General | 2026-01-08
ROC | January | YWS + NYWS NORMAL Angelica Chepiga signing out | All Water System ROC General | 2026-01-10
ROC | January | RHRSTR - Activated duty 1. | All Water System ROC General | 2026-01-11
ROC | January | Ethan Ullalkar signing out. | All Water System ROC General | 2026-01-07
ROC | January | NMETIB - Total Chlorine Hi alarm came in. Checked site. Tower is draining. Total chlorine levels are higher than normal. Will continue to monitor site 20:28 - Combined Chlorine Hi alarm came in. Levels are higher than normal. Will continue to monitor 20:49 - Both combined and total chlorine levels are rising. Suspected analyzer issue. Called Jason G. who directed to monitor site and give him a call back if levels start reaching 3.85 mg/L 21:13 - Levels kept rising. Called Jason G. who is headed to site. CMU5 created W11577489 21:49 - Jason G. called back to inform that he is finished on site. Jason informed that he took grab samples and they were all within range. There seems to be an issue with the analyzer, and he will get instrumentation to take a look tomorrow. Jason informed that because he took grab samples, if the levels go above 4 again, it is not a real reading. #CONSULT #CMU5 | All Water System ROC General | 2026-01-11
ROC | January | MKRSEM - Request TO (Peter) to drop 2 pumps | All Water System ROC General | 2026-01-08
ROC | January | GWTP- ZW3 membrane tank level hi alarm came in notified Stephen B. Will take a look on SCADA once Network on call troubleshoots Stephens Bs tablet 16:25- GWTP- Stephen B directed to disregard alarm as it will clear once done neutralizing and membrane drains. Stephen B directed to place train back online once done Rclean sequence in roughly 30 mins. #consult | All Water System ROC General | 2026-01-09
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-11
ROC | January | Angelica Chepiga signing in, weather 0C | All Water System ROC General | 2026-01-07
ROC | January | Angelica Chepiga signing out | All Water System ROC General | 2026-01-08
ROC | January | AUETAD, Total/combined Cl2 Lo alarm, Trends show a exponential drop, activated D1 so flow can go to the tower. If residuals dont start recovering after the duty is activated, will contack operator 20:18, After 5 minutes with the duty active, no recovery has happened, contacted Jason G, says to wait another 20 minutes for recovery however if residual doesn't recover, he would like a call 20:37, Contacted Jason G as requested, informed him that the residual has continued to drop but is holding at its current level, Jason G will open up SCADA to monitor, if residual gets to .40mg/L, he would like a call 21:12, Jason G followed up with the ROC. Tower is currently holding its residual at this time. If the residual drops down to .30mg/L when the tower is either filling or draining, Jason G wants to be notified and will head to site. RO will continue to monitor the tower to make sure it doesn't hit those residuals consult | All Water System ROC General | 2026-01-08
ROC | January | NMMCAD- Ton valve chamber flood alarm came in. Notified Graham at the town of Newmarket of alarm as per interim | All Water System ROC General | 2026-01-09
ROC | January | MKPSSA- Kingsley M working on OIT disregard historian heartbeat alarm BLETNL- Tower level lo alarm East Water team deep cycling tower | All Water System ROC General | 2026-01-08
ROC | January | NRETCR- Doanld M on site to work on Cl2 analyzers and test hi lo temp alarm | All Water System ROC General | 2026-01-08
ROC | January | AURSBS, Activated D1 | All Water System ROC General | 2026-01-09
ROC | January | RHRSTR, Deactivated D1 | All Water System ROC General | 2026-01-07
ROC | January | YWS + NYWS NORMAL | All Water System ROC General | 2026-01-10
ROC | January | YWS + NYWS NORMAL | All Water System ROC General | 2026-01-11
ROC | January | VNRSKS - Swapped supply pumps to two MAPS pumps. | All Water System ROC General | 2026-01-11
ROC | January | AUW14, Placed wells 1/4 in man/on to help drain the res slower | All Water System ROC General | 2026-01-08
ROC | January | GWTP- Train 1 shutdown on turbidity hihi alarm. Notified Patrick F. Will take a look on site. Patrick F is working on train 3, cleaning NTU analyzers, Chem pump maintenance and will be testing Cl2 leak detection alarm MKRSEM- Talha working on OIT disregard historian heartbeat until done BLETNL- Sean from town of Whitchurch and Stouffville called to notify ROC that they will be flushing in system | All Water System ROC General | 2026-01-08
ROC | January | SHTP- Jake M on site testing eye washes and working on KMNO systems, UV systems and running generator. | All Water System ROC General | 2026-01-08
ROC | January | KSETWB- Ian W rebooting OIT disregard historian heartbeat alarm until done | All Water System ROC General | 2026-01-08
ROC | January | QVW34- Alex B and Will M on site for cylinder change had a slight Cl2 leak but are okay | All Water System ROC General | 2026-01-08
ROC | January | STPSTL- P1 discharge flow lolo alarm came in. Both towers near D1 start STETTL- Activated D1 @ 63% STW12- Placed P1/2 in man/on as per interim STW3- Placed P3 in man/on as per interim | All Water System ROC General | 2026-01-08
ROC | January | Christian Van Beek signing in. Weather: 1C and clear. | All Water System ROC General | 2026-01-13
ROC | January | MAPS PD7, Placed pumps man/off VNPS PD7, Placed pumps 2/3 in auto | All Water System ROC General | 2026-01-07
ROC | January | NMETIB- NMETIB to NMW15 comm alarm came in. Trends okay reset alarm MTW3- Kingsley restarting OIT. Disregard historian heartbeat alarm until done | All Water System ROC General | 2026-01-09
ROC | January | NMETIB - Activated duty 1 to help offset with NMETHW | All Water System ROC General | 2026-01-13
ROC | January | MARS, TMC 317 - Peter from Toronto Water completed test, flow back to one small pump. | All Water System ROC General | 2026-01-08
ROC | January | VNETAG, VNPSAP - Talha H completed work. Alarms cleared. | All Water System ROC General | 2026-01-08
ROC | January | NMETHW- Jay G on site to test eyewash station | All Water System ROC General | 2026-01-08
ROC | January | RHRSTR, Activated D1 to get flow moving to MARS | All Water System ROC General | 2026-01-07
ROC | January | KCETDS, Lee F is finished on site | All Water System ROC General | 2026-01-07
ROC | January | AUW14 - Lee F finished on site, placed Pump 4 back to auto. | All Water System ROC General | 2026-01-07
ROC | January | AUPSRR - Post inj free chlorine HiHi alarm at duty start, quick spike,cleared. | All Water System ROC General | 2026-01-07
ROC | January | NMETHW -David ETO engineering onsite for Vibration monitoring | All Water System ROC General | 2026-01-13
ROC | January | SHTP, Jacob M on site, running the generator and testing the actuator valves | All Water System ROC General | 2026-01-13
ROC | January | AUW14, Joe D on site, placing wells man/off, working on the CL2 analyzers and turbidity analyzer and running the generators | All Water System ROC General | 2026-01-13
ROC | January | STETTL, Talha resetting OIT on site | All Water System ROC General | 2026-01-13
ROC | January | Ethan Ullalkar signing out. | All Water System ROC General | 2026-01-14
ROC | January | STW12 - Place wells back in auto STW3 - Place well back in auto | All Water System ROC General | 2026-01-08
ROC | January | GWTP - Stephen B called back to inform his troubleshooting failed resulting in turbidity fault alarms. Stephen directed to place the UV system manual off to prevent the GWTP from activating until he can attend site. Stephen also directed to activate system duty at 50% | All Water System ROC General | 2026-01-11
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-11
ROC | January | STW12 - Travis W taking he wells OOS until a hypo delivery can be completed. | All Water System ROC General | 2026-01-12
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-15
ROC | January | NMW136 - Alex B. is on site and will be completing pm's for the Turbidimeters, and all the chlorine analyzers | All Water System ROC General | 2026-01-14
ROC | January | Angelica Chepiga signing in,weather +2C | All Water System ROC General | 2026-01-09
ROC | January | HLPSYS - Site power failure, generator running status. All pumps interlocked, not able to clear alarm. Jacob M will check SCADA. Power restored when on the phone with Jacob M. Cleared all alarms. # Consult HLETYS - Site power failure, PAC control failure alarm. All alarms cleared. Trends ok. | All Water System ROC General | 2026-01-09
ROC | January | AUETFC- Joe D on site testing eyewashes and hi lo temp alarm | All Water System ROC General | 2026-01-08
ROC | January | AURSBS, Deactivated D1 | All Water System ROC General | 2026-01-08
ROC | January | MKRSEM - Called Toronto Water (Zoran) and requested they deactivate the pumps pushing flow to MKRSEM. | All Water System ROC General | 2026-01-15
ROC | January | NRETCR- Donald M done on site changed it to controlling tower and will ensure altitude valve is still working | All Water System ROC General | 2026-01-08
ROC | January | NMETIB - Deactivated duty 1 to help offset with NMETHW | All Water System ROC General | 2026-01-14
ROC | January | YWS + NYWS Normal Christian Van Beek signing out. | All Water System ROC General | 2026-01-12
ROC | January | MAP7 - Place pump 1,2 & 4 man/off VNP7 - Place pump 3 auto | All Water System ROC General | 2026-01-14
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-12
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-15
ROC | January | GWTP, Raw Water Sample Pump 1/2/3 // Low Lift Drainage Pump 1/2 E stop Alarm, Patrick F on site with contractors. Lexan (contractor cut the power causing these alarms) | All Water System ROC General | 2026-01-13
ROC | January | Carter D Signing In, 1D/Clear | All Water System ROC General | 2026-01-13
ROC | January | AUW14 - Joe D onsite for sampling will be running 4 wells in man/on | All Water System ROC General | 2026-01-14
ROC | January | VNRSKS - Swapped supply pumps to two MAPS pumps. | All Water System ROC General | 2026-01-14
ROC | January | HLETYS - Post-injection combined chlorine hi. Informed David T, will look into issue | All Water System ROC General | 2026-01-14
ROC | January | BVPS, Artour L on site, working with electricians. testing pump start/stops and running the generator | All Water System ROC General | 2026-01-13
ROC | January | NMTKKC - Jason G onsite working on analyzers, flood test, and temp alarm. Chem pump off fore work while filling | All Water System ROC General | 2026-01-13
ROC | January | MAPS PD7- Placed P1/2 in auto JFRS- Activated D2 | All Water System ROC General | 2026-01-08
ROC | January | NMETIB, Placed valve man/open and set flow to 40L/sec | All Water System ROC General | 2026-01-08
ROC | January | JFPS - WPS Pump 4 fault. 3 pumps available for the night. Informed Ryan B. disregard for the night Consult | All Water System ROC General | 2026-01-14
ROC | January | HLETYS - Post-injection combined chlorine lo. Informed Jordan B, rotated hypo pump 2 to duty 1. Will deactivate duty 1 if continue to drop in reading as per Jordan B. Consult | All Water System ROC General | 2026-01-14
ROC | January | Christian Van Beek signing in. Weather: -3C and clear. | All Water System ROC General | 2026-01-14
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-14
ROC | January | YWS + NYWS Normal Adeela Khan signing out | All Water System ROC General | 2026-01-14
ROC | January | HLETYS - Post injection combined chlorine low alarm. Residual reading is not recovering, deactivated duty 1 as per Jordan B. | All Water System ROC General | 2026-01-14
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-15
ROC | January | MARS, TMC 317 - Peter from Toronto water testing big pump for 20 minutes. | All Water System ROC General | 2026-01-08
ROC | January | NBET27- Historian heartbeat alarm came in. Notified Artour L will take a look on SCADA | All Water System ROC General | 2026-01-09
ROC | January | MAPS PD8 - pump 1 failed to start and discharge valve failed to open alarm. Checked site, duty recently activated. Duty 1 rotated to pump 3 which started. | All Water System ROC General | 2026-01-14
ROC | January | STETBR- Tower hi level came in STW12/3- Placed wells back in auto as per interim | All Water System ROC General | 2026-01-09
ROC | January | ANW23 - Generator running on site. Checked Hydro one site, crew working in the area, notified Jacob M as requested. Site looks normal. Will monitor. | All Water System ROC General | 2026-01-09
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-10
ROC | January | STETBR - Duty 1 almost complete. Placed STW12 and STW3 in auto mode. | All Water System ROC General | 2026-01-14
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-14
ROC | January | KSETWB - Combined inlet chlorine out of range alarm. Checked site, outlet and header chlorine analyzers are operating normally. Inlet analyzer alarms are disregards on the shift report. | All Water System ROC General | 2026-01-14
ROC | January | NMMCBA- Placed valve in man/open at 40 L/s | All Water System ROC General | 2026-01-09
ROC | January | Ethan U signing in Weather 4. | All Water System ROC General | 2026-01-14
ROC | January | STPSMR- Travis W onsite for health and safety work orders. | All Water System ROC General | 2026-01-09
ROC | January | NMW136- Station turbidity hi alarm came in. Wells not active no water directed towards users. Will continue to monitor | All Water System ROC General | 2026-01-09
ROC | January | NBW3 - Influent free chlorine lolo alarm. Checked site, well recently activated to fill the system. Trending shows the influent free chlorine reading dipped on well activation and then recovered. Rotated duty 1 back to hypo pump 2 and cleared alarms. Monitored well activation. | All Water System ROC General | 2026-01-12
ROC | January | NMETIB - Talha working on OIT, disregard heartbeat alarm | All Water System ROC General | 2026-01-12
ROC | January | KLW34 - Benson S onsite for a chlorine leak detection test. | All Water System ROC General | 2026-01-12
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-11
ROC | January | NMETHW - Deactivate duty 1 | All Water System ROC General | 2026-01-12
ROC | January | MAPS PD7/8, Tim H on site, running generators and testing pumps KBSP, Lauren S on site working on the air compressors | All Water System ROC General | 2026-01-13
ROC | January | BLW3 - Phil D onsite for chlorine analyzer, silicate injection point, chlorine system for booster pump, NTU maintenance, generator test tun and scrubber W/O | All Water System ROC General | 2026-01-13
ROC | January | AURSBS - Deactivated Duty 1 to help with MARS level recovery. | All Water System ROC General | 2026-01-10
ROC | January | NBET - OIT reboot completed, placed well pumps in auto. | All Water System ROC General | 2026-01-12
ROC | January | HLPSYS - PAC Control panel power failure alarm, site power failure, generator fault alarms.2plus pumps not available. Checked Hydro one website. Power outage in the area. Notified Jacob M. He will check SCADA. HLETYS - Pac Control panel power failure, site power failure, Post-injection Combine chlorine low alarms. Jacob M will check SCADA. #Consult and CMU5 W11577192 EGMCRW - PAC control panel power failure. Power outage in the area. | All Water System ROC General | 2026-01-09
ROC | January | HLETYS - Power restored, all alarms cleared. EGMCRW - Power restored. HLPSYS - Power restored, Generator fault alarm outstanding. Notified Jacob M. He is on his way to site. | All Water System ROC General | 2026-01-09
ROC | January | HLPSYS - Jacob M on site, he spoke with Stephen B and ok to leave Generator fault alarm outstanding until morning. Requested to call Dan B first thing in the morning. Jacob M leaving site. | All Water System ROC General | 2026-01-10
ROC | January | YWS + NYWS Normal Adeela Khan signing out | All Water System ROC General | 2026-01-10
ROC | January | GWTP - Make up air unit 1 Coil low temp alarm. Notified Stephen B. Requested disregard alarm for the night. He will attend site tomorrow morning. # Consult | All Water System ROC General | 2026-01-09
ROC | January | Carter D Signing Out | All Water System ROC General | 2026-01-09
ROC | January | ANW23, Stephen B on site, running generator and working on the analyzers NBSP, Gavin W working on the dewatering screws/bar screen and vortex equipment, directed to disregard alarms from headworks till he is finished | All Water System ROC General | 2026-01-13
ROC | January | HLW1- Silicate Pump 2 Uncommanded Stop Alarm. Pump 1 took over in duty 1. Cleared alarm. | All Water System ROC General | 2026-01-09
ROC | January | KSETWB - Inlet combine chlorine OOR, Duty not active. Will send email Stephen B. | All Water System ROC General | 2026-01-10
ROC | January | YWS + NYWS NORMAL | All Water System ROC General | 2026-01-10
ROC | January | BLW12 - Phil D onsite working on NTU and both chlorine analyzer | All Water System ROC General | 2026-01-12
ROC | January | NMETIB - Activated duty to keep level offset from NMETHW | All Water System ROC General | 2026-01-11
ROC | January | AURSBS - Post injection free ammonia hihi alarm. Checked site, chemical system is not running and reservoir is neither filling nor draining. Trending shows a small increase of the post injection free ammonia reading. Will monitor site. | All Water System ROC General | 2026-01-11
ROC | January | BVPS, Kyle R simulating a power outage | All Water System ROC General | 2026-01-13
ROC | January | MARS - TMC317 Mahdi from Toronto water called, Pump 4 failed, Mahdi restarting Pump 6 , same flow. | All Water System ROC General | 2026-01-07
ROC | January | BLW3 - Phil D running generator | All Water System ROC General | 2026-01-13
ROC | January | NMW12, Alex B is on site, trouble shooting the interlock that locked out the wells | All Water System ROC General | 2026-01-07
ROC | January | GWTP - Stephen B heading to site shortly. Created CMU5#W11577453 #CMU5 | All Water System ROC General | 2026-01-11
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-11
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-13
ROC | January | AUW57 - Influent free chlorine LoLo alarms, Well 5 pump man/off, no water directed to users.? | All Water System ROC General | 2026-01-11
ROC | January | STETBR - Placed STW12 and STW3 pumps man/on for ET fill cycle. | All Water System ROC General | 2026-01-10
ROC | January | Connor Smith signing in 3C Rainy | All Water System ROC General | 2026-01-09
ROC | January | NMETIB- Activated D1 to offset from NMETHW | All Water System ROC General | 2026-01-09
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-07
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-07
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-08
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-08
ROC | January | NMVCBA - Changed valve setpoint from 40L/s to 80L/s while both NMETIB and NMETHW fill. NMVCIB - Changed valve setpoint from 80L/s to 20L/s while both NMETIB and NMETHW fill. | All Water System ROC General | 2026-01-13
ROC | January | VNRSKS - Swapped supply pumps to two MAPS pumps. | All Water System ROC General | 2026-01-13
ROC | January | ANW23- Generator Running Status Alarm HLPSYS- Pump 4 Fault Alarm Notified Jacob M. He will confirm if needs to attend site. | All Water System ROC General | 2026-01-09
ROC | January | AUPSWS - Intrusion alarm, FMC will notify Corp. security. | All Water System ROC General | 2026-01-09
ROC | January | MKRSEM - Requested Toronto water (Brett) start filling Res with 2 pumps. | All Water System ROC General | 2026-01-09
ROC | January | STW12 and STW3 pumps back to auto. | All Water System ROC General | 2026-01-10
ROC | January | Adeela Khan signing in. Weather: -5 and Windy | All Water System ROC General | 2026-01-11
ROC | January | MTW3- Historian heartbeat alarm outstanding. Notified Kingsley M will take a look issue. Placed well in man/off | All Water System ROC General | 2026-01-09
ROC | January | Carter Dunn Signing In, 1D/Clear | All Water System ROC General | 2026-01-08
ROC | January | KCETDS - Lee F on site, checking leak on altitude valve. | All Water System ROC General | 2026-01-07
ROC | January | ANW23- Jake M called to inquire lo discharge pressure alarms that came in. High lift pump 2 was Inhibited with D1/2 running. Cleared alarms before ROC had time to investigate. No issues found pressure okay station still on generator. Jake M req call if power is not returned to utility power GWTP- Placed ZW3 in on and let prime. Once Priming sequence completed placed back in off and neutralization exceeded alarm cleared. Placed back in auto. Made changes as per Stephen B | All Water System ROC General | 2026-01-09
ROC | January | NBW3 - Effluent free chlorine Low alarm, well not running, no water directed to users?. | All Water System ROC General | 2026-01-09
ROC | January | GWTP - ZW3 Shutdown, ZW3 Maintenance Clean Aborted, Backpulse pump 2 not available and ZW3 BP Pump 2, Backpulse Flow LoLo alarms came in. Checked site. Called Stephen B. who will take a look on SCADA 10:41 - ZW1, ZW2, ZW3, ZW4, ZW8 Permeate Turbidity fault alarms came in. Stephen B. is looking into this. 11:20 - Stephen B. is headed to site. CMU5 for outstanding Make up Air Unit 1 Coil Low Temp alarm W11577254 Stephen also requested a CMU5 for Permeate turbidity faults CMU5 created W11577261 12:01 - GWTP - ZW4 Shutdown and Maintenance clean aborted alarms came in. Called Stephen B. who is on site but no answer. Will try again 12:05 - Stephen cleared the alarm 13:42 - Stephen B. called back to inform that he us having trouble with the Backpulse Tank 1 Fill Valve as there is an issue with the actuator. Stephen directed to leave the Backpulse Tank Fill Valve Uncommanded open alarm outstanding. He will have maintenance take a look at it on Monday. 14:13 - Stephen is leaving site #Consult #CMU5 | All Water System ROC General | 2026-01-10
ROC | January | NMVCIB - flow setpoint from 80 to 40l/s NMVCBA - flow setpoint from 40 to 80l/s | All Water System ROC General | 2026-01-10
ROC | January | NMETIB - Deactivated Duty 1 to offset with NMETHW. NMVCIB - flow setpoint from 40 to 80l/s NMVCBA - flow setpoint from 80 to 40l/s | All Water System ROC General | 2026-01-10
ROC | January | YWS + NYWS NORMAL | All Water System ROC General | 2026-01-11
ROC | January | Adam Button signing out YWS+NYWS normal | All Water System ROC General | 2026-01-08
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-08
ROC | January | SHETCS - Cole W on site working on hypo pump 1. May see associated alarms. | All Water System ROC General | 2026-01-12
ROC | January | Angelica Chepiga signing in, weather +2C | All Water System ROC General | 2026-01-10
ROC | January | YWS + NYWS NORMAL | All Water System ROC General | 2026-01-10
ROC | January | YWS + NYWS Normal VNPS - Noted all pumps in manual mode. Placed pumps in auto mode. | All Water System ROC General | 2026-01-11
ROC | January | NMW12 - Station turbidity Hi alarm , received alarm just before duty deactivated. Pumps off, no water directed to users.? | All Water System ROC General | 2026-01-10
ROC | January | MARS/JFRS - Maple to Jefferson feed complete. | All Water System ROC General | 2026-01-11
ROC | January | VNRSKS - Swapped supply pumps from two MAPS pumps to one VNPS and one MAPS pump. | All Water System ROC General | 2026-01-11
ROC | January | NMW136 - Silicate pump 1 fault and uncommanded stop alarm. Checked site, well recently activated. Silicate pump duty rotated to pump 2 which is operating normally Reset alarms. | All Water System ROC General | 2026-01-14
ROC | January | KSETWB - Ian W working on PAC panel wiring. | All Water System ROC General | 2026-01-07
ROC | January | GWTP - Makeup Air Unit 1 Low Temp critical alarm from earlier. Called Stephen B. again who directed to disregard alarm for the night and he will let property services take a look tomorrow. STW12 and STW3 - Stephen B. also directed to place well 2 and 3 into man/on #CONSULT | All Water System ROC General | 2026-01-11
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-11
ROC | January | MARS- Cell1 (North) Lvl Lo Alarm. VNRSKS- Deactivated duty | All Water System ROC General | 2026-01-09
ROC | January | KCETDS - Activated D1. | All Water System ROC General | 2026-01-10
ROC | January | NMVCBA - man/open 40l/s to extend NMETIB drain cycle. | All Water System ROC General | 2026-01-10
ROC | January | NMTKKC - Header free CL2 hihi, flow leaving is really low not triggering chemical system to run. Informed Jason G who just got to site, will look into issue | All Water System ROC General | 2026-01-12
ROC | January | GWTP - Sutton Header fluoride Hi alarm. SUETDR duty just deactivated, no flow. | All Water System ROC General | 2026-01-10
ROC | January | AURSBS - Chlorinator 1 vlv failed to open at duty stop. Alarm cleared. | All Water System ROC General | 2026-01-08
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-14
ROC | January | Christian Van Beek signing in. Weather: -2C and clear. | All Water System ROC General | 2026-01-11
ROC | January | HLW2 - Combined Chlorine Lo and Treated Total Chlorine Lo alarms came in. Well is local/off for rehab and is not being directed to users | All Water System ROC General | 2026-01-11
ROC | January | NMW12 - Alex B on site to complete troubleshooting on the silicate system. | All Water System ROC General | 2026-01-12
ROC | January | BVPS - Travis W on site to activate duty and inspect pump 4. | All Water System ROC General | 2026-01-12
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-12
ROC | January | KLET27 - Talha H rebooting OIT. | All Water System ROC General | 2026-01-12
ROC | January | Angelica Chepiga signing out | All Water System ROC General | 2026-01-11
ROC | January | GWTP- Neutralization exceeded duration alarm came in. Tank draining. Notified Stephen B. Directed to place in auto once train has drains and filled back up to 2.2m, let prime and place back in off position to clear alarm if it does not clear alarm. Stephen B directed to try this 2 times to see if train will clear alarm. STETBR- Stephen B called directed to activate D1 and place STW12/3 in manual (already running) #consult | All Water System ROC General | 2026-01-09
ROC | January | Christian Van Beek signing out. | All Water System ROC General | 2026-01-14
ROC | January | Adeela Khan signing in | All Water System ROC General | 2026-01-14
ROC | January | Ethan Ullalkar signing out. | All Water System ROC General | 2026-01-12
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-12
ROC | January | NBW5 - High turbidity alarm outstanding. Placed well 5 pump man/off. | All Water System ROC General | 2026-01-11
ROC | January | MARS/JFRS - Initiated Maple to Jefferson feed. | All Water System ROC General | 2026-01-11
ROC | January | NMETHW - Activated duty 1 to help offset with NMETIB | All Water System ROC General | 2026-01-12
ROC | January | wrong book | All Water System ROC General | 2026-01-11
ROC | January | VNPS- Placed P2/3 in auto MAPS Placed P1/2 in man/off | All Water System ROC General | 2026-01-09
ROC | January | KSTP - CO2 Adjusted pH LoLo Alarm, value recovered and alarm cleared. | All Water System ROC General | 2026-01-10
ROC | January | YWS + NYWS NORMAL | All Water System ROC General | 2026-01-10
ROC | January | AUW14 - Joe D onsite testing flood and eyewash alarm | All Water System ROC General | 2026-01-13
ROC | January | Adeela Khan signing in. Weather: -1 and cloudy | All Water System ROC General | 2026-01-10
ROC | January | NMW12 - Influent Free Chlorine HiHi alarm came in. Checked site. Duty recently activated and wells just started up. After 5 mins, influent levels went back to optimal range and alarm cleared | All Water System ROC General | 2026-01-10
ROC | January | NBW5- Turbidity Hi alarm outstanding. Switched silicate pumps. Pump 1 to duty 1. | All Water System ROC General | 2026-01-11
ROC | January | BVPS - Deactivated duty 1 | All Water System ROC General | 2026-01-13
ROC | January | MKRSEM - Called Toronto Water (Peter) and requested to stop pumping to reservoir | All Water System ROC General | 2026-01-12
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-13
ROC | January | VNRSKS - Activated duty 1 | All Water System ROC General | 2026-01-13
ROC | January | RHRSWA - Deactivate duty 1 for Travis W who is onsite | All Water System ROC General | 2026-01-13
ROC | January | MAPS PD7, Placed pumps 1/2 back to auto VNPS PD7, Placed pumps 2/3 back to man/off | All Water System ROC General | 2026-01-13
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-13
ROC | January | GWTP - UV reactor 1 critical fault, normal power loss, lamp detected fault. Followed up with Patrick F & Jack P. Jack P is doing UV maintenance. Shutting down plant and draining UV 1 now in local off | All Water System ROC General | 2026-01-13
ROC | January | NMETIB, Deactivated D1 to allow NMETHW fill | All Water System ROC General | 2026-01-09
ROC | January | Ethan U signing in | All Water System ROC General | 2026-01-13
ROC | January | MKRSEM, Notified Toronto operator Paul to stop pumping to the res | All Water System ROC General | 2026-01-09
ROC | January | YWSS + NYWSS Normal | All Water System ROC General | 2026-01-09
ROC | January | SHETCS - Uncmdhypo pump 1 stop. Came in twice, infomred Jacob M. Is looking into issue, if it comes back will notify again of reoccurring issue | All Water System ROC General | 2026-01-12
ROC | January | AURSBS - Activated duty 1. | All Water System ROC General | 2026-01-14
ROC | January | NMW12 - Station turbidity hi alarm. Checked site, well is off no water being directed to users. trending shows a gradual increase of the turbidity reading, possible analyzer drift. Will monitor site to determine effect on operations when the well activates. | All Water System ROC General | 2026-01-14
ROC | January | AURSBS - GLCR 2 vvlv fail to open. Able to clear Chlorinator 1 pos dev (info) alarm, able to clear | All Water System ROC General | 2026-01-05
ROC | January | MAPS PD7 - Pump 2 uncommanded stop and pump 2 discharge valve uncommanded close. Checked site, pumps recently placed in auto to run. Cleared alarms after inhibit and monitored. | All Water System ROC General | 2026-01-05
ROC | January | MKPSSA - Generator stopped running | All Water System ROC General | 2026-01-06
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-06
ROC | January | Town of Stouffville - Lane from the Town of Stouffville called to inform that he will be flushing in zone 2 | All Water System ROC General | 2026-01-02
ROC | January | NBW3 - Influent free chlorine lolo alarm. Checked site, well recently activated in schedule mode. Trending shows a sudden dip of the influent free chlorine reading on well activation. Monitored site, influent free chlorine reading recovered. Rotated chlorine pump to the original pump and cleared alarms. Monitored well start. | All Water System ROC General | 2026-01-03
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-04
ROC | January | Vaughan - City of Vaughan (Nolan) called to inform of chamber leak @ Islington & Langstaff Rd E. Going South side of road towards river bend informed of decent amount of water noted coming from chamber, water is chlorinated as tested by Vaughan operator. Not impacting roads. Allpipes does show assets in area, followed up with Harsh P of situation. Harsh will head to site to investigate. Informed Roads to salt area as could be impacted by time operator attends site. CMU =11556935 14:58 - Nolan from City of Vaughan called back to inform appears water has runoff into river. They have informed SAC (1PZBW4W). No change in flow observed by them, equivalent of a 2in being blown off is what was descibed by their operator onsite. Informed Harsh P as well. 15:22 - Nolan called back with case number 17:22 - Harsh P called back, confirming leak behind drain valve after pumping down chamber. Will notify CPD and Ron V | All Water System ROC General | 2026-01-04
ROC | January | MKRSEM - Called Toronto Water and requested they deactivate the pumps pushing flow to MKRSEM. | All Water System ROC General | 2026-01-06
ROC | January | STETBR- Changed duty start from 60 to 45% to prevent duty from activating and taking water from Zone 2 while break repairs are ongoing. 21:00- Reverted duty change | All Water System ROC General | 2026-01-03
ROC | January | NMTKKC - Donald M. called to inform that he will be performing a hot flush on the chemical system and will be placing all of the chemical pumps man/off until flush is complete | All Water System ROC General | 2026-01-02
ROC | January | AURSBS - Deactivated duty 1. Confirmed with Will M. | All Water System ROC General | 2026-01-02
ROC | January | MAPS PD7, Placed pumps 1-4 man/off VNPS PD7, Placed pumps 2/3 in auto | All Water System ROC General | 2026-01-05
ROC | January | Christian Van Beek signing in. Weather: -9 and clear. | All Water System ROC General | 2026-01-05
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-06
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-02
ROC | January | QVW12 - Treated free chlorine hihi, well 1 just came on. monitored site, rotated ammonia pump 2 to duty 1 as well as TK2_MV1. Continued to monitor site. Residuals came within range next couple reading, cleared alarm | All Water System ROC General | 2026-01-04
ROC | January | VNRSKS - Swapped supply pumps to one VNPS and one MAPS pump to even the demand on MARS and RHRSTR. | All Water System ROC General | 2026-01-04
ROC | January | Christian Van Beek signing in. | All Water System ROC General | 2026-01-02
ROC | January | AUW14 - Influent Chlorine Lo alarm came in. Site has been running for some time. After 10 mins, levels came back to optimal range and alarm has cleared | All Water System ROC General | 2026-01-01
ROC | January | NBW3 - Silicate pump 1 fault alarm. Checked site, well is active. This is the second alarm for this silicate pump tonight. Placed silicate pump 1 manual/off and leaving alarm outstanding to prevent duty rotation. Sent email to area ops. | All Water System ROC General | 2026-01-04
ROC | January | NMW12- Station Turbidity Fault Alarm. Interlocked wells. Placed wells in manual and notified Jerry Z. 04:20- Cleared alarms and placed back into auto 04:40- Station Turbidity Fault Alarm came back in. Placed wells man/off. CONSULT | All Water System ROC General | 2026-01-02
ROC | January | NMETHW - Activated duty 1. | All Water System ROC General | 2026-01-02
ROC | January | ARPS, Martin from OCWA called, they are changing the reagents for the ammonia analyzers, they have people on site making sure everything is in compliance, analyzers should only be down for 15 minutes 08:51, Martin from OCWA called back, they are finished with the replacing of the reagents for the ammonia analyzers. Analyzer totals have come back to normal | All Water System ROC General | 2026-01-06
ROC | January | NBW37, Jordan B on site running the generator and working on the Cl2 analyzers QVW12, Mike B from property services is on site STW12, Joe M on site, working on the Cl2 analyzers, running generator and working on the turbidity analyzers | All Water System ROC General | 2026-01-06
ROC | January | BVPS- Dan Z on site with Dan B and Kyle R to troubleshoot generator work. Dan Z on site monitor BLW12/3- Kingsley rebooting OIT disregard historian heartbeat until done AUPSWS- Tyler S on site to work on P4. Req. P4 to be placed in D2 and P5 in D1. P2 failed to start. P4 started up. Confirmed with Tyler S. Placed P4 in manual. P5 started up in D1 | All Water System ROC General | 2026-01-06
ROC | January | AUW57, Joe D on site, working on the Cl2/Silicate system, directed to disregard alarms on site GWTP, UV Reactor 1/2 alarms, Pat F on site working on the UVs | All Water System ROC General | 2026-01-06
ROC | January | MKRSEM- Called Toronto (Mehdi) and requested pumps off. | All Water System ROC General | 2026-01-03
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-03
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-03
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-03
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-06
ROC | January | VNRSKS- Deactivated duty MAPS- Placed PD7 Duty 1 pumps in manual VNPS- Placed PD7 duty 1 pumps in auto 14:33- Noticed that MAPS PD7 Pumps were running in auto. Placed man/off | All Water System ROC General | 2026-01-01
ROC | January | NMETIB- Activated duty | All Water System ROC General | 2026-01-01
ROC | January | Connor Smith signing in -19 Cloudy | All Water System ROC General | 2026-01-01
ROC | January | VNRSKS- Deactivated D1 at 80% VNPS PD7 Placed P2/3 in manual MAPS- Placed P1/3 in auto | All Water System ROC General | 2026-01-01
ROC | January | STW12 - Place wells back in auto STW3 - Place well back in auto | All Water System ROC General | 2026-01-07
ROC | January | YWS+NYWS normal QVW12- Effluent free Cl2 hi alarm came in. Check trends looks like influent spiked resulting in delayed spike in effluent will continue to monitor | All Water System ROC General | 2026-01-01
ROC | January | YWS+NYWS normal | All Water System ROC General | 2026-01-02
ROC | January | YWS + NYWS normal | All Water System ROC General | 2026-01-01
ROC | January | SHTP - Raw water pump N/A, fire panel alarm. Power blip in area. Alarms cleared, generator not running | All Water System ROC General | 2026-01-06
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-03
ROC | January | NBET - Joe W. is on site and will be activating duty 1 | All Water System ROC General | 2026-01-02
ROC | January | QVW12 - treated free chlorine hihi and Combined chlorine low alarms. Checked site, well recently activated to fill the system. Trending shows a sudden spike of the treated free chlorine alarm and a drop of the combined chlorine alarms. Ammonia system is running, rotated ammonia pump duty to pump 2. Monitoring site. 14:32 - Treated free not dropping, noticed the ammonia tank level is not dropping as rapidly as it usually does when the ammonia pumps activate, rotated ammonia tank valves. Monitoring site. 14:34 - Treated free chlorine value is dropping, and combined chlorine value is rising. | All Water System ROC General | 2026-01-03
ROC | January | NBW3 - Influent free chlorine lolo, dip in reading before coming back up. Able to clear next reading | All Water System ROC General | 2026-01-05
ROC | January | KCETDS- Outlet Total CL2 Res LoLo Alarm. Analyzer dropped out but returned to normal after the next reading. Cleared alarm. | All Water System ROC General | 2026-01-04
ROC | January | AUPSRR - Post-inj free chlorine hihi, comb lolo. Reading came back within range next reading and able to clear alarm | All Water System ROC General | 2026-01-05
ROC | January | Ethan U signing in | All Water System ROC General | 2026-01-05
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-05
ROC | January | STW12- Joe M done on site directed to placed silicate pump setpoint back to auto | All Water System ROC General | 2026-01-06
ROC | January | AUPSRR - Post injection free chlorine hihi alarm. Checked site, trending shows a small spike of the post injection free chlorine that returned to normal range within one reading interval. Reset alarm. | All Water System ROC General | 2026-01-03
ROC | January | VNRSKS - Activate duty 1. | All Water System ROC General | 2026-01-06
ROC | January | AUPSWS- Tyler Z req P4 to run. Placed P5 in manual so it doesn't start on D1 activation VFD faults on site outstanding. Req Tyler S to reset before placing in D1. VFD alarms cleared activated D1 | All Water System ROC General | 2026-01-06
ROC | January | NMTKBS - Activated duty 1. | All Water System ROC General | 2026-01-03
ROC | January | GWTP- ZW5 Channel 1,2 Part Counts Out of Range. Disregard as per SCADA Report | All Water System ROC General | 2026-01-01
ROC | January | YWS+NYWS normal | All Water System ROC General | 2026-01-01
ROC | January | SHTP - Well 2 uncommanded start alarm came in. Checked site. Plant was shutting down and well 4 was running. Alarm was able to reset 09:03 - Alarm came in again. Plant was not running and alarm cleared. If this alarm comes in again, will reach out to West water team | All Water System ROC General | 2026-01-02
ROC | January | STW12/STW3 - Place wells in man/on as Bethesda is active | All Water System ROC General | 2026-01-05
ROC | January | NBW3 - silicate pump 1 uncommanded stop alarm. Checked site, well is active. Duty rotated to pump 2. operations normal. Reset alarm. | All Water System ROC General | 2026-01-04
ROC | January | SHTP- Well 2 uncommanded stop alarm came in. Reset alarm well not running or being called upon | All Water System ROC General | 2026-01-01
ROC | January | AURSOH- Activated D1 GWTP- LLP2 Hydraulic valve uncommanded open alarm came in. Reset as per shift report | All Water System ROC General | 2026-01-02
ROC | January | ROYKS to ROPKS Communication alarm came in. Checked site. Alarm cleared right away. Trending is okay | All Water System ROC General | 2026-01-02
ROC | January | Christian Van Beek signing in. Weather: -11 and clear. | All Water System ROC General | 2026-01-04
ROC | January | Christian Van Beek signing out. | All Water System ROC General | 2026-01-05
ROC | January | VNRSKS - Swapped supply pumps to two MAPS pumps. | All Water System ROC General | 2026-01-05
ROC | January | GWTP - ZW4 shutdown on permeate turbidity hihi alarm. Checked site, plant is active and producing flow. Contacted Patrick F who is already watching and will reset the filter. #consult | All Water System ROC General | 2026-01-03
ROC | January | MKRSEM- Called Toronto (Mehdi) and requested pumps on. | All Water System ROC General | 2026-01-03
ROC | January | KSTP - CO2 Adjusted pH lolo alarm, checking pH reading came back within range and alarm cleared | All Water System ROC General | 2026-01-06
ROC | January | MMW1- Evgeny rebooting OIT GWTP- Patrick F on site to work on Cl2 analyzers and NTU analyzers, JHS inspections as well as test flood alarms HLW1- Dave T on site work on CL2 system, Test Cl2 leak alarm , working on Cl2 analyzers and NTU analyzers and work on silicate systems | All Water System ROC General | 2026-01-06
ROC | January | STW3- Placed in man/on as per interim STW12 is man/off for Joe M workorders | All Water System ROC General | 2026-01-06
ROC | January | SHTP - Air compressor 1 and 2 fault alarms. Alarms came in after a power failure in Schomberg. Checked site, air compressors are local off. Contacted Benson S who will attend site and reset the air compressors. Created CMU5#W11556979 #consult # CMU5 | All Water System ROC General | 2026-01-04
ROC | January | Adeela Khan signing out | All Water System ROC General | 2026-01-01
ROC | January | YWS + NYWS Normal Connor Smith signing out | All Water System ROC General | 2026-01-01
ROC | January | MARS - Cell 1 Level HiHi alarm came in. Activated duty 1 at VNRSKS to help lower levels at MARS | All Water System ROC General | 2026-01-02
ROC | January | NMW12 - Station Turbidity Fault alarm came in. Checked site. Wells were running. Turbidity did not go out of range. Unable to reset alarm. Spoke to Donald M. who will head to site | All Water System ROC General | 2026-01-02
ROC | January | NMETIB - Activated duty 1 to help offset with NMETHW | All Water System ROC General | 2026-01-02
ROC | January | MKPSSA - Dan Z. called to inform that she is exercising pump 2 STETTL - Dan also informed she is deep cycling the tower and directed to start pumping once tower hits 40% | All Water System ROC General | 2026-01-02
ROC | January | GWTP - Patrick F onsite Acid recovery clean on train 4. | All Water System ROC General | 2026-01-05
ROC | January | RHMCMD - Placed valve in auto | All Water System ROC General | 2026-01-02
ROC | January | Carter Dunn Signing In, -3D/Snow | All Water System ROC General | 2026-01-05
ROC | January | RHRSTR - Activated duty 1. RHMCMD - Placed in manual as per the interim procedure. | All Water System ROC General | 2026-01-02
ROC | January | HLW2- Combined Chlorine LoLo. Well is Local off. Not directing water to users. | All Water System ROC General | 2026-01-01
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-01
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-01
ROC | January | GWTP- Train 8- Transmembrane Pressure LoLo, ZW8 Shutdown Alarm. Notified Patrick F. Directed to leave alarms outstanding. Will attend to it in the morning. CONSULT | All Water System ROC General | 2026-01-01
ROC | January | NMETIB- Deactivated duty | All Water System ROC General | 2026-01-01
ROC | January | Connor Smith signing out | All Water System ROC General | 2026-01-03
ROC | January | QVW34, Influent Free hihi remaining hi, notified Will T, he is on site doing work | All Water System ROC General | 2026-01-05
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-05
ROC | January | GWTP- Train 5 channel 12 parts count out of range alarm came in. Disregard on shift report | All Water System ROC General | 2026-01-01
ROC | January | AURSBS- Activated D1 | All Water System ROC General | 2026-01-02
ROC | January | KCETDS - Outlet Total CL2 Residual LoLo alarm came in. Checked site. Trends indicate a sudden drop. Value recovered within 2 readings and alarm cleared | All Water System ROC General | 2026-01-02
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-01
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-01
ROC | January | Adam Button signing in -1 Clear | All Water System ROC General | 2026-01-06
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-03
ROC | January | MARS - Cell 1 level low alarm. Swapped supply pumps to VNRSKS from MAPS to VNPS. | All Water System ROC General | 2026-01-03
ROC | January | AURSOH - Activate duty 1 to help with MARS reaching hi level. Place wells 1-4 man/off | All Water System ROC General | 2026-01-04
ROC | January | BVPS, Dan Z is finished on site SHTP, Jacob M is finished on site AUW57, Joe D is finished on site, Well will be man/off for the night, can be run if needed | All Water System ROC General | 2026-01-06
ROC | January | RHMCMD - Placed valve man/open at 50% 04:15 - placed valve back to auto | All Water System ROC General | 2026-01-01
ROC | January | SHTP - Plant air pressure lolo alarm. Air compressors at SHTP faulted following a power failure in Schomberg. Benson S has been dispatched to site. | All Water System ROC General | 2026-01-04
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-03
ROC | January | STETBR - Tower hi level alarm. Placed STW12/ STW3 in auto mode. | All Water System ROC General | 2026-01-05
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-05
ROC | January | AURSBS - Activated duty 1. | All Water System ROC General | 2026-01-06
ROC | January | STPSMR - Alex from Clearway Construction called to inform that a ball valve on the Stouffville Road Bypass watermain has broken and there is a large amount of water bring released from the pipe. Alex has requested the assistance of a York Region operator to throttle the distribution valves and slow the ejection of water. Contacted linear on call operator Harsh P who will attend site ASAP. Harsh will contact Alex to gather necessary information and determine whether he needs backup from East Water Operations. Alex from Clearway stated that if the response time is too long he and his team are comfortable entering the valve chamber and manipulating the valve themselves. Harsh requested that Water on call manager (Ron V) be informed of the situation and that he would be contacting Ron to determine the protocol regarding the rotation of the valve by a contractor. Also contacted Patrick F, area operator on call, to be on stand by if he is needed for additional help or a chamber entry. Conatcted Jerry Z as the ORO for the system as well. Created CMU5#W11555326 for Harsh. Stouffville on call supervisor (Chris) contacted the ROC to ask if we were aware of the situation. Chris stated that he as a Stouffville operator in the field today and will ask that operator to remain in the field for one additional hour or until he hears that the situation is under control. Joe Oliviera from CPD also called to say that he is dispatching himself and Dimitri who are both familiar with the project. KSTP - Conduit level lolo and Co2 adjusted pH lolo alarms triggered. While on the phone with Patrick F regarding the watermain bypass break consulted him regarding the KSTP issues. Patrick directed to close the filter effluent valves until the conduit level can recover. Made necessary changes. Patrick stated he will monitor site and take over once on SCADA. #Consult #CMu5 | All Water System ROC General | 2026-01-03
ROC | January | AUPSRR - Post injection free chlorine hihi and post injection combined chlorine lolo alarms. Checked site, system recently started filling which activated the chemical system. trending shows a dip of the combined chlorine and an associated spike of the free chlorine which both returned to normal range quickly. Cleared alarms. | All Water System ROC General | 2026-01-03
ROC | January | Spoke with Patrick F and made the following system changes. STETBR - Deactivated duty 1 while the watermain bypass on Stouffville road is being repaired. STETTL - Activated duty 1 and placed the STW12 and STW3 well pumps back in auto to float the tower while the watermain bypass on Stouffville road is repaired. | All Water System ROC General | 2026-01-03
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-03
ROC | January | NMETIB - Activated duty 1 | All Water System ROC General | 2026-01-01
ROC | January | RHMCMD - Placed valve man/open at 100% | All Water System ROC General | 2026-01-01
ROC | January | MTW12- MTW12 to MTETNL Communication Alarm. Interlocked well. Placed well in manual and cleared alarm just in case it comes back in. | All Water System ROC General | 2026-01-03
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-04
ROC | January | ARPS- Airport Rd Discharge Flow Lo Alarm. KBET27- Activated duty as per Interim Procedure ARPS- Airport Rd Free Ammonia Fault, Airport Rd Total Ammonia Fault Alarm. Cleared all alarms. | All Water System ROC General | 2026-01-04
ROC | January | KLPS27, Kingsley M resetting OIT on site | All Water System ROC General | 2026-01-05
ROC | January | KCETDS- Benson S on site to work on Cl2, test hi lo lvl and temp alarms, JHS inspections and valve exercising | All Water System ROC General | 2026-01-06
ROC | January | NMW12- Alex B on site for Cl2 leak detection | All Water System ROC General | 2026-01-06
ROC | January | RHRSTR, Deactivated D1 | All Water System ROC General | 2026-01-06
ROC | January | Christian Van Beek signing out. | All Water System ROC General | 2026-01-06
ROC | January | Carter D Signing Out | All Water System ROC General | 2026-01-05
ROC | January | AURSBS - Activated duty 1 | All Water System ROC General | 2026-01-01
ROC | January | BVPS - Deactivated duty 1 | All Water System ROC General | 2026-01-01
ROC | January | SHTP - Benson S has reset the air compressors are the plant is active and operations are normal. Benson S leaving site. YWS + NYWS Normal | All Water System ROC General | 2026-01-04
ROC | January | NMW12- Influent free Cl2 lolo alarm came in interlocking wells. Trends indicate issue with analyzer as the gas chlorinator was stable throughout the drop in residual. Will continue to monitor for residual to return to normal | All Water System ROC General | 2026-01-06
ROC | January | MKRSEM - Reservoir 1 Level Lo Alarm came in. Called Toronto Water (Mehdi) and requested 2 pumps on | All Water System ROC General | 2026-01-02
ROC | January | SHTP- KMNO Pump 2 Uncomm Stop Alarm. Pump 1 took over in duty 1. Alarm cleared. | All Water System ROC General | 2026-01-03
ROC | January | MAP7 - Place pump 2 & 3 man/off VNP7 - Place pumps 1-4 back in auto | All Water System ROC General | 2026-01-06
ROC | January | Carter Signing Out | All Water System ROC General | 2026-01-06
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-06
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-07
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-05
ROC | January | NMW12- Influent free Cl2 did not recover. Placed wells 1/2 in man/off and emailed central water team about outstanding issue NMETIB- Deactivated D1 to offset from NMETHW as per shift report NMVCIB- changed flow setpoint from 40 to 80L/s NMVCBA- Changed flow setpoint from 80 to 40L/s | All Water System ROC General | 2026-01-06
ROC | January | MARS - Request TO to go back to normal flow | All Water System ROC General | 2026-01-06
ROC | January | VNPSCD - Sump pump 1 & 2 fault. Sani sump pump 1 & 2 fault. Central shift report requests for email about sump pump faults & Sani pump fault. Will notify if hi level alarms comes in | All Water System ROC General | 2026-01-07
ROC | January | NMW15- Influent free hihi alarm came in. Spike on well start up trends recovered after 3 mins. NMETHW- Activated D2 NMVCBA- Placed in manual at 40 L/s | All Water System ROC General | 2026-01-01
ROC | January | ARPS - Noticed pump 1 and 2 in auto. Due to the pressure loop scenario interim, only 1 pump should be running in auto. Called Peel water but no answer. Will try again 06:19 - Called Peel water again. Spoke to Jerry who informed this pump may have been placed in auto by mistake and has since placed pump 1 back to man/off. | All Water System ROC General | 2026-01-02
ROC | January | VNRSKS - Swapped supply pumps to two MAPS pumps. | All Water System ROC General | 2026-01-02
ROC | January | GWTP- ZW1, ZW2 Turbidity Fault Alarms. Patrick F will attend site. W11552922 CMU5 | All Water System ROC General | 2026-01-01
ROC | January | GWTP - ZW4 R-Clean Exceeded Duration Alarm came in. Checked site. Called Patrick F. who informed he is on site and is performing a clean on train 4 and will take a look. | All Water System ROC General | 2026-01-02
ROC | January | HLETYS- Post-Injection Combined Chlorine Lo Alarm. Value began to recover after a few minutes but then started decreasing again. Deactivated duty and alarm cleared. NMTKKC- Header Combined/Total CL2 Lo Alarm. Came in after duty shut down. Value recovered. Cleared alarms. | All Water System ROC General | 2026-01-03
ROC | January | GWTP- ZW3 Shutdown, ZW3 Neutralization Aborted, Backpulse Pump 2 Not Available, ZW3- BP Pump 2, Backpulse Flow Low Low Alarms. Notified Patrick F. He will look into it. CONSULT | All Water System ROC General | 2026-01-01
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-03
ROC | January | MAPS PD7 - Pump 3 discharge valve uncommanded close and pump 3 uncommanded stop alarm. Checked site, pumps were recently called for to fill VNRSKS duty. Able to reset alarms, duty rotated to pump 2. Placed pump 2 in auto and monitored start. | All Water System ROC General | 2026-01-03
ROC | January | NMETIB - Deactivate 1 to assist in off set with Harry Walker | All Water System ROC General | 2026-01-05
ROC | January | VNRSKS - Activated duty 1 | All Water System ROC General | 2026-01-01
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-02
ROC | January | Adeela Khan signing out | All Water System ROC General | 2026-01-02
ROC | January | Christian Van Beek signing in. Weather: -10C and clear. | All Water System ROC General | 2026-01-03
ROC | January | VNRSKS - Switched to VNPS PD7. Placed pump 2 and 3 into auto. MAPS PD7 - Placed all pumps man/off | All Water System ROC General | 2026-01-02
ROC | January | MKRSEM, Notified Farshad from Toronto water to start filling the res | All Water System ROC General | 2026-01-05
ROC | January | Connor Smith signing in -8C Cloudy | All Water System ROC General | 2026-01-03
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-03
ROC | January | STPSMR- Harsh P called. The repair is made, bypass is back open and site is back to normal operations. Confirmed ok to now run STPSMR pumps. 20:15- Ron V called. He also spoke with Harsh P. Requested to start up one pump and then start the second duty 1 pump at 21:00. Placed pump 2 in auto. 20:58- Ron V called. Harsh P and contractors are finished onsite. Placed pump 3 back into auto. | All Water System ROC General | 2026-01-03
ROC | January | MAPS/JFRS- Initiated Maple to Jefferson Feed 03:10- Reverted Maple to Jefferson Feed | All Water System ROC General | 2026-01-04
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-04
ROC | January | VNRSKS - Placed Pump 2 man/off at VNPS PD7 and placed pump 1 in auto at MAPS PD8 | All Water System ROC General | 2026-01-02
ROC | January | AUSS - Pump 6 discharge valve failed to open alarm. Checked site, duty rotated to another pump. Operations normal, reset alarm. SUSP - Diversion EQ tank LoE alarm. Disregard as per the shift report. | All Water System ROC General | 2026-01-03
ROC | January | RHPSPA - Generator Warning Alarm came in. Checked site. Site is still running on hydro power. Alarm is disregarded as per shift report | All Water System ROC General | 2026-01-01
ROC | January | JFRS - Lee F onsite, Placed pump 2 man/on for Lee F to work on. Place pump 1 man/off to avoid duty 1 triggering pump to come on. | All Water System ROC General | 2026-01-05
ROC | January | KSTP- Fin Water Fluoride LoLo , Fin Water Tot CL2 Res Fault Alarms. Disregard as per SCADA Report. | All Water System ROC General | 2026-01-03
ROC | January | YWS + NYWS Normal Connor Smith signing out | All Water System ROC General | 2026-01-04
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-04
ROC | January | GWTP - Train 7 shutdown, no other alarms came in for cause of trigger. Informed Patrick F. Will take a look Consult | All Water System ROC General | 2026-01-05
ROC | January | Ethan Ullalkar signing out. | All Water System ROC General | 2026-01-05
ROC | January | AUPSRR - Post-inj chlorine hihi. reading came back within normal range after checking site | All Water System ROC General | 2026-01-07
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-07
ROC | January | QVETQS - Inlet free CL2 hihi, possible due to QVW12 running with high free during run earlier. Will monitor site | All Water System ROC General | 2026-01-04
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-05
ROC | January | BLW12- Generator running alarm came in. Called Tyler Z who informed ROC that generator tech is on site doing a semi annual inspection. Generator will be placed in auto when done BVPS- Dan Z on site to test flood alarms and Cl2 analyzer maintenance. Dan Z will call when done on site GWTP- Zw1 R clean exceed duration alarm outstanding. Notified Patrick F. Patrick is aware of alarm and will try to clear when train is done r clean | All Water System ROC General | 2026-01-06
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-05
ROC | January | VNPS PD8, Placed pumps 1/2/3 back to auto as Tim H is finished his work | All Water System ROC General | 2026-01-06
ROC | January | MKRSEM - Request TO (Peter) to drop both pumps | All Water System ROC General | 2026-01-07
ROC | January | NMVCIB - Dropped flow setpoint from 80L/s to 20L/s to help NMETHW fill while NMETIB is active NMVCBA - Increased flow setpoint from 40L/s to 80L/s to compensate for loss of flow through NMVCIB. | All Water System ROC General | 2026-01-04
ROC | January | NMETIB - Deactivated duty 1 while NMETHW fills. NMVCIB/NMVCBA - Reverted valve setpoints. | All Water System ROC General | 2026-01-05
ROC | January | SHTP - Res total chlorine fault. Informed Jacob M who is onsite | All Water System ROC General | 2026-01-05
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-06
ROC | January | SHTP - Site hydro power failure alarm. Checked site, plant was not active during the power failure. All interlocks have been cleared. Generator did not activate and ATS is pointing to town hydro. SHETCS - PAC control panel power failure and UPS supply power failure alarm. Checked site, tank was draining when power failure occurred. Operations are normal. Cleared alarms. | All Water System ROC General | 2026-01-04
ROC | January | STPSMR- Cl2 emergency system active. Notified Travis W. Travis W will have Joe M attend site. Created CMU5 W11564843 MTW12- Phil D on site for chemical system inspections, Run generator and test hi lo temp SHTP- Jake M on site to work on Cl2 analyzers and NTU analyzer and will be testing Cl2 leak detection test | All Water System ROC General | 2026-01-06
ROC | January | NMVCIB- Changed flow setpoints from 80 to 40L/s NMVCHW- Changed flow setpoints from 40 to 80L/s | All Water System ROC General | 2026-01-06
ROC | January | ARPS- Discharge flow lo alarm came in KLET27- Activated D1 as per interim | All Water System ROC General | 2026-01-02
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-02
ROC | January | NMVCBA- Placed valve manual 20L/s to slow down NMETIB drain cycle 02:26- Placed valve back into auto | All Water System ROC General | 2026-01-02
ROC | January | AUPSOH- P1 speed deviation alarm came in. Trends look okay alarm cleared upon acknowledgment | All Water System ROC General | 2026-01-01
ROC | January | HLETYS - Historian Heartbeat alarm came in. Checked site. Called Ian W. who will take a look. | All Water System ROC General | 2026-01-02
ROC | January | NMW12 - Jerry Z responded to site to investigate the turbidity OOR and fault issues. Jerry noticed moisture on the sample cell and cleaned it. Jerry placed the wells in auto duty 1. If the wells interlock on these alarms again Jerry would like on call instrumentation to come to site and check the instrument. Jerry Z leaving site. | All Water System ROC General | 2026-01-03
ROC | January | Ethan U signing in Weather: -10 | All Water System ROC General | 2026-01-04
ROC | January | GWTP- ZW4 Memb Tank Level Switch HiHi Alarm. Notified Patrick F. Can disregard. Alarm should clear on its own. 19:10- Train 4 back in standby. If MIT fails over the night Patrick F requested an email. CONSULT | All Water System ROC General | 2026-01-02
ROC | January | GWTP - ZW5 channel 1 and channel 2 part counts OOR alarm. Disregard as per shift report. | All Water System ROC General | 2026-01-03
ROC | January | BVPS-Historian Heartbeat alarm outstanding. Notified Talha H. Talha H will check into the issue | All Water System ROC General | 2026-01-06
ROC | January | Carter Dunn Signing In, -3D/Snow | All Water System ROC General | 2026-01-05
ROC | January | MTW12, Wells 1/2 will be off for the night | All Water System ROC General | 2026-01-05
ROC | January | BVPS, Placed pump 2 man/on for Dan B to monitor. Once duty activates, will place pump 2 in D1 and place it back to auto JFPS, Placed pump 2 back to auto | All Water System ROC General | 2026-01-05
ROC | January | NMVCBA - Placed valve back to auto | All Water System ROC General | 2026-01-01
ROC | January | GWTP, Sutton Header Fluoride Hi Alarm, Notified Patrick F that the Sutton PRVs are closed at this time as duty just deactivated at the SUETDR. Directed to disregard at this time however if it goes above 1.20mg/L he would like a call. As we were talking on the phone, ZW4 Neutralization exceeded dur alarm came in, he is going to look into this alarm consult | All Water System ROC General | 2026-01-05
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-06
ROC | January | AURSOH - Activated duty 1. | All Water System ROC General | 2026-01-06
ROC | January | VNRSKS - Swapped supply pumps from two VNPS pumps to one VNPS one MAPS pump to draw evenly from MARS and RHRSTR. | All Water System ROC General | 2026-01-05
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-01
ROC | January | STETBR- Tower level lo STW3- Placed well in man/on as per interim | All Water System ROC General | 2026-01-01
ROC | January | ARPS - ROYKS PAC communication failure. Cant see status of pumps. Peel (Tegbeer) called to inform that pump shutdown shutdown on its own. Pump is off possible due to communication failure/weather imapact. They will call ORO to try and get another pump going ARPS - Called TO (Peter) to get max flow. They informed they will be using a new pump as usual max flow pump is OOS. Will monitor for any abnormal conditions. MKRSEM - Requested for 2 pumps as well to run AUW14 - Pumps 1 & 4 running, place pump 3 in man/on as well | All Water System ROC General | 2026-01-06
ROC | January | ARPS- Airport Rd Discharge Flow Lo Alarm. KLET27- Activated duty. Cleared alarm. Interim Procedure | All Water System ROC General | 2026-01-03
ROC | January | Christian Van Beek signing out. | All Water System ROC General | 2026-01-02
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-03
ROC | January | NMTKKC - Inlet combined and total chlorine hihi alarms. Checked site, inlet flow to the tank has dropped significantly which deactivated the chlorination system. This resulted in a spike of the inlet total and combined chlorine readings. NMW12 is still OOS due to turbidity analyzer issues., which is why flow is low into the tank. Contacted Jerry Z who will attend NMW12 to try and resolve the turbidimeter issues. Jerry Z directed to activated AURSOH duty 1 early to increase flow to Newmarket through the Yonge St Valve. Created a CMU5#W11555288 #consult #CMU5 | All Water System ROC General | 2026-01-03
ROC | January | RHRSTR - Activated duty 1. | All Water System ROC General | 2026-01-03
ROC | January | VNPS- Placed PD7 duty 1 pumps man/off MAPS- Placed PD7 duty 1 pumps in auto | All Water System ROC General | 2026-01-03
ROC | January | AUPSRR- Post injection Cl2 hihi alarm came in residuals recovered after 3 mins | All Water System ROC General | 2026-01-06
ROC | January | NMETIB - Deactivated duty 1. | All Water System ROC General | 2026-01-03
ROC | January | VNPS PD7 - Pump 3 valve failed to open alarm. Checked site, pumps recently activated to fill system. Pump 3 interlocked o n a valve fail to open alarm. Reset alarms and monitored pump activation. | All Water System ROC General | 2026-01-03
ROC | January | QVETQS - Inlet free chlorine HiHi alarm. Checked site, trending shows a quick spike of the inlet free chlorine and a drop of the combined chlorine readings. This is due to the QVW12 treated free chlorine spike seen at well start up. Both values trending towards their normal ranges following the dip and spike. Combined chlorine did not reach low alarm levels. Will monitor the outlet free and combined chlorine as the tank drains later in the day. | All Water System ROC General | 2026-01-03
ROC | January | STPSMR - All pumps have been placed manual/off to prevent any additional pressure issues while the Stouffville Road watermain bypass is bring repaired. | All Water System ROC General | 2026-01-03
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-04
ROC | January | Adeela Khan signing in. Weather: -11 and clear | All Water System ROC General | 2026-01-02
ROC | January | BVPS- Disch Free Chlor Hi Alarm. Disregard as per SCADA Report. 02:09- Disch Free Chlor HiHi Alarm. Disregard as per SCADA Report. Emailed Jerry Z and Central Ops. 05:30- Jerry Z called and requested a call if value reaches 0.4mg/L 05:50- Jerry Z called. He will attend site. W11555269 CMU5 | All Water System ROC General | 2026-01-02
ROC | January | STETBR - Tower level hi alarm came in. Placed STW3 back to auto as per interim | All Water System ROC General | 2026-01-02
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-04
ROC | January | GWTP - Sutton header fluoride hi alarm. Checked site, flow to SUETDR recently stopped as the tower duty deactivated, no water being directed to users. Trending shows the fluoride reading spiked following the shutdown of flow to SUETDR. Will send email to OCO. GRTPLL - low lift pump 4 hydraulic valve uncommanded open alarm. Checked site, pump 4 is interlocked on the valve alarm. Duty 1 has rotated to another pump, cleared alarm. | All Water System ROC General | 2026-01-04
ROC | January | KSTP - Fin water fluoride res hi. Looking into issue someone activated duty and fluoride spiked upon startup. Residual dropped to normal range. | All Water System ROC General | 2026-01-04
ROC | January | YWS+NYWS normal | All Water System ROC General | 2026-01-02
ROC | January | RHRSTR- Deactivated D1 | All Water System ROC General | 2026-01-02
ROC | January | KCETDS- Activated duty in preparation for Maple to Jefferson Feed. | All Water System ROC General | 2026-01-03
ROC | January | AUPSOH - Discharge flow lolo alarm. Checked site, flow is within normal range. Reset alarm. | All Water System ROC General | 2026-01-04
ROC | January | NBW3- Influent Free Chlorine LoLo. Well interlocked on schedule mode startup and did not recover. Placed well in manual and emailed Benson S. 08:45- Benson S will attend site. 13:07- Site back to normal operations. Benson S leaving site. W11552891 CMU5 | All Water System ROC General | 2026-01-01
ROC | January | MAPS- PD7 P2 Uncmd Stop, PD7 P2 Disch. Valve 1 Uncmd Close. Placed pump in manual and cleared alarms. Placed pump 3 in auto as second duty 1 pump. | All Water System ROC General | 2026-01-01
ROC | January | YWS+NYWS normal Adam Button signing out | All Water System ROC General | 2026-01-02
ROC | January | KSTP- Backwash P1 uncommanded stop alarm came in. Backwash P2 in D1 and did not rotate. Notified Patrick F. Will take a look on SCADA 19:45- KSTP- Patrick F cleared alarm. filter already running to waste and trends look okay. #consult | All Water System ROC General | 2026-01-01
ROC | January | KSTP- Fin Water Fluoride Res Fault Alarm. Flatlining at 0.2mg/L. Notified Patrick F. Requested to rotate fluoride pump duties so pump 2 in duty 1. Value recovered. Cleared alarm. CONSULT | All Water System ROC General | 2026-01-03
ROC | January | STW12- Placed man/on STW3- Placed man/on For STETBR Fill Cycle | All Water System ROC General | 2026-01-04
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-04
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-01
ROC | January | SHTP - Tyler CS on site to complete work on the air compressors. | All Water System ROC General | 2026-01-02
ROC | January | AUVCBS- PAC Comm Failure Alarm. Alarm cleared after 10 minutes. | All Water System ROC General | 2026-01-01
ROC | January | VNRSKS - Swapped supply pumps to two MAPS pumps. | All Water System ROC General | 2026-01-04
ROC | January | STW3- Placed well back into auto | All Water System ROC General | 2026-01-01
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-01
ROC | January | MKPSSA / MKRSMR - Dan Z called and requested that the ROC exercise the pumps at MKPSSA for 15 minutes each. Dan Z has already activated pump 2. When pump 2 is finished Dan Z requested that the valves be changed at MKRSMR before running pump 1 and 3. | All Water System ROC General | 2026-01-02
ROC | January | YWS+NYWS normal | All Water System ROC General | 2026-01-01
ROC | January | STW12 - Placed wells man/on for STETBR fill cycle, as per interim | All Water System ROC General | 2026-01-02
ROC | January | NMVCBA- Placed valve back in auto | All Water System ROC General | 2026-01-02
ROC | January | VNRSKS - Activated duty 1 to draw down MARS. | All Water System ROC General | 2026-01-03
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-03
ROC | January | NBW3 - Influent free chlorine lolo, came back up within range shortly after. Clear alarm | All Water System ROC General | 2026-01-04
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-02
ROC | January | Christian Van Beek signing out. | All Water System ROC General | 2026-01-03
ROC | January | NMVCBA- Placed Valve in manual 60L/s | All Water System ROC General | 2026-01-03
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-04
ROC | January | RHRSTR, Deactivated D1 | All Water System ROC General | 2026-01-05
ROC | January | ARPS - Airport comms back, pump 3 running now in auto. Confirmed with Tegbeer at Peel everything is okay on their end and Ian W confirmed we are good no our side as well. Faulted on our end and Ian W was able to remedy situation. Due to loss of trends to confirm when flow stopped, going from time of loss of comms we lost flow presumed from 7:50 to 8:32pm | All Water System ROC General | 2026-01-06
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-04
ROC | January | ARPS - ROYKS PAC communication & COFTA to ROYKS communication alarm. Informed Ian W of issue and nothing reported on Alectra outage map CMU = 11565253 | All Water System ROC General | 2026-01-06
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-06
ROC | January | STW12 - Place wells 1 & 2 back in auto STW3 - Place well back in auto | All Water System ROC General | 2026-01-04
ROC | January | NMETIB - Deactivated duty 1. | All Water System ROC General | 2026-01-06
ROC | January | Ethan Ullalkar signing out. | All Water System ROC General | 2026-01-04
ROC | January | MRKSEM- Called Toronto (Brett) and requested pumps on. | All Water System ROC General | 2026-01-01
ROC | January | Adam Button signing in -10 clear | All Water System ROC General | 2026-01-01
ROC | January | KSSP - Rick L onsite for annual calibrations and focusing work on generator LIT and gas detector as well | All Water System ROC General | 2026-01-05
ROC | January | NMETIB- Jay G on site to test flood alarm and eyewash station | All Water System ROC General | 2026-01-06
ROC | January | Connor Smith signing in -6C Cloudy | All Water System ROC General | 2026-01-02
ROC | January | AUPSRR- Donald M on site for generator run GWTP- ZW5 channel 1/2 part counts OOR alarms came in . Disregard on shift report BLETNL- Travis from town of Stouffville inform ROC of flushing in system | All Water System ROC General | 2026-01-06
ROC | January | Adam Button signing out | All Water System ROC General | 2026-01-06
ROC | January | MKETFA - Water system fire storage vol low. Found all 3 pumps in man/off. Called TO (Peter) to confirm reason why pumps are off and we are recieving fire storage low. They man/started pump 3 as unsure of why pumps were left man/off | All Water System ROC General | 2026-01-06
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-07
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-06
ROC | January | AUPSWS- Deactivated D1 for Tyler S to complete vibrations work | All Water System ROC General | 2026-01-06
ROC | January | BVPS-Talha H done on site RHPSWA- Tim H on site req to run pumps on site. Placed P1-3 in man/off at VNPS PD8 to allow flow from RHPSWA to JFRS and will be testing hi lo temp alarms and flood alarm NMTKKC- header free Cl2 hi alarm came in. Check trends spike reading. Continued to monitor | All Water System ROC General | 2026-01-06
ROC | January | GWTP - Train 1 membrane tank level hihi, noted train 1 going through recovery clean on shift report but nothing on high level for memb tank. Informed Patrick F of hi level and tank neutralization step. Okay to disregard for now and should recover MKPSSA - Informed Patrick F of generator running and Hydo One restoration time being 21:00 Consult | All Water System ROC General | 2026-01-06
ROC | January | Ethan. U Signing the in Weather: 0 freezing rain | All Water System ROC General | 2026-01-06
ROC | January | GWTP - Sutton header fluoride hi, fluoride pump 1 running. Informed Patrick F. Disregard for the night. Should come down and clear. Nothing directed to Sutton, known issue coming in last 3 nights when Sutton PRV closses. Consult | All Water System ROC General | 2026-01-06
ROC | January | QVW12, Tyler Z on site, trying to get the well back up and running, currently running the well to waste | All Water System ROC General | 2026-01-05
ROC | January | HUB3SVR - Artour L restarting server | All Water System ROC General | 2026-01-05
ROC | January | BVPS - Dan B & Kyle C working on pump 2 JFRS - Man/start pump 4 and place pump3 back in auto for Lee F | All Water System ROC General | 2026-01-05
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-04
ROC | January | YWS + NYWS Normal | All Water System ROC General | 2026-01-05
ROC | January | AUETAD, Donald M on site, working on cl2 analyzers, temp alarms and level alarms | All Water System ROC General | 2026-01-06
ROC | January | KSETWB, Jackie S on site, working on the chemical system and testing Cl2 leak alarms | All Water System ROC General | 2026-01-06
ROC | January | NMW12, Alex B on site, working on the ammonia system. Alex will also be doing a leak detection test and then will be cleaning the silicate injection points. | All Water System ROC General | 2026-01-06
ROC | January | JFPS - Lee F finished at site, place pump 2 man/on for an hour as requested to test pump. Place pump 4 back in auto shortly after as well | All Water System ROC General | 2026-01-05
ROC | January | Carter Dunn Signing in | All Water System ROC General | 2026-01-06
ROC | January | MTSP - Aeration Tank 1 DO Lo alarm came in. Checked site. Placed blower 2 man/on as per interim 17:05 - Placed blower back to auto | All Wastewater System ROC General | 2026-01-26
ROC | January | MTSP, Aeration Tank 2 DO Lo alarm, Placed blower 2 man/on to help the DO residual as shift report from the on call operator 12:40, Placed pump back to auto | All Wastewater System ROC General | 2026-01-18
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-18
ROC | January | YDSS + NYSS Normal | All Wastewater System ROC General | 2026-01-23
ROC | January | SUSP - Compressor 1 e stop alarm. Checked site, air compressor 2 rotated into duty 1 and is running. Niel O called to inform that contractors will be working on the air compressor today. | All Wastewater System ROC General | 2026-01-19
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-17
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-17
ROC | January | Carter D signing out, Ethan U on site signing in | All Wastewater System ROC General | 2026-01-15
ROC | January | YDSS+YNSS normal SEOC67- TIT lolo alarm. Due to low temperatures. will monitor | All Wastewater System ROC General | 2026-01-24
ROC | January | NBSP - UV system minor faulr. Disregard as per shift report | All Wastewater System ROC General | 2026-01-17
ROC | January | Ethan Ullalkar signing out. | All Wastewater System ROC General | 2026-01-17
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-22
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-16
ROC | January | YDSS + YNSS Normal Adeela Khan signing out | All Wastewater System ROC General | 2026-01-16
ROC | January | SUSSWB - A resident (David Norbert 905 830 2523) called in to the ROC and informed of the SPS being in alarm mode. After checking site, no alarms were found at SUSSWB or SUSSSR. Sites are trending. 10:02 - Ventilation H2S High, HiHi and fault alarms came in. Checked site. Concentration of H2S is high. Called Mike B. who directed to disregard these alarms as he will be attending site tomorrow for sludge. #CONSULT | All Wastewater System ROC General | 2026-01-17
ROC | January | KCSSKR - Found generator now off. Able to clear status | All Wastewater System ROC General | 2026-01-16
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-16
ROC | January | KSSP - Collection Blower 2 High Differential Pressure came in. Checked site. Noticed that duty rotated to blower 1. Sent an email to Mike B. | All Wastewater System ROC General | 2026-01-17
ROC | January | YDSS+YNSS normal | All Wastewater System ROC General | 2026-01-18
ROC | January | SHSSDK- Evgeny S rebooting OIT. Disregard Heartbeat Alarm. | All Wastewater System ROC General | 2026-01-28
ROC | January | RHAMF1- Marcos T on site with contractors working on recirculation systems | All Wastewater System ROC General | 2026-01-15
ROC | January | Adam Button signing out | All Wastewater System ROC General | 2026-01-21
ROC | January | SEOC 4 - Air DMP2 Uncomm lose alarm. damper in manual with damper 1 in local closed. Reset alarm | All Wastewater System ROC General | 2026-01-26
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-25
ROC | January | SUSP - UV Critical Failure multiple alarms came in. Checked site. All alarms went normal on their own within 1 min. Shift report informs that the UV system may get a critical failure upon plant startup. After checking trends, plant did recently activate when alarms came in. 11:28 - UV Ch 2 Bank 2A and 2B Low UV Intensity fault alarms came in. Both banks are running. No major issues or alarms. Shift report directs to disregard all minor UV alarms 12:50 - UV Critical failure alarms came back in and went normal within a minute. This occurred again on plant startup | All Wastewater System ROC General | 2026-01-17
ROC | January | NMVCBP - Tyson C. informed he will be entering the site and may trigger the hi level alarm. Requested to disregard alarm until he is finished on site | All Wastewater System ROC General | 2026-01-21
ROC | January | KBSP- Marcus R on site for TSSA upgrades will be transferring to and from generator | All Wastewater System ROC General | 2026-01-21
ROC | January | Christian Van Beek signing in. Weather: -13C and clear. | All Wastewater System ROC General | 2026-01-23
ROC | January | Angelica Chepiga signing in, weather -11C | All Wastewater System ROC General | 2026-01-28
ROC | January | RHAMF - Unit 2 Recirculation Pump 2 Emergency Stop and Communication loss alarms came in. Critical alarms. Checked site. Pump is already Local/off | All Wastewater System ROC General | 2026-01-16
ROC | January | KBSP, Marcus R working on the sump pumps in the headworks building | All Wastewater System ROC General | 2026-01-16
ROC | January | PVSS - Young J. is on site and will be testing the hi level alarms | All Wastewater System ROC General | 2026-01-16
ROC | January | RHAMF1 - Kyle C. completed work on OIT. | All Wastewater System ROC General | 2026-01-26
ROC | January | AUSS - David D. informed he is finished running the generator. All alarms were cleared | All Wastewater System ROC General | 2026-01-22
ROC | January | KBSP, Marcus R leaving site, Contractor are on site working on Gen 1. Generator is currently offline, if power outage occurs, generator 2 is available | All Wastewater System ROC General | 2026-01-22
ROC | January | NBSP- Admin Bld. Eyewash Alarm. Notified Harie R. He will look into it. | All Wastewater System ROC General | 2026-01-27
ROC | January | SHSP- Screen room 02 conc hi alarm came in. Disregard on shift report | All Wastewater System ROC General | 2026-01-24
ROC | January | YDSS+YNSS normal | All Wastewater System ROC General | 2026-01-24
ROC | January | AUSS - David D. is on site and will be continuing generator work | All Wastewater System ROC General | 2026-01-21
ROC | January | SUSP - UV Ch2 Bank 2A intensity fault alarm. Bank 2A is running, intensity normal. Left alarm outstanding. | All Wastewater System ROC General | 2026-01-28
ROC | January | Adam Button signing in -13 Clear | All Wastewater System ROC General | 2026-01-26
ROC | January | YDSS+YNSS normal | All Wastewater System ROC General | 2026-01-25
ROC | January | RHAMF1- Unit 2 Recirculation P 2 E stop/ comm alarm came in. Running in local. Shift report directed to disregard alarms from site if minimum of 1 fan running and no power issues. Left outstanding as both fans running okay | All Wastewater System ROC General | 2026-01-26
ROC | January | YDSS+YNSS Normal | All Wastewater System ROC General | 2026-01-25
ROC | January | Adam Button signing out | All Wastewater System ROC General | 2026-01-25
ROC | January | KSSP - Sludge Holding Air Flow LoLo alarm outstanding. Checked site and trends. Nothing on shift report. Noticed that levels were still below the lo level. Called Neil O. who directed to disregard as the two tanks are empty SUSP - UV Ch 2 Bank 2A Low UV Intensity Fault alarm came in numerous times. Neil directed to disregard as this is a known issue #CONSULT | All Wastewater System ROC General | 2026-01-29
ROC | January | NMVCBP - ROC FM valve fault alarm. Checked site, pumps are active and forcemain 2 is open. Unable to clear alarm for forcemain 1. Contacted Niel O who will check SCADA to determine if the controlling valve needs to be adjusted. 21:55 - NMVCBP - Niel O called and directed to leave the alarm outstanding until Sunday when he is in for schedule overtime. #consult | All Wastewater System ROC General | 2026-01-30
ROC | January | KSSP - Chan aeration blower 2 high diff pressure alarm. Checked site, duty has rotated to blower 1 which is active. Unable to reset alarm, sent email to OCO. | All Wastewater System ROC General | 2026-01-31
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-31
ROC | January | YDSS + YNSS normal Adeela Khan Signing out | All Wastewater System ROC General | 2026-01-21
ROC | January | Adeela Khan signing in | All Wastewater System ROC General | 2026-01-30
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-30
ROC | January | YDSS + YNSS Normal KSSP - MUA 6 temp low alarm. Checked site, MUA 6 is not for a chemical room. Disregard as per shift report. | All Wastewater System ROC General | 2026-01-31
ROC | January | Adeela Khan signing out | All Wastewater System ROC General | 2026-01-29
ROC | January | YDSS+YNSS normal Adam Button signing out | All Wastewater System ROC General | 2026-01-18
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-23
ROC | January | NMSSBP- Marcos T called and requested CMU5 for Pump 1 Multilin Trip Alarm. W11617597 CMU5 | All Wastewater System ROC General | 2026-01-27
ROC | January | LSSS- Artour L working on UPS. Disregard Historian Heartbeat alarm. | All Wastewater System ROC General | 2026-01-27
ROC | January | SHSP- David D onsite working on Sludge Holding Tank Blower 2 | All Wastewater System ROC General | 2026-01-28
ROC | January | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-01-28
ROC | January | KSSSQW - Pump 3 Vibration OOR, disregard as per Scada review. | All Wastewater System ROC General | 2026-01-29
ROC | January | RHAMF1, Barry M is on site with NAC, they are turning off the fans to do some testing on site | All Wastewater System ROC General | 2026-01-29
ROC | January | KSSP - Alum chem room MUA 11 Diff press switch hi alarm. Checked site, fan is still running. Called Chris C who directed to disregard but call if the low temperature alarm comes in for any chemical room MUA fan. #consult | All Wastewater System ROC General | 2026-01-23
ROC | January | QVSSSC- Preclogged filter aalrm came in. Emailed North Wastewater about outstanding alarm. Odor control system still online and no other alarms outstanding | All Wastewater System ROC General | 2026-01-24
ROC | January | SHSP - Eric S working on Alum pumps 6&7 flowmeter. | All Wastewater System ROC General | 2026-01-27
ROC | January | PVSS - Eric S on site to replace the H2S sensor. | All Wastewater System ROC General | 2026-01-23
ROC | January | YDSS+YNSS normal | All Wastewater System ROC General | 2026-01-24
ROC | January | 11:30-MTSP- Terry R done on site. YDSS+YNSS normal | All Wastewater System ROC General | 2026-01-25
ROC | January | SEOC Shaft 6/7, Shaft 6/7 Gas High Facility Shutdown alarm, notified Terry R, directed to disregard as long as the fan continues to run consult | All Wastewater System ROC General | 2026-01-26
ROC | January | KBSP, Compressor 1 Motor Overload/Pressure Switch hihi, Marcus R called and is now heading to site to investigate further | All Wastewater System ROC General | 2026-01-29
ROC | January | Connor Smith signing out | All Wastewater System ROC General | 2026-01-28
ROC | January | SEOC4- Ric L finished onsite. | All Wastewater System ROC General | 2026-01-29
ROC | January | LSSS2 - Kyle C and Kevin S working on site. Kyle stated that all alarms from LSSS2 can be disregarded. | All Wastewater System ROC General | 2026-01-23
ROC | January | KSSP - UV Ch. 1 Bank 1A Low UV Intensity Fault alarm came again and cleared right away. 05:15 KSSP - UV Ch.1 Bank 1A Low Intensity Fault alarm. Mike B requested to assign UV Ch. 2 to duty 1. # Consult. 05:15 SUSP - Notified Mike B about outstanding alarm. | All Wastewater System ROC General | 2026-01-20
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-29
ROC | January | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-01-30
ROC | January | YDSS+YNSS normal | All Wastewater System ROC General | 2026-01-24
ROC | January | MTSP- Placed Aeration blower 3 on man/on as per interim 17:45- SHSP- WAS P2 uncommanded stop alarm came in. Reset alarm. | All Wastewater System ROC General | 2026-01-24
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-25
ROC | January | Connor Smith signing in -10C Cloudy | All Wastewater System ROC General | 2026-01-22
ROC | January | AUSS - David D. is on site and will be completing generator maintenance | All Wastewater System ROC General | 2026-01-26
ROC | January | YDSS + YNSS Normal Adeela Khan signing out | All Wastewater System ROC General | 2026-01-30
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-30
ROC | January | KSSP, Neut Process (RC) Took Too Long Alarm, Critical Alarm, notified Chris C, he will look into the issue consult | All Wastewater System ROC General | 2026-01-24
ROC | January | Ethan U signing out | All Wastewater System ROC General | 2026-01-16
ROC | January | Carter Dunn Signing In, -4D/Clear | All Wastewater System ROC General | 2026-01-22
ROC | January | KSSP - Chase J on site to complete membrane filter maintenance. Chase stated there may be some membrane shutdown alarms that can be disregarded. | All Wastewater System ROC General | 2026-01-22
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-16
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-28
ROC | January | KSSP- Alum chem rm MUA dif press Sw hi alarm came in. Fan running okay. Will monitor and call for lo temp alarm | All Wastewater System ROC General | 2026-01-27
ROC | January | KSSSQW - Pump 3 vibration OOR alarm, disregard as per SCADA review. | All Wastewater System ROC General | 2026-01-29
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-26
ROC | January | HLSSBS - Hydrogen Sulphide Sample 1 Fault alarm came in. Critical alarm. Called Chris C. who directed to disregard alarm for the night | All Wastewater System ROC General | 2026-01-26
ROC | January | EGSSSC- Tyson C on site for wetwell inspection. Directed to disregard hi wet well level/overflow alarms | All Wastewater System ROC General | 2026-01-21
ROC | January | KSSP - UV Ch 2 Bank 2A Adjustment Lamp fail alarm. Disregard as per Scada review. | All Wastewater System ROC General | 2026-01-28
ROC | January | AUSS - Pump 6 W discharge header MV3 failed to open alarm. Checked site, duty 1 rotated to another pump which activated and is pushing flow. Reset alarm. | All Wastewater System ROC General | 2026-01-31
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-31
ROC | January | SEOC - SEC H2S monitor pump fault alarm came in. Reset alarm | All Wastewater System ROC General | 2026-01-27
ROC | January | YDSS+YNSS normal | All Wastewater System ROC General | 2026-01-28
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-17
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-17
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-21
ROC | January | KBSP- Artour L done on site diesel levels are not available via SCADA and operations will have to check on site until new LITs are commissioned | All Wastewater System ROC General | 2026-01-21
ROC | January | KSSP - Channel Aeration Blower 2 High Differential Pressure Alarm came in. Blower 1 rotated to duty 1. Sent an email to Chris C. | All Wastewater System ROC General | 2026-01-26
ROC | January | Adam Button signing in -4 Clear | All Wastewater System ROC General | 2026-01-17
ROC | January | MTSP- Reject pump running in local. Notified Dan K. Pump runs in local on a float switch. Directed to disregard #consult | All Wastewater System ROC General | 2026-01-17
ROC | January | KSSP- CIP pH level hi alarm came in. Notified Mike B. Directed to disregard and if train 3 which is currently neutralizing shuts down to leave outstanding for night and email North waste water OPs about issue. #consult | All Wastewater System ROC General | 2026-01-17
ROC | January | YDSS+YNSS normal | All Wastewater System ROC General | 2026-01-18
ROC | January | Angelica Chepiga signing in | All Wastewater System ROC General | 2026-01-27
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-19
ROC | January | KBSP- Marcus R testing influent chamber flood alarm. | All Wastewater System ROC General | 2026-01-27
ROC | January | KSSP - UV channel 1 bank a low UV intensity fault/ UV panel lamp low intensity alarm came in. Fault cleared upon acknowledgement. Intensity normal. Emailed North WW Ops about outstanding alarm. | All Wastewater System ROC General | 2026-01-28
ROC | January | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-01-28
ROC | January | NBSP - UV System Minor fault alarm. UV Bank 1B is running, duty switched recently. Disregard alarm as per Scada review. | All Wastewater System ROC General | 2026-01-29
ROC | January | Angelica Chepiga signing out | All Wastewater System ROC General | 2026-01-29
ROC | January | RHAMF1- Unit 2 Recirculation P 2 Overload/ Failed to start alarms. As per shift report disregard all alarms from site if at least 1 fan running and no power issues. Left outstanding as both fans running normal. | All Wastewater System ROC General | 2026-01-28
ROC | January | KSSP - UV channel 1 bank a low UV intensity fault alarm cleared upon acknowledgement. | All Wastewater System ROC General | 2026-01-28
ROC | January | AUSSSR - Aysix System Heartbeat Alarm came in. Checked site. Unable to clear alarms. Called Chris R. and Ian W. who will take a look 11:00 - Alarm has cleared and site is back to normal operations | All Wastewater System ROC General | 2026-01-29
ROC | January | YDSS + YNSS Normal Connor Smith signing out | All Wastewater System ROC General | 2026-01-22
ROC | January | MTSS- Ric L onsite for calibration on FIT 14:58- Finished onsite. | All Wastewater System ROC General | 2026-01-28
ROC | January | Adeela Khan signing in. Weather: -17C and Cloudy | All Wastewater System ROC General | 2026-01-29
ROC | January | Christian Van Beek signing in. | All Wastewater System ROC General | 2026-01-29
ROC | January | Christian Van Beek signing out. | All Wastewater System ROC General | 2026-01-19
ROC | January | SEOC 6/7 - Gas high facility shutdown alarm. Checked site, fan 1 is running. No obvious impact to operations. Unable to clear alarm, contacted operations. 11:29 - SEOC 6/7 - Spoke with Chris R who stated this alarm is to be disregarded and will remain outstanding until instrumentation can check the gas monitors on site. Chris R will have the alarm added to the shift report. | All Wastewater System ROC General | 2026-01-28
ROC | January | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-01-29
ROC | January | YDSS + YNSS normal | All Wastewater System ROC General | 2026-01-17
ROC | January | Christian Van Beek signing out. | All Wastewater System ROC General | 2026-01-22
ROC | January | LSSS - Kingsley M. will be restarting the server. Will receive a historian heartbeat alarm but will not affect operations 17:17 - Kingsley called back to inform that he is finished restarting the server and alarm has been reset | All Wastewater System ROC General | 2026-01-22
ROC | January | KSSSQW- Chris C leaving site. P1 may be clogged do to grinders being OOS for power outage.P1 should run later tonight and blockage may clear upon start up. Directed to place P1 in man/off if low issues arise. QVSSSC- Chris C directed to disregard outstanding odor control alarm from earlier and to email if odor control system goes offline overnight. YDOC- Reoccurring Biofilter 1 med temp lo alarm came in. Disregard on shift report resets upon acknowledgment | All Wastewater System ROC General | 2026-01-24
ROC | January | MTSP- Placed Blower 3 in auto as per interim YDSS+YNSS normal Adam Button signing out | All Wastewater System ROC General | 2026-01-24
ROC | January | NBSP - UV system minor fault alarm. Checked site, UV Bank 1B is active, normal operations, UV banks recently changed duties . Alarm disregard as per shift report. | All Wastewater System ROC General | 2026-01-21
ROC | January | EGSSSC - Historian Heartbeat alarm came in. Informed Yash S. | All Wastewater System ROC General | 2026-01-21
ROC | January | Adam Button signing out | All Wastewater System ROC General | 2026-01-28
ROC | January | wrong book | All Wastewater System ROC General | 2026-01-21
ROC | January | LSSS - Artour L completed work on site, leaving. | All Wastewater System ROC General | 2026-01-27
ROC | January | MTSP- Air compressor pressure lo alarm came in. Notified Phil R will take a look on site | All Wastewater System ROC General | 2026-01-21
ROC | January | KSSP - MUA2 Diff Pressure Switch High alarm came in. Disregarded as per shift report | All Wastewater System ROC General | 2026-01-21
ROC | January | KSSP- CIP clean/recirc flow lo alarm came in. Reset upon acknowledgement | All Wastewater System ROC General | 2026-01-25
ROC | January | YDSS+YNSS normal | All Wastewater System ROC General | 2026-01-25
ROC | January | YDSS+YNSS normal | All Wastewater System ROC General | 2026-01-25
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-30
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-22
ROC | January | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-01-29
ROC | January | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-01-30
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-30
ROC | January | NBSP- UV system minor fault alarm. Bank 1B running okay. Disregard on shift report SECC- O2 monitor alarm/ HVAC general alarm. O2 sensors and temo analyzers all reading normal. Will monitor for change and email Central East Wastewater Ops about outstanding alarms SEDC- CDC to shaft 4 comms fail. SEOC2- Shaft 2 to shaft 4 comms fail alarm SECC- Shaft 13 to shaft 4 comms fail SEOC4- PAC comm fail waited 10 mins comms returned all comm alarms related cleared | All Wastewater System ROC General | 2026-01-27
ROC | January | YDSS+ YNSS Normal | All Wastewater System ROC General | 2026-01-31
ROC | January | MTSP, Aeration Tank 2 DO lo alarm, placed blower 1 man/on to help with the DO, once DO has recovered, will place back to auto as per shift report | All Wastewater System ROC General | 2026-01-31
ROC | January | YDSS + YNSS Normal Christian Van Beek signing out. | All Wastewater System ROC General | 2026-01-31
ROC | January | SUSP - Niel O on site completing maintenance on the UV system. Niel stated that related alarms can be disregarded. | All Wastewater System ROC General | 2026-01-23
ROC | January | SUSP- Neil O finished working on UVs | All Wastewater System ROC General | 2026-01-27
ROC | January | Adam Button signing in -15 Clear | All Wastewater System ROC General | 2026-01-27
ROC | January | YDSS+YNSS normal | All Wastewater System ROC General | 2026-01-28
ROC | January | SUSP - UV channel 2 Bank 2 A low intensity fault alarm. Checked site, UV channel 2 bank 2A is active and showing normal intensity and dosage readings. Shift report states this is a disregard if the previous criteria are met. Alarm status changed to Normal following alarm trigger. Alarm cleared on acknowledgment. | All Wastewater System ROC General | 2026-01-31
ROC | January | KSSP - Makeup Air unit 6 Temp sw Lo alarm, gen_ MAU 2 alarm, disregard as per SCADA review. | All Wastewater System ROC General | 2026-01-30
ROC | January | KBSP - Young J on site to test the influent float alarm. | All Wastewater System ROC General | 2026-01-28
ROC | January | Adeela Khan signing in. | All Wastewater System ROC General | 2026-01-26
ROC | January | Carter Dunn Signing In, -13D/Clear | All Wastewater System ROC General | 2026-01-18
ROC | January | Ethan U signing in | All Wastewater System ROC General | 2026-01-19
ROC | January | LSSS - Kyle C. will be working on the local SCADA server for an hour. Ops are aware | All Wastewater System ROC General | 2026-01-23
ROC | January | Adam Button signing in | All Wastewater System ROC General | 2026-01-30
ROC | January | Carter D Signing Out | All Wastewater System ROC General | 2026-01-16
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-18
ROC | January | YDSS + YNSS normal | All Wastewater System ROC General | 2026-01-19
ROC | January | NBSP - UV system minor fault alarm. Checked site, UV Bank 1B is running. Trending shows normal operations. This alarm is a disregard on the shift report if the system is running. | All Wastewater System ROC General | 2026-01-23
ROC | January | LSSS- LSSS2to LSSS4 comm fail. Trends on site okay reset alarm | All Wastewater System ROC General | 2026-01-24
ROC | January | EGSSSC- Dominic from Honey well is done on site but Notified ROC that chain is missing for lower gate and no way to lock it. Notified Tyson C. Snow removal contractors struck the gate damaging chain. Site secure at top of hill for now. NMSSBP-Eric S done on site as well as Terry R. Terry R directed to disregard hi wet well dialer alarm | All Wastewater System ROC General | 2026-01-21
ROC | January | MTSP- Clarifier 1/2 no RAS pumps. Confirmed with Terry R still on site wasting AUSS- P2 MV4 fault alarm. Pump is man/off | All Wastewater System ROC General | 2026-01-25
ROC | January | SECC, Rick L is heading to site to do annual calibrations | All Wastewater System ROC General | 2026-01-29
ROC | January | Christian Van Beek signing in. Weather: -18C and clear. | All Wastewater System ROC General | 2026-01-30
ROC | January | Ethan U signing in Weather -3. snow | All Wastewater System ROC General | 2026-01-16
ROC | January | Adeela Khan signing out | All Wastewater System ROC General | 2026-01-17
ROC | January | YDSS+YNSS normal | All Wastewater System ROC General | 2026-01-18
ROC | January | YDSS+YNSS normal | All Wastewater System ROC General | 2026-01-17
ROC | January | NMSSBP- HVAC BAS system general alarm. Would not reset. Emailed Central-East wastewater. | All Wastewater System ROC General | 2026-01-17
ROC | January | SEOC - OCF Fan Room 1 GO2 Low alarm came in. Disregarded as per shift report | All Wastewater System ROC General | 2026-01-19
ROC | January | SUSSWB - Cam B and Niel O on site to complete wet well maintenance. Cam stated that high float, high level and overflow alarms can be disregarded. | All Wastewater System ROC General | 2026-01-19
ROC | January | MTSP- Aeration tank 1 DO lo alarm. Will monitor for 30 mins and placed another aeration blower in manual if DO does not recover | All Wastewater System ROC General | 2026-01-24
ROC | January | KSSSQW- P1 in auto but interlocked due to lolo switch cleared alarm as D1 active | All Wastewater System ROC General | 2026-01-24
ROC | January | MTSP, Aeration DO for tank 1 was lower than normal, placed blower 2 man/on to help the DO problem, will continue to monitor, as per shift report 20:30, Placed blower 2 back to auto | All Wastewater System ROC General | 2026-01-25
ROC | January | KBSP- Marcus R working on UV system 1 | All Wastewater System ROC General | 2026-01-21
ROC | January | Christian Van Beek signing in. | All Wastewater System ROC General | 2026-01-28
ROC | January | SUSP- UV Ch 2 bank 2b Low UV intensity fault alarm came in after no flow to UVs due to low flows through plant. Intensity within normal range and dosage not in alarm. Emailed North wastewater about outstanding alarm | All Wastewater System ROC General | 2026-01-18
ROC | January | SUSP - Alum Tank 3 Level LoLo alarm came in. Checked site. All three tank have lolo levels. Will send an email to Chris C. | All Wastewater System ROC General | 2026-01-21
ROC | January | KCSSKR - Generator running status alarm came in. Checked site. Noticed site is connected to generator power. Fuel level is okay. Ongoing issue. Sent a follow up email to west wastewater | All Wastewater System ROC General | 2026-01-16
ROC | January | KBSP - Marcus R on site to work on the aeration basin DO sensors. Marcus directed to disregard associated alarms. | All Wastewater System ROC General | 2026-01-28
ROC | January | NMSSBP - Mech Screen 1 Fault alarm came in. Called Marcos T. who informed maintenance is on site looking into this | All Wastewater System ROC General | 2026-01-16
ROC | January | NMSSBP, Surge Tank 2 hihi/hihi switch alarm (critical alarm), Trends showing it shot up, hi alarm is consistently coming in at this time, notified Dan K, he will look into it 16:37, Dan K would like an email if it comes in again, believes it the PIT might need a flushing, directed to disregard for the night. 16:52, Surge Tank 2 hihi/hihi switch alarm, was able to reset, sent Dan K an email to let him know as per his request. consult | All Wastewater System ROC General | 2026-01-18
ROC | January | NMSSBP - Rick L and Eric S on site for annual calibrations. May see associated alarms. | All Wastewater System ROC General | 2026-01-22
ROC | January | YDSS+YNSS normal | All Wastewater System ROC General | 2026-01-27
ROC | January | AUSS - Sean P on site to complete work on generator 1. Can disregard associated alarms. | All Wastewater System ROC General | 2026-01-19
ROC | January | Connor Smith signing out | All Wastewater System ROC General | 2026-01-20
ROC | January | KSSP - Darren B on site to complete a generator test run. | All Wastewater System ROC General | 2026-01-20
ROC | January | Christian Van Beek signing in. Weather: -10C and clear. | All Wastewater System ROC General | 2026-01-19
ROC | January | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-01-29
ROC | January | KSSP - CIP pH level hi alarm, checked site appears spike in pH level after netrilazation tank level dropped, reading camer back to normal after | All Wastewater System ROC General | 2026-01-15
ROC | January | YDSS+YNSS Normal | All Wastewater System ROC General | 2026-01-28
ROC | January | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-01-21
ROC | January | Angelica Chepiga signing out | All Wastewater System ROC General | 2026-01-20
ROC | January | KBSP- Filter Sluice Gate 4 Open Failed Alarm. Notified Marcus R. He will look into it. | All Wastewater System ROC General | 2026-01-20
ROC | January | KSSP- Chan Aeration Blwr 2 High Diff Press Alm. Blower 1 running in duty 1. Will email Mike B. | All Wastewater System ROC General | 2026-01-16
ROC | January | SHSP - Effluent pump 3 signal Error. Checked site, effluent pump 3 is currently manual/off. Effluent pump 1 and 2 are available in auto and have been assigned duty 1 and duty 2. Lance J is on site. | All Wastewater System ROC General | 2026-01-19
ROC | January | SEOC6- Eric S onsite replacing O2 sensors. | All Wastewater System ROC General | 2026-01-28
ROC | January | EGSSSC - Chris S. will be rebooting the OIT and this will trigger a Historian Heartbeat | All Wastewater System ROC General | 2026-01-21
ROC | January | MTSP - Compressor 1 E. Stop alarm came in. Called Phil R. who informed that there are contractors working on both compressors today | All Wastewater System ROC General | 2026-01-22
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-23
ROC | January | SUSP - UV channel 2 Bank 2A low UV intensity alarm. Checked site, UV system is active and operations appear normal. Shift report states this alarm can be disregarded if UV dosage is above 30, which it is. | All Wastewater System ROC General | 2026-01-30
ROC | January | KSSP - Channel Aeration Blower 2 High Differential Pressure Alarm. Blower 1 rotated to duty 1. Sent an email to Neil O. | All Wastewater System ROC General | 2026-01-30
ROC | January | QVSSQS - Mike B onsite testing drywell flood | All Wastewater System ROC General | 2026-01-19
ROC | January | SEOC, Shaft 6/7 Gas High Facility Shutdown Alarm, Fans stopped running, notified Barry M, he is heading to site CMU5: W11611843 | All Wastewater System ROC General | 2026-01-24
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-24
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-31
ROC | January | NMVCBP, EGSSSC/ROC FM Pressure lo/lolo alarm, as per Neil O email that was sent out, I gave him a call informing him that the lolo came in again. Directed to disregard at this time. if the lolo comes in when the pumps are off and the pressure doesn't recover after 10 minutes, he would like a call consult | All Wastewater System ROC General | 2026-01-31
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-31
ROC | January | SEOC67- Barry M done on site running fan 1 in Local for weekend. Leaving site 08:32-SEOC67- Shaft 6/7 gas high facility shutdown. Fan one in Local/on showing interlocked. Called Barry M to clarify if the run status is still accurate. Barry M said fan should stay running despite interlock. Site showing airflow #consult | All Wastewater System ROC General | 2026-01-24
ROC | January | KSSSQW- Power failure on site. Generator started up but went back to hydro. P1-4 and channel grinders OOS with VFD faults Hydrostatic/Ultrasonic wet well level hihi alarms came in All supply/ exhaust fans on site failed to start. Could nto reset alarms. P1 started in local in ultrasonic mode wetwell pumping down. Notified Chris C. heading to site created CMU5 W11611919 #CMU5 | All Wastewater System ROC General | 2026-01-24
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-25
ROC | January | SUSP - UV Ch. 2 Bank 2B low UV intensity fault alarm came in. Disregarded as per shift report | All Wastewater System ROC General | 2026-01-19
ROC | January | Adeela Khan signing out | All Wastewater System ROC General | 2026-01-19
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-25
ROC | January | Adam Button signing -24 C clear | All Wastewater System ROC General | 2026-01-24
ROC | January | Carter Dunn Signing Out | All Wastewater System ROC General | 2026-01-24
ROC | January | Connor Smith signing in -12C Clear | All Wastewater System ROC General | 2026-01-28
ROC | January | SUSSHS - Terry C. is on site and will be working on pump 1 10:34 - Terry C. and Brent P. are finished on site | All Wastewater System ROC General | 2026-01-26
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-23
ROC | January | Adeela Khan signing out | All Wastewater System ROC General | 2026-01-23
ROC | January | YDSS + YNSS Christian Van Beek signing out. | All Wastewater System ROC General | 2026-01-23
ROC | January | Connor Smith signing out | All Wastewater System ROC General | 2026-01-30
ROC | January | YDSS+YNSS normal | All Wastewater System ROC General | 2026-01-27
ROC | January | KBSP- Plant effluent flow trends missing. Notified Yash S. Created CMU5 W11617951 20:45- KBSP- Yash S called back trends are back up #CMU5 | All Wastewater System ROC General | 2026-01-27
ROC | January | KBSP - David from ETO engineering completed work on air compressor 2 , cleared outstanding alarm as per Marcus R. David will work on air compressor 1. | All Wastewater System ROC General | 2026-01-26
ROC | January | KSSP- Train 5 memb tank lo Darren B on site working on it BLSS- Screen diff lvl hi alarm came in. Disregard on shift report | All Wastewater System ROC General | 2026-01-30
ROC | January | KSSP - UV Ch. 1 Bank 1A Low UV Intensity Fault and UV Panel 1 Lamp Low Intensity Alarms. Checked site, bank 1A running with normal intensity readings. No major or critical faults. Fault alarm cleared. Emailed area about outstanding alarm. | All Wastewater System ROC General | 2026-01-20
ROC | January | Adam Button signing in -18 C clear | All Wastewater System ROC General | 2026-01-25
ROC | January | Connor Smith signing in -13C Clear | All Wastewater System ROC General | 2026-01-29
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-18
ROC | January | YDSS + YNSS normal | All Wastewater System ROC General | 2026-01-19
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-31
ROC | January | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-01-19
ROC | January | YDSS + NYSS Normal | All Wastewater System ROC General | 2026-01-31
ROC | January | Christian Van Beek signing in. Weather: -17C and clear. | All Wastewater System ROC General | 2026-01-31
ROC | January | SECC - Yash S. is on site and will be completing a panel inspection | All Wastewater System ROC General | 2026-01-23
ROC | January | HMSS - Gavin W. called to inform that he is on site and has placed bar screen 2 offline as he will be fixing the bins | All Wastewater System ROC General | 2026-01-23
ROC | January | AUSSSR - Aysix system heartbeat alarm. Checked site, no obvious impact to operations. Able to clear alarm. | All Wastewater System ROC General | 2026-01-31
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-18
ROC | January | RHAMF1 - Recirculation unit 1 water flow lolo. pressure lolo. Informed Dan K, disregard for the night. Called NAC Jimmy H at request of Dan K as NAC still assuming responsibility for site. No response from Jaime Consult 18:30 - called back, Jimmy mentioned they shut down system today with operator. Okay to disregard for night | All Wastewater System ROC General | 2026-01-15
ROC | January | YDOC20 - Communication loss to YDOC20 SEOC8/10/9/4 - PAC communication loss Informed Artour L of alarms and loss of trends, will look into issue CMU = 11593677 | All Wastewater System ROC General | 2026-01-16
ROC | January | Carter Dunn Signing In, -5D/Clear | All Wastewater System ROC General | 2026-01-16
ROC | January | KBSP- Marcus R working on RAS P2 | All Wastewater System ROC General | 2026-01-30
ROC | January | NMVCBP - EGSSSC FM pressure lolo alarm. Checked site, pump is active to push wastewater to the Newmarket pumping station. Trending shows that when the pump is active the pressure is dropping below the usual range and into the low and lolo alarm setpoint territory. No obvious impact to operations as the pressure increases once the duty deactivates. Sent email to OCO and will have day shift operator contact on call operator if issue persists. | All Wastewater System ROC General | 2026-01-31
ROC | January | AUSS - Pump 3 E disc header MV4 fault alarm. Checked site, duty rotated to another pump which activated and is pushing flow. Unable to reset alarm, sent email to OCO. | All Wastewater System ROC General | 2026-01-31
ROC | January | SUSSSR - Recieved call from local civilian detailing they hear an audible alarm coming from station. Informed Neil O who will head to site shortly | All Wastewater System ROC General | 2026-01-19
ROC | January | YDSS + YNSS Normal Ethan Ullalkar signing out. | All Wastewater System ROC General | 2026-01-19
ROC | January | KCSSKR - Young J on site to complete tests on the pressure sensors. May see associated alarms. | All Wastewater System ROC General | 2026-01-20
ROC | January | NMVCBP- Discharge flow hihi alarm came in. Found pump in manual speed set point. Emailed North Wastewater Ops about potential issue. Long-term trends indicate pump speed at current manual speed setpoint 19:08- NMVCBP- Placed P2 in auto speed setpoint | All Wastewater System ROC General | 2026-01-17
ROC | January | KLSP- Marcus R on site with Lauren S to work on UV system | All Wastewater System ROC General | 2026-01-15
ROC | January | KCSSKR- Generator shutdown Lauren S on site. Will ensure site is running okay YDSS+YNSS normal Adam Button signing out | All Wastewater System ROC General | 2026-01-15
ROC | January | YDSS + YNSS normal | All Wastewater System ROC General | 2026-01-17
ROC | January | NBSP - Process building control power failure and RAS valve 4 failed to close alarms came in. Spoke to Harie R. who informed that there was a power blip on site and will clear alarms | All Wastewater System ROC General | 2026-01-23
ROC | January | AUSSSR- Aysix system heartbeat alarm came in. Reset alarm trends okay. Emailed Central-East Wastewater about alarm occurrence | All Wastewater System ROC General | 2026-01-17
ROC | January | YDBR - Fan 2 uncommanded stop alarm. Checked site. Ack/ reset, alarm cleared. | All Wastewater System ROC General | 2026-01-20
ROC | January | LSSS - Ubah F. from EME is on site for testing. Needs pump 6 running for a sample. Rotated duties so that pump 6 is in duty 1 | All Wastewater System ROC General | 2026-01-16
ROC | January | NBSP- Vortex 2 water scour uncm close alarm came in. Reset alarm as per shift report SECC- HVAC alarm/ O2 monitor alarm. ALrms would not reset sent email to Central East Wastewater team | All Wastewater System ROC General | 2026-01-28
ROC | January | AUSS- David D onsite for generator work. Will be running on load. Disregard related alarms. | All Wastewater System ROC General | 2026-01-20
ROC | January | Christian Van Beek signing in. Weather: -14C and clear. | All Wastewater System ROC General | 2026-01-20
ROC | January | KSSSQW- Wet Well 1 Ultrasonic Loss of Echo Alarm. Checked site, LIT2 is controlling. Alarm cleared. | All Wastewater System ROC General | 2026-01-21
ROC | January | YDOC9 - Ricardo L. is on site and will be taking a look at the o2 sensors 13:50 - Ricardo is finished on site and is headed to SEOC4 | All Wastewater System ROC General | 2026-01-29
ROC | January | AUSS - East forcemain MV2 fault alarm. Checked site, East forcemain is local and showing as half closed or travelling. Checked log book which details Chris R on site to close the east forcemain valve for a trial isolation. | All Wastewater System ROC General | 2026-01-28
ROC | January | SHSP - Lance J testing reject sump pump | All Wastewater System ROC General | 2026-01-19
ROC | January | KSSSQW - Pump 4 VFD Fault alarm. Spoke to Chase J. who directed to disregard alarm | All Wastewater System ROC General | 2026-01-26
ROC | January | AUSSYS - Wetwell 1 no discharge flow path alarm. Checked site, all pumps are manual/off. The wet well 1 forcemain 1 discharge valve is closed. Daniel K is signed in on site in the logbook. Forcemain 2 is open and available. | All Wastewater System ROC General | 2026-01-22
ROC | January | MTSP - Aeration Tank 2 DO Lo alarm came in. Called Phil R. who will take a look | All Wastewater System ROC General | 2026-01-23
ROC | January | AUSS - Pump 1 E stop and multiple other alarms came in. Checked site. Noticed that the discharge valve is in local. Called Barry M. who informed maintenance is on site working on pump 1 | All Wastewater System ROC General | 2026-01-21
ROC | January | LSSS- LSSS2 to LSSS4 Comm Failure Alarm. Alarm cleared. | All Wastewater System ROC General | 2026-01-29
ROC | January | Angelica Chepiga signing in, weather -19C | All Wastewater System ROC General | 2026-01-29
ROC | January | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-01-21
ROC | January | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-01-21
ROC | January | YDSS + YNSS Normal Christian Van Beek signing out. | All Wastewater System ROC General | 2026-01-28
ROC | January | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-01-21
ROC | January | NMSSBP - Eric S. and Ricardo L. are finished on site | All Wastewater System ROC General | 2026-01-22
ROC | January | AUSS- Generator 1 Warning Alarm. Gen1 Engine Coolant Temperature Low Alar (Cleared), Gen1 Engine (Warning) Alarm (Cleared). Also Aurora Sewage Pumping Station Diesel Failure Alarm on dialer. Disregard generator alarms as per SCADA Report. Alarms keep coming in and out. Notified Terry R to confirm as SCADA Report not updated today. Confirmed to disregard. CONSULT | All Wastewater System ROC General | 2026-01-21
ROC | January | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-01-29
ROC | January | KSSP- Membrane air blower 2 speed deviation alarm came in cleared upon acknowledgment | All Wastewater System ROC General | 2026-01-24
ROC | January | KBSP, Trend Checking, when checking the UV page, noticed the Plant Effluent Flow Value has been flat lining since, Jan 29/2026 with also a few missing trends from Jan 27th. Contacted Young J of these observations but no response, will give another call back within 25 minutes 09:44, Young J called back, he will look into this issue | All Wastewater System ROC General | 2026-01-31
ROC | January | MTSP- Ras lolo flow. Terry R on site wasting NBSP- Process building lo temp alarm. Due to lo temperature | All Wastewater System ROC General | 2026-01-25
ROC | January | SEOC- Shaft 6/7 gas high duty rotation imminent/ Fan duty imminent. Disregard on shift report 05:45- SEOC- Shaft 6/7 gas hi facility shutdown. Fan 1 still running in auto | All Wastewater System ROC General | 2026-01-28
ROC | January | YDSS+YNSS normal | All Wastewater System ROC General | 2026-01-28
ROC | January | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-01-27
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-31
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-22
ROC | January | MTSS- Ric L onsite for annual calibrations. 15:08- Finished onsite. | All Wastewater System ROC General | 2026-01-27
ROC | January | RHAMF1, Recirculation pump 1 overload, directed to disregard as per shift report | All Wastewater System ROC General | 2026-01-25
ROC | January | MTSP, Aeration Tank 1 DO Lo alarm, Placed blower 1 man/on to help increase the DO as per shift report | All Wastewater System ROC General | 2026-01-26
ROC | January | KSSP, Neut Process (RC) Took Too Long Alarm, Critical Alarm, notified Chris C, pH Valve lower than normal, Chris C says to let the CIP neutralization process do its thing, may take a couple of cycles. If after a few cycles the pH doesn't recover or that the CIP system doesn't go back to normal, he would like a call back 04:33, Neutralization process went through 4 cycles but no improvement, notified Chris C as per his request, directed to disregard for the rest of the night consult | All Wastewater System ROC General | 2026-01-26
ROC | January | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-01-19
ROC | January | SECC - HVAC general alarm and O2 monitor alarm. Checked site, operations normal. Sent email to OCO. | All Wastewater System ROC General | 2026-01-31
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-31
ROC | January | SUSP, UV Ch. 2 Bank 2A Low UV Intensity Fault, As per shift report can disregard, Dosing is above 30, will continue to monitor. 1 UV Bank is currently active at this time. NMVCBP, ROC FM/EGSSSC FM Pressure lolo, when pumps turned on, pressure dropped, after monitoring for 5 minutes and the pumps turned off, Pressure came back to normal levels. | All Wastewater System ROC General | 2026-01-31
ROC | January | Carter D Signing Out | All Wastewater System ROC General | 2026-01-29
ROC | January | Carter D Signing Out | All Wastewater System ROC General | 2026-01-31
ROC | January | YDSS + YNSS Normal Carter D signing Out | All Wastewater System ROC General | 2026-01-18
ROC | January | SUSSSR - Cam B & Neil O onsite testing hi level alarm | All Wastewater System ROC General | 2026-01-19
ROC | January | KBSP - Marcus R called, he is replacing UV bulbs. Constractors working on compressors, disregard alarms for the duration of the work. | All Wastewater System ROC General | 2026-01-26
ROC | January | SUSP - Mike B called back.Requested disregard Low UV intensity fault Bank 2A and 2B alarms. He will check it tomorrow. UV Ch 2 Bank 2B is running normal. | All Wastewater System ROC General | 2026-01-20
ROC | January | LSSS - Sluice Gate 2 Uncommanded Open alarm came in. Checked site. Called Kevin S. who informed Kyle C. is working on the control panel and this alarm may have been triggered. Kevin informed he will try to clear alarm | All Wastewater System ROC General | 2026-01-23
ROC | January | AUEQSJ - Electrical room smoke detector alarm. Checked site, operations normal. Alarm cleared upon reset. | All Wastewater System ROC General | 2026-01-23
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-22
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-22
ROC | January | SUSP- UV System Critical Failure Alarm, UV Ch.1 High Level Alarm, UV CH.1 Common Critical Alarm, UV Ch.2 High Level Alarm. UV CH2. Common Critical Alarm. All alarms cleared on their own. Known issue on scada report caused by high channel level. UV. Ch.2 Bank 2A/2B Low UV Intensity Fault. Both are running. Notified Chris C. Can disregard. CONSULT | All Wastewater System ROC General | 2026-01-22
ROC | January | Adam Button signing in | All Wastewater System ROC General | 2026-01-30
ROC | January | MTSP, Aeration Tank 1 DO lo, placed blower 1 man/on as per shift report 20:25, Placed blower back to auto | All Wastewater System ROC General | 2026-01-24
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-24
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-26
ROC | January | SUSP- UV channel 1 bank 1a lo UV intensity. Bank 1b running and 1a was slowly starting up. Dosage not affected and intensity of 1b was steady as 1a started up. left alarm outstanding | All Wastewater System ROC General | 2026-01-28
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-18
ROC | January | Connor Smith signing out | All Wastewater System ROC General | 2026-01-27
ROC | January | NBSP- Vortex 2 air scour uncmd close alarm came in. Reset as per shift report | All Wastewater System ROC General | 2026-01-18
ROC | January | YDSS + YNSS normal | All Wastewater System ROC General | 2026-01-19
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-21
ROC | January | AUSS - Eric S. called to inform that he has finished comissioning pump 3 and spoke to Daniel K. who will prime the pump today or tomorrow. | All Wastewater System ROC General | 2026-01-26
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-15
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-16
ROC | January | SUSP- UV System Critical Failure Alarm. UV Ch. 1 High Level Alarm. Known issue according to SCADA Report caused by Hi Channel Level. Alarm went normal and cleared on its own. | All Wastewater System ROC General | 2026-01-22
ROC | January | Adam Button signing in | All Wastewater System ROC General | 2026-01-21
ROC | January | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-01-20
ROC | January | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-01-29
ROC | January | YDSS + YNSS Normal Connor Smith signing out | All Wastewater System ROC General | 2026-01-23
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-23
ROC | January | AUSSSR - Terry R attended site to reset the line 2 valve overtorque alarm. Able to reset alarm. Created CMU5#W11611762 for Terry R. #CMU5 | All Wastewater System ROC General | 2026-01-23
ROC | January | KSSSQW - Pump 4 VFD fault, Matt S working on it. | All Wastewater System ROC General | 2026-01-26
ROC | January | SUSSHS - Neil O & testing hi level and wet well | All Wastewater System ROC General | 2026-01-19
ROC | January | SHSP - Compressor 1 e stop alarm and motor overload alarm and pressure switch hihi alarm. Contacted Lance J who informed that there is a contractor on site to complete compressor maintenance. | All Wastewater System ROC General | 2026-01-20
ROC | January | SEOC4 - Stephen from AB working on site (dusty work). Requested disregard fire/smoke alarm for the duration of the work. | All Wastewater System ROC General | 2026-01-27
ROC | January | KSSSQW- Sump Pump Panel High High Level Alarm, Sump Pump Panel General Fault Alarm. Called Tyson C. No answer, will try again 14:45- Tyson C called back. He is onsite and cleared alarms. | All Wastewater System ROC General | 2026-01-29
ROC | January | Carter Dunn Signing In | All Wastewater System ROC General | 2026-01-29
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-24
ROC | January | AUSS - Sean P finished at site | All Wastewater System ROC General | 2026-01-19
ROC | January | RHAMF1 - Marcos T. is on site and is working on the installation of Recirculation Pump 2. Marcos informed he is unable to access the OIT on site and requested PCS's assistance. Called Yash S. who will look into this | All Wastewater System ROC General | 2026-01-21
ROC | January | AUSS, David D is on site with Total Power contractor, looking at the generators | All Wastewater System ROC General | 2026-01-22
ROC | January | Adeela Khan signing in. Weather: -6 and sunny | All Wastewater System ROC General | 2026-01-22
ROC | January | AUSS - Brent St. Croix is on site resetting the generator | All Wastewater System ROC General | 2026-01-23
ROC | January | AUSS- P4 MV2 failed to open alarm came in. Reset alarm | All Wastewater System ROC General | 2026-01-25
ROC | January | NBSP, Process Bld UPS Fault, contacted Yash S, he will look into it 19:19, Yash S says to disregard for the night, if a power outage comes in, Yash would like a call consult | All Wastewater System ROC General | 2026-01-25
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-28
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-24
ROC | January | Carter Dunn Signing In, -15D/Snowing | All Wastewater System ROC General | 2026-01-24
ROC | January | SEOC6/7 - Shaft 6/7 Gas High Facility Shutdown alarm came in. Called Daniel K. who directed to disregard alarm for the time being. He has created a work order for instrumentation | All Wastewater System ROC General | 2026-01-26
ROC | January | MTSP- Aeration tank 1 DO lo alarm came in. If outstanding for 30 mins will run blower 2 in manual . 19:02- MTSP- Placed Blower 2 in manual as per shift report 19:20- MTSP- Placed Blower 2 in auto as per shift report | All Wastewater System ROC General | 2026-01-26
ROC | January | YDSS+YNSS normal | All Wastewater System ROC General | 2026-01-26
ROC | January | MTSP- Placed Aeration blower 2 in man/on as DO did not recover. Made changes as per shift report 00:42- MTSP- Placed aeration blower 2 back in auto | All Wastewater System ROC General | 2026-01-27
ROC | January | NMSSBP- P1 Multilin trip uncommanded stop and mulitlin warning alarms came in. Placed P1 in manual. Emailed Central East Wastewater OPS | All Wastewater System ROC General | 2026-01-27
ROC | January | Adam Button signing out | All Wastewater System ROC General | 2026-01-30
ROC | January | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-01-26
ROC | January | Adeela Khan signing out | All Wastewater System ROC General | 2026-01-26
ROC | January | YDSS+YNSS normal | All Wastewater System ROC General | 2026-01-27
ROC | January | NMSSBP - Surge Tank 2 HiHi level Switch alarm came back in. Daniel K. is aware. Surge tank level came back to optimal range and alarm cleared 18:23 - Surge Tank 1 LoLo Switch alarm came in. Checked site and noticed that the pumps were not interlocked but the surge tank 1 compressed air valve is interlocked. Called Daniel K. who will head to site. CMU5 Created W11596464 19:50 - Surge Tank 2 HiHi level alarm came in along with the wet well 1 and 2 ultrasonic and hydrostatic alarms. Called Daniel K. for an ETA who informed he is on site now. Daniel informed it will over flow to NMEQBP 19:52 - Wet Well 1 and 2 overflow alarms came in. Daniel K. is aware 19:58 - Daniel K. called back and directed to give Chris S. a call. 20:15 - Daniel K. called to inform that there was a burst water pipe in the screen room which affected to level sensors for the surge tanks. Daniel K. informs this is due to the pipe being frozen and has since shut down the ventilation for the time being. Daniel informed that the leak has been isolated. Daniel also informed he would like to consult with instrumentation. Gave Ricardo L. a call but no answer. Will try again. 20:22 - Called Ricardo L. again. No answer. Left a message. Relayed this information to Daniel K 20:40 - Ricardo L. called back and will give Daniel K. a call 21:34 - Ricardo L. called back to inform that he is on site with Daniel K. CMU5 created W11596475 22:18 - Ricardo L. called back to inform that he and Daniel K. are finished on site. The analyzer and sensor issues have been resolved but the ventilation unit will remain off #CONSULT #CMU5 | All Wastewater System ROC General | 2026-01-18
ROC | January | AUSS - Pump 2 W Disc Hdr MV3 failed to open. Reset alarm. | All Wastewater System ROC General | 2026-01-29
ROC | January | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-01-29
ROC | January | NBSP - UV system minor fault. Checked site, UV bank 1B is running. Trending shows normal operations. Disregard as per the shift report. | All Wastewater System ROC General | 2026-01-31
ROC | January | HLSSBS - Mike B on site to test the dry well flood alarm. | All Wastewater System ROC General | 2026-01-22
ROC | January | Angelica Chepiga signing in, weather -16C | All Wastewater System ROC General | 2026-01-26
ROC | January | HMSS, Young J on site testing the hi level alarms | All Wastewater System ROC General | 2026-01-16
ROC | January | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-01-21
ROC | January | KSSP - Neil O. on site and will be working on the channel aeration blowers | All Wastewater System ROC General | 2026-01-30
ROC | January | RHAMF1 - Kyle C. will be restarting the OIT. Will receive a Historian Heartbeat alarm | All Wastewater System ROC General | 2026-01-26
ROC | January | Angelica Chepiga signing out | All Wastewater System ROC General | 2026-01-21
ROC | January | SUSP - UV Channel 2 Bank 2A and Bank 2B low UV intensity fault alarms. Checked site, Bank 2B running with normal intensity readings. No major or critical faults present, UV minor fault alarms can be disregarded as per shift report. Emailed North wastewater about outstanding alarm. SUSP - EQ tank level Hi alarm. Back to normal value, Cleared alarm. | All Wastewater System ROC General | 2026-01-20
ROC | January | NMSSBP - Eric S. is on site and will be working on the LIT for the valve chamber | All Wastewater System ROC General | 2026-01-21
ROC | January | AUSS- Generator 1 Warning Alarm. Disregard as per SCADA Report | All Wastewater System ROC General | 2026-01-22
ROC | January | RHAMF -Joe O. from Property Services called to inform that Daniel K. would like all the alarms to be cleared. Called Daniel K. who directed to place both fans back to auto | All Wastewater System ROC General | 2026-01-29
ROC | January | Angelica Chepiga signing out | All Wastewater System ROC General | 2026-01-26
ROC | January | YDSS+YNSS normal MTSP- Aeration tank 1 DO lo alarm came in. Will continue to monitor and reach out to OCO if lolo comes in | All Wastewater System ROC General | 2026-01-27
ROC | January | YDSS+YNSS normal | All Wastewater System ROC General | 2026-01-27
ROC | January | KSSP UV channel 1 bank a low UV intensity fault/ UV panel lamp low intensity alarm came in. Fault cleared upon acknowledgement. Dosage held steady during slight dip in intensity and recovered after 2 minutes. Emailed North Waste Water Ops about outstanding alarm | All Wastewater System ROC General | 2026-01-27
ROC | January | LSSS- LSSS2 to LSSS4 comm alarm. Reset alarm trends okay | All Wastewater System ROC General | 2026-01-28
ROC | January | SUSP - Artour L. is on site with Neil O. and will be working on the UV panel | All Wastewater System ROC General | 2026-01-23
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-15
ROC | January | Adeela Khan signing in | All Wastewater System ROC General | 2026-01-16
ROC | January | SUSP - UV Ch2 Bank 2A and 2B Low UV intensity fault alarms. Both Bank 2A and 2B running, UV Ch 2 Bank 2B intensity is 47,6. Disregard alarms as per Mike B. | All Wastewater System ROC General | 2026-01-21
ROC | January | SUSP - UC Ch. 1 high level, critical failure, intensity fault. Switched to normal status right away and found. UV system fault upon plant start up due to a high channel level. Alarm will clear once UV gates open as noted in shift report. Alrams cleared when acknowledged | All Wastewater System ROC General | 2026-01-17
ROC | January | KCSSKR, Generator Running Status Alarm, notified Lauren S as King City SS has been off and on all day and wanted to inform her that it is running again. If the generator runs for another 3 hours, she would like a follow up. Contacted Hydro 1 and informed them of the possible outage, Thalia is passing the message to their team and someone will reach out to the ROC | All Wastewater System ROC General | 2026-01-15
ROC | January | Ethan U signing in Weather -10. | All Wastewater System ROC General | 2026-01-15
ROC | January | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-01-26
ROC | January | Carter Dunn Signing Out | All Wastewater System ROC General | 2026-01-25
ROC | January | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-01-20
ROC | January | SEOC4 - Shaft 4 Gas High Facility Shutdown alarm came in. Checked site. Spoke to Daniel K. who informed this alarm comes in because of a new O2 sensor and instrumentation will need to check the issue. Daniel informed that this alarm can be disregarded | All Wastewater System ROC General | 2026-01-16
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-16
ROC | January | NBSP- Vortex 1 water scour uncmnd close alarm came in rest as per shift report | All Wastewater System ROC General | 2026-01-26
ROC | January | YDSS+YNSS normal | All Wastewater System ROC General | 2026-01-26
ROC | January | YDSS+YNSS normal | All Wastewater System ROC General | 2026-01-24
ROC | January | KSSSQW- Chris C on site cleared all VFD alarms and will remain on site to see if sites running okay. | All Wastewater System ROC General | 2026-01-24
ROC | January | NMSSHS, Rick L heading to site to work on the O2 sensor | All Wastewater System ROC General | 2026-01-15
ROC | January | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-01-20
ROC | January | SUSP - UV Ch1 common critical alarm and UV Ch 1 High level, UV system critical failure alarm. Alarms cleared right away, UV Ch 2 on duty 1. UV Ch2 Bank 2A and 2B low UV intensity alarms. Mike B will check SCADA. # Consult | All Wastewater System ROC General | 2026-01-20
ROC | January | KSSP- Neut process RC took too long notified Chris C. Directed to disregard for night. Issues with the pH probe. Chris C manual operating the neutralization process but alarm may be outstanding for night #consult | All Wastewater System ROC General | 2026-01-27
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-17
ROC | January | HMSS - Illegal Entry Alarm came in on the dialer. No operator called to inform they would be attending site. Called Corporate Security (Bivij) who informed he will look into this 12:41 - Lauren S. called to inquire about a delivery at KCSSKR and informed that she did enter HMSS which triggered the Illegal Entry alarm on the dialer. Called Corporate Security to let them know | All Wastewater System ROC General | 2026-01-17
ROC | January | NMSSBP - Kevin S on site to complete work orders including a flood alarm test, sump pit inspection and hi temp alarm test. | All Wastewater System ROC General | 2026-01-20
ROC | January | Connor Smith signing in -4C Snowy | All Wastewater System ROC General | 2026-01-21
ROC | January | KSSP - Sludge Holding Air Flow LoLo alarm came in. Checked site and trends. Called Darren B. who will take a look. | All Wastewater System ROC General | 2026-01-29
ROC | January | Connor Smith signing out | All Wastewater System ROC General | 2026-01-29
ROC | January | SHSSDK, Hydrostatic mode/Hi Pressure, notified Lance J that the station seems to be having some issues, he will investigate further | All Wastewater System ROC General | 2026-01-16
ROC | January | Angelica Chepiga signing in, weather -9C | All Wastewater System ROC General | 2026-01-19
ROC | January | KSSP - UV channel 1 bank a low UV intensity fault in and out. Notified Neil O, requested to rotate UV Duty. # Consult SUSP - UV Ch 2 Bank 2A Low UV intensity Fault alarm outstanding. UV intensity normal. Neil O requested disregard alarm. | All Wastewater System ROC General | 2026-01-28
ROC | January | HMSS - Dan H. called and directed to place all the pumps in manual and then place running pump 3 into man/off. Once pump 3 shut off, Dan H. directed to place pump 4 which is now in duty 1 into auto. Dan also directed to place the rest of the pumps back to auto. Dan informed he is on site testing air valves | All Wastewater System ROC General | 2026-01-29
ROC | January | YDSS + YNSS normal | All Wastewater System ROC General | 2026-01-18
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-21
ROC | January | Carter Dunn Signing In, -21D/Clear | All Wastewater System ROC General | 2026-01-31
ROC | January | SEBR - S2 Nutrient Tank Low Level alarm came in. Checked site. Spoke to Chris R. who directed to disregard alarm until tomorrow. | All Wastewater System ROC General | 2026-01-26
ROC | January | SUSP - Neil O and Cam B working on UVs, disregard alarms for the duration of the work. | All Wastewater System ROC General | 2026-01-27
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-20
ROC | January | NBSSJA - Diesel Tank Level HiHi alarm came in. Disregarded as per shift report | All Wastewater System ROC General | 2026-01-21
ROC | January | KBSP - Marcus R on site to inspect air compressors | All Wastewater System ROC General | 2026-01-20
ROC | January | AUSS - Pump 3 E disc hdr MV4 fault alarm. Pump 3 was on man/off mode , not running. | All Wastewater System ROC General | 2026-01-21
ROC | January | YDSS + YNSS Normal Adeela Khan signing out | All Wastewater System ROC General | 2026-01-22
ROC | January | SECC, HVAC General/O2 Monitor, Phil R called saying he is going to site to check on the pump system. CMU5: W11625805 | All Wastewater System ROC General | 2026-01-31
ROC | January | YDOC- Bio F1 med temp lolo alarm outstanding for weekend. Notified Terry R to see if there was any response needed for prolonged lolo temperature .Directed to disregard. #consult | All Wastewater System ROC General | 2026-01-25
ROC | January | YDSS + YNSS Normal Christian Van Beek signing out. | All Wastewater System ROC General | 2026-01-20
ROC | January | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-01-20
ROC | January | SUSP - UV Ch 2 Bank 2 A Low UV intensity fault alarm, checked site, UV 2 Bank 2A is running, intensity normal. Alarm to disregard as per ROC Transfer of Information Checklist / Neil O. | All Wastewater System ROC General | 2026-01-29
ROC | January | AUSSYS- Office FCV1 deviation alarm came in cleared upon acknowledgment | All Wastewater System ROC General | 2026-01-27
ROC | January | SEOC6 Shaft 6/7 O2 Monitor and Shaft 6/7 Fan Duty Rotation Imminent alarms - disregard alarms as per shift report. | All Wastewater System ROC General | 2026-01-21
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-26
ROC | January | Carter D Signing Out | All Wastewater System ROC General | 2026-01-26
ROC | January | LSSS - Bar Screen Fault alarm came in. Kyle C. directed to disregard alarm as its caused by a new level transmitter | All Wastewater System ROC General | 2026-01-22
ROC | January | KSSP- ZW1 not all devices in auto alarm came in. Chris C on site working on NTU analyzer for train 1 causing interlock | All Wastewater System ROC General | 2026-01-21
ROC | January | YDSS+YNSS normal | All Wastewater System ROC General | 2026-01-25
ROC | January | KBSP - Artour L. is on site to assist Ferguson Electric with the TSSA Generator test | All Wastewater System ROC General | 2026-01-21
ROC | January | YDSS+YNSS NORMAL Angelica Chepiga signing out | All Wastewater System ROC General | 2026-01-27
ROC | January | YDOC- F2 Make up flow OOR. Disregard on shift report | All Wastewater System ROC General | 2026-01-25
ROC | January | KSSP-Membrane Blower 2 lo flow alarm and shutdown while ZW2 running. ZW2 shutdown and no blowers available. Notified Chris C. Directed to ack reset alarms and see if blower 2 will un in D1. If not try to run blower 2 in manual. Both interlocked due to air valves not open. Chris C already heading to site for weekly plant duties 07:29-KSSP- Chris C called back. As train 1 is in production membrane blowers are not being called for. Chris will take a look on SCADA when on site but seems site is running okay 8:00- KSSP- Chris C confirmed on site membrane system running okay and placed train 2 back online establishing air flow from blower 2. 8:00-YDSS+YNSS normal #consult | All Wastewater System ROC General | 2026-01-25
ROC | January | AUSS - PUmp 4 e discharge header valve fail to open alarm. Checked site, duty rotated to pump 5. cleared alarms. | All Wastewater System ROC General | 2026-01-22
ROC | January | MAPSN1 - Kyle C. is restarting the server. Should take no more than 5 mins | All Wastewater System ROC General | 2026-01-23
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-25
ROC | January | Christian Van Beek signing out. | All Wastewater System ROC General | 2026-01-29
ROC | January | Adeela Khan signing in | All Wastewater System ROC General | 2026-01-23
ROC | January | KSSP - Neutralization Process (MC) Took Too Long alarm came in. Checked site. Called Chase J. who directed to disregard for the night | All Wastewater System ROC General | 2026-01-26
ROC | January | AUSSSR - Lane 2 Valve overtorque alarm, Lane 3 valve overtorque alarm outstanding. Only one lane available. Notified Barry M, he will attend. # CMU5 W11617770 | All Wastewater System ROC General | 2026-01-27
ROC | January | Connor Smith signing in -20C Clear | All Wastewater System ROC General | 2026-01-30
ROC | January | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-01-30
ROC | January | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-01-30
ROC | January | Angelica Chepiga signing out | All Wastewater System ROC General | 2026-01-30
ROC | January | LSSS- Bar Screen 2 Fault Alarm. Terry C is onsite and will look into it. 14:04- Terry C called back. Bar Screen will be OOS. He will inform Operations. | All Wastewater System ROC General | 2026-01-27
ROC | January | YDSS+YNSS normal | All Wastewater System ROC General | 2026-01-27
ROC | January | Connor Smith signing in -14C Clear | All Wastewater System ROC General | 2026-01-27
ROC | January | Adam Button signing out | All Wastewater System ROC General | 2026-01-27
ROC | January | KSSP- Neutralization Aborted Alarm. Notified Neil O. Informed that Chirs C and Kevin K are working on it. | All Wastewater System ROC General | 2026-01-28
ROC | January | Connor Smith signing in | All Wastewater System ROC General | 2026-01-20
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-22
ROC | January | NBSP - Plant Diesel Generator Running alarm came in. Checked site. Noticed the generator running but the plant transfer switch hydro power fail and switch faulted alarms are active. Spoke to Dan H. who informed they are having issues with the power on site and an electrician is headed to site | All Wastewater System ROC General | 2026-01-23
ROC | January | SUSP - Arthur Leaving site. | All Wastewater System ROC General | 2026-01-23
ROC | January | KSSP - Chase J. called to inform that he is on site and will be working on the membranes. Chase informed this may trigger low level and shutdown alarms for the trains | All Wastewater System ROC General | 2026-01-21
ROC | January | YDSS + YNSS normal | All Wastewater System ROC General | 2026-01-16
ROC | January | Carter D Signing In, -13D/Snowing | All Wastewater System ROC General | 2026-01-25
ROC | January | MTSP, Aeration Tank 1 DO lo, Placed blower 2 man/on as per shift report 01:07, Placed blower back to auto | All Wastewater System ROC General | 2026-01-26
ROC | January | Adeela Khan signing in. Weather: -10 and partly cloudy | All Wastewater System ROC General | 2026-01-18
ROC | January | SEOC4 - shaft Satnam M onsite working on generator with contractor. running with load bank | All Wastewater System ROC General | 2026-01-19
ROC | January | YDSS+YNSS normal | All Wastewater System ROC General | 2026-01-17
ROC | January | NMSSHS, Eric S is heading to site to work on the O2 monitor 14:44, Eric S is finished on site | All Wastewater System ROC General | 2026-01-16
ROC | January | Adeela Khan signing in. Weather: -14 and clear | All Wastewater System ROC General | 2026-01-21
ROC | January | SHSP- Young J Lance J on site working on UV system and will cause a UV diversion alarm and channel hi alarm as efffluent pumps 1-3 will be placed in man/off but will monitor on site | All Wastewater System ROC General | 2026-01-15
ROC | January | Adeela Khan signing in. Weather: -3 and cloudy | All Wastewater System ROC General | 2026-01-17
ROC | January | PVSS - Eric S unable to gain access to site. Leaving location. | All Wastewater System ROC General | 2026-01-23
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-15
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-17
ROC | January | YDSS + YNSS normal | All Wastewater System ROC General | 2026-01-17
ROC | January | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-01-20
ROC | January | MTSP - Air Compressor 1 Excessive Run time alarm came in. Checked site. Called Terry R. who directed to rotate duties so that air compressor 2 is running in duty 1. Rotated duties and alarm cleared 17:20 - Air Compressor 2 Excessive Run time alarm came in. Checked site. Called Terry R. again who directed to swap duties again and directed to continue swapping duties until the morning. 17:30 - Air Compressor Pressure 2 LoLo and Air compressor 1 pressure lo alarms came in. Checked site. Called Terry R. who is headed to site. Due to the snow, Terry R. requested a call to Mechanical on-call to see if they could get there faster. Called Tyler Smith but no answer. Left a message 17:37 - Air Compressor pressure's are rising and within normal operating parameters. Called Terry R. back to relay this information. Terry R. will no longer head to site. 17:45 - Terry R. informed Barry M. will head to site. CMU5 Created W11611787 #CONSULT | All Wastewater System ROC General | 2026-01-23
ROC | January | Carter Dunn Signing In, -14D/Clear | All Wastewater System ROC General | 2026-01-23
ROC | January | Angelica Chepiga signing in, weather -15C | All Wastewater System ROC General | 2026-01-20
ROC | January | KSSP, LSSS - Kingsley called to inform that he will be working on the local SCADA Servers and the work will trigger Historian Heartbeat alarms. Kingsley informed this will not interlock the anything on site | All Wastewater System ROC General | 2026-01-22
ROC | January | LSSS, KSSP - Kingsley M completing extended server work at these locations today. Local OIT's will not be available. Kingsley will be informing area ops. Kingsley stated that the historian heartbeat alarms can be disregarded. | All Wastewater System ROC General | 2026-01-22
ROC | January | SHSP - Kingsley M completing server work and will trigger a Historian heartbeat alarm which can be disregarded. | All Wastewater System ROC General | 2026-01-22
ROC | January | KCSSKR, Generator Running Alarm, Generator has been running since 10AM, notified Lauren S of this observation, it did clear earlier but did come back. Lauren S is heading back to NBSP, she will monitor it from there 14:55, Contacted Hydro One operator Dylan to inform them of a possible power outage, Dylan is transferring us to the outage team, they will call the ROC within 10 minutes to verify if its a power outage or if they need someone to go to site 15:16, Lauren S is heading to site to verify if site has power CMU5: W11593606 | All Wastewater System ROC General | 2026-01-15
ROC | January | KCSSKR - Hydro One onsite requesting access thorough gate. Informed Lauren S on what ETA would be, seeing it be over an hour, checked in with Mobile security if they are in area and appeared to be closer so Mannat from mobile security is heading to site in response. Informed Hydo One onsite contact as well 19:50 - Grant with Hydron One called back confirming everything is okay on their end with readings and no issues with power on their transformer. Believed to be possible issue with loss a a phase within the building. Informed Lauren S of update and that we have enough diesel for the night. Requested to inform Sean P as well. Informed Sean P of situation and both parties confirm its okay to leave for the night and respond firth thing in the morning. Consult | All Wastewater System ROC General | 2026-01-15
ROC | January | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-01-19
ROC | January | Christian Van Beek signing in. | All Wastewater System ROC General | 2026-01-22
ROC | January | RHAMF1, Unit 2 Recirculation Pump pressure/flow lolo and Pump 2 overload alarm, as per shift report, can disregard as both fans are currently running and the power is fine. Did Notify Jimmy from NAC who will head to site on Saturday to fix the pump issue | All Wastewater System ROC General | 2026-01-23
ROC | January | KSSP-Aeration disch temp lolo alarm came in. Notified Chris C. Directed to disregard as long as flow is maintained to aeration tanks. MUA 5 diff pressure switch alarm came in shortly after call. Chris C directed to disregard MUA alarms unless chem room temp lo alarms come in. #contsult | All Wastewater System ROC General | 2026-01-24
ROC | January | NBSP- Process building lo temp alarm emailed West Wastewater operators about outstanding alarm and will escalate if lolo temp alarm comes in. | All Wastewater System ROC General | 2026-01-24
ROC | January | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-01-20
ROC | January | SEOC67- Satnam M onsite for generator work. Generator will be unavailable until this afternoon. | All Wastewater System ROC General | 2026-01-20
ROC | January | SUSP- Influent Flow HiHi Alarm. Cleared alarm | All Wastewater System ROC General | 2026-01-22
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-23
ROC | January | KSSP- Chris C testing hihi membrane sump alarm | All Wastewater System ROC General | 2026-01-21
ROC | January | MTSP- Final Effluent Flow LoLo Alarm. Disregard as per SCADA Report. | All Wastewater System ROC General | 2026-01-22
ROC | January | KCSSKR- Hydro 1 (Brandon) called back and want the operator attending site to confirm the meter is blank on site and will attend site if electricity to site is being supplied to site. Notified Lauren S who will attend site. | All Wastewater System ROC General | 2026-01-15
ROC | January | NBSP - UV system minor fault alarm. Checked site, UV Bank 1B is active. Trending shows normal operations, the UV banks recently changed duties and Bank B activated. Shift report states that UV minor faults can be disregarded if one bank is running. | All Wastewater System ROC General | 2026-01-15
ROC | January | AUSS - Generator 1,2,3 not in auto alarms. Ack/reset - all alarms cleared. All generators in auto, pump 5 running. | All Wastewater System ROC General | 2026-01-11
ROC | January | HLSSBS- Inlet channel hihi alarm came in. Notified Tyson C. OPs already heading to site | All Wastewater System ROC General | 2026-01-15
ROC | January | KSSP - ZW5 TMP Control Low Alarm and ZW5 TMP Control Delta High alarm came in. Disregarded as per shift report | All Wastewater System ROC General | 2026-01-12
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-15
ROC | January | Carter Dunn Signing In, -13D/Blizzard | All Wastewater System ROC General | 2026-01-15
ROC | January | Adam Button signing in KCSSKR- Screen un commanded stop alarm. Cleared alarm | All Wastewater System ROC General | 2026-01-15
ROC | January | HLSSBS, Channel Grinder Temp Hi alarm, Notified Tyson C, he will look into the issue | All Wastewater System ROC General | 2026-01-15
ROC | January | Christian Van Beek signing in. Weather: 1C and clear. | All Wastewater System ROC General | 2026-01-13
ROC | January | KSSP - ZW5 TMP control delta high alarm and TMP control low alarm. Disregard all TMP control alarms as per the shift report. | All Wastewater System ROC General | 2026-01-13
ROC | January | Angelica Chepiga signing in,weather +2C | All Wastewater System ROC General | 2026-01-09
ROC | January | MTSP - MAn/start blower 1 as aeriation tank 1 DO lo 22:33 - Place blower 1 back in auto | All Wastewater System ROC General | 2026-01-07
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-07
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-08
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-08
ROC | January | KBSP - Lauren S working on Headworks. Requested disregard all headworks alarms for the duration of the work. | All Wastewater System ROC General | 2026-01-08
ROC | January | AUSSYS - Barry M running generator. | All Wastewater System ROC General | 2026-01-08
ROC | January | KSSP - Collection blower 2 high diff pressure alarm. Checked site, duty rotated to blower 1 and operations are normal. Called Cam B who directed to disregard this alarm and also disregard if blower 1 goes down. #consult | All Wastewater System ROC General | 2026-01-11
ROC | January | KCSSKR - Generator running status alarm. Checked site, generator is running and ATS is pointing to the generator indicating a power failure. Checked Alectra Utilities website, no reported outages on the outage map. Will monitor site. | All Wastewater System ROC General | 2026-01-11
ROC | January | NMSSBP - Pump 4 Vibration Hi alarm came in. Disregarded as per shift report | All Wastewater System ROC General | 2026-01-10
ROC | January | KCSS - Power restored. Generator stopped. | All Wastewater System ROC General | 2026-01-10
ROC | January | LSSS - Bar Screen 2 fault alarm, Chris R will attend site. # CMU5 W11577290 | All Wastewater System ROC General | 2026-01-10
ROC | January | LSSS - Bar screen 2 back in service, alarm cleared, Chris R leaving site. | All Wastewater System ROC General | 2026-01-10
ROC | January | SUSP, Neil O on site, running generator and temp alarms | All Wastewater System ROC General | 2026-01-07
ROC | January | KCSS - Young J running generator, testing sump pit, drywell flood, diesel containment flood, temperature alarms. | All Wastewater System ROC General | 2026-01-08
ROC | January | Connor Smith signing in 3C Rainy | All Wastewater System ROC General | 2026-01-09
ROC | January | MTSP, Aeration Tank 1 DO lo alarm, Placed blower 1 man/on to help the DO, will continue to monitor. As per shift report | All Wastewater System ROC General | 2026-01-09
ROC | January | NBSSJA- Gavin W onsite testing high level alarm | All Wastewater System ROC General | 2026-01-09
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-08
ROC | January | LSSS, Artour L is leaving site | All Wastewater System ROC General | 2026-01-07
ROC | January | KSSP- Rick L done on site | All Wastewater System ROC General | 2026-01-09
ROC | January | KBSP, Lauren S on site working on all the blowers | All Wastewater System ROC General | 2026-01-07
ROC | January | KSSP, Rick L/Eric S on site, doing annual calibrations | All Wastewater System ROC General | 2026-01-07
ROC | January | Christian Van Beek signing out. | All Wastewater System ROC General | 2026-01-15
ROC | January | Ethan Ullalkar signing out. | All Wastewater System ROC General | 2026-01-07
ROC | January | BLSS - Chris from PS onsite for monthly fire alarm testing | All Wastewater System ROC General | 2026-01-12
ROC | January | KCSSKR - Generator running status alarm. Known issue of generator running for one hour during power blips. Will monitor site. | All Wastewater System ROC General | 2026-01-14
ROC | January | MTSP, Aeration Tank 1 DO Lo alarm, Placed Blower 1 man/on to help the DO recover as per the on call shift report 15:58, Placed blower 1 back to auto | All Wastewater System ROC General | 2026-01-07
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-07
ROC | January | SEOC shaft 4 - Chris R onsite running generator and testing eyewash | All Wastewater System ROC General | 2026-01-14
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-15
ROC | January | Received a phone call from Edward Alfaro from MARS. Reported Glycol/water 50/50% mix spill at 7:50AM Yesterday morning. Tolal amount 150liters. 60 liters was contained and 90 liters spilled to the drain. - Notified Daniel K. and followed up with Edward . | All Wastewater System ROC General | 2026-01-07
ROC | January | LSSS - Artour L working on generator controller. | All Wastewater System ROC General | 2026-01-08
ROC | January | AUSSYS - Daniel K on site to test the dry well flood alarm and the hi/low temp alarms. | All Wastewater System ROC General | 2026-01-12
ROC | January | PVSS- Evgeniy S restarting OIT. | All Wastewater System ROC General | 2026-01-08
ROC | January | wrong book | All Wastewater System ROC General | 2026-01-08
ROC | January | JDSS - Tyson C onsite testing flood, temp, and autodialer alarm KSSP - Chase J onsite working on UV & turbidity | All Wastewater System ROC General | 2026-01-12
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-10
ROC | January | NMSSBP - Wet well 1 and 2 hydrostatic and ultrasonic level hi and hihi alarms came in with pump 3 pillow block hihi alarm. Checked site. Overflow not reached and duty 1, 2 and 3 active. Will continue to monitor site 10:20 - Alarms have cleared | All Wastewater System ROC General | 2026-01-10
ROC | January | SEOC4, Fans not running/Gas Hi Facility Shutdown, notified Chris R, he is looking into it | All Wastewater System ROC General | 2026-01-15
ROC | January | LSSS - Artour L on site , working on generator controller. | All Wastewater System ROC General | 2026-01-07
ROC | January | NMSSBP-SHTP- Evgeny S done work on OIT LSSS- Chris R on site to inspect Suction valves, bubbler system, Hydrostatic LIT and test hi lo temp alarm NBW2- Jordan B on site working on NTU and Cl2 analyzers and will test Cl2 leak alarm STPSMR- Travis W on site with Joe M to change Cl2 cylinder, Test Cl2 leak and scrubber | All Wastewater System ROC General | 2026-01-08
ROC | January | KSSSQW, Boiler 1 Fault, notified Cam B, directed to disregard for the night | All Wastewater System ROC General | 2026-01-13
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-13
ROC | January | Carter Dunn Signing Out | All Wastewater System ROC General | 2026-01-07
ROC | January | KSSP - Neut process (MC) Took too long. Informed Cam B, as CIP/neutralization appears its just finishing its cycle and now filling CIP_TK1. Cam B will monitor on SCADA to ensure steps are complete and tank fills Consult | All Wastewater System ROC General | 2026-01-07
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-11
ROC | January | RHAMF1 - Historian heartbeat alarm. Checked site, operations appear normal, trending is not impacted. Unable to reset alarm. Contacted Arthur L who will check site. Created CMU5#W11577439 #consult # CMU5 | All Wastewater System ROC General | 2026-01-11
ROC | January | Ethan U signing in Weather 4. | All Wastewater System ROC General | 2026-01-14
ROC | January | Ethan U signing in Weather 2. | All Wastewater System ROC General | 2026-01-07
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-12
ROC | January | Adeela Khan signing out | All Wastewater System ROC General | 2026-01-12
ROC | January | Ethan Ullalkar signing out. | All Wastewater System ROC General | 2026-01-14
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-14
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-10
ROC | January | MTSP - Aeration tank 1 DO lower than LoLo alarm setpoint. No alarm on SCADA. Aeration Blower 2/ duty 2 just activated. will monitor. 18:38 Aer tank 1 DO not recovering. Placed aeration blower 3 man/off / duty4 and selected Aeration tank 1 to duty 1. As per Chris R. # Consult | All Wastewater System ROC General | 2026-01-10
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-13
ROC | January | HLSSBS- Generator Running Status Alarm, Channel Grinder Uncommanded Stop Alarm. Cleared alarms. | All Wastewater System ROC General | 2026-01-09
ROC | January | BLSS - Lance J leaving site. Station back to normal OP. | All Wastewater System ROC General | 2026-01-09
ROC | January | Adeela Khan signing in | All Wastewater System ROC General | 2026-01-14
ROC | January | VNPSAP- Historian Heartbeat Alarm. Artour L is working on it. *Wrong Book | All Wastewater System ROC General | 2026-01-09
ROC | January | KCSSKR - Generator running alarm came in. Checked site. Generator is running and site is currently connected to generator power. Checked Hydro One outage map but no outage in the area. Called Lance J. who informs this may be a blip but if site does not go back to hydro power before 18:00, he would like a call back 17:47 - Gave Lance a call back and he will take a look on SCADA #CONSULT | All Wastewater System ROC General | 2026-01-10
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-12
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-12
ROC | January | Christian Van Beek signing in. Weather: -3C and clear. | All Wastewater System ROC General | 2026-01-12
ROC | January | Christian Van Beek signing out. | All Wastewater System ROC General | 2026-01-14
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-14
ROC | January | NMSSBP- Mech screen E stop and fault alarm came in. Terry C on site working on screens AUSS- OC Room H2s faults/OOR Combustible gas OOR and exhaust fan fault alarms came in. Called Barry M no answer. Will call again 12:57- AUSS- BarryM called back maintenance is working on installing heating units and has panel open. Once panel work is done Barry M will clear alarms | All Wastewater System ROC General | 2026-01-09
ROC | January | HLSSBS, Tyson C is finished on site CMU5: W11593358 | All Wastewater System ROC General | 2026-01-15
ROC | January | NBSP- Vortex 1 water scour uncmd close alarm reset as per shift report | All Wastewater System ROC General | 2026-01-15
ROC | January | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-01-10
ROC | January | LSSS- Generator 3 Warning Alarm, Generator 3 DGC Not in Auto Alarm. Chris R requested to notify Artour L. Artour L will look into it. W11577121 CMU5 | All Wastewater System ROC General | 2026-01-09
ROC | January | LSSS- Artour L was able to clear Gen 3 alarms and should be able to clear if they do return no issues found. | All Wastewater System ROC General | 2026-01-09
ROC | January | QVSSQS - Evgeni S onsite rebooting OIT, disregard hearbeat alarm SUSP - Air compressor pressure 1 & 2 lo. Informed Cam B, disregard as Neil O cleaning sand filter and using air from those compressors. | All Wastewater System ROC General | 2026-01-12
ROC | January | MTSS- Evgeny S. working on OIT | All Wastewater System ROC General | 2026-01-15
ROC | January | LSSS- Received a phone call from FMC about intrusion alarm. Called Chris R, he is heading to site. No response. Site disarmed, alarm cleared. | All Wastewater System ROC General | 2026-01-10
ROC | January | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-01-11
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-13
ROC | January | SHSP- Young J on site to work on UVs was P1/2 and will be testing sump hi level alarm | All Wastewater System ROC General | 2026-01-15
ROC | January | HMSS- Young J on site to test force main diversion hi level float and inspect motors and pumps | All Wastewater System ROC General | 2026-01-09
ROC | January | KBSP- Marcus R increasing aeration tank level to remove dead animal. will call when done KSSP- Chase J on site to work on alum system | All Wastewater System ROC General | 2026-01-08
ROC | January | SUSSWB- Satnam M on site working on auto dialer system | All Wastewater System ROC General | 2026-01-15
ROC | January | LSSS - David D on site with ABB to work on the pump 2 VFD. Pump 2 will be OOS until the end of the day | All Wastewater System ROC General | 2026-01-12
ROC | January | Ethan Ullalkar signing out. | All Wastewater System ROC General | 2026-01-13
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-12
ROC | January | YDSS + YNSS normal | All Wastewater System ROC General | 2026-01-13
ROC | January | LSSS - Intrusion alarm. FMC will notify corp. security. 00:37 Security reported site secured. | All Wastewater System ROC General | 2026-01-11
ROC | January | SEOC OCF - Fan 2 uncommanded stop alarm, alarm cleared. Fan 1 running on duty 2 , Assigned Fan 2 back to duty 1. | All Wastewater System ROC General | 2026-01-11
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-11
ROC | January | BLSS- Talha H working on OIT disregard historian until done work SUSP- UV Ch 1 high level and common critical and system critical failure alarm came in. Came in on UV start up disregard on shift report and alarms cleared upon acknowledgement | All Wastewater System ROC General | 2026-01-09
ROC | January | EGSSSC- Diesel Containment Flood Alarm. Notified Mike B. Can disregard. | All Wastewater System ROC General | 2026-01-09
ROC | January | MTSP- Aeration Tank 1 DO Lo Alarm. Placed Aeration Blower 1 man/on as per SCADA Report. 17:40- Placed Aeration Blower 1 back into auto | All Wastewater System ROC General | 2026-01-09
ROC | January | SEOC Shaft 6/7, Chris R on site running generator | All Wastewater System ROC General | 2026-01-07
ROC | January | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-01-10
ROC | January | SUSP - Lagoon flow lolo. Checked site, lagoon pumps operating. Shift report states that the lagoon flowmeter is currently OOS. | All Wastewater System ROC General | 2026-01-13
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-14
ROC | January | Angelica Chepiga signing out | All Wastewater System ROC General | 2026-01-07
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-09
ROC | January | BLSS - Gavin W on site to test the following alarms, hi/lo temp, dry well flood alarm and sump pit inspection. | All Wastewater System ROC General | 2026-01-12
ROC | January | PVSS, Young J on site, testing generator/temp/level and health and safety alarms | All Wastewater System ROC General | 2026-01-07
ROC | January | Ethan Ullalkar signing out. | All Wastewater System ROC General | 2026-01-08
ROC | January | JDSS- Chris C on site for JHS inspections and run diesel generator | All Wastewater System ROC General | 2026-01-08
ROC | January | LSSS - David D. called to inform that he will be shutting down pump 4 and 5 until tomorrow | All Wastewater System ROC General | 2026-01-14
ROC | January | YDSS + YNSS Normal Christian Van Beek signing out. | All Wastewater System ROC General | 2026-01-12
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-13
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-08
ROC | January | SECC - Hydrogen peroxide tank 1 level hi/hihi, Tank 1 at SECC has a hose slowly filling the tank with water. The high-level alarm is to be disregarded as per operator. Email sent | All Wastewater System ROC General | 2026-01-08
ROC | January | Angelica Chepiga signing in, weather +2C | All Wastewater System ROC General | 2026-01-08
ROC | January | SEOC - S2 Humid Chamber LoLo level switch alarm. Disregard as per the shift report. Alarm continues to come in. Will reset each time. | All Wastewater System ROC General | 2026-01-14
ROC | January | NMSSBP - Screen 1 overtorque alarm. Checked site, screen 2 is operating. Sent email to area ops as it is within 6 hours of them starting shift. | All Wastewater System ROC General | 2026-01-15
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-15
ROC | January | QVSSSC- Power loss on site. Generator running sewage pump 2/3 e stop alarm cleared pump alarms. Generator still running HLSSBS- Channel grinder failed to start hi temp alarm came in. Able to reset failed to start alarm | All Wastewater System ROC General | 2026-01-15
ROC | January | Adam Button signing in | All Wastewater System ROC General | 2026-01-09
ROC | January | PVSS - H2S OOR alarm, Young J requested disregard alarm. | All Wastewater System ROC General | 2026-01-07
ROC | January | QVSSSC - Chris C and Mike B working onsite. | All Wastewater System ROC General | 2026-01-07
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-07
ROC | January | Carter Dunn Signing In | All Wastewater System ROC General | 2026-01-07
ROC | January | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-01-08
ROC | January | PVSS - Evgeny S completed work. Historian Heartbeat alarm cleared. | All Wastewater System ROC General | 2026-01-08
ROC | January | AUSS- P4 disc hdr MV4 failed to open alarm came in. Reset alarm SEOC6 Shaft 6/7 gas high duty Rotation imminent reset as acknowledgment /Fan duty rotation imminent alarm and O2 alarms came in disregard on shift report | All Wastewater System ROC General | 2026-01-09
ROC | January | NBSP - Vortex #1 Water Scour Uncommanded Close alarm came in. Ack/reset as per shift report | All Wastewater System ROC General | 2026-01-12
ROC | January | KSSP - Rick L and Eric S on site for annual calibration. | All Wastewater System ROC General | 2026-01-08
ROC | January | LSSS- Generator 1/2 shutdown and generator 1/2/3 DGC/PGC not in auto alarms came in all generators in local. Dan B and Chris R will attend site. # CMU 5 W11573927 ( Chris R, Dan B). | All Wastewater System ROC General | 2026-01-08
ROC | January | KSSP- ZW2 permeate lo flow alarm/ train shutdown and permeate turbidity hihi alarms came in .notified Chris C | All Wastewater System ROC General | 2026-01-09
ROC | January | KCSS - Generator Running status alarm, power failure alarm on the dialer. Power blip, generator stopped. alarm cleared. | All Wastewater System ROC General | 2026-01-08
ROC | January | LSSS- Chris R done on site | All Wastewater System ROC General | 2026-01-08
ROC | January | KSSP- Alum tank hihi alarm came in. Notified Cam B. Kevin K on site receiving alum #consult | All Wastewater System ROC General | 2026-01-08
ROC | January | AUSS- Conveyor 2 not in auto alarm came in and Bar screen general alarm came in. Bar screen in local. | All Wastewater System ROC General | 2026-01-09
ROC | January | BLSS- Talha H done work on OIT cleared historian heartbeat alarm | All Wastewater System ROC General | 2026-01-09
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-11
ROC | January | Connor Smith signing out | All Wastewater System ROC General | 2026-01-09
ROC | January | RHAMF - Kingsley M rebooting the OIT and directed to disregard the Historian Heartbeat alarm. | All Wastewater System ROC General | 2026-01-12
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-08
ROC | January | SHSP- Lance J testing sludge holding tank hi level | All Wastewater System ROC General | 2026-01-09
ROC | January | SUSP- Equalization tank level hi alarm came in. Notified Cam B Decant at 95% the equalization pumps will catch up once completed. Cam B will check SCADA later tongiht to ensure plants keeping up with higher f lows | All Wastewater System ROC General | 2026-01-09
ROC | January | HMSS- Evgeny S rebooting OIT disregard historian heartbeat alarm until done NBSSJA- Evgeny S done rebooting OIT | All Wastewater System ROC General | 2026-01-08
ROC | January | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-01-09
ROC | January | KSSP- Kevin K done on site | All Wastewater System ROC General | 2026-01-08
ROC | January | LSSS- Generator 1/2 shutdown and generator 1/2/3 DGC/PGC not in auto alarms came in all generators in local. Notified Chris R. Will consult Dan B about issue. #Consult | All Wastewater System ROC General | 2026-01-08
ROC | January | LSSS, Artour L is currently on site, notified the ROC that him and Matt S are requesting the on call operator to come to site and start up the generator to make sure that it works. Artour/Matt have been updating the programming of the generator and are wanting to make sure the generator works. Both Chris R/Dan B are currently heading to site. Contacted both of them to let them know they are there and that they are wanting assistance. | All Wastewater System ROC General | 2026-01-08
ROC | January | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-01-10
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-10
ROC | January | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-01-11
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-11
ROC | January | YDSS + YNSS normal | All Wastewater System ROC General | 2026-01-13
ROC | January | LSSS - Kent R onsite, requested to have pump 3 running. | All Wastewater System ROC General | 2026-01-12
ROC | January | Bayview OCF - Kevin S onsite turning off fan for few minutes for work | All Wastewater System ROC General | 2026-01-12
ROC | January | YDSS+YNSS NORMAL Angelica Chepiga signing out | All Wastewater System ROC General | 2026-01-10
ROC | January | SUSP - UV channel critical alarms. Checked site, flow to the UV channel recently started. Known issue, disregard as per the shift report. | All Wastewater System ROC General | 2026-01-11
ROC | January | KCSSKR - Generator still running, called Lance J to inform so he is aware of the situation. Lance stated that this occurs when power blips trigger the generator and it should shut down after an hour. #Consult | All Wastewater System ROC General | 2026-01-11
ROC | January | AUSS - Barry M onsite testing dry well flood alarm | All Wastewater System ROC General | 2026-01-14
ROC | January | SHSSDK- Evgeny S done rebooting OIT NBSSJA - Evgeny S rebooting OIT disregard historian heartbeat alarm until done | All Wastewater System ROC General | 2026-01-08
ROC | January | HLSSBS - Mike B. and Tyson C. are on site for a wet well entry. Mike informed that this will trigger a hihi switch and overflow alarm | All Wastewater System ROC General | 2026-01-14
ROC | January | Adam Button signing out YDSS+YNSS normal | All Wastewater System ROC General | 2026-01-08
ROC | January | Carter Dunn Signing In, 1D/Clear | All Wastewater System ROC General | 2026-01-08
ROC | January | KSSP, Rick L is leaving site | All Wastewater System ROC General | 2026-01-07
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-14
ROC | January | KCSSKR - Generator running. Monitoring site. No issues with pump | All Wastewater System ROC General | 2026-01-14
ROC | January | SUSP - Ian W working on OIT, disregard historian heartbeat alarm for the duration of the work. | All Wastewater System ROC General | 2026-01-08
ROC | January | Angelica Chepiga signing out | All Wastewater System ROC General | 2026-01-08
ROC | January | KCSSKR - Generator running alarm from earlier. Checked site and noticed that the generator is no longer running and site is back to running on hydro power. Cleared alarm | All Wastewater System ROC General | 2026-01-11
ROC | January | MTSP- Aeration tank 1 do lo alarm. Blower 1 placed in man/on as per shift report 15:52- MTSP- Aeration tank 1 DO recovered cleared alarm placed blower1 in auto as pershift report | All Wastewater System ROC General | 2026-01-09
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-11
ROC | January | Angelica Chepiga signing in, weather 0C | All Wastewater System ROC General | 2026-01-07
ROC | January | AUSS - Barry M running generator. | All Wastewater System ROC General | 2026-01-07
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-09
ROC | January | YDOC - Chris R running generator and testing eyewash alarm. | All Wastewater System ROC General | 2026-01-07
ROC | January | RHAMF1 - Kyle C working on PAC cabinet. Disregard commfail alarm for the duration of the work. | All Wastewater System ROC General | 2026-01-07
ROC | January | LSSS, Chris R/Dan B/Artour L are leaving site | All Wastewater System ROC General | 2026-01-08
ROC | January | MTSP- Aeration tank 1 DO lo alarm came in. Placed Blower 1 in man/on as per interim 15:32-MTSP- Aeration tank 1 DO lo recovered Placed Blower 1 in auto as per interim SHSSDK- Evgeny S rebooting OIT disregard historian heartbeat alarm until done | All Wastewater System ROC General | 2026-01-08
ROC | January | NMSSBP- Wet well 1/2 hydrostatic and ultrasonic hi alarms came in. Duty 2 active most likely due to hi flows will monitor | All Wastewater System ROC General | 2026-01-09
ROC | January | Christian Van Beek signing in. Weather: -2C and clear. | All Wastewater System ROC General | 2026-01-11
ROC | January | NMSSJA - Diesel tank level HiHi alarm, disregard as per shift report. | All Wastewater System ROC General | 2026-01-11
ROC | January | NBSP - Vortex #1 Air Scour Uncommanded Close alarm came in. Ack/reset as per shift report | All Wastewater System ROC General | 2026-01-11
ROC | January | YDSS + YNSS normal | All Wastewater System ROC General | 2026-01-12
ROC | January | SUSP - Inlet flow hihi alarm. Checked site, flow spiked while a pumping station wet well was pumped down. Flow normal, reset alarm. | All Wastewater System ROC General | 2026-01-11
ROC | January | MTSS- Phil R on site testing dry well flood alarm | All Wastewater System ROC General | 2026-01-09
ROC | January | NMSSBP, Mech Screen 2 Overtorque Alarm, Operators will be on site in the morning, will send email so operators can attend site. Screen 1 is still available | All Wastewater System ROC General | 2026-01-09
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-13
ROC | January | HMSS- Evgeny S done rebooting OIT | All Wastewater System ROC General | 2026-01-08
ROC | January | NBSP- Mech bar screen max successive starts/ inlet channel hi hi and hi float alarms/diff level hihi alarms came in. Trends recovering. Notified Gavin W. On site clearing out rags causing mech screen to run more often | All Wastewater System ROC General | 2026-01-09
ROC | January | STETTL - Cory from Town of Stouffville flushing in zone 2. | All Wastewater System ROC General | 2026-01-07
ROC | January | SUSP - Neil O called to disregard filter feed N/A and UV alarms while working on site | All Wastewater System ROC General | 2026-01-13
ROC | January | YDSS + YNSS Normal Adeela Khan signing out | All Wastewater System ROC General | 2026-01-10
ROC | January | SEOC/SUSSHS, Evgeni S resetting OITs, disregard historian alarms from site | All Wastewater System ROC General | 2026-01-13
ROC | January | KCSSKR- FMC called about intrusion alarm. OPs not check in on site FMC will follow up with Security | All Wastewater System ROC General | 2026-01-08
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-11
ROC | January | EGSSSC - Eric S. and Ricardo L. are finished on site | All Wastewater System ROC General | 2026-01-14
ROC | January | NMSSHS - Oxygen LoLo alarm came in. As this is a critical alarm, called Chris R who directed to disregard alarm and he will warn the team in the morning #CONSULT | All Wastewater System ROC General | 2026-01-12
ROC | January | EGGSSC- Mike B on site for generator run | All Wastewater System ROC General | 2026-01-08
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-08
ROC | January | Adeela Khan signing in. Weather: -5 and Windy | All Wastewater System ROC General | 2026-01-11
ROC | January | SUSSHS - Terry C finished at site | All Wastewater System ROC General | 2026-01-13
ROC | January | HLSSBS - Mike B on site for a generator test. | All Wastewater System ROC General | 2026-01-12
ROC | January | SUSP- Basin 1 level hi alarm came in. Notified Cam B. SBR 1 currently in settling sequence and will flow into EQ during decant cycle | All Wastewater System ROC General | 2026-01-09
ROC | January | Adeela Khan signing out | All Wastewater System ROC General | 2026-01-13
ROC | January | SEOC/SUSSHS - Evgeny S working on OIT. Disregard heartbeat alarm | All Wastewater System ROC General | 2026-01-13
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-07
ROC | January | KSSP - Darren B. called to inform that he will be in the headworks building testing the gas detectors | All Wastewater System ROC General | 2026-01-14
ROC | January | EGSSSC - Rick L & Erick S onsite looking into wet well overflow fault | All Wastewater System ROC General | 2026-01-14
ROC | January | NBSP- Gavin W working on aeration, grit sludge blowers RHAMF1- Dan K on site and directed to disregard alarms on site SUSP- Ian W done working on OIT SHSSDK/NBSSJA/HMSS/PVSS- Evgeny S working on OITs instructed to call if historian heartbeat alarm comes in | All Wastewater System ROC General | 2026-01-08
ROC | January | NBSP - Aeration Basin 2 Back DO Lo alarm came in. Checked site. Only one blower is running. Placed Aeration blower 1 man/on, as per interim procedure 19:00 - Placed blower 1 back to auto 21:27 - Alarm came back in. Called Lance J. who directed to switch the controlling probe to tank 2 and monitor 21:56 - Lance called back to inform that he will head to site for the lo DO. CMU5 created W11577497 23:33 - Lance called back to inform that he cleaned the probes, and it seems to be reading consistently now. Lance directed to place the second blower on if the levels start to dip again. #CONSULT #CMU5 | All Wastewater System ROC General | 2026-01-11
ROC | January | Carter D Signing In, 1D/Clear | All Wastewater System ROC General | 2026-01-13
ROC | January | KBSP, Lauren S on site working on the air compressors | All Wastewater System ROC General | 2026-01-13
ROC | January | SUSSWB - Neil O running generator | All Wastewater System ROC General | 2026-01-08
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-14
ROC | January | YDSS + YNSS Normal Adeela Khan signing out | All Wastewater System ROC General | 2026-01-14
ROC | January | Christian Van Beek signing in. Weather: -3C and clear. | All Wastewater System ROC General | 2026-01-14
ROC | January | KSSSQW- Channel Grinder 1 Overload Alarm, Channel Grinder 1 Failed to Start Alarm. Overload Alarm will not clear. Notified Cam B. Will leave outstanding. He will check on it on Sunday. CONSULT | All Wastewater System ROC General | 2026-01-09
ROC | January | YDSS+YNSS normal Adam Button signing out | All Wastewater System ROC General | 2026-01-09
ROC | January | KSSP- Rick L on site with Eric S on site for annual calibrations SUSP- Bar Screen hi level alarm came in alarm reset as acknowledged | All Wastewater System ROC General | 2026-01-09
ROC | January | SUSP - UV channel 1 high level, common critical and critical failure alarm. Checked site, UV channel 1 active. Trending shows that flow recently started for this UV channel. Alarm status changed to normal immediately after alarms triggered. Disregard as per the shift report. Cleared alarms. | All Wastewater System ROC General | 2026-01-14
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-15
ROC | January | YDOC - Talha H onsite working on OIT, disregard heartbeat alarm | All Wastewater System ROC General | 2026-01-12
ROC | January | KSSSQW - Tyson C on site to complete work orders including a generator test, eyewash test and dry well flood alarm test. | All Wastewater System ROC General | 2026-01-12
ROC | January | YDSS + YNSS Normal NBSP - Vortex #1 Water Scour Uncommanded Close alarm came in. Ack/reset as per shift report | All Wastewater System ROC General | 2026-01-10
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-11
ROC | January | KSSP - ZW5 TMP Control Delta High alarm came in. Disregarded as per shift report | All Wastewater System ROC General | 2026-01-11
ROC | January | SUSP- Basin 1 High Level Alarm. Notified Cam B. He will log in and divert Wood River Bend Flow. CONSULT | All Wastewater System ROC General | 2026-01-09
ROC | January | Ethan U signing in | All Wastewater System ROC General | 2026-01-12
ROC | January | NBSSJA - Bill VB and terry C on site to complete maintenance on pump 1. | All Wastewater System ROC General | 2026-01-12
ROC | January | KSSSQW and SUSP - Evgeny S working on the OIT's. Directed to disregard Historian heartbeat alarm. YDSS - Talha H rebooting the OIT. Directed to disregard Historian heartbeat alarm. | All Wastewater System ROC General | 2026-01-12
ROC | January | KCSSKR - Generator running status alarm came in. Checked site. Site is connected to generator power. Pumps were not affected | All Wastewater System ROC General | 2026-01-14
ROC | January | NMSSBP- Evgeny S working on OIT disregard historian heartbeat until done | All Wastewater System ROC General | 2026-01-08
ROC | January | NMSSBP - Satnam M and Brent St C on site to complete work on the autodialer system. | All Wastewater System ROC General | 2026-01-12
ROC | January | SUSP - UV Channel 1 Bank 1 A low UV intensity fault alarm. Checked site, both UV banks in channel 1 are active. Trending shows that Bank 1 recently activated and followed a normal sequence of intensity readings. No major or critical faults present, disregard as per the shift report which states that UV minor fault alarms can be disregarded. | All Wastewater System ROC General | 2026-01-14
ROC | January | KSSP- Membrane Chem room/ Admin eye wash station activation alarms came in . Notified Chase J on site with Chris C testing alarms SHSP- Sldg Blower 2 fan overload alarm came in fan in man/off currently. Notified Lance J directed to disregard and will investigate later today | All Wastewater System ROC General | 2026-01-08
ROC | January | BLSS - Pump 3 uncommanded stop alarm, Pump 4 started on duty 1. Mechanical bar screen failed, cleared alarm, restarted ok. Pump 3 discharge valve alarm. Cleared alarm. Pump 3 restarted on duty 1. | All Wastewater System ROC General | 2026-01-09
ROC | January | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-01-09
ROC | January | EGSSSC - Power failure alarm on the dialer. No alarms on SCADA. All trends ok. | All Wastewater System ROC General | 2026-01-10
ROC | January | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-01-10
ROC | January | SHSP - Lance J on site to complete head works maintenance work orders. Lance will be triggering emergency stop alarms on equipment. | All Wastewater System ROC General | 2026-01-12
ROC | January | KSSSKR - Generator running status. Checked site, operations normal, generator running, ATS pointing to generator. Likely a power blip, the generator is programmed to run for one hour. Will monitor site. | All Wastewater System ROC General | 2026-01-12
ROC | January | KSSSQW- Chris C and Mike B on site to test wet well level alarms | All Wastewater System ROC General | 2026-01-09
ROC | January | KSSP - Mem Basement MUA -9 temp switch low alarm, disregard as per SCADA review. | All Wastewater System ROC General | 2026-01-11
ROC | January | NBSP - UV system Minor fault alarm, UV Bank 1B is running, disregard alarm as per shift report. | All Wastewater System ROC General | 2026-01-11
ROC | January | NBSP, Gavin W working on the dewatering screws/bar screen and vortex equipment, directed to disregard alarms from headworks till he is finished | All Wastewater System ROC General | 2026-01-13
ROC | January | KBSP, Reject Sump Pump 1 E Stop Alarm, as per shift report will disregard, if second sump fails, will contact operator | All Wastewater System ROC General | 2026-01-07
ROC | January | GRSSWA, Chris C/Mike B on site testing the overflow and flood alarms on site, directed to disregard | All Wastewater System ROC General | 2026-01-07
ROC | January | SUSP - UV system critical failure, Cam B cleared alarms remotely. # Consult | All Wastewater System ROC General | 2026-01-09
ROC | January | YDSS + YNSS Normal Christian Van Beek signing out. | All Wastewater System ROC General | 2026-01-11
ROC | January | KSSP - Rick L and Eric S finished on site. | All Wastewater System ROC General | 2026-01-08
ROC | January | KSSP - ZW2 TMP Control delta high alarm, disregard as per shift report. | All Wastewater System ROC General | 2026-01-10
ROC | January | SUSP - UV Channel Critical alarm came in and went normal right away. Checked site. Shift report indicates this is a known issue. | All Wastewater System ROC General | 2026-01-11
ROC | January | KSSSQW - Channel grinder 1 fail to start and overload alarms. Checked site, grinder showing in local mode. Cleared alarms and monitored site. noticed that the grinder stopped in local mode, then activated, then stopped in manual mode and then started in auto mode. The swapping of control modes is abnormal but operations appear normal in auto. Will send an email to Area ops if no other issues arise. Will call out if other issues arise. | All Wastewater System ROC General | 2026-01-11
ROC | January | NBSP - Vortex 1 water scour uncommanded close alarm. Reset alarm as per shift report. | All Wastewater System ROC General | 2026-01-11
ROC | January | KSSP - Collection blower 2 high diff pressure alarm. Checked site, collection blower duty rotated to blower 1, operations appear normal. Unable to reset alarm. Sent email to OCO to check the blower today during their site visit. | All Wastewater System ROC General | 2026-01-11
ROC | January | AUSS- Chris R called. He is going to site to inspect possible high water levels and requested a CMU W11577112 CMU5 | All Wastewater System ROC General | 2026-01-09
ROC | January | Adeela Khan signing in. Weather: -1 and cloudy | All Wastewater System ROC General | 2026-01-10
ROC | January | KSSP - ZW5 TMP Control Delta High Alarm came in. Disregarded as per shift report | All Wastewater System ROC General | 2026-01-10
ROC | January | LSSS- P2 failed to start alarm came in. reset alarm | All Wastewater System ROC General | 2026-01-08
ROC | January | JDSS- Chris S done on site site back to normal ops | All Wastewater System ROC General | 2026-01-08
ROC | January | BLSS - Gavin W on site to test the wetwell overflow alarm. | All Wastewater System ROC General | 2026-01-12
ROC | January | YDSS+YNSS normal | All Wastewater System ROC General | 2026-01-09
ROC | January | Adam Button signing in | All Wastewater System ROC General | 2026-01-08
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-08
ROC | January | SHSP- Power Failure alarms came in. Notified Lance J. He is onsite and will monitor. SHSSDK- Generator Running Alarm. Still on utility power. Will clear once generator shuts down | All Wastewater System ROC General | 2026-01-09
ROC | January | KCSSKR- Control Panel Power Failure, Pump 1,2 Failed to Start, Dewatering Press Overload Alarm, Pump 1 Fault and Dewatering Press Overload Alarm would not clear. Notified Lance J. He will attend site. W11577055 CMU5 | All Wastewater System ROC General | 2026-01-09
ROC | January | Ethan Ullalkar signing out. | All Wastewater System ROC General | 2026-01-12
ROC | January | SUSSSR - Niel O on site testing the low temperature alarm. | All Wastewater System ROC General | 2026-01-12
ROC | January | YDBR - Fan 2 uncommanded stop alarm came in. Checked site. Ack and reset and alarm cleared. Will continue to monitor | All Wastewater System ROC General | 2026-01-10
ROC | January | YDSS + YNSS normal | All Wastewater System ROC General | 2026-01-10
ROC | January | Angelica Chepiga signing in, weather +2C | All Wastewater System ROC General | 2026-01-10
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-12
ROC | January | NBSP - UV System Minor Fault alarm came in. One bank is running. Disregarded as per shift report | All Wastewater System ROC General | 2026-01-13
ROC | January | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-01-10
ROC | January | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-01-11
ROC | January | YDSS+YNSS NORMAL | All Wastewater System ROC General | 2026-01-11
ROC | January | SUSP, Rick L is on site, working on the UV system | All Wastewater System ROC General | 2026-01-13
ROC | January | Adeela Khan signing in. Weather: -1C and Cloudy | All Wastewater System ROC General | 2026-01-12
ROC | January | BLSS - Pump 3 failed, Mechanical screen system not OK alarms. Alarm panel low battery alarm and diesel failure alarm on the dialer. Generators started and stopped. Pump 4 OOS alarm. Pump 1 fault alarm. Pump 2 running. Notified Lance J. Requested leave alarms outstanding, he will check SCADA. Consult 19:40 BLSS - Lance J will attend site . # CMU5 W11577171 | All Wastewater System ROC General | 2026-01-09
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-13
ROC | January | NBSP, UV System Minor Fault, Bank B is running, directed to disregard as per shift report | All Wastewater System ROC General | 2026-01-09
ROC | January | Carter D Signing Out | All Wastewater System ROC General | 2026-01-09
ROC | January | KSOCMA, Rick L on site working on the fans QVSSSC, Chris C on site, running generator and doing health and safety alarms | All Wastewater System ROC General | 2026-01-13
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-14
ROC | January | Angelica Chepiga signing out | All Wastewater System ROC General | 2026-01-11
ROC | January | LSSS- Phil from Public Health requested Pump 6 in duty 1 for sampling. | All Wastewater System ROC General | 2026-01-09
ROC | January | LSSS - Pump 2 OOS, David D will continue work tomorrow KSSP - Eric S onsite finished working at site | All Wastewater System ROC General | 2026-01-12
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-12
ROC | January | Carter Dunn Signing Out | All Wastewater System ROC General | 2026-01-13
ROC | January | Ethan U signing in | All Wastewater System ROC General | 2026-01-13
ROC | January | NMSSBP, Wet Well 1/2 hi alarms, Marcos T on site testing alarms | All Wastewater System ROC General | 2026-01-13
ROC | January | BLSS- Lauren S on site working on P5 | All Wastewater System ROC General | 2026-01-09
ROC | January | NMEQBP - Kingsley M working on the OIT and will trigger a historian heartbeat alarm. | All Wastewater System ROC General | 2026-01-02
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-04
ROC | January | Christian Van Beek signing in. Weather: -9 and clear. | All Wastewater System ROC General | 2026-01-05
ROC | January | KBSP - Reject Sump Pump 1 E. Stop alarm came in. Checked site. Reject sump pump 2 is available and in duty 1. Alarm can be disregarded as per shift report | All Wastewater System ROC General | 2026-01-02
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-03
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-02
ROC | January | KSSP - ZW2 MDF flow TMP delta high, TMP, pressure lo, TMP control low/delta high. Disregard as per shift report | All Wastewater System ROC General | 2026-01-04
ROC | January | PVSS - H2S OOR alarm. Disregard as per the shift report. KSSP - ZW2 TMP control delta high and control delta low. Disregard all TMP alarms for membranes as per the shift report. | All Wastewater System ROC General | 2026-01-05
ROC | January | SUSP - UV Ch.1 critical failure, common critical alarm. Shift report mentions as known issue with start up. Alarm went to normal state shortly | All Wastewater System ROC General | 2026-01-04
ROC | January | Christian Van Beek signing in. | All Wastewater System ROC General | 2026-01-02
ROC | January | MKRSEM- Called Toronto (Mehdi) and requested pumps off. | All Wastewater System ROC General | 2026-01-04
ROC | January | MTSP - Aeration tank 1 DO level has recovered. Deactivated second blower and placed in auto. | All Wastewater System ROC General | 2026-01-05
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-01
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-05
ROC | January | SUSP, Neil O on site, testing the filter sump alarms and the filter reject pumps, directed to disregard alarms | All Wastewater System ROC General | 2026-01-06
ROC | January | NMEQBP, Evgeni S resetting OIT | All Wastewater System ROC General | 2026-01-06
ROC | January | Carter Signing Out | All Wastewater System ROC General | 2026-01-06
ROC | January | KBSP - Reject sump pmp 1 E. stop. Disregard as per shift report as known issue with this reject sump triggering e. stop and W/O had been made. Will notify ops if pump2 faults as well | All Wastewater System ROC General | 2026-01-06
ROC | January | LSSS - Barry M called to request PCS assistance for Generator 3 not in auto issue. CMU = 11565263 | All Wastewater System ROC General | 2026-01-06
ROC | January | LSSS- FMC Called about intrusion alarm. NO one checked in on site. FMC will follow up with security | All Wastewater System ROC General | 2026-01-06
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-07
ROC | January | LSSS - Barry M finished at site with generator. Gen 3 still local off for the night. Will be further looked into tomorrow | All Wastewater System ROC General | 2026-01-07
ROC | January | YDSS+YNSS normal | All Wastewater System ROC General | 2026-01-01
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-05
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-06
ROC | January | MTSP - Aeriation tank 1 DO lo, man/start blower 1 | All Wastewater System ROC General | 2026-01-06
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-02
ROC | January | KSSP - ZW5 TMO control delta hi alarm. Disregard as per the shift report. | All Wastewater System ROC General | 2026-01-03
ROC | January | KBSP- Historian Heart beat alarm. Trends flatlined. Notified Marcus R. directed to disregard as this is part of PCS work to simulate power loss on site | All Wastewater System ROC General | 2026-01-06
ROC | January | NBSP- UV system minor fault alarm came in. UV bank 1B running okay disregard on shift report | All Wastewater System ROC General | 2026-01-01
ROC | January | NMEQBP - PAC Minor fault alarm. No impact to operations. Will send email to on call PCS. | All Wastewater System ROC General | 2026-01-06
ROC | January | AUSSYS, Barry M working on boiler 1 CMU5: W11565052 | All Wastewater System ROC General | 2026-01-06
ROC | January | SHSP - ALum pump 6 and 7 no flow alarm. Checked site, alum pump 6/7 are in auto but not running and the duty is set to OOS. Contacted Dan H who is on site and will check and reset the pump duties. | All Wastewater System ROC General | 2026-01-02
ROC | January | KBSP - AUT Tranf switch alarm, called and confirmed Marcus R &Lauren S onsite running generator | All Wastewater System ROC General | 2026-01-05
ROC | January | NMSSHS - Dan K onsite testing drywell flood | All Wastewater System ROC General | 2026-01-05
ROC | January | SECC, Chris R on site, Testing health and safety alarms, directed to disregard alarms till he leaves site | All Wastewater System ROC General | 2026-01-05
ROC | January | YDSS + YNSS Normal NBSP - Influent floe hihi alarm. Checked site, influent flow is reading slightly higher than the hihi alarm setpoint. Two pumps are active at NBSSJA which has provided high flow to NBSP. Monitoring situation. | All Wastewater System ROC General | 2026-01-04
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-06
ROC | January | Adam Button signing in -1 Clear | All Wastewater System ROC General | 2026-01-06
ROC | January | KSSP- Blower 2 lo flow/ No membrane blowers available. Zw3 shutdown. Notified Neil O. Will check SCADA and reset alarms. Directed to reset blower later in the night if it comes back in and to disregard if one train goes down overnight #Consult | All Wastewater System ROC General | 2026-01-01
ROC | January | KSSP - ZW5 TMP Control Low and Delta high alarms came in. Disregarded as per shift report | All Wastewater System ROC General | 2026-01-02
ROC | January | KBSP - Laureen S working on clarifier as well | All Wastewater System ROC General | 2026-01-05
ROC | January | Connor Smith signing in -8C Cloudy | All Wastewater System ROC General | 2026-01-03
ROC | January | KSSP - ZW2 TMP control low alarm, MDF flow incycle TMP low alarm, MDF Flow TMP delta high alarm and transmembrane pressure low alarm. Alarm status changed to normal shortly after the alarms triggered. Disregard TMP alarms as per the shift report. SEBR - S2 Humid chamber lolo level switch alarm has been consistently triggering. Every time this alarm triggers its condition status returns to normal and it clears itself on acknowledgement. Called Barry M to confirm this is not an issue, Barry directed to disregard until Monday at 10:00. #consult | All Wastewater System ROC General | 2026-01-04
ROC | January | SHSP - WAS pump 2 uncommanded stop alarm. Checked site, trending shows that there was no WAS flow when the alarm triggered, indicating the pump was not running when the alarm triggered. Able to reset alarm. | All Wastewater System ROC General | 2026-01-05
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-05
ROC | January | YDSS + YNSS normal | All Wastewater System ROC General | 2026-01-01
ROC | January | KSSP- ZW3 Control delta hi alarm came in. Disregard on shift report | All Wastewater System ROC General | 2026-01-01
ROC | January | SHSP - UV major fault alarm. Checked site, both UV banks are currently running. Trending shows that the alarm triggered shortly after UV Bank B activated. Trending shows that the UV transmittance intensity remained stable for UV bank A and UV Bank B. Shift report directs to disregard alarm if the UV transmittance levels are stable. Unable to clear alarm, sent email to area ops for investigation on site. | All Wastewater System ROC General | 2026-01-05
ROC | January | SHSSDK - Generator running alarm. Checked site, generator is running but ATS is pointing to town hydro indicating a short power failure. Pumps are available in auto. Operations normal. SHSP - Multiple alarms related to power failure triggered. Able to reset all alarms except Clarifier 2 rake drive cut out. Contacted Daniel H who will attend site to reset the clarifier. Operations appear normal. Created CMU5#W11556971 #consult # CMU5 | All Wastewater System ROC General | 2026-01-04
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-04
ROC | January | KSSP - Ricardo L. is on site for annual calibrations | All Wastewater System ROC General | 2026-01-02
ROC | January | KSSP - Blower 2 air flow switch alarm and no membrane blowers available alarm. Checked site, membrane blower 1 is manual/off and blower 2 is interlocked. Called Kevin K who will check the system. | All Wastewater System ROC General | 2026-01-02
ROC | January | LSSS - Chris R & Kevin S onsite running generator | All Wastewater System ROC General | 2026-01-05
ROC | January | NMSSBP - Terry C. is on site working on Mechanical Bar Screen 1 and has triggered the mechanical screen 1 Emergency Stop | All Wastewater System ROC General | 2026-01-02
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-03
ROC | January | SHSP- Effluent Pump 1,2,3 Uncommanded Start Alarm. Effluent Pump 1,2,3 Fail to Stop. Notified Dan H. He will attend site. 12:09- Dan H requested to have Ric L give him a call regarding LIT issue. Called Ric L. He will call Dan H. 12:45- Dan H. repaired issue and is leaving site. W11552910 CMU5 | All Wastewater System ROC General | 2026-01-01
ROC | January | KSSP - No Membrane Blowers available alarm came in but the value turned normal right away. This happened once before and cleared on its own. ZW2 Shutdown Alarm came in. Called Neil O. who directed to disregard the shutdown alarm but to call again if another train shutsdown. Neil also informed that he is aware of No membrane Blowers available alarm and to reset alarm if it comes in again #CONSULT | All Wastewater System ROC General | 2026-01-01
ROC | January | YDSS + YNSS normal | All Wastewater System ROC General | 2026-01-01
ROC | January | HMSS- Lauren S on site to run generator test hi lo temp and drywell flood alarm | All Wastewater System ROC General | 2026-01-06
ROC | January | SEOC- OCF dampener station flood alarm came in. Disregard on shift report | All Wastewater System ROC General | 2026-01-06
ROC | January | AUSSYS- Boiler 1 fault outstanding Notified Barry M will take a look NMSSHS- David D on site to work on sump pumps | All Wastewater System ROC General | 2026-01-06
ROC | January | KSSP- Blower 2 Air Flow Switch Low Alarm, ZW3 Shutdown Alarm, ZW3- Blowers Not Available Alarm. Notified Neil O. He will log on to reset. CONSULT | All Wastewater System ROC General | 2026-01-01
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-03
ROC | January | YDSS + YNSS Normal Christian Van Beek signing out. | All Wastewater System ROC General | 2026-01-03
ROC | January | SUSP - Bar screen hi/ not available. Informed Neil O, is aware and will reset. Disregard for now Consult | All Wastewater System ROC General | 2026-01-04
ROC | January | Ethan U signing in | All Wastewater System ROC General | 2026-01-05
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-06
ROC | January | Adam Button signing out | All Wastewater System ROC General | 2026-01-06
ROC | January | QVSSSC - Inlet channel high switch and loss of echo alarms. Checked site, operations appear normal. Disregard alarms as per the shift report. | All Wastewater System ROC General | 2026-01-06
ROC | January | SUSP - UV channel 1 common critical, high level and UV system critical failure alarm. Checked site, flow through the UV channel recently started. Shift report details that this is a common alarm sequence when the UV channel initiates flow and can be reset when it occurs. All alarm statuses changed to "Normal" quickly and cleared on acknowledgement. | All Wastewater System ROC General | 2026-01-05
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-06
ROC | January | NMSSBP - Mechanical screen 1 uncommanded start alarm. Checked site, barscreen 1 is manual/off and barscreen 2 is running un auto. Disregard alarm as per the shift report. NBSP - ALUM tank level low alarm. Checked site, alum tank is low. Based on the trending for 24 hours the alum level should remain above the lolo level alarm setpoint through the weekend. Area ops should be on site tomorrow for their scheduled weekend visit. Will send an email to area ops. | All Wastewater System ROC General | 2026-01-03
ROC | January | MTSP- Aeration Tank 1 DO Lo Alarm. Placed Blower 1 man/on as per SCADA Report. 20:55- Placed Blower 1 man/off 22:20- Placed Blower 1 back into auto | All Wastewater System ROC General | 2026-01-03
ROC | January | Christian Van Beek signing out. | All Wastewater System ROC General | 2026-01-06
ROC | January | Carter Dunn Signing in | All Wastewater System ROC General | 2026-01-06
ROC | January | KSSP, Rick L on site doing annual calibrations | All Wastewater System ROC General | 2026-01-06
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-01
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-01
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-04
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-01
ROC | January | SHSSDK, Lance J on site running generator | All Wastewater System ROC General | 2026-01-06
ROC | January | Connor Smith signing in -19 Cloudy | All Wastewater System ROC General | 2026-01-01
ROC | January | Adeela Khan signing out | All Wastewater System ROC General | 2026-01-02
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-03
ROC | January | Connor Smith signing out | All Wastewater System ROC General | 2026-01-03
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-01
ROC | January | Adam Button signing in -10 clear | All Wastewater System ROC General | 2026-01-01
ROC | January | KSSP- Membrane blower 2 speed deviation alarm came in cleared upon acknowledgement | All Wastewater System ROC General | 2026-01-01
ROC | January | LSSS, Generator 1/2 Warning Alarm//PGC & DGC Not in auto alarm, notified Barry M, he will head to site 17:35, Barry M called back, requesting assistance from on call electrician. Notified Kyle R of the issue, he will get in contact with Barry M CMU5: W11565200 (Barry M) CMU5: W11565223 (Kyle R) | All Wastewater System ROC General | 2026-01-06
ROC | January | KSSP, Rick L finished on site | All Wastewater System ROC General | 2026-01-06
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-07
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-07
ROC | January | MTSP, Terry R on site doing a generator run | All Wastewater System ROC General | 2026-01-05
ROC | January | Connor Smith signing in -6C Cloudy | All Wastewater System ROC General | 2026-01-02
ROC | January | YDSS+YNSS normal | All Wastewater System ROC General | 2026-01-01
ROC | January | MTSP- Thickening tank level fault alarm came in. Disregard on shift report | All Wastewater System ROC General | 2026-01-02
ROC | January | YDSS+YNSS normal | All Wastewater System ROC General | 2026-01-02
ROC | January | Christian Van Beek signing out. | All Wastewater System ROC General | 2026-01-02
ROC | January | Ethan Ullalkar signing out. | All Wastewater System ROC General | 2026-01-05
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-06
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-03
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-03
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-04
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-04
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-04
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-04
ROC | January | AUSS- P4 MV2 failed to open alarm came in. Reset alarm KSSP- Collection blower 2 hi diff pressure alarm came in. Blower 1 running okay. Emailed North Waste water team | All Wastewater System ROC General | 2026-01-06
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-04
ROC | January | Christian Van Beek signing in. Weather: -11 and clear. | All Wastewater System ROC General | 2026-01-04
ROC | January | NMVCBA- Placed valve back into auto | All Wastewater System ROC General | 2026-01-04
ROC | January | KSSP - Membrane blower 2 low flow and No blowers available alarms came in. Checked site. Ack/reset as per shift report ZW3 Shutdown alarm came in. Called Neil O. who will check Scada and reset alarm #CONSULT | All Wastewater System ROC General | 2026-01-02
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-03
ROC | January | NBSP, Gavin W on site running the generator | All Wastewater System ROC General | 2026-01-05
ROC | January | KSSP - Train 3 shutdown alarm. Membrane blower 2 is faulting occasionally on low air flow/no blowers available when train 3 runs. Disregard as per shift report | All Wastewater System ROC General | 2026-01-05
ROC | January | Ethan U signing in Weather: -10 | All Wastewater System ROC General | 2026-01-04
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-06
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-06
ROC | January | YDSS + YNSS Normal Connor Smith signing out | All Wastewater System ROC General | 2026-01-04
ROC | January | LSSS - Bar screen 2 fault. Informed Barry M, will head to site CMU = 11556947 | All Wastewater System ROC General | 2026-01-04
ROC | January | NBSP - Mechanical barscreen fail to stop and OOS alarms. Site is currently receiving higher than normal flows from the NBSSJA. Able to reset alarms but they triggered again. Monitoring situation. | All Wastewater System ROC General | 2026-01-04
ROC | January | Christian Van Beek signing out. | All Wastewater System ROC General | 2026-01-05
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-05
ROC | January | NBSP - Inlet channel level hihi and mech bar screen diff level hihi. Plant is currently experiencing high inlet flows from NBSSJA. The pumping station is near duty 2 stop, which will reduce flows into the plant and allow it to catch up. Monitoring situation. | All Wastewater System ROC General | 2026-01-04
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-05
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-02
ROC | January | KSSP- Neut Process (MC) Took Too Long Alrm. Notified Neil O. He will look into it. CONSULT | All Wastewater System ROC General | 2026-01-02
ROC | January | SHSP - David D & Lance J onsite working on UV bank 1 | All Wastewater System ROC General | 2026-01-05
ROC | January | Carter Dunn Signing In, -3D/Snow | All Wastewater System ROC General | 2026-01-05
ROC | January | Ethan U signing in | All Wastewater System ROC General | 2026-01-05
ROC | January | YDSS+YNSS Normal Adam Button signing out | All Wastewater System ROC General | 2026-01-02
ROC | January | Adeela Khan signing out | All Wastewater System ROC General | 2026-01-01
ROC | January | SEOC- Chris R on site for generator run and eye wash test NMSSBP- Power fail alarms on site Discharge valves faulted generator running pumps all off P2 running in auto. Reset alarms. Barry M on site to complete work orders NMVCBP- Power loss on site pumps shutdown cleared alarms related to NMSSBP generator alarm | All Wastewater System ROC General | 2026-01-06
ROC | January | YDSS+YNSS normal | All Wastewater System ROC General | 2026-01-01
ROC | January | Adeela Khan signing in. Weather: -11 and clear | All Wastewater System ROC General | 2026-01-02
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-03
ROC | January | NMEQBP, PAC minor fault alarm. Ian W believes it may come back in after his work, directed to disregard for the night | All Wastewater System ROC General | 2026-01-05
ROC | January | NBSSJA- Harie R on site to run generator, test dialer. Drywell flood alarm as well as hi lo temp alarms | All Wastewater System ROC General | 2026-01-06
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-01
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-01
ROC | January | SHSP - Power blip in area, clarifier rake 2 drive cut, RAS pumps uncmd stop, sludge blower alarms. Unable to clear clarifier drive cut alarm after informing Dan H. Dan H will head to site CMU = 11565272 | All Wastewater System ROC General | 2026-01-06
ROC | January | SHSP, Lance J on site running generator | All Wastewater System ROC General | 2026-01-05
ROC | January | NMSSHS, Daniel K on site running generator SUSSHS, Neil O on site running generator and testing temp alarms | All Wastewater System ROC General | 2026-01-05
ROC | January | GRSSWA - Mech screen E stio, power N/A. Called Tyson C, no response | All Wastewater System ROC General | 2026-01-05
ROC | January | KBSP, Sludge/CP/Teritary/RASWAS/Alum PAC Minor fault, Lauren S on site, requesting PCS to look into it, notified Ian W, he will look into it | All Wastewater System ROC General | 2026-01-05
ROC | January | Carter D Signing Out | All Wastewater System ROC General | 2026-01-05
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-05
ROC | January | KSSP- Blower 2 air flow lo/ ZW3 shutdown and no blowers available alarms came in. Reset membrane blower alarms and emailed North Wastewater about train 3 OOS as per Neil O | All Wastewater System ROC General | 2026-01-02
ROC | January | YDSS+YNSS normal | All Wastewater System ROC General | 2026-01-02
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-03
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-04
ROC | January | MTSP - Aeration tank 1 DO low alarm. Activated a second blower in manual mode as per the shift report. | All Wastewater System ROC General | 2026-01-04
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-05
ROC | January | MTSP- Aeration tank DO lo alarm came in. Placed Aeration blower 1 in man/on as per interim 21:35-MTSP-Placed Aeration blower 1 in Auto as per interim | All Wastewater System ROC General | 2026-01-01
ROC | January | KSSP - Rick L finished and leaving site. | All Wastewater System ROC General | 2026-01-02
ROC | January | KSSSQW - Kevin K. called to inform he is running the pumps in manual | All Wastewater System ROC General | 2026-01-02
ROC | January | KSSP- Blower 2 AIr Flow Switch Low Alarm, ZW3- Blowers Not Available Alarm, No Membrane Blowers Available Alarm, Cleared alarms as per SCADA Report. ZW3 Shutdown Alarm. Emailed Neil O. Will call if a second Membrane shuts down, as per SCADA Report. | All Wastewater System ROC General | 2026-01-02
ROC | January | NMEQBP- PAC Minor Fault Alarm. Will email Ian W. | All Wastewater System ROC General | 2026-01-03
ROC | January | SECC- Sump 1 Level Low Switch, Sump 1 Inlet MV1 Failed to Open. Alarms cleared. | All Wastewater System ROC General | 2026-01-03
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-02
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-03
ROC | January | SUSP- UV System Critical Failure, UV. Ch. 1 High Level Alarm, UV CH. 1 Common Critical Alarm. Notified. Neil O. Requested to clear alarms. CONSULT | All Wastewater System ROC General | 2026-01-01
ROC | January | Christian Van Beek signing in. Weather: -10C and clear. | All Wastewater System ROC General | 2026-01-03
ROC | January | KSSSQW - Pump 3 Vibration OOR Alarm came in. Disregarded as per shift report | All Wastewater System ROC General | 2026-01-01
ROC | January | Ethan Ullalkar signing out. | All Wastewater System ROC General | 2026-01-04
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-06
ROC | January | YDSS + YNSS Normal Connor Smith signing out | All Wastewater System ROC General | 2026-01-01
ROC | January | KCSSKR - Generator running, called and informed Dan H. Outage map shows restoration time around 20:10 | All Wastewater System ROC General | 2026-01-06
ROC | January | KBSP- Marcus R on site with PCS and will be simulating power fails on the network side of things | All Wastewater System ROC General | 2026-01-06
ROC | January | Ethan. U Signing the in Weather: 0 freezing rain | All Wastewater System ROC General | 2026-01-06
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-05
ROC | January | SUSP - Neil O onsite working on bar screen | All Wastewater System ROC General | 2026-01-05
ROC | January | YDSS + YNSS Normal | All Wastewater System ROC General | 2026-01-04
ROC | January | BLSS, Young J on site running generator and testing temp alarms | All Wastewater System ROC General | 2026-01-06
ROC | January | KSSP - Chan aeration blower 2 high diff pressure alarm. Checked site, channel aeration blower 1 is running in duty 1. Unable to clear alarm. Will contact area ops during regular hours. | All Wastewater System ROC General | 2026-01-02
ROC | January | KSETWB, Jackie S on site, working on the chemical system and testing Cl2 leak alarms | All Wastewater System ROC General | 2026-01-06
ROC | January | NBSP, Filter Drain Sump hihi float, Gavin W on site testing the float | All Wastewater System ROC General | 2026-01-06
ROC | January | LSSS, Kevin S is on site, testing dialer alarms and is doing wet well tests, directed to disregard alarms in the morning | All Wastewater System ROC General | 2026-01-06
ROC | January | GRSSWA, Tyson C on site, running generator/testing temp/flood/eye wash alarms | All Wastewater System ROC General | 2026-01-05
ROC | January | KSSP, Darren B on site testing all the floats/spill alarms on site | All Wastewater System ROC General | 2026-01-06
WEST | January | On site for station check and collection of weekly bacT samples Reviewed scada and trends, Duty off, reservoir at 73%, activated duty for station check Visual inspection in and around station Verification of equipment and instrumentation Verified chlorine analyzers readings. Outstanding alarm: None Chlorine residual Grabs @ 1519 hrs Reservoir pre: FCL = 3.42 mg/l. Analyzer: 3.39 mg/l @ 1507 hrs: Reservoir Post: FCL= 1.51 mg/l. Analyzer: 1.53 mg/l @ 1455 hrs: Treated FCL = 1.53 mg/l Analyzer: 1.51 mg/l TCL = 1.74 mg/l Chemicals: Hypo System: Duty1: pump2 Pumps speed: 42% Dosage: 9.02 mL/min Standby: hypo pump1 Chlorine Dosage factor for P1 ~ 125% P2 ~ 125% Well pump discharge pressure: P2 ~ 452 P3 ~ 738 System pressure: 345 kpa | Ansnorveldt Wells 2, 3 & Reservoir | 2026-01-21
WEST | January | -on site to complete station check and to collect samples -sample work order # W11550771 -activated well duty , reservoir = 74% -hypo pump # 1 running at 43%, 5.0 rpm, DF = 125% -verified analyzers: 13:14 - reservoir inlet FCL analyzer = 2.85 mg/L Grab = 2.88 mg/L 13:23 - post reservoir FCL analyzer = 1.36 mg/L Grab = 1.60/1.61/1.61 mg/L 13:29 - adjusted post reservoir FCL analyzer to 1.61 mg/L based on average of 3 grabs 13:31 - treated water FCL analyzer = 1.72 mg/L 13:31 - treated water grab: Free chlorine = 1.55/1.57/1.58 mg/L Total chlorine = 1.73 mg/L 13:36 - adjusted treated FCL analyzer to 1.57 mg/L based on average of 3 grabs 13:44 - collected weekly treated water micro sample 13:45 - collected weekly well # 2 raw water micro sample 13:45 - collected weekly well #3 raw water micro sample -checked equipment -reviewed trends -recorded readings in PWQ sheet -no issues found | Ansnorveldt Wells 2, 3 & Reservoir | 2026-01-28
WEST | January | -on site to complete station check 09:22 - flushed turbidimeter sample lines causing temporary reading spike -well duty not active, reservoir = 62 % -activated well duty for station check -filled hypo tanks 33/33 L to 42/43 L -hypo pump # 2 running at 42%, 4.9 rpm, DF = 125% -verified analyzers: 09:34 - post reservoir FCL analyzer = 1.60 mg/L Grab = 1.50/1.49/1.48 mg/L 09:39 - adjusted post reservoir FCL analyzer to 1.49 mg/L based on average of 3 grabs 09:41 - treated water FCL analyzer = 1.43 mg/L 09:41 - treated water grabs: Free chlorine = 1.45 mg/L Total chlorine = 1.68 mg/L 09:48 - reservoir inlet FCL analyzer = 3.44 mg/L Grab = 3.38 mg/L -checked equipment -reviewed trends -recorded readings in PWQ sheet -no issues found | Ansnorveldt Wells 2, 3 & Reservoir | 2026-01-16
WEST | January | On site for station check Reviewed scada and trends, Duty active, reservoir at 87%, Visual inspection in and around station Verification of equipment and instrumentation Verified chlorine analyzers readings. Outstanding alarm: None Chlorine residual Grabs @ 1005 hrs Reservoir pre: FCL = 3.56 mg/l. Analyzer: 3.60 mg/l @ 1000 hrs: Reservoir Post: FCL= 1.62 mg/l. Analyzer: 1.09 mg/l Adjusted Post reservoir analyzer FCL from 1.09 to 1.62 based on average of 3 grabs @ 1022 hrs: Treated FCL = 1.61 mg/l Analyzer: 1.09 mg/l TCL = 1.79 mg/l Adjusted treated FCL analyzer reading from 1.09 to 1.61 mg/l as per 2 repeated grabs Chemicals: Hypo System: Duty1: pump1 Pumps speed: 42% Dosage: 9.03 mL/min Standby: hypo pump2 Chlorine Dosage factor for P1 ~ 125% P2 ~ 125% Well pump discharge pressure: P2 ~ 458 P3 ~ 737 System pressure: 405 kpa | Ansnorveldt Wells 2, 3 & Reservoir | 2026-01-30
WEST | January | On site for station check Reviewed Scada and trends, Duty off, reservoir at 64%, activated duty for station check Visual inspection in and around station Verification of equipment and instrumentation Verified chlorine analyzers readings. Outstanding alarm: None Chlorine residual Grabs @ 1037 hrs Reservoir pre: FCL = 3.58 mg/l. Analyzer: 3.57 mg/l @ 1050 hrs: Reservoir Post: FCL= 1.54 mg/l. Analyzer: 0.87 mg/l Adjusted Post reservoir analyzer FCL from0.87 to 1.54 based on average of 3 grabs @ 1030 hrs: Treated FCL = 1.55 mg/l Analyzer: 1.69 mg/l TCL = 1.16 mg/l Adjusted treated FCL analyzer reading from 1.16 to 1.55 mg/l as per average of 3 grabs Chemicals: Hypo System: Duty1: pump2 Pumps speed: 42% Dosage: 9.03 mL/min Standby: hypo pump1 Chlorine Dosage factor for P1 ~ 125% P2 ~ 125% Well pump discharge pressure: P2 ~ 451 P3 ~ 736 System pressure: 405 kpa | Ansnorveldt Wells 2, 3 & Reservoir | 2026-01-26
WEST | January | On site for station check Reviewed scada and trends, Duty off, reservoir at 63%, activated duty for station check Visual inspection in and around station Verification of equipment and instrumentation Verified chlorine analyzers readings. Outstanding alarm: None Chlorine residual Grabs @ 0943 hrs Reservoir pre: FCL = 3.20 mg/l. Analyzer: 3.16 mg/l @ 0947 hrs: Reservoir Post: FCL= 1.36 mg/l. Analyzer: 1.33 mg/l @ 0949 hrs: Treated FCL = 1.35 mg/l Analyzer: 1. mg/l TCL = 1.49 mg/l Chemicals: Hypo System: Duty1: pump1 Pumps speed: 42% Dosage: 9.03 mL/min Standby: hypo pump1 Chlorine Dosage factor for P1 ~ 125% P2 ~ 125% Well pump discharge pressure: P2 ~ 452 P3 ~ 738 System pressure: 405 kpa | Ansnorveldt Wells 2, 3 & Reservoir | 2026-01-23
WEST | January | On site for station check Reviewed scada and trends, Duty off, reservoir at 65%, activated duty for station check Visual inspection in and around station Verification of equipment and instrumentation Verified chlorine analyzers readings. Outstanding alarm: None Chlorine residual Grabs @ 1010 hrs Reservoir pre: FCL = 3.68 mg/l. Analyzer: 3.63 mg/l @ 1014 hrs: Reservoir Post: FCL= 1.52 mg/l. Analyzer: 1.50 mg/l @ 1033 hrs: Treated FCL = 1.50 mg/l Analyzer: 1.45 mg/l TCL = 1.69 mg/l Adjusted Treated FCL chlorine analyzer based on 2 repeated grab samples collected ~ 1.45 mg/l to 1.50 mg/l Chemicals: Hypo System: Duty1: pump1 Pumps speed: 43% Dosage: 9.20 mL/min Standby: hypo pump1 Chlorine Dosage factor for P1 ~ 125% P2 ~ 125% Well pump discharge pressure: P2 ~ 453 P3 ~ 738 | Ansnorveldt Wells 2, 3 & Reservoir | 2026-01-19
WEST | January | Filled hypo tanks 29/30 L to 40/37 L | Ansnorveldt Wells 2, 3 & Reservoir | 2026-01-26
WEST | January | on site to complete the following WOs: - Chlorine analyzer maintenance (3 analyzers) - Turbidity analyzer maintenance Notified ROC placed HL pumps in off position and ran HL pump1 in local during analyzers maintenance (ran HL p1 within pressure setpoint ~ 310 to 410 kpa) 1220 hrs verified both treated and Post reservoir chlorine analyzers. adjusted treated analyzer from 1.35 to 1.54 mg/l and Post from 1.34 to 1.54 based on average of 3 grabs each. activated duty, verified pre reservoir chlorine analyzer, adjusted from 5.73 mg/l down to 3.48 mg/l based on 2 grabs No issues on site Notified ROC before leaving site. | Ansnorveldt Wells 2, 3 & Reservoir | 2026-01-22
WEST | January | Discharge low pressure alarm came in Duties active but no pumps running one pump inhibited Ack rest alarms Deactivated and reactivated duties Pumps stated , clearing alarms | Ansnorveldt Wells 2, 3 & Reservoir | 2026-01-09
WEST | January | Onsite to complete the following WOs: - Generator Test run - Pressure regulating valve maintenance - JHSC Health and Safety inspection - Pumps 2/3 Strainer inspection Notified ROC before starting WOs Generator start hour: 310 hrs Stop hours: 311.6 hrs Generator start time: 1327 hrs Stop time: 1432 hrs Cleared and reset alarms Notified ROC before leaving site No issues | Ansnorveldt Wells 2, 3 & Reservoir | 2026-01-13
WEST | January | On site for station check and collection of quarterlies and bacT samples Reviewed scada and trends, Duty off, reservoir at 66%, requested ROC to activated duty @ for station check and sample collection Visual inspection in and around station Verification of equipment and instrumentation Verified chlorine analyzers readings. Outstanding alarm: None Chlorine residual Grabs @ 1001 hrs Reservoir pre: FCL = 3.54 mg/l. Analyzer: 3.52 mg/l @ 0955 hrs: Reservoir Post: FCL= 1.62 mg/l. Analyzer: 1.48 mg/l Adjusted post FCL analyzer from 1.48 to 1.62 based on average of 3 grabs @ 1032 hrs: Treated FCL = 1.60 mg/l Analyzer: 1.62 mg/l TCL = 1.73 mg/l Chemicals: Hypo System: Duty1: pump 1 Pumps speed: 46% Dosage: 9.78 mL/min Target dose: 8 Standby: hypo pump1 Chlorine Dosage factor for P1 ~ 134% / P2 ~ 125% Well pump discharge pressure: P2 ~ 455 / P3 ~ 740 System pressure: 353 kpa | Ansnorveldt Wells 2, 3 & Reservoir | 2026-01-14
WEST | January | On site for station check Reviewed scada and trends, Duty off, reservoir at 78%, activated duty @ 1000hrs for station check Visual inspection in and around station Verification of equipment and instrumentation Verified chlorine analyzers readings. Outstanding alarm: None Chlorine residual Grabs @ 1050 hrs Reservoir pre: FCL = 3.88 mg/l. Analyzer: 3.55 mg/l Adjusted Pre FCL analyzer from 3.55 to 3.88 mg/l based on average of 3 grabs @ 1039 hrs: Reservoir Post: FCL= 1.62 mg/l. Analyzer: 1.61 mg/l @ 1032 hrs: Treated FCL = 1.67 mg/l Analyzer: 1.64mg/l TCL = 1.82 mg/l Chemicals: Hypo System: Duty1: pump 1 Pumps speed: 46% Dosage: 9.78 mL/min Target dose: 8 Standby: hypo pump1 Chlorine Dosage factor for P1 ~ 134% / P2 ~ 125% Well pump discharge pressure: P2 ~ 455 / P3 ~ 740 System pressure: 353 kpa | Ansnorveldt Wells 2, 3 & Reservoir | 2026-01-12
WEST | January | On site for station check Reviewed scada and trends, Duty off, reservoir at 81%, activated duty for station check Visual inspection in and around station Verification of equipment and instrumentation Verified chlorine analyzers readings. Outstanding alarm: None Chlorine residual Grabs @ 0856 hrs Reservoir pre: FCL = 3.22 mg/l. Analyzer: 3.19 mg/l @ 0854 hrs: Reservoir Post: FCL= 1.54 mg/l. Analyzer: 1.55 mg/l @ 0903 hrs: Treated FCL = 1.53 mg/l Analyzer: 1.40 mg/l TCL = 1.70 mg/l Chemicals: Hypo System: Duty1: pump1 Pumps speed: 46% Dosage: 9.78 mL/min Target dose: 8 Standby: hypo pump1 Chlorine Dosage factor for P1 ~ 134% P2 ~ 125% Well pump discharge pressure: P2 ~ 455 P3 ~ 740 Adjusted treated free chlorine analyzer based on average of 3 grabs from 1.40 to 1.54 mg/l Well pump3 not starting in auto, ran pump3 in manual for station check and returned to auto. TL troubleshooting remote with PCS. | Ansnorveldt Wells 2, 3 & Reservoir | 2026-01-09
WEST | January | On site for station check and collection of weekly bacT samples. Reviewed scada and trends, Duty off, reservoir at 61%, activated duty for station check Visual inspection in and around station Verification of equipment and instrumentation Verified chlorine analyzers readings. Outstanding alarm: None Chlorine residual Grabs @ 1408 hrs Reservoir pre: FCL = 3.40 mg/l. Analyzer: 3.44 mg/l @ 1410 hrs: Reservoir Post: FCL= 1.55 mg/l. Analyzer: 1.54 mg/l @ 1416 hrs: Treated FCL = 1.40 mg/l Analyzer: 1.37 mg/l TCL = 1.68 mg/l Chemicals: Hypo System: Duty1: pump1 Pumps speed: 46% Dosage: 9.78 mL/min Target dose: 8 Standby: hypo pump1 Chlorine Dosage factor for P1 ~ 134% P2 ~ 125% Well pump discharge pressure: P2 ~ 455 P3 ~ 740 System pressure: 307 kpa Turb: 0.192 NTU Well pump3 failed to start to in auto and did not generate alarms. Notified TL, CMU has been created for PCS to investigate. Ran pump3 in manual for raw water bacT sample collection. Operation of well pmp3 in manual distorted sample flow to pre injection analyzer, ( air in sample line to analyzer - pre). Returned well pmp3 in auto, pump shut down. Well pump2 running at 1.8 l/s. Recorded station readings into pwq data sheet No issues | Ansnorveldt Wells 2, 3 & Reservoir | 2026-01-07
WEST | January | On site for station check Reviewed scada and trends, Duty off, reservoir at 78%, activated duty for station check Visual inspection in and around station Verification of equipment and instrumentation Verified chlorine analyzers readings. Outstanding alarm: None Chlorine residual Grabs @ 1000 hrs Reservoir Inlet: FCL = 1.74 mg/l. Analyzer: 1.54 mg/l @ 0949 hrs: Reservoir Inlet: FCL= 3.16 mg/l. Analyzer: 3.12 mg/l @ 1009 hrs: Treated FCL = 1.60 mg/l Analyzer: 1.55 mg/l Deactivated well duty. No issues on site | Ansnorveldt Wells 2, 3 & Reservoir | 2026-01-05
WEST | January | On site for station check Check Trends: All okay Well off Topped up hypo tanks- 18.87cm,30.48;19.08cm,30.81L - 25.12cm,40.58L;24.71cm,39.92L Verified Analyzers 08:30-Post Reservoir Free Grab: 1.55 mg/L, Analyzer 1.47 mg/L 08:38-Post Reservoir (treated) Free- grab 1.57mg/L, Analyzer 1.47mg/L Entered Values in PWQ sheet. Equipment okay | Ansnorveldt Wells 2, 3 & Reservoir | 2026-01-02
CENTRAL | January | Onsite for station check/collect sample- WO# W11551518: Sample results (14:18): Free- 0.02, Total- 2.92 * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Aurora (East) First Commerce Elevated Tank | 2026-01-28
CENTRAL | January | Onsite for station check/collect samples- WO# W11539009, W11476655: Sample results (09:25): Free- 0.02, Total- 2.82 * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Aurora (East) First Commerce Elevated Tank | 2026-01-21
CENTRAL | January | Adjusted chlorine room low temp alarm to clear false alarm. Heating in room operational. | Aurora (East) First Commerce Elevated Tank | 2026-01-22
CENTRAL | January | Onsite for station check/collect samples- WO# W11504220, W11504190, W11476866; Sample results (08:54): Free- 0.07, Total- 2.80 * Adjusted total analyzer from 2.65 to 2.80 based on multiple grabs (2.80, 2.82, 2.80) * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Aurora (East) First Commerce Elevated Tank | 2026-01-07
CENTRAL | January | -Received phone call from ROC this morning regarding inlet standby heat trace fault - reviewed trends, tower level was still trending and inlet main heat trace was running - the fault alarm might cause by the extreme cold - informed ROC disregarding the alarm | Aurora (East) First Commerce Elevated Tank | 2026-01-31
CENTRAL | January | Onsite to complete assigned work orders: H/S inspection Low temp test Inlet/outlet heat trace inspection Manual valve exercise Dehumidifier inspection Ventilation inspection Depolox analyzer maintenance Portable generator test Performed station housekeeping Station/equipment- Ok | Aurora (East) First Commerce Elevated Tank | 2026-01-08
CENTRAL | January | Onsite for station check/collect sample- W11523440: Sample results (08:12): Free- 0.03, Total- 2.86 * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Aurora (East) First Commerce Elevated Tank | 2026-01-14
CENTRAL | January | Onsite for station check/collect sample- WO# W11551518: Sample results (12:10): Free- 0.04, Total- 2.90 * Adjusted total analyzer from 2.49 to 2.90 based on multiple grabs (2.88, 2.90, 2.90) * Verified analyzers Depolox reagents- Ok Low water temp outstanding- heat trace system is ON. Will continue to monitor * Station/equipment- Ok | Aurora (North) Orchard Heights Elevated Tank | 2026-01-28
CENTRAL | January | Onsite for station check/collect samples- WO# W11539009, W11476288: Sample results (11:25): Free- 0.03, Total- 2.78 * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Aurora (North) Orchard Heights Elevated Tank | 2026-01-21
CENTRAL | January | Onsite to complete assigned work orders- informed ROC: H/S inspection High/Low temp test Sump system inspection Dechlorination puck dispenser inspection Depolox analyzer maintenance Valve exercise Performed station housekeeping Station/equipment- Ok | Aurora (North) Orchard Heights Elevated Tank | 2026-01-22
CENTRAL | January | Onsite for station check/collect sample- WO# W11523440: Sample results (13:15): Free- 0.07, Total- 2.70 * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Aurora (North) Orchard Heights Elevated Tank | 2026-01-14
CENTRAL | January | Onsite for station check/collect samples- WO# W11504220, W11504190: Sample results (14:10): Free- 0.09, Total- 2.86 * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Aurora (North) Orchard Heights Elevated Tank | 2026-01-07
CENTRAL | January | Onsite for station check: Station offline * Station/equipment- Ok | Aurora Well 6 | 2026-01-19
CENTRAL | January | -Performed station check -Performed H&S inspection | Aurora Well 6 | 2026-01-26
CENTRAL | January | Onsite for station check: Station offline * Station/equipment- Ok | Aurora Well 6 | 2026-01-15
CENTRAL | January | ****site off line***** Building and property secured, no issues found. | Aurora Well 6 | 2026-01-02
CENTRAL | January | Onsite for station check: Station offline * Station/equipment- Ok | Aurora Well 6 | 2026-01-06
CENTRAL | January | Onsite to collect chlorine emergency scrubber media for semi annual testing. No issues found. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2026-01-22
CENTRAL | January | On site for station check. 11:21 outlet flow at 504 l/s. Rechloramination running. Reservoir level at74%. Topped up ammonia tank 1. Verified residuals (mg/l): 11:40 Pre-injection/outlet grabs: Free grab: 0.05 Depolox 5: 0.06. Total grab: 1.75 Micro2000: 1.69. Chemscan: 1.73. Monochloramine grab: 1.61. Chemscan: 1.68. Free ammonia grab: 0.07. Chemscan: 0.07. Total ammonia grab: 0.39. Chemscan: 0.43. 12:00 ost-injection chlorine grabs: Free grab: 0.06. Depolox 5: 0.07. Total grab: 3.28. Micro2000: 3.25 Chemscan: 3.29. Monochloramine grab: 2.85. Chemscan: 2.88 Free ammonia grab: 0.09. Chemscan: 0.02. Adjusted to match grab. Total ammonia grab: 0.65. Chemscan: 0.63. Adjusted chlorine to ammonia ratio from. 4.6 to 4.7. No new issues found. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2026-01-30
CENTRAL | January | Onsite to complete work orders: 09:52 notified roc of work. Placed chemical system offline. Outlet flow is 0 L/s. 10:07 tested eyewash?s and triggered alarm. 10:12 Chlorine leak detection test. Alarm triggered. Emergency valve closure system ok. 10:30 placed chemical dosing systems back 10:47 triggered basement level four alarm. Chemscan offline alarm triggered during inspection and cleaning. Placed dosing system back online. JHSC inspection. Sump pit inspection. Dehumidifier cleaning and inspection. Depolox/micro 2000 cleaning and inspection. Verified analyzers. 11:24: pre-injection.: Free: 0.05. Analyzer: 0.06. Total : 1.65. Analyzer: 1.68. Chemical: 1.65. 11:30 post injection: Free: 0.09. Analyzer: 0.05. Total : 3.32. Analyzer: 3.30. Chemscan 3.36 Ammonia chemical system inspection. Placed dosing system offline and had ROC close aurora wellington valve so outlet flow from station is 0 l/.s Adjusted ammonia p2 max pump rate from 1600 ml to 1500 ml. No issues found. Chlorine chemical system inspection. 14:20 hihi post injection total chlorine alarm triggered. 5 mg/l. Notified by roc. While purging the chlorine system to perform a negative vacuum test a small amount of chlorine was injected into system. System was not directing water to users at the time. Residual returned shortly to 2.60 mg/l by 14:35. Chlorinated 2 knob was loose. Realigned pin and tightened knob back place. Passed negative vacuum test on both chlorinators. 14:50 grab. 1.85 mg/l. Analyzer 1.95 mg/l. Placed dosing system?s back to auto and notified roc. No issues remaining on site. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2026-01-15
CENTRAL | January | On-site for Rechlor station check. Replaced green/grey chemscan analyzer reagents. Batched ammonia tank 1. Grab/analyzer results as follows (mg/L): Pre-Injection: Free Cl (11:00): G: 0.05 A: 0.06 Total Cl (11:02): G: 1.73 A: 1.75 Post-Injection: Free Cl (11:09): G: 0.05 A: 0.02 Total Cl (11:10): G: 1.73 A: 1.77 Checked station and equipment, no new issues found. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2026-01-19
CENTRAL | January | On site for station check. Changed chlorine cylinder bank A with Joe Williams. 10:25 Outlet flow at 534 l/s and chloramine boosting active. Reservoir level at 54%. Verified residuals (mg/l): 10:30 Pre-injection/outlet grabs and collected sample. Free grab: 0.05 Depolox 5: 0.06. Total grab: 1.70 Micro2000: 1.70. Chemscan: 1.72. Monochloramine grab: 1.59. Chemscan: 1.64. Free ammonia grab: 0.09. Chemscan: 0.08. Total ammonia grab: 0.41. Chemscan: 0.40. 10:45 Post-injection chlorine grabs: Free grab: 0.04 Depolox 5: 0.07. Total grab: 3.24/ 3.24/ 3.24. Micro2000: 3.38 Chemscan: 3.27. Adjusted micro2000 to match grab average. Monochloramine grab: 2.86. Chemscan: 2.87 Free ammonia grab: 0.06. Chemscan: 0.08. Total ammonia grab: 0.63. Chemscan: 0.65. No new issues found. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2026-01-16
CENTRAL | January | Received 24 full cylinders and gave back 24 empties for chlorine cylinder delivery. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2026-01-27
CENTRAL | January | On site for station check and sampling. MBHP - W11550691 10:59 outlet flow at 427 l/s. Rechloramination running. Reservoir level at 49%. Verified residuals (mg/l): 11:04 Pre-injection/outlet grabs and collected sample. Free grab: 0.07 Depolox 5: 0.06. Total grab: 1.87 Micro2000: 1.88. Chemscan: 1.79. Monochloramine grab: 1.76. Chemscan: 1.77. Free ammonia grab: 0.05. Chemscan: 0.04. Total ammonia grab: 0.40. Chemscan: 0.39. 11:17 Post-injection chlorine grabs: Free grab: 0.04 Depolox 5: 0.06. Total grab: 3.20. Micro2000: 3.15 Chemscan: 3.28. Monochloramine grab: 2.88. Chemscan: 2.88 Free ammonia grab: 0.05. Chemscan: 0.06. Total ammonia grab: 0.62. Chemscan: 0.55.. Adjusted to match grab. No new issues found. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2026-01-28
CENTRAL | January | On-site for station check. Switched to ammonia tank 2 and batched ammonia tank 1. Changed Cl2 bank B with Ben Hess. 10:34 adjusted post-inj offset for FA from 0.16 to 0.12 and TA from 0.10 to 0.00 (FA G: 0.04 A: 0.12, TA G: 0.37 A: 0.48) and will monitor residuals. Checked station and equipment, no new issues found. Verified analyzers and entered station readings into shared PD excel file. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2026-01-23
CENTRAL | January | Station Check (no issues found) Input data to PWQ Verified Depoloxs (mg/L) 12:00 Pre: Free: Grab 0.04, A 0.06 Total: Grab 1.76, A 1.71 12:20 Post: Free: Grab 0.05, A 0.06 Total: Grab 3.10, A 3.01 Depolox (topped up KI/distilled ) Chemscan (topped up distilled) Ammonia Tank #2 (new batch) | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2026-01-26
CENTRAL | January | Station Check (no issues found) Input data to PWQ Verified Depoloxs (mg/L) 11:00 Pre: Free: Grab 0.03, A 0.06 Total: Grab 1.80, A 1.82 11:15 Post: Free: Grab 0.04, A 0.02 Total: Grab 1.74, A 1.78 Ammonia tank #2 (new batch) 11:35 samples #11538234, 11476655, & operational Depolox: acetate top up | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2026-01-21
CENTRAL | January | On site for station check 12:50 Outlet flow at 472 l/s and chloramine boosting active. Reservoir level at 80%. Topped up ammonia tank 2. Verified residuals (mg/l): 13:00 Pre-injection/outlet grabs and collected samples. Free grab: 0.02 Depolox 5: 0.06. Total grab: 1.71 Micro2000: 1.64Chemscan: 1.75. Monochloramine grab: 1.62. Chemscan: 1.70. Free ammonia grab: 0.09. Chemscan: 0.07. Total ammonia grab: 0.41. Chemscan: 0.44. 13:08 Post-injection chlorine grabs: Free grab: 0.02 Depolox 5: 0.04. Total grab: 3.22/3.14/3.10 Micro2000: 3.09 Chemscan: 3.04. Adjusted both analyzers to match grab average. Monochloramine grab: 2.81. Chemscan: 2.79.. Free ammonia grab: 0.19 Chemscan: 0.07. adjusted analzyer offset to match. Total ammonia grab: 0.75. Chemscan: 0.66. Adjusted analyzer offset to match. Adjusted post injection chlorine setpoint from 3.2 to 3.3. Adjusted chlorine/ammonia ratio from 4.4 to 4.5. 13:45 Verified post injection readings. Total chlorine: 3.28. Micro2000: 3.19. Chemscan: 3.32 Free ammonia: 0.16. Chemscan: 0.18. Totoal ammonia: 0.73. Chemscan: 0.76. Monochloramine: 2.88. Chemscan: 2.91 13:56 Adjusted chlorine/ammonia ratio from 4.5 to 4.6. Adjusted chlorinator 1 high rotation setpoint from 70% to 85% to hopefully allow chlorinator 1 time to fully open before switching to chlorinator 2 and prevent the chlorinator 1 failed to open fault alarms. No new issues found. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2026-01-09
CENTRAL | January | On site for station check and reservoir sampling. MBHP - W11522607 10:26 Outlet flow at 404 l/s and chloramine boosting active. Reservoir level at 45%. Topped up ammonia tank 2. Verified residuals (mg/l): 10:45 Pre-injection/outlet grabs and collected sample. Free grab: 0.04 Depolox 5: 0.06. Total grab: 1.73 Micro2000: 1.77. Chemscan: 1.72. A Monochloramine grab: 1.64. Chemscan: 1.67. Free ammonia grab: 0.09. Chemscan: 0.08. Total ammonia grab: 0.42. Chemscan: 0.43. Nitrite: 0.001 11:00 Post-injection chlorine grabs: Free grab: 0.05 Depolox 5: 0.05. Total grab: 3.16 Micro2000: 3.31 Chemscan: 3.20. Monochloramine grab: 2.83. Chemscan: . Adjusted offset to match grab. Free ammonia grab: 0.09 Chemscan: 0.09. Total ammonia grab: 0.64. Chemscan: 0.69. No new issues found. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2026-01-14
CENTRAL | January | Onsite to change CL2 cylinders: 55kg/0kg to 55kg/68kg | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2026-01-08
CENTRAL | January | On site for station check 08:20 Outlet flow at 445 l/s and chloramine boosting active. Reservoir level at 50%. Topped up ammonia tank 1. Verified residuals (mg/l): 08:35 Pre-injection/outlet grabs and collected samples. Free grab: 0.04 Depolox 5: 0.05. Total grab: 1.73/1.73/1.73 Micro2000: 1.63. Chemscan: 1.74. Adjusted Micro2000 analyzer to match grabs. Monochloramine grab: 1.65. Chemscan: 1.66. Free ammonia grab: 0.07. Chemscan: 0.04. Total ammonia grab: 0.39. Chemscan: 0.42. 08:25 Post-injection chlorine grabs: Free grab: 0.10 Depolox 5: 0.05. Total grab: 3.20 Micro2000: 3.30 Chemscan: 3.30. Monochloramine grab: 2.96. Chemscan: 3.09. Adjusted offset to match grab. Free ammonia grab: 0.08 Chemscan: 0.12. Adjusted analyzer offset to match. Total ammonia grab: 0.67. Chemscan: 0.70. 09:17 chlorinator 1 failed to open alarm triggered. Adjusted minimum flow setpoint from 200 to 185 l/s to give chlorinator 1 longer to open during low flow scenarios during opening and closing. Entered data into process sheets. No other new issues found. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2026-01-12
CENTRAL | January | On site for station check and sampling. ANSCAN - W11503562. MBDW - W11503217. 11:16. Outlet flow at 0 l/s as AUVCWS valve is currently closed. Reservoir level at 50%. Topped up chemscan distilled water. Verified residuals (mg/l): 11:30 Pre-injection/outlet grabs and collected samples. Free grab: 0.03 Depolox 5: 0.06. Total grab: 1.70 Micro2000: 1.62 Chemscan: 1.72. Monochloramine grab: 1.65. Chemscan: 1.72. Free ammonia grab: 0.10. Chemscan: 0.07 Total ammonia grab: 0.42. Chemscan: 0.44. 12:41 Post-injection chlorine grabs: Free grab: 0.03 Depolox 5: 0.01. Total grab: 1.78 Micro2000: 1.71 Chemscan: 1.61 Adjusted chemcan to match grab average. Monochloramine grab: 1.68. Chemscan: 1.77. Free ammonia grab: 0.09 Chemscan: 0.09. Total ammonia grab: 0.42. Chemscan: 0.45. No new issues found. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2026-01-07
CENTRAL | January | On site for station check. 11:30. Outlet flow at 289 l/s and chloramine boosting is active. ANVCWS valve is currently closing. 11:38. Chlorinator 1 failed to open fault triggered. Flow is dropping quickly, may have dropped below the dosing limit before valve could open. Will continue to monitor. Acknowledged and cleared alarm. Reservoir level at 75%. Topped up ammonia tank 1. 12:18 chemcan offline alarm triggered. Chemscan placed offline to change out sulhpuric acid reagent. Acknowledged and reset alarm. Verified residuals (mg/l): 12:39 Pre-injection chlorine grabs. Free grab: 0.07 Depolox 5: 0.05. Total grab: 1.81/1.76/1.76 Micro2000: 1.71 Chemscan: 1.73. Adjusted micro2000 to match grab average. Monochloramine grab: 1.75. Chemscan: 1.76. Free ammonia grab: 0.10. Chemscan: 0.06 Total ammonia grab: 0.45. Chemscan: 0.41. 12:41 Post-injection chlorine grabs: Free grab: 0.05 Depolox 5: 0.01. Total grab: 1.78/1.78/1.81 Micro2000: 1.70 Chemscan: 1.94 Adjusted both analyzer to match grab average. Monochloramine grab: 1.67. Chemscan: 1.81. Free ammonia grab: 0.09 Chemscan: 0.07. Total ammonia grab: 0.42. Chemscan: 0.48. No new issues found. | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2026-01-05
CENTRAL | January | On-site for a station and equipment check No issues found Topped up ammonia day tank 2 Changed CL2 cylinders bank 1 with JZ Chemical levels and systems ok. Verified analyzers and entered all readings and grabs into PWQ sheet Pre-Free@0849 G:0.04 A:0.05mg/L Pre-Total@0849 G:1.61 A:1.57mg/L Post-Free@0849 G:0.04 A:0.01mg/L Post-Total@0849 G:1.67 A:1.68mg/L | Aurora (South) Bathurst Reservoir, Booster & Rechloramination Facility | 2026-01-02
CENTRAL | January | On site for station check and sampling. MBDW - W11550691. 12:08 Tower level at 54% and draining at 4.4 l/s. 12:20 Verified chlorine analyzer (mg/l) and collected sample. Free chlorine grab: 0.03. Analyzer: 0.0. Total chlorine grab: 2.12/2.10/2.12. analyzer: 2.24. Adjusted to match grab average. Nitrite grab: 0.004. Free ammonia: 0.06. Total ammonia: 0.43. Monochloramine: 1.89. No issues on site. | Aurora (Southwest) Allenvale Elevated Tank | 2026-01-28
CENTRAL | January | Onsite for CMU5 - total AIT Informed ROC Put device into cal mode on scada Found stirrer not rotating Removed cell and realigned stirrer. Added new grease Replaced assembly and monitored operation. Ok now Took grabs and adjusted A = 2.33mg/L G = 2.31mg/L Cleared associated alarms Informed ROC, armed building and left site | Aurora (Southwest) Allenvale Elevated Tank | 2026-01-16
CENTRAL | January | Onsite to investigate lolo total chlorine alarm from 15:52. Found analyzer stir assembly to have malfunction and not stirring. 17:01 total Analyzer reading 0.14 mg/l. Grab 2.17 mg/l. Free chlorine grab: 0.06. Analyzer 0.06. Notified ROC and instrumentation on call Ricardo. 17:04 historian heartbeat alarm triggered. Notified roc. | Aurora (Southwest) Allenvale Elevated Tank | 2026-01-16
CENTRAL | January | Station Check (no issues found) Input data to PWQ 12:42 Verified Depolox (mg/L) Free: Grab 0.04, A 0.02 Total: Grab 2.10, A 2.14 12:55 #11538234, 11476655, & operational samples | Aurora (Southwest) Allenvale Elevated Tank | 2026-01-21
CENTRAL | January | Onsite to calibrate total AIT Informed ROC Used calibration mode on scada during the work Replaced AIT stirrer assembly and peristaltic motor Took grabs and adjusted A = 2.17mg/L G = 2.17mg/L Cleared associated alarms Informed ROC, armed building and left site | Aurora (Southwest) Allenvale Elevated Tank | 2026-01-16
CENTRAL | January | 08:23 adjusted zone 3 duty start from 40 to 45%. Low fire alarm triggered from lower start. Cleared alarm. | Aurora (Southwest) Allenvale Elevated Tank | 2026-01-16
CENTRAL | January | Onsite for annual calibrations Informed ROC Used cal mode on scada during the calibrations Asked ROC to place Ridge Road pumps in manual while performing TWR LIT calibration Instruments calibrated: FIT, LIT and Free AIT Free AIT as found 0.08mg/L Free AIT as left 0.08mg/L No adjustments made Will return for Total AIT Cleared associated alarms. Checked pumps duty was back to AUTO Informed ROC, armed building and left site | Aurora (Southwest) Allenvale Elevated Tank | 2026-01-15
CENTRAL | January | On site for station check and sampling. MBDW - W11522607. 11:52 deactivated zone 3 duty. Tower level at 57%. 12:15 Verified chlorine analyzer (mg/l) and collected sample. Free chlorine grab: 0.08. Analyzer: 0.08. Total chlorine grab: 2.05. analyzer: 2.09. Adjusted zone 3 duty start from 45% to 40%. Adjusted duty stop from 60 to 80% No issues on site. | Aurora (Southwest) Allenvale Elevated Tank | 2026-01-14
CENTRAL | January | Onsite to investigate low total reading of 0.50 mg/l. Found analyzer tubing to be damaged and leaking. 10:16 grab: 2.36 mg/l. Analyzer 0.58 mg/l. Notified ROC and they issued cmu5 for instrumentation to repair this afternoon. No other issues found. | Aurora (Southwest) Allenvale Elevated Tank | 2026-01-09
CENTRAL | January | Attending site to check leak on Total Chlorine analyzer (W11576219). Found sample water tubing had small tear allowing water to escape. Replaced sample water tubing and reagent/buffer pump tubing. Adjusted Total Chlorine reading to 2.17mg/L, based on the average of 3 DPD grab samples. ROC was notified before and after maintenance work was performed. | Aurora (Southwest) Allenvale Elevated Tank | 2026-01-09
CENTRAL | January | On site for station check and sampling. MBDW - W11503217. ANSCAN - W11503562. 12:40 Tower draining at 49 l/s. Tower level at 54%. 12:45 Verified chlorine analyzer (mg/l) and collected sample. Free chlorine grab: 0.08. Analyzer: 0.07. Total chlorine grab: 2.19. analyzer: 2.27. No issues on site. | Aurora (Southwest) Allenvale Elevated Tank | 2026-01-07
CENTRAL | January | On-site to complete work orders: Portable gas generator run. Inlet/outlet heat trace inspection. Manual valve exercise JHSC inspection. 10:08 Low temperature alarm test. Chlorine analzyer maintenance. Topped up depolox electrolyte. 11:06. Verified analyzer (mg/l): Free grab: 0.10. Analyzer: 0.08. Total: 2.36 Analyzer: 2.30. flushed LIT transmitter. 11:24 Tested building flood alarm. Site cleaning. No issues on site. | Aurora (Southwest) Allenvale Elevated Tank | 2026-01-06
CENTRAL | January | Onsite to complete assigned work orders- informed ROC: H/S inspection High/Low temp tests Vent inspection Hoist system inspection Pump and motor inspection Depolox analyzer maintenance Dehumidifier inspection Performed station housekeeping Generator test run: Start time- 09:00 Stop time- 10:05 Start fuel- 2550 L Stop fuel- 2540 L Start hours- 203.3 Stop hours- 204.4 Pre test inspection completed- no abnormalities* Generator tested under load (P3 and P4): 1799 rpm 600 V 60 Hz 94 A Oil pressure- 436 kpa Coolant temp- 87 C No abnormalities during generator test run- placed generator back into auto once test completed- station back on hydro power * Station/equipment- Ok | Aurora Orchard Heights Pumping Station & Reservoir | 2026-01-20
CENTRAL | January | Onsite for station check: Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Aurora Orchard Heights Pumping Station & Reservoir | 2026-01-23
CENTRAL | January | Onsite for station check/collect samples- WO# W11539009, W11476288: Sample results (10:45): Free- 0.10, Total- 2.88 * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Aurora Orchard Heights Pumping Station & Reservoir | 2026-01-21
CENTRAL | January | -Performed station check - logged station readings into PWQ sheet -Checked Depolox reagents - OK | Aurora Orchard Heights Pumping Station & Reservoir | 2026-01-26
CENTRAL | January | Onsite for station check: Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Aurora Orchard Heights Pumping Station & Reservoir | 2026-01-30
CENTRAL | January | Onsite for station check/collect sample- WO# W11551518: Sample results (11:38): Free- 0.00, Total- 3.10 * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Aurora Orchard Heights Pumping Station & Reservoir | 2026-01-28
CENTRAL | January | Onsite for station check: Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Aurora Orchard Heights Pumping Station & Reservoir | 2026-01-16
CENTRAL | January | Onsite for station check: Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Aurora Orchard Heights Pumping Station & Reservoir | 2026-01-19
CENTRAL | January | Onsite for station check: Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Aurora Orchard Heights Pumping Station & Reservoir | 2026-01-09
CENTRAL | January | Onsite for station check: Replaced depolox KI reagent * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Aurora Orchard Heights Pumping Station & Reservoir | 2026-01-12
CENTRAL | January | Onsite for station check/collect sample- WO# W11523440: Sample results (12:25): Free- 0.00, Total- 2.90 * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Aurora Orchard Heights Pumping Station & Reservoir | 2026-01-14
CENTRAL | January | Onsite for station check/collect samples- WO# W11504220, W11504190: Sample results (13:02): Free- 0.06, Total- 2.94 * Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Aurora Orchard Heights Pumping Station & Reservoir | 2026-01-07
CENTRAL | January | Onsite for station check: Verified analyzers Depolox reagents- Ok Station/equipment- Ok | Aurora Orchard Heights Pumping Station & Reservoir | 2026-01-05
CENTRAL | January | -Performed station check - logged station readings into PWQ sheet -Checked Depolox reagents - OK | Aurora Orchard Heights Pumping Station & Reservoir | 2026-01-02
CENTRAL | January | On site for station check. 12:40 Reservoir inlet filling at 60 l/s. Zone 3 Pump 1 and 2 in standby. Chemical boosting not active. Reservoir level at 73%. Topped up ammonia tank 2. Replaced cl17 pre-injection total analyzer reagent. Verified analyzer residuals (mg/l): 13:10 Pre-injection grabs: Free chlorine grab: 0.03. Analyzer: 0.03. Total Chlorine grab: 1.67 CL17: 1.74. Chemscan: 1.74 Monchloramine grab: 1.51. Chemscan: 1.55 Free ammonia: 0.09. Chemscan: 0.05. Adjusted to match grab. Total ammonia: 0.48. Chemscan: 13:25 Post-injection grabs: Free chlorine grab: 0.05 Analyzer: 0.05. Total Chlorine grab: 2.52 CL17: 2.51. Chemscan: 2.50 Monchloramine grab: 2.19. Chemscan: 2.12 Free ammonia: 0.06. Chemscan: 0.02. Adjusted to match grab. Total ammonia: 0.49. chemscan: 52 13:31 Reservoir outlet grabs: Free chlorine grab:0.07. Analyzer: 0.04 Total chlorine grab: 2.20. Analyzer: 2.25. 13:31 Zone 3 grabs: Free chlorine grab: 0.07. Analyzer: 0.04. Total chlorine grab: 2.20 Analyzer: 2.25. Station and equipment ok. No issues found. Entered readings into process sheets. | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2026-01-16
CENTRAL | January | On-site for pumping/rechlor station check. Replaced CL17 analyzer reagents for Z3 Free/Total Cl and Post-Injection Free Cl analyzers. Grab/analyzer results as follows (mg/L): Pre-Injection: Free Cl (08:59): G: 0.04 A: 0.03 Total Cl (08:59): G: 1.69 A: 1.76 Post-Injection: Free Cl (09:01): G: 0.06 A: 0.05 Total Cl (09:03): G: 2.54 A: 2.55 Z3: Free Cl (09:04): G: 0.02 A: 0.03 Total Cl (09:04): G: 2.15 A: 2.21 Entered station readings into shared PD excel file. Checked station and equipment, no new issues found. | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2026-01-19
CENTRAL | January | On-site for station check, JHSC inspection and visual inspection of chemical injection points. Found that fire extinguisher in electrical room needs to be replaced (needs recharge), created follow up WO W11611618 to address issue, there is another fire extinguisher on-site. Entered station readings into shared PD excel file. Checked station and equipment, no other new issues found. | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2026-01-23
CENTRAL | January | Station Check (no issues found) Input data to PWQ Verified CL17s (mg/L) 9:00 Pre: Free: Grab 0.04, A 0.03 Total: Grab 1.74, A 1.78 9:20 Post: Free: Grab 0.06, A 0.05 Total: Grab 2.56, A 2.59 9:35 Reservoir: Free: Grab 0.05, A 0.03 Total: Grab 2.36, A 2.29 9:45 Zone 3: Free: Grab 0.06, A 0.03 Total: Grab 2.30, A 2.24 #11518832 Cl2 system Chlorine injection valve #2 alarms generated (january 25th @ 10:30pm) (fail to open), cleared alarm on scada Chemscan (topped up grey, new muratic/distilled reagents) | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2026-01-26
CENTRAL | January | Onsite for station check recordings in PD sheet adjusted pre injection total chlorine analyzer station ok | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2026-01-30
CENTRAL | January | Onsite for annual calibrations Informed ROC and OIC Performed maintenance and calibration on Zone 3 Free AIT only A = 0.04mg/L G = 0.04mg/L Pump station duty about to activate and Res filling. Cannot continue calibrations and maintenance Informed ROC, armed building and left site | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2026-01-29
CENTRAL | January | On site for station check and sampling. MBHP - W11550691 08:25 Reservoir inlet filling at 61 l/s. Zone 3 Pump 1 and 2 in standby. Chemical boosting active. Reservoir level at 64%. Verified analyzer residuals (mg/l): 08:36 Pre-injection grabs: Free chlorine grab: 0.03. Analyzer: 0.03. Total Chlorine grab: 1.74 CL17: 1.80. Chemscan: 1.81 Monchloramine grab: 1.55 Chemscan: 1.61 Free ammonia: 0.07. Chemscan: 0.07. Total ammonia: 0.37. Chemscan: 0.34. 08:47 Post-injection grabs: Free chlorine grab: 0.03 Analyzer: 0.05. Total Chlorine grab: 2.54 CL17: 2.55. Chemscan: 2.59 10:09 Monchloramine grab: 2.08. Chemscan: 2.12 Free ammonia: 0.04. Chemscan: 0.02. Total ammonia: 0.45. chemscan: 0.52. 08:53 Reservoir outlet grabs and collected sample: Free chlorine grab: 0.01. Analyzer: 0.03 Total chlorine grab: 2.38 Analyzer: 2.30. 08:53 Zone 3 grabs: Free chlorine grab: 0.01. Analyzer: 0.03. Total chlorine grab: 2.38 Analyzer: 2.28. Station and equipment ok. No issues found. Entered readings into process sheets. | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2026-01-28
CENTRAL | January | Station Check (no issues found) Input data to PWQ Verified CL17s (mg/l) 9:24 Pre: Free: Grab 0.02, A 0.03 Total: Grab 1.71, A 1.76 9:32 Post: Free: Grab 0.03, A 0.04 Total: Grab 1.72, A 1.79 9:55 Zone 3 Free: Grab 0.05, A 0.04 Total: Grab 2.22, A 2.30 8:55 Res. Out: Free: Grab 0.02, A 0.03 Total: Grab 2.20, A 2.28 9:10 Samples #11538234, 1476655 (and operational samples) 10:15 Cl2 cylinder change with JG Chemscan (filled distilled) | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2026-01-21
CENTRAL | January | Onsite to complete work orders: 10:22 Notified ROC of work. 10:57 Outlet and zone 2 CL17 analyzer maintenance. Shut down chemical dosing. 10:57 pre and post injection cl17 analyzers. 11:31 verified outlet and zone 3 analyzer: Outlet free: 0.04. cl17: 0.03. outlet total: 2.30. cl17: 2.31 Zone 3 Free: 0.04. cl17: 0.04. Zone 3 total: 2.30. cl17: 2.34. 11:40 verified pre and post injection analyzers: Pre free: 0.08. cl17: 0.03. pre total: 1.78. cl17. 1.87. Post free: 0.07. cl17: 0.05. pre total: 1.85. Cl17. 1.80. Chemscan analyzer maintenance. Cleaned all analyzer inlet strainers. Clean flushed chemscan analyzer 3 times. no issues found. 12:55 tested chlorine leak alarm and emergency valve closure system. No issues. Tested station eyewash. No issues found. 13:00 Ammonia system and pump inspection. Adjusted ammonia pump 2 max pumprate from 210 ml/min to 215 ml/min. 13:35 tested ammonia tank containment flood alarm. No issues. Placed chemcial dosing system back online. No issues remain on site. | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2026-01-20
CENTRAL | January | Restarted the Operator Interface Terminal due to Windows memory issues. Notified the Remote Operations Center prior to restart. | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2026-01-19
CENTRAL | January | On site for station check and sampling. MBDW - W11503217. ANSCAN - W11503562. 13:31. Reservoir inlet filling at 57 l/s. Zone 3 Pump 1 and 2 in standby. Chemical boosting active. Reservoir level at 66%. Verified analyzer residuals (mg/l): 13:38 Pre-injection grabs: Free chlorine grab: 0.05. Analyzer: 0.04. Total Chlorine grab: 1.80 CL17 Analyzer: 1.74. Chemscan: 1.83. 13:44 Post-injection grabs: Free chlorine grab: 0.06. Analyzer: 0.06. Total Chlorine grab: 2.56 CL17: 2.62. Chemscan: 2.48 13:50 Reservoir outlet chlorine grab: Free grab: 0.06. Analyzer: 0.04. Total grab: 2.33 Analyzer: 2.32. Monchloramine grab: 2.06. Free ammonia: 0.06. Total ammonia: 0.46. Nitrite: 0.001. Collected samples. 13:57 Zone 3 grabs: Free chlorine grab: 0.06. Analyzer: 0.04. Total chlorine grab: 2.33 Analyzer: 2.29. Station and equipment ok. | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2026-01-07
CENTRAL | January | On site for station check 10:49. Reservoir inlet filling at 47 l/s. Zone 3 Pump 2 running at 70.1 l/s. Chemical boosting active. Reservoir level at 59%. Replaced pre-injection free anlayzer reagent. Verified analyzer residuals (mg/l): 11:00 Pre-injection grabs: Free chlorine grab: 0.05. Analyzer: 0.03. Total Chlorine grab: 1.70/1.70/1.71 CL17 Analyzer: 1.74. Chemscan: 1.83. Adjusted chemscan to match grab average. Monchloramine grab: 1.52 Chemscan: 1.58 Free ammonia: 0.08. Chemscan: 0.08 Total ammonia: 0.38. Chemscan: 0.33. 11:15 Post-injection grabs: Free chlorine grab: 0.11. Analyzer: 0.06. Total Chlorine grab: 2.56 CL17: 2.50. Chemscan: 2.63 Monchloramine grab: 2.16 Chemscan: 2.32. Free ammonia: 0.06. Chemscan: 0.04. Total ammonia: 0.48. Chemscan: 0.54. 11:22 Reservoir outlet chlorine grab: Free grab: 0.06. Analyzer: 0.04. Total grab: 2.40 Analyzer: 2.30. 11:26Zone 3 grabs: Free chlorine grab: 0.06. Analyzer: 0.04. Total chlorine grab: 2.40 Analyzer: 2.30. Station and equipment ok. No issues found. Entered readings into process sheets. | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2026-01-09
CENTRAL | January | On site for station check and sampling. MBHP -W11522607 08:30. Reservoir outlet draining at 20 l/s. Zone 3 Pump 2 running at 69.9 l/s. Chemical boosting not active. Reservoir level at 66%. Replaced outlet free chlorine anlayzer reagent. Verified analyzer residuals (mg/l): 08:45 Pre-injection grabs: Free chlorine grab: 0.02. Analyzer: 0.04. Total Chlorine grab: 2.38 CL17: 2.34. Chemscan: 2.34 08:50 Post-injection grabs: Free chlorine grab: 0.03. Analyzer: 0.04. Total Chlorine grab: 2.34 CL17: 2.36. Chemscan: 2.41 08:56 Reservoir outlet chlorine grab and collected sample. Free grab: 0.02. Analyzer: 0.04. Total grab: 2.30 Analyzer: 2.31. Monchloramine grab: 2.06. Free ammonia: 0.07. Total ammonia: 0.48. Nitrite: 0.001. pH: 7.98. Temperature: 6.4 celsius. 09:00 Zone 3 grabs: Free chlorine grab: 0.02. Analyzer: 0.04. Total chlorine grab: 2.30 Analyzer: 2.30. Station and equipment ok. No issues found. Entered readings into process sheets. | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2026-01-14
CENTRAL | January | On site for station check. 10:29. Reservoir inlet filling at 47 l/s. Zone 3 Pump 1 running at 70.1 l/s. Chemical boosting not active. Reservoir level at 60%. Replaced outlet total anlayzer reagent. Replaced chemscan sulphuric acid reagent. Verified analyzer residuals (mg/l): Pre-injection grabs: 10:49 Monchloramine grab: 2.06 Chemscan: 2.04 Free ammonia: 0.08. Chemscan: 0.02. Adjusted to match grab average. Total ammonia: 0.49. Chemscan: 0.48. 11:00 Free chlorine grab: 0.04. Analyzer: 0.04. Total Chlorine grab: 1.73 CL17 Analyzer: 1.77 Chemscan: 1.71. 11:12 Post-injection grabs: Free chlorine grab: 0.10. Analyzer: 0.05. Total Chlorine grab: 2.58 CL17: 2.53. Chemscan: 2.64 Monchloramine grab: 2.11 Chemscan: 2.07. Free ammonia: 0.07. Chemscan: 0.04. Total ammonia: 0.49. Chemscan: 0.53. 11:20 Reservoir outlet chlorine grab: Free grab: 0.02. Analyzer: 0.04. Total grab: 2.34 Analyzer: 2.30. 11:25 Zone 3 grabs: Free chlorine grab: 0.02. Analyzer: 0.04. Total chlorine grab: 2.34 Analyzer: 2.30. Station and equipment ok. No issues found. Entered readings into process sheets. | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2026-01-12
CENTRAL | January | On-site to complete monthly Gen run. Preinspection ok. Found small amount of water/coolant under generator. Coolant overflow container tipped over. Secured container. Likely blown in snow from previous snowstorms. Coolant level ok. Heater ok recirculating pump ok. Oil level ok. Fuel level 2205 L. Run hours 238 hours, 28 minutes. 13:15 notified roc and ran generator test. 14:24 completed gen test. Fuel level. 2191. Run hours 239:40 No issues found. | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2026-01-06
CENTRAL | January | On-site for a station and equipment check Chemical levels and systems ok. Verified analyzers and entered all readings and grabs into PWQ sheet Pre-injection Free@1049 G:0.04 A:0.04mg/L Total@1053 G:1.77 A:1.76mg/L Post-injection Free@1055 G:0.05 A:0.05mg/L Total@1057 G:1.80 A:1.76mg/L Zone 3 Free@1104 G:0.07 A:0.04mg/L Total@1106 G:2.32 A:2.31mg/L Reservoir Outlet Free@1108 G:0.04 A:0.04mg/L Total@1111 G:2.30 A:2.32mg/L | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2026-01-02
CENTRAL | January | On-site for station check. 09:51 Reservoir inlet filling at 41 l/s. Zone 3 Pump 1 and 2 in standby. Chemical boosting active. Reservoir level at 71%. Topped up ammonia tank 1. Replaced post injection total cl17sc analyzer reagent. Verified analyzer residuals (mg/l): 10:19 Pre-injection grabs: Free chlorine grab: 0.04. Analyzer: 0.04. Total Chlorine grab: 1.80 CL17 Analyzer: 1.74. Chemscan: 1.83. Monchloramine grab: 1.52. Chemscan: 1.54. Free ammonia: 0.06. Chemscan: 0.05. Total ammonia: 0.36. Chemscan: 0.34. 10:28 Post-injection grabs: Free chlorine grab: 0.08. Analyzer: 0.06. Total Chlorine grab: 2.59 CL17: 2.54. Chemscan: 2.62. Monchloramine grab: 2.13. Chemscan: 2.19 Free ammonia: 0.02. Chemscan: 0.02. Total ammonia: 0.44. Chemscan: 0.51. 10:33 Reservoir outlet chlorine grab. Free grab: 0.02. Analyzer: 0.04. Total grab: 2.36 Analyzer: 2.30. 10:43 Zone 3 grabs: Free chlorine grab: 0.02. Analyzer: 0.04. Total chlorine grab: 2.36 Analyzer: 2.29. Station and equipment ok. | Aurora Ridge Road Reservoir, Booster & Rechlorination Facility | 2026-01-05
CENTRAL | January | Onsite for station check: Verified analyzers Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok Well 5 remains OOS due to motor issues * | Aurora Well 5 | 2026-01-28
CENTRAL | January | Onsite for station check: Verified analyzers Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok Well 5 remains in Local/Off | Aurora Well 5 | 2026-01-30
CENTRAL | January | Station and equipment check Well 5 OOS Took grabs @ 12:35 pm (treated) Total: 2.60 mg/l Free: 0.05 mg/l Chemicals/reagents ok Ops normal | Aurora Well 5 | 2026-01-23
CENTRAL | January | Station and equipment check Took grabs @ 1:40 pm Treated Total: 2.66 mg/l Treated Free: 0.05 mg/l Well 5 OOS Chemicals/reagents ok Ops normal | Aurora Well 5 | 2026-01-15
CENTRAL | January | -Performed station check - logged station readings into PWQ sheet -Changed treated free reagents | Aurora Well 5 | 2026-01-26
CENTRAL | January | Onsite for station check: Replaced influent free CL17 reagents * Verified analyzers Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok Well 5 remains OOS due to motor issues * | Aurora Well 5 | 2026-01-21
CENTRAL | January | Onsite for station check: Replaced effluent free CL17 reagents * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok Well 5 remains OOS due to motor issues * | Aurora Well 5 | 2026-01-19
CENTRAL | January | Onsite for station check: Performed turbidimeter cleaning/maintenance* Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok Well 5 remains OOS due to ongoing motor issues. Man/Off OOS- ROC aware * | Aurora Well 5 | 2026-01-09
CENTRAL | January | Onsite to complete assigned work order- informed ROC: CL2 leak alarm test Station/equipment- Ok | Aurora Well 5 | 2026-01-15
CENTRAL | January | Remove nut off motor and deliver to canaco for thread matching | Aurora Well 5 | 2026-01-09
CENTRAL | January | Station and equipment check Well 5 remains OOS Took grabs @ 3:20 pm Treated Total: 2.60 mg/l Treated Free: 0.05 mg/l Analyzer Total: 2.56 mg/l Analyzer Free: 0.06 mg/l Chemicals/reagents ok | Aurora Well 5 | 2026-01-07
CENTRAL | January | Onsite for station check: Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok Well 5 remains offline due to motor issues- ROC aware * | Aurora Well 5 | 2026-01-12
CENTRAL | January | Onsite for station check: Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok Well 5 remains OOS due to motor issues * | Aurora Well 5 | 2026-01-14
CENTRAL | January | Onsite for station check: Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok Placed well in man/off once station check completed * | Aurora Well 5 | 2026-01-05
CENTRAL | January | -Performed station check - logged station readings into PWQ sheet -Topped up drip oil reservoir -Changed treated total reagents | Aurora Well 5 | 2026-01-02
CENTRAL | January | Onsite to complete assigned work orders- informed ROC: H/S inspection Exhaust fans/dampers inspection Deep well exhaust inspection CL17 analyzer maintenance Turbidimeter maintenance Ammonia pump inspections Silicate pump inspections Chlorine system visual inspection Performed station housekeeping Station/equipment- Ok Well 5 to remain man/off due to ongoing motor issues * | Aurora Well 5 | 2026-01-06
CENTRAL | January | Onsite for treated station check: Replaced treated total CL17 reagents * Adjusted treated total analyzer from 2.89 to 3.10 based on multiple grabs (3.06, 3.10, 3.10) * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok Onsite for raw station check: Station/equipment- Ok | Aurora Wells 1-4 Water Treatment Plant | 2026-01-19
CENTRAL | January | Onsite for treated station check: Adjusted influent free analyzer from 2.62 to 2.50 based on multiple grabs (2.48, 2.50, 2.50) Adjusted treated total analyzer from 3.04 to 2.84 based on multiple grabs (2.84, 2.84, 2.86) Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok Onsite for raw station check: Station/equipment- Ok | Aurora Wells 1-4 Water Treatment Plant | 2026-01-30
CENTRAL | January | Onsite for station check: Changed CL2 cylinders: 0/66 kg to 68/66 kg * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok | Aurora Wells 1-4 Water Treatment Plant | 2026-01-16
CENTRAL | January | Changed chlorine cylinder bank B with Joe D. | Aurora Wells 1-4 Water Treatment Plant | 2026-01-29
CENTRAL | January | Restarted the Local SCADA server due to Windows updates. Notified the Remote Operations Center. Wells were shutdown during updates. | Aurora Wells 1-4 Water Treatment Plant | 2026-01-22
CENTRAL | January | Onsite for station check/collect samples- W11551518: Sample results (09:25): Free- 0.09, Total- 3.22 * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok | Aurora Wells 1-4 Water Treatment Plant | 2026-01-28
CENTRAL | January | Onsite for treated station check: Replaced influent free CL17 reagents * Silicate dosage not achieving target set point- performed silicate drawdown on pumps 1 and 2: Silicate P#1- 680 mL/min Silicate P#2- 740 mL/min Adjusted silicate pump 1 max flow rate from 850 mL/min to 680 mL/min- based on multiple drawdown attempts Adjusted silicate pump 2 max flow rate from 850 mL/min to 740 mL/min- based on multiple drawdown attempts Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok Onsite for raw station check: Station/equipment- Ok | Aurora Wells 1-4 Water Treatment Plant | 2026-01-23
CENTRAL | January | -Performed station check - logged station readings into PWQ sheet -Checked CL17 reagents - OK -Collected in-house water quality samples | Aurora Wells 1-4 Water Treatment Plant | 2026-01-26
CENTRAL | January | Onsite for station check/collect samples- WO# W11539009, W11476260: Sample results (12:55): Free- 0.12, Total- 3.06 * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok | Aurora Wells 1-4 Water Treatment Plant | 2026-01-21
CENTRAL | January | Onsite to clean ammonia system chemical board | Aurora Wells 1-4 Water Treatment Plant | 2026-01-22
CENTRAL | January | Onsite to complete assigned work orders: PRV inspection Chlorine system inspection Silicate system inspection Ammonia system inspection Performed station housekeeping Butterfly valve exercise/inspections Air relief valve exercise/inspections Station/equipment- Ok | Aurora Wells 1-4 Water Treatment Plant | 2026-01-15
CENTRAL | January | Onsite for treated station check: Replaced treated free CL17 reagents * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok Onsite for raw station check: Station/equipment- Ok | Aurora Wells 1-4 Water Treatment Plant | 2026-01-12
CENTRAL | January | Onsite for station check: Changed CL2 cylinders- 62/0 to 62/68 kg * Noticed crack in pig tail washer (right bank cylinder #3). Replaced pig tail washer with new one. Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok Onsite for raw station check: Station/equipment- Ok | Aurora Wells 1-4 Water Treatment Plant | 2026-01-09
CENTRAL | January | On site to pick up silicate for Mount Albert wells 1,2 and 3. No issues. | Aurora Wells 1-4 Water Treatment Plant | 2026-01-08
CENTRAL | January | On site to collect silicate to top up Ballentrae wells 1/2. No issues. | Aurora Wells 1-4 Water Treatment Plant | 2026-01-08
CENTRAL | January | Onsite for station check/collect samples- WO# W11523440: Sample results (10:30): Free- 0.13, Total- 3.00 * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok | Aurora Wells 1-4 Water Treatment Plant | 2026-01-14
CENTRAL | January | Change oil motor 4 | Aurora Wells 1-4 Water Treatment Plant | 2026-01-07
CENTRAL | January | Onsite to complete assigned work orders- informed ROC: H/S inspection Silicate pump inspections Ammonia pump inspections CL17 analyzer maintenance Turbidimeter maintenance CL2 leak alarm test Generator test run (test under load: P1 and P4) Start time- 12:16 Stop time- 13:53 Start fuel- 7,152 L (27 cm) Stop fuel- 7,142 L (27 cm) Start hours- 89.55 Stop hours- 91.15 Pre test inspection completed- no abnormalities to report * Generator operating stats: 1804 rpm 79 psi oil pressure 188 F oil temp 179 F coolant temp 60 Hz 603 Volts 188 A Generator test run completed- no abnormalities. Generator back into auto as per normal operations. Station/equipment- Ok | Aurora Wells 1-4 Water Treatment Plant | 2026-01-13
CENTRAL | January | -Performed station check - logged station readings into PWQ sheet -Checked CL17 reagents - OK -Changed chlorine cylinders | Aurora Wells 1-4 Water Treatment Plant | 2026-01-02
CENTRAL | January | Picked up silicate from bulk tank. 750 L. | Aurora Wells 1-4 Water Treatment Plant | 2026-01-13
CENTRAL | January | Onsite for station check/collect sample- WO# W11504220: Sample results (11:24): Free- 0.07, Total- 3.00 * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok Onsite for raw station check: Collected raw samples Station/equipment- Ok | Aurora Wells 1-4 Water Treatment Plant | 2026-01-07
CENTRAL | January | Onsite for treated station check: Received CL2 cylinder delivery * Replaced effluent free CL17 reagents * Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Station/equipment- Ok Onsite for raw station check: Station/equipment- Ok | Aurora Wells 1-4 Water Treatment Plant | 2026-01-05
WEST | January | Onsite for station Reviewed scada, activated booster pumps duty for station Visual inspection in and around station Verification of equipment and instrumentation. Did chlorine grab readings: Outstanding alarm: None Grab Residuals @ 1330hrs Sample location. Grab reading. Analyzer reading Time: Grab: FCL =. 0.02 mg/l. mg/l 1330 hrs TCL = 2.03 mg/l. mg/l Recorded station readings into PWQ data sheet No issues | Holland Landing Sherwood Pumping Station | 2026-01-19
WEST | January | On-site for station check Review scada and trends Visual inspection of equipment and instrumentation Verified analyzer reading Outstanding alarms: None Residual Chlorine @ 1257hrs: FCL = 0.02 mg/l TCL = 2.66 mg/l No issues | Holland Landing Sherwood Pumping Station | 2026-01-26
WEST | January | Complete station check, enter data into PWQ. Monitor duty cycle. No issues. | Holland Landing Sherwood Pumping Station | 2026-01-30
WEST | January | On-site for station check Review scada and trends Visual inspection of equipment and instrumentation Verified analyzer reading Outstanding alarms: None Residual Chlorine @ 1200hrs : FCL = 0.02 mg/l TCL = 2.13 mg/l No issues | Holland Landing Sherwood Pumping Station | 2026-01-23
WEST | January | -on site to complete station check -checked equipment -reviewed trends remotely -pump #1 hours = 35561.8 -pump #2 hours = 7780.0 -pump #3 hours = 7360.2 -pump #4 hours = 2259.2 10:24 - collected grab sample: Free chlorine = 0.04 mg/L Total chlorine = 1.52 mg/L -recorded readings in PWQ sheet -no issues found | Holland Landing Sherwood Pumping Station | 2026-01-16
WEST | January | On site for generator test run and JHSC health and safety checks notified ROC Generator start hours: 1429.0 Start time: 1418 hrs Diesel level at start:L 681 L Hours at stop: 1430.5 Stop time: 1553 hrs Diesel level at stop: 674 L Reviewed scada before leaving site, no issues Notified ROC | Holland Landing Sherwood Pumping Station | 2026-01-15
WEST | January | On site for station check Reviewed scada and trends Visual inspection in and around station Verification of equipment and instrumentation. Verified chlorine analyzers readings. Recorded station readings into pwq data sheet Chlorine residual grabs: @ 1034 hrs: FCL = 0.03 mg/l TCL = 1.57 mg/l No issues | Holland Landing Sherwood Pumping Station | 2026-01-09
WEST | January | Arrived onsite to investigate generator fault alarm Earlier site had power failure and generator failed to start. Utility power was restored but fault was outstanding. On arrival noticed overcrank light on generator illuminated. Tried to test generator First put ats toggle to eng start no response Then tried to put in manual and switch to emergency power. Power failure alarm came back in and nothing happened with generator After discussion with ORO decided to leave outstanding and have electrician look at it in the morning. | Holland Landing Sherwood Pumping Station | 2026-01-10
WEST | January | Call out for generator not working. Arrived on site and found generator battery flat. Also found generator battery charger in the off position. Replaced battery made sure charger was on and working. Station transfer test and engine start all working correctly. | Holland Landing Sherwood Pumping Station | 2026-01-10
WEST | January | Sherwood Forerst Pumping Station On site for station check Visual inspection in and around station Verification of equipment and instrumentation. Verified chlorine analyzers readings. Recorded station readings into pwq data sheet Chlorine residual grabs: @ 1155 hrs: FCL = 0.05 mg/l TCL = 2.08 mg/l Checked battery charger ok. No issues | Holland Landing Sherwood Pumping Station | 2026-01-12
WEST | January | On site for station check Visual inspection in and around station Verification of equipment and instrumentation. Recorded station readings into pwq data sheet Outstanding alarm: none Grabs: Residual: Grab Time (HR). FCL. 0.05 mg/l 1503 hrs TCL. 2.09 mg/l No issues | Holland Landing Sherwood Pumping Station | 2026-01-05
WEST | January | On site for station check. Check trends: All okay. 09:25-Took grab Free: 0.02 mg/L Total: 2.01 mg/L Entered values in PWQ sheet Equipment okay | Holland Landing Sherwood Pumping Station | 2026-01-02
EAST | January | On site for station check. Collected CL grab residual on Discharge Header: 14:40hrs: Free Cl2 grab residual: 0.04mg/l, Total Cl2 grab residual: 1.39mg/l Checked station readings. All information in PWQ sheet. Checked site and equipment. Equipment out of service: None. | Bayview Pumping Station | 2026-01-19
EAST | January | Under Direction of OIC (joe Mazza) On site for; - Station checks Grabs @ 11:43 hrs. FCl: 0.04 mg/L TCl: 1.59 mg/L Analyzer Free Chlorine 0.08 mg/L Analyzer Total Chlorine: 1.68 mg/L Duty Active Equipment OOS: Pump 2 (being rebuilt off-site) Facility OK | Bayview Pumping Station | 2026-01-30
EAST | January | Under Direction of OIC (Dan Zhou) On site for; - Station checks Data in PWQ workbook Grabs @ 13:35 hrs. FCl: 0.08 mg/L TCl: 1.44 mg/L Analyzer Free Chlorine 0.06 mg/L Analyzer Total Chlorine: 1.44 mg/L Equipment OOS: Pump 2 (being rebuilt off-site) Facility OK | Bayview Pumping Station | 2026-01-16
EAST | January | On site to check station. Duty is active upon arrival. P1 and P3 are running in duty 1.? 13:28 Chlorine verification are below (grab/analyzer in mg/l): Free: 0.04/0.07 Total: 1.45/1.45 Readings are in PWQ sheet.? Reviewed trends, station is under normal operation.? Equipment OOS: Pump 2 due to rebuild.? | Bayview Pumping Station | 2026-01-23
EAST | January | On site to check station and equipment. P1 and P3 are running in duty 1 upon arrival. Manual stopped P3. Switch P4 to duty 1.? So that P1 and P4 are in lead duty. 12:45 Chlorine verification are below (grab/analyzer in mg/l) Total: 1.57 / 1.55 Free: 0.07 / 0.07 Readings are in PWQ sheet.? Reviewed trends, station is under normal operation.? Pump 2 remains OOS. | Bayview Pumping Station | 2026-01-26
EAST | January | Chris Iliohan Tyler Smith Kyle Rae in to remove pump 2 for rebuild. | Bayview Pumping Station | 2026-01-08
EAST | January | On site with Gary P, Travis W, Will M, Peter for Saycamore PRV testing.? Pump duty is not active upon arrival. Performed Sycamore valve chamber inspection. Tested flood alarm and sump pump maintenance.? Kyle R, Arthur L and Kyle B are on site to trouble shoot power outage issues. 10:32 Activated duty to simulate a power outage.? 10:51 Power is out by tripping incoming breaker. Confirmed the duty 1 pumps has staggered start now.? Assigned pump 1 and 3 to priority 1 so they stay in duty 1 in case of power failure. Worked with Gary to test sycamore PRV.? Confirmed that Sycamore PRV is set to open when down stream pressure is dropped below 300kpa.? Station is back to normal standby? Pump 2 remains OOS.? | Bayview Pumping Station | 2026-01-13
EAST | January | On site with Artour Litvinov and Dan Zhou to simulate and troubleshoot generator failure. ROC notified. Opened 27.6kv switch to interrupt station power. Generator run in auto and pumps tested to ensure no issues with duty on restart. Testing completed without further issues. 27.6kv switch closed and station returned to utility supply. ROC notified. | Bayview Pumping Station | 2026-01-13
EAST | January | Under Direction of OIC (Dan Zhou) On site for; - Station checks Data in PWQ Workbook Grabs @ 12:21 hrs. FCl: 0.07 mg/L TCl: 1.55 mg/L Analyzer Free Chlorine 0.07 mg/L Analyzer Total Chlorine: 1.51 mg/L Duty Not Active At NE side of building, drainage from adjacent property bilging at PAC panel platform, dug channel for water to flow through piled up snow and informed Supervisor Aaron to notify property services. Equipment OOS: Pump 2 (being rebuilt off-site) Facility OK | Bayview Pumping Station | 2026-01-09
EAST | January | Under Direction of OIC (Stephen Baidy) On site for; - Station checks - Pump 4 inspection Data in PWQ Workbook @ 13:09 manually activated duty 1 (pumps 1 and 4) Inspected pump 4, visual, audible, vibration and trends, pump OK Grabs @ 13:35 hrs. FCl: 0.08 mg/L TCl: 1.48 mg/L Analyzer Free Chlorine 0.06 mg/L Analyzer Total Chlorine: 1.45 mg/L Equipment OOS: Pump 2 (being rebuilt off-site) Facility OK | Bayview Pumping Station | 2026-01-12
EAST | January | On site to do more operational testing with the generator while pumps are running. Tested two pumps running in duty one and killed main power to the station and observed the automatic response. Found that once the generator was up and running that multiple pumps were starting simultaneously. This caused the generator to bog down and fault out. Found that as long as only one pump starts at a time with a few minutes in between starting subsequent pumps, the generator operates correctly. Will follow up with the PCS department to see if we can stagger the start commands for each pump. Also, input correct times into the clock setting of all multilin protection relays. | Bayview Pumping Station | 2026-01-06
EAST | January | On site to check station and equipment. Duty is not active upon arrival.? 13:00 grab free chlorine = 0.03 mg/l, analyzer free = 0.09mg/l.? Grab total chlorine = 1.54 mg/l, analyzer total = 1.60 mg/l. Adjusted free analyzer reading to 0.03 mg/l according to 3 grabs average.? Pump 2 is Man/Off due to electrical issue.?WO created for electricians to investigate. P1 and P3 ?are in duty 1 standby.? Reviewed trends, no issues. | Bayview Pumping Station | 2026-01-02
EAST | January | After communication with Dan B, placed pump 2 and pump 4 in auto duty 1. Activate duty. RHRSTR level is 70%. | Bayview Pumping Station | 2026-01-05
EAST | January | On site with Travis W, Will M. Dan B, Kyle R. Assigned pump 2 and 3 to duty 1.? Activated duty. Dan B. Tripped the main incoming 27.6kv breaker to simulate a real power outage. Generator started OK. But the pumps switched duty automatically, even auto duty rotation is disabled. (P3 and P4 switched to duty 1). Once ack+reset the alarms, both duty 1 pumps tried to start at the same time, faulted the generator, and generator uncommanded stop. By ack+reset the alarms, the generator resumed operation. Deactivated duty and re-activated, staggered duty 1 pumps starting resumed and it is no issue to run 2 pumps on generator power. Deactived the duty so that Dan B can close the main incoming 27.6kv breaker.? Station is back on utility power. | Bayview Pumping Station | 2026-01-06
EAST | January | -Responded hihi treated free analyzer reading - upon arrival, analyzer reading treated total=1.56mg/L free=0.26mg/L - performed grab test treated total=1.52mg/L free=0.03mg/L - calibrated free analyzer based on 3 grab tests | Bayview Pumping Station | 2026-01-03
EAST | January | On site to troubleshoot generator and pump starting issue left over from holiday break on December 27. Investigated event logs on motor protection relays. Insulation resistance tested pump two. Test ran pump two. Pump two seems to be operating correctly. Put pump two back in automatic and in-service. | Bayview Pumping Station | 2026-01-05
EAST | January | Under Direction of OIC (Dan Zhou) On site for; - Station checks Data in PWQ Workbook Grabs @ 13:41 hrs. FCl: 0.05 mg/L TCl: 1.51 mg/L CCl: 1.46 mg/L Pump 2 put in manual on by ROC at request of Maintenance after grabs were taken. Equipment OOS: none Facility OK | Bayview Pumping Station | 2026-01-05
EAST | January | Under direction of OIC Dan Zhou On site for; - Dehumidifier cleaning and inspection - Surge anticipatory test, discharge chamber - Ventilation system inspection - Pipe supports visual inspection - Centrifugal pump 1,2 and 3 inspection - Siemens analyzer maintenance - Sump pump maintenance - JHSC health and safety inspection Analyzer verification Grabs @ 14:26 hrs. FCl: 0.04 mg/L TCl: 1.45 mg/L Analyzer FCl: 0.09 mg/L TCl: 1.32 mg/L Adjusted analyzer to 1.45 mg/L after 3 grab average | Bayview Pumping Station | 2026-01-06
WEST | January | -on site for station check -site not plowed - informed team lead -checked trends: all ok -entered reading in PWQ: all ok -verified analyzer 10:35 -analyzer free: 0.04mg/l grab: 0.02mg/l -analyzer total:1.95mg/l grab: 1.92mg/l -reagents all ok -flushed sanitary pit -equipment all ok | East Vaughan Teston Pumping Station | 2026-01-16
WEST | January | -on site to reset sanitary pumps -locally tested pumps: all ok -drained the pit down | East Vaughan Teston Pumping Station | 2026-01-16
WEST | January | -on site for station check -check trends: all ok -entered readings in PWQ: all ok - verified analyzer 11:00 -analyzer free: 0.03mg/l grab: 0.06mg/l -analyzer total: 2.03mg/l grab: 2.00mg/l -reagents all ok | East Vaughan Teston Pumping Station | 2026-01-19
WEST | January | Vibration testing Pd 7 and 8 | East Vaughan Teston Pumping Station | 2026-01-19
WEST | January | -on site for station check -check trends: all ok -entered readings in PWQ: all ok -verified analyzer 10:15 -analyzer free: 0.08mg/l grab: 0.09mg -analyzer total: 2.12/l grab: 2.09mg/l -reagents all ok -investigated HVAC temp alarm - heater working no issues -adjusted low and low low alarm 15/10 - 10/5 degrees - alarm cleared -flushed sanitary pit | East Vaughan Teston Pumping Station | 2026-01-30
WEST | January | -on site to investigate PD8 pump 4 VFD fault caused by discharge valve fail to open -inspected valve - no issues -reset VFD and alarms -placed pump 4 into duty 1 and activated -informed ROC | East Vaughan Teston Pumping Station | 2026-01-22
WEST | January | -noticed flatline on PD7 free reading -checked analyzer and unit is trending correctly -zero calibrated free and took grab at 11:30 -free cl: 0.03mg/l | East Vaughan Teston Pumping Station | 2026-01-16
WEST | January | -on site for station check -checked trends: all ok -entered reading in PWQ: all ok -verified analyzer 11:35 -analyzer free: 0.08mg/l grab: .10mg/l -analyzer total: 2.07mg/l grab: 2.07mg/l -topped up KI reagents -equipment all ok | East Vaughan Teston Pumping Station | 2026-01-26
WEST | January | -on site to complete station check -checked trends: all ok -entered readings in PWQ: all ok -verified analyzer 09:55 -analyzer free: 0.03mg/l grab: 0.08mg/l - adjusted -analyzer total: 1.99mg/l grab: 1.95mg/l -replaced acetate -heating all ok | East Vaughan Teston Pumping Station | 2026-01-23
WEST | January | -on site for station check and completed following work orders -checked trends: all ok -entered readings in PWQ: all ok -verified and completed maintenance on analyzer 11:30 -analyzer free: 0.04mg/l grab: 0.05mg/l -analyzer total: 2.01mg/l grab: 2.01mg/l -reagents, pressure and cell all ok - adjusted flow to unit -ran diesel -diesel start: 234.6 -diesel stop: 235.8 -diesel level: 1845L (73% day tank), 6508L (48.4% bulk tank) -flushed PD7 and PD8 air valves -completed general housekeeping of Main floor -flushed sanitary pit | East Vaughan Teston Pumping Station | 2026-01-08
WEST | January | On site for station Check Check trend, all ok Enter readings on PWQ Analyzer free 0.04 mg/l , grab 0.04mg/l Analyzer total 2.08 mg/l, grab 2.02 mg/l - adjusted to 2.02 Equipment all ok | East Vaughan Teston Pumping Station | 2026-01-12
WEST | January | -on site for station check -checked trends: all ok -entered readings in PWQ: all ok -verified analyzer 11:20 -analyzer free: 0.04mg/l grab:0.06mg/l -analyzer total: 2.02mg/l grab: 1.98mg/l -reagents all ok -equipment all ok | East Vaughan Teston Pumping Station | 2026-01-05
WEST | January | On site to complete station check. Flushed sanitary pit Free chlorine Grab: 0.05mg/L Analyzer: 0.04mg/L Total chlorine Grab: 2.01mg/L Analyzer 2.02mg/L Reagents - all ok | East Vaughan Teston Pumping Station | 2026-01-02
WEST | January | On site for station check and completion of the following WOs: - Low temp alarm test - JHSC health and safety inspection - Portable generator run test Did visual inspection of station, no issues found inspected equipment and instrumentation no issues Notified ROC before and completion of WOs | Holland Landing East Elevated Tank | 2026-01-26
WEST | January | On site for station check Tower offline, no flow Visual inspection in and around station Verification of equipment and instrumentation. No issues | Holland Landing East Elevated Tank | 2026-01-12
WEST | January | On-site for station check and collection of weekly bacT samples Reviewed scada and trends, duty active, Verified chlorine analyzers readings Visual inspection on instrumentation and equipment AOK Chemical pumps: Chlorine: chlorinator#1 opened @ 34% and dosing at 37 ppd Chlorine dose scada = 15.3 kg/d Chlorinator2 and BP2 in dury2 Chlorine booster pressure: 142 psi Ammonia: Pump1 in duty1 running at 51 % speed Dosing 53.76 mL/min P1 MAX flow = 106 mL/min P2 MAX flow = 100 mL/min Pump discharge pressure: 550 kpa Silicate : pump1 running in duty1 @ 37% Silicate dose = 34.80 mL/min Chlorine grabs: @ 0928 hrs Influent FCL FCL = 2.82mg/l Analyzer reading: FCL = 2.84 mg/l Effluent FCL @ 0942 hrs: FCL = 2.86 mg/l Analyzer: 2.82 mg/l Treated grabs @ 0939 hrs FCL : 0.09 mg/l Analyzer reading: FCL : 0.14 mg/l TCL : 3.42 mg/l TCL : 3.39 mg/ SL1000 grab @ 0920 hrs: Mono = 2.80 mg/l FA = 0.06 mg/l TA = 0.61 mg/l No issues | Holland Landing Well No. 1 | 2026-01-21
WEST | January | On-site for station check Reviewed scada and trends, duty active, Verified chlorine analyzers readings Visual inspection on instrumentation and equipment AOK Chemical pumps: Chlorine: chlorinator#1 opened @ 35% and dosing at 37 ppd Chlorine dose scada = 15.3 kg/d Chlorinator2 and BP2 in dury2 Chlorine booster pressure: 142 psi Ammonia: Pump1 in duty1 running at 43% speed Dosing 52.87 mL/min P1 MAX flow = 106 mL/min P2 MAX flow = 100 mL/min Pump discharge pressure: 550 kpa Silicate : pump1 running in duty1 @ 36% Silicate dose = 34.43 mL/min Chlorine grabs: @ 1520 hrs Influent FCL FCL = 2.84mg/l Analyzer reading: FCL = 2.81 mg/l Effluent FCL @ 1522 hrs: FCL = 2.98 mg/l Analyzer: 2.93 mg/l Treated grabs @ 1522 hrs FCL : 0.09 mg/l Analyzer reading: FCL : 0.14 mg/l TCL : 3.44 mg/l TCL = 3.44 SL1000: @ 1322 hrs: FA = 0.04 mg/l TA = 0.60 mg/l Mono = 2.83 mg/l | Holland Landing Well No. 1 | 2026-01-26
WEST | January | Attending site to check Silicate Pump# run relay issues (W11617594). Removed pump to perform repairs to circuit board. Ran out of time - returning tomorrow. ROC was notified that there will be outstanding alarms until the pump repairs have been completed. | Holland Landing Well No. 1 | 2026-01-29
WEST | January | Install rebuild kit flow control valve | Holland Landing Well No. 1 | 2026-01-27
WEST | January | On-site for station check Reviewed scada and trends, duty active, Verified chlorine analyzers readings Visual inspection on instrumentation and equipment AOK Chemical pumps: Chlorine: chlorinator#1 opened @ 35% and dosing at 38 ppd Chlorine dose scada = 15.3 kg/d Chlorinator2 and BP2 in dury2 Chlorine booster pressure: 155 psi Ammonia: Pump2 in duty2 running at 52 % speed dosing 51.06 mL/min pump discharge pressure: 600 kpa Silicate : pump1 running in duty1 @ 36% Silicate dose = 34.43 mL/min Chlorine grabs: @ 1510 hrs Influent FCL FCL = 2.78mg/l Analyzer reading: FCL = 2.81 mg/l Effluent FCL @ 1520 hrs: FCL = 2.74 mg/l Analyzer: 2.69 mg/l Treated grabs @ 1539 hrs FCL : 0.08 mg/l Analyzer reading: FCL : 0.14 mg/l TCL : 3.28 mg/l TCL : 3.23 mg/l Dave T collected SL1000 readings and recorded in pwq data sheet | Holland Landing Well No. 1 | 2026-01-19
WEST | January | On-site for station check Reviewed scada and trends, duty active, ET at 79% Verified chlorine analyzers readings Visual inspection on instrumentation and equipment AOK Chemical pumps: Chlorine: chlorinator#1 opened @ 34% and dosing at 38 ppd Chlorine dose scada = 15.3 kg/d Chlorinator2 and BP2 in dury2 Chlorine booster pressure: 155 psi (1,069 kpa) Ammonia: Pump1 in duty1 running at 42% speed Dosing 49.66 mL/min P1 MAX flow = 120 mL/min P2 MAX flow = 120 mL/min Pump discharge pressure: 453 kpa Silicate : pump1 running in duty1 @ 36% Silicate dose = 34.07 mL/min Chlorine grabs: @ 1228 hrs Influent FCL FCL = 2.80mg/l Analyzer reading: FCL = 2.80 mg/l Effluent FCL @ 1238 hrs: FCL = 2.60 mg/l Analyzer: 2.63 mg/l Treated grabs @ 0916 hrs FCL: 0.08 mg/l Analyzer reading: FCL: 0.14 mg/l TCL: 3.33 mg/l TCL: 3.29 mg/l SL1000: @ 1238 hrs with Ammonia pump1 FA = 0.03 mg/l TA = 0.54 mg/l Mono = 2.52 mg/l | Holland Landing Well No. 1 | 2026-01-30
WEST | January | On-site for station check Reviewed scada and trends, duty not active, ET at 72% Activated duty for SL1000 grab Verified chlorine analyzers readings Visual inspection on instrumentation and equipment AOK Chemical pumps: Chlorine: chlorinator#1 opened @ 35% and dosing at 37 ppd Chlorine dose scada = 15.3 kg/d Chlorinator2 and BP2 in dury2 Chlorine booster pressure: 142 psi Ammonia: Pump1 in duty1 running at 43% speed Dosing 52.87 mL/min P1 MAX flow = 106 mL/min P2 MAX flow = 100 mL/min Pump discharge pressure: 550 kpa Silicate : pump1 running in duty1 @ 36% Silicate dose = 34.43 mL/min Chlorine grabs: @ 0933 hrs Influent FCL FCL = 2.90mg/l Analyzer reading: FCL = 2.93kjmzjmz mg/l Effluent FCL @ 0933 hrs: FCL = 2.90 mg/l Analyzer: 2.93 mg/l Treated grabs @ 0930 hrs FCL : 0.10 mg/l Analyzer reading: FCL : 0.15 mg/l TCL : 3.38 mg/l TCL : 3.32 mg/l SL1000: @ 0933 hrs with Ammonia pump2 FA = 0.02 mg/l TA = 0.49 mg/l Mono = 2.47 mg/l Switched ammonia pump duty, placed ammonia pump1 in lead duty and adjusted max flow setpoint from 106 to 120 mL/min. Collected sample for SL1000 reading. Returned ammonia pump1 to service. SL1000: @ 0954 hrs: FA = 0.05 mg/l TA = 0.59 mg/l Mono = 2.75 mg/l 1344 hrs activated duty after rebuild of FCV by MAINT, Lee adjusted flow to 23.9 l/s. placed ammonia pump2 in lead duty. Collected SL1000 grabs at 1430 hrs Eff FCL = 1.68 mg/l Analyzer = 1.70 mg/l FA = 0.01 mg/l TA = 0.52 mg/l Mono = 2.60 mg/l | Holland Landing Well No. 1 | 2026-01-27
WEST | January | -on site to change cylinder -68kg - 136kg | Holland Landing Well No. 1 | 2026-01-29
WEST | January | On-site for station check Reviewed scada and trends, duty active, Verified chlorine analyzers readings Visual inspection on instrumentation and equipment AOK Chemical pumps: Chlorine: chlorinator#1 opened @ 34% and dosing at 37 ppd Chlorine dose scada = 15.3 kg/d Chlorinator2 and BP2 in dury2 Chlorine booster pressure: 142 psi Ammonia: Pump1 in duty1 running at 41% speed Dosing 49.43 mL/min P1 MAX flow = 106 mL/min P2 MAX flow = 120 mL/min Pump discharge pressure: 550 kpa Silicate : pump1 running in duty1 @ 36% Silicate dose = 34.43 mL/min Chlorine grabs: @ 1705 hrs Influent FCL FCL = 2.90mg/l Analyzer reading: FCL = 2.85 mg/l Effluent FCL @ 1718 hrs: FCL = 2.90 mg/l Analyzer: 2.88 mg/l Treated grabs @ 1720 hrs FCL : 0.09 mg/l Analyzer reading: FCL : 0.14 mg/l TCL : 3.42 mg/l TCL : 3.45 mg/l SL1000: @ 1600 hrs: FA = 0.23 mg/l TA = 0.80 mg/l Effluent Grab: 2.82 mg/l Mono = 2.93 mg/l Effluent FCL analyzer reading: 2.79 mg/l Adjusted ammonia pump2 max flow from 90 to 120 mL/min. Also, increased chlorine ammonia ratio from 4.30 to 4.7 mg/l SL1000: @ 1655 hrs: FA = 0.05 mg/l Effluent Grab: 2.90 mg/l TA = 0.61 mg/l Mono = 2.84 mg/l Effluent FCL analyzer reading: 2.88 mg/l Placed ammonia pump1 in manual off for the weekend, and will return on Monday to troubleshoot with ammonia issue with pump2. will notify operator on call and ROC | Holland Landing Well No. 1 | 2026-01-23
WEST | January | On-site for station check and collection of weekly bacT samples Reviewed scada and trends, duty active, ET at 40% Verified chlorine analyzers readings Visual inspection on instrumentation and equipment AOK Chemical pumps: Chlorine: chlorinator#1 opened @ 34% and dosing at 38 ppd Chlorine dose scada = 15.3 kg/d Chlorinator2 and BP2 in dury2 Chlorine booster pressure: 155 psi (1,069 kpa) Ammonia: Pump1 in duty1 running at 42% speed Dosing 49.66 mL/min P1 MAX flow = 120 mL/min P2 MAX flow = 120 mL/min Pump discharge pressure: 453 kpa Silicate : pump1 running in duty1 @ 36% Silicate dose = 34.07 mL/min Chlorine grabs: @ 0900 hrs Influent FCL FCL = 2.84mg/l Analyzer reading: FCL = 2.82 mg/l Effluent FCL @ 1040 hrs: FCL = 2.68 mg/l Analyzer: 2.66 mg/l Treated grabs @ 0916 hrs FCL : 0.08 mg/l Analyzer reading: FCL : 0.14 mg/l TCL : 3.33 mg/l TCL : 3.29 mg/l SL1000: @ 1040 hrs with Ammonia pump1 FA = 0.03 mg/l TA = 0.56 mg/l Mono = 2.72 mg/l Adjusted chlorine DF on chlorinator1 from 112 to 115% | Holland Landing Well No. 1 | 2026-01-28
WEST | January | -on site to complete station check -well running in auto -cl2 booster pump # 2 running at 140 psi -chlorinator # 2 34% open dosing 35 ppd, vac = -60 mbar, DF = 115% -silicate pump # 1 running at 35%, 19.4 rpm -ammonia pump # 1 running at 48%, 85 psi, 88 strokes/min -checked equipment -reviewed trends -CL17 reagents ok -verified chlorine analyzers: 13:38 - Treated water analyzers: FCL = 0.14 mg/L TCL = 3.15 mg/L 13:38 - Treated water grabs: FCL = 0.11 mg/L TCL = 3.14 mg/L MCL = 2.71 mg/L TNH3 = 0.61 mg/L FNH3 = 0.08 mg/L 13:52 - Influent FCL Analyzer = 2.82 mg/L 13:52 - Influent grab: Free chlorine = 2.80 mg/L 13:48 - Effluent FCL Analyzer = 2.64 mg/L 13:48 - Effluent grab: Free chlorine = 2.60 mg/L -filled ammonia #1 80 L to 361 L -recorded readings in PWQ sheet -no issues found -completed Chemical System Inspection - Ammonia | Holland Landing Well No. 1 | 2026-01-16
WEST | January | Attending site to check sodium silicate pump#2 (W11617594 - Fail to Start). Found run output relay in pump is no longer making contact. Replaced relay and tested running status back to PAC. All good now. ROC was notified before and after maintenance activities. | Holland Landing Well No. 1 | 2026-01-30
WEST | January | On-site to collect operational samples for inhouse lab Reviewed scada and trends, duty active, Verified chlorine analyzers readings Visual inspection on instrumentation and equipment AOK Chemical pumps: Chlorine: chlorinator#2 opened @ 34% and dosing at 38 ppd Chlorine dose scada = 15.3 kg/d Chlorinator1 and BP2 in dury1 Chlorine booster pressure: 155 psi Ammonia: Pump2 in duty2 running at 48 % speed dosing 51.34 mL/min pump discharge pressure: 600 kpa Silicate : Pump1 running in duty1 @ 35% Silicate dose = 33.70 mL/min Chlorine grabs: @ 0953 hrs Influent FCL FCL = 2.84mg/l Analyzer reading: FCL = 2.79 mg/l Effluent FCL @ 0956 hrs: FCL = 2.80 mg/l Analyzer: 2.75 mg/l Treated grabs @ 1025 hrs FCL : 0.10 mg/l Analyzer reading: FCL : 0.14 mg/l TCL : 3.40 mg/l TCL : 3.36 mg/l Deactivated duty for MAINT electrician to troubleshoot with silicate pump2 | Holland Landing Well No. 1 | 2026-01-20
WEST | January | -on site to troubleshoot silicate pump 2 running issue. With Stephen we tested and I tried tightening connections but the signal was still acting erratic. Placed pump back to manual and will need to return to further test. Under direction of oic. | Holland Landing Well No. 1 | 2026-01-20
WEST | January | On-site for station check and collection of quarterlies and weekly bacT samples Reviewed scada and trends, duty active, Verified chlorine analyzers readings Visual inspection on instrumentation and equipment AOK Chemical pumps: Chlorine: chlorinator#1 opened @ 34% and dosing at 38 ppd Chlorine dose scada = 14.8 kg/d Chlorinator2 and BP2 in dury2 Chlorine BP discharge pressure:155 psi Ammonia: Pump2 in duty2 running at 53 % speed dosing 52.61 mL/min pump discharge pressure: 600 kpa Silicate : pump1 running in duty1 @ 36% Silicate dose = 34.43 mL/min Chlorine grabs: @ 1519 hrs Influent FCL FCL = 2.82mg/l Analyzer reading: FCL = 2.82 mg/l Effluent FCL @ 1516 hrs: FCL = 2.70 mg/l Analyzer: 2.69 mg/l Treated grabs @ 1530 hrs FCL: 0.10 mg/l Analyzer reading: 0.15 mg/l TCL: 3.30 mg/l SL1000: @ 1424 hrs: FA = 0.12 mg/l TA = 0.69 mg/l Mono = 2.86 mg/l Effluent FCL analyzer reading: 2.70 mg/l 1510 hrs adjusted the max flow on ammonia pump2 from 97 to 100 mL/min Ammonia pump2 speed now 51% and dosing 51.58 mL/min SL1000: @ 1528 hrs: FA = 0.08 mg/l TA = 0.60 mg/l Mono = 2.61 mg/l Effluent FCL analyzer reading: 2.68 mg/l System pressure: 443 Kpa | Holland Landing Well No. 1 | 2026-01-14
WEST | January | On-site for station check s Reviewed scada and trends, duty not active, controlling ET @ 72% and drainig Activated duty @ 1140hrs Verified chlorine analyzers readings Visual inspection on instrumentation and equipment AOK Chlorine grabs: @ 1355 hrs Influent FCL FCL = 2.76mg/l Analyzer reading: FCL = 2.08 mg/l Effluent FCL @ 1350 hrs: FCL = 2.62 mg/l Analyzer: 2.59 mg/l SL1000: @ 1350 hrs: FA = 0.00 mg/l TA = 0.47 mg/l Mono = 2.38mg/l Effluent FCL analyzer reading: 2.38 mg/l Chemical pumps: Chlorine: chlorinator#2 opened @ 33% Chlorine dose scada = 14.8 kg/d Chlorinator2 and BP2 in dury1 Silicate : pump2 running duty1 @ 40% Silicate dose = 48.32 mL/min System pressure: 44 kpa | Holland Landing Well No. 1 | 2026-01-12
WEST | January | On-site for station check and collection of weekly bacT samples Reviewed scada and trends OK Duty active. well 1 running in auto Verified chlorine analyzers readings Visual inspection on instrumentation and equipment AOK Chlorine grabs: @ 0934 FCL = 0.10 mg/l Analyzer reading: FCL = 0.13 mg/l TCL = 2.82 mg/l TCL = 2.77 mg/l SL1000: FA = 0.18 mg/l TA = 0.62 mg/l Mono = 2.25 mg/l Unable to troubleshoot with ammonia system issues as regulatory sample collection in progress. will return tomorrow for further troubleshooting no issues | Holland Landing Well No. 1 | 2026-01-07
WEST | January | -on site to check ammonia dosing 09:21 - treated grab ammonia pump #1 running: MCL = 2.70 TNH3 = 0.56 FNH3 = 0.03 09:34 - treated grab ammonia pump #2 running: MCL = 2.62 TNH3 = 0.50 FNH3 = 0.00 -decreased ammonia pump #2 max flow setpoint 120 to 97 ml/min, adjusted BPV to 85 psi 10:46 - treated grab ammonia pump #2 running: MCL = 2.69 TNH3 = 0.58 FNH3 = 0.05 -will continue to monitor | Holland Landing Well No. 1 | 2026-01-13
WEST | January | Returned chlorine dosing to auto | Holland Landing Well No. 1 | 2026-01-13
WEST | January | Filled silicate tanks 170/154 L to 398/364 L | Holland Landing Well No. 1 | 2026-01-12
WEST | January | On-site for station check Reviewed scada and trends OK Duty active. well 1 running in auto Verified chlorine analyzers readings Visual inspection on instrumentation and equipment AOK Chlorine grabs: @ 1240 FCL = 0.11 mg/l Analyzer reading: FCL = 0.17 mg/l TCL = 3.08 mg/l TCL = 3.05 mg/l SL1000: @ 1240 hrs: FA = 0.12 mg/l TA = 0.64 mg/l Mono = 2.65 mg/l 1256 hrs: Made adjustment on ammonia system, increased ammonia pump1 max flow setpoint from 102 to 106 ~ Dave 1303 hrs: Did 2nd grab SL100 reading from Ammonia Pump1 FCL = 0.11 mg/l Analyzer reading: FCL = 0.17 mg/l TCL = 3.08 mg/l TCL = 3.05 mg/l FA = 0.06 mg/l TA = 0.56 mg/l Mono = 2.55 mg/l deactivated duty 1321 hrs: 3rd SL1000 grab from Ammonia Pump2 FA = 0.01 mg/l Eff FCL analyzer @ 2.52 mg/l TA = 0.50 mg/l Mono = 2.50 mg/l | Holland Landing Well No. 1 | 2026-01-09
WEST | January | -on site to troubleshoot ammonia system -collected grab, ammonia pump #2 running MCL = 2.31 TNH3 = 0.59 FNH3 = 0.13 -collected grab, ammonia pump #2 running MCL = 2.59 TNH3 = 0.57 FNH3 = 0.05 -collected grab, ammonia pump #2 running MCL = 2.29 TNH3 = 0.56 FNH3 = 0.11 -collected grab, ammonia pump #2 running MCL = 2.34 TNH3 = 0.59 FNH3 = 0.13 -collected grab, ammonia pump #2 running FCL = 0.05 MCL = 2.34 TNH3 = 0.56 FNH3 = 0.09 -put influent analyzer into signal average 1 to monitor dosing consistency -verified influent analyzer: 10:27 - analyzer = 2.86 grabs = 2.46/2.48/2.52 10:40 - adjusted analyzer to 2.49 mg/L based on average of grabs -returned analyzer to signal average 2 -verified effluent analyzer: 10:40 - analyzer = 2.60 grabs = 2.30/2.32/2.26 10:44 - adjusted effluent analyzer to 2.29 mg/L based on average of grabs -verified treated total chlorine analyzer: 10:46 - analyzer = 2.97 grabs = 2.72/2.78/2.76 10:53 - adjusted analyzer to 2.75 mg/L based on average of grabs -collected treated grab, ammonia pump #2 running MCL = 2.32 TNH3 = 0.49 FNH3 = 0.03 -collected treated grab, ammonia pump #1 running MCL = 2.36 TNH3 = 0.59 FNH3 = 0.13 -increased ammonia pump #1 max flow setpoint 85 to 102 ml/min -collected treated grab, ammonia pump #1 running MCL = 2.47 TNH3 = 0.51 FNH3 = 0.02 FCL = 0.05 -increased chlorinator #2 DF 108% to 113% -increased chlorinator #1 DF 103% to 108% -filled ammonia tank #2 82 L to 367 L -completed cylinder change -completed work orders, informed ROC of work -completed Flow Control Valve, Test -completed Cl2 Emergency Repair Kit Inspection -completed Chlorine Gas Detector, Test -completed Chlorine Scrubber, Check -completed Chemical System Inspection - Chlorine: -completed vacuum test on both chlorinators, no issues -completed Chlorine Analyzer, Maintenance -verified analyzers after maintenance: 14:02 - Influent FCL Analyzer = 2.25 mg/L 14:02 - Influent grab: Free chlorine = 2.42/2.42/2.48 mg/L 14:12 - adjusted influent analyzer to 2.44 mg/L based on average of 3 grabs 14:13 - Effluent FCL Analyzer = 0.11 mg/L 14:13 - Effluent grab: Free chlorine = 0.07 mg/L 14:17 - Treated water analyzers: FCL = 0.22 mg/L TCL = 2.32 mg/L 14:17 - Treated water grabs: FCL = 0.23 mg/L TCL = 2.28 mg/L -completed Turbidity Analyzer TU5300, Maintenance and Calibration -started well, site back to normal operation | Holland Landing Well No. 1 | 2026-01-08
WEST | January | -on site to complete work orders -informed ROC of work -completed Chemical System Inspection - Silicate: -cleaned and flushed injection points -found injection point #1 seized in ball valve - replaced ball valve and injection point -replaced both injection point check valves -ran pumps into graduated cylinder: -pump #1 max flow = 104 ml/min, adjusted SCADA setpoint from 85 to 95 ml/min, will monitor dosage calculations -pump #2 max flow = 86 ml/min, SCADA setpoint = 85 ml/min -returned silicate system to normal operation -completed JHSC Health and Safety Inspection | Holland Landing Well No. 1 | 2026-01-06
WEST | January | -on site to complete work orders -informed ROC of work -completed JHSC Health and Safety Inspection -completed Low Temperature Alarm, Test -completed Sump Pit System, Inspection -completed Flood Alarm, Test -completed Storm Sump Pump, Maintenance -completed Bypass Valve Actuator, Exercise & Inspection -completed Bypass Manual Valve, Exercise -completed Pressure Relief Valve, Inspection -completed Chlorine Analyzer, Maintenance -verified analyzers after maintenance: 13:20 - Analyzer readings: Free Chlorine = 0.02 mg/L Total Chlorine = 1.90 mg/L 13:20 - Grabs: Free Chlorine = 0.02 mg/L Total Chlorine = 1.99/2.02/1.99 mg/L 13:34 - adjusted total chlorine analyzer to 2.00 mg/L based on average of grabs -completed Pump & Motor, Inspection -completed station check -system duty active -checked equipment -reviewed trends -recorded readings in PWQ sheet -replaced KI reagent -no issues found -site back to normal operation | Kleinburg HWY 27 Booster Pumping Station | 2026-01-15
WEST | January | on site for station check Well running manual on. Check Trends, All okay Verified Analyzers 13:30- Influent Free Grab: 2.70mg/L(avg-3.65,3.75,3.70), Analyzer: 3.10mg/L Adjusted analyzer down to 2.80 mg/L 13:35- Effluent Free Grab: 2.64mg/L, Analyzer: 2.69mg/L 13:20- Treated Free Grab: 0.09mg/L, Analyzer: 0.13mg/L 13:20- Treated Total Grab: 3.06 mg/L, Analyzer: 3.06 mg/L 13:20-SL1000 Mono- 2.42 mg/l Free NH3- 0.13 Total NH3-0.61 Adjusted ammonia Pump 2 max flow from 100 ml/min to 115 ml/min 14:25-SL1000 Mono- 2.48 mg/l Free NH3- 0.14 Total NH3-0.63 Adjusted ammonia Pump 2 max flow from 115 ml/min to 120 ml/min 13:45-SL1000 Mono- 2.43 mg/l Free NH3- 0.11 Total NH3-0.59 Replaced influent free an analyzer reagent entered values in PWQ sheet. Topped up ammonia tank 1- 19.32cm,89.06L-79.73cm,363.61L. Put well back to auto. equipment okay. | Holland Landing Well No. 1 | 2026-01-02
WEST | January | On site for Station Check. Check Trends: All okay Station Duty not Active. 12:48-Verified Analyzers Free Cl2 Grab- 0.04mg/L Free Cl2 Analyzer- 0.02mg/L Total Cl2 Grab- 2.08mg/L Total Cl2 Analyzer- 2.10mg/L Reagents All okay Entered values into PWQ sheet. Equipment Okay. | Kleinburg HWY 27 Booster Pumping Station | 2026-01-19
WEST | January | On site for Station Check. Check Trends: All okay Station Duty Active: Pump 1& 2 running 11:20-Verified Analyzers Free Cl2 Grab- 0.02mg/L Free Cl2 Analyzer- 0.02mg/L Total Cl2 Grab- 1.99mg/L Total Cl2 Analyzer- 1.96mg/L Reagents All okay Entered values into PWQ sheet. Equipment Okay. | Kleinburg HWY 27 Booster Pumping Station | 2026-01-30
WEST | January | On site for Station Check. Check Trends: All okay Station Duty Active, P1 & P3 running. 11:05-Verified Analyzers Free Cl2 Grab- 0.01mg/L Free Cl2 Analyzer- 0.02mg/L Total Cl2 Grab- 2.17mg/L Total Cl2 Analyzer- 2.11mg/L Reagents All okay Entered values into PWQ sheet. Equipment Okay. | Kleinburg HWY 27 Booster Pumping Station | 2026-01-23
WEST | January | On site for Station Check. Check Trends: All okay Station Duty not Active. 12:50-Verified Analyzers Free Cl2 Grab- 0.04mg/L Free Cl2 Analyzer- 0.03mg/L Total Cl2 Grab- 2.14mg/L Total Cl2 Analyzer- 2.07mg/L Reagents All okay W11585317- Washroom light cleaning and supplies check complete Entered values into PWQ sheet. Equipment Okay. | Kleinburg HWY 27 Booster Pumping Station | 2026-01-26
WEST | January | On site for Station Check. Check Trends: All okay Station Duty Active. 12:10-Verified Analyzers Free Cl2 Grab- 0.02mg/L Free Cl2 Analyzer- 0.02mg/L Total Cl2 Grab- 2.00mg/L Total Cl2 Analyzer- 1.96mg/L Reagents All okay Entered values into PWQ sheet. Equipment Okay. | Kleinburg HWY 27 Booster Pumping Station | 2026-01-12
WEST | January | On site for Station Check. Check Trends: All okay Station Duty Active. 11:30-Verified Analyzers Free Cl2 Grab- 0.02mg/L Free Cl2 Analyzer- 0.02mg/L Total Cl2 Grab- 1.96mg/L Total Cl2 Analyzer- 1.92mg/L Reagents All okay Entered values into PWQ sheet. Equipment Okay. | Kleinburg HWY 27 Booster Pumping Station | 2026-01-09
WEST | January | Station Check (no issues found) Input data to PWQ 12:40 Verified Depolox (mg/l) Free: Grab 0.05, A 0.02 Total: Grab 2.00, A 1.93 Depolox (acetate top up) | Kleinburg HWY 27 Booster Pumping Station | 2026-01-02
WEST | January | On site for Station Check. Check Trends: All okay Station Duty Active. 09:25-Verified Analyzers Free Cl2 Grab- 0.03mg/L Free Cl2 Analyzer- 0.02mg/L Total Cl2 Grab- 2.03mg/L Total Cl2 Analyzer- 1.97mg/L Reagents All okay Entered values in to PWQ sheet. Equipment Okay. | Kleinburg HWY 27 Booster Pumping Station | 2026-01-05
WEST | January | On-site for station check Review scada and trends Visual inspection of equipment and instrumentation Verified analyzer reading Outstanding alarms: station under rehab, well OOS, contractor on site @ 1322 hrs: Residual Chlorine ~ Treated Grab: FCL = 0.05 mg/l TCL = 1.53 mg/l Analyzer reading: FCL = 0.03 mh/l TCL = 1.55 mh/l No issues on site | Holland Landing Well No. 2 | 2026-01-26
WEST | January | Reduced chlorinator 2 df 157 to 153 % due to high treated combined chlorine | Holland Landing Well No. 2 | 2026-01-29
WEST | January | -on site to local run well to waste for IWS to set and test level indicator -verified distribution valve closed - no flow to system -contractor request well at 100% -opened discharge valve and backflush -14:41 to 14:43 -no issues | Holland Landing Well No. 2 | 2026-01-27
WEST | January | On-site for station check and to respond to combine chlorine hi alarm, Upon arrival treated analyzer was reading 3.50 mg/l 1222 hrs, did 2 grabs on treated analyzer (3.46 and 3.46) and adjusted analyzer accordingly. Reviewed scada and trends, duty active, ET at 80% Verified chlorine analyzers readings Visual inspection on instrumentation and equipment AOK Chlorine grabs: @ 1421 hrs Influent FCL FCL = 2.52mg/l Analyzer reading: FCL = 2.30 mg/l Unable to adjust influent FCL analyzer reading due to issues with keyboard, reported issue with Instrumentation and WO has been issued. Effluent FCL @ 1423 hrs: FCL = 2.52 mg/l Analyzer: 2.47 mg/l Treated grabs @ 1426 hrs FCL: 0.10 mg/l Analyzer reading: FCL: 0.18 mg/l TCL: 3.06 mg/l TCL: 3.01mg/l SL1000: @ 1342 hrs with Ammonia pump2 FA = 0.13 mg/l TA = 0.62 mg/l Mono = 2.51 mg/l 1413 hrs ~ increased ammonia pump2 max flow from 93 to 113 mL/min to fine tune ammonia dosage. FA = 0.03 mg/l TA = 0.53 mg/l Mono = 2.65 mg/l Chemical pumps: Chlorine: chlorinator#1 opened @ 68% and dosing at 68 ppd Chlorine dose scada = 29.7 kg/d Chlorinator2 and BP2 in dury2 Chlorine booster pressure: 1,350 kpa Ammonia: Pump2 in duty1 running at 59% speed Dosing 68.60 mL/min P1 MAX flow = 100 mL/min P2 MAX flow = 115 mL/min Pump discharge pressure: 453 kpa Silicate : pump1 running in duty2 @ 36% Silicate dose = 43.38 mL/min | Holland Landing Well No. 2 | 2026-01-30
WEST | January | Onsite to collect sample for well post rehab Opened inside station distribution valve and opened back flush valve Still isolated with valve in driveway closed Dechlor added to chamber Started well @1048 Noticed low flow and nothing coming from sample tap, closed exhaust valve and flown increased. Still no flow to sample tap Stopped well @1100 Electricians did some rewiring Started well again @1109 Tapered back flush valve until flow came from raw water tap Took grab and no chlorine residual at @1120 Disinfected tap with hypo @1140 Collected first sample W11617535 @1200 Second sample @1231 Stopped well and put back to local Closed station distribution valve Closed back flush valve Hit lockout reset for ct slider because it was ran to waste | Holland Landing Well No. 2 | 2026-01-27
WEST | January | -on site to complete station check -well offline for rehab -reviewed trends -replaced treated CL17 reagents -verified treated analyzers: 14:30 - Treated water analyzers: FCL = 0.04 mg/L TCL = 1.76 mg/L 14:30 - Treated water grabs: FCL = 0.03 mg/L TCL = 1.81 mg/L 14:38 - Sharon Valve grab: TCL = 1.42 mg/L MCL = 0.55 mg/L TNH3 = 0.29 mg/L FNH3 = 0.18 mg/L -no issues | Holland Landing Well No. 2 | 2026-01-16
WEST | January | -on site to test HLW2 selector switch -site was backflush and chlorine system primed -local start well at 11:43 -created work order for influent analyzer buttons W11622780 -CT achieved -took samples W11622652 -took chlorine grab 12:40 -free cl: 0.08mg/l analyzer: 0.18mg/l - unable to adjust -total cl: 3.30mg/l analyzer 3.35mg/l -changed influent reagents | Holland Landing Well No. 2 | 2026-01-29
WEST | January | On site with Tim Hudson to investigate Well Pump 2 fail to start. ROC notified. Found fuse on control circuit to be open. Replaced fuse and tested pump. Pump 2 returned to normal operation. ROC notified. | Holland Landing Well No. 2 | 2026-01-29
WEST | January | Onsite to complete the following WOs JHSC Health and Safety Inspection, Chlorine Gas Detector, Test, Chlorine Analyzer Maintenance, Chemical System Inspection - Chlorine, Pressure Relief Valve, Maintenance, Chemical System Inspection - Ammonia, Chlorine Scrubber, Check, Low/High Temperature Alarm, Test Turbidimeter, Maintenance, Holland Landing, Well Chemical System Inspection - Silicate, Pressure Relief Valve, Maintenance, Chlorine Scrubber, Media Sampling, Notified ROC before and completion of WOs Deactivated duty, controlling ET at 80% Completed station check after WOs completion On-site for station check Reviewed scada and trends, not duty active, Verified chlorine analyzers readings Visual inspection on instrumentation and equipment AOK 1430 hrs verified analyzers readings 1430 hr: Treated ~ FCL = 0.05 mg/l TCL = 1.92 mg/l Analyzer reading ~ FCL = 0.04 mg/l TCL = 1.94 mg/l cleared all alarms and reset No issues on site Notified ROC before leaving site | Holland Landing Well No. 2 | 2026-01-20
WEST | January | -on site to put the well back into service -passing results W11617535 -opened distribution valve and discharge vale -tested chlorine system -backflushed/dechlored contact tank -backflushed until 10:00 - influent total 1.70mg/l -well failed to start multiple time -contact electrical - Kyle Rae on site at 10:45 -found blown fuse -change cylinder with Steven B - 22kg - 90kg | Holland Landing Well No. 2 | 2026-01-29
WEST | January | On-site for station check Review scada and trends Visual inspection of equipment and instrumentation Verified analyzer reading Outstanding alarms: station under rehab, well OOS, contractor on site @ 1155 hrs: Residual Chlorine ~ Treated Grab: FCL = 0.04 mg/l TCL = 1.81mg/l Analyzer reading: FCL = 0.03 mg/l TCL = 1.83 mg/l Awaiting bacT sample results No issues on site | Holland Landing Well No. 2 | 2026-01-28
WEST | January | Check flow valves maintenance while well is out Picking up parts | Holland Landing Well No. 2 | 2026-01-12
WEST | January | Install new speed control on wasting valve flow control valve, have spare parts on hand for any further problems | Holland Landing Well No. 2 | 2026-01-12
WEST | January | On-site for station check Reviewed scada and trends OK Duty active. well 1 running in auto Verified chlorine analyzers readings Visual inspection on instrumentation and equipment AOK Chlorine grabs: @ 1250 hrs: Treated Analyzer FCL = 0.05 mg/l Analyzer reading: FCL = 0.05 mg/l TCL = 1.67 mg/l TCL = 1.68 mg/l Well 2 pmp OOS No issues | Holland Landing Well No. 2 | 2026-01-12
WEST | January | On-site for station check Reviewed scada and trends OK Duty active. well 1 running in auto Verified chlorine analyzers readings Visual inspection on instrumentation and equipment AOK Chlorine grabs: @ 1500 hrs: Treated Analyzer FCL = 0.05 mg/l Analyzer reading: FCL = 0.05 mg/l TCL = 2.13 mg/l TCL = 2.13 mg/l Well 2 pmp OOS No issues | Holland Landing Well No. 2 | 2026-01-09
WEST | January | on site for station check. check trends all okay Site offline for rehab Verified Analyzers 15:13- Treated Free Grab: 0.02mg/L, Analyzer: 0.05mg/L 15:13- Treated Total Grab: 2.19mg/L, Analyzer: 2.12mg/L 15:15- Effluent Free Grab: 0.02mg/L Analyzer: 0.06mg/L Reagent All okay. entered values in pwq sheet. equipment okay. | Holland Landing Well No. 2 | 2026-01-02
WEST | January | In to complete station check. Enter data into PWQ. All analyzer reagent levels good. Chemical dosing appears good at higher inlet flow (50l/s or above). Inlet ammonia SP matches inlet ammonia grab at higher end of cycle. Mono 75% of treated on post-inj; -adjust chlorine:ammonia ratio from 4.6 to 4.7 -post chlorine is slightly below target, but ammonia is within range No issues. | Holland Landing West Elevated Tank | 2026-01-30
WEST | January | On-site for station check and collection of weekly bacT samples Reviewed scada and trends, not duty active, Verified chlorine analyzers readings Visual inspection on instrumentation and equipment AOK Upon arrival duty was not active, tower at 62% and draining at 68 s/l Chemical pumps: Chlorine: Hypo pump #2 in duty1 and running at 36% speed Dose scada: 68.62 mL/min Hypo system pressure:440 Kpa Ammonia: Pump2 in duty1 running 19% speed Dosing 23.05 mL/min P1 MAX flow = 125 mL/min P2 MAX flow = 120 mL/min Pump discharge pressure: 320 Chlorine grabs: @ 1300 hrs Tank Grabs: Analyzer reading TCL = 2.52 mg/l TCL = mg/l FCL = 0.03 mg/l FCL = mg/l Mono = 0.67 mg/l TA = 0.30 mg/l FA = 0.20 mg/l Nitrite = 0.003 mg/=y Nitrate = 0.059 Did grabs on Pre. Pre Grabs: @ 1222 hrs: Analyzer TCL = 0.96 TCL = 1.00 mg/l FCL = 0.04 FCL = 0.02 mg/l Mono = 0.17 mg/l TA = 0.23 mg/l FA = 0.27 mg/l Post/ Treated Sample Grab @ 1240 hrs Mono = 2.58 mg/l TA = 0.54 mg/l FA = 0.03 mg/l FCL = 0.06 mg/l Analyzer: FCL = 0.02 mg/l TCL = 3.24 mg/l TCL = 3.20 mg/l | Holland Landing West Elevated Tank | 2026-01-28
WEST | January | On-site for station check Reviewed scada and trends, not duty active, Verified chlorine analyzers readings Visual inspection on instrumentation and equipment AOK Upon arrival duty was not active, tower at 39% and draining at 27 s/l Chemical pumps: Chlorine: Hypo pump #2 in duty1 and running at 30% speed Dose scada: 57.13 mL/min Hypo system pressure:440 kpa Ammonia: Pump2 in duty1 running 14% speed Dosing 17.00 mL/min P1 MAX flow = 125 mL/min P2 MAX flow = 120 mL/min Pump discharge pressure: 320 Chlorine grabs: @ 1039 hrs Tank Grabs: Analyzer reading TCL = 2.48 mg/l TCL = 2.50 mg/l FCL = 0.04 mg/l FCL = 0.03mg/l Mono = 0.37 TA = 0.15 mg/l FA = 0.22 mg/l Nitrite = 0.003 mg/l Nitrate = 0.086 mg/l (tower in deep cycle @ 39% and draining) 1125 hrs: Activated duty at the wells for pre and post grabs: Did grabs on Pre. Pre Grabs: @ 1221 hrs: Analyzer TCL = 1.34 mg/l TCL = 1.38 mg/l FCL = 0.04 mg/l FCL = 0.04 mg/l Mono = 0.29 mg/l TA = 0.23 mg/l FA = 0.17 mg/l Post/ Treated Sample Grab @ 1836 hrs Mono = 2.65 mg/l TA = 0.55 mg/l FA = 0.03 mg/l FCL = 0.04 mg/l Analyzer: FCL = 0.03 mg/l TCL = 3.30 mg/l TCL = 3.35 mg/l No | Holland Landing West Elevated Tank | 2026-01-23
WEST | January | Onsite to troubleshoot lo ammonia in the system. Upon arrival duty was active, tower at 78% Chemical pumps: Chlorine: Hypo pump #2 duty1 Speed: 36% Dose scada: 63.82 mL/min Hypo system pressure: Ammonia: Pump1 in duty2 running 8 % speed Dosing 10.11 mL/min P1 MAX flow = 125 mL/min P2 MAX flow = 120 mL/min Pump discharge pressure: Did grabs on Pre. Pre Grabs: @ 1320 hrs: Analyzer TCL = 1.34 TCL = 1.38 mg/l FCL = 0.08 FCL = 0.02 mg/l Mono = 0.39 mg/l TA = 0.22 mg/l FA = 0.15 mg/l Post grabs @ 1336 hrs Analyzer reading TCL = 3.44 mg/l TCL : 3.34 mg/l FCL = 0.07 mg/l FCL : 0.03 mg/l Mono = 2.12 mg/l TA = 0.41 mg/l FA = 0.00 mg/l 1404 hrs: Made adjustment to inlet free ammonia (FA) setpoint from 0.30 mL/min down to 0.15 mL/min to combat lo ammonia in the system. Collected grab after 3 mins. Mono = 2.58 mg/l TA = 0.62 FA = 0.11 1427 hrs ~ Adjusted inlet free ammonia again, from 0.15 back up to 0.25 mL/min Mono = 2.32 mg/l TA = 0.50 mg/l FA = 0.05 mg/l FCL = 0.05 mg/l Analyzer: FCL = 0.03 mg/l TCL = 2.30 mg/l TCL = 2.34 mg/l Deactivated duty recorded readings into PWQ data sheet No issues | Holland Landing West Elevated Tank | 2026-01-22
WEST | January | On-site for station check and collection of weekly bacT samples Reviewed scada and trends, not duty active, Verified chlorine analyzers readings Visual inspection on instrumentation and equipment AOK Chemical pumps: Chlorine: Hypo pump #1 duty1 Hypo dose scada Hypo system pressure: Ammonia: Pump1 in duty2 off at 0 % speed Dosing 53.76 mL/min P1 MAX flow = 125 mL/min P2 MAX flow = 120 mL/min Pump discharge pressure: Chlorine grabs: @ 1346 hrs Tank Grabs: Analyzer reading TCL = 1.99 mg/l TCL = FCL = 0.04 mg/l FCL = mg/l Mono = 0.50 mg/l TA = 0.26 mg/l FA = 0.17 mg/l Nitrite = 0,007 mg/l Nitrate = 0.044 mg/l Pre Grabs: @ hrs: Analyzer TCL = 1.25 TCL = 1.30 mg/l FCL = 0.05 FCL = 0.02 mg/l Mono = 0.47 mg/l TA = 0.17 mg/l FA = 0.07 mg/l Post grabs @ 1146 hrs Analyzer reading TCL : 3.38 mg/l TCL : 3.41 mg/l FCL : 0.05 mg/l FCL : 0.03 mg/l Mono = 2.22 mg/l TA = 0.40 FA = 0.00 | Holland Landing West Elevated Tank | 2026-01-21
WEST | January | On site for station check and collection quarterly samples Reviewed SCADA and trend, duty not active, ET @ 60% Visual inspection in and around station Verification of equipment and instrumentation. Verified chlorine analyzers readings. Recorded station readings into pwq data sheet Activated duty for station check and SL1000 Outstanding alarm: none1 Grabs: Tank Residual: Grab Time (HR). Analyzer FCL. 0.02mg/l 1220 hrs 0.03mg/l TCL. 2,54mg/l 2.11mg/l Mono. 0.39 mg/l Total Amm. 0.26 mg/l Free Amm. 0.18mg/l Nit 0.001mg/l Temp. 6.2 C 1257 hrs: Activated duty for SL1000 grabs on pre and post Grab: Pre @ 1420 hrs FCL. 0.03 mg/l 0.04mg/l TCL. 1.74mg/l 1.81 mg/l Mono. 0.30 mg/l Total Amm. 0.30 mg/l Free Amm. 0.24 mg/l Grab: Post Analyzer reading FCL. 0.02mg/l 0.02 mg/l TCL 2.82 mg/l 2.78 mg/l Mono. 0.38 mg/l Total Amm. 0.20 mg/l Free Amm. 0.12 mg/l Nitrite 0.001 mg/l Nitrate 0.038 mg/l Chemical System: Hypo pumps: pump1 in duty1 Pump1 speed ~ 14% Pump dosage ~ 25.79 mL/min Ammonia Pumps: Pump2 in duty Pump2 speed ~ 1% 0.00 mL/min | Holland Landing West Elevated Tank | 2026-01-19
WEST | January | Onsite for SL1000 grab for on tank, Tower level at 79% and draining. duty off Chlorine grabs: @ 0815 hrs Tank Grabs: Analyzer reading TCL = 2.80 mg/l TCL = mg/l FCL = 0.05 mg/l FCL = mg/l Mono = 0.54 mg/l TA = 0.28 mg/l FA = 0.18 mg/l Nitrite = 0.002 mg/l Nitrate = 0.049 mg/l | Holland Landing West Elevated Tank | 2026-01-30
WEST | January | onsite to respond to post injection combine chlorine lo alarm Upon arrival, found post injection chlorine analyzer total reading at 2.56 mg/l, FCL at 0.04 mg/l 1050 hrs: Collected grabs on analyzer~ TCL = 2.94 mg/l, FCL = 0.05 mg/l Analyzer = 2.59 mg/l 1057 hrs: Collected grabs on analyzer ~ TCL = 3.10 mg/l Analyzer = 2.56 mg/l 1103 hrs: Collected grabs on analyzer ~ TCL = 3.08 mg/l Analyzer ~ 2.54 mg/l 1107 hrs: Adjusted post injection analyzer total reading from 2.54 mg/l to 3.08 mg/l based on average of 3 grabs. Completed the following WOs while on site: - Ammonia system inspection - JHSC Health and safety inspection - Hi/Lo water level alarm test - Heat trace sensing line inspection - Low temp alarm test - Hypo system inspection - Depolox 5 chlorine analyzer maintenance - Sump pit system inspection Notified ROC before starting WOs verified chlorine analyzers readings after maintenance, no adjustment required Hypo pump2 leaking from suction of side of dice bloc, notified TL, will be taken care tomorrow as parts are needed hypo pump2 leak caused post total chlorine analyzer to drop a little and recovered quickly no issues on site, notified ROC before leaving site | Holland Landing West Elevated Tank | 2026-01-15
WEST | January | -On-site to complete station check -system duty not active, tower = 69 % 10:37 - Grabs from tank: Free Chlorine = 0.05 mg/L Total Chlorine = 1.67 mg/L MCL = 0.43 mg/L TNH3 = 0.27 mg/L FNH3 = 0.19 mg/L NO2 = 0.002 mg/L temp = 6.1 -activated system duty for station check -checked equipment -reviewed trends -depolox reagents ok -rechlor active, reform only -repaired fitting on hypo pump #2, completed drawdown - max flow = 177 ml/min -verified chlorine analyzers: 11:17 -Pre injection Analyzer readings: Free Chlorine = 0.05 mg/L Total Chlorine = 1.97 mg/L 11:17 -Pre injection Grabs: Free Chlorine = 0.03 mg/L Total Chlorine = 1.93 mg/L MCL = 0.36 mg/L TNH3 = 0.25 mg/L FNH3 = 0.18 mg/L -decreased inlet free ammonia setpoint 0.30 to 0.20 to activate boost mode for station check -hypo pump #2 running at 16%, 34 strokes/min, 60 psi -ammonia pump # 1 running at 6%, 12 strokes/min, 55 psi 11:30 -Post injection Analyzer readings: Free Chlorine = 0.04 mg/L Total Chlorine = 3.05 mg/L 11:30 -Post injection Grabs: Free Chlorine = 0.05 mg/L Total Chlorine = 2.98 mg/L MCL = 1.67 mg/L TNH3 = 0.43 mg/L FNH3 = 0.11 mg/L -increased ammonia pump #1 max flow setpoint from 120 to 125 ml/min 12:10 -collected post injection grab: MCL = 2.15 mg/L TNH3 = 0.49 mg/L FNH3 = 0.07 mg/L -returned inlet free ammonia setpoint to 0.30 mg/L -recorded readings in PWQ sheet -no other issues found | Holland Landing West Elevated Tank | 2026-01-16
WEST | January | On site for station check and collection quarterly samples Reviewed scada and trend, duty not active, ET @ 49% Visual inspection in and around station Verification of equipment and instrumentation. Verified chlorine analyzers readings. Recorded station readings into pwq data sheet Activated duty for station check and SL1000 Outstanding alarm: none1 Grabs: Pre Residual: Grab Time (HR). Analyzer FCL. mg/l hrs mg/l TCL. mg/l mg/l Mono. mg/l Total Amm. mg/l Free Amm. mg/l Grab: Post FCL. mg/l hrs mg/l TCL. mg/l mg/l Mono. mg/l Total Amm. mg/l Free Amm. mg/l Grab Tank: FCL. 0.02mg/l 0819 hrs. TCL 2.39 mg/l Mono. 0.38 mg/l Total Amm. 0.20 mg/l Free Amm. 0.12 mg/l Nitrite 0.001 mg/l Nitrate 0.038 mg/l | Holland Landing West Elevated Tank | 2026-01-14
WEST | January | On site for station check and collection of NDMA and bacT sample Reviewed scada, trends OK, ET @ 85% and filling @ 43 l/s Visual inspection in and around station Verification of equipment and instrumentation. Verified chlorine analyzers readings. Recorded station readings into pwq data sheet Outstanding alarm: none Grabs: Pre Residual: Grab Time (HR). Analyzer FCL. 0.05 mg/l 0812 hrs 0.02 mg/l TCL. 1.08 mg/l 1.07 mg/l Mono. 0.32 mg/l Total Amm. 0.39 mg/l Free Amm. 0.33 mg/l Nitrite 0.006 mg/l Grab: Post FCL. 0.05 mg/l 0822 hrs 0.03 mg/l TCL. 3.42 mg/l 3.33 mg/l Mono. 2.51 mg/l Total Amm. 0.35 mg/l Free Amm. 0.09 mg/l Nitrite 0.001 mg/l Grab Tank: FCL. 0.03. 0842 hrs. TCL 1.85 Mono. 0.62 mg/l Total Amm. 0.39 mg/l Free Amm. 0.26 mg/l Nitrite 0.003 mg/l 1244 hrs: returned to site to site to collect bacT samples. Tower in drain cycle @ 18 l/s FCL= 0.05 mg/l. Analyzer = FCL:0.04 mg/l TCL = 2.43 mg/l. TCL: 2.44 mg/l | Holland Landing West Elevated Tank | 2026-01-07
WEST | January | On site responding to high post total chlorine alarm. Took grabs on analyzer total grab 3.02mg/L analyzer reading 3.71mg/L Adjusted post treated analyzer from 3.71-3.02mg/L after multiple grabs | Holland Landing West Elevated Tank | 2026-01-14
WEST | January | On site for station check Reviewed scada and trend, duty not active, ET @ 51% Visual inspection in and around station Verification of equipment and instrumentation. Verified chlorine analyzers readings. Recorded station readings into pwq data sheet Activated duty for station check and SL1000 readings ~ Dave Outstanding alarm: none1 Grabs: Pre Residual: Grab Time (HR). Analyzer FCL. 0.03 mg/l 1100 hrs 0.04 mg/l TCL. 1.63 mg/l 1.57 mg/l Mono. 0.35 mg/l Total Amm. 0.31 mg/l Free Amm. 0.25 mg/l Grab: Post FCL. 0.04 mg/l 1123 hrs 0.03 mg/l TCL. 2.98 mg/l 2.96 mg/l Mono. 2.21 mg/l Total Amm. 0.49 mg/l Free Amm. 0.06 mg/l Grab Tank: FCL. 0.03 mg/l 11401 hrs. TCL 2.05 mg/l Mono. 0.45 mg/l Total Amm. 0.35 mg/l Free Amm. 0.27 mg/l Nitrite 0.003 mg/l | Holland Landing West Elevated Tank | 2026-01-09
WEST | January | -On-site to complete station check -system duty active, tower = 62 % -checked equipment -reviewed trends -depolox reagents ok -rechlor active, reform and boost -hypo pump #2 running at 33%, 64 strokes/min, 58 psi -ammonia pump # 1 running at 15%, 34 strokes/min, 55 psi -verified chlorine analyzers: 11:29 -Pre injection Analyzer readings: Free Chlorine = 0.02 mg/L Total Chlorine = 0.89 mg/L 11:29 -Pre injection Grabs: Free Chlorine = 0.03 mg/L Total Chlorine = 0.92 mg/L MCL = 0.18 mg/L TNH3 = 0.32 mg/L FNH3 = 0.28 mg/L 12:06 -Post injection Analyzer readings: Free Chlorine = 0.03 mg/L Total Chlorine = 3.22 mg/L 12:06 -Post injection Grabs: Free Chlorine = 0.07 mg/L Total Chlorine = 3.40/3.34/3.38 mg/L MCL = 2.61 mg/L TNH3 = 0.56 mg/L FNH3 = 0.04 mg/L 12:10 - adjusted post injection total chlorine analyzer to 3.37 mg/L based on average of 3 grabs 12:17 -Grabs from tank: Free Chlorine = 0.09 mg/L Total Chlorine = 1.88 mg/L MCL = 0.59 mg/L TNH3 = 0.34 mg/L FNH3 = 0.23 mg/L NO2 = 0.003 mg/L -recorded readings in PWQ sheet -no issues found | Holland Landing West Elevated Tank | 2026-01-13
WEST | January | -On-site to complete station check -filled ammonia tank 163 to 308 L -activated system duty, tower = 48 % -checked equipment -reviewed trends -replaced pre injection KI reagent -rechlor active, reform only -verified chlorine analyzers: 09:32 -Pre injection Analyzer readings: Free Chlorine = 0.05 mg/L Total Chlorine = 2.05 mg/L 09:32 -Pre injection Grabs: Free Chlorine = 0.03 mg/L Total Chlorine = 2.01 mg/L MCL = 0.38 mg/L TNH3 = 0.24 mg/L FNH3 = 0.17 mg/L -decreased inlet free ammonia setpoint from 0.30 to 0.17 mg/L to activate boost mode for station check -hypo pump #2 running at 15%, 31 strokes/min, 58 psi -ammonia pump # 1 running at 7%, 14 strokes/min, 52 psi 09:52 -Post injection Analyzer readings: Free Chlorine = 0.04 mg/L Total Chlorine = 3.04 mg/L 09:52 -Post injection Grabs: Free Chlorine = 0.06 mg/L Total Chlorine = 2.98 mg/L MCL = 1.56 mg/L TNH3 = 0.50 mg/L FNH3 = 0.20 mg/L -increased ammonia pump #1 max flow setpoint 105 to 120 ml/min -collected post injection grab: MCL = 1.81 mg/L TNH3 = 0.41 mg/L FNH3 = 0.05 mg/L -switched to ammonia pump #2 -collected post injection grab: MCL = 1.84 mg/L TNH3 = 0.45 mg/L FNH3 = 0.08 mg/L -returned inlet free ammonia setpoint to 0.30 mg/L -recorded readings in PWQ sheet -no other issues found | Holland Landing West Elevated Tank | 2026-01-14
WEST | January | On site for station check Reviewed scada, trends OK, ET @61% and draining Visual inspection in and around station Verification of equipment and instrumentation. Verified chlorine analyzers readings. Recorded station readings into pwq data sheet Outstanding alarm: none Grabs: Pre Residual: Grab Time (HR). Analyzer FCL. 0.05 mg/l 1400 hrs 0.05 mg/l TCL. 2.11 mg/l 2.12 mg/l Grab: Post FCL. 0.04 mg/l 14010 hrs 0.10 mg/l TCL. 2.11 mg/l 2.22 mg/l Adjusted post free chlorine analyzer reading based on average of 3 grabs. | Holland Landing West Elevated Tank | 2026-01-05
WEST | January | -on site to repair hypo injection point leak -replaced fitting on injection lance -repaired leaking suction and discharge fittings on hypo pump #1 -activated system duty and primed hypo line while tower filling -no further issues | Holland Landing West Elevated Tank | 2026-01-06
WEST | January | Received hypo delivery, filled tank 226 L to 524 L | Holland Landing West Elevated Tank | 2026-01-06
WEST | January | On site for station check. Check trends: all okay. Activated Duty. Tower filling (85%) Verified Analyzers 10:10-Pre injection FCL- Grab- 0.03 mg/L; Analyzer - 0.05 mg/L TCL- Grab-1.96 mg/L; Analyzer - 2.00 mg/L 10:40-Post injection FCL- Grab- 0.04 mg/L; Analyzer - 0.09 mg/L TCL- Grab-3.08 mg/L; Analyzer - 3.13 mg/L 10:40-SL1000 grabs Mono-1.86 mg/L FNH3-0.12 mg/L TNH3-0.48 mg/L Adjusted Ammonia pump max flow from 105ml/min to 110 ml/min 11:15-SL1000 grabs Mono-1.76 mg/L FNH3-0.20 mg/L TNH3-0.55 mg/L Adjusted Ammonia pump max flow from 110ml/min to 120 ml/min 11:40-SL1000 grabs Mono-2.00 mg/L FNH3-0.20 mg/L TNH3-0.60 mg/L Adjusted Ammonia pump max flow from 120ml/min to 105 ml/min 11:55-SL1000 grabs Mono-1.99 mg/L FNH3-0.20 mg/L TNH3-0.59 mg/L 12:15-SL1000 grabs Mono-0.19 mg/L FNH3-0.39 mg/L TNH3-0.43 mg/L Adjusted inlet free ammonia set point from 0.27 to 0.30 mg/L will verify the dosing later. Reagents all good. entered values in PWQ sheet Equipment okay. | Holland Landing West Elevated Tank | 2026-01-02
WEST | January | -on site for station check -checked trends: all ok -entered readings in PWQ: all ok -took chlorine grab 08:55 -free cl: 0.07mg/l -total cl: 1.94mg/l -heating all ok | Jefferson Pumping Station & Reservoir | 2026-01-23
WEST | January | -on site to complete station check -checked trends: all ok -entered readings in PWQ: all ok -took chlorine grab 13:10 -free cl: 0.04mg/l -total cl: 1.91mg/l -check oil in diesel - the oil is past the full mark - informed Team Lead -equipment all ok | Jefferson Pumping Station & Reservoir | 2026-01-16
WEST | January | -on site for station check and weekly bacti W11550963 -checked trends: all ok -entered reading in PWQ: all ok -took sample and chlorine grab from east cell 13:55 -free cl: 0.02mg/l -total cl: 1.95mg/l -west cell chlorine grab 14:00 -free cl: 0.04mg/l -total cl:1.92mg/l -equipment all ok | Jefferson Pumping Station & Reservoir | 2026-01-28
WEST | January | -on site for station check and weekly bacti W11538514 -checked trends: all ok -entered reading in PWQ: all ok -took chlorine grab and sample from west 14:00 -free cl: 0.08mg/l -total cl: 1.81mg/l -east cell grab 14:05 -free cl: 0.08mg/l -total cl: 1.87mg/l -equipment all ok | Jefferson Pumping Station & Reservoir | 2026-01-21
WEST | January | -on site for station check -checked trends: all ok -took reading in PWQ: all ok -took chlorine grab 14:35 -free cl: 0.09mg/l -total cl: 1.92mg/l -equipment all ok | Jefferson Pumping Station & Reservoir | 2026-01-26
WEST | January | -on site to run diesel generator -diesel start: 652.0 -diesel stop: 653.0 -diesel level -6263l -all ok | Jefferson Pumping Station & Reservoir | 2026-01-27
WEST | January | -on site to complete station check -checked trends: all ok -entered readings in PWQ: all ok -took chlorine grab 09:45 -free cl: 0.05mg/l -total cl: 1.92mg/l -equipment all ok | Jefferson Pumping Station & Reservoir | 2026-01-30
WEST | January | -on site responding pump 4 fault -reset pump 4 multilin -man/started pump to test - all ok -placed in auto | Jefferson Pumping Station & Reservoir | 2026-01-15
WEST | January | -on site to complete station check -checked trends: all ok -entered readings in PWQ: all ok -took chlorine grab 14:45: -free cl:0.06mg/l -total cl: 1.89mg/l -equipment all ok | Jefferson Pumping Station & Reservoir | 2026-01-19
WEST | January | Check coolant level and check engine oil on diesel Engine oil 1 inch high on the dipstick. Check coolant levels- ok | Jefferson Pumping Station & Reservoir | 2026-01-14
WEST | January | -on site to complete work orders -informed ROC of work Pumping Station: -completed Sump Pit System Inspection -completed JHSC Health and Safety Inspection -completed Low Temperature Alarm Test -completed Ventilation System Inspection -completed Check Valve Service & Inspection -completed Dehumidifier Inspection & Cleaning -completed Actuated Valves Exercise & Inspection -completed Pump & Motor Inspection -during generator test run pre-inspection found oil level high. Informed CMS and will wait until oil level is corrected to run generator Reservoir: -completed Ventilation System Inspection -completed Dehumidifier Inspection & Cleaning -completed Sump Pit System Inspection -completed External Venting Screens Inspection -completed JHSC Health and Safety Inspection Valve House: -completed JHSC Health and Safety Inspection -completed Sump Pit System Inspection -completed Dehumidifier Inspection & Cleaning -completed Flood Alarm Test -completed reservoir station check and collected sample -reservoir level =72 %, filling -checked equipment -reviewed trends -collected grab samples: 13:57 - East Cell: Free Chlorine = 0.03 mg/L Total Chlorine = 1.87 mg/L 14:10 - West Cell: Free Chlorine = 0.04 mg/L Total Chlorine = 1.87 mg/L MCL = 1.72mg/L TNH3 = 0.39 mg/L FNH3 = 0.05 mg/L NO2 = 0.000 mg/L temp = 7.0 14:13 - collected weekly regulatory micro. sample from West Cell - W/O # W11503497 -collected operational ATP and phosphorus samples -recorded readings in PWQ sheet -no issues found | Jefferson Pumping Station & Reservoir | 2026-01-07
WEST | January | -on site for PS station check -checked trends: all ok -entered reading in PWQ : all ok -took chlorine grab 10:25 -free cl: 0.07mg/l -total cl: 1.73mg/l -equipment all ok | Jefferson Pumping Station & Reservoir | 2026-01-08
WEST | January | -On-site to complete reservoir station check and collect samples -reservoir level = 66%, filling -checked equipment -reviewed trends -collected grab samples: 12:53 - West Cell: Free Chlorine = 0.03 mg/L Total Chlorine = 1.87 mg/L 12:57 - East Cell: Free Chlorine = 0.02 mg/L Total Chlorine = 1.88 mg/L MCL = 1.71 mg/L TNH3 = 0.39 mg/L FNH3 = 0.05 mg/L NO2 = 0.000 mg/L temp = 7.4 13:00 - collected weekly regulatory micro. sample from East Cell - W/O # W11522897 -collected quarter #1 samples - W/O # W11476218 -recorded readings in PWQ sheet -no issues found | Jefferson Pumping Station & Reservoir | 2026-01-14
WEST | January | -previous on site entry did not save -remote entry for work done 13:45 - 14:15 -on site for station grab -enter readings in PWQ: all ok -took chlorine grab 13:50 -free cl: 0.05mg/l -total cl: 2.00mg/l -equipment all ok | Jefferson Pumping Station & Reservoir | 2026-01-12
WEST | January | On site to complete pumping station check. Free Chlorine Grab: 0.05mg/L Total Chlorine Grab: 1.73mg/L No issues on site | Jefferson Pumping Station & Reservoir | 2026-01-02
WEST | January | -on site for station check -checked trends: all ok -entered reading in PWQ: -took chlorine grab 14:30 -free cl: 0.08mg/l -total cl: 1.75mg/l -equipment all ok | Jefferson Pumping Station & Reservoir | 2026-01-05
WEST | January | Vibration and greasing Took vibration readings all 4 pumps Removed plugs in pump outbound bearings and pumped all old grease out of bearings filled with new grease all 4 pumps | Jefferson Pumping Station & Reservoir | 2026-01-05
WEST | January | Onsite for station check Check trends: All okay Station duty not active 13:35- Grabs taken Grab free CL2- 0.03 mg/L Grab Total Cl2- 1.76 mg/L entered values in PWQ sheet Equipment okay | King City Dufferin Booster Pumping Station | 2026-01-23
WEST | January | Onsite for station check Check trends: All okay Station duty active; Pump 2 running 14:05- Grabs taken Grab free CL2- 0.03 mg/L Grab Total Cl2- 1.86 mg/L entered values in PWQ sheet Equipment okay | King City Dufferin Booster Pumping Station | 2026-01-26
WEST | January | -on site for station check -checked trends:all ok -entered reading in PWQ: -took chlorine grab 14:15 -free cl: 0.09mg/l -total cl: 1.87mg/l -equipment all ok | King City Dufferin Booster Pumping Station | 2026-01-15
WEST | January | Onsite for station check Check trends: All okay Station duty not active 14:00- Grabs taken Grab free CL2- 0.05 mg/L Grab Total Cl2- 1.76 mg/L entered values in PWQ sheet Equipment okay | King City Dufferin Booster Pumping Station | 2026-01-19
WEST | January | Onsite for station check Check trends: All okay Station duty not active 14:40- Grabs taken Grab free CL2- 0.06 mg/L Grab Total Cl2- 1.77 mg/L entered values in PWQ sheet Equipment okay | King City Dufferin Booster Pumping Station | 2026-01-09
WEST | January | Onsite for station check Check trends: All okay Station duty active 13:00- Grabs taken Grab free CL2- 0.04 mg/L Grab Total Cl2- 1.71 mg/L entered values in PWQ sheet Equipment okay | King City Dufferin Booster Pumping Station | 2026-01-12
WEST | January | on site for the scheduled PM Work orders. informed ROC about the works being done. W11535241 KCPSDS, JHSC Health and Safety Inspection W11535271 KCPSDS, VFD Air Filter Change W11535276 KCPSDS, Pump & Motor Inspection W11535318 KCPSDS, Critical Air Valve Flush and Inspection W11535567 KCPSDS, Hoist System Inspection | King City Dufferin Booster Pumping Station | 2026-01-06
WEST | January | -on site to complete station check -system duty not active -checked equipment -reviewed trends -recorded readings in PWQ sheet -checked residuals: 08:58 - Grabs: Free Chlorine = 0.00 mg/L Total Chlorine = 1.80 mg/L -no issues found | King City Dufferin Booster Pumping Station | 2026-01-02
WEST | January | Onsite for station check Check trends: All okay Station duty not active 09:19- Grabs taken Grab free CL2- 0.02 mg/L Grab Total Cl2- 1.98 mg/L entered values in PWQ sheet Equipment okay | King City Dufferin Booster Pumping Station | 2026-01-05
WEST | January | -on site to respond to meter chamber flood alarm -when arrived on site found water line in storage room had broken causing chamber to flood -isolated broken water line and ran chamber sump pump in hand to pump out chamber | King City Dufferin Elevated Tank | 2026-01-30
WEST | January | -on site to collect weekly bacti W11538336 and station check -checked trends: all ok -entered reading in PWQ -verified analyzer 10:25 -analyzer free: 0.02mg/l grab: 0.03mg/l -analyzer total: 1.78mg/l grab: 1.75mg/l -reagents all ok -equipment all ok | King City Dufferin Elevated Tank | 2026-01-21
WEST | January | -on site to collect weekly bacti W11550949 and station check -checked trends: all ok - Tower draining- 44% -verified analyzer 13:45 -analyzer free: 0.02mg/l grab: 0.02mg/l -analyzer total: 1.70mg/l grab: 1.75mg/l -reagents all ok -entered reading in PWQ -equipment all ok | King City Dufferin Elevated Tank | 2026-01-28
WEST | January | -on site to collect weekly bacti W11503319 and station check -checked trends: all ok -entered reading in PWQ -verified analyzer 14:20 -analyzer free: 0.03mg/l grab: 0.05mg/l -analyzer total: 1.77mg/l grab: 1.74mg/l -reagents all ok -equipment all ok | King City Dufferin Elevated Tank | 2026-01-07
WEST | January | Check leak on altitude valve Repair leak replace o rings Back in operation | King City Dufferin Elevated Tank | 2026-01-07
WEST | January | On site for the scheduled PM Work orders listed below. informed ROC about the works being done. W11486111 KCETDS, JHSC Health and Safety Inspection W11485348 KCETDS, Inlet/Outlet Heat Trace System, Inspection W11485407 KCETDS, High & Low Water Level Alarm, Test W11485447 KCETDS, Drain Valve Exercise W11485492 KCETDS, Actuated Valve, Exercise & Inspection W11486416 KCETDS, Dehumidifier, Cleaning & Inspection W11486774 KCETDS, Ventilation System, Inspection W11486925 KCETDS, Low Temperature Alarm Test W11551506 KCETDS, Dechlorination Puck Dispenser Inspection and Cleaning W11485317 KCETDS, CL17 Chlorine Analyzer, Maintenance 10:42- verified Analyzers Grab Free CL2- 0.02mg/L;Analyzer- 0.05 mg/L Grab Total CL2- 1.75 mg/L;Analyzer- 1.73 mg/L | King City Dufferin Elevated Tank | 2026-01-06
WEST | January | On site for station check, W11522883 Micro Sampling and W11476036 Q1 Water Samples-King City Storages Check Trends- All Okay Tower draining- 73% 15:10- Verified Analyzers Free Cl2 Grab - 0.09mg/L; Analyzer 0.03mg/L Total Cl2 Grab - 1.70 mg/L; Analyzer 1.67mg/L Samples collected Equipment Okay | King City Dufferin Elevated Tank | 2026-01-14
WEST | January | On site for station check, W11538336 Micro Sampling Check Trends- All Okay Tower filling- 73% 09:35- Verified Analyzers Free Cl2 Grab - 0.01mg/L; Analyzer 0.03mg/L Total Cl2 Grab - 1.78 mg/L; Analyzer 1.85mg/L Reagents all good. Samples collected Equipment Okay | King City Fisher Elevated Tank | 2026-01-21
WEST | January | Onsite for annual calibrations Informed ROC Used cal mode on scada during calibration Only Free and Total AIT maintenance and calibration Took grabs Free : G = 0.03mg/L A = 0.03mg/L No change no adjustments Total : G = 1.71mg/L A = 1.71mg/L Total is a little noisy. Will take at least 24hrs to settle down Cleared associated alarms Informed ROC Armed building and left site | King City Fisher Elevated Tank | 2026-01-27
WEST | January | Onsite for annual calibrations Informed ROC Used cal mode on scada Instrumentation calibrated: FIT, LIT, PIT, LCV (100% only) Will return for AITs Cleared associated alarms Informed ROC, armed building and left site | King City Fisher Elevated Tank | 2026-01-26
WEST | January | On site for station check, W11550949 Micro Sampling Check Trends- All Okay Tower draining- 45% 11:50- Verified Analyzers Free Cl2 Grab - 0.02mg/L; Analyzer 0.01mg/L Total Cl2 Grab - 1.68 mg/L(avg-1.67,1.68,1.69); Analyzer 1.93mg/L Adjusted Total reading to 1.68 based on grabs. Topped up KI reagent. Samples collected Equipment Okay | King City Fisher Elevated Tank | 2026-01-28
WEST | January | On site for station check, W11503319 Micro Sampling, W11476852 Q1 NDMA Water Samples, W11503755 KING WATER, Kleinburg / King City Storage - Operational Sampling (FCl/TCl, T, ATP) Check Trends- All Okay Tower filling- 76% 14:50- Verified Analyzers Free Cl2 Grab - 0.04mg/L; Analyzer 0.03mg/L Total Cl2 Grab - 1.77 mg/L; Analyzer 1.73mg/L Topped up Acetate Buffer. Samples collected Equipment Okay | King City Fisher Elevated Tank | 2026-01-07
WEST | January | On site for the following Scheduled PM work orders, Informed ROC about the works being done. W11547493 KCETFS, JHSC Health and Safety Inspection W11547347 KCETFS, PRV Valve, Inspection W11547376 KCETFS, Inlet/Outlet Heat Trace System, Inspection W11547385 KCETFS, Facility Outfall, Inspection and Cleaning W11547420 KCETFS, Manual Valve, Exercise W11547657 KCETFS, Low Temperature Alarm, Test W11547700 KCETFS, Sensing Line Heat Trace Sytem, Inspection W11547755 KCETFS, Portable Gasoline Generator, Test W11547709 KCETFS, Siemens Depolox 5/Micro 2000, Chlorine Analyzer, Maintenance 13:40- Verified Analyzers Free CL2 Grab- 0.02 mg/L,Analyzer- 0.03 mg/L Total CL2 Grab- 1.60 mg/L, Analyzer- 1.63/L | King City Fisher Elevated Tank | 2026-01-13
WEST | January | On site for station check, W11522883 Micro Sampling and W11476036 Q1 Water Samples-King City Storages Check Trends- All Okay Tower filling- 73% 14:30- Verified Analyzers Free Cl2 Grab - 0.05mg/L; Analyzer 0.03mg/L Total Cl2 Grab - 1.60 mg/L; Analyzer 1.63mg/L Samples collected Equipment Okay | King City Fisher Elevated Tank | 2026-01-14
WEST | January | On site for Station Check, W11538528 Micro Sampling Check Trends: All Okay Tower Draining (74%) 11:35- Grabs Taken FCL- 0.05 mg/L TCL- 2.09 mg/L Samples Taken. Entered Values in PWQ sheet. Equipment Okay. | Kleinburg Elevated Tank | 2026-01-21
WEST | January | -On-site to complete station check and collect sample -deactivated system duty, tower = 66% -checked equipment -reviewed trends 10:29 - collected grab sample: Free Chlorine = 0.02 mg/L Total Chlorine = 2.03 mg/L MCL = 1.99 mg/L TNH3 = 0.47 mg/L FNH3 = 0.08 mg/L NO2 = 0.000 mg/L temp = 4.5 C 10:36 - collected weekly regulatory micro. sample - W/O # W11551066 -recorded readings in PWQ sheet -no issues found | Kleinburg Elevated Tank | 2026-01-28
WEST | January | On site for Station Check, W11523000 Micro Sampling & W11476106 Q1 water samples- Kleinburg ET Check Trends: All Okay Tower Draining (72%) 11:45- Grabs Taken FCL- 0.05 mg/L TCL- 2.00 mg/L Samples Taken. Entered Values in PWQ sheet. Equipment Okay. | Kleinburg Elevated Tank | 2026-01-14
WEST | January | On site for Station Check, W11503511 Micro Sampling & W11476754 Q1 NDMA Water Samples Check Trends: All Okay Deactivated Duty Tower Draining (68%) 12:35- Grabs Taken FCL- 0.06 mg/L TCL- 2.00 mg/L Samples Taken. Duty Activated Entered Values in PWQ sheet. Equipment Okay. | Kleinburg Elevated Tank | 2026-01-07
WEST | January | -on site to complete work orders -informed ROC of work -completed Inlet/Outlet Heat Trace System, Inspection -found outlet heat trace has low temp alarm active, informed CMS to investigate -completed Manual Valve, Exercise -completed Low Temperature Alarm, Test -completed Dehumidifier, Cleaning & Inspection -completed Gasoline Generator, Test Run -ran generator and transferred network power to generator -no issues -filled generator fuel -completed JHSC Health and Safety Inspection -site back to normal operation | Kleinburg Elevated Tank | 2026-01-15
WEST | January | On site for station check Check trends: All okay Ran pump 1 & 2 locally for 15 minutes 10:55- Verified Analyzers Grab free Cl2- 0.03 mg/L Analyzer free Cl2- 0.07 mg/L Grab Total Cl2- 2.03 mg/L Analyzer Total Cl2- 2.01 mg/L Reagents All good entered values into PWQ sheet Equipment okay. | Kleinburg Whisper Lane Booster Pumping Station | 2026-01-26
WEST | January | On site for station check Check trends: All okay Ran pump 1 & 2 locally for 10 minutes 10:45- Verified Analyzers Grab free Cl2- 0.05 mg/L Analyzer free Cl2- 0.10 mg/L Grab Total Cl2- 1.77 mg/L Analyzer Total Cl2- 1.70 mg/L Reagents All good entered values into PWQ sheet Equipment okay. | Kleinburg Whisper Lane Booster Pumping Station | 2026-01-30
WEST | January | On site for station check Check trends: All okay Ran pump 1 & 2 locally 10:05- Verified Analyzers Grab free Cl2- 0.04 mg/L Analyzer free Cl2- 0.06 mg/L Grab Total Cl2- 2.09 mg/L Analyzer Total Cl2- 2.01 mg/L Reagents All good entered values into PWQ sheet Put pump 1 & 2 back to local off. Equipment okay. | Kleinburg Whisper Lane Booster Pumping Station | 2026-01-23
WEST | January | On site for station check Check trends: All okay Ran pump 2 locally 10:40- Verified Analyzers Grab free Cl2- 0.03 mg/L Analyzer free Cl2- 0.06 mg/L Grab Total Cl2- 1.95 mg/L Analyzer Total Cl2- 1.90 mg/L Reagents All good entered values into PWQ sheet Put pump 2 back to local off. Equipment okay | Kleinburg Whisper Lane Booster Pumping Station | 2026-01-19
WEST | January | Onsite for the following PM Work orders. Informed ROC about the works being done. W11486788- High/Low temp Alarm test W11486801 - Flood Alarm test W11486811- PRV inspection W11486900- pump and motor inspection W11486985- Siemens Depolox 5/Micro 2000, Chlorine Analyzer, Maintenance 13:25- Verified Analyzer Free cl2 Grab- 0.02 mg/L, Analyzer - 0.04 mg/L Total Cl2 Grab- 2.01 mg/L, Analyzer - 2.02 mg/L W11487008 Manual Valve exercise W11487618 Hoist System inspection | Kleinburg Whisper Lane Booster Pumping Station | 2026-01-08
WEST | January | On site for station check Check trends: All okay Ran pump 2 locally 10:55- Verified Analyzers Grab free Cl2- 0.02 mg/L Analyzer free Cl2- 0.06 mg/L Grab Total Cl2- 1.95 mg/L Analyzer Total Cl2- 1.89 mg/L Reagents All good entered values into PWQ sheet Put pump 2 back to local off. Equipment okay. | Kleinburg Whisper Lane Booster Pumping Station | 2026-01-12
WEST | January | On site for station check Check trends: All okay Ran pump 1 locally 10:55- Verified Analyzers Grab free Cl2- 0.03 mg/L Analyzer free Cl2- 0.04 mg/L Grab Total Cl2- 1.94 mg/L Analyzer Total Cl2- 1.89 mg/L Reagents All good entered values into PWQ sheet Put pump 1 back to local off. Equipment okay. | Kleinburg Whisper Lane Booster Pumping Station | 2026-01-09
WEST | January | On site for station check Check trends: All okay Station Duty not active. 11:30- Verified Analyzers Grab free Cl2- 0.02 mg/L Analyzer free Cl2- 0.04 mg/L Grab Total Cl2- 1.92 mg/L Analyzer Total Cl2- 1.93 mg/L Reagents All good entered values in to PWQ sheet Equipment okay. | Kleinburg Whisper Lane Booster Pumping Station | 2026-01-05
WEST | January | Station Check (no issues found) Input data to PWQ 13:40 Verified Depolox (mg/l) Free: Grab 0.04, A -0.01 (zero calibration performed) Total: Grab 1.95, A 1.96 Acetate top up | Kleinburg Whisper Lane Booster Pumping Station | 2026-01-02
W-MAINT | January | Details: Totalizer: 486218m3 Discharge pressure: 30.65 Kpa Flow Rate: 11.1 L/s Monitoring well: 219.2 masl Well 8 RPM: 2450 AMP: 5.5 %: 42 Level: 207.9 masl Well 13 RPM: 2112 AMP: 4.9 %: 21 Level: 205.7 masl | Major MacKenzie and Newkirk Road Dewatering Wells | 2026-01-22
W-MAINT | January | Station check Flow 11.1L/s 30.7 ops Well pump 13 205.7 mask Well pump 8 207.9 mask Flow totals Jan 28 555L/s Well pump hrs today Well 8 - 14 Total 34,922 Well 13 - 14 Total 34,248 | Major MacKenzie and Newkirk Road Dewatering Wells | 2026-01-28
W-MAINT | January | Totalizer: 485546m3 Discharge pressure: 30.73 Kpa Flow Rate: 11.2 L/s Monitoring well: 219.2 masl Well 8 RPM: 2450 AMP: 5.5 %: 42 Level: 207.8 masl Well 13 RPM: 2112 AMP: 4.6 %: 21 Level: 205.7 masl Cleaned ac filters and adjusted heater temp | Major MacKenzie and Newkirk Road Dewatering Wells | 2026-01-15
W-MAINT | January | Totalizer: 484957 m3 Discharge pressure: 30.78 Kpa Flow Rate: 11.2 L/s Monitoring well: 219.2 masl Well 8 RPM: 2450 AMP: 5.5 %: 42 Level: 208.0 masl Well 13 RPM: 2111 AMP: 4.9 %: 21 Level: 205.7 masl | Major MacKenzie and Newkirk Road Dewatering Wells | 2026-01-09
WEST | January | Restarted the Operator Interface Terminal due to Windows memory issues. Notified the Remote Operations Center prior to restarting. | Maple North Reservoir | 2026-01-19
WEST | January | -on site for station check and weekly bacti W11538514 -checked trends: all ok -entered readings in PWQ: all ok -took chlorine grab and sample from West call 09:40 -free cl: 0.06mg/l -total cl: 1.69mg/l -east cell grab 09:45 -free cl: 0.05mg/l -total cl: 1.66mg/l -equipment all ok | Maple North Reservoir | 2026-01-21
WEST | January | -on site to complete following work orders -JHSC inspection: all ok -air valve flush: all ok -sump pit inspection: all ok -exterior ventilation: all ok -5 ton hoist inspection: all ok | Maple North Reservoir | 2026-01-15
WEST | January | -on site for station check, weekly bacti w11522897 and Q1 W11325832 -checked trends: all ok -entered readings in PWQ -took sample and grab from east cell 09:00 -free cl: 0.06mg/l -total cl: 1.69mg/l -west cell grab 09:05 -free cl: 0.09mg/l -total cl: 1.67mg/l -equipment all ok | Maple North Reservoir | 2026-01-14
WEST | January | -on site to for station check and collect weekly bacti W11550963 -checked trends:all ok -entered reading in PWQ: all ok -took chlorine grab and sample from east cell 09:30 -free cl: 0.10mg/l -total cl: 1.67mg/l -west cell grab 09:35 -free cl: 0.06mg/l -total cl: 1.69mg/l -equipment all ok | Maple North Reservoir | 2026-01-28
WEST | January | -on site for station check and weekly bacti W11503497 -checked trends: all ok -entered readings in PWQ: all ok -sampled west cell and chlorine grab 09:25 -free cl: 0.04mg/l -total cl: 1.69mg/l -east cell grab 09:30 -free cl: 0.01mg/l -total cl: 1.70mg/l -equipment all ok | Maple North Reservoir | 2026-01-07
WEST | January | -on site to troubleshoot PD8 pump 1 - discharge valve fail to open -placed well into local off and exercised discharge valve -pump did not start -informed Ernie H and Kyle R on site and assisted in troubleshoot -rotors not showing proper position -required full power cycle -tested pump again: all ok | Maple Pumping Station | 2026-01-20
WEST | January | -on site to complete station check -checked trend: all ok -entered readings in PWQ: all ok -verified PD7 analyzer 09:35 -analyzer free: 0.04mg/l grab: 0.06mg/l -analyzer total: 1.79mg/l grab: 1.77mg/l -verified PD8 analyzer 09:40 -analyzer free: 0.06mg/l grab: 0.06mg/l -analyzer total: 1.63mg/l grab: 1.61mg/l -equipment all ok -complete bathroom cleaning | Maple Pumping Station | 2026-01-26
WEST | January | -on site for station check -checked trends: all ok -entered readings in PWQ: all ok -verified PD7 analyzer 09:40 -analyzer free: 0.04mg/l grab:0.04mg/l -analyzer total: 1.73mg/l grab: 1.74mg/l -verified PD8 analyzer 09:45 -analyzer free: 0.05mg/l grab: 0.08mg/l -analyzer total:1.55mg/l grab: 1.57mg/l -ABB and electricians on site for PD8 MCC upgrade | Maple Pumping Station | 2026-01-19
WEST | January | On site with Ernesto Hidalgo and Phil Taylor from ABB to replace fan unit on PD8 P4 vfd. Installation complete and vfd reenergized. With assistance from operator Tim Hudson, P4 tested to ensure proper operation. ROC notified. P4 returned to normal operation. | Maple Pumping Station | 2026-01-21
WEST | January | Restarted the Local SCADA server due to Windows updates. Notified the Remote Operations Center. | Maple Pumping Station | 2026-01-22
WEST | January | -on site for station check -checked trends: all ok -entered readings in PWQ: all ok -verified PD7 analyzer 09:00 -analyzer free: 0.04mg/l grab: 0.06mg/l -analyzer total: 1.70mg/l grab/ 1.69mg/l -verified PD8 analyzer 09:05 -analyzer free: 0.06mg/l grab:0.05 -analyzer total: 1.76mg/l grab: 1.68mg/l - adjusted -equipment all ok | Maple Pumping Station | 2026-01-16
WEST | January | -on site for station check -checked trends: all ok -entered readings in PWQ: all ok -verified PD7 analyzer 13:30 -analyzer free: 0.04mg/l grab: 0.02mg/l -analyzer total: 1.87mg/l grab: 1.84mg/l -verified PD8 analyzer 13.35 -analyzer free: 0.06mg/l grab:0.08mg/l -analyzer total: 1.70ng/l grab: 1.68mg/l -equipment all ok | Maple Pumping Station | 2026-01-30
WEST | January | -on site for station check -checked trends: all ok -entered readings in PWQ: all ok -verified PD7 analyzer 12:45 -analyzer free: 0.04mg/l grab:0.08mg/l -analyzer total: 2.12mg/l grab: 2.13mg/l -verified PD8 analyzer 12:50 -analyzer free:0.05mg/l grab: 0.06mg/l -analyzer total: 1.62mg/l grab: 1.66mg/l -equipment all ok | Maple Pumping Station | 2026-01-23
WEST | January | - on site to complete following work order -sump pit inspection -changed PD8 MCC filters | Maple Pumping Station | 2026-01-22
WEST | January | -on site to complete following work orders -JHSC inspection- site is currently a construction project -analyzer verification/maintenance -PD7 verification 10:45 -analyzer free: 0.10mg/l grab: 0.04mg/l - adjusted -analyzer total: 1.93mg/l grab: 1.82 - adjusted -PD8 verification 11:00 -analyzer free: 0.05mg/l grab: 0.06mg/l -analyzer total: 1.63mg/l grab: 1.64mg/l -cell, pressure, flow all ok -ran diesel generator -start time: 481.6/495.4 -stop time: 482.7/496.5 -diesel level: 492/682 - 28635L -PD8 pumps 1,2,3 VFD faults will not reset Dan B will attend -diesel containment test: all ok -diesel transfer pumps exercised: all ok -sump pump inspection: -screen inspection: -PD8 filter replacement -PD7&PD8 air valve flush: -Dan B, Tyler Z on site to troubleshoot VFD -contact ABB support - mcc keypad had to be on local to reset alarm -placed station back to auto | Maple Pumping Station | 2026-01-13
WEST | January | On site to preform station check Checked trends, all ok Verified PD7 analyzer @ 10:05 Analyzer free 0.04 mg/l, grab 0.10 mg/l - adjusted to match grab Analyzer total 1.78 mg/l, grab 1.78 mg/l Verified PD8 analyzer @ 10:10 Analyzer free 0.01 mg/l, grab 0.05 mg/l - adjusted to match grab Analyzer total 1.57 mg/l, grab 1.53 mg/l Tried to reset air compressor fault alarm, unsuccessful but system still running, supervisor informed | Maple Pumping Station | 2026-01-12
WEST | January | -on site for station check -checked trends: all ok -took readings in PWQ: all ok -verified PD7 analyzer 09:50 -analyzer free: 0.04mg/l grab: 0.06mg/l -analyzer total: 1.77mg/l grab: 1.74mg/l -verified PD8 analyzer 09:55 -analyzer free: 0.02mg/l grab:0.04mg/l -analyzer total: 1.75mg/l grab: 1.72mg/l -equipment all ok | Maple Pumping Station | 2026-01-05
WEST | January | -on site for station check -checked trends -entered reading in PWQ: all ok -verified PD7 analyzer 08:45 -analyzer free: 0.05mg/l grab: 0.04mg/l -analyzer total: 1.74mg/l grab: 1.71mg/l -verified PD8 analyzer 09:55 -analyzer free: 0.02mg/l grab: 0.03mg/l -analyzer total: 1.82mg/l grab: 1.78mg/l -equipment all ok -contractors on site | Maple Pumping Station | 2026-01-09
WEST | January | On site to Complete Station Check. Residuals PD8 Total Grab: 1.76mg/L, Analyzer: 1.76mg/L PD8 Free Grab: 0.04mg/L, Analyzer: 0.02mg/L PD7 Total Grab: 1.68mg/L, Analyzer: 1.75mg/L PD7 Free Grab: 0.05mg/L, Analyzer: 0.04mg/L No issues on site | Maple Pumping Station | 2026-01-02
WEST | January | -on site for station check and weekly bacti W -checked trends: all ok -entered readings in PWQ: all ok -verified peel analyzer 08:30 -analyzer: 1.73mg/l grab: 1.73mg/l -took chlorine grab north cell 08:35 -free cl: 0.09mg/l -total cl: 1.73mg/l -verified metro analyzer 08:40 -analyzer free: 0.04mg/l -analyzer total: 1.76mg/l grab: 1.74mg/l -construction on going | Maple South Reservoir | 2026-01-28
WEST | January | -on site to complete station check and collect weekly bacti W11538514 -construction on going on south cell -checked trends: all ok -entered readings in PWQ: all ok -verified peel analyzer 08:45: 1.76mg/l grab:1.76mg/l -reagents all ok -took chlorine grab of north cell 08:55 -free cl: 0.01mg/l -total cl: 1.76mg/l -verified metro analyzer 09:00 -analyzer free: 0.04mg/l grab: 0.07mg/l -analyzer total: 1.83mg/l grab: 1.77mg/l - adjusted | Maple South Reservoir | 2026-01-21
WEST | January | -on site to complete following work orders -analyzer cleaning and maintenance -verified peel analyzer 11:10: 1.82mg/l grab: 1.79mg/l -reagents all ok -verified metro analyzer 11:05 -analyzer free: 0.10mg/l grab:0.04mg/l - adjusted -analyzer total: 1.78mg/l grab: 1.81mg/l -flow/pressure/sand/electrolyte all ok -sump pit inspection: all ok -dehumidifier inspected: all ok -external vent check: unable to check due to construction | Maple South Reservoir | 2026-01-15
WEST | January | -on site responding to high treated free alarm -adjusted flow -took grab at 11:05 -analyzer: 0.24mg/l grab: 0.08mg/l - adjusted | Maple South Reservoir | 2026-01-14
WEST | January | -on site for station check, weekly bacti W11522897 and Q1 W11476134 -construction on going -checked trends all ok -entered readings in PWQ -verified Peel analyzer 08:05: 1.69mg/l grab: 1.66mg/l -reagents all ok -took chlorine grab of north cell 08:10 -free cl: 0.05 mg/l -total cl: 1.64mg/l -verified metro analyzer 08:15 -analyzer free: 0.02mg/l grab: 0.03mg/l -analyzer total: 1.75mg/l grab: 1.71mg/l -equipment all ok | Maple South Reservoir | 2026-01-14
CENTRAL | January | On-site due to a call dromROC operations, Adeela. Heat Trace 1 system fault alarm. Reset and acknowledged heat trace system. Heat trace operating at 100% More flow to sample taps. Cleared alarm on OIT panel | Newmarket (East) Harry Walker Elevated Tank | 2026-01-26
WEST | January | -on site for station check and weekly bacti W11503497, NDMA sample W11476768 -checked trends -contractor on site/south cell isolated -took chlorine grab north cell 08:30 -free cl: 0.03mg/l -total cl: 1.71mg/l -verified peel analyzer 08:40: 1.72mg/l grab: 1.76mg/l -replaced reagents -verified metro analyzer 08:45 -analyzer free: 0.02mg/l grab: 0.05mg/l -analyzer total: 1.78mg/l grab: 1.82mg/l -no other issues | Maple South Reservoir | 2026-01-07
CENTRAL | January | Station and equipment check Take weekly BacT sample W11551532 and grabs @ 8:10 am Total: 2.68 mg/l Free: 0.02 mg/l Analyzer Total: 2.48 mg/l Analyzer Free: 0.01 mg/l *standardized analyzer to match grabs, reagents ok ET ops normal | Newmarket (East) Harry Walker Elevated Tank | 2026-01-28
CENTRAL | January | Onsite responding to frozen LIT Raised setpoints on all 3 heat trace units. Turned on sensing line sample tap with low flow to keep readings at heat trace thermostat closer to real water temp. Notified ROC Carter Dunn work is complete and put NMETHW back to controlling tower | Newmarket (East) Harry Walker Elevated Tank | 2026-01-24
CENTRAL | January | Station and equipment check Take weekly BacT sample W11503259 and grabs @ 8:00 am Total: 2.66 mg/l Free: 0.02 mg/l Analyzer Total: 2.67 mg/l Analyzer Free: 0.01 mg/l No adjustments required, reagents ok ET 48% and draining at 64 L/s ET ops normal | Newmarket (East) Harry Walker Elevated Tank | 2026-01-07
CENTRAL | January | Station and equipment check Take weekly samples and grabs @ 8:25 am (draining) Total: 2.48 mg/l Free: 0.02 mg/l Analyzer Total 2.49 mg/l Analyzer Free: 0.01 mg/l In-house advanced monitoring readings on PD sheets Reagents ok ET ops normal | Newmarket (East) Harry Walker Elevated Tank | 2026-01-21
CENTRAL | January | Station and equipment check Take weekly BacT sample W11523454 and grabs @ 8:40 am (draining) Total: 2.58 mg/l Free: 0.02 mg/l Analyzer Total: 2.23 mg/l Analyzer Free: 0.0 mg/l *standardized analyzer to match grabs, reagents ok ET ops normal | Newmarket (East) Harry Walker Elevated Tank | 2026-01-14
CENTRAL | January | Onsite to complete maximo workorders Informed ROC (Adam B) of ongoings and verified eye wash flow switch alarm - all ok Depolox maintenance - requires "grit" none onsite JHSC inspection complete - no issues Heat Trace inspection - all ok General housekeeping complete ET ops normal | Newmarket (East) Harry Walker Elevated Tank | 2026-01-08
CENTRAL | January | Station and equipment check Took grabs @ 1:30 pm (filling) Inlet sample tap Total: 1.72 mg/l Free: 0.05 mg/l Inlet analyzer Total: 1.69 mg/l Inlet analyzer free: 0.04 mg/l Chemicals/reagents ok Ops normal | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2026-01-19
CENTRAL | January | Onsite for station check: Verified analyzers Calculated dosages Chemical levels- Ok CL17 reagents- Ok Chemscan reagents- Ok Station/equipment- Ok | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2026-01-16
CENTRAL | January | Onsite to top up ammonia tank 2 and assist with contractor after the damaged site sanitary line. Sump pumps from sanitary chamber were turned off so no spill occurred. 15:14 roc notified me that sani pit high alarm triggered. Has vac truck pump out pit. Sani pump failed to stop alarm triggered due to emptying pit. 19:30 contractors completed sani line repair. Placed sani pumps back in service. No issues remain. | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2026-01-30
CENTRAL | January | On-site for station check 08:43 Tank 2 at 53% and filling at 94 l/s. System in chloramine reformation mode. Tank 1 offline. Topped up hypo tanks 2. Domestic water supply remains shut off due to construction activities. Topped up Chemscan distilled water. 09:10 Verified preinjection/ header residuals(mg/l): Free grab: 0.05. Analyzer: 0.03. Total grab: 2.17 CL17: 2.19 Chemscan: 2.25. Monochloramine: 1.15. Chemscan: 1.10 Free ammonia: 0.15. Chemscan 0.13. Total ammonia: 0.38. Chemscan: 0.46 09:20 Post-Injection (inlet). Corrected mislabelling post injection sample point. Free chlorine: 0.03. CL17: 0.04. Total chlorine: 2.66. CL17: 2.65. No issues on site. | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2026-01-30
CENTRAL | January | Received 355L of hypo delivery. | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2026-01-27
CENTRAL | January | Station and equipment check Took grabs @ 8:40 am (filling) Inlet sample tap (post) Total: 2.01 mg/l Free: 0.03 mg/l All other readings on PD sheets Ran chemscan unit through ?flush? Batched ammonia tank 2 Topped up hypo tank 2 Chemicals/reagents ok Contractor onsite (kingdom) for upgrades Ops normal | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2026-01-23
CENTRAL | January | Receive hypo 505 Litres Ops normal Contractor onsite ?kingdom? Ops normal | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2026-01-20
CENTRAL | January | -Performed station check - logged station readings into PWQ sheet -Checked CL17 reagents - OK -Checked ChemScan reagents - OK | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2026-01-26
CENTRAL | January | Station and equipment check Take weekly samples and grabs @ 13:00 20 l/s draining, Outlet sample tap Total: 1.73 mg/l Outlet sample tap Free: 0.02 mg/l Chemicals/reagents ok All other readings on PD sheets Contractor onsite Ops normal | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2026-01-21
CENTRAL | January | Call from TL (Ben H) Contractor hit water service, small domestic Onsite to isolate curb stop Domestic service will remain off until repair can be completed. Contractor cleaned snow, ice and water from driveway and road and spread out salt Onsite to take weekly BacT sample W11551532 and grabs from sample tap @ 13:10 Total: 1.52 mg/l Free: 0.02 mg/l All other readings on PD sheets Changed CL17 reagent ?header total? Chemicals/reagents ok Ops normal | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2026-01-28
CENTRAL | January | Station and equipment check Take weekly BacT sample W11523454 and grabs @ 10:40 am (Draining) Sample tap Total: 1.90 mg/l Free: 0.02 mg/l All other readings on PD sheets Chemicals/reagents ok | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2026-01-14
CENTRAL | January | Restarted the Operator Interface Terminal due to Windows Video driver updates. Notified the Remote Operations Center before restarting the OIT. | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2026-01-14
CENTRAL | January | Station and equipment check Header Free HIHI came in while onsite @ 11:17 am as flow direction switched from filling to draining (Free: 0.45 mg/l) Took grabs right away 11:18 am Free: 0.05 mg/l, analyzer also dropped to normal as ran through cycle, possible one off no adjustments needed Hypo p3 had a small leak on parker fitting discharge side, replaced parker fitting and tubing Topped up Ammonia tank 2 Topped up hypo tank 2 (20 L) Topped up "grey" chemscan reagent Took grabs @ 12:20 pm as system draining Header Total: 3.24 mg/l Header Free: 0.05 mg/l All other readings on PD sheets Receive 585 L of Hypo Station ops normal | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2026-01-12
CENTRAL | January | Station and equipment check Take weekly BacT sample W11503259 and grabs from Header (post) flow fluctuating 0-40 L/s leaving Total: 2.05 mg/l Free: 0.02 mg/l Changed reagent CL17 header Total Topped up hypo tanks 1 and 2 Chemicals/reagents ok All other readings on PD sheets Ops normal | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2026-01-07
CENTRAL | January | Onsite to complete monthly maximo workorders Informed ROC (Ethan U) of ongoings Cleaned ALL analyzers, placed in Cal mode during maintenance and turned off chemical system Tested Flood alarm and Temp alarms - all ok JHSC inspection complete no issues found Checked all chemical pumps and chemical boards (replaced parker fitting and tubing yesterday on Hypo) General tidy Ops normal | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2026-01-13
CENTRAL | January | Station and equipment check Took grabs @ 8:45 am (draining) Header Total: 3.20 mg/l Header Free: 0.05 mg/l All other readings on PD sheets Chemicals/reagents ok Hot water flush all sample lines, informed ROC (Adam B) Analyzers placed in cal mode during work and chemical system off Removed garbage Ops normal | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2026-01-09
CENTRAL | January | On-site for station check 11:08 Tank 2 at 61% and filling at 97 l/s. System in chloramine reformation mode. Tank 1 offline. Recieved sodium hypochlorite deliver. Topped up hypo tanks 1 and 2. 11:24. Verified preinjection/ header residuals(mg/l): Free grab: 0.03. Analyzer: 0.02. Total grab: 1.66 CL17: 1.73 Chemscan: 1.65. 11:45 notified ROC. Deactivated all chemical dosing systems and placed analyzers in calibration mode. Completed a hot flush of sampling system lines. 12:18 placed chemcal pumps and analyzers back online. 12:29. Post-Injection (inlet analyzers). Free chlorine: 0.07. CL17: 0.04. Total chlorine: 2.54. CL17: 2.57 No issues on site. | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2026-01-02
CENTRAL | January | On site to complete station check. Site secure and offline. | Newmarket (London) Yonge Street Elevated Tank | 2026-01-26
CENTRAL | January | Station and equipment check Tank 2 filling @ 104 L/s Took grabs @ 10:20 am Post (inlet) Total: 2.70 mg/l Free: 0.06 mg/l All readings on PD sheets, no adjustments to analyzers Changed CL17 reagents on Header Free and Inlet Free Batched ammonia tank 1 Ops normal | Newmarket (Glenway) Kirby Tank & Rechlorination Facility | 2026-01-05
CENTRAL | January | On site for PMs. -Completed JHSC inspection. All good | Newmarket (London) Yonge Street Elevated Tank | 2026-01-15
CENTRAL | January | On site to complete station check. All good. Site offline and secure as per usual ops. | Newmarket (London) Yonge Street Elevated Tank | 2026-01-13
CENTRAL | January | On site to complete station check. Site offline and secure. | Newmarket (London) Yonge Street Elevated Tank | 2026-01-19
CENTRAL | January | On site to complete station check. All good. Site offline and secure as per usual operations. | Newmarket (London) Yonge Street Elevated Tank | 2026-01-06
CENTRAL | January | Station and equipment check Lolo temp in analyzer room ?hut?, heater was OFF Turned back on and Lolo temp cleared Lo temp will clear when room warms up ET remains offline Ops normal | Newmarket (Northeast) Davis Drive Elevated Tank | 2026-01-19
CENTRAL | January | Station and equipment check Site OFFLINE Ops normal | Newmarket (Northeast) Davis Drive Elevated Tank | 2026-01-12
CENTRAL | January | Station and equipment check Visual inspection only as site offline All ops normal | Newmarket (Northeast) Davis Drive Elevated Tank | 2026-01-05
CENTRAL | January | Onsite to complete maximo workorders ET remains OFFLINE as per norm JHSC inspection complete - no issues General Housekeeping duties complete OPs normal | Newmarket (Northeast) Davis Drive Elevated Tank | 2026-01-06
CENTRAL | January | On site with Christian B to inspect heat trace fault alarm. Alarm acknowledged, heaters operating at 100%. | Newmarket (Southeast) Ivsbridge Elevated Tank | 2026-01-26
CENTRAL | January | Station and equipment check Take weekly samples and grabs @ 9:15 am (draining) Total: 2.70 mg/l Free: 0.04 mg/l Analyzer Total: 2.63 mg/l Analyzer Free: 0.03 mg/l In-house advanced monitoring on PD sheets Changed iodide solution for Depolox analyzer ET ops normal | Newmarket (Southeast) Ivsbridge Elevated Tank | 2026-01-21
CENTRAL | January | Station and equipment check Take weekly BacT sample W11551532 and grabs @ 8:50 am Total: 2.92 mg/l Free: 0.04 mg/l Analyzer Total: 2.76 mg/l Analyzer Free: 0.01 mg/l *standardized analyzer to match grabs, reagents ok Ops normal | Newmarket (Southeast) Ivsbridge Elevated Tank | 2026-01-28
CENTRAL | January | Station and equipment check Take weekly BacT sample and grabs @ 9:20 am (filling) Total: 3.00 mg/l Free: 0.02 mg/l Analyzer Total: 3.17 mg/l Analyzer Free: 0.03 mg/l *standardized analyzer to match grabs, reagents ok ET ops normal | Newmarket (Southeast) Ivsbridge Elevated Tank | 2026-01-14
CENTRAL | January | On site to respond to heat trace 2 fault alarm. Alarm did clear, may come back due to ongoing extreme cold weather event. Heat trace circuits 1 and 2 operating at 100%. | Newmarket (Southeast) Ivsbridge Elevated Tank | 2026-01-30
CENTRAL | January | Station and equipment check Take weekly BacT samples W11503259 and grabs @ 9:15 am (draining) Total: 2.86 mg/l Free: 0.02 mg/l Analyzer Total: 2.88 mg/l Analyzer Free: 0.02 mg/l No adjustments required, reagents ok Test ran portable generator as per workorder no issues ET ops normal | Newmarket (Southeast) Ivsbridge Elevated Tank | 2026-01-07
CENTRAL | January | Informed ROC (Christian V) Onsite to check Depolox analyzer Took grabs @ 9:30 am Total: 3.10 mg/l Free: 0.02 mg/l Cleaned analyzer in Cal mode Standardized readings to match grabs Topped up acetate buffer Will monitor ET ops normal | Newmarket (Southeast) Ivsbridge Elevated Tank | 2026-01-12
CENTRAL | January | Call from ROC (Adeela K) analyzer reading hihi Upon arrival analyzer reading over 4.00 mg/L combined, took multiple grabs @ 9:25 pm and average over 3 grabs: Total: 2.95 mg/l Free: 0.02 mg/l Analyzer faulty Air and debris in site glass and over flow tubing, slight leak at E-kcl gel reservoir Managed to slow leak and clean debris from analyzer, readings dropped immediately to normal indicating faulty instrument Will have instrumentation overhaul in morning Analyzer reading @ 9:40 pm Total: 2.95 mg/l Free: 0.02 mg/l Informed ROC of findings ET ops normal | Newmarket (Southeast) Ivsbridge Elevated Tank | 2026-01-11
CENTRAL | January | Onsite to complete maximo workorders Informed ROC (Adam B) of ongoings JHSC inspection no issues Eye wash flush and test all ok Flood alarm test no issues Heat trace system inspection all ok Flushed all sample lines and level transmitter Depolox maintenance added reagent and cleaned exterior Housekeeping complete ET ops normal | Newmarket (Southeast) Ivsbridge Elevated Tank | 2026-01-06
CENTRAL | January | Onsite to complete maximo workorders Informed ROC (Christian V) of ongoings Verified Low Tower level via scada ack/reset no issues (9:10 am) JHSC inspection complete - no issues Dechlorination puck dispenser cleaning complete Depolox 5 maintenance complete, changed potassium iodide solution General housekeeping complete | Newmarket (West) Bathurst Tank | 2026-01-22
CENTRAL | January | Station and equipment check Took samples and grabs @ 11:00 am from outlet sample tap Total: 2.77 mg/l Free: 0.06 mg/l In-house advanced monitoring on PD sheets Reagents ok Ops normal | Newmarket (West) Bathurst Tank | 2026-01-21
CENTRAL | January | Station and equipment check Take weekly BacT sample W11551532 and grabs from Outlet sample tap Total: 2.70 mg/l Free: 0.05 mg/l Reagents ok Ops normal | Newmarket (West) Bathurst Tank | 2026-01-28
CENTRAL | January | -Received phone call from ROC this morning regarding low water temp - reviewed trends, tower level was still trending and water temp was above 2.5oC - the fault alarm might cause by the extreme cold - informed ROC disregarding the alarm | Newmarket (West) Bathurst Tank | 2026-01-31
CENTRAL | January | Onsite to complete Maximo workorders No issues found Will test hil/low level alarms via scada Ops normal | Newmarket (West) Bathurst Tank | 2026-01-08
CENTRAL | January | Station and equipment check Take weekly BacT sample W11503259 and grabs @ 11:00 am from Outlet sample tap Total: 2.80 mg/l Free: 0.06 mg/l Tank filling at 40 L/s Analyzer Total: 2.99 mg/l Analyzer Free: 0.09 mg/l Analyzer grabs Total: 3.00 mg/l Analyzer grabs Free: 0.08 mg/l Topped up Depolox E-KCL/Gel, all other reagents ok no adjustments necessary Ops normal | Newmarket (West) Bathurst Tank | 2026-01-07
CENTRAL | January | Station and equipment check Take weekly BacT sample W11523454 and grabs @ 7:35 am (outlet sample tap) Total: 2.55 mg/l Free: 0.06 mg/l Analyzer Total: 2.52 mg/l Analyzer Free: 0.08 mg/l Reagents ok, no adjustments required Flow out: 120 L/s Ops normal | Newmarket (West) Bathurst Tank | 2026-01-14
CENTRAL | January | Depolox (new acetate buffer) | Newmarket (West) Bathurst Tank | 2026-01-02
CENTRAL | January | On site to complete station check. -Verified analyzers: Influent Free Chlorine @ 10:44 Grab: 2.76 mg/L Analyzer: 2.88 mg/L Effluent Free Chlorine @ 10:38 Grab: 2.86 mg/L Analyzer: 2.95 mg/L Treated Free Chlorine @ 10:27 Grab: 0.11 mg/L Analyzer: 0.15 mg/L Treated Total Chlorine @ 10:27 Grab: 3.36 mg/L Analyzer: 3.44 mg/L -Entered data into PD sheet -Checked trends | Newmarket Well No. 15 | 2026-01-16
CENTRAL | January | Attending site to check Total chlorine analyzer due to occasional zero readings (W11611614). Analyzer drops to zero, locking out well. Replaced colorimeter with similar results in erratic readings. Replaced tubing and readings appeared to become more stable. Started well and left it running in auto. ROC was notified before and after analyzer maintenance. | Newmarket Well No. 15 | 2026-01-23
CENTRAL | January | On site to complete station check, collect weekly bacti samples (W11539023), and collect Q1 samples (W11476456). -Created WO W11606529 for maintenance to address nonfunctional heater. -Verified analyzers: Influent Free Chlorine @ 8:20 Grab: 2.90 mg/L Analyzer: 2.91 mg/L Effluent Free Chlorine @ 8:13 Grab: 2.88 mg/L Analyzer: 2.85 mg/L Treated Free Chlorine @ 8:07 Grab: 0.14 mg/L Analyzer: 0.13 mg/L Treated Total Chlorine @ 8:07 Grab: 3.26 mg/L Analyzer: 3.37 mg/L -Corrected valve issue on chemical board which caused treated free hihi -Entered data into PD sheet -Checked trends | Newmarket Well No. 15 | 2026-01-21
CENTRAL | January | On-site to investigate silicate pump 1 issues. 11:10 treated total chlorine hi alarm triggered at 3.73 mg/l. 11:24 Collected grab: 3.38/3.40/3.30. mg/l. Analyzer: 3.53. Adjusted to match grabs. Cleared alarm. 11:25 placed well manual off. Pulled injection point 2 (in service point) and hot flushed using silicate p1. Cleaned checkvalves. Found PRV isolated. Opened, excercised and set 20 PSI higher the PSV. Cleaned both suction foot valves and found footvalve 1 screen fully blocked. Tested max pumprate for P1 to be 270 ml/ min. Adjusted SCADA setpoint to match. Deactivated chlroine room dehumidifier. Ran well 15 in manual to test. No issues found. 14:47 placed back in auto. | Newmarket Well No. 15 | 2026-01-22
CENTRAL | January | On site to complete station check. -Verified analyzers: Influent Free Chlorine @ 13:28 Grab: 2.98 mg/L Analyzer: 2.92 mg/L Effluent Free Chlorine @ 13:25 Grab: 0.15 mg/L Analyzer: 0.19 mg/L Treated Free Chlorine @ 13:22 Grab: 0.14 mg/L Analyzer: 0.09 mg/L Treated Total Chlorine @ 13:22 Grab: 2.80 mg/L Analyzer: 2.87 mg/L -Performed maintenance on deep well exhaust valve while well temporarily placed in manual-off. Returned well to auto once work completed -Entered data into PD sheet -Checked trends | Newmarket Well No. 15 | 2026-01-30
CENTRAL | January | Onsite for annual calibrations Informed ROC and operations Used cal mode on scada during the work Maintenance and Calibration on the chlorine analyzers only Took grabs along with operations Treated free: G= 0.15 A= 0.12 Treated Total: G= 3.08 A= 3.07 Influent free: G= 2.84 A= 2.82 Effluent free: G= 2.56 A= 2.50 No issues upon leaving. Just well house is very cold Informed operations and left site | Newmarket Well No. 15 | 2026-01-20
CENTRAL | January | Onsite for annual calibrations Informed ROC and operations Well duty placed manual off Used cal mode on scada during the work Instruments calibrated: FIT, LITs, NIT, WIT, chlorine gas detector, chlorinators (electronic only) Cleared associated alarms Will complete AITs tomorrow Informed ROC and operations Operations placed duty to auto Armed building and left site | Newmarket Well No. 15 | 2026-01-19
CENTRAL | January | On-site with D Moses for a station and equipment check Changed tube in NaSi pump 1. Cleaned foot valve screen again, primed pumps and lines. Completed draw down and confirmed max dosage setting. Topped up ammonia day tanks 2 Took operational sample Adjusted flows to treated total analyzer Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@1355 G:3.02 A:3.06mg/L Effluent Free@1359 G:0.15 A:0.15mg/L Treated Free@1402 G:0.09 A:0.08mg/L Treated Total@1406 G:2.76 A:2.83mg/L | Newmarket Well No. 15 | 2026-01-26
CENTRAL | January | Silicate load 237 L - 383 L Instrumentation on site Also heater in main room above MCC not working will create workorder Ops normal well 15 off | Newmarket Well No. 15 | 2026-01-20
CENTRAL | January | Silicate Top up: Before: 52.1cm/238.5L After: 84.4cm/384.5L | Newmarket Well No. 15 | 2026-01-28
CENTRAL | January | Brought space heater to site for pump room, manually forced pump room louvres closed as they don?t seem to automatically close (will create WO to address). Will follow up regarding pump room unit heater as it does not appear to be working properly. No other new issues found. | Newmarket Well No. 15 | 2026-01-20
CENTRAL | January | Changed chlorine cylinder bank A with Joe D. | Newmarket Well No. 15 | 2026-01-29
CENTRAL | January | On site to complete station check and collect weekly bacti samples (W11550733). -Well placed in manual-on for duration of work -Verified analyzers: Influent Free Chlorine @ 13:02 Grab: 2.76 mg/L Analyzer: 2.77 mg/L Effluent Free Chlorine @ 12:59 Grab: 2.72 mg/L Analyzer: 2.79 mg/L Treated Free Chlorine @ 12:43 Grab: 0.13 mg/L Analyzer: 0.14 mg/L Treated Total Chlorine @ 12:43 Grab: 3.32 mg/L Analyzer: 3.34 mg/L -Due to rising turbidity, placed silicate pump 2 in manual-off -Valved silicate pumps to use injection point 1, continuing to monitor turbidity. Turbidity returned to normal operating range (NTU = 0.08) -Leaving silicate pump 2 in manual-off due to lack of time for further troubleshooting, but issue likely due to injection point 2 not due to the pump based on dice block manipulation -Entered data into PD sheet -Checked trends -Returned well to auto | Newmarket Well No. 15 | 2026-01-28
CENTRAL | January | On site to complete PMs. Instrumentation on site. -Performed maintenance on and inspected ammonia system. Performed drawdowns. Pump 1 max flow rate setpoint not adjusted. Pump 2 max flow rate setpoint adjusted from 100 to 98 mL/min. -Confirmed with instrumentation that they calibrated turbidimeter (NIT analyzer) and tested the chlorine gas detector yesterday. Confirmed they have performed maintenance on and calibrated CL17 chlorine analyzers today. Took following grabs with well on to verify analyzers: Influent Free Chlorine @ 14:57 Grab: 2.84 mg/L Analyzer: 2.82 mg/L Effluent Free Chlorine @ 14:59 Grab: 2.56 mg/L Analyzer: 2.50 mg/L Treated Free Chlorine @ 15:02 Grab: 0.15 mg/L Analyzer: 0.12 mg/L Treated Total Chlorine @ 15:02 Grab: 3.08 mg/L Analyzer: 3.07 mg/L -Completed JHSC inspection | Newmarket Well No. 15 | 2026-01-20
CENTRAL | January | On site to troubleshoot treated combined chlorine lolo alarm and complete station check. -Based on trends, analyzer at fault since chlorine trend immediately recovered after each dip. Treated free analyzer never read below 0.09 mg/L when treated total analyzer was misreading Took grab: Treated Total Chlorine @ 8:41 Grab: 1.68 mg/L Analyzer: 1.63 mg/L -Cleaned analyzer -Retested analyzer: Treated Total Chlorine @ 8:41 Grab: 1.68 mg/L Analyzer: 1.63 mg/L -Verified other analyzers: Influent Free Chlorine @ 9:24 Grab: 2.54 mg/L Analyzer: 2.58 mg/L Effluent Free Chlorine @ 9:21 Grab: 0.09 mg/L Analyzer: 0.05 mg/L Treated Free Chlorine @ 8:57 Grab: 0.08 mg/L Analyzer: 0.03 mg/L -Changed influent free chlorine analyzer reagents -Topped up well 15 mineral oil -Continued troubleshooting treated total chlorine analyzer with Eric S. He replaced the colorimeter and tubing. Grab after replacement for verification: Treated Total Chlorine @ 10:39 Grab: 1.47 mg/L Analyzer: 1.52 mg/L -Entered data into PD sheet -Checked trends -Returned well to auto | Newmarket Well No. 15 | 2026-01-23
CENTRAL | January | Received chlorine delivery. Exchanged 6 empty for 6 full. | Newmarket Well No. 15 | 2026-01-19
CENTRAL | January | On site to complete station check. -Verified analyzers: Influent Free Chlorine @ 12:18 Grab: 2.98 mg/L Analyzer: 2.90 mg/L Effluent Free Chlorine @ 12:15 Grab: 2.82 mg/L Analyzer: 2.88 mg/L Treated Free Chlorine @ 11:57 Grab: 0.13 mg/L Analyzer: 0.17 mg/L Treated Total Chlorine @ 11:57 Grab: 3.38 mg/L Analyzer: 3.33 mg/L -Entered data into PD sheet -Checked trends -Changed chlorine:ammonia ratio from to 4.10 to 4.00 -Changed chlorine cylinder A with J. Garnett | Newmarket Well No. 15 | 2026-01-09
CENTRAL | January | On site to complete station check and collect operational samples. -Verified analyzers: Influent Free Chlorine @ 8:39 Grab: 2.92 mg/L Analyzer: 2.82 mg/L Effluent Free Chlorine @ 8:36 Grab: 2.78 mg/L Analyzer: 2.89 mg/L Treated Free Chlorine @ 8:31 Grab: 0.13 mg/L Analyzer: 0.15 mg/L Treated Total Chlorine @ 8:31 Grab: 3.24 mg/L Analyzer: 3.39 mg/L -Entered data into PD sheet -Checked trends -Changed chlorine cylinder B with J. Garnett. Accidentally hit chlorine e-stop during process ? notified ROC of false alarm, reset system. Left well off since instrumentation came on site. | Newmarket Well No. 15 | 2026-01-19
CENTRAL | January | On site to complete station check and collect weekly bacti samples (W11504234) -Verified analyzers: Influent Free Chlorine @ 12:22 Grab: 2.90 mg/L Analyzer: 2.91 mg/L Effluent Free Chlorine @ 12:19 Grab: 2.86 mg/L Analyzer: 2.91 mg/L Treated Free Chlorine @ 12:12 Grab: 0.10 mg/L Analyzer: 0.15 mg/L Treated Total Chlorine @ 12:12 Grab: 3.16 mg/L Analyzer: 3.27 mg/L -Entered data into PD sheet -Checked trends -Changed reagents for effluent free chlorine analyzer | Newmarket Well No. 15 | 2026-01-07
CENTRAL | January | On site to complete station check and collect operational samples. -Verified analyzers: Influent Free Chlorine @ 8:34 Grab: 3.00 mg/L Analyzer: 2.90 mg/L Effluent Free Chlorine @ 8:30 Grab: 2.84 mg/L Analyzer: 2.91 mg/L Treated Free Chlorine @ 8:24 Grab: 0.12 mg/L Analyzer: 0.16 mg/L Treated Total Chlorine @ 8:24 Grab: 3.26 mg/L Analyzer: 3.37 mg/L -Entered data into PD sheet -Checked trends -Topped up ammonia tank 1 -Changed reagents for treated total and treated free chlorine analyzers | Newmarket Well No. 15 | 2026-01-13
CENTRAL | January | Topped up silicate 227L to 385L | Newmarket Well No. 15 | 2026-01-13
CENTRAL | January | Silicate Before: 51.2cm/232,3L After: 84.4cm/384.7L | Newmarket Well No. 15 | 2026-01-06
CENTRAL | January | On site to complete station check and collect weekly bacti samples (W11522649). -Placed well in manual-on -Verified analyzers: Influent Free Chlorine @ 12:34 Grab: 2.84 mg/L Analyzer: 2.83 mg/L Effluent Free Chlorine @ 12:31 Grab: 2.92 mg/L Analyzer: 2.85 mg/L Treated Free Chlorine @ 12:21 Grab: 0.15 mg/L Analyzer: 0.14 mg/L Treated Total Chlorine @ 12:29 Grab: 3.30 mg/L Analyzer: 3.39 mg/L -Entered data into PD sheet -Checked trends -Returned well to auto | Newmarket Well No. 15 | 2026-01-14
CENTRAL | January | On-site for a station and equipment check No issues found Cylinder change, bank 2, with J Garnett Chemical levels and systems ok Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@1444 G:2.88 A:2.84mg/L Effluent Free @1448 G:0.10 | Newmarket Well No. 15 | 2026-01-05
CENTRAL | January | On-site for a station and equipment check No issues found. Chemical levels and systems ok Topped up oil on well pump Verified analyzers and entered all readings and grabs into PWQ sheet Influent free@1356 G:3.16 A:3.19mg/L Effluent Free@1358 G:0.18 A:0.18mg/L Treated; Free@1359 G:0.11 A:0.09mg/L Total@1402 G:2.76 A:2.82mg/L | Newmarket Well No. 15 | 2026-01-02
CENTRAL | January | -Performed station check - logged station readings into PWQ sheet | Newmarket Kirby Pumping Station | 2026-01-26
CENTRAL | January | On site perform station check. All pumps in standby. Recorded data into process sheets. FCV 1 flow at 20.2 l/s filling NM central zone. No issues on site. | Newmarket Kirby Pumping Station | 2026-01-30
CENTRAL | January | Onsite for station check: Station/equipment- Ok Contractor onsite for generator upgrades * | Newmarket Kirby Pumping Station | 2026-01-16
CENTRAL | January | On site to perform test runs on all motors. Ran all pumps one at a time in manual mode. Completed tests and all pumps back to automatic mode. | Newmarket Kirby Pumping Station | 2026-01-23
CENTRAL | January | Station and equipment check - all ok Placed all pumps in manual to excercise all actuated valves Returned to normal Ops normal | Newmarket Kirby Pumping Station | 2026-01-23
CENTRAL | January | Station and equipment check All pumps ready in standby FCV 0% Flow: 0 L/s Suction pressure: 45 kPa Discharge pressure: 337 kPa Tank: 54% *Found water leaking through coax cable conduit and junction box in diesel room, possibly from snow melt outside temp +5 Informed team, will monitor All ops at station normal | Newmarket Kirby Pumping Station | 2026-01-09
CENTRAL | January | Station and equipment check All pumps available in auto, duty not active FCV: 0% Suction pressure: 45 kPa Discharge pressure: 339 kPa Flow: 0 L/s Ops normal | Newmarket Kirby Pumping Station | 2026-01-19
CENTRAL | January | Onsite to complete monthly Maximo workorders Informed ROC (Adam B) of ongoings Warranty issue with epoxy under diesel generator, pics/email sent No other issues noted Station ops normal | Newmarket Kirby Pumping Station | 2026-01-15
CENTRAL | January | Restarted the Operator Interface Terminal due to Windows driver updates. Notified the Remote Operation Center. | Newmarket Kirby Pumping Station | 2026-01-12
CENTRAL | January | Station and equipment check FCV 0% 0 L/s All pumps in standby and available Ops normal | Newmarket Kirby Pumping Station | 2026-01-12
CENTRAL | January | On site perform station check. All pumps in standby. Recorded data into process sheets. FCV 1 flow at 19.6 l/s filling NM central zone. No issues on site. | Newmarket Kirby Pumping Station | 2026-01-02
CENTRAL | January | Station and equipment check All pumps standby FCV1 @ 17% Discharge pressure: 328 kPa Suction pressure: 85 kPa Flow: 20 L/s Diesel generator hours: 30.65 Fuel: Above 3/4 Ops normal | Newmarket Kirby Pumping Station | 2026-01-05
CENTRAL | January | On site to complete station check. -Wells placed in manual for duration of check -Verified analyzers: Influent Free Chlorine @ 12:21 Grab: 2.76 mg/L Analyzer: 2.70 mg/L Effluent Free Chlorine @ 12:18 Grab: 2.54 mg/L Analyzer: 2.59 mg/L Treated Free Chlorine @ 12:14 Grab: 0.11 mg/L Analyzer: 0.13 mg/L Treated Total Chlorine @ 12:14 Grab: 3.05 mg/L Analyzer: 2.92 mg/L -Topped up ammonia tank 2 -Entered data into PD sheet -Checked trends -Returned wells to auto | Newmarket Well 1 & 2 | 2026-01-23
CENTRAL | January | On site to complete station check and collect operational samples. -Verified analyzers: Influent Free Chlorine @ 11:24 Grab: 2.56 mg/L Analyzer: 2.57 mg/L Effluent Free Chlorine @ 11:21 Grab: 2.58 mg/L Analyzer: 2.52 mg/L Treated Free Chlorine @ 11:00 Grab: 0.15 mg/L Analyzer: 0.13 mg/L Treated Total Chlorine @ 11:00 Grab: 2.96 mg/L Analyzer: 2.89 mg/L -Entered data into PD sheet -Checked trends -Changed chlorine cylinder bank A with J. Garnett | Newmarket Well 1 & 2 | 2026-01-19
CENTRAL | January | On site to complete station check. -Verified analyzers: Influent Free Chlorine @ 11:29 Grab: 2.62 mg/L Analyzer: 2.60 mg/L Effluent Free Chlorine @ 11:20 Grab: 2.46 mg/L Analyzer: 2.53 mg/L Treated Free Chlorine @ 11:14 Grab: 0.12 mg/L Analyzer: 0.13 mg/L Treated Total Chlorine @ 11:14 Grab: 2.78 mg/L Analyzer: 2.87 mg/L -Entered data into PD sheet -Checked trends | Newmarket Well 1 & 2 | 2026-01-26
CENTRAL | January | Silicate top up: Before: 68.5cm/622L After: 120cm/1089L level sensor loss of signal (read 0)& interlocked silicate feed pumps drained a few liters out of tank & ok | Newmarket Well 1 & 2 | 2026-01-28
CENTRAL | January | On site to complete station check, collect weekly bacti samples (W11539023), and collect Q1 samples (W11476442). -Verified analyzers: Influent Free Chlorine @ 9:57 Grab: 2.48 mg/L Analyzer: 2.55 mg/L Effluent Free Chlorine @ 9:52 Grab: 2.46 mg/L Analyzer: 2.54 mg/L Treated Free Chlorine @ 9:45 Grab: 0.12 mg/L Analyzer: 0.13 mg/L Treated Total Chlorine @ 9:45 Grab: 2.86 mg/L Analyzer: 2.88 mg/L -Changed reagents for influent free and treated free analyzers -Topped up well 2 mineral oil -Entered data into PD sheet -Checked trends -Placed wells in manual for duration of work, returned to auto once finished. Placed NMW136 well 13 in manual. | Newmarket Well 1 & 2 | 2026-01-21
CENTRAL | January | Silicate load 572 L - 1089 L Wells running in duty Ops normal | Newmarket Well 1 & 2 | 2026-01-20
CENTRAL | January | On site to complete station check. -Verified analyzers: Influent Free Chlorine @ 9:25 Grab: 2.44 mg/L Analyzer: 2.52 mg/L Effluent Free Chlorine @ 9:21 Grab: 2.44 mg/L Analyzer: 2.44 mg/L Treated Free Chlorine @ 9:18 Grab: 0.11 mg/L Analyzer: 0.12 mg/L Treated Total Chlorine @ 9:18 Grab: 2.66 mg/L Analyzer: 2.70 mg/L -Entered data into PD sheet -Checked trends -Topped up ammonia tank 1 | Newmarket Well 1 & 2 | 2026-01-16
CENTRAL | January | On site to continue troubleshooting silicate system per W11581469. Notified ROC of relevant alarms. -Performed hot water flush through chemical board, fully operated PRVs -Performed drawdown for silicate pump 2: adjusted SCADA max flow rate from 205 to 220 mL/min -Added dechlor to waste chamber, backflushed well slightly while running silicate pump 2 to observe pressure and operation of pump -Returned everything to auto -Observed function as wells ran. No issues found | Newmarket Well 1 & 2 | 2026-01-15
CENTRAL | January | On site to complete station check and collect weekly bacti samples (W11550733). -Verified analyzers: Influent Free Chlorine @ 10:44 Grab: 2.70 mg/L Analyzer: 2.70 mg/L Effluent Free Chlorine @ 10:41 Grab: 2.60 mg/L Analyzer: 2.62 mg/L Treated Free Chlorine @ 10:37 Grab: 0.13 mg/L Analyzer: 0.13 mg/L Treated Total Chlorine @ 10:37 Grab: 2.90 mg/L Analyzer: 3.00 mg/L -Entered data into PD sheet -Checked trends | Newmarket Well 1 & 2 | 2026-01-28
CENTRAL | January | Receive 9 Full chlorine cylinders, return 9 empty Ops normal | Newmarket Well 1 & 2 | 2026-01-27
CENTRAL | January | On site to complete station check. -Verified analyzers: Influent Free Chlorine @ 11:47 Grab: 2.52 mg/L Analyzer: 2.57 mg/L Effluent Free Chlorine @ 11:44 Grab: 2.46 mg/L Analyzer: 2.51 mg/L Treated Free Chlorine @ 11:39 Grab: 0.12 mg/L Analyzer: 0.13 mg/L Treated Total Chlorine @ 11:39 Grab: 2.96 mg/L Analyzer: 2.89 mg/L -Changed reagents for treated total chlorine analyzer -Topped up ammonia tank 1 -Topped up well 2 mineral oil -Entered data into PD sheet -Checked trends | Newmarket Well 1 & 2 | 2026-01-30
CENTRAL | January | On site to complete station check and collect weekly bacti samples (W11504234) -Verified analyzers: Influent Free Chlorine @ 14:04 Grab: 2.56 mg/L Analyzer: 2.61 mg/L Effluent Free Chlorine @ 14:01 Grab: 2.36 mg/L Analyzer: 2.38 mg/L Treated Free Chlorine @ 13:54 Grab: 0.09 mg/L Analyzer: 0.13 mg/L Treated Total Chlorine @ 13:54 Grab: 2.62 mg/L Analyzer: 2.58 mg/L -Entered data into PD sheet -Checked trends -Returned wells to auto | Newmarket Well 1 & 2 | 2026-01-07
CENTRAL | January | On site to complete station check. -Verified analyzers: Influent Free Chlorine @ 10:32 Grab: 2.46 mg/L Analyzer: 2.52 mg/L Effluent Free Chlorine @ 10:27 Grab: 2.52 mg/L Analyzer: 2.53 mg/L Treated Free Chlorine @ 10:20 Grab: 0.16 mg/L Analyzer: 0.13 mg/L Treated Total Chlorine @ 10:20 Grab: 2.94 mg/L Analyzer: 2.88 mg/L -Entered data into PD sheet -Checked trends -Topped up ammonia tank 2 | Newmarket Well 1 & 2 | 2026-01-09
CENTRAL | January | On site to complete station check and collect weekly bacti samples (W11522649). -Placed wells in manual-on for duration of station check -Verified analyzers: Influent Free Chlorine @ 8:06 Grab: 2.56 mg/L Analyzer: 2.60 mg/L Effluent Free Chlorine @ 8:01 Grab: 2.56 mg/L Analyzer: 2.51 mg/L Treated Free Chlorine @ 7:55 Grab: 0.15 mg/L Analyzer: 0.13 mg/L Treated Total Chlorine @ 7:55 Grab: 2.84 mg/L Analyzer: 2.85 mg/L -Entered data into PD sheet -Checked trends -Activated well 16 in manual-on -Cleaned turbidimeter, analyzer read 0.048 NTU afterwards. Adjusted settings so flowmeter was on. | Newmarket Well 1 & 2 | 2026-01-14
CENTRAL | January | Onsite responding to low influent. Troubleshoot both chlorine trains, unable to find issue. Continued backflushing well from point Alex Bell left at. Once backflushing complete, restarted well with backflush reset. Put well back into service monitored residuals, all ok. Tested both chlorine trains all ok. Leaving site Alex Bell continuing to sample wells | Newmarket Well 1 & 2 | 2026-01-07
CENTRAL | January | On site to complete PMs. Notified ROC of relevant alarms. -Completed JHSC inspection, all good -Performed maintenance on and inspected deep well exhaust valve for well 1 and well 2 -Placed wells in manual -Performed maintenance on and calibrated turbidimeter. Placed analyzer in hold outputs prior to work, and returned it to normal once work completed. Turbidimeter read 0.053 NTU afterwards. -Left wells in manual | Newmarket Well 1 & 2 | 2026-01-08
CENTRAL | January | On site to complete PMs. Notified ROC of relevant alarms. -Performed maintenance on CL17 chlorine analyzers and verified as follows: Influent Free Chlorine @ 12:31 Grab: 2.40 mg/L Analyzer: 2.41 mg/L Effluent Free Chlorine @ 12:34 Grab: 0.11 mg/L Analyzer: 0.15 mg/L Treated Free Chlorine @ 12:38 Grab: 0.12 mg/L Analyzer: 0.08 mg/L Treated Total Chlorine @ 12:42 Grab: 2.48 mg/L Analyzer: 2.47 mg/L -Returned wells to auto | Newmarket Well 1 & 2 | 2026-01-08
CENTRAL | January | On site to respond to lolo influent free chlorine analyzer alarm and interlock. Notified ROC of relevant alarms. Influent Free Chlorine @ 8:01 Grab: 0.11 mg/L Analyzer: 0.09 mg/L Influent Total Chlorine @ 8:01 Grab: 0.23 mg/L Confirmed via grabs that analyzer not at fault for lolo influent free chlorine alarm. Placed both chlorinator 2 and chlorine booster pump 2 in manual-off. Added dechlor to drain chamber. Backflushed well until grabs read as follows: Influent Free Chlorine @ 9:46 Grab: 0.04 mg/L Analyzer: 0.04 mg/L Influent Total Chlorine @ 9:46 Grab: 0.86 mg/L Ended backflushing upon consult with Ben H. Placed Newmarket well 16 in manual-on. | Newmarket Well 1 & 2 | 2026-01-07
CENTRAL | January | On site to complete station check and collect operational samples. -Verified analyzers: Influent Free Chlorine @ 11:36 Grab: 2.56 mg/L Analyzer: 2.47 mg/L Effluent Free Chlorine @ 11:15 Grab: 2.54 mg/L Analyzer: 2.47 mg/L Treated Free Chlorine @ 11:05 Grab: 0.16 mg/L Analyzer: 0.13 mg/L Treated Total Chlorine @ 11:05 Grab: 2.94 mg/L Analyzer: 2.82 mg/L -Entered data into PD sheet -Checked trends -Topped up well 2 mineral oil Troubleshooting silicate system per W11581469. Notified ROC of relevant alarms. -Silicate pump 2 placed OOS - identified as cause of turbidity issue, ruptured tubing. Upon cleaning assembly and replacing tube, unit would not power back on. Silicate pump 2 alarms can be disregarded until pump returned to service. | Newmarket Well 1 & 2 | 2026-01-12
CENTRAL | January | Continued silicate troubleshooting with Donny (who also topped up silicate tanks). Fixed leakage flood alarm. Silicate pump 2 remains off. | Newmarket Well 1 & 2 | 2026-01-13
CENTRAL | January | On site to complete PMs. Notified ROC of relevant alarms. -Inspected ammonia system. Performed pump drawdowns. Pump 1 max flow rate setpoint on SCADA adjusted from 200 to 220 mg/L. Pump 2 max flow rate not changed. -Inspected silicate system. Performed pump drawdowns. Pump 1 max flow rate setpoint on SCADA adjusted from 200 to 180 mg/L. Pump 2 max flow rate setpoint on SCADA adjusted from 230 to 205 mg/L. -Completed bank B chlorine cylinder change with J Garnett (W11564885 quick reported) -Turned off area duty 1 and placed wells in manual-off. Placed wells in local, notified ROC. Isolated raw main via influent side valve of contact chamber. Added dechlor to drain chamber and depressurized raw main. Removed and cleaned silicate injection points. Reopened contact chamber valve and repressurized raw main. Reprimed lines while backflushing slightly. Closed waste valve. -Ran wells 1 and 2 manually to assess silicate system. Confirmed system running properly, ended manual well run. Returned wells to auto. -Performed chlorine leak detection test. System performed as intended, returned everything to normal and cleared alarms. -Added more dechlor to drain chamber and cracked waste valve open slightly to backflush while performing chlorine dosing system inspection. No issues found, closed waste valve | Newmarket Well 1 & 2 | 2026-01-06
CENTRAL | January | Station and equipment check Wells not running, Operational samples to be collected Wednesday with BacT samples Took grabs @ 13:45 Treated Total: 2.45 mg/l Treated Free: 0.05 mg/l Chemicals/reagents ok Ops normal | Newmarket Well 1 & 2 | 2026-01-05
CENTRAL | January | -Responded Turbidimeter fault alarm - upon arrival, turbidity reading=0.047ntu, no alarm outstanding - checked turbidimeter, found sample cell surface was wet - wiped moisture down and cleaned sample cell - put wells back to auto and restarted them | Newmarket Well 1 & 2 | 2026-01-03
CENTRAL | January | 13:30. On-site for station check and to investigate tubidity fault alarm. Wells interlocked at 10:38. Found turbdiity analyzer faulted on vial clarity. Cleaned vial. Placed wells in manual off. Flushed sample line. Cleared alarms with no issues. Verified analyzers (mg/l). 13:43. Influent free grab: 2.46. CL17: 2.43 . 13:46. Effluent free grab: 0.18. CL17. 0.20. 13:48. Treated free grab: 0.09. CL17: 0.07. 13:50. Treated total grab: 2.46. CL17 2.42. Replaced influent analyzer reagent. Topped up ammonia tank 1. Completed process sheet entry. 1118 hrs. Left site with no issues. | Newmarket Well 1 & 2 | 2026-01-02
WEST | January | Filled silicate tank 47.10 cm to 79 cm | Nobleton Wells 3 & 7 | 2026-01-19
WEST | January | -on site to replace hypo lines and install hypo line containment -replaced hypo injection point ball valve -after maintenance complete attempted to start well, but well was interlocked due to well 7 flow meter empty pipe fault, suspect air trapped in flow meter -attempted to run well 7 in local to waste to clear air from line, however VFD shutdown due to waste valve fail to close alarm -temporarily disabled well 7 flow meter empty pipe fault in order to start well and push air out of pipe -after well start up re-enabled flow meter empty pipe fault - no further issues -tested both hypo pumps in auto - no issues -site back to normal operation -received hypo delivery | Nobleton Wells 3 & 7 | 2026-01-20
WEST | January | -On-site to complete station check -well #3 OOS -well # 7 running in manual -hypo pump #1 running at 22%, 49 strokes/min, 100 psi, DF = 55.50% -silicate pump #2 running at 56%, 74 strokes/min, 98 psi -checked equipment -reviewed trends -CL17 reagents ok -verified chlorine analyzers: 13:11 - Effluent Analyzer = 1.29 mg/L 13:11 - Effluent grab: Free chlorine = 1.31 mg/L Total chlorine = 1.49 mg/L 13:13 - Influent Analyzer = 1.94 mg/L 13:13 - Influent grab: Free chlorine = 1.96 mg/L -filled hypo tanks 140/135 L to 200/197L -recorded readings in PWQ sheet -no issues found -well back into auto | Nobleton Wells 3 & 7 | 2026-01-30
WEST | January | -On-site to complete station check -well locked out due to lolo influent over the weekend, influent residual recovered to 1.04 mg/L when arrived on site -primed both hypo pumps while backflushing with dechlorination 11:57 - influent analyzer = 0.94 mg/L grab = 0.92 mg/L -stop backflushing, started well #7 in manual -well #3 OOS -silicate pump #1 OOS -hypo pump #1 running at 25%, 49 strokes/min, 100 psi, DF = 55.25% -silicate pump #2 running at 62%, 74 strokes/min, 100 psi -checked equipment -reviewed trends -CL17 reagents ok -verified chlorine analyzers: 12:13 - Effluent Analyzer = 1.41 mg/L 12:13 - Effluent grab: Free chlorine = 1.40 mg/L Total chlorine = 1.62 mg/L -collected operational iron sequestration samples -recorded readings in PWQ sheet -no other issues found -well back into auto | Nobleton Wells 3 & 7 | 2026-01-26
WEST | January | In to Complete Station Check Residuals Effluent free Grab: 2.22mg/L, Analyzer: 2.14mg/L Influent free Grab: 1.78mg/L, Analyzer: 1.76mg/L Reagents - all okay Topped up hypo tanks No other issues on site | Nobleton Wells 3 & 7 | 2026-01-16
WEST | January | increased chlorine residual setpoint from 1.90 to 2.10 mg/L due to lower effluent residual | Nobleton Wells 3 & 7 | 2026-01-23
WEST | January | In to Complete Station Check and to collect bacti sample w11550785 Residuals Effluent free Grab: 1.60mg/L, Analyzer: 1.55mg/L Effluent total Grab 1.83mg/L Influent free Grab: 2.18mg/L, Analyzer: 2.11mg/L Reagents - all okay No other issues on site | Nobleton Wells 3 & 7 | 2026-01-28
WEST | January | In to Complete Station Check and bacti sample w11538206 Residuals Effluent free Grab: 1.55mg/L, Analyzer: 1.79mg/L Total grab 1.73mg/L Adjusted free effluent from 1.79-1.55mg/L after multiple grabs Influent free Grab: 1.87mg/L, Analyzer: 2.07mg/L Reagents - replaced all reagents No new known issues on site | Nobleton Wells 3 & 7 | 2026-01-21
WEST | January | -On-site to complete station check -well #3 OOS -silicate pump #1 OOS -well # 7 running in manual -hypo pump #2 running at 25%, 49 strokes/min, 102 psi, DF = 55.25% -silicate pump #2 running at 63%, 75 strokes/min, 100 psi -checked equipment -reviewed trends -CL17 reagents ok -verified chlorine analyzers: 09:07 - Effluent Analyzer = 1.37 mg/L 09:07 - Effluent grab: Free chlorine = 1.32 mg/L Total chlorine = 1.60 mg/L 09:12 - Influent Analyzer = 1.81 mg/L 09:12 - Influent grab: Free chlorine = 1.83 mg/L -filled hypo tanks 178/173 L to211/207 L -recorded readings in PWQ sheet -no issues found -well back into auto | Nobleton Wells 3 & 7 | 2026-01-23
WEST | January | Filled silicate tank 48.82 cm to 63.19 cm | Nobleton Wells 3 & 7 | 2026-01-12
WEST | January | In to Complete Station Check Residuals Effluent free Grab: 1.58mg/L, Analyzer: 1.59mg/L Influent free Grab: 1.99mg/L, Analyzer: 2.09mg/L Reagents - all okay No other issues on site | Nobleton Wells 3 & 7 | 2026-01-19
WEST | January | In to Complete Station Check Residuals Effluent free Grab: 1.62mg/L, Analyzer: 1.59mg/L Influent free Grab: 1.45mg/L, Analyzer: 1.38mg/L Reagents - all okay No other issues on site | Nobleton Wells 3 & 7 | 2026-01-09
WEST | January | In to Complete Station Check and bacti sample w11522719 and quarterly sample w11476050 Residuals Effluent free Grab: 1.58mg/L, Analyzer: 1.42mg/L Total grab 1.81mg/L Adjusted effluent free from 1.42-1.58mg/L after multiple grabs Influent free Grab: 1.90mg/L, Analyzer: 1.85mg/L Reagents - all okay Topped up hypo from 40/40-61/62cm No new known issues on site | Nobleton Wells 3 & 7 | 2026-01-14
WEST | January | In to Complete Station Check Residuals Effluent free Grab: 1.49mg/L, Analyzer: 1.55mg/L Influent free Grab: 1.98mg/L, Analyzer: 2.05mg/L Dave on site to fill silicate from 48- Reagents - all okay No other issues on site | Nobleton Wells 3 & 7 | 2026-01-12
WEST | January | In to Complete Station Check and bacti sample w111503161 Ran hypo pump 1 noticed leak on chemical panel board discharge - replaced fittings and primed all ok Backflushed well @10:35hrs placed dechlor pucks in chamber backlashed at ~7L/s from 1035-1045hrs then ~9L/s till 10:55hrs and restarted well with hypo p1 running Residuals Effluent free Grab: 2.00mg/L, Analyzer: 2.00mg/L Influent free Grab: 2.11mg/L, Analyzer: 2.09mg/L Total grab 2.38mg/L Reagents - all ok No new known issues on site | Nobleton Wells 3 & 7 | 2026-01-07
WEST | January | Station Check (no issues found) input data to PWQ 9:40 Verified CL17s (mg/l) Influent: Free Grab 2.00, A 1.96 Treated: Free 1.42, A 1.48 Total Grab: 1.65 Hypo tank top up | Nobleton Wells 3 & 7 | 2026-01-02
WEST | January | 10:40-On site to investigate well 7 interlock on influent free low chlorine. CMU5 W11552891 up on investigation hypu pump 2 was in duty during the interlock. Noticed air in the line. purged both hypo pump lines. 11:00 -backflush initiated with dichlorination, flow 9.4 l/s. 11:45- influent free CL2 grab-1.17 mg/L; Analyzer-1.08mg/L 11:46- Stopped backflush. all alarms cleared. 11:52- Activated duty with hypo pump 2 in duty 1. 12:43- influent free CL2 grab-1.81 mg/L; Analyzer-1.87mg/L 12:45- effluent free CL2 grab-1.44 mg/L; Analyzer-1.41mg/L 12:47- effluent totalCL2 grab-1.61 mg/L equipment all okay. | Nobleton Wells 3 & 7 | 2026-01-01
WEST | January | Silicate delivery | Nobleton Wells 3 & 7 | 2026-01-06
WEST | January | W11483596- consultation regarding well 7 interlock, Requested CMU 5 | Nobleton Wells 3 & 7 | 2026-01-01
WEST | January | On site for the following NBW3, JHSC Health and Safety Inspection, Nobleton Well 3 (1M) NBW3, Deep Well Exhaust Valve, Test, Nobleton Well 3 (1M) NBW3, Sodium Hypochlorite System Maintenance, Nobleton Well 3 (1M) NBW3, Pressure Relief Valve, Test, Nobleton Well 3 (1M) NBW3, Diesel Generator Test Run, Nobleton Well 3 (1M) NBW3, Chlorine Analyzer Maintenance, Nobleton Well 3 (1M) NBW3, Low/High Temperature Alarm, Test, Nobleton Well 3 (1M) NBW3, Ventilation System, Inspection, Nobleton Well 3 (1M) NBW3, Turbidimeter, Maintenance, Nobleton Well 3 (1M) NBW3, Manual Valve, Exercise, Nobleton Well 3 (3M) NBW3, Chemical System Inspection - Silicate, Nobleton Well 3 (1M) NBW3, Sodium Hypochlorite System Inspection, Nobleton Well 3 (1M) NBW3, Sodium Hypochlorite Delivery, Nobleton Well No. 3 (1W) Received hypo and silicate deliveries No new issues on site silicate pump 1 in man off. New one has been ordered. | Nobleton Wells 3 & 7 | 2026-01-06
WEST | January | Details: In to Complete Station Check Residuals Effluent free Grab: 1.68mg/L, Analyzer: 1.63mg/L Influent free Grab: 1.35mg/L, Analyzer: 1.33mg/L Reagents - all ok Investing silicate p1 fault. Changed bleeder and diaphragm pump had a ?power supply alarm? and a ?internal can? alarm No other issues on site | Nobleton Wells 3 & 7 | 2026-01-05
CENTRAL | January | On site to complete station check, collect weekly bacti samples (W11539023), and collect Q1 samples (W11476428). -Verified analyzers: Influent Free Chlorine @ 12:14 Grab: 2.66 mg/L Analyzer: 2.70 mg/L Effluent Free Chlorine @ 12:08 Grab: 2.48 mg/L Analyzer: 2.50 mg/L Treated Free Chlorine @ 12:01 Grab: 0.08 mg/L Analyzer: 0.12 mg/L Treated Total Chlorine @ 12:01 Grab: 2.78 mg/L Analyzer: 2.78 mg/L -Manually switched between wells 13 -> 16 in order to complete sampling -Returned wells to auto when sampling finished -Entered data into PD sheet -Checked trends -Changed reagents for treated free analyzer | Newmarket Wells 13-16 | 2026-01-21
CENTRAL | January | On site to complete station check and collect weekly bacti samples (W11550733). -Verified analyzers: Influent Free Chlorine @ 8:38 Grab: 2.66 mg/L Analyzer: 2.66 mg/L Effluent Free Chlorine @ 8:35 Grab: 2.34 mg/L Analyzer: 2.39 mg/L Treated Free Chlorine @ 8:28 Grab: 0.10 mg/L Analyzer: 0.12 mg/L Treated Total Chlorine @ 8:28 Grab: 2.68 mg/L Analyzer: 2.71 mg/L -Manually switched from well 16 to well 13 to take raw sample -Entered data into PD sheet -Checked trends -Changed well 13 to duty 1, well 16 to duty 2 -Returned wells to auto | Newmarket Wells 13-16 | 2026-01-28
CENTRAL | January | Placed wells 13/16 in manual-off to perform PMs ? temporarily leaving site to receive chlorine delivery at Glenway. | Newmarket Wells 13-16 | 2026-01-27
CENTRAL | January | Silicate top up: Before: 38.5cm/1793L After: 71.4cm/3321L | Newmarket Wells 13-16 | 2026-01-28
CENTRAL | January | On site to complete station check. -Changed chlorine cylinder bank B with J. Garnett | Newmarket Wells 13-16 | 2026-01-19
CENTRAL | January | On site to complete station check. -Verified analyzers: Influent Free Chlorine @ 10:02 Grab: 2.62 mg/L Analyzer: 2.72 mg/L Effluent Free Chlorine @ 9:56 Grab: 2.40 mg/L Analyzer: 2.49 mg/L Treated Free Chlorine @ 9:51 Grab: 0.11 mg/L Analyzer: 0.12 mg/L Treated Total Chlorine @ 9:51 Grab: 2.70 mg/L Analyzer: 2.79 mg/L -Changed reagents for treated total chlorine analyzer -Entered data into PD sheet -Checked trends | Newmarket Wells 13-16 | 2026-01-30
CENTRAL | January | On site to complete station check. -Verified analyzers: Influent Free Chlorine @ 9:59 Grab: 2.62 mg/L Analyzer: 2.75 mg/L Effluent Free Chlorine @ 9:54 Grab: 2.30 mg/L Analyzer: 2.39 mg/L Treated Free Chlorine @ 9:49 Grab: 0.12 mg/L Analyzer: 0.13 mg/L Treated Total Chlorine @ 9:49 Grab: 2.66 mg/L Analyzer: 2.76 mg/L -Topped up ammonia tank 1 -Topped up well 16 mineral oil -Topped up well 13 mineral oil -Entered data into PD sheet -Checked trends | Newmarket Wells 13-16 | 2026-01-26
CENTRAL | January | On site to complete PMs and station check. Notified ROC of relevant alarms. -Placed wells in manual for duration of work -Performed chlorine leak detection test: all good -Inspected chlorine system: prior to inspection, added dechlor to waste chamber and started backflushing slightly to prevent chlorine spikes. Ended backflush once finished -Performed JHSC inspection: all good -Performed maintenance on CL17 chlorine analyzers, verified as follows: Influent Free Chlorine @ 14:19 Grab: 2.36 mg/L Analyzer: 2.41 mg/L Effluent Free Chlorine @ 14:23 Grab: 0.11 mg/L Analyzer: 0.14 mg/L Treated Free Chlorine @ 14:28 Grab: 0.06 mg/L Analyzer: 0.09 mg/L Treated Total Chlorine @ 14:25 Grab: 2.32 mg/L Analyzer: 2.38 mg/L -Entered data into PD sheet -Checked trends -Returned wells to auto | Newmarket Wells 13-16 | 2026-01-16
CENTRAL | January | On site to finish station check and collect operational samples. -Placed well 16 in manual-on -Verified analyzers: Influent Free Chlorine @ 14:30 Grab: 2.56 mg/L Analyzer: 2.63 mg/L Effluent Free Chlorine @ 14:28 Grab: 2.34 mg/L Analyzer: 2.40 mg/L Treated Free Chlorine @ 14:25 Grab: 0.14 mg/L Analyzer: 0.12 mg/L Treated Total Chlorine @ 14:25 Grab: 2.72 mg/L Analyzer: 2.70 mg/L -Entered data into PD sheet -Checked trends -Topped up ammonia tank 2 -Returned well 16 to auto | Newmarket Wells 13-16 | 2026-01-19
CENTRAL | January | On site to troubleshoot silicate pump 1 uncommanded stop. Pump runs fine to sightglass, overpressure stop triggered when ran to system. | Newmarket Wells 13-16 | 2026-01-20
CENTRAL | January | On site to complete station check. -Placed wells in 16 in manual for duration of station check -Adjusted well 16 FCV pilot valve to reduce flow slightly in response to recurrent hi flow alarm upon well startup -Verified analyzers: Influent Free Chlorine @ 11:45 Grab: 2.80 mg/L Analyzer: 2.71 mg/L Effluent Free Chlorine @ 11:39 Grab: 2.40 mg/L Analyzer: 2.35 mg/L Treated Free Chlorine @ 11:31 Grab: 0.17 mg/L Analyzer: 0.12 mg/L Treated Total Chlorine @ 11:31 Grab: 2.76 mg/L Analyzer: 2.73 mg/L -Returned well 16 to auto, placed wells 1 and 2 in manual -Entered data into PD sheet -Checked trends | Newmarket Wells 13-16 | 2026-01-23
CENTRAL | January | Changed influent free chlorine analyzer reagents. | Newmarket Wells 13-16 | 2026-01-26
CENTRAL | January | On site to complete PMs and station check. Notified ROC of relevant alarms. -Placed wells in manual-off -Placed wells in local, added dechlor to waste chamber -Isolated raw main via influent side valve before contact tank. Depressurized raw main via waste valve. Influent free lo and lolo alarms caused by this cutting off flow to the analyzer, read normal once flow restored -Cleaned injection points. Cleared clog in injection point 1 -Repressurized raw main -Backflushed well slightly while repriming silicate injection points -Returned wells to manual, placed well 13 in manual-on -Returned wells to auto | Newmarket Wells 13-16 | 2026-01-29
CENTRAL | January | On site to complete PMs. Notified ROC of relevant alarms. -Placed wells in manual-off -Performed maintenance on turbidity analyzer. Analyzer read 0.081 NTU afterwards. -Returned wells to auto | Newmarket Wells 13-16 | 2026-01-14
CENTRAL | January | On site to complete station check and collect weekly bacti samples (W11522649). -Verified analyzers: Influent Free Chlorine @ 9:41 Grab: 2.72 mg/L Analyzer: 2.75 mg/L Effluent Free Chlorine @ 9:36 Grab: 2.48 mg/L Analyzer: 2.40 mg/L Treated Free Chlorine @ 9:31 Grab: 0.14 mg/L Analyzer: 0.13 mg/L Treated Total Chlorine @ 9:31 Grab: 2.80 mg/L Analyzer: 2.76 mg/L -Entered data into PD sheet -Checked trends -Switched from well 16 manual on to well 13 manual on in order to take raw sample -Changed reagents for effluent free chlorine analyzer -Returned well to auto 13 to auto | Newmarket Wells 13-16 | 2026-01-14
CENTRAL | January | Received chlorine cylinder delivery, exchanged 12 empty for 12 full. | Newmarket Wells 13-16 | 2026-01-08
CENTRAL | January | On site to complete station check. -Verified analyzers: Influent Free Chlorine @ 8:55 Grab: 2.26 mg/L Analyzer: 2.35 mg/L Effluent Free Chlorine @ 8:52 Grab: 0.59 mg/L Analyzer: 0.59 mg/L Treated Free Chlorine @ 8:49 Grab: 0.08 mg/L Analyzer: 0.06 mg/L Treated Total Chlorine @ 8:49 Grab: 2.50 mg/L Analyzer: 2.60 mg/L -Entered data into PD sheet -Checked trends -Topped up ammonia tank 1 | Newmarket Wells 13-16 | 2026-01-09
CENTRAL | January | Dropped off roughly 750 L sodium silicate to bulk tank. | Newmarket Wells 13-16 | 2026-01-13
CENTRAL | January | On site to complete PMs. Notified ROC of relevant alarms. -Performed maintenance on well 13 flow control valve -Inspected ammonia system, all good. Performed pump drawdowns. Pump 2 max flow rate adjusted on SCADA from 200 to 230 mL/min. | Newmarket Wells 13-16 | 2026-01-13
CENTRAL | January | On site to complete station check and collect operational samples. -Verified analyzers: Influent Free Chlorine @ 10:02 Grab: 2.60 mg/L Analyzer: 2.64 mg/L Effluent Free Chlorine @ 9:43 Grab: 2.44 mg/L Analyzer: 2.39 mg/L Treated Free Chlorine @ 9:32 Grab: 0.10 mg/L Analyzer: 0.12 mg/L Treated Total Chlorine @ 9:32 Grab: 2.76 mg/L Analyzer: 2.73 mg/L -Entered data into PD sheet -Checked trends -Topped up well 16 mineral oil | Newmarket Wells 13-16 | 2026-01-12
CENTRAL | January | On site to complete station check and collect weekly bacti samples (W11504234) -Verified analyzers: Influent Free Chlorine @ 10:51 Grab: 2.72 mg/L Analyzer: 2.70 mg/L Effluent Free Chlorine @ 10:48 Grab: 2.50 mg/L Analyzer: 2.46 mg/L Treated Free Chlorine @ 10:26 Grab: 0.20 mg/L Analyzer: 0.18 mg/L Treated Total Chlorine @ 10:26 Grab: 2.74 mg/L Analyzer: 2.76 mg/L -Switched well 16 manual-off and well 13 manual-on in order to collect well 13 raw bacti sample -Returned both wells to auto -Placed NMW15 in manual-on -Entered data into PD sheet -Checked trends | Newmarket Wells 13-16 | 2026-01-07
CENTRAL | January | -Performed station check - logged station readings into PWQ sheet -Checked CL17 reagents - OK | Newmarket Wells 13-16 | 2026-01-02
CENTRAL | January | On-site for station check . 13:24. Ran well 16 in manual. Verified analyzers (mg/L): 13:51. Influent free chlorine grab: 2.82. CL17: 2.80. 14:06. Effluent free chlorine grab: 2.42. CL17: 2.34. 14:13. Treated free chlorine grab: 0.09. CL17: 0.16. 14:13. Treated total chlorine grab: 2.64 CL17: 2.67. Entered readings into process sheets. Adjusted chlorine/ammonia ratio from 4.3 to 4.2. due to low treated free ammonia grob of 0.00 mg/l. 14:29 free ammonia grab: 0.03. 14:36. Placed well 16 back in auto. Topped up well 13 oil reservoir from 1/2 full. No issues found on site. | Newmarket Wells 13-16 | 2026-01-05
WEST | January | On site for station check. Pump running, chamber dry - site all ok | Nobleton Booster Pumping Station | 2026-01-16
WEST | January | -on site to complete station check -chamber lid secure, chamber dry, pump running -no issues | Nobleton Booster Pumping Station | 2026-01-23
WEST | January | On site for station check. Pump running, chamber dry - site all ok | Nobleton Booster Pumping Station | 2026-01-19
WEST | January | On site for station check. Pump running, chamber dry - site all ok Completed jhsc inspection - all ok | Nobleton Booster Pumping Station | 2026-01-12
WEST | January | On site for station check. Pump running, chamber dry - site all ok | Nobleton Booster Pumping Station | 2026-01-09
WEST | January | On site for station check. Pump running, chamber dry - site all ok | Nobleton Booster Pumping Station | 2026-01-05
WEST | January | Station Check (no issues found) | Nobleton Booster Pumping Station | 2026-01-02
WEST | January | In to Complete Station Check and to collect bacti sample w11538206 Residuals free Grab 1.34mg/L Analyzer 1.09mg/L Total Grab: 1.65mg/L, Analyzer: 1.70mg/L Adjusted free analyzer from 1.09-1.34mg/L after multiple grabs No new known issues on site | Nobleton North Elevated Tank | 2026-01-21
WEST | January | In to Complete Station Check and to collect bacti sample w11550785 Residuals free Grab 1.38mg/L Analyzer 1.34mg/L Total Grab: 1.92mg/L, Analyzer: 1.97mg/L No new known issues on site | Nobleton North Elevated Tank | 2026-01-28
WEST | January | On site for the following NBET27, Air Valve, Flush & Inspection, Nobleton North ET (1M) NBET27, Siemens Depolox 5/Micro 2000, Chlorine Analyzer, Maintenance, Nobleton North ET (1M) - grabs free 1.15mg/L total 1.38mg/L Analyzer readings free 0.74mg/L total 1.40mg/L Added grit to analyzer reservoir and free residual came up. Adjusted free to 1.15mg/L after multiple grabs NBET27, Inlet/Outlet Heat Trace System, Inspection, Nobleton North ET [WINTER] (1M) NBET27, Manual Valve, Exercise, Nobleton North ET (2M) NBET27, Low Temperature Alarm, Test, Nobleton North, ET (1M) NBET27, Nobleton North ET - Portable Gasoline Generator Test (1M) | Nobleton North Elevated Tank | 2026-01-13
WEST | January | In to Complete Station Check and to collect bacti sample w11522719 and quarterly sample w11476624 Residuals free Grab 1.09mg/L Analyzer 1.12mg/L Total Grab: 1.48mg/L, Analyzer: 1.30mg/L Adjusted total from 1.30-1.48mg/L after multiple grabs No new known issues on site | Nobleton North Elevated Tank | 2026-01-14
WEST | January | Entry meant for south tower | Nobleton North Elevated Tank | 2026-01-07
WEST | January | In to Complete Station Check and to collect bacti sample w11503161 Residuals free Grab 1.01mg/L Analyzer 1.06mg/L Total Grab: 1.58mg/L, Analyzer: 1.62mg/L No new known issues on site | Nobleton North Elevated Tank | 2026-01-07
WEST | January | In to Complete Station Check and to collect bacti sample w11550785 Residuals free Grab 1.48mg/L Analyzer 1.99mg/L Total Grab: 1.80mg/L, Analyzer: 1.73mg/L Adjusted free from 1.99-1.48mg/L after multiple grabs Reagents all ok No new known issues on site | Nobleton South Elevated Tank | 2026-01-28
WEST | January | In to Complete Station Check and to collect bacti sample w11538206 Residuals free Grab 1.61mg/L Analyzer 1.57mg/L Total Grab: 1.86mg/L, Analyzer: 1.74mg/L No new known issues on site | Nobleton South Elevated Tank | 2026-01-21
WEST | January | In to Complete Station Check and to collect bacti sample w11522719 and quarterly sample w11476624 Residuals free Grab 1.56mg/L Analyzer 1.59mg/L Total Grab: 1.98mg/L, Analyzer: 1.98mg/L No new known issues on site | Nobleton South Elevated Tank | 2026-01-14
WEST | January | In to Complete Station Check and to collect bacti sample w11503161 Residuals free Grab 1.56mg/L Analyzer 1.59mg/L Total Grab: 1.90mg/L, Analyzer: 1.93mg/L No new known issues on site | Nobleton South Elevated Tank | 2026-01-07
WEST | January | In to Complete Station Check and bactisample w11538206 Residuals Effluent free Grab: 1.90mg/L, Analyzer: 1.77mg/L Total grab 2.20mg/L Influent free Grab: 1.94mg/L, Analyzer: 1.97mg/L Reagents - all okay No new known issues on site | Nobleton Well 2 | 2026-01-21
WEST | January | On site for the following NBET, JHSC Health and Safety Inspection, Nobleton South ET (1M) NBET, Sump Pit System, Inspection, Nobleton South ET (1M) NBET, Manual Valve, Exercise, Nobleton South ET (2M) NBET, Siemens Depolox 5/Micro 2000, Chlorine Analyzer, Maintenance, Nobleton South, ET (1M) NBET, Inlet/Outlet Heat Trace System, Inspection, Nobleton South ET [WINTER] (1M) NBET, Sensing Line Heat Trace System, Inspection, Nobleton South, ET [WINTER] (1M) NBET, Low Temperature Alarm, Test, Nobleton South, ET (1M) NBET, Gasoline Generator, Test Run, Nobleton South ET (1M) Heat trace were in alarm - cleared alarms all ok No new issues on site | Nobleton South Elevated Tank | 2026-01-13
WEST | January | -on site for chlorine system overhaul -replaced chlorine regulators, ejectors and all chlorine lines -vacuum tested system - no issues -back flushed after maintenance as a precaution -returned chlorine system to normal operation and started well -tested both chlorinators in auto, no issues -site back to normal operation | Nobleton Well 2 | 2026-01-29
WEST | January | In to Complete Station Check and bactisample w11550785 Residuals Effluent free Grab: 1.58mg/L, Analyzer: 1.61mg/L Total grab 1.85mg/L Influent free Grab: 1.93mg/L, Analyzer: 1.98mg/L Reagents - all okay No new known issues on site | Nobleton Well 2 | 2026-01-28
WEST | January | Filled silicate tank 53.25 cm to 94.46 cm | Nobleton Well 2 | 2026-01-19
WEST | January | Completed station check. Updated data into PWQ. Analyzer reagent levels good, chemical dose calculations good. Unable to calibrate effluent Cl17, creating CMU for INST to inspect/replace control board. No issues. | Nobleton Well 2 | 2026-01-26
WEST | January | -on site to respond to chlorine leak alarm -ran scrubber in local -chlorine leak detector reading 0.00 ppm -isolated both chlorine cylinders, leaving site OOS for the night | Nobleton Well 2 | 2026-01-29
WEST | January | -on site to complete station check -well running in manual -cl2 booster pump # 2 running at 206 psi -chlorinator # 2 43% open dosing 24 ppd, vac = - 680 mbar, DF = 89.5% -silicate pump #2 running at 46%, 55.9 ml/min, 90 psi -checked equipment -reviewed trends -CL17 reagents ok -verified chlorine analyzers: 10:39 - Effluent Analyzer = 1.70 mg/L 10:39 - Effluent grab: Free chlorine = 1.74 mg/L Total chlorine = 2.17 mg/L 10:45 - Influent Analyzer = 1.94 mg/L 10:45 - Influent grab: Free chlorine = 1.96 mg/L -recorded readings in PWQ sheet -no issues found -well back into auto - off | Nobleton Well 2 | 2026-01-23
WEST | January | In to Complete Station Check Residuals Effluent free Grab: 1.78mg/L, Analyzer: 1.80mg/L Influent free Grab: 1.96mg/L, Analyzer: 1.91mg/L Reagents - all okay No other issues on site | Nobleton Well 2 | 2026-01-16
WEST | January | In to Complete Station Check Residuals Effluent free Grab: 1.57mg/L, Analyzer: 1.60mg/L Influent free Grab: 1.58mg/L, Analyzer: 1.66mg/L Reagents - all okay No other issues on site Found chlorine leak on chlorinator 1. Isolated and created work order for inst. | Nobleton Well 2 | 2026-01-30
WEST | January | Collected operational iron sequestration samples | Nobleton Well 2 | 2026-01-26
WEST | January | In to Complete Station Check Residuals Effluent free Grab: 1.88mg/L, Analyzer: 1.89mg/L Influent free Grab: 1.96mg/L, Analyzer: 1.99mg/L Reagents - all okay No other issues on site | Nobleton Well 2 | 2026-01-19
WEST | January | In to Complete Station Check Residuals Effluent free Grab: 1.55mg/L, Analyzer: 1.53mg/L Influent free Grab: 1.78mg/L, Analyzer: 1.72mg/L Reagents - all okay No other issues on site | Nobleton Well 2 | 2026-01-09
WEST | January | In to Complete Station Check and bacti sample w11522719 and quarterly sample w11475994 Residuals Effluent free Grab: 1.59mg/L, Analyzer: 1.57mg/L Total grab 2.00mg/L Influent free Grab: 1.98mg/L, Analyzer: 1.92mg/L Reagents - all okay No new known issues on site | Nobleton Well 2 | 2026-01-14
WEST | January | In to Complete Station Check Residuals Effluent free Grab: 1.83mg/L, Analyzer: 1.82mg/L Influent free Grab: 1.98mg/L, Analyzer: 1.94mg/L Reagents - all okay No other issues on site | Nobleton Well 2 | 2026-01-12
WEST | January | In to Complete Station Check and bactisample w11503161 Residuals Effluent free Grab: 1.84mg/L, Analyzer: 1.81mg/L Total grab 2.28mg/L Influent free Grab: 1.96mg/L, Analyzer: 1.92mg/L Reagents - all okay No new known issues on site | Nobleton Well 2 | 2026-01-07
WEST | January | On site for the following NBW2, JHSC Health and Safety Inspection, Nobleton Well 2 (1M) NBW2, Pressure Relief Valve, Test, Nobleton Well 2 (1M) NBW2, Deep Well Exhaust Valve, Test, Nobleton Well 2 (1M) NBW2, Chlorine Leak Detector, Test, Nobleton Well 2 (1M) NBW2, Turbidimeter, Maintenance, Nobleton Well 2 (1M) NBW2, Chlorine Analyzer, Maintenance, Nobleton Well 2 (1M) NBW2, Chemical System Inspection - Silicate, Nobleton W2 (1M) NBW2, Chemical System Inspection - Chlorine, Nobleton W2 (1M) NBW2, Nobleton Well 2, Chemical System Line and Injection Point Flush - Silicate (1M | Nobleton Well 2 | 2026-01-08
WEST | January | Silicate top up: Before: 41.0cm After: 71.09cm | Nobleton Well 2 | 2026-01-06
WEST | January | Station Check (no issues found) Input data to PWQ 11:40 Verified CL17s (mg/l) Influent: Free Grab 1.85, A 1.88 Effluent: Free Grab 1.85, A 1.83 Total: Grab 2.15 | Nobleton Well 2 | 2026-01-02
WEST | January | In to Complete Station Check Residuals Effluent free Grab: 1.66mg/L, Analyzer: 1.61mg/L Influent free Grab: 1.89mg/L, Analyzer: 1.86mg/L Reagents - all okay Changed chlorine cylinder 2 from 0-68kg with Joe Williams No other issues on site | Nobleton Well 2 | 2026-01-05
WEST | January | In to Complete Station Check Residuals Effluent free Grab: 1.44mg/L, Analyzer: 1.41mg/L Influent free Grab: 1.55mg/L, Analyzer: 1.52mg/L Reagents - all okay No other issues on site | Nobleton Wells 5 & 6 | 2026-01-16
WEST | January | Contacted water resources to ensure we can run well 5 for sampling In to Complete Station Check and to collect bacti sample w11538206 Residuals Effluent free Grab: 2.32mg/L, Analyzer: 2.31mg/L Effluent total Grab 2.50mg/L Influent free Grab: 3.00mg/L, Analyzer: 2.91mg/L Reagents - all okay No other issues on site | Nobleton Wells 5 & 6 | 2026-01-21
WEST | January | Reduced both silicate pump max flow setpoints to 120 ml/min based on slightly high turbidity | Nobleton Wells 5 & 6 | 2026-01-26
WEST | January | In to Complete Station Check and to collect bacti sample w11550785 Residuals Effluent free Grab: 2.22mg/L, Analyzer: 2.19mg/L Effluent total Grab 2.50mg/L Influent free Grab: 2.62mg/L, Analyzer: 2.59mg/L Reagents - all okay No other issues on site | Nobleton Wells 5 & 6 | 2026-01-28
WEST | January | In to Complete Station Check Residuals Effluent free Grab: 1.84mg/L, Analyzer: 1.79mg/L Influent free Grab: 1.78mg/L, Analyzer: 1.76mg/L Reagents - changed out effluent free reagents No other issues on site | Nobleton Wells 5 & 6 | 2026-01-30
WEST | January | In to Complete Station Check Residuals Effluent free Grab: 1.40mg/L, Analyzer: 1.41mg/L Influent free Grab: 1.48mg/L, Analyzer: 1.43mg/L Primed both silicate pumps for when well turns back on Reagents - all okay No other issues on site | Nobleton Wells 5 & 6 | 2026-01-19
WEST | January | Complete station check. Enter data into PWQ. Analyzer reagent levels good. Silicate dose calculation improved, lower NaSi pump max flow SPs from 120 to 110ml/min and will monitor for improvement. NTU analyzer had vial clarity fault. Cleaned vial and monitored. No | Nobleton Wells 5 & 6 | 2026-01-26
WEST | January | Completed cylinder change | Nobleton Wells 5 & 6 | 2026-01-29
WEST | January | Collected operational iron sequestration samples | Nobleton Wells 5 & 6 | 2026-01-26
WEST | January | On site for the following NBW56, JHSC Health and Safety Inspection, Nobleton, Well 5/6 (1M NBW56, Turbidimeter Maintenance, Nobleton Well 5/6 (1M) NBW56, Chlorine Analyzer, Maintenance, Nobleton Well 5/6 (1M) NBW56, Chlorine Cylinder Emergency Repair Kit Inspection, Nobleton, Well 5/6 (1M) NBW56, Chlorine Leak Detector, Test, Nobleton, Well 5/6 (1M) NBW56, High/Low Alarm, Test, Nobleton, Well 5/6 (1M) NBW56, Chemical System Inspection - Silicate, Nobleton W5/6 (1M) NBW56, Diesel Generator Test Run, Nobleton, Well 5/6 (1M) Starting hours 257:33 stop 258:42 Starting fuel 960/933 stop fuel950/925 NBW5, Dehumidifier, Cleaning & Inspection, Nobleton Well NBW56, Diesel Fuel Spill Alarm, Test, Nobleton Well 5/6 NBW56, Chemical System Inspection - Chlorine, Nobleton W5/6 (1M) 5/6 (1M) NBW56, Pressure Relief Valve, Inspection, Nobleton Well NBW56, Manual Valve, Exercise, Nobleton Well 5/6 (2M) NBW56, Chlorine Scrubber, Check, Nobleton, Well 5/6 (1M) Contractors on site well still in manual off No other issue on site | Nobleton Wells 5 & 6 | 2026-01-15
WEST | January | -on site to complete station check -well running in manual -well #6 offline and isolated from distribution system -cl2 booster pump # 1 running at 190 psi -chlorinator # 1 68% open dosing 40 ppd, vac = - 80 mbar, DF = 146% -silicate pump #1 running at 48%, 9.64 rpm, 105 psi -checked equipment -reviewed trends -CL17 reagents ok -verified chlorine analyzers: 11:26 - Effluent Analyzer = 1.85 mg/L 11:26 - Effluent grab: Free chlorine = 1.90 mg/L Total chlorine = 2.44 mg/L 11:31 - Influent Analyzer = 2.59 mg/L 11:31 - Influent grab: Free chlorine = 2.64 mg/L -recorded readings in PWQ sheet -completed drawdowns on silicate pumps: -silicate pump #2 max flow = 130 ml/min, adjusted scada setpoint from 120 to 130 ml/min -silicate pump #1 max flow = 80 ml/min, adjusted scada setpoint from 100 to 80 ml/min -based on pump #1 discharge pressure suspect blockage in line, turned off well to clean injection point -found pump #1 injection point check valve plugged, replaced check valve and cleaned injection lance -switched pump #1 discharge line to 5/8 tubing -reinstalled injection point and started well 13:21 - well locked out on lolo influent, started backflushing well 13:27 - stop backflushing, residual recovered to 1.96 mg/L, grabs = 1.80/1.78/1.79 mg/L 13:33 - adjusted influent analyzer to 1.79 mg/L based on average of 3 grabs -started well in manual, no issues with start up -completed drawdown on silicate pump #1: max flow = 123 ml/min, adjusted scada setpoint from 80 to 123 ml/min -stopped well, primed chlorinator #1discharge line and restarted well to test chlorinator - no issues -site back to normal operation | Nobleton Wells 5 & 6 | 2026-01-23
WEST | January | In to Complete Station Check and bactisample w11503161 Residuals Effluent free Grab: 1.92mg/L, Analyzer: 1.94mg/L Total grab 2.48mg/L Influent free Grab: 2.48mg/L, Analyzer: 2.55mg/L Reagents - all okay No new known issues on site | Nobleton Wells 5 & 6 | 2026-01-07
WEST | January | Entry meant for nbw3/7 | Nobleton Wells 5 & 6 | 2026-01-09
WEST | January | In to Complete Station Check Residuals Effluent free Grab: 1.62mg/L, Analyzer: 1.66mg/L Influent free Grab: 1.68mg/L, Analyzer: 1.69mg/L Reagents - all okay No other issues on site | Nobleton Wells 5 & 6 | 2026-01-09
WEST | January | In to Complete Station Check and bacti sample w11522719 and quarterly sample w11476120 Residuals Effluent free Grab: 1.92mg/L, Analyzer: 1.93mg/L Total grab 2.52mg/L Influent free Grab: 2.64mg/L, Analyzer: 2.61mg/L Reagents - all okay No new known issues on site | Nobleton Wells 5 & 6 | 2026-01-14
WEST | January | In to Complete Station Check Residuals Effluent free Grab: 1.44mg/L, Analyzer: 1.47mg/L Influent free Grab: 1.58mg/L, Analyzer: 1.58mg/L Reagents - all okay No other issues on site | Nobleton Wells 5 & 6 | 2026-01-12
WEST | January | Station Check (no issues found) Input data to PWQ 10:50 Verified CL17s (mg/l) Influent: Free Grab 2.66, A 2.62 (new reagents) Effluent: Free Grab 2.11, A 2.14 Total: Grab 2.86 | Nobleton Wells 5 & 6 | 2026-01-02
WEST | January | Silicate top up: Before : 49.7cm, 1230 L After: 80cm, 1982 L | Nobleton Wells 5 & 6 | 2026-01-06
WEST | January | In to Complete Station Check Residuals Effluent free Grab: 1.75mg/L, Analyzer: 1.80mg/L Influent free Grab: 1.66mg/L, Analyzer: 1.66mg/L Reagents - all okay Changed chlorine cylinder 1 from 0-68kg with Joe Williams No other issues on site | Nobleton Wells 5 & 6 | 2026-01-05
CENTRAL | January | On-site for a station and equipment check No issues found Weekly bacti sample taken Analyzers verified all readings and grabs into PWQ sheet Inlet Free@1422 G:0.08 A:0.02mg/L Inlet Total@1426 G:2.64 A:2.69mg/L Outlet Free@1428 G:0.08 A:0.0g/L Outlet Total@1432 G:1.93 A:1.96mg/L | Queensville Elevated Tank | 2026-01-28
CENTRAL | January | On-site for a station and equipment check No issues found. Tools weekly bacti samples and Q1 samples Also took operational samples. Completed analyzer maintenance on both units. Outlet unit has biofilm build up. Will discuss with team lead Inlet Free@1354 G:0.08 A:0.04mg/L Inlet Total@1358 G:2.66 A:2.58mg/L Outlet Free@1400 G:0.04 A:0.06mg/L Outlet Treated@1403 G:1.95 A:1.99mg/L | Queensville Elevated Tank | 2026-01-21
CENTRAL | January | On-site to perform various work orders: -ventilation system inspection, ok -general housekeeping completed -portable generator tested and run -heating system checked -facility outfall inspected -heat trace inspected systems -dechlor puck dispenser cleaned, ok -drain valve exercised | Queensville Elevated Tank | 2026-01-15
CENTRAL | January | On-site to run generator and monitor while power outage cont | Queensville Elevated Tank | 2026-01-15
CENTRAL | January | On-site for a station and equipment check No issues found Took weekly bacti sample while draining along with an operational sample and NDMA sample Verified analyzers and entered all readings and grabs into PWQ sheet Inlet Free@1041 G:0.04 A:0.02mg/L Inlet Total@1044 G:2.50 A:2.51mg/L Outlet Free@1024 G:0.04 A:0.05mg/L Outlet Total@1027 G:2.28 A:2.33mg/L | Queensville Elevated Tank | 2026-01-07
CENTRAL | January | On-site for a station and equipment check No issues found Took weekly bacti sample while draining Verified analyzers and entered all readings and grabs into PWQ sheet Inlet Free@0817 G:0.01 A:0.02mg/L Inlet Total@0820 G:2.78 A2.75mg/L Outlet Free@0825 G:0.04 A:0.06mg/L Outlet Total@0829 G:2.18 A:2.20mg/L | Queensville Elevated Tank | 2026-01-14
CENTRAL | January | On-site to receive bulk NaSi | Queensville Wells No. 1 and 2 | 2026-01-15
CENTRAL | January | On-site for a station and equipment check Site Off Topped up silicate day tanks. Topped up ammonia day tank 2 Cl2 leak during cylinder bank B change with D Moses Unable to locate leak Left cylinders off and will return with parts to fix shortly. | Queensville Wells No. 1 and 2 | 2026-01-23
CENTRAL | January | On-site to receive CL2 cylinders | Queensville Wells No. 1 and 2 | 2026-01-19
CENTRAL | January | On-site for a station and equipment check. No issues found. Well 1 running in manual. Chemical levels and systems ok. Cl2 cylinders ordered. 1 full cylinder in inventory 7 bags of ammonia on-site Created work order W11599696 to have well 1 FCV to waste rebuilt as it?s leaking at the downstream gasket and allowing too much to waste through copper tubing. Adjusted CL2:Ammonia ratio to 3.90 from 4.00 after 3 consecutive 0.0 grabs of FA Operational samples taken Replaced Influent free reagents Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@0951 G:2.90 A:2.99mg/L Effluent Free@0954 G:2.44 A:2.39mg/L Treated Free@0955 G:0.25 A:0.21mg/L Treated Total@1000 G:3.06 A:3.05mg/L Mono-2.86mg/L FA-0.06mg/L TA-0.63mg/L | Queensville Wells No. 1 and 2 | 2026-01-19
CENTRAL | January | On-site for a station and equipment check. Contractors onsite as well. Received cl2 cylinder delivery 18 cylinders and 4 bags of ammonia in inventory Adjusted ammonia pump 2 max flow rate to 210 instead of 200mL/min to affect FA. FA grab before adjustment was 0.09 and 0.12mg/L After adjustment FA grabs were 0.06 and 0.07mg/L Pump 1 grab was 0.06 and 0.06mg/L Topped up ammonia day tank 2 Topped up silicate day tanks Verified analyzers, entered all readings and grabs into PWQ sheet | Queensville Wells No. 1 and 2 | 2026-01-30
CENTRAL | January | On-site for a station and equipment check Chemical levels and systems ok Inventory is 9 cylinders and 6 bags of ammonia Weekly bacti samples taken While onsite contractors used the same outlet as the current temp generator and blew a fuse to said outlet. It caused a generator fault alarm on SCADA I notified them to contact the PM to remedy Topped up ammonia day tank 1 Verified analyzers and entered all readings and grabs into PWQ sheet Influent free@1246 G:2.74 G:2.84mg/L Effluent Free@1258 G:2.56 A:2.57mg/L Treated Free@1311 G:0.23 A:0.21mg/L Treated Total@1315 G:3.24 A:3.36mg/L Mono-2.79 FA-0.08 TA-0.64mg/L | Queensville Wells No. 1 and 2 | 2026-01-28
CENTRAL | January | On-site with D Moses for a station and equipment check Well 2 running No issues found Chemical levels and systems ok Inventory is 0 cylinders and 2 bags of ammonia, requested an order of 12 cylinders via email. Topped up NaSi day tanks. Topped up oil for well 1. Changed effluent analyzer from 2.48 to 2.62mg/L based on an average of 3 grabs, 2.66, 2.64 & 2.60mg/L Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@0956 G:2.82 A:2.87mg/L Treated Free@1000 G:0.18 A:0.21mg/L Treated Total@1005 G:3.56 A:3.50mg/L Mono-2.57 FA-0.04 TA-0.55mg/L | Queensville Wells No. 1 and 2 | 2026-01-26
CENTRAL | January | -on site 0900 to witness pump 1 running to system with Will. We started the pump at 915 and ran for one hour noticed a speed deviation alarm. I adjusted the minimum speed on the Vfd to be in line with the speed set point. Cleared the deviation alarm and witnessed no other issues during the run. I then locked the motor out 1030 redid the connections in the motor junction box and reenergized placed motor in auto and cleared alarms. Let Will know I was done. Under direction of oic. | Queensville Wells No. 1 and 2 | 2026-01-19
CENTRAL | January | On-site for a station and equipment check while site in manual on No issues found Contractors onsite working on generator Chemical levels and systems ok Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@1001 G:2.92 A:2.8mg/L Effluent Free@1010 G:2.64 A:2.59mg/L Treated Free@1016 G:0.26 A:0.23mg/L Treated Total@1020 G:3.20 A:3.22mg/L Mono-2.67mg/L FA-0.08mg/L TA-0.60mg/L | Queensville Wells No. 1 and 2 | 2026-01-16
CENTRAL | January | -Finished the following work orders *Chemical system inspection *Turbidimeter maintenance *Surge valve inspection *Dechor puck dispenser inspection *Flow control valve inspection | Queensville Wells No. 1 and 2 | 2026-01-22
CENTRAL | January | Informed ROC (Angelica C) of ongoings Complete Maximo workorders Diesel test run, temporary generator onsite - all ok Contractors onsite Receive 9 Full chlorine cylinders, return 9 empty Ops normal | Queensville Wells No. 1 and 2 | 2026-01-27
CENTRAL | January | On site to complete chlorine cylinder change for bank A with Joe D. | Queensville Wells No. 1 and 2 | 2026-01-20
CENTRAL | January | On-site for a station and equipment check Contractors are onsite also. Topped up ammonia day tank 1 Chemical levels and systems ok Inventory of 7 cl2 cylinders and 4 bags of ammonia NTU reading higher again, cleaned vial and will monitor Took weekly bacti samples and Q1 samples Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@1148 G:2.82 A:2.85mg/L Effluent Free@1150 G:2.46 A:2.47mg/L Treated Free@1152 G:0.19 A:0.20mg/L Treated Total@1153 G:3.08 A: 3.11mg/L Mono-2.63 FA-0.02 TA-0.54 | Queensville Wells No. 1 and 2 | 2026-01-21
CENTRAL | January | Onsite to change cylinders with will Mather?s. Minor chlorine leak detected around 09:00. Will notified roc. Purged chlorine line, replaced right chlorine pigtails. Found cylinder to be malfunctioned. Removed and replaced. Reset halogen shut off systems, reopened all cylinders in service. No leaks remaining. Notified ROC around 14:50. | Queensville Wells No. 1 and 2 | 2026-01-23
CENTRAL | January | Changed chlorine cylinder bank A with Ben H. | Queensville Wells No. 1 and 2 | 2026-01-09
CENTRAL | January | On site to install new motor on Queensville w1. Mechanics installed new motor I wired the motor and I called roc (1030) to warn them of alarms from our test. We test ran the motor to confirm the direction. Mechanical recoupled the motor to the well pump. I then found some parameters needed to be changed on the drive. Started that process was not confident on the minimum speed had pcs provide that setting and will return to test well with ops. Left well locked out for the evening. Under direction of oic. | Queensville Wells No. 1 and 2 | 2026-01-07
CENTRAL | January | On-site for a station and equipment check No new issues found Well 1 still OOS Tapped up ammonia day tank 2 Chemical levels and systems ok Took weekly bacti sample W11503273 Verified analyzers and entered all readings into PWQ sheet Influent Free@0850 G:2.60 A:2.65mg/L Effluent Free @0858 G:2.46 A:2.46mg/L Treated Free@0900 G:0.16 A:0.19mg/L Treated Total@0904 G:2.92 A:2.89mg/L | Queensville Wells No. 1 and 2 | 2026-01-07
CENTRAL | January | #11516767 scrubber media samples #11517196, 17517204 outfall #11517471,11517485 deep well #1151755551 jhs Chlorine Cylinder change (b side) with Alex #11517253 CL17s maint. Verified (mg/L) 9:04 Influent: Free Grab 2.66, A 2.73 Effluent: Free Grab 1.08, 1.04 (new reagents) 9:53 Treated: Free Grab 0.12, A 0.10 Total: Grab 2.62, A 2.56 10:20 Well #1 Local on (verified valving to waste with TZ 14:00 Well #2 interlocked on Hi Effluent Verified Analyzer (Grabs 3.00, A 3.24) 14:15 Well 2 auto on | Queensville Wells No. 1 and 2 | 2026-01-13
CENTRAL | January | On-site for a station and equipment check No new issues found Operational samples taken Well 1 still OOS Troubleshooting ammonia pump 1. Still OOS Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@1317 G:2.92 A:2.90mg/L Effluent Free@1318 G:2.70 A:2.76mg/L Treated Free@1320 G:0.21 A:0.22mg/L Treated Total@1325 G:3.14 A:3.22mg/L Mono-2.79mg/L FA-0.05mg/L TA-0.58mg/L | Queensville Wells No. 1 and 2 | 2026-01-12
CENTRAL | January | On-site for a station and equipment check Well 1 still OOS. Ran for 1 hour and collected all weekly bacti samples. Rebuilt ammonia pump 1. Draw down completed. Adjust max dosage from 205mL/min to 218mL/min. Tested. Ran very well back in service Topped ammonia day tank 1 and both NaSi Verified analyzers and entered all readings and grabs into PWQ sheet | Queensville Wells No. 1 and 2 | 2026-01-14
CENTRAL | January | -on site with Joe W to assist with running well one on the Vfd so we can grab a sample. Once completed left the lock off the well and turned starter off when well is ready to run back to system I?ll have to return to complete test. Under direction of oic. | Queensville Wells No. 1 and 2 | 2026-01-13
CENTRAL | January | On-site for station check. Topped up NaSi day tanks. Replaced Treated Free Cl CL17 analyzer reagents. Grab/analyzer results as follows (mg/L): Influent Free Cl (14:31): G: 2.72 A: 2.77 Effluent Free Cl (14:34): G: 2.80 A: 2.82 Treated Free Cl (14:37): G: 0.18 A: 0.22 Treated Total Cl (14:35): G: 3.40 A: 3.26 Site in running in auto/D1. Alex Bell (OIT/Under direction of OIC) on-site for ammonia tank 1 rebatch (ammonia tank 1 valve man/closed, Alex will return to auto before leaving site). No new issues found while on-site, Ammonia P1 remains man/off. | Queensville Wells No. 1 and 2 | 2026-01-09
CENTRAL | January | Drained ammonia tank 1 after prior overfill. Refilled and rebatched the tank. Returned ammonia tank 1 valve to auto on SCADA. | Queensville Wells No. 1 and 2 | 2026-01-09
CENTRAL | January | -on site to remove motor for well 1. Isolated pump from system to run to waste. Under direction of oic | Queensville Wells No. 1 and 2 | 2026-01-05
CENTRAL | January | On-site for cylinder change with Donald Moses and station check. Changed Cl2 bank B with Donald Moses. Batched ammonia tank 1 and topped up NaSi day tanks. Verified CL17 analyzers. Entered station readings into shared PD excel file. Will monitor W2 flow (see previous e-log entry by Jerry Zhang). No new issues found while on-site. W1 remains LOTO/OOS for motor issues, will need to be sampled via raw to waste prior to returning Well online/normal operation. | Queensville Wells No. 1 and 2 | 2026-01-02
CENTRAL | January | On-site for a station and equipment check Well 1 still OOS. Adjusted well 2 flow to 69. 4L/s Took ammonia pump 1 OOS due to dosing issues, causing high free CL2. Will troubleshoot pump when time allows Topped up silicate day tanks. Verified analyzers and adjusted Effluent Free analyzer based on grabs of 2.82, 2.78 and 2.78mg/L previous reading was 3.02 adjusted to 2.79mg/L Influent Free@1027 G:2.92 A2.94mg/L Treated Free@1103 G:0.20 A:0.23mg/L Treated Total@1105 G:3.28 A:3.33mg/L FA is a little high @0.10mg/L. Will adjust once troubleshooting of ammonia pump 1 is completed | Queensville Wells No. 1 and 2 | 2026-01-05
CENTRAL | January | Removed old motor and extended the wires for the motor. Left pump locked out. Under direction of oic | Queensville Wells No. 1 and 2 | 2026-01-05
CENTRAL | January | On-site for a station and equipment check No issues found Well 3 running in manual Chemical levels and systems ok Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@1142 G:2.62 A:2.66mg/L Effluent Free@1145 G:2.32 A:2.35mg/L Treated Free@1146 G:0.09 A:0.13mg/L Treated Total@1151 G:2.90 A:2.9mg/L Mono-2.22mg/L FA-0.06mg/L TA-0.50mg/L | Queensville Wells No. 3 and 4 | 2026-01-16
CENTRAL | January | On-site to run well 4 to waste for raw bacti sample after piping /VFD installation Placed all dosing pumps back into auto. Completed drawdown tests on both ammonia pumps | Queensville Wells No. 3 and 4 | 2026-01-29
CENTRAL | January | On site to continue installation of well 4 VFD. Assisted ops to run well in local mode for sampling purposes. Also worked on cabling for ethernet connection to well 3. Well 3 back in auto with no outstanding alarms. Well for still off-line awaiting scada integration. | Queensville Wells No. 3 and 4 | 2026-01-29
CENTRAL | January | Check water heater info Re and re water heater | Queensville Wells No. 3 and 4 | 2026-01-23
CENTRAL | January | On-site for a station and equipment check Charged new spool piece as installed by Maintenance, leak at tap/weld, notified Zimmerman-Jones Performed analyzer maintenance. Unable to perform it on treated free analyzer as I was unable to scroll through the menu, work order created for instrumentation repair Chemical levels and systems ok Inventory of 15 cylinders and 4 bags of ammonia on-site Took weekly bacti samples with exception of well 4 being offline Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@1023 G:2.56 A:2.68mg/L Effluent Free@1027 G:2.66 A:2.60mg/L Treated Free@1030 G:0.18 A:0.15mg/L Treated Total@1037 G:3.18 A:3.18mg/L Mono-2.55mg/L FA-0.07mg/L TA-0.58mg/L @1045 | Queensville Wells No. 3 and 4 | 2026-01-28
CENTRAL | January | Site was in manual off due to waste valve failure to close interlock. Caught by ROC A Button. CMU 5 W11606521 created. Cleaned filters, exercised pilots, removed lines and flushed. Put back into service. Valve closed when required by system. Weekly bacti samples taken along with Q1 samples. Chemical systems and levels ok, including 15 cl2 cylinders and 4 bags of ammonia on-site Topped up well pump 3 oil Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@0900 G:2.66 A:2.59mg/L Effluent Free@0905 G:2.34 A:2.28mg/L Treated Free@0907 G:0.15 A:0.12mg/L Treated Total@0911 G:2.90 A:2.91mg/L Mono-2.39 FA-0.05 TA-0.52 | Queensville Wells No. 3 and 4 | 2026-01-21
CENTRAL | January | On-site with D Moses Well 3 running Station and equipment check. No issues found. D Moses Valved and locked out well 4 for check valve and VFD upgrades Well 4 left in manual off Chemical levels and systems ok Inventory of 15 cylinders and 4 bags of ammonia Operational sample taken Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@0814 G:2.78 A:2.79mg/L Effluent Free@0818 G:2.60 A:2.54mg/L Treated Free@0822 G:0.08 A:0.13mg/L Treated Total@0827 G:3.06 A:3.15mg/L Mono-2.49mg/L FA-0.06mg/L TA-0.56mg/L | Queensville Wells No. 3 and 4 | 2026-01-26
CENTRAL | January | On-site for a station and equipment check No issues found. Well 3 running in manual Topped up well 4 oil Changed treated total reagents Topped up ammonia day tank 2 15 full CL2 cylinders on-site 4 bags ammonia in inventory Operational sample taken Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@1323 G:2.88 A:2.76mg/L Effluent Free@1325 G:2.60 A:2.69mg/L Treated Free@1329 G:0.16 A:0.14mg/L Treated Total@1333 G:3.36 A:3.37mg/L Mono-2.59mg/L FA-0.08mg/L TA-0.59mg/L | Queensville Wells No. 3 and 4 | 2026-01-19
CENTRAL | January | Chris Iliohan Tyler Smith Erin H Dan B and Kyle R Into remove flow control valve for check valve and VFD install work in progress | Queensville Wells No. 3 and 4 | 2026-01-26
CENTRAL | January | On site to continue well 4 VFD upgrade work. Ran well r for initial VFD testing with well valved to waste. After approximately 15 minute waste run test, realized that chemical pumps were in automatic mode and because the wasting water ran past the flow meter, that the chemical pumps dosed as per the flow meter, even though we were hard valved to waste and there was no flow into the system. Communicated this to the remote operation center and operations team lead. Station operator on site to assist with back flushing as a response. | Queensville Wells No. 3 and 4 | 2026-01-28
CENTRAL | January | On-site to backfliush after accidental dosage while running to waste. Used sodium thio and flushed for approximately 4 mins. | Queensville Wells No. 3 and 4 | 2026-01-28
CENTRAL | January | On-site for a station and equipment check No issues found. Chemical levels and systems ok 15 cylinders and 4 bags of ammonia in inventory Verified analyzers, entered all readings and grabs into PWQ sheet Influent Free@1225 G:2.64 A:2.72mg/L Effluent Free@1227 G:0.88 A:0.90mg/L Treated Free@1229 G:0.03 A:0.04mg/L Treated Total@1231 G:2.30 A:2.28mg/L | Queensville Wells No. 3 and 4 | 2026-01-23
CENTRAL | January | On site to continue off-line work on well 4 upgrade project. | Queensville Wells No. 3 and 4 | 2026-01-15
CENTRAL | January | On-site to receive bulk NaSi order. | Queensville Wells No. 3 and 4 | 2026-01-15
CENTRAL | January | Onsite for station check Recordings in PD sheet Creating work order for isolation valve on surge line that has small leak. Changed influent cl17 reagents Station ok | Queensville Wells No. 3 and 4 | 2026-01-09
CENTRAL | January | Reviewed elog entries and returned W3/4 to remote/auto via remote SCADA. W3 shutdown as duty not called for. | Queensville Wells No. 3 and 4 | 2026-01-14
CENTRAL | January | On-site for a station and equipment check No issues found Topped NaSi tanks Took weekly bacti samples Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@1442 G:2.72 A:2.66mg/L Effluent Free@1444 G:2.76 A:2.71mg/L Treated Free@1447 G:0.10 A:0.15mg/L Treated Total@1452 G:3.46 A:3.39mg/L Mono-2.57mg/L FA-0.07mg/L TA-0.58mg/L | Queensville Wells No. 3 and 4 | 2026-01-14
CENTRAL | January | Work orders #11507631 Silicate (cleaned injection pts and draw down (no change)) #11507655 cl2 system #11505616 cl2 leak #11507671 Ammonia system (draw down, no changes) | Queensville Wells No. 3 and 4 | 2026-01-14
CENTRAL | January | Changed chlorine cylinder bank B with Will M. | Queensville Wells No. 3 and 4 | 2026-01-08
CENTRAL | January | On-site for various PM work orders; Generator testing delayed due to inability to start. D Boate on-site to help trouble shoot issues. Found that the batteries needed to be replaced. Began test under load: Time start @1215 704.45hrs End@1317 Fuel: Start 1174L End: 1140L Volts 601 HZ 60.0 Oil Temp 160F Coolant Temp 161F Oil pressure 90psi Flow control valve exercised well 3, well 4 not due to maintenance Deep well exhaust inspections completed Dechlor dispenser inspected Outfall inspections completed Cylinder bank 2 changed with A Bell | Queensville Wells No. 3 and 4 | 2026-01-08
CENTRAL | January | On-site for a station and equipment check No issues found Well 4 to running in manual at time of arrival to expedite for weekly bacti samples to be taken Well placed back into auto after sampling Chemical levels and systems ok Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@1251 G:2.70 A:2.72mg/L Effluent Free@1253 G:2.56 A:2.55mg/L Treated Free@1255 G:0.09 A:0.14mg/L Treated Total@1257 G:3.18 A:3.26mg/L | Queensville Wells No. 3 and 4 | 2026-01-07
CENTRAL | January | On-site for a station and equipment check No issues found Operational samples taken Chemical levels and systems ok. JHSC inspection completed NTU analyzer maintenance completed Surge/Pressue Relief valve maintenance completed Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@1033 G:2.60 A:2.69mg/L Effluent Free@1036 G:2.38 A:2.34mg/L Treated Free@1039 G:0.09 A:0.12mg/L Treated Total@1042 G:3.04 A:2.96mg/L | Queensville Wells No. 3 and 4 | 2026-01-12
CENTRAL | January | Onsite for station check. 08:33 Well 3 and 4 in standby. Chlorinator 1 OOS awating rebuild. Verified analyzers(mg/l): 08:45 verified Influent free grab: 2.58. CL17: 2.68. 08:55 Effluent free grab: 0.53 CL17: 0.58 08:55 Treated free grab: 0.03. CL17: 0.04. 08:57. Treated total grab: 2.42 CL17: 2.43. Topped up well 4 oil pot from 2/3 full. No other issues on site. | Queensville Wells No. 3 and 4 | 2026-01-02
CENTRAL | January | On-site for a station and equipment check. No new issues found. Wells in standby upon arrival Put well 4 into manual on to take grabs after clearing the contact tank. Operational sample taken Chemical levels and systems ok. Verified analyzers and entered all readings and grabs into PWQ sheet Influent Free@1326 G:3.06 A:3.15mg/L Effluent Free@1330 G:1.73 A:1.68mg/L Treated Free@1331 G:0.14 A:0.09mg/L Treated Total@1334 G:2.38 A:2.27mg/L Mono-2.19mg/L FA-0.05mg/L TA-0.48mg/L | Queensville Wells No. 3 and 4 | 2026-01-05
WEST | January | Restarted the VNPS Local SCADA server. Notified the Remote Operations Center and the OIC. | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2026-01-22
WEST | January | -on site to complete station check -checked trends: all ok -entered reading in PWQ -verified pre analyzer 11:05 -analyzer free: 0.05mg/l grab: 0.06mg/l -analyzer total: 1.60mg/l grab: 1.61mg/l -reagents all ok -verified post analyzer 11:20 -analyzer free: 0.05mg/l grab: 0.08mg/l -analyzer total: 2.18mg/l grab: 2.19mg/l -reagents all ok -verified chemscan: all ok -reagents all ok | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2026-01-30
WEST | January | -on site to complete following work orders -chemscan cleaning -min/max -0.011/0.003 -parameter 230 & 248 - 2734/3567 -verified pre 12:30 -analyzer mono: 1.36mg/l grab: 1.35mg/l -analyzer free nh: 0.08mg/l grab: 0.08mg/l -analyzer total my: 0.35mg/l grab: 0.35mg/l -verified post 12:49 -analyzer mono: 1.61mg/l grab: 1.61mg/l -analyzer free nh: 0.05mg/l grab: 0.08mg/l -analyzer total nh: 0.42mg/l grab: 0.39mg/l -reagents all ok -JHSC inspection: all ok -chlorine leak test: took several test to get all halogens working -scrubber inspection: all ok -completed chlorine inspection: all ok -Will M on site at 12:30 - changed cylinders 53 kg - 121kg -no other issues | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2026-01-20
WEST | January | -reset sump pit alarms in both VNPS and VNPSCD | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2026-01-16
WEST | January | -on site to complete station check and weekly bacti W11538514 -checked trends: all ok -entered reading in PWQ: -to chlorine grab and sample from north cell 10:45 -free cl: 0.04mg/l -total cl: 1.99mg/l -west cell 10:50 -free cl: 0.05mg/l -total cl: 2.02mg/l -south cell 10:45 -free cl: 0.05mg/l -total cl: 2.05mg/l -equipment all ok -complete re-chlor station check -verified pre analyzer 11:25 -analyzer free: 0.05mg/l grab: 0.06mg/l -analyzer total: 1.56mg/l grab: 1.55mg/l -reagents all ok -verified post analyzer 11:35 -analyzer free: 0.04mg/l grab: 0.05mg/l -analyzer total: 1.77mg/l grab:1.77mg/l -reagents all ok -verified chemscan -reagents all ok | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2026-01-21
WEST | January | -on site for station check -checked trends: all ok -took readings in PWQ -requested BVPS activated -entered readings in PWQ: -verified pre-analyzer 12:30 -analyzer free: 0.04mg/l grab: 0.04mg/l -analyzer total: 1.48mg/l grab: 1.53mg/l - adjusted -topped up KI reagent -verified post analyzer 12:40 -analyzer free: 0.16mg/l grab: 0.08mg/l - adjusted -analyzer total: 2.22mg/l grab: 2.18mg/l -topped up Ki reagent -verified chemscan -reagents all ok | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2026-01-26
WEST | January | -on site for station check -checked trends: all ok -entered readings in PWQ: all ok -verified pre analyzer 10:55 -analyzer free: 0.04mg/l grab:0.07mg/l -analyzer total: 1.56mg/l grab: -reagents all ok -verified post analyzer 11:05 -analyzer free: 0.05mg/l grab: 0.03mg/l -analyzer total: 2.14mg/l grab: 2.10mg/l -reagents all ok -verified chemscan: all ok -reagents all ok -equipment all ok | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2026-01-16
WEST | January | -on site to complete station check -checked trends: all ok -entered reading in PWQ: all ok -verified pre analyzer 12:10 -analyzer free: 0.04mg/l grab: 0.07mg/l -analyzer total: 1.44mg/l grab: 1.43mg/l -reagents all ok -verified post analyzer 12:20 -analyzer free:0.05mg/l grab:0.04mg/l -analyzer total: 2.21mg/l grab:2.20mg/l -reagents all ok -verified chemscan: all ok -reagents all ok -topped up ammonia tank 1 15- 75cm - | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2026-01-19
WEST | January | -on site to complete station check -checked trends: all ok -entered readings in PWQ: all ok -verified pre analyzer 11:00 -analyzer free: 0.05mg/l grab: 0.06mg/l -analyzer total: 1.53mg/l grab: 1.54mg/l -reagents all ok -verified post analyzer 11:15 -analyzer free: 0.03mg/l grab: 0.09mg/l - adjusted -analyzer total: 1.59mg/l grab:1.57mg/l -reagents all ok -verified chemscan -topped up green and grey reagent -requested BVPS to activate - re-verified post free 12:00 - 0.16mg/l - 0.11mg/l - adjusted -equipment all ok | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2026-01-23
WEST | January | -on site for deplox chlorine maintenance -reservoir/flow/pressure all ok -topped up reagents -verified pre analyzer 10:55 -analyzer free: 0.05mg/l grab:0.06mg/l -analyzer total: 1.59mg/l grab: 1.56mg/l -verified post analyzer 11:00 -analyzer free:0.03mg/l grab: 0.05mg/l -analyzer total:1.60mg/l grab: 1.58mg/l -completed drain valve exercise in reservoir -cleaned lower level of VNPS | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2026-01-27
WEST | January | -on site to complete station check and weekly bacti W -checked trends: -entered reading in PWQ: -took sample and chlorine grab of north cell 10:20 -free cl: 0.09mg/l -total cl: 2.00mg/l -west cell 10:25 -free cl: 0.04mg/l -total cl: 2.02mg/l -south cell 10:30 -free cl: 0.11mg/l -total cl: 2.06mg/l Complete station check of rechlor building -checked trends: all ok -entered readings in PWQ: all ok -verified pre- analyzer 11:00 -analyzer free: 0.05mg/l grab: 0.03mg/l -analyzer total: 1.70mg/l grab: 1.68mg/l -reagents all ok -verified post - analyzer 11:10 -analyzer free: 0.04mg/l grab: 0.04mg/l -analyzer total: 2.06mg/l grab: 2.09mg/l -reagents all ok -verified chemscan: all ok -reagents all ol -equipment all ok | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2026-01-28
WEST | January | -on site for station check -checked trends: all ok -entered readings in PWQ: all ok -verified pre analyzer 12:20 -analyzer free: 0.05mg/l grab: 0.07mg/l -analyzer total: 1.55mg/l grab: 1.56mg/l -reagents all ok -verified post analyzer 12:30 -analyzer free: 0.04mg/l grab: 0.04mg/l -analyzer total: 1.84mg/l grab: 1.82mg/l -reagents all ok -verified chemscan: all ok -reagents all ok -equipment all ok | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2026-01-14
WEST | January | Check trends, all good Enter readings into pwq Refilled tank 2, 15cm - 75cm Verified pre analyzer 12:40, free 0.05mg/l grab 0.03 mg/l, total 1.60 mg/l grab 1.62 mg/l Verified post analyzer12:50, free 0.04 mg/l grab 0.05 mg/l, total 1.90 mg/l grab 1.92 mg/l Reagents ok Verified chem scan ok | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2026-01-12
WEST | January | -on site for station check -checked trends: all ok -entered readings in PWQ: all ok -verified pre analyzer 09:45 -analyzer free: 0.04mg/l grab:0.03mg/l -analyzer total: 1.55mg/l grab: 1.51mg/l -reagents all ok -verified post analyzer 10:25 -analyzer free: 0.06mg/l grab: 0.04mg/l -analyzer total: 2.46mg/l grab: 2.44mg/l -reagents all ok | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2026-01-09
WEST | January | -on site for station check, weekly bacti W11522897, and Q1 W11476204 -checked trends: all ok -entered readings in PWQ -took samples and chlorine grab of north cell 10:15 -free cl: 0.06mg/l -total cl: 1.96mg/l -cell 3 grab 10:20 -free cl: 0.07mg/l -total cl: 1.97mg/l -cell 2 10:25 -free cl: 0.10mg/l -total cl:2.01mg/l | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2026-01-14
WEST | January | -on site to complete station of reservoir and rechlor building -collected weekly bacti W11503497 and NDMA W11476824 -checked trends -entered reading in PWQ: all ok -reset sump pumps in dechlor and PS -took chlorine grab of north cell (1) 10:45 -free cl: 0.04mg/l -total cl: 1.92mg/l -took chlorine grab cell 3 10:50 -free: 0.03mg/l -total: 1.93mg/l -took chlorine grab cell 2 10:55 -free cl: 0.10mg/l -total cl: 2.04mg/l -verified pre-injection analyzer 11:55 -analyzer free: 0.01mg/l grab: 0.03mg/l -analyzer total: 1.48mg/l grab: 1.44mg/l -reagents all ok -verified post injection analyzer 12:00 -analyzer free: 0.05mg/l grab: 0.07mg/l -analyzer total: 2.08mg/l grab: 2.11mg/l -reagents all ok -chemscan reagents all ok -adjust post mono - 1.77 - 1.88mg/l (-0.1 - 0.01) -topped up ammonia tank 1 - 15- 75cm | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2026-01-07
WEST | January | on site from 10:30 to 11:30 and changed cylinders with T. Hudson. | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2026-01-06
WEST | January | -on site for station check -checked trends: all ok -took readings in PWQ: all ok -verified pre-analyzer 12:15 -analyzer free: 0.01mg/l grab: 0.02mg/l -analyzer total: 1.48mg/l grab: 1.44mg/l -reagents all ok -verified post analyzer 12:25 -analyzer free: 0.05mg/l grab: 0.07mg/l -analyzer total: 2.00mg/l grab: 1.90mg/l - adjusted -reagents all ok -verified chemscan - topped up green reagents - | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2026-01-05
WEST | January | On site for station check Rechlor Pre inj (mg/L) Fcl Analyzer: 0.02; Grab: 0.05 TCL Analyzer: 1.51; Grab: 1.58 Fa Analyzer: 0.08; Grab: 0.07 Ta Analyzer: 0.35; Grab: 0.38 Mcl Analyzer: 1.31; Grab: 1.32 Nitrite: 0.000mg/L Post inj Fcl Analyzer: 0.04; Grab: 0.05 TCL Analyzer: 1.64; Grab: 1.62 Fa Analyzer: 0.07; Grab: 0.06 Ta Analyzer: 0.42; Grab: 0.41 Mcl Analyzer: 1.35; Grab: 1.37 Nitrite: 0.000mg/L | South Richmond Hill Teston Reservoir & Rechlorination Facility | 2026-01-02
WEST | January | -on site to complete station check -checked trends: all ok -entered reading in PWQ: all ok -took chlorine grab 12:40 -free cl: 0.07mg/l -total cl: 1.73mg/l -equipment all ok | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2026-01-16
WEST | January | -on site for station check -checked trends: all ok -entered reading in PWQ: all ok -took chlorine gra. 14:05 -free cl: 0.09mg/l -total cl: 1.43mg/l - equipment all ok | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2026-01-26
WEST | January | -on site to complete station check and weekly bacti W11538514 -checked trends: all ok -entered reading PWQ: all ok -took chlorine grab and sample west cell 13:20 -free cl: 0.06mg/l -total cl: 1.32mg/l -east cell grab 13:25 -free cl: 0.09mg/l -total cl: 1.28mg/l -equipment all ok | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2026-01-21
WEST | January | -remotely test pump 1,2,3 -on site mechanic Chris I reported cavitation -pumps will be man/off | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2026-01-23
WEST | January | Chris Iliohan Tyler Smith Dan Boate complete installation of pump 3 ran pump. Pump has cavitation same compared to pump 1 Pump in auto back to active duty | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2026-01-22
WEST | January | -on site to complete station check -checked trends: all ok -entered readings in PWQ: all ok -too chlorine grab 09:15 -free cl: 0.08mg/l -total cl: 1.72mg/l -equipment all ok -heating all ok | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2026-01-23
WEST | January | -on site for station check and collect weekly bacti W -checked trends: all ok -entered reading in PWQ: all ok -took chlorine grab east cell 13:00 -free cl: 0.04mg/l -total cl: 1.33mg/l -took grab 13:05 -free cl: 0.04mg/l -total cl: 1.34mg/l -equipment all ok | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2026-01-28
WEST | January | -on site to complete station check -checked trends: all ok -entered reading in PWQ: all ok -took chlorine grab 14:05 -free cl: 0.06mg/l -total cl: 1.77mg/l -replaced RHPSWA eyewash | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2026-01-19
WEST | January | -on site for station check -checked trends: all ok -entered readings in PWQ: all ok -took chlorine grab 09:30 -free cl: 0.04mg/l -total cl: 1.63mg/l -equipment all ok | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2026-01-30
WEST | January | -on site to remove operator lock on pump 3 | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2026-01-22
WEST | January | -on site for station check and weekly bacti W11503497 -checked trends: all ok -entered reading in PWQ -took grab and sample from west cell 13:45 -free cl: 0.07mg/l -total cl: 1.34mg/l -east cell grab 13:50 -free cl: 0.05mg/l -total cl: 1.30mg/l -equipment all ok | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2026-01-07
WEST | January | -on site for station check, weekly bacti W11522897 and Q2 W11476190 -checked trends: all ok -entered reading in PWQ: all ok -took grab and samples from east cell 14:00 -free cl:0.08mg/l -total cl: 1.34mg/l -west cell grab 14:00 -free cl: 0.06mg/l -total cl: 1.38mg/l -equipment all ok | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2026-01-14
WEST | January | Onsite for station check Chlorine Grab free 0.05 @ 1:22 Grab total 1.73 @ 1:24 Trends ok Took readings into pwq Equipment ok | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2026-01-12
WEST | January | Pumping Station Check Chlorine Grab (mg/L): Free: 0.05 Total: 1.65 No issues on site | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2026-01-02
WEST | January | -on site for PS station check -checked trends: all ok -entered readings in PWQ: all ok -took chlorine grab 10:40 -free cl: 0.02mg/l -total cl: 1.58mg/l -equipment all ok -check reservoir exterior vents and hatches: all ok | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2026-01-08
WEST | January | -on site for station check -checked trends: all ok -entered readings in PWQ: -took chlorine grab 13:55 -free cl: 0.05mg/l -total cl: 1.72mg/l -equipment all ok | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2026-01-05
WEST | January | -on site to complete following work orders -JHSC inspection: all ok -station flood alarm in RS/PS: all ok -pump run and inspection- ran pump 1&2 all ok -RS/PS sump pump inspection: all ok -temp alarm: all ok -PS manual valve exercise: all ok -PS PRV exercise: all ok -RS dehumidifier inspection: all ok -RS actuated valve exercise: all ok - | Richmond Hill (North) Woodland Acres Pumping Station & Reservoir | 2026-01-06
CENTRAL | January | Check solenoids on altitude valve | Richmond Hill Bloomington Elevated Tank | 2026-01-16
CENTRAL | January | #11524657 CL17 maint Verified (mg/L) Inlet: Total Grab 1.70, A 1.76 (adjusted to match grabs) Outlet: Total Grab 1.70, A 1.71 #11524639 air valve #11524714 hi/lo level #11524722 act. valve #11524857 jhs #11525032 heat trace #11525065 circ. pump #11525089 prv #115525187 low temp #11525198 ventilation (vent fan manual switched to manual off in MCC rm) #11595922 created for washroom unit heater no working | Richmond Hill Bloomington Elevated Tank | 2026-01-16
CENTRAL | January | Responding to FCV deviation alarm. Opened valve to atmosphere to bleed water off top of valve and closed normally closed downstream ball valve off of valve body, cleared alarms. No other new issues found. | Richmond Hill Bloomington Elevated Tank | 2026-01-20
CENTRAL | January | On-site for station and sampling. MBHP - W11550813. 19:32 Tower level 66% and draining at 96 l/s. 09:35 Verified outlet analyzer and collected sample. Free chlorine grab: 0.07 Total chlorine grab: 1.75. analyzer: 1.75 Free ammonia: 0.07 Total ammonia: 0.37. Monochloramine: 1.50. Nitrite: 0.005. Temperature: 3.9 Celsius. 10:11 Verified inlet analyzer (mg/l): Free chlorine grab: 0.09. Total chlorine grab: 1.79. Analyzer: 1.83. Replaced analyzer reagents. Recorded readings into PD sheets. Station and equipment: No issues identified. | Richmond Hill Bloomington Elevated Tank | 2026-01-28
CENTRAL | January | Station Check (no issues found) Input data to PWQ Verified CL17s (mg/l) 14:10 Inlet: Free: Grab 0.08 Total: Grab 1.86, A 1.88 13:45 Outlet: Free: Grab 0.08 Total: Grab 1.71, A 1.71 14:05 #11538378, 11476232, & operational samples | Richmond Hill Bloomington Elevated Tank | 2026-01-21
CENTRAL | January | Flow valve repairs Installed new solenoid valves ball valves flood and put back in service | Richmond Hill Bloomington Elevated Tank | 2026-01-20
CENTRAL | January | On-site for station and sampling. COC W11503361. 10:10. Tower level 76% and draining 72 l/s. 10:10 Verified inlet analyzer (mg/l): Free chlorine grab: 0.02. Total chlorine grab: 1.82. Total chlorine analyzer: 1.88. 10:25. Verified outlet analyzer and collected sample. Free chlorine grab: 0.11 Total chlorine grab: 1.71 Total chlorine analyzer: 1.71. Free ammonia: 0.08. Total ammonia: 0.37. Monochloramine: 1.47. Nitrite: 0.001. Temperature: 6.5 Celsius. Recorded readings into PD sheets. Station and equipment: No issues identified. | Richmond Hill Bloomington Elevated Tank | 2026-01-07
CENTRAL | January | On-site for station and sampling. COC W11522747. 13:37 Deactivated PD9 duty. 13:45. Tower level 65% and draining at 54 l/s. 13:45 Verified inlet analyzer (mg/l): Free chlorine grab: 0.02. Total chlorine grab: 1.82. Total chlorine analyzer: 1.85. 13:50 Verified outlet analyzer and collected sample. Free chlorine grab: 0.02 Total chlorine grab: 1.69 Total chlorine analyzer: 1.69. Free ammonia: 0.09 Total ammonia: 0.39. Monochloramine: 1.52. Nitrite: 0.003. Temperature: 7.2 Celsius. Recorded readings into PD sheets. Station and equipment: No issues identified. | Richmond Hill Bloomington Elevated Tank | 2026-01-14
CENTRAL | January | On site to collect sample and verify analyzers. 09:40 draining at 150 l/s. Tower level 58%. 09:42 outlet free grab: 0.05 mg/l Total grab: 1.77/1.73/1.72 (average 1.74). analyzer: 1.86. Adjusted to match grabs. Collected sample. 09:53 inlet total grab: 1.81. Analyzer 1.88. No other issues found. | Richmond Hill Coon's Elevated Tank | 2026-01-29
CENTRAL | January | On-site for station check and sampling. MBHP - W11550813. 13:25 deactivated PD9 duty. 13:33 Tower level 63% and draining at 23 l/s. Replaced cl17 analyzer reagents. Pocket colorimeter faulted and giving E1 error and I am unable to verify analyzer or collect grabs. Will return tomorrow to complete work. 13:45 collected following grab using Sl000. Monochloramine grab: 1.51. Free ammonia grab: 0.07. Total ammonia grab: 0.37. Nitrite: 0.002. Temperature: 6.0 Celsius. pH: 8.02. No issues found on site. | Richmond Hill Coon's Elevated Tank | 2026-01-28
CENTRAL | January | Station Check (no issues found) Input data to PWQ Verified CL17s (mg/L) 3:20 Inlet: Free: Grab 0.05 Total: Grab 1.90, A 1.91 2:55 Outlet: Free: Grab 0.08 Total: Grab 1.74, A 1.78 3:05 #11538378, 11476246 & operational samples | Richmond Hill Coon's Elevated Tank | 2026-01-21
CENTRAL | January | On-site for station check and sampling. COC - W11503361. 08:50. Tower level 77% and draining at 174 l/s. 08:54. Verified outlet analyzer (mg/l) and collected sample. Free chlorine grab: 0.05. Total chlorine grab: 1.71 Analyzer: 1.70 Monochloramine grab: 1.54. Free ammonia grab: 0.08. Total ammonia grab: 0.38. Nitrite: 0.002. Temperature: 6.9 Celsius. pH: 8.02. 09:05 Verified inlet analyzer (mg/l) Free chlorine grab: 0.07. Total chlorine grab: 1.87/1.87/1.85. Analyzer: 2.00. Adjusted to match grab average. Entered readings into process sheets. No issues found. | Richmond Hill Coon's Elevated Tank | 2026-01-07
CENTRAL | January | On-site for station check and sampling. COC - W11522747. 14:14. Tower level 62% and draining at 88 l/s. 14:15. Verified outlet analyzer (mg/l) and collected sample. Free chlorine grab: 0.05. Total chlorine grab: 1.70 Analyzer: 1.76 Monochloramine grab: 1.52 Free ammonia grab: 0.09. Total ammonia grab: 0.39. Nitrite: 0.004. Temperature: 7.2 Celsius. pH: 8.02. 14:20 Verified inlet analyzer (mg/l) Free chlorine grab: 0.02. Total chlorine grab: 1.74. Analyzer: 1.75. Entered readings into process sheets. No issues found. | Richmond Hill Coon's Elevated Tank | 2026-01-14
CENTRAL | January | 09:25. Isolated tower to replace outlet check valve with Lee and Sean. Roc notified and changed Bloomington to controlling tower. Completed the following work orders: 10:22. Chlorine analyzer maintenace. Notified ROC. 11:18 outlet grab: 1.71 mg/l. Analyzer 1.75 Inlet grab: 1.71/1.68/1.70. Analyzer:1.82. Adjusted to match grabs. Air relief valve maintenance. Heat trace system inspection. Jhsc inspection. Actuated valve inspection. Low building temp alarms tested for chlorine, electrical, valve, ammonia rooms. Prv maintenance and inspection. Circulation pump inspection. 12:30 completed check valve repair. Placed back in service and back to controlling tower with no issues. Notified roc. | Richmond Hill Coon's Elevated Tank | 2026-01-08
CENTRAL | January | Check valve repairs Installed new rubber flap and gasket | Richmond Hill Coon's Elevated Tank | 2026-01-08
EAST | January | Under Direction of OIC Joe Mazza On Site for; - Station checks Data in PWQ Workbook Grabs @ 12:44 FCl: 0.06 mg/L TCl: 1.56 mg/L Pump 3 and 4 active in duty 1 Equipment OOS: none Facility OK | Richmond Hill Pugsley Pumping Station | 2026-01-30
EAST | January | Under Direction of OIC Dan Zhou On Site for; - Station checks Data in PWQ Workbook Grabs @ 14:46 FCl: 0.10 mg/L TCl: 1.53 mg/L Pump 3 and 4 active in duty 1 Equipment OOS: none Facility OK | Richmond Hill Pugsley Pumping Station | 2026-01-16
EAST | January | On site to check station and equipment. P1 and P4 are running in duty 1 upon arrival. 14:02 grab Chlorine residual are: FCL = 0.03 mg/l, TCL = 1.57 mg/l.? Readings are in PWQ sheet.? Able to ack+reset gen warning alarm. No other alarms outstanding. Reviewed trends, station is under normal operation.? | Richmond Hill Pugsley Pumping Station | 2026-01-26
EAST | January | On site to check station and equipment. Duty is active upon arrival. P3 and P4 are running in duty 1.? 14:18 grab chlorine residual are: Free = 0.04 mg/l, total = 1.59 mg/l. Readings are in PWQ sheet.? Reviewed trends, station is under normal operation.? | Richmond Hill Pugsley Pumping Station | 2026-01-23
EAST | January | Under Direction of OIC Dan Zhou On Site for; - Station checks Data in PWQ Workbook Grabs @ 13:30 hrs. FCl: 0.15 mg/L TCl: 1.54 mg/L Pump 2 and 3 active in duty 1 Equipment OOS: none Facility OK | Richmond Hill Pugsley Pumping Station | 2026-01-09
EAST | January | On site responding to Generator warning Alarm. Informed by ROC @ 08:18 hrs. Arrived on site and checked generator components. Heating block is still working, and space heaters inside closure. Was unable to clear alarm on generator in stop mode as temp is maintaining low. Informed ROC at 09:33 hrs. of the issue. Generator warning alarm may come in repeatedly during low temp days. | Richmond Hill Pugsley Pumping Station | 2026-01-15
EAST | January | Under Direction of OIC Stephen Baidy On Site for; - Station checks Data in PWQ Workbook Grabs @ 14:33 FCl: 0.03 mg/L TCl: 1.50 mg/L Pump 2 and 3 active in duty 1 Equipment OOS: none Facility OK | Richmond Hill Pugsley Pumping Station | 2026-01-12
EAST | January | Under direction of OIC Dan Zhou On site for; - Generator test - Pump inspections pumps 1,2,3,4 - JHSC Health and Safety Inspection - Flood alarm test - Surge anticipatory test (PRV) test - Sump pump inspection and test - Comprehensive housekeeping @ 13:33 Dan Zhou called ROC and deactivated duty (pumps 1 and 2 in duty 1 ) Generator Pre run checks; Batteries OK Oil OK Heating block OK Hoses and lines OK Generator test run: @ 13:45 generator ATS switched to test @ 13:54 generator warning alarm (cold temp alarm - acknowledged, OK) @ 14:04 activated pumps 3 and 4 in duty 1 @ 14:41 called ROC and deactivated duty (pumps 3,4) Operating Current: 14.5 Operating Frequency: 60. Hz Operating Voltage: 600 Volts, Engine speed: 1798 RPM Water/coolant Temp: 162 f Oil Pressure: 64 psi kPa Oil temp 180 f Oil psi 103 Flipped ATS back to auto @ 15:04 Dan Zhou created work orders to repair surge anticipator test switch (high pressure side), surge anticipator control panel lights, pump 2 re-pressurize the check valve Equipment OOS: None Facility OK | Richmond Hill Pugsley Pumping Station | 2026-01-13
EAST | January | On site to check station and equipment. P1 and P2 are running in duty 1.? 14:15 grab free chlorine = 0.05 mg/l, total = 1.48 mg/l.? Reviewed trends, no issues. | Richmond Hill Pugsley Pumping Station | 2026-01-02
EAST | January | Under Direction of OIC Dan Zhou On Site for; - Station checks Data in PWQ Workbook Grabs @ 14:48 FCl: 0.07 mg/L TCl: 1.51 mg/L Pump 1 and 2 active in duty 1 Equipment OOS: none Facility OK | Richmond Hill Pugsley Pumping Station | 2026-01-05
WEST | January | Onsite to complete station check and collect weekly micro samples W11538476 Hl @1024 Total analyzer 3.38 grab 3.44 Free grab 0.05 Mcl grab 2.88 Through plant @1345 Total analyzer 2.31 grab 2.42 Free grab 0.02 Reservoir @1400 Total analyzer 3.73 grab 3.70 Free 0.01 Mcl grab 3.42 Ran well 3 to get sample Increased filter backwash runtimes from 20 to 22 hrs on each of the filters Received call from ROC about lower tower volume and hi flow, Town of King flushing. Increased speed set point for each high lift to 100%. | Schomberg Water Treatment Plant & Wells 2-4 | 2026-01-21
WEST | January | Reservoir total chlorine lolo alarm came in, switched sample pumps and residual recovered. Analyzer fault still active, will monitor | Schomberg Water Treatment Plant & Wells 2-4 | 2026-01-31
WEST | January | Onsite for station check and to collect weekly micro sample W1155091 Checked residuals mg/l Hl @0954 Total analyzer 3.30 grab 3.20 Free grab 0.01 Mcl grab 2.88 Reservoir @1200 Total analyzer 3.66 grab 3.62 Free grab 0.03 Mcl grab 3.08 Through plant @1209 Total analyzer 2.14 grab 2.06 Free grab 0.04 Topped up kmno tank 2 | Schomberg Water Treatment Plant & Wells 2-4 | 2026-01-28
WEST | January | -on site to respond to reservoir total chlorine analyzer fault -found sample pumps #1 had tubing leak, pump #2 had flow but analyzer flow was still reading zero -flushed analyzer flow meter - now reading adequate flow -repaired pump #1 and tested - ok -cleared fault alarm, no further issues -verified analyzer: 15:43 - analyzer reading = 3.71 grab = 3.60 | Schomberg Water Treatment Plant & Wells 2-4 | 2026-01-31
WEST | January | 8:55 - trends checked good, equipment checked good 9:05 - W4 sample grabbed 9:38 - F1,F2,F3 and raw combined sample grabbed 9:44- high lifts free grabbed, 0.07. Total grab, 3.42 vs. Analyzer, 3.46. Monochloramine 2.87 mg/l 10:10 - post filter free grabbed, 0.15. Total grab 2.39 vs. Analyzer 2.33 10:30 - Reservoir grab free 0.05. Total grab 3.60 vs analyzer 3.75. Monochloramine 3.11 2:43 pm, changed reagents in the post filter cl17sc analyzer | Schomberg Water Treatment Plant & Wells 2-4 | 2026-01-26
WEST | January | Onsite for station check Through plant @1005 Total analyzer 2.20 grab 2.19 Free grab 0.04 Reservoir @1018 Total analyzer 3.66 grab 3.56 Free grab 0.02 Mcl grab 3.22 Hl @1333 Total analyzer 3.40 grab 3.36 Free grab 0.05 Mcl grab 3.12 Changed reagents on reservoir analyzer Changed high lift duty to 10-40% | Schomberg Water Treatment Plant & Wells 2-4 | 2026-01-16
WEST | January | -completed cylinder change -replaced high lift CL17 reagents | Schomberg Water Treatment Plant & Wells 2-4 | 2026-01-30
WEST | January | 9:00 trends checked and ok. Equipment was inspected and in good conditions 9:15 highlift sample collected. Free grab 0.03. Total grab 3.42 vs analyzer 3.42 Monochloramine 3.05 mg/l 10:10 Reservoir free grab 0.07, total grab 3.56 vs analyzer 3.69. Monochloramine 3.29 10:23 W4 sample grabbed 10:30 post filter free grab 0.04, analyzer total 2.33 vs grab total 2.25 11:02 cleaned turbidity meter on HL sensor. | Schomberg Water Treatment Plant & Wells 2-4 | 2026-01-30
WEST | January | Onsite for station check Checked residuals mg/L High lift @0858 Total analyzer 3.40 grab 3.42 Free grab 0.02 Mcl grab 3.04 Reservoir @0924 Total analyzer 3.72 grab 3.56 Free grab 0.04 Mcl 3.42 Through plant @0944 Total analyzer 2.26 grab 2,17 Free grab 0.04 | Schomberg Water Treatment Plant & Wells 2-4 | 2026-01-23
WEST | January | Onsite for station checked residuals mg/l Hl @1155 Total analyzer 3.45 grab 3.42 Free grab 0.03 Mcl grab 3.03 Reservoir @1208 Total analyzer 3.75 grab 3.74 Free grab 0.04 Mcl grab 3.38 Through plant @1234 Total analyzer 2.23 grab 2.17 Free grab 0.03 Rotated reservoir cells | Schomberg Water Treatment Plant & Wells 2-4 | 2026-01-19
WEST | January | Restarted the Local SCADA server due to windows updates. Notified the Remote Operations Center and the OIC. Plant was shut off during the updates. | Schomberg Water Treatment Plant & Wells 2-4 | 2026-01-22
WEST | January | Onsite to complete work orders Turned off hl duty Reduced start from 15% to 5% to deep cycle Put back afterwards Cleaned kmno injection point Did monthly kmno pump inspection Ran both pumps to sight glass, increased max flow for p1 to 395 ml/min Rotated chlorinator duty to put #4 into post uv duty | Schomberg Water Treatment Plant & Wells 2-4 | 2026-01-15
WEST | January | Onsite to complete work orders Completed monthly uv sensor check Completed reactors 1&3 while duty was active and did reactor 2 in local Cleaned uvt sensor Deactivated plant Completed jhsc, no issues Exercised high lift manual valves , actuated valves and prv Flushed and calibrated filter ntu analyzers with 20 ntu vial Reactivated plant with no issues afterwards | Schomberg Water Treatment Plant & Wells 2-4 | 2026-01-08
WEST | January | Check filter tank treaded rods and nuts | Schomberg Water Treatment Plant & Wells 2-4 | 2026-01-09
WEST | January | w/o 11508584, 11508603 Permaginate system Tank #1 (new batch) Permaginate pumps 1&2 (new elements Performed draw down (no change) | Schomberg Water Treatment Plant & Wells 2-4 | 2026-01-08
WEST | January | Onsite to complete station check and to collect weekly micro samples and Iron and Manganese samples W11503459 W11462117 W11503620 Activated High lift duty to collect samples and make room in reservoir Cycled well duty to collect sample from Well 3 Checked residuals mg/L High lift @10:43 Total analyzer 3.49 grab 3.46 Free grab 0.03 Through plant @1054 Total analyzer 2.38 grab 2.34 Free grab 0.07 Reservoir @1104 Total analyzer 3.63 grab 3.66 Free grab 0.04 | Schomberg Water Treatment Plant & Wells 2-4 | 2026-01-07
WEST | January | Onsite for station check Activated hl duty early to collect in house lab sample Checked residuals mg/l Hl @1004 Total analyzer 3.44 grab 3.42 Free grab 0.05 Through plant @1008 Total analyzer 2.32 grab 2.32 Free grab 0.05 Reservoir @1025 Total analyzer 3.75 grab 3.62 Free grab 0.05 Topped up Kmno tank 2 | Schomberg Water Treatment Plant & Wells 2-4 | 2026-01-12
WEST | January | Onsite to complete station check and to collect weekly micro sample and Q1 quarterly samples W11522925 W11476008 Checked residuals mg/l Through plant @1026 Total analyzer 2.32 grab 2.28 Free grab 0.05 Reservoir @1041 Total analyzer 3.61 grab 3.56 Free grab 0.03 Mcl 3.13 High lift @1129 Total analyzer 3.46 grab 3.32 Free grab 0.06 Mcl grab 3.09 Ran well 3 to sample placed back to manual off afterwards | Schomberg Water Treatment Plant & Wells 2-4 | 2026-01-14
WEST | January | Onsite for station check Checked residuals Hl @0913 Total analyzer 3.45 grab 3.42 Free grab 0.02 Mcl grab 3.07 Through plant @0903 Total analyzer 2.34 grab 2.34 Free grab 0.07 Reservoir @0939 Total analyzer 3.69 grab 3.58 Free grab 0.04 Mcl grab 3.22 Changed cl2 cylinder with J bloye Power blip caused alarms Plant was off,ack and reset | Schomberg Water Treatment Plant & Wells 2-4 | 2026-01-09
WEST | January | Onsite to complete work orders Completed monthly generator run Start Fuel 85.7/ 85.5 cm 1656/1650 L Hrs 540.1 Stop Fuel 85.2/84.2 cm 1644/1627 L Hrs 541.5 Stopped hl duty Switched over, started plant and hl duty to put on load Stopped to switch back Reactivated everything afterwards Completed jhsc on well 2 Exercised actuated valves on wells | Schomberg Water Treatment Plant & Wells 2-4 | 2026-01-13
WEST | January | W11483596- Consultation regarding SHTP Air compressor fault. Requested CMU. | Schomberg Water Treatment Plant & Wells 2-4 | 2026-01-04
WEST | January | Onsite for station check Activated hl duty for in house lab sample collection, deactivated afterwards Rotated reservoir cells Closed south, opened north Caused dip in trend and fault Changed tubing for sample pump 1 due to leak Cleared fault Checked residuals mg/l HL Treated analyzers 3.42 grab 3.42 Free analyzer 0.05 Reservoir @1254 Total analyzer 3.75 grab 3.74 Free analyzer 0.08 Post filter @1311 Total analyzer 2.32 grab 2.30 Free 0.04 | Schomberg Water Treatment Plant & Wells 2-4 | 2026-01-05
WEST | January | Check repairing raw water access covers | Schomberg Water Treatment Plant & Wells 2-4 | 2026-01-06
WEST | January | On site to reset Air compressor- CMU W11556979. 09:27- reset and started both Air compressors air compressor trends look okay. watched plant starting up. everything looks normal. Informed ROC about the work done. | Schomberg Water Treatment Plant & Wells 2-4 | 2026-01-04
WEST | January | -on site to complete station check and lab - plant duty active and high lift duty active -wells 2 and 4 in duty - KMnO4 pump 2 running at 15.2%, 58 psi, 60.1 ml/min - chlorinator 1 53% open, df 144%, 0.53 kg/hr, vac = -740 mbar - chlorinator 2 27% open, df 162%, 0.28 kg/hr, vac = -850 mbar - recorded data in PWQ sheet - checked equipment - CL17 reagents ok - reviewed trends - no issues found -completed wells 2,3,4 station checks -verified analyzers: 11:14 - high lift treated water TCL analyzer = 3.24 mg/L 11:14 - high lift treated water grab: FCL = 0.00 mg/L TCL = 3.26 mg/L Mono = 2.85 mg/L 11:25 - reservoir TCL analyzer = 3.63 mg/L 11:25 - reservoir grab: TCL = 3.62 mg/L Mono = 3.17 mg/L 11:41 - post filter TCL analyzer = 2.36 mg/L 11:41 - post filter grab: TCL = 2.32 mg/L -filled KMnO4 tank #1 16.2 cm to 82.4 cm -completed lab, results in PWQ sheet | Schomberg Water Treatment Plant & Wells 2-4 | 2026-01-02
WEST | January | Onsite to complete work orders Adjusted plant start level to do work with plant off Reservoir low level came in Completed cl2 system inspection with no issues Inspection of compressors no issues Tested cl2 leak alarm and scrubber Cleaned cl17sc analyzers Grabs after Treated Total analyzer 3.35 grab 3.36 Reservoir Total analyzer 3.59 grab 3.58 Through plant Total analyzer 2.25 grab 2.19 | Schomberg Water Treatment Plant & Wells 2-4 | 2026-01-06
EAST | January | On site to complete station check. Time: 11:22 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.90 1.95 Time: 11:25 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.46 1.45 Total: 1.68 Verified analyzers with grabs all ok. Checked station and trends. No OOS equipment. One outstanding alarm Generator tank hi alarm. Disregard due to this being the generator topped up to full. | Mount Albert Wells 1 & 2 | 2026-01-16
EAST | January | On site to complete station check. Collecting weekly Bac-t Samples. W11538262 Weekly Bac-t Samples. Time: 12:55 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.99 1.98 Time: 12:58 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.50 1.46 Total: 1.81 Verified analyzers with grabs all ok. Checked site and trends. One outstanding alarm for diesel generator fuel tank hi alarm. Well 1 OOS due to water quality issues. Started well 1 at 13:00 to run to waste not to system to sample raw water. At 13:31 shut down well 1 after collecting sample and put well 2 back to auto and reactivated well. | Mount Albert Wells 1 & 2 | 2026-01-21
EAST | January | Silicate top up: Before: 64.9cm/ 306L After: 105.5cm/ 497L | Mount Albert Wells 1 & 2 | 2026-01-29
EAST | January | Silicate top up: Before: 65.2cm/308L After: 105.6cm/498L | Mount Albert Wells 1 & 2 | 2026-01-22
EAST | January | Received diesel fuel delivery - 675 L Tank level - 11.2 cm to 23.0 cm | Mount Albert Wells 1 & 2 | 2026-01-16
EAST | January | On site to complete station check. Time: 09:30 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.46 1.38 Time: 09:32 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.42 1.44 Total: 1.64 Verified analyzers with grabs. Checked site and trends. Entered data into PWQ. Only one outstanding alarm on site due to hi fuel level for the generator. No OOS equipment on site. | Mount Albert Wells 1 & 2 | 2026-01-19
EAST | January | On site for station check. Duty active, tower level 71%. Verified analyzer readings with grab residuals. Influent taken 14:00 Free Grab: 1.91 mg/L Analyzer: 1.88 mg/L Effluent taken at 14:02 Free Grab: 1.65 mg/L Analyzer: 1.63 mg/L Total Grab: 1.93 mg/L Chemical systems: Hypo p2 speed 26%, DF= 89%. DP= 440 kpa. Silicate P2 speed 37%, DP= 500 kpa. Visual inspection of chemical systems - all ok. Entered station readings in PWQ sheet. Reviewed trends, equipment ok. Station ok | Mount Albert Wells 1 & 2 | 2026-01-30
EAST | January | On site to complete station check. Time: 13:45 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.94 1.98 Time: 13:48 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.67 1.61 Total: 1.91 Verified analyzers with grabs. Checked station and equipment. Entered data into PWQ sheet. Well 1 OOS due to water quality issues. Disregard hi generator fuel tank alarm. | Mount Albert Wells 1 & 2 | 2026-01-26
EAST | January | On site to complete station check. Collecting weekly Bac-t Samples. Collecting Q1 Samples. W11550719 Weekly Bac-t Samples. W11476386 Q1 Samples. Time: 13:35 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.87 1.95 Time: 13:40 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.63 1.67 Total: 1.91 At 13:34 put chemical pumps to manual speed and then started well 1 which is not going to system it is running to waste. At 14:00 shut well 1 off and placed chemical pumps back to auto dosage. Verified analyzers on site with grabs. Checked site and trends. Well 1 OOS due to water quality issues. Disregard generator hi tank level alarm. | Mount Albert Wells 1 & 2 | 2026-01-28
EAST | January | On site to complete station check. Time: 13:30 Grab (mg/l) Analyzer (mg/l) Free: 1.84 1.91 Time: 13:32 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.66 1.62 Total: 1.82 Verified analyzers with grabs all ok. Checked equipment and trends. Well 1 OOS due to water quality issues. Outstanding alarm on generator disregard. | Mount Albert Wells 1 & 2 | 2026-01-23
EAST | January | On site to complete station check. Time: 13:40 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.81 1.86 Time: 13:45 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.44 1.42 Total: 1.72 Verified analyzers with grabs. Checked station and trends. No outstanding alarms on site. No OOS equipment on site. Entered data into PWQ sheet. At 13:55 shut off well to perform NTU maintenance ROC has already been informed. At 14:03 put well back to auto to finish duty run. | Mount Albert Wells 1 & 2 | 2026-01-09
EAST | January | On site to complete station check and collect weekly operational sample. Started well at 13:10. Time: 13:37 Influent Grab (mg/l) Analyzer (mg/l) Free: 2.00 1.92 Time: 13:40 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.54 1.56 Total: 1.82 Verified analyzers with grabs all ok. Checked site and trends. Entered data into PWQ sheet. No outstanding alarms on site. No OOS equipment except well 1 which is in local off. Lo diesel fuel level will let team lead know so that diesel can be ordered for site. Shut well off at 13:48 and put well back to auto at 13:52. | Mount Albert Wells 1 & 2 | 2026-01-12
EAST | January | On site to complete station check. Collecting weekly Bac-t Samples. W11522635 Weekly Bac-t Samples. Time: 09:08 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.88 1.93 Time: 09:10 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.64 1.61 Total: 1.94 Verified analyzers with grabs all ok. Checked site and trends. Entered data into PWQ. No outstanding alarms on site. No OOS equipment. Started well 1 in local at 09:32. All chemical pumps have been put to manual due to the flow going to waste. Also no water is going to system as well has been valves off to waste. Shut well 1 off at 10:03 after sample was collected. Placed all chemical pumps back into auto and cleared all associated alarms that were created. | Mount Albert Wells 1 & 2 | 2026-01-14
EAST | January | Station Check (no issues found) Input data to PWQ 14:20 Verified CL17s (mg/L) Influent: Free Grab 2.02, A 1.99 Effluent: Free Grab 1.40, A 1.41 Total: Grab 1.53 13:38 Well 1 local on (verified isolation and chemical pumps manual off) 14:00 #11504389, #11503245 samples 14:35 Samples (well 2) | Mount Albert Wells 1 & 2 | 2026-01-07
EAST | January | On site to top up silicate day tank with silicate from Aurora wells 1-4. Start: 31.9cm/151L Stop: 99.1cm/467L No issues with top up. | Mount Albert Wells 1 & 2 | 2026-01-08
EAST | January | Silicate top up: Before: 58.6cm/276L After: 105.0cm/495L | Mount Albert Wells 1 & 2 | 2026-01-15
EAST | January | On site to assist with hypo top up. Start: 28.2cm/196L Stop: 87.3cm/605L 86.3cm/599L At 09:45 equalized both tanks so that they can be topped up. While on site will be completing the following work orders: W11498927 Generator Monthly Test W11498810 Sodium Hypo System Maintenance. W11498796 Butterfly Valve Exercise W11498767 Hi/Low Temperature Test W11498759 Sodium Hypo Pump Maintenace W11498751 Sodium Silicate Pump Maint. W11498739 Sodium Hypo Panel Board Insp. W11498590 Deep Well Exhaust Valve Test W11497946 CL-17 Analyzer Maintenance W11497904 CL-17 Analyzer Maintenance W11493549 JHSC Insp. After analyzer maintenance took grabs to verify analyzers. Time: 10:40 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.34 1.31 Time: 10:43 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.68 1.72 Pocket colorimetre passed calibration. No issues with analyzers. Started generator test at 12:40, started well at 12:40 to run generator on load. At 13:41 stopped well, and at 13:51 generator switched back to station power. Below is the data taken from test: Before Diesel Generator Test Run Sheet running generator, the following were inspected: Battery cell levels Battery terminal and cables Oil level Coolant level Fluid leaks Coolant Recirculating pump Faulty gauges Diesel generator start time: 12:40 hrs Diesel hours at start: 204 Fuel Level @ start: Tank #1 ~ 11.3cm/747L Start time: 12:40 After 30 min of running: Operating current = 36 A Operating frequency = 60 Hz Operating voltage = 348 V Engine speed = 1800 RPM Water temperature = 82 C Oil temperature = 195 F Oil pressure = 404 psi Fuel pressure. = ? Pyrometer/Exhaust = Stopped and transferred power to hydro @ 13:51 hrs Diesel generator hours after shutdown: 205.40 hrs Tank #1 ~ 11cm/722.6L Additional information/ Observations: Activated duty and conducted generator test under load, no issues. Put well 2 back to auto at 14:03. Any changes in trends are due to work orders being completed. | Mount Albert Wells 1 & 2 | 2026-01-06
EAST | January | On site for station check. Duty not active, tower level 62% Verified analyzer readings with grab residuals. Influent taken 13:51 Free Grab: 1.43 mg/L Analyzer: 1.40 mg/L Effluent taken at 13:54 Free Grab: 1.44 mg/L Analyzer: 1.48 mg/L Total Grab: 1.71 mg/L Visual inspection of chemical systems - all ok. Entered station readings in PWQ sheet. Reviewed trends, equipment ok. Station ok | Mount Albert Wells 1 & 2 | 2026-01-02
EAST | January | On site to complete station check. Time: 13:30 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.43 1.41 Time: 13:32 Effluent Grab (mg/) Analyzer (mg/l) Free: 1.45 1.44 Total: 1.78 Cleared outstanding alarms at 13:12. One outstanding alarm of hypo tank 1 lolo alarm. At 13:13 put well 2 in manual for the night due to Lo hypo tank level. Informed on call operator about well being in manual off. Entered data into PWQ sheet. Verified analyzers with grabs. Checked site and trends. | Mount Albert Wells 1 & 2 | 2026-01-05
EAST | January | On site responding to heat trace fault alarm. W11611871 Inlet/Outlet heat trace fault alarm. Arrived on site checked heat trace nothing out of place. Was able to ack and reset alarm at 11:50. Informed ROC of no issues. Will monitor off site. | Stouffville Zone 2 Elevated Tank | 2026-01-24
EAST | January | On site for monthly maintenance: 11:50hrs: HACH CL17 Analyzer cleaning. Verified Analyzer after cleaning: Cl2 Grab residuals: 1.63mg/l, Analyzer: 1.67mg/l JHSC Inspection, sump pump inspection, heat trace inspection, housekeeping on site. | Stouffville Zone 2 Elevated Tank | 2026-01-15
EAST | January | On site to investigate Heat Trace Fault alarm on SCADA. Alarm was triggered due to the low temperature being triggered on the Heat Trace system due to the lower temperatures (3 C). Heat Trace systems are working and heaters are on. The low temp alarm has cleared as the temperature has increased as the tower is now filling. Informed On Call operator about heat trace stage alarm. | Stouffville Zone 2 Elevated Tank | 2026-01-30
EAST | January | On site for station check and to collect weekly micro samples (W11550799) and quarterly samples (W11476568). Collected Cl2 grab residuals on Header tap @10:05hrs and Sample: FCL: 1.95mg/l Analyzer FCL: 1.98mg/l TCL: 2.16mg/l Checked station readings, verified Cl2 analyzer. All information in PWQ sheet. Equipment out of service: None. | Stouffville Zone 2 Elevated Tank | 2026-01-28
EAST | January | Attending site to check Chlorine analyzer push buttons (W11593415). Push button switches were found to have limited functionality. Replaced bush buttons and verified reading. Adjusted Free chlorine readings from 1.68 to 1.74mg/L, based on average of 3 grabs. ROC was notified before and after maintenance activities. | Stouffville Zone 2 Elevated Tank | 2026-01-30
EAST | January | On site to check station and equipment. Tower is on a draining cycle at 57%. 10:28 grab chlorine residual from riser pipe: FCL = 1.68 mg/l, TCL = 1.87 mg/l. Analyzer free = 1.69 mg/l. 10:28 Collected micro sample, YD W11522733. Duty 1 start level changed from 60% to 40% to deep cycle the tower.? Will change it back later today. Station readings are entered in PWQ sheet.? Reviewed trends, no issues. | Stouffville Zone 2 Elevated Tank | 2026-01-14
EAST | January | On site for station check and to collect weekly micro samples (W11538350). Collected Cl2 grab residuals on Header tap @13:10hrs and Sample: FCL: 1.65mg/l Analyzer FCL: 1.69mg/l TCL: 1.81mg/l Checked station readings, verified Cl2 analyzer. All information in PWQ sheet. Equipment out of service: None. | Stouffville Zone 2 Elevated Tank | 2026-01-21
EAST | January | On site for station check and to collect weekly micro samples (W11503333) and in house ATP/iron samples. Collected Cl2 grab residuals on Header tap @12:50hrs and Sample: FCL: 1.75mg/l Analyzer FCL: 1.80mg/l TCL: 1.92mg/l Checked station readings, verified Cl2 analyzer. All information in PWQ sheet. Equipment out of service: None. | Stouffville Zone 2 Elevated Tank | 2026-01-07
LINEAR | January | Replenished declorination pucks at the leak site on Stouffville Road and McCowan Road. Grab chlorine residual test as follows Free- 0.00 mg/l Total- 0.00 mg/l | Linear Water System | 2026-01-19
LINEAR | January | Replenished the declorination pucks at the leak site on Stouffville Road east of McCowan Road. Grab chlorine residual test as follows Free- 0.00 mg/l Total- 0.00 mg/l | Linear Water System | 2026-01-17
LINEAR | January | Replenished the declorination pucks at the leak site on Stouffville Road east of McCowan Road. Grab chlorine residual test as follows Free- 0.00 mg/l Total- 0.00 mg/l | Linear Water System | 2026-01-16
LINEAR | January | Assisted North Rock with replacement of air valve at. Took residuals upon replacement. T9718-04 Free - 0.04 mg/l Total - 1.49 mg/l T9718-02 Free - 0.05 mg/l Total - 1.57 mg/l Reopened all valves. Watermain from T9718-04 to T9718-01 back in service. | Linear Water System | 2026-01-29
LINEAR | January | Replenished the declorination pucks at the leak site on Stouffville Road east of McCowan Road. Grab chlorine residual test as follows Free- 0.00 mg/l Total- 0.00 mg/l | Linear Water System | 2026-01-15
LINEAR | January | Assisted North Rock with replacement of air valve at 16th and William Berczy. Took residuals upon replacement. Free - 0.04 mg/l Total - 1.53 mg/l Reopened all valves. Watermain from Kennedy to William Berczy on 16th back in service. | Linear Water System | 2026-01-27
LINEAR | January | Replenished the declorination pucks at the leak site on Stouffville Road east of McCowan Road. Grab chlorine residual test as follows Free- 0.00 mg/l Total- 0.00 mg/lI?m | Linear Water System | 2026-01-18
LINEAR | January | Replenished declorination pucks at leak site on Stouffville Road east of McCowan. Grab chlorine residual test as follows Free- 0.00mg/l Total-0.00mg/l | Linear Water System | 2026-01-10
LINEAR | January | Replenished the declorination pucks at the leak site on Stouffville Road east of McCowan Road. Grab chlorine residual test as follows Free-0.00mg/l Total- 0.00mg/l | Linear Water System | 2026-01-20
LINEAR | January | Filled and flushed the 500 mm watermain between Pine Valley and Islington ave after the drain valve was replaced. Grab chlorine residual test as follows Free- 0.05mg/l Total- 1.25mg/l The valves are all open and the watermain is back in service. | Linear Water System | 2026-01-09
LINEAR | January | Replenished the declorination pucks at the leak site on Stouffville Road east of McCowan Road. Grab chlorine residual test as follows Free- 0.00 mg/l Total- 0.00 mg/l | Linear Water System | 2026-01-14
LINEAR | January | Replenished the declorination pucks at the break site on Stouffville Road east of McCowan Road. Grab chlorine residual test as follows Free- 0.00mg/l Total- 0.00mg/l | Linear Water System | 2026-01-09
LINEAR | January | Replenished the declorination pucks at the leak site on Stouffville Road east of McCowan Road. Grab chlorine residual as follows Free- 0.00 mg/l Total- 0.00 mg/l | Linear Water System | 2026-01-13
LINEAR | January | Replenished the declorination pucks at the leak site on Stouffville Road east of McCowan Road. Grab chlorine residual as follows Free- 0.00 mg/l Total- 0.00 mg/l | Linear Water System | 2026-01-11
LINEAR | January | Topped up Dechlorination pucks at Stouffville Rd and McCowan Main break. Collected CL2 grab residuals downstream of dechlorination: FCL: 0.00mg/l, TCL: 0.00mg/l. | Linear Water System | 2026-01-07
LINEAR | January | under direction of OIC Dan Zhou Topped up Dechlorination pucks at Stouffville Rd and McCowan Main break. Collected CL2 grab residuals downstream of dechlorination: FCl: 0.00 mg/l, TCl: 0.01 mg/l. | Linear Water System | 2026-01-08
LINEAR | January | Topped up dechlorinaion pucks at main break site Stouffville Rd/McCowan. Collected Cl2 grab residuals downstream of dechlor site: FCL: 0.00mg/l, TCL: 0.00mg/l | Linear Water System | 2026-01-05
LINEAR | January | Replenished the declorination pucks at the break site on Stouffville Road east of McCowan Road. Grab chlorine residual test as follows Free- 0.00mg/l Total- 0.00mg/l | Linear Water System | 2026-01-02
LINEAR | January | Replenished the declorination pucks at the break site on Stouffville Road east of McCowan Road. Grab chlorine residual test as follows Free- 0.00mg/l Total- 0.00mg/l | Linear Water System | 2026-01-04
LINEAR | January | 2:30 pm: ROC notified me about the potential main leak on Langstaff Rd, East of Islington Ave near chamber T04107-02. 4:15 pm: I reached on site to investigate. Found out that the leak is inside the Chamber T04107-02. 4:40 pm: Started to pump out the chamber to investigate further. 5:20 pm: Found leak between the spool piece and the drain valve. Possibly between the flange or the gasket might be busted. 5:30 pm: Informed ROC, Manager on-call, ORO and CPD. 5:45 pm: CPD said they will be on-site soon. 6:20 pm: CPD on site. 7:30 pm: After investigating we decided to isolate and possibly start repair tomorrow, 5th Jan 2026. Also, dechlor pucks to be put on top of the Chamber lid today. 9:20 pm: Dechlor pucks have been laid down on top of the chamber lid | Linear Water System | 2026-01-04
LINEAR | January | Replenished the declorination pucks at the break site on Stouffville Road east of McCowan Road. Grab chlorine residual test as follows Free- 0.00mg/l Total- 0.00mg/l | Linear Water System | 2026-01-01
LINEAR | January | Topped up Dechlorination pucks at Stouffville Rd and McCowan Main break. Collected CL2 grab residuals downstream of dechlorination: FCL: 0.00mg/l, TCL: 0.00mg/l. | Linear Water System | 2026-01-06
LINEAR | January | Replenished the declorination pucks at the break site on Stouffville Road east of McCowan Road. Grab chlorine residual test as follows Free- 0.00mg/l Total- 0.00mg/l | Linear Water System | 2026-01-03
WW-WEST | January | Disregard entry, it was to be entered at kBsP | Nobleton Water Resource Recovery Facility | 2026-01-24
WW-WEST | January | Harie Rajamithiran(OIT) working under the direction of Daniel Hirstwood (OIC). -Supernated sludge thickening tank and transferred to sludge holding tank -Started batch wasting process at 10:00, wasting from 11:00-13:00 for 15m^3 per train in 6 cycles -Completed lab analysis, no abnormalities found -Completed station check, no abnormalities found -Added 1 bag of soda ash into each aeration -Received 3 skids of soda ash -Turned RAS to auto and WAS pumps/valves into manuel off | Nobleton Water Resource Recovery Facility | 2026-01-16
WW-WEST | January | Harie Rajamithiran(OIT) working under the direction for Gavin Walker(OIC). -Completed lab analysis, no abnormalities found -Completed station check, no abnormalities found -Added 1 bag of soda ash into each aeration tank -Received alum from 0.82m to 3.68m | Nobleton Water Resource Recovery Facility | 2026-01-20
WW-WEST | January | Power loss occurred at 13:09 due to a local power outage. Diesel generator started but the ATS failed to transfer. Was eventually able to troubleshoot and reset the ATS which then allowed power to restore after 22 minutes. Tertiary bypass occurred during this time with an estimated 18m3 based on the flow rate from the Janet St SPS. Anna Lacourt reported bypass and completed intelex procedure. Samples collected and driven to YD Lab. Electrical dispatched to check the ATS to see if there are any obvious issues. Hydro power outage is ongoing. Checked the hydro outage reports and it is already reported. Hydro restored and ATS transferred back to source 1 by itself at approx 15:15. Transferred sludge to holding tank. Once wasting completed restored RAS flow and disabled WAS system | Nobleton Water Resource Recovery Facility | 2026-01-23
WW-WEST | January | Harie Rajamithiran(OIT) working under the direction of Gavin Walker(OIC). -Supernated sludge thickening tank and transferred to sludge holding tank -Completed lab analysis, no issues found -Completed station check, no issues found -Added 2 bags of soda ash into each aeration tank -Sprayed water on aeration and broke up top ice layer -Cleaned filter inlet channel -Started batch wasting process at 10:00, wasting from 11:00-13:00 for 10m^3 per each train | Nobleton Water Resource Recovery Facility | 2026-01-27
WW-WEST | January | Checked condition of generator air filter Filter requires replacement. Replacement ordered. | Nobleton Water Resource Recovery Facility | 2026-01-29
WW-WEST | January | Picked up new air filter for generator and installed. Complete. | Nobleton Water Resource Recovery Facility | 2026-01-29
WW-WEST | January | Harie Rajamithiran(OIT) working under the direction of Daniel Hirstwood(OIC). -Collected weekly compliance samples -Completed lab analysis, no abnormalities found -Completed station check, no abnormalities found -Started batch wasting process at 10:00, wasting from 11:00-2:00 for 10m^3 per train -Added 1 of bag soda ash into each aeration tank -Cleaned aeration floating solids and exit weirs -Cleaned clarifier sumps -Completed online DO probe maintenance | Nobleton Water Resource Recovery Facility | 2026-01-21
WW-WEST | January | Added 2 x 25kg bags of soda ash to each aeration basin. | Nobleton Water Resource Recovery Facility | 2026-01-24
WW-WEST | January | Harie Rajamithiran(OIT) working under the direction of Daniel Hirstwood(OIC) -Completed lab analysis, no issues found -Completed station check, no issues found -Started batch wasting process at 10:00, wasting from 11:00-13:00 for 10m^3 per train -Added 2 bags soda ash in each aeration tank -Prepared compliance sample bottles | Nobleton Water Resource Recovery Facility | 2026-01-26
WW-WEST | January | Completed the station check and daily lab work Batch wasted 10m3 from each clarifier Added 2 bags of soda ash to each aeration tank Cleaned the do probes in the aeration tanks Removed floating debris from the aeration tanks Cleaned up around site | Nobleton Water Resource Recovery Facility | 2026-01-28
WW-WEST | January | Completed the station check and daily lab work Batch wasted 10m3 from each clarifier Added 2 bags of soda ash to each aeration tank Cleaned up in the aeration blower building Verified do probes | Nobleton Water Resource Recovery Facility | 2026-01-22
WW-WEST | January | Cleaned aeration inlet channel | Nobleton Water Resource Recovery Facility | 2026-01-21
WW-WEST | January | On site to perform scheduled work. Added 2 bags of soda ash into each aeration tank | Nobleton Water Resource Recovery Facility | 2026-01-31
WW-WEST | January | Collected the weekly compliance sample | Nobleton Water Resource Recovery Facility | 2026-01-28
WW-WEST | January | Harie Rajamithiran(OIT) working under the direction of Daniel Hirstwood(OIC)) -Supernated sludge thickening tank -completed lab analysis, no issues found -Total loss of power ats failed at 13:15 to transfer and data loss until time restored -Prepared compliance bypass samples for WO#w11611668 | Nobleton Water Resource Recovery Facility | 2026-01-23
WW-WEST | January | Added 1 bag of soda ash to each aeration tank | Nobleton Water Resource Recovery Facility | 2026-01-17
WW-WEST | January | Harie Rajamithiran(OIT) working under the direction of Daniel Hirstwood(OIC). -Transferred STT to SHT -Completed lab analysis, no issues found -Completed station check, no issues found -Started batch wasting process at 9:00, wasting from 10:00-12:00 for 20m^3 per train -Added 2 bags of soda ash into each aeration tank | Nobleton Water Resource Recovery Facility | 2026-01-30
WW-WEST | January | Attending site to check D.O. air-clean system (W11590035). Found air lines broken on both D.O. probes. Replaced both air lines and returned to service. Used maintenance mode in transmitter to hold values while probes were removed from process. | Nobleton Water Resource Recovery Facility | 2026-01-27
WW-WEST | January | Harie Rajamithiran(OIT) working under the direction of Daniel Hirstwood(OIC) -Supernated STT and transferred to SHT -Completed lab analysis, no issues found -Completed station check, no issues found -Started batch wasting process at 10:00, wasting from 11:00-13:00 for 10m^3 per train -Cleaned aeration tank floating solids -Bled aeration condensation lines | Nobleton Water Resource Recovery Facility | 2026-01-29
WW-WEST | January | Harie Rajamithiran(OIT) working under the direction of Gavin Walker (OIC). -Supernated sludge holding tank and transferred to sludge thickening tank -Completed lab analysis, no abnormalities found -Completed station check, no abnormalities found -Added 1 bag of soda ash into each aeration tank -Received 100 bags of soda ash -Completed UV bank inspection/cleanup -Completed UV channel cleanup -Prepared weekly compliance sample bottles | Nobleton Water Resource Recovery Facility | 2026-01-19
WW-WEST | January | Harie Rajamithiran(OIT) working under the direction of Gavin Walker(OIC). -Supernated sludge thickening tank and transferred to sludge holding tank -Collected weekly compliance samples -Conducted lab analysis, no abnormalities found -Conducted station check, no abnormalities found -Added 1 bag of soda ash into each aeration tank -Started batch wasting process at 10:00, wasting from 12:00-2:00 for 20m^3 per train in 6 cycles -Completed online DO probe maintenance -Completed aeration floating solids removal -Completed aeration outlet weirs cleaning -Completed aeration condensation line bleed out -Turned RAS to auto -Turned WAS pumps/valves to manuel off | Nobleton Water Resource Recovery Facility | 2026-01-07
WW-WEST | January | Harie Rajamithiran(OIT) working under the direction of Gavin Walke(OIC). -Supernated sludge thickening tank and transferred to sludge holding tank -Completed lab analysis, no abnormalities found -Completed station check, no abnormalities found -Added 1 bag of soda ash into each aeration tank -Started batch wasting process at 10:00, wasting from 12:00-1:00 for 15m^3 per train in 6 cycle's -Turned WAS pumps/valves to manuel off -Turned RAS to auto | Nobleton Water Resource Recovery Facility | 2026-01-09
WW-WEST | January | Harie Rajamithiran(OIT) working under the direction of Gavin Walker(OIC) . -Supernated sludge thickening tank and transferred to sludge holding tank -Started batch wasting process at 9:15, wasting from 11:00-1300 for 15m^3 per train -Completed lab analysis, no abnormalities found -Completed station check, no abnormalities found -Added 1 bag of soda ash into each aeration tank -Turned RAS into auto -Turned WAS pumps/valves -Completed consolidated headworks inspection -Prepared weekly compliance sample bottles | Nobleton Water Resource Recovery Facility | 2026-01-13
WW-WEST | January | Collected weekly and monthly sewage and sludge samples | Nobleton Water Resource Recovery Facility | 2026-01-07
WW-WEST | January | On site to investigate DO problems: tank 1 reading high and inconsistent, while probe 2 reading low, but consistent. No rags blocking either inlet gate. Picked a few rags off of the DO probes, which seemed to help. Verified online probes with hand held meter. Reading adequately. Reset controlling probe to tank 1, the tank with the lower reading. | Nobleton Water Resource Recovery Facility | 2026-01-11
WW-WEST | January | Collected weekly sewage samples | Nobleton Water Resource Recovery Facility | 2026-01-14
WW-WEST | January | Harie Rajamithiran(OIT) working under the direction of Gavin Walker(OIC) . -Supernated sludge thickening tank and transferred to sludge holding tank -Started batch wasting process at 11:00, wasting from 12:00-2:00 for 15m^3 per train -Completed lab analysis, no abnormalities found -Completed station check, no abnormalities found -Added 1 bag of soda ash into each aeration tank -Turned RAS into auto -Turned WAS pumps/valves -Completed aeration weir and floating solids removal -Bled condensation aeration lines -Inspected aeration DO probes, found broken compress air lines. Sent in work order for repair. -Cleaned up filter room and alum room | Nobleton Water Resource Recovery Facility | 2026-01-14
WW-WEST | January | Added 1 bag of soda ash to each train. | Nobleton Water Resource Recovery Facility | 2026-01-11
WW-WEST | January | Harie Rajamithiran(OIT) working under the direction of Daniel Hirstwood(OIC) . -Supernated sludge thickening tank and transferred to sludge holding tank -Completed lab analysis , re-did Total phosphorus on Final Effluent as initial Tot.P was 0.096 mg/L. After testing was re-done Tot.P was 0.013 mg/L , other then the aforementioned issue no abnormalities were found -Completed station check, no abnormalities found -Started batch wasting process at 11:00, wasting from 12:00-1400 for 15m^3 per train in 6 cycles -Added 1 bag of soda ash into each aeration tank -Turned WAS valves/pumps to manuel off -Turned RAS pumps to auto | Nobleton Water Resource Recovery Facility | 2026-01-12
WW-WEST | January | Harie Rajamithiran(OIT) working under the direction of Gavin Walker(OIC). -Supernated sludge thickening tank and transferred to sludge holding tank -Started batch wasting process at 10:00, wasting from 11:00-13:00 for 15m^3 per train in 6 cycles -Completed lab analysis, no abnormalities found -Completed station check, no abnormalities found -Added 1 bag of soda ash into each aeration tank -Completed filter inlet channel cleaning -Turned RAS to auto and WAS pumps/valves into manuel off | Nobleton Water Resource Recovery Facility | 2026-01-15
WW-WEST | January | Harie Rajamithiran(OIT) working under the direction of Gavin Walker(OIC). -Supernated sludge thickening tank and transferred to sludge holding tank -Completed lab analysis, no abnormalities found -Completed station check, no abnormalities found -Started batch wasting process at 9:40, wasting from 11:00-1200 for 20m^3 per train in 8 cycles -Added 1 bag of soda ash into each aeration tank -Turned WAS pumps/valves to manuel off -Turned RAS to auto -Completed sand filter valve exercise -Completed WAS, RAS and SCUM pump inspections, no abnormalities found -Completed sludge, aeration and grit blower inspections , no abnormalities found | Nobleton Water Resource Recovery Facility | 2026-01-08
WW-WEST | January | Harie Rajamithiran(OIT) working under the direction of Gavin Walker(OIC). -Completed lab analysis, no abnormalities found -Completed station check, no abnormalities found -Added 2 bags of soda ash into each aeration tank -Started batch wasting process at 10:00, wasting from 12:00-2:00 for 25m^3 per train in 8 cycles -Turned RAS to auto -Turned WAS to Manuel off -Completed basement sump pump inspection | Nobleton Water Resource Recovery Facility | 2026-01-06
WW-WEST | January | Received an alum delivery filling the tank to 3.3m Test ran the diesel generator Completed the daily lab work and station check Pulled an air lift that wasn?t pulling sand Entered data into SharePoint Cleaned air compressors and topped up oil Completed the jhsc inspection Batch wasted 25m3 from each clarifier Decanted and emptied the sludge thickening tank Inspected the sanitary sump Added 2 bags of soda ash to each aeration tank | Nobleton Water Resource Recovery Facility | 2026-01-05
WW-WEST | January | Add 1 x 25kg bags of soda ash to each aeration basin. | Nobleton Water Resource Recovery Facility | 2026-01-04
WW-WEST | January | Harie Rajamithiran(OIT) working under the direction of Daniel Hirstwood(OIC). -Supernated sludge thickening tank and transferred to sludge holding tank -Completed lab analysis, no abnormalities found -Completed station check, no abnormalities found -Started batch wasting process at 11:00, wasting from 12:00-14:00 for 25m^3 per train in 8 cycles -Added 2 bags of soda ash in each aeration tank -Turned RAS pumps in auto -Turned WAS pumps/valves in manuel off | Nobleton Water Resource Recovery Facility | 2026-01-02
WW-WEST | January | Removed outlet coupling on blower one. Installed new coupler. Ran blower and checked for leaks, okay. Left spare couplers on site. Complete. | Nobleton Water Resource Recovery Facility | 2026-01-06
WW-CEAST | January | Station Check completed(See details on SharePoint). Checked drywell. OK Checked screen room, changed out rag bin. Cleaned/hose down screen room. Pumps 3, 2, 5, and 6 available in timed-auto duty rotation every 4 hours. Pumps 1 and 4 out of service. All standby power generators available in auto. Drained condensates from the surge tanks air compressors. | Markham Leslie Pumping Station | 2026-01-23
WW-CEAST | January | On site to continue work on pump 2 VFD. Completed work on pump 2. Pump 2 back in service. Started work on pump 5 VFD. Notified ROC pump 5 is unavailable. | Markham Leslie Pumping Station | 2026-01-14
WW-CEAST | January | Station check complete and the readings have been entered into the sharepoint Responded to Barscreen 2 fault @ 10:15am. Noticed barscreen 2 rake is missing one roller. 3/4 rollers intact. Pushed out rag bins for pick up Chris R on site to assist with closing barscreen 2 inlet gate. Closed barscreen 2 inlet, shut off screen 2. Created follow up CMU3 for CMS to install a roller on screen 2 rake | Markham Leslie Pumping Station | 2026-01-21
WW-CEAST | January | Station Check completed(See details on SharePoint). Checked drywell. OK Checked screen room, changed out rag bin. Cleaned/hose down screen room. Pumps 3, 2, 5, and 6 available in timed-auto duty rotation every 4 hours. Pumps 1 and 4 out of service. All standby power generators available in auto. Drained condensates from the surge tanks air compressors. | Markham Leslie Pumping Station | 2026-01-16
WW-CEAST | January | -station check of site -reviewed SCADA -entered data into Sharepoint -inspected site -rotated bins in screen room -station okay | Markham Leslie Pumping Station | 2026-01-30
WW-CEAST | January | Station Check completed (See details on SharePoint). Checked drywell. OK checked scada, ok Checked screen room, changed out rag bin. Cleaned/hose down screen room. Pumps 3, 2, 5, and 6 available in timed-auto duty rotation every 4 hours. Pumps 1 and 4 out of service. All standby power generators available in auto. Drained condensates from the surge tanks air compressors. | Markham Leslie Pumping Station | 2026-01-26
WW-CEAST | January | On site for PMs on the bar screens , presses and compressors. All completed and back in auto | Markham Leslie Pumping Station | 2026-01-28
WW-CEAST | January | Station check complete and the readings have been entered into the sharepoint. Pushed out rag bins for pick up | Markham Leslie Pumping Station | 2026-01-28
WW-CEAST | January | Restarted the LSSS local SCADA server due to Windows updates. Notified the Remote Operations Center. | Markham Leslie Pumping Station | 2026-01-22
WW-CEAST | January | Under direction of OIC Daniel Kim. Worked with Kyle B. To remove a failed UPS from gmcp panel and use a different 24Vdc supply to power gmcp OIT. No outstanding issues remaining. | Markham Leslie Pumping Station | 2026-01-27
WW-CEAST | January | Replaced roller on barscreen 2 Replaced gearbox on screw conveyor. Looked at barscreen and will have to open gates and run tomorrow to clear channel. | Markham Leslie Pumping Station | 2026-01-27
WW-CEAST | January | On site to finish upgrades to Pump 2 and Pump 5 New capacitors installed by many and ABB New Fans installed on Pumps 2 and 5 Will place pumps in auto to test and continue to motor for normal operation. | Markham Leslie Pumping Station | 2026-01-15
WW-CEAST | January | On site to work on Pump 5 VFD. Completed work. Pump 5 back in service. | Markham Leslie Pumping Station | 2026-01-15
WW-CEAST | January | On site to lift Genie Boom from B3 to B2 with crane tech. Started disassembly of pump 4 discharge valve. Valve is removed. Pump is isolated and drained. | Markham Leslie Pumping Station | 2026-01-12
WW-CEAST | January | Station check complete and the readings have been entered into the sharepoint. Changed out rag bin. Hosed down screen room floor. Cleaned press drain | Markham Leslie Pumping Station | 2026-01-19
WW-CEAST | January | On site to work on disassembly of discharge valve #4. | Markham Leslie Pumping Station | 2026-01-13
WW-CEAST | January | Station check completed, readings entered into SharePoint. Checked drywell. OK Pumps 3, 2, 5, and 6 available in timed-auto duty rotation every 4 hours. Pumps 1 and 4 out of service. All standby power generators available in auto. Drained condensates from the surge tanks air compressors. Checked screen room. changed out rag bin. Found plugged drain and mess under the screw press. Screen was missing in the screw press causing rags to just drop through the screw press drain. Created CMU W11576992 to install the missing screen. Daniel capped the drain temporarily. Cleaned the area after clearing the mess. Hoist inspection WO completed | Markham Leslie Pumping Station | 2026-01-09
WW-CEAST | January | On site to assist ABB with scheduled work on pump 2 and pump 5 VFd?s. Started work on pump 2 VFD. Work is ongoing. Notified ROC that pump 2 is locked out and unavailable for today and overnight. Work will continue tomorrow. | Markham Leslie Pumping Station | 2026-01-12
WW-CEAST | January | Reset bar screen 2 fault alarm Inspected screen, no issues Reviewed SCADA, reset alarms | Markham Leslie Pumping Station | 2026-01-10
WW-CEAST | January | -was not able to complete all consolidated wet well work orders due to the screw press being broken and needing to be swapped -swapped out large screw press for smaller screw press, and cleaned out larger one. Larger one is not spinning. -creating a work order for maintenance -hi level alarm came in because pump duty rotated away from pump 6 which was in auto, reached 8.7m but still 7 meters from overflow, reset backup mode, put all pumps in auto that are available -pumps 1 and 4 remain OOS -pumps 2,3,5,6 in auto | Markham Leslie Pumping Station | 2026-01-08
WW-CEAST | January | On-site to complete Maximo w.os and to look into generator alarms from last night. Station check complete and the readings have been entered into the SharePoint. CMS/PCS investigated Generator alarms today. Found Generator 3 PGC needs to be replaced. CMS/PCS will schedule Thomson control to be on-site to further investigate this issue. Generator 1,2,3 warning alarms, Generator PGC/DCG not in auto alarms outstanding for the generators. Transfer test last night confirmed Generator 1 and 2 are available as an emergency power. If Generator 3 is needed in case of Powerfail, CMS electricians would need to be called out to manually start gen 3 and close G3 breaker switch Pushed out rag bins for pick up. Screen room roll-up door control still not working, PS aware of this issue. Cleaned screen room floor | Markham Leslie Pumping Station | 2026-01-07
WW-CEAST | January | Station Check completed(See details on SharePoint). Checked drywell. OK Checked screen room, changed out rag bin. Cleaned/hose down screen room. Pumps 3, 5, and 6 available in timed-auto duty rotation every 4 hours. Pumps 1,2 and 4 out of service. All standby power generators available in auto. Drained condensates from the surge tanks air compressors. Cleaned board room and entrance area for city of Toronto meeting. Checked screen room. Replaced rag bins. Screen room overhead doors fixed by property services. | Markham Leslie Pumping Station | 2026-01-12
WW-CEAST | January | Station Check completed(See details on SharePoint). Checked drywell. OK Checked screen room, changed out rag bin. Cleaned/hose down screen room. Bar Screen Bin Removal and Replacement Pumps 1,2 and 4 out of service. All standby power generators available in auto. Drained condensates from the surge tanks air compressors. Cleaned board room and entrance area for city of Toronto meeting. Reset Air Handling Unit no.2 Pumps switched back to auto duty rotation , timed every 4 hrs. | Markham Leslie Pumping Station | 2026-01-14
WW-CEAST | January | -on site with Kevin Shaji to complete consolidated wet well work order, which includes: -bar screen cleaning/lubrication -screw conveyor inspection -sluice gate exercising -wetwell inspection/cleaning -bubbler system test -high level alarm test -odour control inspection -manual valve exercise -pumps 2,3,5 manual off, pumps 1,4 OOS, pump 6 left in auto, for suction valve exercising | Markham Leslie Pumping Station | 2026-01-08
WW-CEAST | January | -on site with PCS and electrical to fix generator 1 and 2 issues, after PCG controller is having an issue -generator 3 remains OOS -put pump 5 duty 1 auto, active, pump 6 duty 2 auto, off -pumps 1 OOS, pumps 2,3 manual off to test generators 1 and 2 -will be testing generator 1 and 2 with PCS electrical to get them back in service -all 3 generators are running, was able to get gen 3 working as well, half the facility is on generator power to test generator performance, pump 3 manual on -generators seem to be working properly after PCS/electrical work -tested all 3 generators on load, after PCG controller repair, ongoing issue seems to be resolved -electrical Dan Boate, PCS Artour Litvinov and Matt Spitzig on site -will put pumps 2,3,5,6 back to auto, and site back on utility power before leaving -notifying ROC | Markham Leslie Pumping Station | 2026-01-08
WW-CEAST | January | Weather today Light Snow and -5 Celsius -On site responding to Bar screen 2 fault alarm W11556947. -Reset bar screen to monitored for a few cycles appears to be running fine now. | Markham Leslie Pumping Station | 2026-01-04
WW-CEAST | January | Station check completed, readings entered into SharePoint. Checked drywell. OK Checked screen room, changed out rag bin Monthly diesel generator test run completed with Chris, readings entered into SharePoint. 10.15 - Transferred site to generator power. 11.30 - Transferred site back to utility power. Gen 1: Start time: 227.85, Stop time: 229.1, Run time: 1:25hrs. Gen 2: Start time: 114.22, Stop time: 115.476, Run time: 1:256hrs. Gen 3: Start time: 102.19, Stop time: 103.44, Run time: 1:25hrs. | Markham Leslie Pumping Station | 2026-01-05
WW-CEAST | January | Weather today Partly Cloudy and -5 Celsius -On site to complete work orders W114690096, W11472957. -Completed station check. -Entered station readings into SharePoint. -Pumps 3, 2, 5, and 6 available in timed-auto duty rotation every 4 hours. -Pumps 1 and 4 out of service. -All standby power generators available in auto. -Switched sump pump duty. -Drained condensates from the surge tanks air compressors. -Checked dry well, ok. -Checked bar screens. Switched rag bin. Cleaned/hosed down bar screen room. -Bar Screen Bin Removal and Replacement - pushed rag bins back in after pick up by Miller Waste. -SCADA Review. | Markham Leslie Pumping Station | 2026-01-02
WW-CEAST | January | On site with Operator Barry Middleton to investigate Generator 3 PGC and DGC Not In Auto Alarms. Both PGC and DGC have power and are connected to the network. Power cycled both units without resolution. Generator 3 will require further investigation. Generator station transfer performed with Generators 1 and 2 running. Pump #3 run to test. Station transferred back to utility power. | Markham Leslie Pumping Station | 2026-01-06
WW-CEAST | January | On site to complete work orders W11515404, W11515473 Dry well consolidated WO completed. completed check valve inspection completed flood test alarm and sump pit inspection completed RS pump and motor inspection completed air relief valve inspection completed auto dialer test, BAS check cleaned seal water strainer and air compressor inspection completed. surge tanks valves, actuators and drain inspection completed. | Markham Leslie Pumping Station | 2026-01-06
WW-CEAST | January | -On site responding to Generator #1 and #2 Warning alarms also generator #3 not in Auto alarm W11565200. -On arrival I tried to reset generator #3 but unable to reset or clear alarms. -I didn?t see any issues or alarms on generator #1 and #2 and also unable to clear alarms. -Notified ROC to call in the on call electrician Kyle Rae. -Test ran Generators but only generator #1 and #2 started generator #3 didn?t start. -Will leave station with the generators #1 and #2 available for tonight and finish troubleshooting tomorrow. -Pumps 3, 2, 5, and 6 available in timed-auto duty rotation every 4 hours. -Pumps 1 and 4 out of service -Cleared outstanding alarms but unable to clear outstanding alarms for generators. | Markham Leslie Pumping Station | 2026-01-06
WW-CEAST | January | -assisted Kevin Shaji with monthly generator test run at Leslie PS | Markham Leslie Pumping Station | 2026-01-05
EAST | January | On site to complete station check. Time: 10:50 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.62 1.56 Time: 10:53 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.60 1.55 Total: 2.05 Verified analyzers with grabs. Checked station and trends. Entered data into PWQ sheet. No outstanding alarms. No OOS equipment. | Mount Albert Well 3 | 2026-01-19
EAST | January | Silicate top up: Before: 69.2cm After: 87.6cm | Mount Albert Well 3 | 2026-01-29
EAST | January | On site for station check. Duty active, tower level 66%. Verified analyzer readings with grab residuals. Influent taken 12:22 Free Grab: 1.84 mg/L Analyzer: 1.77 mg/L Effluent taken at 12:24 Free Grab: 1.70 mg/L Analyzer: 1.67 mg/L Total Grab: 1.97 mg/L Chemical systems: Chlorinator 2 open 32%, DF= 53%. Booster P1 DP= 990 kpa. Silicate P2 speed 42%, DP= 500 kpa. Visual inspection of chemical systems - all ok. Entered station readings in PWQ sheet. Reviewed trends, equipment ok. Station ok Placed well manual off at 13:04 for turbidimeter maintenance. Notified ROC. Placed well back in auto at 13:21. | Mount Albert Well 3 | 2026-01-30
EAST | January | on site to complete station check. Time: 12:50 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.72 1.76 Time: 12:55 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.68 1.66 Total: 2.00 Verified analyzers with grabs. Checked station and equipment. Entered data into PWQ | Mount Albert Well 3 | 2026-01-26
EAST | January | Silicate Top up Before: 57.6cm/1827L After: 75.9cm/2415L | Mount Albert Well 3 | 2026-01-22
EAST | January | On site to complete house keeping. No issues on site. | Mount Albert Well 3 | 2026-01-27
EAST | January | On site to complete station check. Cleaning NTU analyzer. Time: 12:05 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.85 1.80 Time: 12:08 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.71 1.70 Total: 1.99 Cleaned NTU analyzer causing a spike and interlocking well at 12:20. Cleared alarm when NTU dropped back down to 0.09 ack and reset restarted well at 12:27. Verified analyzers all ok. Checked station and trends. No OOS equipment. | Mount Albert Well 3 | 2026-01-23
EAST | January | On site to complete station check. Collecting weekly Bac-t Samples. Collecting Q1 Samples. W11550719 Weekly Bac-t Samples. W11476414 Q1 Samples. Time: 14:25 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.82 1.75 Time: 14:28 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.69 1.66 Total: 2.05 Verified analyzers on site with grabs. Checked site and trends. No OOS equipment. No outstanding alarms on site. | Mount Albert Well 3 | 2026-01-28
EAST | January | silicate top up | Mount Albert Well 3 | 2026-01-15
EAST | January | On site to complete station check. Collecting weekly Bac-t Samples. W11538262 Weekly Bac-t Samples. Time: 13:55 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.79 1.79 Time: 14:00 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.71 1.70 Total: 2.04 Verified analyzers with grabs all ok. Checked site and trends. No outstanding alarms on site. No OOS equipment on site. | Mount Albert Well 3 | 2026-01-21
EAST | January | On site to complete station check. Time: 10:57 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.92 1.98 Time: 11:00 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.70 1.73 Total: 1.96 No outstanding alarms on site. No OOS equipment on site. Verified analyzers with grabs all ok. Checked site and trends. | Mount Albert Well 3 | 2026-01-16
EAST | January | On site to complete following work orders: W11485458 Supply Fans Check W11485464 Exhaust Fans Check W11487905 Chemical System Insp. W11485470 Exercise Valves W11485484 Deep Well Exhaust Check W11485612 Standby Generator Test W11507262 Housekeeping W11485626 Chlorine Analyzer Maint. W11486006 JHSC Inspection W11486639 Chlorine Scrubber Check W11487767 Chlorine Cylinder Emergency Insp. W11487717 Chemical System Silicate Insp. Joe Williams is on site to top up silicate with silicate from Queensville wells 3/4. Start: 45.4cm/1445L Stop: 63cm/2002L Stopped well in manual at 10:52. At 12:20 started generator and well. At 13:26 shut well off and stopped generator. Attached is a copy of the generator information. Verifying analyzer after maintenance. Time: 14:05 Influent Grab (mg/l) Analyzer (mg/l) Free: 2.03 2.00 Time: 14:08 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.64 1.62 No issues with analyzers after grabs were taken. Pocket colorimeter passed calibration. Any changes in trends are due to work orders being completed on site. No issues with work orders on site. | Mount Albert Well 3 | 2026-01-15
EAST | January | Station Check (no issues found) Input data to PWQ 14:00 Verified CL17s (mg/L) Influent: Grab 1.78, A 1.86 Effluent: Grab 1.69, A 1.73 Total: Grab 1.91 15:10 #11503245, #11504389 samples | Mount Albert Well 3 | 2026-01-07
EAST | January | On site to complete station check. Time: 11:40 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.62 1.58 Time: 11:45 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.60 1.60 Total: 1.87 Informed ROC that the NTU was going to be cleaned at 11:46. Put well back to auto at 12:00. Verified analyzers with grabs. Checked station and trends. No OOS equipment. No outstanding alarms. Entered data into PWQ sheet. | Mount Albert Well 3 | 2026-01-09
EAST | January | On site to complete station check. Collecting weekly Bac-t Samples. W11522635 Weekly Bac-t Samples. Time: 10:25 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.78 1.79 Time: 10:30 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.71 1.68 Total: 1.98 Verified analyzers with grabs all ok. Checked site and trends. Entered data into PWQ. No outstanding alarms on site. No OOS equipment. | Mount Albert Well 3 | 2026-01-14
EAST | January | Restarted the Operator Interface Terminal due to Windows driver updates. Notified the Remote Operations Center and well was off and placed in Remote-Manual during the update process. | Mount Albert Well 3 | 2026-01-09
EAST | January | On site to change chlorine cylinder with Jack Palmer. Start: 0.0/44.4kg Stop: 68/44.4kg Also on site to complete station check. Time: 09:50 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.77 1.76 Time: 09:52 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.68 1.67 Total: 1.96 Verified analyzers with grabs. Checked station and trends. Cleared alarms at 10:28. Entered data into PWQ sheet. No OOS equipment. | Mount Albert Well 3 | 2026-01-12
EAST | January | On site to complete station check. Time: 11:52 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.66 1.60 Time: 11:55 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.61 1.57 Total: 1.84 Verified analyzers with grabs. No outstanding alarms on site. No OOS equipment on site. Checked site and trends. Entered data into PWQ sheet. | Mount Albert Well 3 | 2026-01-05
EAST | January | On site for station check. Duty not active, tower level 63% Verified analyzer readings with grab residuals. Influent taken 13:07 Free Grab: 2.11 mg/L Analyzer: 2.21 mg/L Effluent taken at 13:10 Free Grab: 1.54 mg/L Analyzer: 1.48 mg/L Total Grab: 1.74 mg/L Visual inspection of chemical systems - all ok. Entered station readings in PWQ sheet. Reviewed trends, equipment ok. Station ok Placed well in manual for turbidimeter cleaning and calibration. Returned to auto mode afterwards. | Mount Albert Well 3 | 2026-01-02
EAST | January | On site to complete station check. Collecting weekly Bac-t Sample. W11538262 Weekly Bac-t Sample. Time: 11:50 Grab (mg/l) Analyzer (mg/l) Free: 1.40 1.37 Total: 1.56 Checked site and trends. No outstanding alarms on site. No OOS equipment on site. Verified analyzers with grabs all ok. Activated duty for sampling wells at 11:58. | Mount Albert North Elevated Tank | 2026-01-21
EAST | January | On site to complete station check. Collecting weekly Bac-t Sample. Collecting Q1 Samples. W11550719 Weekly Bac-t Sample. W11476400 Q1 Samples. Time: 09:00 Grab (mg/l) Analyzer (mg/l) Free: 1.42 1.38 Total:1.46 Verified analyzer on site. Checked station and grabs. No outstanding alarms. No OOS equipment. | Mount Albert North Elevated Tank | 2026-01-28
EAST | January | On site to replace the CL-17 analyzer reagents. No issues on site. | Mount Albert North Elevated Tank | 2026-01-27
EAST | January | #11518638 gen #11517561 jhs #11518183 low temp #11518161 sump #11518174 heat trace (DZ created w/o 11617899 to investigate alarms (low current & low temp Outlet)) #11516817 CL17 maint. 14:00 Verified (mg/l) Free: Grab 1.37, A 1.41 Total: Grab 1.70 | Mount Albert North Elevated Tank | 2026-01-27
EAST | January | On site to complete station check. Collecting weekly Bac-t Sample. W11522635 Weekly Bac-t Sample. Time: 11:35 Grab (mg/l) Analyzer (mg/l) Free: 1.53 1.45 Total: 1.72 Verified analyzer with grabs all ok. Checked site and trends. No outstanding alarms on site. No OOS equipment. | Mount Albert North Elevated Tank | 2026-01-14
EAST | January | Station Check (no issues found) Input data to PWQ 12:45 Verified CL17 (mg/l) Free: Grab 1.39, A 1.39 Total: Grab 1.56 12:50 #11503245, #11504384, & operational samples | Mount Albert North Elevated Tank | 2026-01-07
EAST | January | On site for station check. Collected CL grab residual on Discharge Header: 12:35hrs: Free Cl2 grab residual: 1.56mg/l, Total Cl2 grab residual: 1.74mg/l Checked station readings. All information in PWQ sheet. Checked site and equipment. Equipment out of service: None. | Stouffville Zone 1 Booster Pumping Station | 2026-01-23
EAST | January | On site for station check. Collected CL grab residual on Discharge Header: 12:50hrs: Free Cl2 grab residual: 1.59mg/l, Total Cl2 grab residual: 1.67mg/l Checked station readings. All information in PWQ sheet. Checked site and equipment. Equipment out of service: None. | Stouffville Zone 1 Booster Pumping Station | 2026-01-16
EAST | January | On site for station check. Collected CL grab residual on Discharge Header: 11:05hrs: Free Cl2 grab residual: 1.37mg/l, Total Cl2 grab residual: 1.57mg/l Checked station readings. All information in PWQ sheet. Checked site and equipment. Equipment out of service: None. | Stouffville Zone 1 Booster Pumping Station | 2026-01-30
EAST | January | On site for station check. Collected CL grab residual on Discharge Header: 10:45hrs: Free Cl2 grab residual: 2.00mg/l, Total Cl2 grab residual: 2.20mg/l Checked station readings. All information in PWQ sheet. Checked site and equipment. Equipment out of service: None. | Stouffville Zone 1 Booster Pumping Station | 2026-01-19
EAST | January | On site for station check. Collected CL grab residual on Discharge Header: 11:05hrs: Free Cl2 grab residual: 1.55mg/l, Total Cl2 grab residual: 1.69mg/l Checked station readings. All information in PWQ sheet. Checked site and equipment. Equipment out of service: None. | Stouffville Zone 1 Booster Pumping Station | 2026-01-26
EAST | January | On site for station check. Checked station readings. All information in PWQ sheet. Checked site and equipment. Equipment out of service: None. | Stouffville Zone 1 Booster Pumping Station | 2026-01-12
EAST | January | On site for monthly maintenance: Conducted Generator Test Run (10:12hrs): Diesel Generator Run Monthly Test: Start Runtime: 10:12hrs (Run hrs: 513.3hrs) Fuel Start: 778.9L Stop Runtime: 11:25 (Run hrs: 514.6hrs) Fuel Stop: 750L Generator Performance Data recorded below: Battery Cell Levels: OK Battery Terminals/Cables: Ok Oil and Coolant: Ok Amps: 94amps Volts: 600 Hertz: 60 RPM: 1800 Oil Pressure: 57psi Water temp: 176 F No issues during generator run test. Ran Booster P2 and STW3 during test under load. Bypass valve exercise, BFV exercise, Y-Strainer inspection | Stouffville Zone 1 Booster Pumping Station | 2026-01-15
EAST | January | Man/off all pumps. Opened FCV to 60 l/s to deep cycle zone 1 ET to 40%. Informed ROC. | Stouffville Zone 1 Booster Pumping Station | 2026-01-13
EAST | January | On site for station check. Collected CL grab residual on Discharge Header: 10:45hrs: Free Cl2 grab residual: 1.58mg/l, Total Cl2 grab residual: 1.75mg/l Checked station readings. All information in PWQ sheet. Checked site and equipment. Equipment out of service: None. | Stouffville Zone 1 Booster Pumping Station | 2026-01-09
EAST | January | On site for station check. Collected CL2 grab residual on Discharge Header: 12:50hrs: Free Cl2 grab residual: 1.68mg/l, Total Cl2 grab residual: 1.86mg/l Checked station readings. All information in PWQ sheet. Checked site and equipment. Equipment out of service: None. | Stouffville Zone 1 Booster Pumping Station | 2026-01-05
EAST | January | @15:23 - closed FCV - STETBR Level - 43% Placed pumps back to auto - duty is active, P2 started | Stouffville Zone 1 Booster Pumping Station | 2026-01-02
EAST | January | Opened FCV to 60 l/s. Man/off pumps. | Stouffville Zone 1 Booster Pumping Station | 2026-01-02
EAST | January | Under Direction of OIC (Dan Zhou) On Site for; - Station Checks Data in PWQ Excel Workbook Grabs @ 14:30 hrs. FCl: 1.24 mg/L TCL: 1.48 mg/L Equipment OOS: none Facility OK | Stouffville Zone 1 Booster Pumping Station | 2026-01-02
EAST | January | Under Direction of OIC Dan Zhou On Site for; - Station checks - Chlorine cylinder change (bank 2) Data in PWQ workbook @ 10:44 hrs. chlorine leak alarm, informed ROC - Investigated chlorine leak and system after scrubbers cleared room, re-tested system @ 11:08 hrs. Chlorine leak alarm - Dawned PPE and investigated leak, found leaking regulator at discharge connection, replaced Parker fittings on both ends and line to PVC @ 11:44 hrs. Dawned PPE and Tested system, Alarm came in after repairs @ 12:45 OIC Joe Mazza came to site and helped diagnose the issue, took apart regulators and put back together, manually resetting the regulators, (cleared alarm) tested system, started up system, no Alarm. Influent Water Grab @ 14:18 hrs. TCL: 1.46 mg/L Analyzer 1.48 mg/L Effluent Water Grab @ 14:24 hrs. FCl: 1.99 mg/L TCl: > 4.40 mg/L Analyzer: Free Chlorine FCl: 2.07 mg/L Analyzer Total Chlorine TCl: 4.83 mg/L Simulated Free Grab @ 14:26 hrs. Sim FCl: 1.83 mg/L, Analyzer: FCl: 1.75 mg/L Duty Inactive Equipment OOS: Pump 4 Facility OK | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2026-01-19
EAST | January | On site to check station and test generator. Duty is active upon arrival. Placed pumps to man/off.? Performed pre-checks on the generator system. Gen hour: Start 460.8 hours, stop time: 461.9? Diesel fuel tank level: Start: 2987/2349L. Stop: 2987/2287. 11:00 started the generator test. Informed ROC. Ran P1 and P3 in manual to load the generator. Performed station checks while on site. 11: 20 Chlorine verification are below (grab/analyzer in mg/l) Influent total: 1.49 / 1.44 Effluent Free: 2.08 / 2.09 Sim Free: ?1.85 / 1.82 Sim Total: 2.36 (grab only) Readings are in PWQ sheet.? 12:07 Generator stopped.? Placed the pumps back to auto. Reviewed trends, station is under normal operation.? | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2026-01-23
EAST | January | On site with Travis Wyatt to perform pump 4 maintenance. Opened the manual valves to chlorinator 3. Manual start pump 4. Chlorine booster pump 1 started with chlorinator 3 in duty. Attempted to select the chlorine booster 1 to chlorinator 3 in chemical setpoint page, it did not work. Changed it back to booster 1 to chlorinator 1. Ran pump 4 for about 15 minutes.? Closed the manual ball valves around chlorinator #3. Re-assigned pump duties so that P1 and P2 are in duty 1.? Station is in standby with no outstanding alarms.? | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2026-01-20
EAST | January | Vibration testing No pumps running Unable open scada | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2026-01-26
EAST | January | Under Direction of OIC Dan Zhou On Site for; - Station checks Data in PWQ workbook Influent Water Grab @ 09:29 hrs. TCL: 1.54 mg/L Analyzer: TCl:: 1.51 mg/L Effluent Water Grab @ 09:33 hrs. FCl: 2.00 mg/L TCl: > 4.40 mg/L Analyzer: Free Chlorine FCl: 2.07 mg/L Analyzer Total Chlorine TCl: 4.92 mg/L Simulated Free Grab @ 09:42 hrs. Sim FCl: 1.74 mg/L, Analyzer: FCl: 1.73 mg/L Duty 1 Active (pumps 1 and 3) Equipment OOS: Pump 4 Facility OK | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2026-01-30
EAST | January | Under Direction of OIC Dan Zhou On Site for; - Station checks Data in PWQ workbook Influent Water Grab @ 09:05 hrs. TCL: 1.43 mg/L Analyzer 1.50 mg/L Effluent Water Grab @ 09:13 hrs. FCl: 1.98 mg/L TCl: > 4.40 mg/L Analyzer: Free Chlorine FCl: 2.06 mg/L Analyzer Total Chlorine TCl: 4.89 mg/L Simulated Free Grab @ 09:17 hrs. Sim FCl: 1.75 mg/L, Analyzer: FCl: 1.71 mg/L Duty 1 Active (pumps 1 and 3) Equipment OOS: Pump 4 Facility OK | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2026-01-28
EAST | January | Under Direction of OIC Dan Zhou On Site for; - Station checks Data in PWQ workbook Influent Water Grab @ 14:18 hrs. TCL: 1.43 mg/L Analyzer 1.44 mg/L Effluent Water Grab @ 09:18 hrs. FCl: 2.03 mg/L TCl: > 4.40 mg/L Analyzer: Free Chlorine FCl: 2.05 mg/L Analyzer Total Chlorine TCl: 4.49 mg/L Simulated Free Grab @ 09:32 hrs. Sim FCl: 1.63 mg/L, Analyzer: FCl: 1.64 mg/L Duty 1 Active (pumps 1 and 3) Equipment OOS: Pump 4 Facility OK | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2026-01-21
EAST | January | On site to check station and equipment. Duty is active upon arrival. P1 and P3 are running in duty 1.? 10:10 Chlorine verification are below (grab / analyzer in mg/l) Influent total: 1.53 / 1.46 Effluent Free: 2.08 / 2.04 Sim Free: ?1.73 / 1.74 Sim Total: 2.34 (grab only) Readings are in PWQ sheet.? Reviewed trends, station is under normal operation.? | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2026-01-26
EAST | January | Under direction of OIC Dan Zhou On site for PM?s - Fixed throat injector 1 inspection - Emergency Chlorine Repair Kit Inspection - 2 ton hoist (overhead crane) inspection - Manual Valve exercise - Pump 1-3 inspection - Chlorine analyzer maintenance influent total, effluent free and total, and simulated free - Critical air valves maintenance and inspection Chlorine analyzer maintenance; Influent Total Analyzer Start Clean @ 12:37 hrs. Stop Clean @ 13:20 hrs. Post Analyzer Maintenance Verification Grab @ 13:35 hrs. TCl: 1.51 mg/L Analyzer: 1.52 mg/L Simulated Free Chlorine Analyzer Start Clean @ 12:37 hrs. Stop Clean @ 13:20 hrs. Post Analyzer Maintenance Verification Grab @ 13:41hrs. FCl: 1.96 mg/L Analyzer: 2.01 mg/L Effluent Free Chlorine Analyzer Start Clean @ 12:37 hrs. Stop Clean @ 13:20 hrs. Post Analyzer Maintenance Verification Grab @ 13:44 hrs. FCl: 1.98 mg/L Analyzer:1.93 mg/L Effluent Total Analyzer: Start Clean @ 12:37 hrs. Stop Clean @ 13:20 hrs. Post Analyzer Maintenance Verification Grab @ 13:44 hrs. TCl: 2.88 mg/L Analyzer: 2.86 mg/L Pump 1-3 Inspections; P1: Manual Start @ 13:50 hrs. - Smooth start up, valve actuated, pump pressure gauge (630 Kpa) Manual Stop @ 14:02 P2: Manual Start @ 14:16 hrs. - Smooth start up, valve actuated, pump pressure gauge (610 Kpa) Manual Stop @ 14:27 hrs. P3: Manual Start @ 14:42 hrs. - Smooth start up, valve actuated, pump pressure gauge (broken/doesn?t read) informed team lead Dan Zhou. Manual Stop @ 14:56 hrs. Pumps 1-3 returned to auto @ 15:02 | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2026-01-15
EAST | January | Under Direction of OIC Dan Zhou On Site for; - Station checks Data in PWQ workbook Influent Water Grab @ 10:36 hrs. TCL: 1.45 mg/L Analyzer 1.47 mg/L Effluent Water Grab @ 10:43 hrs. FCl: 1.80 mg/L TCl: 3.16 mg/L Analyzer: Free Chlorine FCl: 1.74 mg/L Analyzer Total Chlorine TCl: 3.21 mg/L Simulated Free Grab @ 10:38 hrs. Sim FCl: 1.72 mg/L Analyzer: FCl: 1.73 mg/L Duty Inactive Equipment OOS: Pump 4 Facility OK | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2026-01-16
EAST | January | Under Direction of OIC Dan Zhou On Site for; - Station checks - JHSC Health and Safety Inspection - Comprehensive housekeeping Influent Water TCL: 1.43 mg/L Analyzer 1.43 mg/L Effluent Water FCl: 1.99 mg/L Analyzer: FCl: 2.04 mg/L TCl: > 4.40 mg/L Analyzer TCl: 4.70 mg/L Simulated Free Sim FCl: 1.79 mg/L Analyzer: 1.88 mg/L Pumps 2 and 3 in Duty 1 (Active) Equipment OOS: Pump 4 Facility OK | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2026-01-09
EAST | January | Under direction of OIC Joe Dan Zhou On site for PM?s; - Change chlorine cylinders on bank 1 - Perform Chlorine Leak detector test - Perform chlorine system inspection and safety equipment - Perform chlorine scrubber system check @ 09:56 OIC Joe Mazza placed booster pumps in manual off for PM?s Leak detector test successful. @ 10:39 hrs. Returned booster pumps to auto Chlorine system up and running, system inspection OK, scrubber check OK | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2026-01-08
EAST | January | Under Direction of OIC Dan Zhou On Site for; - Station checks Grab @ 10:02 hrs. Influent Water TCL: 1.48 mg/L Analyzer 1.48 mg/L Effluent Water Grab @ 10:10hrs. FCl: 1.91 mg/L Analyzer: FCl: 1.94 mg/L TCl: > 4.40 mg/L Analyzer TCl: 4.68 mg/L Simulated Free Grab @ 10:14 hrs. Sim FCl: 1.85 mg/L Analyzer: FCl: 1.90 mg/L Pumps 2 and 3 in Duty 1 (Active) Equipment OOS: Pump 4 Facility OK | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2026-01-12
EAST | January | Under Direction of OIC Dan Zhou On Site for; - Station checks Data in PWQ workbook Influent Water Grab @ 08:47 hrs. TCL: 1.43 mg/L Analyzer 1.41 mg/L Effluent Water Grab @ 08:50 hrs. FCl: 2.10 mg/L TCl: 2.96 mg/L Analyzer: Free Chlorine FCl: 2.06 mg/L Analyzer Total Chlorine TCl: 2.94 mg/L Simulated Free Grab @ 08:56 hrs. Sim FCl: 2.09 mg/L Analyzer: FCl: 2.12 mg/L Duty Inactive Equipment OOS: Pump 4 Facility OK | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2026-01-14
EAST | January | On site for CL2 Cylinder change and to swap out CL2 regulator #2. | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2026-01-08
EAST | January | Under Direction of OIC Dan Zhou On site for; - Station checks Data in PWQ Workbook Influent (Pre-Injection) Grab @ 11:58 hrs. FCl:1.46 mg/L Analyzer FCl: 1.44 mg/L Effluent (post Injection) Grabs @ 11:58 hrs. FCl: 2.09 mg/L TCl: >4.40 mg/L Analyzer Free Chlorine FCl: 2.05 mg/L Analyzer Total Chlorine: TCL: 4.68 mg/L Simulated Free Chlorine Grab @ 12:05 hrs. FCl:1.91 mg/L Analyzer FCl:1.89 mg/L Equipment: Pump 4 OOS, Pump 2/3 Active Facility OK | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2026-01-05
EAST | January | On site to check station and equipment. P2 and P3 are running in duty 1.? Chlorine grabs and station readings are in PWQ sheet. 09:40 Influent total grab = 1.46 mg/l, analyzer = 1.43 mg/l Effluent free grab = 2.12 mg/l, analyzer = 2.11 mg/l.? Lowered chlorine target from 2.1 to 2.0 mg/l.? Reviewed trends, no issues. | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2026-01-02
EAST | January | On site responding to CL2 leak alarm lockout. Chlorine leak detector level was 0.00mg/l when arriving on site and Cl2 scrubber was running. Reset emergency valve closure system and re-opened Chlorine Cylinders. No indication of leak when reporting cylinders. Checked system for leaks. No issues. Acitvated duty to run station to see if leak would return. Suspect CHlrine bank #2 regulator released gas at vent when Cylinder bank switched over. Will replaced Cl2 Bank #2 Chlorine regulat | Stouffville Zone 2 Pumping Station & Rechlorination Facility | 2026-01-06
EAST | January | On site for station check and to collect weekly micro samples (W11538350). Collected Cl2 grab residuals on Header tap @11:50hrs and Sample: FCL: 1.77mg/l Analyzer FCL: 1.77mg/l TCL: 1.91mg/l Checked station readings, verified Cl2 analyzer. All information in PWQ sheet. Equipment out of service: None. | Stouffville Zone 1 Elevated Tank | 2026-01-21
EAST | January | On site for station check and to collect weekly micro samples (W11550799) and quarterly samples (W11476582). Collected Cl2 grab residuals on Header tap @11:00hrs and Sample: FCL: 1.64mg/l Analyzer FCL: 1.65mg/l TCL: 1.85mg/l Checked station readings, verified Cl2 analyzer. All information in PWQ sheet. Equipment out of service: None. | Stouffville Zone 1 Elevated Tank | 2026-01-28
EAST | January | On site for monthly maintenance: JHSC Inspection - no issues. 09:30hrs: HACH CL17 Free Chlorine Analyzer cleaning. Verified Analyzer after cleaning: FCL Grab residual: 1.81mg/l, Analyzer: 1.84mg/l Portable Generator test run Manual valve exercise Heat trace inspection Housekeeping | Stouffville Zone 1 Elevated Tank | 2026-01-20
EAST | January | On site for station check and to collect weekly micro samples (W1150333) and ANSCAN (W11503590). Collected in house operational samples. Collected Cl2 grab residuals on Header tap @09:40hrs and Sample: FCL: 1.42mg/l Analyzer FCL: 1.40mg/l TCL: 1.63mg/l Checked station readings, verified Cl2 analyzer. All information in PWQ sheet. Equipment out of service: None. | Stouffville Zone 1 Elevated Tank | 2026-01-07
EAST | January | On site to check station and equipment. Tower is on fillling cycle upon arrival. 12:41 grab chlorine residual from header: FCL = 1.97 mg/l, TCL = 2.22 mg/l. Analyzer free = 1.96 mg/l. 12:41 collected micro sample from header, YD W11522733. 12:45 outlet grab free chlorine = 1.77 mg/l.? Station readings are entered in PWQ sheet.? Reviewed trends, no issues. | Stouffville Zone 1 Elevated Tank | 2026-01-14
EAST | January | Adjusted Tower Low level alarm back to 60% | Stouffville Zone 1 Elevated Tank | 2026-01-02
EAST | January | Under direction of OIC Dan Zhou On site for; - Station checks - Regulatory sampling ( Micro, W11538392)) - Operational sampling (nitrification) Data in PWQ workbook Regulatory sample taken @ 10:39 from north cell. South Cell Grab @ 10:39 hrs. TCl: 1.48 FCl: 0.08 Analyzer: TCl: 1.50 mg/L North Cell Grab @ 10:39 TCl: 1.45 mg/L FCl: 0.08 Cells Draining Equipment OOS: none Facility OK | Markham PD6 Reservoir | 2026-01-21
EAST | January | Under Direction of OIC Dan Zhou On site for; - Low/high water level alarm - Dehumidifier inspection and cleaning* - Sump pump inspection/test - Flood alarm test - Chlorine analyzer maintenance and cleaning (total analyzer) - Clean venting screens Flood alarm level tested at 11:10 hrs. (Successful) High/low water level test at 11:33 hrs. (Successful) Chlorine Analyzer maintenance and cleaning: Clean start at 13:10 hrs Clean stop at 13:30 hrs. Verification grabs at 13:42 TCl: 1.48 mg/L Analyzer: TCl: 1.53 mg/L *Joe Mazza had inspected the dehumidifier last PM day and had put in a work order for maintenance. I inspected and cleaned filters. Reservoir being fed by Toronto and York permissive valve open during clean/verification. | Markham PD6 Reservoir | 2026-01-08
EAST | January | On site to check station and equipment. Reservoir is on a down cycle. 09:16 grab chlorine residual from north cell: FCL = 0.05 mg/l, TCL = 1.45 mg/l. Analyzer total = 1.52 mg/l.? 09:16 collected micro sample, YD W11503375. Also collected in-house ATP and phosphorous samples. Performed SL1000 monitoring, resulted entered in PWQ sheet.? Reviewed trends, station is under normal operation.? | Markham PD6 Reservoir | 2026-01-07
EAST | January | Under direction of OIC Dan Zhou On site for; - Station checks - Regulatory sampling ( Micro, W11522775) - Operational sampling (nitrification) Data in PWQ workbook Regulatory sample taken @ 09:39 from north cell. South Cell Grab @ 09:31 TCl: 1.52 FCl: 0.06 Analyzer: TCl: 1.52 mg/L North Cell Grab @ 09:39 TCl: 1.43 mg/L FCl: 0.05 Cells Draining Equipment OOS: none Facility OK | Markham PD6 Reservoir | 2026-01-14
EAST | January | On site to check station and equipment. Tower is on a drain cycle.? 08:42 header grab Chlorine residual are: FCL = 1.58 mg/l, TCL = 1.92 mg/l.? Header analyzer readings are: FCL = 1.58 mg/l, TCL = 1.80 mg/l. 08:42 collected micro sample, YD W11551591. 08:43 collected Q1 samples, YD W11476669. 08:57 outlet grab chlorine residual are: FCL = 1.60 mg/l, TCL = 1.91 mg/l. Outlet analyzer readings are: FCL = 1.41 mg/l, TCL = 1.76 mg/l.? 09:55 standardized header total reading according to 3 grabs' average. When attempting to standardize the outlet free reading, the LED screen showed "No signal". Not able to perform standardization.? The analyzer is flat lining. W11621070 created for instrumentation. 10:17 inlet grab chlorine residuals are: FCL = 1.48 mg/l, TCL = 1.87 mg/l. Inlet analyzer reading are: FCL = 1.51 mg/l, TCL = 1.86 mg/l.? Readings are in PWQ sheet.? Reviewed trends, station is under normal operation.? Outlet analyzer is OOS and flat lining, informed ROC.? | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2026-01-28
EAST | January | Attending site to check error on Outlet Chlorine analyzer (W11621070). Analyzer was unresponsive until power was cycled. Found low flow alarm active once analyzer re-booted. Checked flow sensor and flow began to register normally again. Suspect flow sensor float may have become stuck but is not moving freely. Verified Total reading with no adjustments required. Verified Free reading and adjusted from 1.53 to 1.65mg/L. ROC was notified before and after maintenance activities. | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2026-01-28
EAST | January | On site for station check, weekly micro sampling (W11539074) Tower level - 75% and filling at 83 L/s Recorded station readings in PWQ sheets Verified analyzer reading: Header @ 10:08 Free Grab: 1.46 mg/L Analyzer: 1.50 mg/L Total Grab: 1.76 mg/L Analyzer: 1.77 mg/L Inlet @ 10:14 Free Grab: 1.48 mg/L Analyzer: 1.22 mg/L Total Grab: 1.85 mg/L Analyzer: 1.80 mg/L Adjusted inlet free chlorine analyzer after three grab samples. Outlet @ 10:23 Free Grab: 1.47 mg/L Analyzer: 1.47 mg/L Total Grab: 1.82 mg/L Analyzer: 1.75 mg/L Collected micro sample from header @ 10:16 Reviewed trends, equipment ok Station ok | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2026-01-21
EAST | January | Attended site for chlorine system inspection - all okay | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2026-01-27
EAST | January | On site for station check. Duty active - Tower level 60% and filling Recorded station readings in PWQ sheets Verified analyzer readings, took grab samples between 9:13-9:21. No adjustments needed. Reviewed trends, equipment ok. Outstanding alarms: N/A Station ok | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2026-01-26
EAST | January | On site to test Halogen lockout system alarms for SCADA. Activated and Fault alarms both work. Left actuators off cylinders as they were found. | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2026-01-27
EAST | January | On site for station check Verified chlorine analyzers, 9:04, mg/L Header: FCl - G 1.48; A 1.51 TCl - G 1.85; A 1.80 Inlet: FCl - G 1.75; A 2.15 Adjusted analyzer and continuing to monitor TCl - G 2.13; A 2.16 Outlet: FCl - G 1.48; A 1.52 TCl - G 1.85; A 1.78 Reviewed SCADA trends Inspected station equipment Recorded observations in the shared PWQ sheet Station and equipment okay | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2026-01-16
EAST | January | On site for station check Station filling at the time of station check Recorded observations in the shared PWQ sheet Verified chlorine analyzers, 14:40, recorded in the shared PWQ sheet Adjusted inlet free chlorine to match average of grabs Station and equipment okay | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2026-01-19
EAST | January | On site for station check. Duty not active - Tower level 79% and filling Recorded station readings in PWQ sheets Verified analyzer readings, took grab samples between 9:13-9:21. No adjustments needed. Reviewed trends, equipment ok Station ok | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2026-01-23
EAST | January | On site for station check, weekly micro sampling (W11504322), and operational sampling (W11503721). Tower level - 72% and draining at 32 L/s Recorded station readings in PWQ sheets Verified analyzer reading: Header @ 8:58 Free Grab: 1.62 mg/L Analyzer: 1.67 mg/L Total Grab: 2.00 mg/L Analyzer: 1.93 mg/L Inlet @ 9:10 Free Grab: 1.69 mg/L Analyzer: 2.04 mg/L Total Grab: 1.99 mg/L Analyzer: 2.05 mg/L Outlet @ 9:18 Free Grab: 1.60 mg/L Analyzer: 1.56 mg/L Total Grab: 1.95 mg/L Analyzer: 1.90 mg/L Collected micro and operational samples from header @ 9:02 and 9:07 Reviewed trends, equipment ok Station ok Tested chlorine leak alarm, notified ROC. Alarm triggered and was cleared. | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2026-01-07
EAST | January | On site for station check. Duty not active - Tower level 65% and draining at 67.04 L/s Recorded station readings in PWQ sheets Verified analyzer readings: Header @ 9:53 Free Grab: 1.50 mg/L Analyzer: 1.70 mg/L Total Grab: 1.87 mg/L Analyzer: 1.77 mg/L Adjusted free chlorine reading after three grab residuals. Inlet @ 10:01 Free Grab: 1.75 mg/L Analyzer: 2.07 mg/L Total Grab: 1.98 mg/L Analyzer: 1.99 mg/L Adjusted free chlorine reading after three grab residuals. Outlet @ 10:09 Free Grab: 1.56 mg/L Analyzer: 1.64 mg/L Total Grab: 1.86 mg/L Analyzer: 1.77 mg/L Reviewed trends, equipment ok Station ok Attempted to start portable generator for run test - could not start. | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2026-01-09
EAST | January | @10:05 Changed controlling Tower to Woodbine ET. Current power fail at West park heights | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2026-01-15
EAST | January | On site for station check and sampling W11523513 Collected samples from the station header while station draining and verified chlorine analyzers, 8:39, mg/L Header: FCl - G 1.44; A 1.49 TCl - G 1.82; A 1.74 Inlet: FCl - G 1.75; A 2.15 - monitoring TCl - G 2.07; A 2.14 Outlet: FCl - G 1.47; A 1.54 TCl - G 1.76; A 1.72 Recorded observations in shared PWQ sheet Reviewed station trends on SCADA Station and equipment okay | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2026-01-14
EAST | January | Onsite to connect Halogen IO points to PAC and upsize breaker feeding the Halogen controller. | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2026-01-08
EAST | January | On site for station check. Tower level 68% and draining at 41 L/s Recorded station readings in PWQ sheets Verified analyzer reading: Header @ 9:30 Free Grab: 1.62 mg/L Analyzer: 1.49 mg/L Total Grab: 1.99 mg/L Analyzer: 1.97 mg/L Adjusted free chlorine reading after three grab residuals. Inlet @ 9:40 Free Grab: 1.81 mg/L Analyzer: 1.75 mg/L Total Grab: 2.17 mg/L Analyzer: 2.05 mg/L Adjusted total chlorine reading after three grab residuals. Outlet @ 9:59 Free Grab: 1.65 mg/L Analyzer: 1.54 mg/L Total Grab: 2.02 mg/L Analyzer: 1.97 mg/L Adjusted free chlorine reading after three grab residuals. Reviewed trends, equipment ok Station ok | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2026-01-05
EAST | January | On site for monthly work orders, Notified ROC of work orders being done. Inlet/Outlet Heat Trace Inspection, Ventilation system inspection, Dehumidifier cleaning and inspection, Circulation pump test, JHSC inspections, Chlorine scrubber check, Actuated valve exercise, Chlorine analyzer maintenance: Flushed and cleaned y-screens, inspected analyzer reservoirs, verified chlorine residuals. Adjusted inlet analyzer free chlorine residual after three grab samples. Chlorine Gas Feed System Performance Check, And Chemical System Inspection - Chlorine. | Keswick Woodbine Elevated Tank and Rechlorination Facility | 2026-01-06
EAST | January | Under direction of OIC (Dan Zhou) On site for; - Station checks - Exercise pump 2 @ 12:04 hrs. manually started pump 2, smooth start up (500 Kpa) Grabs @ 12:23 hrs. FCl: 0.07 mg/L TCl: 1.43 mg/L Analyzer: FCl: 0.04 mg/L TCl: 1.45 mg/L @ 12:27 hrs. Returned pump 2 to manual off. Duty inactive in Manual Off after grabs Equipment OOS: None Facility OK | Markham Pumping Station | 2026-01-16
EAST | January | On site to respond to building flood alarm. Checked the chamber, it is dry. Shook the float, able to reset the alarm. Alarm cleared and station is back to normal. | Markham Pumping Station | 2026-01-23
EAST | January | On site to check station and equipment. All pumps are man/off as normal operation. 10:47 Chlorine verification are below (grab/analyzer in mg/l) Total: 1.43 / 1.41 Free: 0.02 / 0.07 Standardized free analyzer reading according to 3 grabs' average.? Readings are in PWQ sheet.? Reviewed trends, station is under normal operation.? | Markham Pumping Station | 2026-01-26
EAST | January | Under Direction of OIC (Phil Degroot) Worked with OIC Phil DeGroot On Site for PM?s - Surge System Valve exercise - JHSC Health and Safety checks - Pump and motor intention - Butterfly valve exercise - Flood alarm test - Siemens Analyzer maintenance - Eyewash cleaning and solution replacement - Dehumidifier cleaning and inspection - Generator test run - Ventilation system inspection Generator Test: Start hours: 587.6 Start time: 11:17 hrs. Stop Hours: 589.0 (includes cool down time) Stop Time: 12:40 hrs. Run Time: 1.4 hrs. Start Fuel: 612/613 L Stop Fuel: 580/578 L Pre run checks; Battery Cell Levels: Ok Battery Terminals and Cables: Ok Oil Level: Ok Coolant Level: Ok Fluid Leaks: Ok Coolant Recirculating pump: Ok Faulty Gauges: Ok @ 11:21 hrs. Put pump 3 in Manual On @ 11:43 manually stopped pump 3 @ 11:49 put pump 2 in Manual On @ 12:06 hrs. Manually stopped pump 2 @ 12:11 hrs. Manually started pump 1 @ 12:28 manually stopped pump 1 Operating Current: 30 Operating Frequency: 60.1 Hz Operating Voltage: 601 Volts, Engine speed: 1800 RPM Engine temp: 197 f Water/coolant Temp: 183 f Oil Pressure: 58 psi Analyzer Verification: 13:55 hrs. FCl: 0.01 mg/L TCl: 1.39 mg/L Analyzer: FCl: 0.01 mg/L TCl: 1.39 mg/L | Markham Pumping Station | 2026-01-22
EAST | January | Under direction of OIC (Dan Zhou) On site for; - Station checks Grabs @ 10:35 hrs. FCl: 0.04 mg/L TCl: 1.42 mg/L Analyzer: FCl: 0.02 mg/L TCl: 1.36 mg/L Duty inactive Equipment OOS: None Facility OK | Markham Pumping Station | 2026-01-30
EAST | January | On site to check station and equipment. Man/start P1 to exercise the pump. 12:01 it had un-commanded stop alarm.? Closed discharge valve locally since it was not closing in remote fashion. 12:06 man/start Pump 3. It ran for 15 minutes with no issues.? 12:30 man/start Pump 1 again. It ran for 15 minutes with no issues.? 12:53 verified chlorine analyzer reading with grab. Grab free = 0.05 mg/l, analyzer = 0.06 mg/l. Grab total = 1.46 mg/l, analyzer = 1.49 mg/l.? Station readings entered in PWQ sheet. Reviewed trends, no issues.? All pumps man/off as normal operation.? | Markham Pumping Station | 2026-01-07
EAST | January | Under direction of OIC (Stephen Baidy) On site for; - Station checks - Exercise pump 1 @ 11:16 manually started pump 1 Grabs @ 11:49 hrs. FCl: 0.06 mg/L TCl: 1.37 mg/L Analyzer: FCl: 0.05 mg/L TCl: 1.41 mg/L @ 11:52 hrs. Returned pump 1 to manual off. Duty inactive in Manual Off Equipment OOS: None Facility OK | Markham Pumping Station | 2026-01-12
EAST | January | Under direction of OIC (Dan Zhou) On site for; - Station checks Grabs @ 14:38 FCl: 0.05 mg/L Analyzer: FCl: 0.07 mg/L TCl: 1.47 mg/L Analyzer: TCl: 1.43 mg/L Duty inactive pumps in Manual Off Equipment OOS: None Facility OK | Markham Pumping Station | 2026-01-09
EAST | January | On site to check station and equipment. All pumps are man/off as normal operation. Man/Start P2 to exercise the pump. 11:15 grab free chlorine = 0.06 mg/l, analyzer free = 0.12 mg/l.? Grab total chlorine = 1.49 mg/l, analyzer total = 1.49 mg/l. Adjusted free analyzer reading to 0.05 mg/l according to 3 grabs average.? Requested ROC to exercise the rest of pumps remotely. Reviewed trends, no issues. | Markham Pumping Station | 2026-01-02
EAST | January | On site for station check and to collect weekly micro samples (W11538350) Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 2.72mg/l FCL Analyzer: 2.68mg/l 09:50hrs: Effluent Free Cl2 grab residual: 2.68mg/l FCL Analyzer: 2.67mg/l Effluent Total Cl2 grab residual: 2.88mg/l Raw collected @ 09:50hrs. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: Chlorinator #2 out of service. | Stouffville Well 3 | 2026-01-21
EAST | January | On site for station check. Collected in house Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 2.50mg/l FCL Analyzer: 2.57mg/l 10:25hrs: Effluent Free Cl2 grab residual: 2.48mg/l FCL Analyzer: 2.50mg/l Effluent Total Cl2 grab residual: 2.90mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: Chlorinator #2 out of service. | Stouffville Well 3 | 2026-01-26
EAST | January | On site with Phil to replace 500ppd regulator with 200ppd regulator and tubing. | Stouffville Well 3 | 2026-01-27
EAST | January | On site for station check and to collect weekly micro samples (W11550799) and quarterly samples (W11476540). Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 2.64mg/l FCL Analyzer: 2.65mg/l 09:10hrs: Effluent Free Cl2 grab residual: 2.50mg/l FCL Analyzer: 2.55mg/l Effluent Total Cl2 grab residual: 2.86mg/l Raw collected @ 09:15hrs. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: Chlorinator #2 out of service. | Stouffville Well 3 | 2026-01-28
EAST | January | On site for station check. Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 2.64mg/l FCL Analyzer: 2.59mg/l 11:35hrs: Effluent Free Cl2 grab residual: 2.58mg/l FCL Analyzer: 2.53mg/l Effluent Total Cl2 grab residual: 2.88mg/l Tested Chlorine Leak detector. No issues. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: Chlorinator #2 out of service. | Stouffville Well 3 | 2026-01-16
EAST | January | On site for station check. Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 2.66mg/l FCL Analyzer: 2.67mg/l 11:50hrs: Effluent Free Cl2 grab residual: 2.58mg/l FCL Analyzer: 2.62mg/l Effluent Total Cl2 grab residual: 2.84mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: Chlorinator #2 out of service. | Stouffville Well 3 | 2026-01-23
EAST | January | On site for station check. Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 2.58mg/l FCL Analyzer: 2.64mg/l 09:50hrs: Effluent Free Cl2 grab residual: 2.58mg/l FCL Analyzer: 2.55mg/l Effluent Total Cl2 grab residual: 2.84mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: Chlorinator #2 out of service. | Stouffville Well 3 | 2026-01-30
EAST | January | On site for station check. Joe Williams on site for chlorine cylinder change. Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 2.58mg/l FCL Analyzer: 2.62mg/l 09:20hrs: Effluent Free Cl2 grab residual: 2.60mg/l FCL Analyzer: 2.56mg/l Effluent Total Cl2 grab residual: 2.92mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: Chlorinator #2 out of service. | Stouffville Well 3 | 2026-01-19
EAST | January | On site for station check. Duty active, tower level 79% Verified analyzer readings with grab residuals. Influent taken 10:38 Free Grab: 2.66 mg/L Analyzer: 2.67 mg/L Effluent taken at 10:42 Free Grab: 2.52 mg/L Analyzer: 2.60 mg/L Total Grab: 2.82 mg/L Chemical systems: Chlorinator open 79%, DF= 258%. Booster P1 DP= 620 kpa Silicate P1 speed 63%, DP= 490 kpa. Visual inspection of chemical systems - all ok. Entered station readings in PWQ sheet. Reviewed trends, equipment ok. Station ok | Stouffville Well 3 | 2026-01-12
EAST | January | On site to check station and equipment. Well 3 was man/on to aid Zone 1 filling. 10:46 collected well 3 raw micro sample, YD W11522733. 10:52 effluent grab chlorine residual: FCL = 2.64 mg/l, TCL = 2.74 mg/l. Effluent analyzer free = 2.60 mg/l. 10:52 collected treated micro sample. 10:55 influent grab free = 2.64 mg/l, analyzer free = 2.64 mg/l. Station readings are entered in PWQ sheet.? Reviewed trends, no issues. Chlorine system 2 remains OOS.? | Stouffville Well 3 | 2026-01-14
EAST | January | On site for station check and to collect weekly micro samples (W1150333) Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 2.62mg/l FCL Analyzer: 2.67mg/l 11:25hrs: Effluent Free Cl2 grab residual: 2.64mg/l FCL Analyzer: 2.62mg/l Effluent Total Cl2 grab residual: 2.88mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: Chlorinator #2 out of service. | Stouffville Well 3 | 2026-01-07
EAST | January | On site to receive Silicate bulk delivery. | Stouffville Well 3 | 2026-01-15
EAST | January | On site for monthly maintenance: 12:40hrs: HACH CL17 Influent and Effluent Analyzer cleaning. Verified Analyzer after cleaning: Influent: 2.60mg/l, Analyzer: 2.64mg/l Effluent: 2.60mg/l, Analyzer: 2.57mg/l Turbidimeter maintenance and calibration completed. Conducted Silicate and Chlorine system inspection. Ran hot water through silicate system. Conducted Silicate system drawdowns and ensured proper dosing. Ran well in manual to monitor CL2 and Silicate system. Housekeeping on site. | Stouffville Well 3 | 2026-01-08
EAST | January | On site for Cl2 cylinder change with Travis Wyatt. | Stouffville Well 3 | 2026-01-08
EAST | January | On site for station check. Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 2.66mg/l FCL Analyzer: 2.67mg/l 09:40hrs: Effluent Free Cl2 grab residual: 2.60mg/l FCL Analyzer: 2.60mg/l Effluent Total Cl2 grab residual: 2.86mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: Chlorinator #2 out of service. | Stouffville Well 3 | 2026-01-09
EAST | January | On site for station check. Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 2.64mg/l FCL Analyzer: 2.71mg/l 13:20hrs: Effluent Free Cl2 grab residual: 2.64mg/l FCL Analyzer: 2.62mg/l Effluent Total Cl2 grab residual: 2.90mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: Chlorinator #2 out of service. | Stouffville Well 3 | 2026-01-05
CENTRAL | January | Restarted the Local SCADA server due to windows updates. Notified the ROC and the OIC. Plant was shutdown during the updates. | Keswick Water Treatment Plant | 2026-01-22
EAST | January | Under direction of OIC (Dan Zhou) On-site for; - station checks Data in PWQ excel Workbook Influent Water Grab @ 13:47 hrs. FCl: 2.66 mg/L Analyzer FCl: 2.66 mg/L Effluent (Treated Water) Grab @ 13:47 hrs. FCl: 2.52 mg/L TCL: 3.00 mg/L Analyzer: FCl: 2.50 mg/L Equipment OOS: Booster pump 2, Gas Chlorinator 2 Facility?s OK | Stouffville Well 3 | 2026-01-02
CENTRAL | January | -Cleaned CL17 analyzers -Performed station check - logged station readings into PWQ sheet -Changed raw total & free reagents | Keswick Water Treatment Plant | 2026-01-23
CENTRAL | January | -Reviewed filter performance, both filters 100% | Keswick Water Treatment Plant | 2026-01-28
CENTRAL | January | Onsite for station check, lab analysis, BACTI samples and regulatory samples Raw Water Grab Samples @ 14:55 Free Cl: 0.00 mg/L Total Cl: 0.03 mg/L Turbidity: 0.228 NTU Temperature: 3.0 C Raw Water analyzers @ 14:55 Free Cl: 0.01 mg/L Total Cl: 0.04 mg/L Turbidity: 0.233NTU Temperature: 1.0 C Treated Water Grab Sample @ 14:20 Free Cl: 1.50 mg/L Total Cl: 1.91 mg/L Turbidity: 0.054 NTU Temperature: 3.4 C PH: 7.24 Treated Water Analyzers @ 14:20 Free Cl: 1.48 mg/L Total Cl: 1.90 mg/L Turbidity: 0.045 NTU Temperature: 1.8 C PH: 7.24 Filter performance, both 100% Station ok | Keswick Water Treatment Plant | 2026-01-28
CENTRAL | January | Completed daily filter performance review via SCADA, both filters 100% for the month, no issues. | Keswick Water Treatment Plant | 2026-01-15
CENTRAL | January | Onsite for station check. 09:37 placed all raw water analyzers in calibration mode. Chris I. and Tyler S. onsite to investigate raw water sample line flow issues. Triggered raw water analyzer fualts due to flushing line around 09:05. 09:46 placed high lift pumps man off. 09:56 Completed filter performance review. Both filters at 100%. 10:10 initiated filter manual concurrent backwash. Run hours at 23. Found backwash pump interlocked when not in auto. Stopped aeration phase of backwash. Ben Hess notified Chris Scott of issue. Continued backwash in auto with no issues. Topped up pacl and fluoride day tanks. 12:52 collected treated sample and verified chlrine and turbidity analzyer: Free chlorine 1.16. Analyzer: 1.20. Total chlorine: 1.64. Analyzer: 1.57. Turbidity: 0.078. Analyzer: 0.06. Raw water pump back in service. Chris and Tyler found a pinch in the raw water sample line. Installed a temporary line into the wetwell to take raw water measurements. 13:00 placed high lifts back in auto. Station now running in duty 1 at 80 l/s. 13:30 Raw water ph analyzer faulted on high impedence. Flushed and cleaned probe with no improvements. SCADA reading ph 14. Analyzer on site reading typical 8.1. Jerry Zhang created work order for instrumentation to investigate. No other issues found. Chlorine pre injection dosing system continues to fail to dose. Adjuste post-injection dosing from 140 to 145% to compensate. | Keswick Water Treatment Plant | 2026-01-19
CENTRAL | January | Onsite to troubleshoot raw water pH. Informed ROC and operations Monitored pH and found it to be stable Disabled pH glass impedance warning Alarms cleared on scada Informed operations and ROC Left site | Keswick Water Treatment Plant | 2026-01-21
CENTRAL | January | -Finished the following work orders *Blowers maintenance *Replaced pre chorine regualtor | Keswick Water Treatment Plant | 2026-01-15
CENTRAL | January | Re and re 4 inch p trap over tank | Keswick Water Treatment Plant | 2026-01-21
CENTRAL | January | -Finished the following work orders *Tested pressure relief valve *Changed pre-chlor chlorine line & rebuilt chlorine ejector #2 -Responded raw water turibimeter fault alarm - notice no sample flow to the turibidimeter, resulted from raw water sample pump faulted - reset the alarm - raw water sample pump restarted - tripped out again, due to engine oil leak - a CMU4 #W11617877 has been created to have a mechanician look at it - informed ORO D. Zhou and oncall operator P. Degrout - put high lift pumps in manual off to have the plant offline over the night | Keswick Water Treatment Plant | 2026-01-27
CENTRAL | January | Checked filter performance, both 100% | Keswick Water Treatment Plant | 2026-01-23
CENTRAL | January | -Performed station check - logged station readings into PWQ sheet -Checked CL17 reagents - OK -Reviewed filter performance - 100% -Ran new diesel generator for test under normal load, 80L/s - On start-up, finish water turbidimeter spiked to 0.67NTU - Confirmed with East Area On-call operator, Jack Palmer, finish water turbidimeter is not a reportable analyzer - reviewed trends turbidity at the filter were always under 0.1NTU | Keswick Water Treatment Plant | 2026-01-30
CENTRAL | January | -Performed station check - logged station readings into PWQ sheet *Performed backwash tube maintenance -Checked CL17 reagents - OK -Troubleshooting pre chlorine not dosing - checked all the fitting and chloirnators - couldn't find the cause - will continue next Monday | Keswick Water Treatment Plant | 2026-01-16
CENTRAL | January | -Noticed some floc sludge were floating on the top of filter #1 due to a high flow at settling tank yesterday - increased PACL dosage from 7.0mg/L to 8.0mg/L under the direction of Donald Mose -Turned off pre-chlorine system to collect GLIP samples@11:45 - Restarted pre-chlorine @ 13:00 -Reduced post chlorine dosage factor from 145% to 142% due to high treated free chlorine -Reviewed filter performance - 100% -Helped commissioning diesel generator | Keswick Water Treatment Plant | 2026-01-29
CENTRAL | January | checked filter performance, both at 100% | Keswick Water Treatment Plant | 2026-01-22
CENTRAL | January | -Performed lab analysis -Finished the following work orders *Turbidimeter maintenance *Performed fluoride analyzer maintenance *Performed turbidimeter maintenance | Keswick Water Treatment Plant | 2026-01-20
CENTRAL | January | 08:34 activated filter 2 backwash remotely. Run hours at 31.5. | Keswick Water Treatment Plant | 2026-01-29
CENTRAL | January | Onsite for station check Contractors onsite load bank testing new generator Adjusted fluoride dose from 0.78 to 0.70 mg/L. Station check and lab recordings in PD sheet Checked filter performance, both at 100% Station ok | Keswick Water Treatment Plant | 2026-01-26
CENTRAL | January | -on site to assist Drew from Ferguson with the new generator tripping our ats breaker. We found that a neutral grounding bar was not removed. We removed and tested confirmed site transfer to generator by opening the main breaker. Jerry ran site on generator confirm operation. During test the raw water sample pump Vfd had tripped. We reset and increased the set point on Vfd. Confirmed operation ran plant for 30 minutes we then returned site back to normal power. Under direction of oic. | Keswick Water Treatment Plant | 2026-01-30
CENTRAL | January | Received call last night at 22:39, from ROC about hi fluoride that was persistent for 15mins at 1.10mg/l. Due to this put the hi lifts to manual for the weekend. Will inform team on Monday. | Keswick Water Treatment Plant | 2026-01-24
CENTRAL | January | Check damaged drain line | Keswick Water Treatment Plant | 2026-01-16
CENTRAL | January | Completed daily filter performance review at 15:25 via remote SCADA, both filters 100% for the month, no issues. | Keswick Water Treatment Plant | 2026-01-16
CENTRAL | January | Completed daily filter performance review via remote SCADA at 14:05, both filters 100% for the month, no new issues. | Keswick Water Treatment Plant | 2026-01-20
CENTRAL | January | Checked filter performance, both at 100% | Keswick Water Treatment Plant | 2026-01-21
CENTRAL | January | Checked filter performance, both filters 100% | Keswick Water Treatment Plant | 2026-01-27
CENTRAL | January | Completed daily filter performance review at 12:56, both filters 100% for the month. | Keswick Water Treatment Plant | 2026-01-19
CENTRAL | January | Lack of flow noticed on raw water PD pump, inspected unit and found no immediate signs of damage or wear. Inspected Suction line and notice kink/ potential crack in underwater portion of the line. Installed bypass suction line which resulted in normal pump and flow operations of the raw water tap. Ops notified of issues with original suction line. | Keswick Water Treatment Plant | 2026-01-19
CENTRAL | January | Onsite to complete station check with Jerry Zhang. Collected weekly and quarterly samples. Changed post injection chlorine cylinder B. Eric and Rick (ins) onsite and corrected fault on raw ph probe. 10:30 station running in duty at 80 l/s. Completed filter performance review. Both filters 100%. 10:32 collected raw samples. 11:35 collected treated samples. Verified analyzers (mg/l). grab 1.56 free chlorine. Analyzer 1.56. grab 1.91 total chlorine. Analyzer 1.98. Fluoride grab: 0.773. Analyzer: 0.83. Recorded all data into process sheets. 13:00 placed preinjection chlorinators man off. To work on chlorine system. Triggered alarm. Notified ROC. Connected chlorinate 1 directly to regulator one. Connected chlorinator 2 directly to regulator 2. Regulator 2 failed to engage when testing. Placed man off. Regulator 1 appears ok. Placed back in service. By 14:01 low lift analyzers reading 0.20 total chlorine. Adjusted ph dropped to 6.5 briefly triggering alarm and interlocking station. Acknowledged and cleared alarm and station resumed with ph back to target. Lee F on site and replaced a leaking p trap in the settling tube tank room. No other new issues found. | Keswick Water Treatment Plant | 2026-01-21
CENTRAL | January | On 25/01/26 Received call from ROC at 16:58 due to a hi Flouride reading of 1.36mg/l told ROC to shut plant off till Monday morning. This is a contingency entry for this issue. | Keswick Water Treatment Plant | 2026-01-29
CENTRAL | January | On-site with Jerry Zhang for station check/lab, weekly GLIP sampling, weekly micro sampling (W11522803), and monthly THM/backwash sampling (W11503203) work orders. Adjusted backwash aeration timer for both F1 and F2 from 180 to 300seconds based on filter bed observations/previous filter 2 backwash observations on January 12 2026, will monitor for improved efficiency following backwashes. Will discuss with Team Lead the possibility of concurrent backwashes while on-site as filter UFRV trending downwards. Completed station check/lab/sampling with Jerry Zhang. Treated water grab/analyzer at 10:34 results as follows: Free Cl (mg/L): G: 1.33 A: 1.34 Total Cl (mg/L): G: 1.75 A: 1.69 Turbidity (NTU): G: 0.083 A: 0.053 pH: G: 7.08 A: 7.14 Fluoride (mg/L): G: 0.71 A: 0.79 Collected raw/treated samples and manually triggered backwash for filter 2 at 10:40 for backwash sampling. Observed backwash for filter 2, will continue to monitor. Placed both fluoride pumps man/off prior to HLPs starting again following backwash which triggered fluoride/total Cl fault alarm and lolo fluoride alarm, returned fluoride pumps to auto and alarms cleared, returned to normal operating range. Filter performance review at 13:04: both filters 100% for the month, no new issues. Collected backwash raw water sample and collected composite sample for backwash treated sample over 11:35-13:35. Entered station readings into shared PWQ/Lab excel files. No other new issues found, will continue to monitor filter efficiency and pre-treatment system. | Keswick Water Treatment Plant | 2026-01-14
CENTRAL | January | Filter performance review as per workorder via scada @ 15:00 F1 and F2 100% - All ok | Keswick Water Treatment Plant | 2026-01-09
CENTRAL | January | -Changed chlorine cylinder | Keswick Water Treatment Plant | 2026-01-13
CENTRAL | January | Filter performance check via scada @ 14:30 F1 & F2 100% - all ok | Keswick Water Treatment Plant | 2026-01-07
CENTRAL | January | Filter performance review as per workorder via scada @ 3:15 PM F1 and F2 100% - All ok | Keswick Water Treatment Plant | 2026-01-12
CENTRAL | January | -Performed station check - logged station readings into PWQ sheet -Changed treated free reagents | Keswick Water Treatment Plant | 2026-01-12
CENTRAL | January | Filter performance review as per workorder via scada @ 15:00 F1 and F2 100% - All ok | Keswick Water Treatment Plant | 2026-01-13
CENTRAL | January | Monthly filter performance log, both filters at 100% | Keswick Water Treatment Plant | 2026-01-05
CENTRAL | January | On-site for station check and Lab. Ferguson Electric Contractors on-site for generator upgrade project. Topped up Fluoride day tank and PACl Wash/Day tanks. Completed lab (duty active). Adjusted CO2 adjusted target setpoint via controller from 7.3 to 7.2, will monitor. Clearwell Influent Free Cl grab/analyzer results as follows (mg/L): Free Cl Grab (11:22): 1.61 Free Cl Analyzer (11:22): 1.58 Treated Water grab/analyzer residuals at 11:25 as follows: Free Cl (mg/L): G: 1.39 A: 1.38 Total Cl (mg/L): G: 1.70 A: 1.73 Turbidity (NTU): G: 0.068 A: 0.057 pH: G: 7.29 A: 7.20 (adjusted analyzer offset from 0.15 to 0.24 to match grab results, analyzer now reading 7.29) Temperature (?C): G: 1.4 A: 1.5 No new issues found while on-site. Daily filter performance review: no issues, both filters 100% for the month. | Keswick Water Treatment Plant | 2026-01-09
CENTRAL | January | Filter performance review via scada @ 14:40 F1 and F2 100% all ok | Keswick Water Treatment Plant | 2026-01-08
CENTRAL | January | -Finished the following work orders *Washwater transfer pump inspection and maintenance *H&S inspection *Tested chlorine leak alarm *Diesel generator test run Pre-test inspection - All good -Put settling tanks' discharge valve in manual closed, low lift pumps & backwash pumps manual off -During generator run, fluoride pumps were in manual off, which caused a low fluoride alarm. Total chlorine fault alarm was attached to the fluoride alarm, as a result finished water chlorine was outstanding during generator run as well. -Raw sample pump went faulted during power source switch, which caused turbidity and pH lost sample flow and faulted. When sample flow restored, alarms reset. Diesel hours: Start=918.9 Stop 920.0 Fuel Level: Start=1843L Stop 1814L Amps=150 Voltage=620 Htz=60 Engine speed=1700RPM Water temp=172F Oil pressure=30psi Oil temp=180F -While running diesel generator, raw sample pump faulted which caused raw turbidity and pH reading faulted - reset sample pump and analyzers | Keswick Water Treatment Plant | 2026-01-08
CENTRAL | January | -Performed station check - logged station readings into PWQ sheet Grab: free=1.48mg/L total=1.86mg/L@10:45 Analyzer: free=1.44mg/L total=1.79mg/L -Checked analyzer reagents - OK -Collected weekly BacT sample YD# W11503403 & monthly algae samples YD# W11503548 | Keswick Water Treatment Plant | 2026-01-07
CENTRAL | January | @16:51 - ROC called regarding CO2 adjusted PH Lolo, filters 1/2 Lo, and settled water Lolo alarms. Low lifts had interlocked due to CO2 pH alarms. Directed ROC Christian to Ack/reset alarm, and place the filter #1 and #2 effluent valves to manual close in order to allow the filters / conduit to recover. Will check SCADA shortly. @17:12 logged onto SCADA, reviewed trends. Saw that the CO2 adjusted pH had dropped low for a short period, and immediately recovered, following a filter backwash / change in low lift flow. @17:15 placed filters #1 and 2 effluent valves back to auto, filters went back in production. Conduit levels have recovered. Facility operation has returned to normal. | Keswick Water Treatment Plant | 2026-01-03
CENTRAL | January | ROC called regarding backwash P1 uncommanded stop. Reviewed SCADA, filter 2 in backwash. The backwash process had just completed low wash #2 when the alarm came in. Filter is now in filter to waste step @07:37. Backwash is proceeding as normal. Cleared alarm on backwash P1. Will inform central team tomorrow. | Keswick Water Treatment Plant | 2026-01-01
CENTRAL | January | -Performed filter turbidity performance check - 100% | Keswick Water Treatment Plant | 2026-01-01
CENTRAL | January | -Performed filter turbidity performance check - 100% | Keswick Water Treatment Plant | 2026-01-03
CENTRAL | January | On-site with Jerry Zhang for station check/lab. Verified analyzers and topped up PACl day/wash water tanks. Found that pre-chlorine regulator 2 needs to be replaced as it is pulling in air, switched to other cylinder and will create WO to replace regulator. No other new issues found while on-site. Entered station readings into shared PWQ/lab excel files. | Keswick Water Treatment Plant | 2026-01-05
CENTRAL | January | On-site for station check/lab and cylinder change. Changed Post Cl2 cylinder B with Donald Moses. Entered station readings into shared PWQ excel/lab files. Adjusted CO2 adjusted analyzer at 12:49 to better reflect pH grab (grab of 8.05, analyzer reading 7.20). Monitored and adjusted analyzer further to better reflect grab samples, and placed setting tank valves man/closed for more consistent low lift flow while troubleshooting. New CO2 adjusted pH grab at 14:13 of 7.27, analyzer reading 7.32. Will continue to monitor. Adjusted settling tank valve cycle time to 2 hours with 30 minute offset between both valves for winter operations, will monitor. Returned settling valves to auto. Topped up PACl day/wash water tanks. Filter performance review, both filters 100%, no issues. Site running in auto/duty, no other new issues found while on-site. | Keswick Water Treatment Plant | 2026-01-02
CENTRAL | January | -Performed filter turbidity performance check - 100% -Performed station check - logged station readings into PWQ sheet | Keswick Water Treatment Plant | 2026-01-05
CENTRAL | January | Received CO2 delivery 24-124cm. | Keswick Water Treatment Plant | 2026-01-06
CENTRAL | January | -Performed filter turbidity performance check - 100% | Keswick Water Treatment Plant | 2026-01-02
EAST | January | On site for station check, weekly micro sampling (W11539060) Tower level - 69% and filling at 29.7 L/s Recorded station readings in PWQ sheets Verified analyzer reading: Outlet @ 8:52 Free Grab: 1.55 mg/L Analyzer: 1.51 mg/L Total Grab: 1.87 mg/L Collected micro and operational sample @ 8:55 from inlet/outlet. Reviewed trends, equipment ok Station ok | Sutton Elevated Tank | 2026-01-21
CENTRAL | January | -Performed filter turbidity performance check - 100% -Finished the following work orders *Chemical system inspection *Filter Top Sample Water Pump Maintenance *High Lift Pump 2 Flow Control Valve Test *Performed Washwater Transfer Pumps maintenance and inspection | Keswick Water Treatment Plant | 2026-01-06
EAST | January | On site to check station and equipment. Tower is on a filling cycle.? 12:11 header grab Chlorine residual are: FCL = 1.71 mg/l, TCL = 2.02 mg/l.? Header analyzer free readings is : FCL = 1.71 mg/l. 12:11 collected micro sample, YD W11551577. 12:12 collected Q1 samples, YD W11476703. Readings are in PWQ sheet.? Reviewed trends, station is under normal operation.? | Sutton Elevated Tank | 2026-01-28
EAST | January | Attended site for preventative maintenance work orders Completed Chlorine analyzer maintenance Hi/Lo temperature alarm test Sump pit system inspection Heat trace system inspection Housekeeping JHSC inspection Generator test run Station and equipment okay | Sutton Elevated Tank | 2026-01-15
EAST | January | On site for station check, weekly micro sampling (W11504308), and operational sampling (W11503729) Tower level - 67% and filling at 44.3 L/s Recorded station readings in PWQ sheets Verified analyzer reading: Outlet @ 11:05 Free Grab: 1.58 mg/L Analyzer: 1.61 mg/L Total Grab: 2.14 mg/L Collected micro and operational sample @ 11:09 from inlet/outlet. Reviewed trends, equipment ok Station ok | Sutton Elevated Tank | 2026-01-07
EAST | January | On site for station check and sampling W11523513 Collected samples while station draining and verified free chlorine analyzer, 9:29, in mg/L FCl - G 1.45; A 1.41 TCl - G 1.75 Recorded observations in the shared PWQ sheet Reviewed trends on SCADA Station and equipment okay | Sutton Elevated Tank | 2026-01-14
EAST | January | Onsite to download to the PAC in preparation for Tower upgrades, Tower is offline | Keswick Deer Park Elevated Tank | 2026-01-20
EAST | January | On site meet with Landmark, Capital and the linear team, in order to charge, the inlet and outlet header to the first isolation valve Tower remains isolated from the the system, with the main isolation butterfly valves closed on the inlet and outlet sides Linear team opened the distribution valves on Boyers Rd and Queensway S Opened Inlet / Outlet valves in the chamber in the yard outside the tower, once linear had confirmed distribution valves opened. Header of the inlet / outlet charged with distribution water @approx 12:00, with no issues KSETDP is isolated from the system, pressure testing of the pipe gallery will take place next week Station ok | Keswick Deer Park Elevated Tank | 2026-01-30
EAST | January | On site for station check and work orders, Visual check of station - station offline. Tested building low temperature alarm, alarm triggered and cleared. Tested Gas leak alarm, alarm triggered and cleared. Station ok. | Keswick Deer Park Elevated Tank | 2026-01-20
EAST | January | Attended site to investigate smoke alarm Contractor was grinding a flange proximal to the smoke detector. Grinding was short duration and alarm reset. Station and equipment okay | Keswick Deer Park Elevated Tank | 2026-01-16
EAST | January | On site for station check, Landmark contractors on site. Performed visual check of station, all ok. | Keswick Deer Park Elevated Tank | 2026-01-07
EAST | January | On site for station check Station is offline, in contractor custody, on site for rehabilitation. Electricians, Ernesto and Sean on site for work as well. | Keswick Deer Park Elevated Tank | 2026-01-14
EAST | January | SITE OFFLINE On site for station check and monthly work orders: Performed visual check of station, JHSC inspections, Portable generator test run. | Keswick Deer Park Elevated Tank | 2026-01-09
CENTRAL | January | -Performed station check - logged station readings into PWQ sheet -Checked CL17 reagents - OK *Tested chlorine leak alarm | Keswick West Park Reservoir | 2026-01-16
CENTRAL | January | -Responded power outage - switch station power back to city power when city power restored - stopped gas generator, more than half gasoline available - reset chlorine emergency valve fault alarm - checked SCADA - OK | Keswick West Park Reservoir | 2026-01-15
CENTRAL | January | Onsite for station check Recordings in PD sheet Station ok | Keswick West Park Reservoir | 2026-01-26
CENTRAL | January | -Performed station check - logged station readings into PWQ sheet -Checked CL17 reagents - OK | Keswick West Park Reservoir | 2026-01-19
CENTRAL | January | -Performed station check - logged station readings into PWQ sheet -Checked CL17 reagents - OK | Keswick West Park Reservoir | 2026-01-30
CENTRAL | January | wrong log entry | Keswick West Park Reservoir | 2026-01-15
CENTRAL | January | Onsite for station check and weekly BACTI sample ?Chlorine residuals @ 15:47 Grab Free: 1.60 mg/L Total: 1.81 mg/L Analyzer Free: 1.53 mg/L Analyzer Total: 1.78 mg/L Recordings in PD sheet Station ok | Keswick West Park Reservoir | 2026-01-28
CENTRAL | January | Onsite to complete station check and sampling. HAA - W11476838 MBDW - W11539217 ANSCAN- W11476838 08:54 Reservoir level at 70% and draining at 54 l/s. 08:58 Verified analyzer (mg/l). Jerry Zhang collected samples. Free chlorine grab: 1.36. Analyzer: 1.39. Total Chlorine grab: 1.69. Analyzer: 1.73. Chlorinator 1 placed back in service in duty 2 with duty rotation disabled. Outstanding work order for instrumentation to investigate its closing limit triggering failure to close alarms. No issues found. | Keswick West Park Reservoir | 2026-01-21
CENTRAL | January | -Performed station check - logged station readings into PWQ sheet -Checked CL17 reagents - OK | Keswick West Park Reservoir | 2026-01-23
CENTRAL | January | -Performed station check - logged station readings into PWQ sheet Grab: free=1.42mg/L total=1.72mg/L@9:25 Analyzer: free=1.40mg/L total=1.71mg/L -Checked CL17 reagents - OK -Collected weekly BacT sample YD# W11504690 | Keswick West Park Reservoir | 2026-01-07
CENTRAL | January | -Performed station check - logged station readings into PWQ sheet -Checked CL17 reagents - OK | Keswick West Park Reservoir | 2026-01-12
CENTRAL | January | On-site to respond to site power fail. Connected generator to site and powered on site/cleared alarms, no light in chlorine room, will ask electrical to come and investigate. Grab/analyzer results at 09:15 (mg/L): Free Cl: G: 1.33 A: 1.32 Total Cl: G: 1.60 A: 1.65 No other new issues found. Site on gen power. | Keswick West Park Reservoir | 2026-01-15
CENTRAL | January | -Finished the following work orders *H&S inspection *Gas generator test run *CL17 analyzer maintenance *Chemical system inspection | Keswick West Park Reservoir | 2026-01-13
CENTRAL | January | On-site for station check. Replaced Free Cl CL17 analyzer reagents. Tank filling upon arrival. Grab/analyzer results as follows (mg/L): Free Cl (13:51): G: 1.45 A: 1.40 Total Cl (13:51): G: 1.71 A: 1.70 No new issues found while on-site. Chlorinator 1 remains man/off but can be used if required. | Keswick West Park Reservoir | 2026-01-09
CENTRAL | January | -Performed station check - logged station readings into PWQ sheet Grab: free=1.31mg/L total=1.65mg/L@9:10 Analyzer: free=1.33mg/L total=1.66mg/L -Checked CL17 reagents - OK -Collected weekly BacT sample YD #W11523684 & quarterly sample YD #W11504676 | Keswick West Park Reservoir | 2026-01-14
CENTRAL | January | On-site for station check. Verified CL17 analyzers. Reviewed trends. No new issues found while on-site, station readings in shared PWQ excel file. Chlorinator 1 remains man/off. | Keswick West Park Reservoir | 2026-01-02
CENTRAL | January | -Performed station check - logged station readings into PWQ sheet -Changed treated total reagents | Keswick West Park Reservoir | 2026-01-05
EAST | January | On site to complete station check. Collecting weekly Bac-t Sample. W11538248 Weekly Bac-t Sample Time: 11:05 Grab (mg/l) Analyzer (mg/l) Free: 1.52 1.55 Total: 1.69 Verified analyzer with grabs all ok. Checked site and trends. No outstanding alarms on site. No OOS equipment. | Musselman's Lake Elevated Tank | 2026-01-21
EAST | January | #11488019 Heat tr #11525448 gen #11524787 jhs #11525301 valves #11525315 alt. vavle #11552754 heat tr Cl17 maint. 11:25 Verified (mg/l) Free: Grab 1.34, A 1.38 (no change) Tower Drain frozen at outfall (fenceline), w/o #11617863 | Musselman's Lake Elevated Tank | 2026-01-27
EAST | January | Thaw drain line | Musselman's Lake Elevated Tank | 2026-01-30
EAST | January | On site to complete station check. Collecting weekly Bac-t Sample. Collecting Q1 Samples. W11550705 Weekly Bac-t Sample. W11476330 Q1 Samples. Time: 10:15 Grab (mg/l) Analyzer (mg/l) Free: 1.34 1.40 Total: 1.45 Checked site and trends. Verified analyzer with grabs. Tower outlet is frozen maintenance will be coming to site to thaw it out. No outstanding alarms on site. | Musselman's Lake Elevated Tank | 2026-01-28
EAST | January | Station Check (no issues found) Input data to PWQ 9:05 Verified CL17 (mg/L) Free: Grab 1.30, A 1.36 (new reagents) Total: Grab 1.52 9:10 #11503231 weekly bact. & operational samples | Musselman's Lake Elevated Tank | 2026-01-07
EAST | January | At 08:56 adjusted duty start set point from 50% to 72%. Also cleared fire storage low alarm at this time. | Musselman's Lake Elevated Tank | 2026-01-09
EAST | January | Changed duty 1 start set point from 72% to 50% to draw it down to improve water quality. | Musselman's Lake Elevated Tank | 2026-01-06
EAST | January | On site to complete station check. Collecting weekly Bac-t Sample. W11522621weekly Bac-t Sample. Time: 12:40 Grab (mg/l) Analyzer (mg/l) Free: 1.37 1.38 Total: 1.47 Verified analyzer with grabs all ok. Checked site and trends. Activated duty at 12:43 for sampling. | Musselman's Lake Elevated Tank | 2026-01-14
EAST | January | Under direction of OIC Dan Zhou On site for; - station checks - regulatory sampling none, (W11538392) - Operational sampling, nitrification Data in PWQ workbook Regulatory sample taken @ 14:02 FCl: 0.07 TCl: 1.68 Analyzer: FCl: 0.02 TCl: 1.70 Tower at 83 % Equipment OOS: none Facility OK | Markham Milliken Elevated Tank | 2026-01-21
EAST | January | Under direction of OIC Dan Zhou On Site for PM?s; - Inlet/outlet Heat trace Inspection - Low temp alarm test - Sump pit system inspection - Chlorine analyzer maintenance - Comprehensive cleaning - JHSC health and safety inspection - Manual valve exercise - Actuated valve exercise and inspection - Dehumidifier inspection and cleaning Analyzer verification; Grabs @ 11:39 hrs. FCl: 0.08 mg/L TCl: 1.64 mg/L Analyzer: FCl: 0.02 mg/L TCl: 1.66 mg/L | Markham Milliken Elevated Tank | 2026-01-20
EAST | January | On site to check station and equipment. Tower is on a filling cycle. 13:33 grab chlorine residual, FCL = 0.04 mg/l, TCL = 1.61 mg/l. Analyzer free = 0.03 mg/l, total = 1.82 mg/l. 13:33 collected micro sample (W11503375) and in-house ATP, phosphorous samples. 13:40 standardized analyzer total reading to 1.62 mg/l (3 grabs' average) Performed SL1000 monitoring and data entered in PWQ sheet. Reviewed trends, station is under normal operation.? | Markham Milliken Elevated Tank | 2026-01-07
EAST | January | Under direction of OIC Dan Zhou On site for; - station checks - regulatory sampling none, (Micro, W11550841), quarterly samples (ANSCAN, VOC, HAA) (W11476176) - Operational sampling, nitrification Data in PWQ workbook Regulatory sample taken @ 13:15 Grabs @ 13:15 FCl: 0.08 TCl: 1.67 Analyzer: FCl: 0.04 TCl: 1.73 Tower at 58 % (Filling) Equipment OOS: none Facility OK | Markham Milliken Elevated Tank | 2026-01-28
EAST | January | Under direction of OIC Dan Zhou On site for; - station checks - regulatory sampling none, (W11522775) - Operational sampling, nitrification Data in PWQ workbook Regulatory sample taken @ 12:32 FCl: 0.07 TCl: 1.65 Analyzer: FCl: 0.02 TCl: 1.62 Tower at 53 % Equipment OOS: none Facility OK | Markham Milliken Elevated Tank | 2026-01-14
EAST | January | Under direction of OIC Dan Zhou On site for; - station checks - Regulatory sampling ( Micro, W11550841), quarterly samples (ANSCAN, VOC, HAA) (W11476176) - Operational sampling (nitrification) Data in PWQ workbook Regulatory sample taken @ 11:13 hrs. West Cell Grabs @ 11:13 hrs. FCl: 0.06 TCl: 1.41 Analyzer: FCl: 0.03 TCl: 1.50 Equipment OOS: East Cell Facility OK | Markham PD5 Reservoir | 2026-01-28
EAST | January | Under direction of OIC Dan Zhou On site for; - station checks - Regulatory sampling Micro, W11538392 - Operational sampling (nitrification) Data in PWQ workbook Regulatory sample taken @ 11:49 hrs. West Cell Grabs @ 11:49 hrs. FCl: 0.10 TCl: 1.41 Analyzer: FCl: 0.03 TCl: 1.44 Equipment OOS: East Cell Facility OK | Markham PD5 Reservoir | 2026-01-21
EAST | January | Under direction of OIC Dan Zhou On site for; - station checks - Regulatory sampling Micro, W1111522775 - Operational sampling (nitrification) Data in PWQ workbook Regulatory sample taken @ 11:17 hrs. West Cell FCl: 0.08 TCl: 1.31 Analyzer: FCl: 0.03 TCl: 1.38 @ 11:31 hrs. ROC called about a LOLO Total Chlorine alarm from 11:10 hrs. Grabs were taken and the analyzer is in range of grabs. Turning on sample tap may have disrupted the analyzer flow. Disregard alarm. Equipment OOS: East Cell Facility OK | Markham PD5 Reservoir | 2026-01-14
EAST | January | On site to check station and equipment. Reservoir is on a down cycle. 10:05 grab chlorine residual from west cell: FCL = 0.03 mg/l, TCL = 1.35 mg/l. Analyzer free = 0.07 mg/l, total = 1.38 mg/l.? 10:05 collected micro sample, YD W11503375. Also collected in-house ATP and phosphorous samples. 10:09 collected NDMA sample, YD W11476782. Performed SL1000 monitoring, resulted entered in PWQ sheet.? Performed following PMs while on site.? Chlorine analyzer maintenance Reservoir hi/low alarm test JHSC inspection External venting screen inspection Reviewed trends, station is under normal operation.? East cell remains offline due to CPD project.? | Markham PD5 Reservoir | 2026-01-07
EAST | January | Hypo delivery received: 1900L. | Stouffville Well 1 & 2 | 2026-01-27
EAST | January | On site for station check and to collect weekly micro samples (W11538350) Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 3.50mg/l FCL Analyzer: 3.57mg/l 08:40hrs: Effluent Free Cl2 grab residual: 2.11mg/l FCL Analyzer: 2.15mg/l Effluent Total Cl2 grab residual: 2.90mg/l Well 1 Raw collected @ 08:45hrs. Well2 Raw collected @ 08:45hrs. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Stouffville Well 1 & 2 | 2026-01-21
EAST | January | On site for station check. Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 3.44mg/l FCL Analyzer: 3.46mg/l 09:10hrs: Effluent Free Cl2 grab residual: 1.87mg/l FCL Analyzer: 1.93mg/l Effluent Total Cl2 grab residual: 2.34mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Stouffville Well 1 & 2 | 2026-01-30
EAST | January | On site for station check. Collected in house iron samples. Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 3.52mg/l FCL Analyzer: 3.53mg/l 09:10hrs: Effluent Free Cl2 grab residual: 222mg/l FCL Analyzer: 2.19mg/l Effluent Total Cl2 grab residual: 2.82mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Stouffville Well 1 & 2 | 2026-01-26
EAST | January | On site for station check. Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 3.56mg/l FCL Analyzer: 3.59mg/l 11:35hrs: Effluent Free Cl2 grab residual: 2.13mg/l FCL Analyzer: 2.18mg/l Effluent Total Cl2 grab residual: 2.78mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Stouffville Well 1 & 2 | 2026-01-19
EAST | January | On site for station check. Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 3.60mg/l FCL Analyzer: 3.68mg/l 10:15hrs: Effluent Free Cl2 grab residual: 2.13mg/l FCL Analyzer: 2.15mg/l Effluent Total Cl2 grab residual: 2.84mg/l Chemical System inspection completed. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Stouffville Well 1 & 2 | 2026-01-23
EAST | January | On site to receive Hypo delivery: 670L/664L to 961/955L. | Stouffville Well 1 & 2 | 2026-01-20
EAST | January | On site for station check. Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 1.78mg/l FCL Analyzer: 1.81mg/l 13:35hrs: Effluent Free Cl2 grab residual: 1.40mg/l FCL Analyzer: 1.44mg/l Effluent Total Cl2 grab residual: 1.60mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Stouffville Well 1 & 2 | 2026-01-16
EAST | January | On site for station check and to collect weekly micro samples (W11550799) and quarterly samples (W11476540). Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 3.48mg/l FCL Analyzer: 3.49mg/l 08:35hrs: Effluent Free Cl2 grab residual: 2.05mg/l FCL Analyzer: 2.09mg/l Effluent Total Cl2 grab residual: 2.84mg/l Well 1 Raw collected @ 08:40hrs. Well2 Raw collected @ 08:45hrs. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Stouffville Well 1 & 2 | 2026-01-28
EAST | January | On site for silicate bulk tank top up | Stouffville Well 1 & 2 | 2026-01-15
EAST | January | Restarted the Operator Interface Terminal due to Windows driver updates. Wells were off. Notified the Remote Operations Center before restarting the OIT. | Stouffville Well 1 & 2 | 2026-01-09
EAST | January | On site to check station and equipment. Well 1 and 2 were man/on to aid Zone 1 filling. 11:16 collected well ?1 and 2 raw micro sample, YD W11522733. 11:26 effluent grab chlorine residual: FCL = 2.28 mg/l, TCL = 2.76 mg/l. Effluent analyzer free = 2.26 mg/l. 11:26 collected treated micro sample. 11:33 influent grab free = 3.70 mg/l, analyzer free = 3.74 mg/l. Reduced chlorine residual setpoint from 3.70 to 3.60 mg/l.? Station readings are entered in PWQ sheet.? Reviewed trends, no issues. | Stouffville Well 1 & 2 | 2026-01-14
EAST | January | On site for station check. Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 3.72mg/l FCL Analyzer: 3.72mg/l 09:00hrs: Effluent Free Cl2 grab residual: 2.22mg/l FCL Analyzer: 2.27mg/l Effluent Total Cl2 grab residual: 2.94mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Stouffville Well 1 & 2 | 2026-01-09
EAST | January | Under direction of OIC Stephen Baidy Placed well pumps in manual off at 09:41 hrs. | Stouffville Well 1 & 2 | 2026-01-12
EAST | January | On site to top up hypo bulk tanks. Start: 47cm/309L 45.5cm/299L Stop: 206.4cm/1357L 206cm/1355L No issues with hypo delivery. Put wells 1 and 2 back in auto. | Stouffville Well 1 & 2 | 2026-01-13
EAST | January | On site for station check. Duty not active, tower level 88% Verified analyzer readings with grab residuals. Influent taken 12:13 Free Grab: 2.01 mg/L Analyzer: 1.94 mg/L Effluent taken at 12:15 Free Grab: 1.44 mg/L Analyzer: 1.48 mg/L Total Grab: 1.64 mg/L Visual inspection of chemical systems - all ok. Entered station readings in PWQ sheet. Reviewed trends, equipment ok. Station ok | Stouffville Well 1 & 2 | 2026-01-12
EAST | January | On site for station check. Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 3.64mg/l FCL Analyzer: 3.63mg/l 11:20hrs: Effluent Free Cl2 grab residual: 2.28mg/l FCL Analyzer: 2.27mg/l Effluent Total Cl2 grab residual: 2.90mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Stouffville Well 1 & 2 | 2026-01-05
EAST | January | On site for station check and to collect weekly micro samples (W11503333) Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 3.69mg/l FCL Analyzer: 3.77mg/l 10:20hrs: Effluent Free Cl2 grab residual: 2.15mg/l FCL Analyzer: 2.21mg/l Effluent Total Cl2 grab residual: 2.96mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Stouffville Well 1 & 2 | 2026-01-07
EAST | January | Under direction of OIC (Dan Zhou) On-site for; - Station checks - Receive hypo order Data in PWQ excel Workbook Influent Water Grab @ 13:09 hrs. Grab FCl: 1.97 mg/L Analyzer FCl: 2.00 mg/L Treated Water (Effluent) Grabs @ 13:09 hrs. Grabs FCl: 1.49 mg/L TCl: 1.71 mg/L Analyzer FCl: 1.53 mg/L Tank 1; Start cm: 60.5 cm Stop cm: 185.8 cm Start V: 398 L Stop V: 1222 L Tank 2; Start cm: 59.9 cm Stop cm: 184.7 cm Start V: 394 L Stop V: 1266 L 1650 L delivered Equipment OOS: None Facility OK | Stouffville Well 1 & 2 | 2026-01-02
EAST | January | Placed both well 1 and 2 in duty 1, auto standby. | Stouffville Well 1 & 2 | 2026-01-02
EAST | January | On site for monthly maintenance: 09:00hrs: HACH CL17 Influent and Effluent Analyzer cleaning. Verified Analyzer after cleaning: Influent: 2.60mg/l, Analyzer: 2.66mg/l Effluent: 1.95mg/l, Analyzer: 1.99mg/l Conducted Generator Test Run (09:35hrs): Diesel Generator Run Monthly Test: Start Runtime: 09:38hrs (Run hrs: 660.1) Fuel Start: 996L Stop Runtime: 10:50hrs (Run hrs: 661.4) Fuel Stop: 983L Generator Performance Data recorded below: Battery Cell Levels: OK Battery Terminals/Cables: Ok Oil and Coolant: Ok Amps: 50amps Volts: 600 Hertz: 61 RPM: 1750 Oil Pressure: 25psi Water temp: 150F Oil temp: 180F No issues during generator run test. Ran Well 2 during run test. Turbidimeter maintenance and calibration completed. Conducted chemical system inspection including injection points. JHSC Inspection | Stouffville Well 1 & 2 | 2026-01-06
EAST | January | On site for station check. Verified HACH Cl17 Analyzer and checked site and equipment. All readings in PWQ sheet. Equipment out of service: None. | Stouffville Highway 48 Booster Pumping Station | 2026-01-16
EAST | January | On site for station check. Verified HACH Cl17 Analyzer and checked site and equipment. All readings in PWQ sheet. Equipment out of service: None. | Stouffville Highway 48 Booster Pumping Station | 2026-01-23
EAST | January | On site for station check. 13:30hrs: Verified FCL Cl2 Analyzer: FCL grab residual: 1.72mg/l Analyzer: 1.70mg/l TCL grab residual: 1.76mg/l Ran air compressor to regulate water level in pressure tanks. Verified HACH Cl17 Analyzer and checked site and equipment. All readings in PWQ sheet. Equipment out of service: None. | Stouffville Highway 48 Booster Pumping Station | 2026-01-30
EAST | January | On site for station check. 14:30hrs: Cleaned HACH CL17 Analyzer. Verified Cl2 Analyzer after cleaning: Cl2 grab residual: 1.84mg/l Analyzer: 1.82mg/l Verified HACH Cl17 Analyzer and checked site and equipment. All readings in PWQ sheet. Equipment out of service: None. | Stouffville Highway 48 Booster Pumping Station | 2026-01-26
EAST | January | Station Check (no issues found) input data to PWQ | Stouffville Highway 48 Booster Pumping Station | 2026-01-19
EAST | January | Repair leak | Stouffville Highway 48 Booster Pumping Station | 2026-01-22
EAST | January | On site for station check. Verified analyzer reading with grab residuals. Effluent @ at 14:13 Free Grab: 1.71 mg/L Analyzer: 1.76 mg/L Total Grab: 1.87 mg/L Entered station readings in PWQ sheet. Station ok | Stouffville Highway 48 Booster Pumping Station | 2026-01-12
EAST | January | On site for station check. Verified HACH Cl17 Analyzer and checked site and equipment. All readings in PWQ sheet. Equipment out of service: None. | Stouffville Highway 48 Booster Pumping Station | 2026-01-09
EAST | January | Repair leak on pressure relief valve | Stouffville Highway 48 Booster Pumping Station | 2026-01-06
EAST | January | On site for station check. Readings in PWQ sheet. No issues on site. | Stouffville Highway 48 Booster Pumping Station | 2026-01-05
EAST | January | #11505552 Generator Test Pre-check complted Start: 1019.7hrs, 9:18am, Fuel 69.1cm/673L End: 1021.2hrs,10:40am, Fuel 67.2cm/653L 30min readings: 60hz, 30amps, oil press 60psi, water temp 130F, oil temp 150F #11508071 Silicate system, draw down performed (no change) #11505491 Hypo system Hypo daytank top up Before: 52.5cm/271L After: 73.5cm/ 380L | Ballantrae Well 1 & 2 | 2026-01-20
EAST | January | Under direction of OIC (Dan Zhou) On Site for; - Station Checks Data in PWQ Workbook Grabs @ 12:03 FCl: 1.87 mg/L TCL: 2.08 mg/L Analyzer: FCl: 1.93 mg/L Turbidity spike due running air compressor. Equipment out of Service: None Facility OK | Stouffville Highway 48 Booster Pumping Station | 2026-01-02
EAST | January | On site to complete station check. Time: 09:43 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.94 1.94 Time: 09:45 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.72 1.72 Total: 2.08 No outstanding alarms on site. Checked station and trends. Verified analyzers with grabs. No OOS equipment. | Ballantrae Well 1 & 2 | 2026-01-23
EAST | January | On site to receive Hypo: 150L. | Ballantrae Well 1 & 2 | 2026-01-27
EAST | January | Silicate top up: Before: 34.3cm/ 2090L After: 43.8cm/ 2670L | Ballantrae Well 1 & 2 | 2026-01-29
EAST | January | On site to complete station check. Collecting weekly Bac-t Samples. W11538248 Weekly Bac-t Samples. Time: 09:55 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.94 1.94 Time: 10:00 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.70 1.70 Total: 2.01 Verified analyzers with grabs all ok. Checked site and trends. No outstanding alarms on site. No OOS equipment on site. At 10:02 started up well 2 for sampling. Shut down well 2 at 10:32 and reactivated well 1 at 10:33. | Ballantrae Well 1 & 2 | 2026-01-21
EAST | January | On site for station check. Duty not active, tower level 92%. Contractors on site. Verified analyzer readings with grab residuals at 10:13, no adjustments needed. Visual inspection of chemical systems - all ok. Entered station readings in PWQ sheet. Reviewed trends, equipment ok. Station ok. | Ballantrae Well 1 & 2 | 2026-01-30
EAST | January | On site to complete station check. Time: 14:16 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.81 1.81 Time: 14:20 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.57 1.65 Total: 1.96 Verified analyzers with grabs. Checked station and trends. No outstanding alarms on site. No OOS equipment on site. | Ballantrae Well 1 & 2 | 2026-01-16
EAST | January | On site to complete station check. Collecting weekly Bac-t Samples. Collecting Q1 Samples. Time: 10:55 Influent Grab (mg/l) Analyzer (mg/l) Free: 2.06 2.09 Time: 10:58 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.53 1.58 Total: 1.84 Verified analyzers on site with grabs. Checked site and trends. No OOS equipment on site. No outstanding alarms on site. Shut down well 2 after sampling at 12:10. Put both wells and activated well 1 in duty at 12:11. Samples without issue. | Ballantrae Well 1 & 2 | 2026-01-28
EAST | January | 7:34 Manual stopped well 1. ROC informed hypo day tank containment flood alarm. Operator will attend site. | Ballantrae Well 1 & 2 | 2026-01-22
EAST | January | On site to complete station Time: 10:00 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.79 1.74 Time: 10:03 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.60 1.51 Total: 1.85 Verified analyzers on site. Checked station. | Ballantrae Well 1 & 2 | 2026-01-26
EAST | January | On site to replace 1/2 inch tubing in the vent line that caused a hypo containment leak. Pumped the containment down and into hypo carboys. No other issues on site. Activating pump in duty to test. No issues with hypo system. | Ballantrae Well 1 & 2 | 2026-01-22
EAST | January | On site to complete station check. Time: 13:45 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.85 1.84 Time: 13:48 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.74 1.66 Total: 1.97 Verified analyzers with grabs all ok. Checked site and trends. No outstanding alarms on site. No OOS equipment on site. | Ballantrae Well 1 & 2 | 2026-01-19
EAST | January | On site to complete station check. Collecting weekly Bac-t Samples. W11522621 Weekly Bac-t Samples. Time: 13:07 Influent Grab (mg/l) Analyzer (mg/l) Free: 2.11 2.14 Time: 13:10 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.50 1.58 Total: 1.87 Verified analyzers with grabs all ok. Checked site and trends. No outstanding alarms on site. No OOS equipment. | Ballantrae Well 1 & 2 | 2026-01-14
EAST | January | On site to top up silicate bulk tank with silicate from Aurora wells 1-4. Start: 27.3cm/1665L Stop: 40.7cm/2481L While on site completed JHSC inspection and house keeping work orders. No issues with top up and no issues with work orders. | Ballantrae Well 1 & 2 | 2026-01-08
EAST | January | Re and re block heater on diesel Check coolant level Fill block heater with coolant Need electrician to wire it | Ballantrae Well 1 & 2 | 2026-01-14
EAST | January | Check diesel block heater Plug burnt up. Ordering new one | Ballantrae Well 1 & 2 | 2026-01-07
EAST | January | On site to complete station check. Time: 08:50 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.83 1.75-1.83 after multiple grabs adjusted the influent CL-17 analyzer from 1.75mg/l to 1.83mg/l at 08:50. Time: 08:52 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.83 1.84 Total: 2.12 Verified analyzers with grabs all ok. Checked station and trends. No outstanding alarms. No OOS equipment. | Ballantrae Well 1 & 2 | 2026-01-09
EAST | January | Station Check (no issues found) Input data to PWQ 10:00 Verified CL17s (mg/l) Influent: Free Grab 1.96, A 2.02 Effluent: Free Grab 1.52, A 1.65 (adjusted to match grabs) Total: Grab 1.80 # 11503231 weekly bact. 10:10 treated & well 2 raw), (10:30 well 1 raw) 10:20 Well 1, switched from duty 2 to duty 1 | Ballantrae Well 1 & 2 | 2026-01-07
EAST | January | On site to complete following work orders and station check. W11505680 NTU Maintenance. W11505522 CL-17 Chlorine Analyzer Maint. W11505599 CL-17 Chlorine Analyzer Maint. Time: 11:50 Influent Grab (mg/l) Analyzer (mg/l) Free: 2.19 2.19 Time: 11:54 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.60 1.54 Total: 1.94 Cleared all alarms associated with chlorine analyzer maintenance. Started well up at 11:26 to run for operational sampling collection. Verified analyzer with grabs after maintenance no issues. Also pocket colorimeter passed its calibration. Changed reagents for the influent and effluent free CL-17 analyzers on site. Hypo tank was topped up. Start: 46.86cm Stop: 80.96cm Stopped well at 12:01. Completed NTU analyzer maintenance. Replaced vial with a new one. Any changes in trends are due to work orders being completed. | Ballantrae Well 1 & 2 | 2026-01-12
EAST | January | On site for station check. Duty not active, tower level 74% Verified analyzer readings with grab residuals. Influent taken 10:34 Free Grab: 1.68 mg/L Analyzer: 1.72 mg/L Effluent taken at 10:38 Free Grab: 1.71 mg/L Analyzer: 1.79 mg/L Total Grab: 1.93 mg/L Visual inspection of chemical systems - all ok. Entered station readings in PWQ sheet. Reviewed trends, equipment ok. Station ok Received Hypo delivery Start level: 258 L Stop level: 434 L | Ballantrae Well 1 & 2 | 2026-01-02
EAST | January | On site to complete station check. Time: 09:20 Influent Grab (mg/l) Analyzer (mg/l) Free: 2.03 2.01 Time: 09:25 Effluent Grab (mg/l) Analyzer (mg/l) Free: 2.00 2.02 Total: 2.20 No outstanding alarms on site. No OOS equipment on site. Verified analyzers with grabs all ok. Checked site and trends. | Ballantrae Well 1 & 2 | 2026-01-05
EAST | January | On site to complete station check. Time: 10:10 Influent Grab (mg/l) Analyzer (mg/l) Free: 2.14 2.22 Time: 10:15 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.55 1.60 Total: 1.74 Verified analyzers with grabs on site. Checked station and trends. No outstanding alarms on site. No OOS equipment. | Ballantrae Well 3 | 2026-01-23
EAST | January | On site to complete station check. Collecting weekly Bac-t Samples. W11538248 Weekly Bac-t Samples. Time: 09:15 Influent Grab (mg/l) Analyzer (mg/l) Free: 2.15 2.20 Time: 09:18 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.60 1.55 Total: 2.18 Verified analyzers with grabs. Checked site and trends. No outstanding alarms on site. No OOS equipment. | Ballantrae Well 3 | 2026-01-21
EAST | January | On site to top up silicate day tank with silicate from Queensville wells 3/4. Start: 135L Stop: Was not able to top up silicate due to pump being frozen. | Ballantrae Well 3 | 2026-01-16
EAST | January | Silicate top up: before: 20L (approx) after: 195L | Ballantrae Well 3 | 2026-01-29
EAST | January | On site for station check. Duty active, tower level 87%. Contractors on site. Verified analyzer readings with grab residuals. Influent taken 9:18 Free Grab: 2.17 mg/L Analyzer: 2.23 mg/L Effluent taken at 9:20 Free Grab: 1.55 mg/L Analyzer: 1.55 mg/L Total Grab: 1.84 mg/L Chemical systems: Chlorinator 2 open 52%, DF= 68%. Booster P1 DP= 1490 kpa. Silicate P1 speed 28%, DP= 740 kpa. Visual inspection of chemical systems - all ok. Entered station readings in PWQ sheet. Reviewed trends, equipment ok. Station ok | Ballantrae Well 3 | 2026-01-30
EAST | January | On site for Influent free lo lo chlorine lockout Cleaned Influent free chlorine analyzer and replaced reagents. Verified analyzer flow Placed chlorine booster pump 1 and chlorinator 1 in manual off, duty 3 and disabled duty rotation. Tested chlorine booster pump 2 and chlorinator 2. Verified booster pump making vacuum and verified chlorinator rotameter Backflushed well between 13:30 and 15:30 at approximately 5 L/s until an Influent free chlorine of 0.70 mg/L was achieved on the analyzer. Directed the backflush water towards the driveway as per Shahin (Torbear), because unable to access the chamber. Ran the well in manual, monitoring Influent free chlorine for recovery. Informed ROC that well is back in service. Carter will monitor well for one hour to ensure the contact tank has turned over. Station and equipment okay | Ballantrae Well 3 | 2026-01-31
EAST | January | On site to complete station check. While on site fixed the silicate pump 1 injection point and put it into auto for the weekend. At 12:54 activated pump in manual to test silicate pump 1 injection point. At 13:34 put well back to auto and that shut down the well. Time: 13:20 Influent Grab (mg/l) Analyzer (mg/l) Free: 2.18 2.22 Time: 13:25 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.57 1.54 Total: 1.72 Verified analyzers with grabs all ok. Checked site and trends. No outstanding alarms on site. No OOS equipment on site. | Ballantrae Well 3 | 2026-01-16
EAST | January | On site to complete station check. Time: 10:40 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.47 1.47 Time: 10:43 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.48 1.52 Total: 1.66 Checked site and station. Verified analyzers with grabs. Entered data into PWQ sheet. | Ballantrae Well 3 | 2026-01-26
EAST | January | On site with Phillip Degroot to change Cl2 Cylinder. | Ballantrae Well 3 | 2026-01-27
EAST | January | On site to complete station check. Time: 12:30 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.62 1.58 Time: 12:32 Effluent Grab (mg/) Analyzer (mg/l) Free: 1.58 1.56 Total: 1.73 Verified analyzers with grabs all ok. Checked site and trends. No outstanding alarms on site. No OOS equipment on site. | Ballantrae Well 3 | 2026-01-19
EAST | January | On site to complete station check. Collecting weekly Bac-t Samples. Collecting Q1 Samples. W11550705 Weekly Bac-t Samples. W11476344 Q1 Samples. Time: 12:25 Influent Grab (mg/l) Analyzer (mg/l) Free: 2.14 2.22 Time: 12:30 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.57 1.59 Total: 1.78 Verified analyzers with grabs. Checked station and trends. No OOS equipment. No outstanding alarms. | Ballantrae Well 3 | 2026-01-28
EAST | January | On site due to investigate call from ROC for generator running alarm, chlorine gas leak alarm, and gas scrubber running on SCADA. Generator and scrubber not running at time of arrival. Checked trends - no indication of a gas leak and No issues in the chlorine room. Scrubber system ok. Generator off but still hot. Station ok. | Ballantrae Well 3 | 2026-01-30
EAST | January | On site to top up silicate day tank with silicate from Aurora wells 1-4. Start: 89L Stop: 195L No issues with silicate top up. | Ballantrae Well 3 | 2026-01-08
EAST | January | On site to complete station check. Time: 09:52 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.59 1.58 Time: 09:55 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.54 1.54 Total: 1.74 No outstanding alarms on site. No OOS equipment on site. Checked site and trends. Verified analyzers with grabs. | Ballantrae Well 3 | 2026-01-09
EAST | January | On site to complete station check. Collecting weekly Bac-t Samples. W11522621 Weekly Bac-t Samples. Time: 14:20 Influent Grab (mg/l) Analyzer (mg/l) Free: 2.10 2.16 Time: 14:23 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.53 1.52 Total: 1.74 Verified analyzers with grabs all ok. Checked station and trends. Silicate pump 1 will be OOS for the night. Will be fixed tomorrow. No outstanding alarms. | Ballantrae Well 3 | 2026-01-14
EAST | January | Station Check (no issues found) Input data to PWQ 11:25 Verified CL17s (mg/L) Influent: Free Grab 2.07, A 2.13 Effluent: Free Grab 1.46, A 1.52 Total: Grab 1.71 New reagents for both CL17s 11:35 #11503231 weekly bact. samples | Ballantrae Well 3 | 2026-01-07
EAST | January | On site to complete following work orders: W11507282 House Keeping W11533779 Chlorine Emergency Repair Kit Insp. W11535651 Silicate Inspection W11533789 Low Temp Alarm Test W11533800 Exhaust Fan Check W11533806 Supply Fan 1 Check W11535675 CL2 Chemical System Insp. W11533830 Valve Exercise W11533844 CL2 Scrubber Check W11533854 Generator Test W11535145 JHSC Inspection W11533902 Well Pump Oil Drip Insp. W11533907 CL2 Analyzer Maint. W11535225 NTU Analyzer Maint. At 09:06 called ROC to inform them of work to be completed. Also at this time put the well in manual off. Verifying chlorine analyzers with grabs after maintenance. Time: 10:20 Influent Grab (mg/l) Analyzer (mg/l) Free: 1.51 1.48 Time: 10:22 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.54 1.56 Calibrated pocket colorimetre passed. No issues with grabs verifying chlorine analyzers. Started generator test at 12:10. Started well in manual at 12:11. Stopped well at 13:04. While generator and well were running silicate pump 1 5/8inch line popped out and had to be isolated. Pump 1 will remain off for the night I?ll it can be fixed tomorrow. Before Diesel Generator Test Run Sheet running generator, the following were inspected: Battery cell levels Battery terminal and cables Oil level Coolant level Fluid leaks Coolant Recirculating pump Faulty gauges Diesel generator start time: 12:10 hrs Diesel hours at start: 407.5 Fuel Level @ start: Tank #1 ~ 89.2cm Tank #2 ~ 83.9cm Start time: 12:10 After 30 min of running: Operating current = 74A Operating frequency = 60 Hz Operating voltage = 600 V Engine speed = 1800 RPM Water temperature = 174 F Oil temperature = 195 F Oil pressure = 52 psi Fuel pressure. = ? Pyrometer/Exhaust = Stopped and transferred power to hydro @ 13:09 hrs Diesel generator hours after shutdown: 408.8 hrs Tank #1 ~ 88.5cm Tank #2 ~ 83.1cm Additional information/ Observations: Activated duty and conducted generator test under load, no issues. No issues with work orders on site. | Ballantrae Well 3 | 2026-01-13
EAST | January | On site to complete station check. Time: 14:33 Influent Grab (mg/l) Analyzer (mg/l) Free: 2.10 2.12 Time: 14:35 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.48 1.45 Total: 1.64 Activated well at 14:13. No outstanding alarms on site. No OOS equipment on site. Checked site and trends. At 14:43 shut well 3 off and put it into auto. | Ballantrae Well 3 | 2026-01-12
EAST | January | On site for station check. Duty active, tower level 72% Verified analyzer readings with grab residuals. Influent taken 12:33 Free Grab: 2.11 mg/L Analyzer: 2.21 mg/L Effluent taken at 12:35 Free Grab: 1.30 mg/L Analyzer: 1.36 mg/L Total Grab: 1.59 mg/L Chemical systems: Chlorinator 1 open 52%, DF= 73%. Booster P1 DP= 1450 kpa. Silicate P2 speed 22%, DP= 695 kpa. Visual inspection of chemical systems - all ok. Entered station readings in PWQ sheet. Reviewed trends, equipment ok. Station ok | Ballantrae Well 3 | 2026-01-02
EAST | January | On site to complete station check. Time: 10:30 Influent Grab (mg/l) Analyzer (mg/l) Free: 2.16 2.21 Time: 10:33 Effluent Grab (mg/l) Analyzer (mg/l) Free: 1.57 1.62 Total: 1.76 No outstanding alarms on site. No OOS equipment Verified analyzers with grabs all ok. Checked site and trends. Contractors on site working in pump room. | Ballantrae Well 3 | 2026-01-05
EAST | January | Repair leak on high lift 2 flow control valve Had panel switch duties pump 1 wouldn?t shut off shut off manually. Ran two then switched to pump 1 Had panel switch back to pump 2 and it kept running while 2 started finally shut down Operations is going to test it and keep an eye on it | Stouffville Reservoir and Wells 5 & 6 | 2026-01-22
EAST | January | On site for station check. Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 1.87mg/l FCL Analyzer: 1.90mg/l 10:40hrs: High Lift Effluent Free Cl2 grab residual: 1.82mg/l FCL Analyzer: 1.87mg/l Effluent Total Cl2 grab residual: 1.95mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Stouffville Reservoir and Wells 5 & 6 | 2026-01-16
EAST | January | On site for station check. Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 1.91mg/l FCL Analyzer: 1.95mg/l 09:00hrs: High Lift Effluent Free Cl2 grab residual: 1.81mg/l FCL Analyzer: 1.80mg/l Effluent Total Cl2 grab residual: 1.95mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Stouffville Reservoir and Wells 5 & 6 | 2026-01-23
EAST | January | On site for station check. Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 2.10mg/l FCL Analyzer: 2.11mg/l 12:55hrs: High Lift Effluent Free Cl2 grab residual: 1.92mg/l FCL Analyzer: 1.91mg/l Effluent Total Cl2 grab residual: 2.02mg/l There is a broken nipple on HLP2 flow control valve causing a leak. HLP 2 placed to local off. WO issued to maintenance. HLP1 placed to Duty 1. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Stouffville Reservoir and Wells 5 & 6 | 2026-01-30
EAST | January | On site for station check. Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 1.88mg/l FCL Analyzer: 1.94mg/l 12:30hrs: High Lift Effluent Free Cl2 grab residual: 1.83mg/l FCL Analyzer: 1.82mg/l Effluent Total Cl2 grab residual: 1.94mg/l Switched influent discharge line from West Cell to East Cell and Sample lines. Conducted monthly maintenance: 12:55hrs: Cleaned Influent HACH CL17 Analyzer. Verified Cl2 Analyzer after cleaning: Cl2 grab: 1.96mg/l, Analyzer: 1.94mg/l JHSC Inspection. Turbidimeter maintenance and calibration. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Stouffville Reservoir and Wells 5 & 6 | 2026-01-26
EAST | January | #11497753 Generator Test Pre-check complete 13:10 Start: 13.10hrs, Fuel 90%, 69.7cm (3112L) 30 minute check (1799 rpm, oil pres 37.7psi, coolant temp 168.8F)( 60hz, 598V, 46.89amps) 14:15 End: 14.25hrs, Fuel 90%, 69.4cm (3101L) #11547330 CL17 maint (hi lift) 13:30 Verified (mg/L): Free: Grab 1.72, A 1.76 Total Grab: 1.85 | Stouffville Reservoir and Wells 5 & 6 | 2026-01-22
EAST | January | On site for Chlorine leak alarm test and chlorine scrubber check. | Stouffville Reservoir and Wells 5 & 6 | 2026-01-27
EAST | January | On site for station check and to collect weekly micro samples (W11538350) Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 2.06mg/l FCL Analyzer: 2.06mg/l 11:15hrs: High Lift Effluent Free Cl2 grab residual: 1.84mg/l FCL Analyzer: 1.84mg/l Effluent Total Cl2 grab residual: 1.95mg/l Well 5 collected @ 10:45hrs. Well 6 collected @ 10:50hrs. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Stouffville Reservoir and Wells 5 & 6 | 2026-01-21
EAST | January | On site for station check and to collect weekly micro samples (W11550799) and Quarterly Samples (W11476526). Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 2.09mg/l FCL Analyzer: 2.08mg/l 12:55hrs: High Lift Effluent Free Cl2 grab residual: 1.91mg/l FCL Analyzer: 1.93mg/l Effluent Total Cl2 grab residual: 2.01mg/l Well 5 collected @ 12:35hrs. Well 6 collected @ 12:20hrs. Chlorine System inspection. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Stouffville Reservoir and Wells 5 & 6 | 2026-01-28
EAST | January | Station Check (no issues found) Input data to PWQ Verified CL17s (mg/l) 15:26 Influent Free: Grab 2.08, A 2.15 (new reagents) 15:10 Effluent Free: Grab 1.84, A 1.88 (new reagents) | Stouffville Reservoir and Wells 5 & 6 | 2026-01-19
EAST | January | On site for station check and to collect weekly micro samples (W1150333) Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 2.03mg/l FCL Analyzer: 2.05mg/l 08:55hrs: High Lift Effluent Free Cl2 grab residual: 1.86mg/l FCL Analyzer: 1.88mg/l Effluent Total Cl2 grab residual: 2.00mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Stouffville Reservoir and Wells 5 & 6 | 2026-01-07
EAST | January | On site to respond to influent chlorine lolo alarm. Well 5 and 6 are interlocked due to the alarm. 13:14 grab influent chlorine free = 0.01 mg/l. 13:15 Started chlorine booster 2 with chlorinator 2 locally to dose chlorine to reservoir.? Reviewed trends, the lolo influent happened shortly after high lift pump shut off. Man/off HLP1 that was running, notice the cl2 BPS2 discharge pressure (post PRV) dropped from 100 psi to around 30 psi. Adjusted the PRV.? 13:38 Tested HLP shut off again. The discharge pressure post cl2 booster pump PRV stayed the same around 98 psi.? 13:40 grab influent free = 0.75 mg/l. 13:41 Stopped manual dosing chlorine and return chlorine #2 system back to auto.? 13:44 grab influent free > 2.2 mg/l.? Ack+Reset alarms and activated well duty.? Chlorine #1 system is in duty 1.? 13:56 Tested another HLP shut down.? Chlorine #1 stayed the same performance.? 14:04 Ack+reset all alarms and return the station back to normal operation. HLP1 and well 5, 6 are active in duty.? | Stouffville Reservoir and Wells 5 & 6 | 2026-01-14
EAST | January | On site to check station and equipment. Well duty and Zone 2 system duty is off. 08:30 Manual start HLP2 and switched it to duty 1 as well. Activated well 5 and 6 duty.? 08:40 grab influent free = 2.11 mg/l, analyzer free = 2.11 mg; Chlorine booster pump 1 discharge pressure = 100 psi.? Adjusted the PRV so the post PRV presssure is at 90 psi.? Switched to chlorine system #2 to check function, no issues.? 09:05 Collected well 5 and 6 Raw micro samples. YD W11522733.? 09:18 collected treated water sample. 09:18 treated grab free = 1.88 mg/l, grab total = 1.92 mg/l. Analyzer free = 1.87 mg/l.? There is a minor leak on pump 2 FCV's sensing line (1/2" copper), will create WO to maintenance.? Will place pump 2 to duty 2 later today. Reviewed trends, no issues. Honeywell technician is onsite working on security system. | Stouffville Reservoir and Wells 5 & 6 | 2026-01-14
EAST | January | On site for station check. Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 1.91mg/l FCL Analyzer: 1.94mg/l 12:15hrs: High Lift Effluent Free Cl2 grab residual: 1.83mg/l FCL Analyzer: 1.85mg/l Effluent Total Cl2 grab residual: 1.91mg/l Collected CL2 scrubber samples. Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Stouffville Reservoir and Wells 5 & 6 | 2026-01-09
EAST | January | On site for station check and operational sampling. System duty not active, tower level 81%. Well duty active - Well 5 running 27.4 L/s, well 6 running 18.6 L/s. Switched sample line and reservoir flow from East to West. Verified analyzer readings with grab residuals. Res Influent @ 13:27 Free Grab: 2.08 mg/L Analyzer: 2.10 mg/L Place high lift pump 1 manual on for operational sampling. High Lift Effluent @ at 13:45 Free Grab: 1.89 mg/L Analyzer: 1.92 mg/L Total Grab: 2.00 mg/L Took operational sample at 13:58 Placed high lift pump 1 back in auto. Visual inspection of chemical systems - all ok. Entered station readings in PWQ sheet. Reviewed trends, equipment ok. Station ok | Stouffville Reservoir and Wells 5 & 6 | 2026-01-12
EAST | January | On site for station check and to change out CL2 Cylinder with Travis Wyatt. Verification of HACH CL17 Chlorine Analyzer: Influent Free CL2 grab residual: 2.07mg/l FCL Analyzer: 2.09mg/l 09:40hrs: Effluent Free Cl2 grab residual: 1.88mg/l FCL Analyzer: 1.91mg/l Effluent Total Cl2 grab residual: 1.98mg/l Checked station readings, dosages and verified Cl2 analyzers. All information in PWQ sheet. Visually inspected chemical feed systems. Checked site and equipment. Equipment out of service: None. | Stouffville Reservoir and Wells 5 & 6 | 2026-01-05
EAST | January | Under direction of OIC (Dan Zhou) On-site for; - Station Checks Data in PWQ excel Workbook (Influent) Grabs @ 11:40 hrs. FCl: 2.00 mg/L Analyzer: 2.08 mg/L Effluent (Treated Water) Grabs @ 11:40 hrs. FCl: 1.85 mg/L TCL: 2.03 mg/L Analyzer: 1.91 mg/L Equipment OOS: none Facility OK | Stouffville Reservoir and Wells 5 & 6 | 2026-01-02
EAST | January | Under Direction of OIC Joe Mazza On site to change chlorine cylinder. Worked with OIC Joe Mazza | Stouffville Reservoir and Wells 5 & 6 | 2026-01-05
WW-NORTH | January | Checked facility - site is secured | Holland Landing Lagoons | 2026-01-19
WW-NORTH | January | Performed station check Entered readings into SharePoint Checked OCU - ok Checked diesel containment - ok | Holland Landing Sewage Pumping Station | 2026-01-19
WW-NORTH | January | Onsite to check station Review scada/trends No alarms Enter data in sharepoint | Holland Landing Sewage Pumping Station | 2026-01-26
WW-NORTH | January | Performed station check Entered readings into SharePoint Completed assigned EZMax work orders: - Hoist inspection - Consolidated dry well inspection | Holland Landing Sewage Pumping Station | 2026-01-22
WW-NORTH | January | Performed station check Entered readings into SharePoint Checked OCU - ok | Holland Landing Sewage Pumping Station | 2026-01-29
WW-NORTH | January | Completed monthly PM work order: -Consolidated wet well inspection | Holland Landing Sewage Pumping Station | 2026-01-14
WW-NORTH | January | Performed facility station check Data in sharepoint Responding to channel grinder high temp alarm and inlet channel hihi switch; Reset alarm, ran grinder locally in reverse and then placed back in auto- continued to monitor and has not faulted. Channel level went down Equipment OOS: none | Holland Landing Sewage Pumping Station | 2026-01-15
WW-NORTH | January | Performed station check Entered readings into SharePoint Checked OCU | Holland Landing Sewage Pumping Station | 2026-01-08
WW-NORTH | January | Performed station check Entered readings into SharePoint Checked diesel containment - ok Completed assigned EZMax work orders: - Diesel generator test run - JHS inspection | Holland Landing Sewage Pumping Station | 2026-01-12
WW-NORTH | January | Performed station check Entered readings into SharePoint Checked diesel containment - ok | Holland Landing Sewage Pumping Station | 2026-01-05
WW-NORTH | January | Onsite to check station Review scada/trends No alarms Enter data in sharepoint | East Gwillimbury 2nd Concession Sewage Pumping Station | 2026-01-26
WW-NORTH | January | Performed station check Entered readings into SharePoint Replaced filter for OCU | East Gwillimbury 2nd Concession Sewage Pumping Station | 2026-01-16
WW-NORTH | January | Performed station check Entered readings into SharePoint Checked OCU - ok | East Gwillimbury 2nd Concession Sewage Pumping Station | 2026-01-29
WW-NORTH | January | Performed station check Entered readings into SharePoint Checked OCU - ok Checked diesel containment - 1 inch of water frozen in containment (alarm was cleared) | East Gwillimbury 2nd Concession Sewage Pumping Station | 2026-01-19
WW-NORTH | January | Performed consolidated wet well work order - tested overflow alarm - exercised valves - inspected channel grinder - cleared level transmitters | East Gwillimbury 2nd Concession Sewage Pumping Station | 2026-01-21
WW-NORTH | January | Need to reboot the OIT, after a memory error occurred | East Gwillimbury 2nd Concession Sewage Pumping Station | 2026-01-21
WW-NORTH | January | Performed station check Entered readings into SharePoint Checked OCU - ok | East Gwillimbury 2nd Concession Sewage Pumping Station | 2026-01-22
WW-NORTH | January | Performed station check Entered readings into SharePoint Completed assigned EZMax work orders: - Diesel generator test run - JHS inspection - Hot water tank inspection | East Gwillimbury 2nd Concession Sewage Pumping Station | 2026-01-08
WW-NORTH | January | Performed station check Entered readings into SharePoint Checked diesel containment - containment between diesel tanks has small amount of water. Will return with shop vac to clear out. Checked OCU - removed filter to give a thorough clean | East Gwillimbury 2nd Concession Sewage Pumping Station | 2026-01-12
WW-NORTH | January | Onsite to troubleshoot wwel overflow LIT Informed ROC Put device into cal mode on scada and connected new transducer for testing. Seemed ok Created CSE permit and entered wet well Removed old transducer and replaced with new. Terminated wiring and put back in service Monitored for a while to see if any faults appeared. All ok. Will monitor on scada Informed ROC, armed building and left site | East Gwillimbury 2nd Concession Sewage Pumping Station | 2026-01-14
WW-NORTH | January | Performed station check Entered readings into SharePoint Checked diesel containment - ok | East Gwillimbury 2nd Concession Sewage Pumping Station | 2026-01-05
WW-NORTH | January | Completed assigned EZMax work orders: - Actuator exercise - Diesel containment inspection Also assisted maintenance with grinder inspection / replacement - isolated inlet channel valve before grinder. Flow is being fed to wet wells through bar screens. | Queensville West Sewage Pumping Station | 2026-01-15
WW-NORTH | January | On site to un wire and remove motor for channel grinder. | Queensville West Sewage Pumping Station | 2026-01-16
WW-NORTH | January | Performed station check Entered readings into SharePoint Checked OCU - ok | Queensville West Sewage Pumping Station | 2026-01-22
WW-NORTH | January | Performed station check Entered readings into SharePoint Checked OCU | Queensville West Sewage Pumping Station | 2026-01-29
WW-NORTH | January | Onsite to check station Review scada/trends Clear outstanding alarms (low temp, ocu filter pre clogged) Enter data in sharepoint Swap OCU mist eliminator | Queensville West Sewage Pumping Station | 2026-01-26
WW-NORTH | January | Performed station check Entered readings into SharePoint Checked OCU - ok Performed assigned EZMax work orders: - Consolidated Wet Well - Hoist Inspection | Queensville West Sewage Pumping Station | 2026-01-19
WW-NORTH | January | On site to provide access for GFL to vac truck out the channel before the grinder Performed CSE- M. Balmer went down to inspect work and observe grinder | Queensville West Sewage Pumping Station | 2026-01-28
WW-NORTH | January | On site with maintenance to replace channel grinder but we are unable to remove the old grinder- it continually is getting stuck when lifting out. Will return tomorrow and continue the replacement. | Queensville West Sewage Pumping Station | 2026-01-14
WW-NORTH | January | On site with maintenance to replace channel grinder; when lifting the grinder out, it was continually getting stuck. Will return tomorrow to re-attempt grinder removal again. | Queensville West Sewage Pumping Station | 2026-01-14
WW-NORTH | January | Onsite for wetwell entry to complete grinder debris removal Alert roc Enter wetwell to remove gate logs in inlet channel Clear debris around grinder | Queensville West Sewage Pumping Station | 2026-01-07
WW-NORTH | January | Performed station check Entered readings into SharePoint Checked diesel containment | Queensville West Sewage Pumping Station | 2026-01-12
WW-NORTH | January | Continued work removing channel grinder. Discovered motor coupler rubber insert broken. Will return to continue at a later date | Queensville West Sewage Pumping Station | 2026-01-14
WW-NORTH | January | Performed station check Entered readings into SharePoint Checked OCU | Queensville West Sewage Pumping Station | 2026-01-08
WW-NORTH | January | Onsite for grinder installation Maintenance got sent to another job site - grinder job postponed Alert ROC Diesel run - transfer station to diesel power at 10:47hrs JHSC inspection | Queensville West Sewage Pumping Station | 2026-01-13
WW-NORTH | January | Performed station check Entered readings into SharePoint Checked OCU | Queensville West Sewage Pumping Station | 2026-01-15
WW-NORTH | January | Performed station check Entered readings into SharePoint Checked diesel containment | Queensville West Sewage Pumping Station | 2026-01-05
WW-NORTH | January | Performed facility station check Data in sharepoint Rotated Odour control fan duty and adjusted associated valves: Duty 1 = Fan 2 Duty 3 = Fan 1 Flushed re-circulation pump rotameter Drained exterior media unit Equipment OOS: none | Morton Avenue Air Management Facility | 2026-01-19
WW-NORTH | January | Attended for station check Recorded station/monthly meter readings in rounds sheet Checked blower room - rotated fan 1 into duty Flushed blowdown on recirc line Drained water from temporary OCU Reviewed SCADA/trends. | Morton Avenue Air Management Facility | 2026-01-26
WW-NORTH | January | Performed facility station check Data in sharepoint Flushed re-circulation pump rotameter Drained exterior media unit Completed monthly PM work orders: -JHSC H&S inspection -Blower 1 & 2 inspection -Recirculation pump and strainer inspection -Fan body and drip leg drainage Equipment OOS: none | Morton Avenue Air Management Facility | 2026-01-22
WW-NORTH | January | Performed facility station check Data in sharepoint Flushed re-circulation pump rotameter Drained exterior media unit Equipment OOS: none | Morton Avenue Air Management Facility | 2026-01-29
WW-NORTH | January | Adjusted exhaust fan 1 speed setpoint = 65% --> 75% (placed in manual speed control) | Morton Avenue Air Management Facility | 2026-01-27
WW-NORTH | January | Performed facility station check Data in sharepoint Rotated Odour control fan duty and adjusted associated valves: Duty 1 = Fan 1 Duty 3 = Fan 2 Flushed blowdown Drained liquid from outside media unit Equipment OOS: none | Morton Avenue Air Management Facility | 2026-01-12
WW-NORTH | January | Performed facility station check Data in sharepoint Flushed re-circulation pump rotameter Drained outside media unit Outstanding Alarms: Exhaust fan low pressure alarm Equipment OOS: none | Morton Avenue Air Management Facility | 2026-01-15
WW-NORTH | January | Onsite to troubleshoot blower low pressure switch alarm Informed ROC Found that under current conditions the suction side pressure is not enough to actuate the switch and therefore the alarm is active Informed operations of the findings Informed ROC, armed building and left site | Morton Avenue Air Management Facility | 2026-01-13
WW-NORTH | January | Performed facility station check Data in SharePoint Rotated Odour fan duty and adjusted associated valves: Duty 1 = Fan 2 Duty 3 = Fan 1 Drained liquid from exterior OCU Equipment OOS: none | Morton Avenue Air Management Facility | 2026-01-05
WW-NORTH | January | Attended for daily operations Performed station check Completed lab and entered readings into ACE sheet Decanted sludge thickening tank and initiated transfer once hauler took load Collected weekly regulatory samples for delivery to Newmarket Hosed bar screen and surrounding area Checked sand filters. | Sutton Water Resource Recovery Facility | 2026-01-21
WW-NORTH | January | Attended for daily operations Performed station check Completed lab and entered readings into ACE sheet Decanted sludge thickening/holding tanks and initiated transfer while hauler took load, then returned blowers to auto Hosed bar screen and surrounding area Rotated UV banks - switched from 1B to 2B Checked sand filters Bill/Terry were here to look at grit removal system and unclogged the plug valve on the horizontal line, ran and observed good flow into classifier AC Electric here installing new cameras. | Sutton Water Resource Recovery Facility | 2026-01-16
WW-NORTH | January | Attended for daily operations Performed station check Completed lab and entered readings into ACE sheet Decanted sludge thickening tank and initiated transfer after hauler took load Turned off sludge blowers in advance of a planned decant Collected weekly regulatory samples (W11550677) for delivery to Newmarket Hosed bar screen and surrounding area Rotated UV bank 2A into lead duty Completed scheduled work orders Performed consolidated headworks equipment inspections Checked sand filters. | Sutton Water Resource Recovery Facility | 2026-01-28
WW-NORTH | January | Onsite for sludge handling Decant stt to 2.02m plus transfer Clear rags from barscreen area Check filters Sht hihi came in at 02:38hrs this morning. Decant SHT to 3.54m, clear alarms place SHT blowers in auto and transfer. SHT now at 3.26m | Sutton Water Resource Recovery Facility | 2026-01-25
WW-NORTH | January | Started decanting S.T.T Checked and leveled grit and rag bins Collected samples for in house labs Cleaned bar screen equipment Pulled sand filter 2 and lanced center of lift / now pulling sand properly Finished decanting and raised gate back to top position Started transfer to S.T.T Recorded readings in SharePoint | Sutton Water Resource Recovery Facility | 2026-01-15
WW-NORTH | January | Attended for daily operations Performed station check Completed lab and entered readings into ACE sheet Decanted sludge thickening tank and initiated transfer after hauler took load Hosed bar screen and surrounding area Reset bar screen on panel - screen is running continuously and not resting (will ask maintenance to investigate) Rolled out headworks bins for pickup Completed scheduled work orders Checked blower air relief valves Inspected SBR inlet channel Performed housekeeping in lab Performed maintenance on UV bank 2A and notified ROC of work being completed - replaced cracked intensity probe and replaced 1-3 and 1-6 bulbs and sleeves Checked sand filters. | Sutton Water Resource Recovery Facility | 2026-01-27
WW-NORTH | January | Continued investigating grit vortex #2 not lifting grit Turned off sludge holding blowers in advance of a planned decant. | Sutton Water Resource Recovery Facility | 2026-01-15
WW-NORTH | January | Performed sludge handling | Sutton Water Resource Recovery Facility | 2026-01-18
WW-NORTH | January | Attended for daily operations Performed station check Completed lab and entered readings into ACE sheet Decanted sludge thickening tank and initiated transfer after hauler took load Cleaned bar screen area Checked sand filters. | Sutton Water Resource Recovery Facility | 2026-01-30
WW-NORTH | January | Attended for daily operations Performed station check Completed lab and entered readings into ACE sheet Decanted sludge thickening/holding tanks and initiated transfer Returned sludge blowers to auto Cleaned bar screen area Performed housekeeping around plant Checked sand filters. | Sutton Water Resource Recovery Facility | 2026-01-29
WW-NORTH | January | Attended for daily operations Performed station check Completed lab and entered readings into ACE sheet Decanted sludge thickening tank and initiated transfer while hauler took load Hosed bar screen and surrounding area Rolled out headworks bins for pick up Checked sand filters. | Sutton Water Resource Recovery Facility | 2026-01-20
WW-NORTH | January | Attended for daily operations Performed station check Completed lab and entered readings into ACE sheet Decanted sludge thickening tank and initiated transfer Received alum delivery Hosed bar screen and surrounding area Checked sand filters - took 75 L/s with filter feed pump running at 100%. | Sutton Water Resource Recovery Facility | 2026-01-22
WW-NORTH | January | Attended for daily operations Performed station check Completed lab and entered readings into ACE sheet Decanted sludge thickening tank and initiated transfer after hauler took load Hosed bar screen and surrounding area Completed scheduled work orders Checked blower air relief valves Inspected SBR inlet channel Performed housekeeping around plant Checked sand filters Turned off flow to UVs while Artour (PCS) worked in the panel. | Sutton Water Resource Recovery Facility | 2026-01-23
WW-NORTH | January | Under direction of OIC Neil Ott. Worked on wiring a YR standard ATS circuit in the SUSPUV control panel. Removed old ATS. With the help of Neil. Powered down the panel with plant stopped to make final connections. 5-10min. Once connections were made control panel was energized and ATS circuit tested. Installed a network card in the UPS and connected it to the switch. No outstanding work remaining. Cleaned up and armed the site. | Sutton Water Resource Recovery Facility | 2026-01-23
WW-NORTH | January | Started decanting S.T.T Collected samples for in house labs Checked and leveled grit and rag bins Assist with air compressor repairs Checked and cleaned off bar screen equipment Checked sand filters Finished decanting and raise gate back to top position Once sludge hauler finished taking load out started transfer from S.H.T to S.T.T Recorded readings in SharePoint | Sutton Water Resource Recovery Facility | 2026-01-19
WW-NORTH | January | Started decanting S.T.T and S.H.T Closed Woodriver Bend diversion valve @7:10am Total flow diverted 1129m3 Checked and leveled grit and rag bins Cleaned bar screen equipment Finished decanting and raised gates back to top position Started transfer to S.T.T | Sutton Water Resource Recovery Facility | 2026-01-11
WW-NORTH | January | Started decanting S.T.T Collected samples for in house labs Collected samples for YD labs Checked and leveled grit and rag bins Cleaned bar screen equipment Checked sand filters Completed diesel generator test run Completed H+S inspections Completed chemical pump inspections Completed hazardous waste removal Finished decanting and raised gate back to top position Started transfer to S.T.T Recorded readings in SharePoint | Sutton Water Resource Recovery Facility | 2026-01-07
WW-NORTH | January | Started decanting S.T.T Collected YD samples Collected samples for in house labs Checked and leveled grit and rag bins Cleaned bar screen equipment | Sutton Water Resource Recovery Facility | 2026-01-14
WW-NORTH | January | Started decanting S.T.T Checked and leveled grit and rag bins Cleaned bar screen equipment Collected samples for in house labs Checked sand filters Completed OCU inspection Finished decanting and raised gate back to top position Started transfer to S.T.T Recorded readings in SharePoint | Sutton Water Resource Recovery Facility | 2026-01-08
WW-NORTH | January | Remove and replace flow meter. Electricians require additional parts to complete wiring. | Sutton Water Resource Recovery Facility | 2026-01-14
WW-NORTH | January | Started decanting S.T.T Collected samples for in house labs Checked and leveled grit and rag bins Cleaned off bar screen equipment *Increased waste time for SBR 1 from 420 seconds to 450 seconds* *Shelved diversion EQ LOE alarm* Finished decanting and raised gate back to top position Started transfer to S.T.T Placed lagoon pumps in manual off to mitigate any unnecessary additional flow Yearly sand filter maintenance completed on filters 4 and 5 | Sutton Water Resource Recovery Facility | 2026-01-09
WW-NORTH | January | Attending site to re-install UV transmittance sensor after factory repairs (W11452693). Sensor was reinstalled and reading was verified at the local Trojan OIT. UV intensity is now back to UV sensor control and no longer set to a manual value of 65%. | Sutton Water Resource Recovery Facility | 2026-01-13
WW-NORTH | January | Instrumentation installed the repaired UVT sensor. UV dose dropped to 0 W/cm2 for less than four minutes on the trends but this was a false reading. All UVs started in response to no transmittance input during that timeframe, which is why the calculated dosage of 0 W/cm2 was indicated. Verified that operations returned to normal. | Sutton Water Resource Recovery Facility | 2026-01-13
WW-NORTH | January | Opened Woodriver Bend SPS diversion valve to help with high flows @6:30pm | Sutton Water Resource Recovery Facility | 2026-01-09
WW-NORTH | January | Started decanting S.T.T Cleaned bar screen equipment Collected samples for in house labs Checked sand filters Hosed SBR channels Completed blower inspections Finished decanting and raised gate back to top position Started transfer to S.T.T Pulled rags from bottom of vortex 1 Flushed grit lift line to vortex Put vortex back on line and will be monitored over the next few days Entered readings in SharePoint | Sutton Water Resource Recovery Facility | 2026-01-13
WW-NORTH | January | Started decanting S.T.T Checked and leveled grit and rag bins Cleaned bar screen equipment Collected samples for in house labs Completed sand filter inspections on filters 1,2,3 and 6 Finished decanting and raised gate back to top position Started transfer to S.T.T Entered readings in SharePoint | Sutton Water Resource Recovery Facility | 2026-01-12
WW-NORTH | January | Started decanting Collected samples for in house labs Checked and leveled grit and rag bins Cleaned bar screen equipment Finished decanting and raised gate back to top position Started transfer to S.T.T from S.H.T after GFL took a load out Recorded readings in SharePoint | Sutton Water Resource Recovery Facility | 2026-01-05
WW-NORTH | January | Started decanting S.T.T Checked grit and rag bins Rolled out grit and rag bins Cleaned off bar screen equipment Collected samples for in house labs Completed sump pit inspection Completed SBR channel hose out Completed chamber pump outs Completed EQ line flush Finished decanting and raise gate back to top position Started transfer to S.T.T Recorded readings in SharePoint | Sutton Water Resource Recovery Facility | 2026-01-06
WW-NORTH | January | Placed both sludge holding tank blowers in manual off. | Sutton Water Resource Recovery Facility | 2026-01-01
WW-NORTH | January | Attended for sludge handling Decanted sludge thickening tank and initiated transfer Hosed bar screen and surrounding area. | Sutton Water Resource Recovery Facility | 2026-01-04
WW-NORTH | January | Attended for daily operations Performed station check Completed lab and entered readings into ACE sheet Decanted sludge thickening/holding tank and initiated transfer after hauler took load Returned sludge holding blowers to auto Hosed bar screen and surrounding area Lowered alum dosage from 160 to 155 mg/L Completed scheduled work orders Flushed alum line Checked air compressors Inspected OCU Cleaned DO probes Checked sand filters. | Sutton Water Resource Recovery Facility | 2026-01-02
WW-NORTH | January | Performed facility station check Data in sharepoint Equipment OOS: Odour control system | Keswick Sewage Pumping Station | 2026-01-22
WW-NORTH | January | Performed facility station check Data in sharepoint Equipment OOS: Odour control system | Keswick Sewage Pumping Station | 2026-01-15
WW-NORTH | January | Performed facility station check Data in sharepoint Equipment OOS: Odour control system | Keswick Sewage Pumping Station | 2026-01-19
WW-NORTH | January | Onsite responding to CMU5 W11611919 Receive call 14:49hrs regarding power blip and causing all 4 pump VFD?s, both grinders, and all supply fans to fault. Ultrasonic back up mode activated and ran a pump locally until ROC could reset it Upon arrival find p1 running in auto - all other pumps grinders and fans still faulted Reset all and clear all alarms Monitor station - no apparent issues | Keswick Sewage Pumping Station | 2026-01-24
WW-NORTH | January | Station checks completed Enter data into SharePoint MIC mechanical on site looking into boiler heater system Also looking into heating fan in drywell basement | Keswick Sewage Pumping Station | 2026-01-26
WW-NORTH | January | Onsite to reset VFD 4 fault came in at 13:06hrs Vfd fault code on scada: 84 Reset vfd and clear alarms. Within a minute of reset - VFD faulted again @ 14:26hrs VFD interface reads: F1.1 fault - Fieldbus fault Scada code fault: 84 again. Clear vfd fault and reset alarms Place p4 in duty to test pump/vfd functionality Monitor vfd 4 - no apparent issues. | Keswick Sewage Pumping Station | 2026-01-26
WW-NORTH | January | Performed facility station check Data in sharepoint Completed monthly PM work orders -Hoist system inspection -Consolidated dry well inspection Sump pump 2 not working Auto dialer test not working Flow rates @ Pump speed 100% (WWL = 2.31 m) P1 = 204 L/s P2 = 216 L/s P3 = 207 L/s P4 = 210 L/s Equipment OOS: Odour control system and sump pump 2 | Keswick Sewage Pumping Station | 2026-01-29
WW-NORTH | January | In to clear channel grinder 1 over load alarm Ran channel grinder in reverse in local Placed grinder back in auto | Keswick Sewage Pumping Station | 2026-01-11
WW-NORTH | January | Onsite to complete consolidated wetwell work orders Alert roc Tip mezzanine flood float - alarm received on scada at 12:03hrs Cycle both inlet channel gate valves Confirm with ROC alarm received | Keswick Sewage Pumping Station | 2026-01-09
WW-NORTH | January | Ran pump 4 several times at 100% in manual speed. Noticed flow from pump not as high as usual while running. Pump back in auto 211l/s | Keswick Sewage Pumping Station | 2026-01-14
WW-NORTH | January | Onsite to check station Review scada/trends No alarms Enter data in sharepoint | Keswick Sewage Pumping Station | 2026-01-08
WW-NORTH | January | Ran pumps 3 and 4 alternately at 100% in manual several times to clear blockage. Appear to be ragged due to high flows from melting of snow. both ran 210L/S or greater | Keswick Sewage Pumping Station | 2026-01-12
WW-NORTH | January | Performed facility station check Data in sharepoint Completed monthly PM work orders: -Heat trace inspection -JHSC H&S Inspection -Dry well flood alarm test -Generator test run Date: January 12, 2026 Start time: 11:29 Start hours: 70.42 Stop Hours: 71.48 Run Time hours: 1.06 Start Fuel: 3411 L (90.5 cm) Stop Fuel: 3405 L (90.3 cm) Pre run checks: Battery Cell Levels: Ok Battery Terminals and Cables: Ok Oil Level: Ok Coolant Level: Ok Fluid Leaks: Ok Coolant Recirculating pump: Ok Faulty Gauges: Ok Operating Current: 44 Amps Operating Frequency: 60.0 Hz Operating Voltage: 603 Volts Engine speed: 1800 RPM Water/coolant Temp: 183 F Oil Pressure: 66 psi Equipment OOS: Odour control system | Keswick Sewage Pumping Station | 2026-01-12
WW-NORTH | January | Onsite to check station Review scada/trends Clear outstanding alarms Enter data in sharepoint | Keswick Sewage Pumping Station | 2026-01-06
WW-NORTH | January | Ran pump 3 in manual to clear blockage. | Keswick Sewage Pumping Station | 2026-01-02
WW-NORTH | January | Attended for station check Recorded station readings in rounds sheet Checked generator enclosure Gate open upon arrival Reviewed SCADA/trends. | Sutton Woodriver Bend Sewage Pumping Station | 2026-01-19
WW-NORTH | January | Attended for station check Recorded station readings in rounds sheet Checked generator enclosure Reviewed SCADA/trends. | Sutton Woodriver Bend Sewage Pumping Station | 2026-01-29
WW-NORTH | January | Attended for station check Recorded station/monthly meter readings in rounds sheet Checked generator enclosure Cleared ice buildup from OCU discharge vent Performed station housekeeping Reviewed SCADA/trends. | Sutton Woodriver Bend Sewage Pumping Station | 2026-01-26
WW-NORTH | January | Attended for wetwell inspection Notified ROC of work being completed Tested wet well high level alarm - in @ 11:59 Exercised wet well valves Flushed air relief valve. | Sutton Woodriver Bend Sewage Pumping Station | 2026-01-19
WW-NORTH | January | Attended for station check Recorded station readings in rounds sheet Checked generator enclosure Inspected facility outfall Reviewed SCADA/trends. | Sutton Woodriver Bend Sewage Pumping Station | 2026-01-22
WW-NORTH | January | Attended for station check Recorded station readings in rounds sheet Checked generator enclosure Reviewed SCADA/trends. | Sutton Woodriver Bend Sewage Pumping Station | 2026-01-15
WW-NORTH | January | Attended for station check Recorded station readings in rounds sheet Checked generator enclosure Reviewed SCADA/trends. | Sutton Woodriver Bend Sewage Pumping Station | 2026-01-12
WW-NORTH | January | Attended for station check Recorded station readings in rounds sheet Checked generator enclosure Reviewed SCADA/trends. | Sutton Woodriver Bend Sewage Pumping Station | 2026-01-05
WW-NORTH | January | Attended for station check Recorded station readings in rounds sheet Completed scheduled work orders and notified ROC of work being completed Performed standby generator test run and recorded readings in rounds sheet Start: 356.0 h Stop: 357.4 h Run time: 1.4 h Performed H&S inspection Reviewed SCADA/trends. | Sutton Woodriver Bend Sewage Pumping Station | 2026-01-08
WW-NORTH | January | Attended for wetwell inspection Notified ROC of work being completed Tested wet well high level alarm - in @ 11:17 Exercised wet well valves. | Sutton South River Sewage Pumping Station | 2026-01-19
WW-NORTH | January | Attended for station check Recorded station readings in rounds sheet Found dialer beeping but no alarm shown Reviewed SCADA. | Sutton South River Sewage Pumping Station | 2026-01-19
WW-NORTH | January | Attended for station check Recorded station readings in rounds sheet Reviewed SCADA. | Sutton South River Sewage Pumping Station | 2026-01-29
WW-NORTH | January | Attended for station check Recorded station/monthly meter readings in rounds sheet Cleaned snow off hatches Reviewed SCADA. | Sutton South River Sewage Pumping Station | 2026-01-26
WW-NORTH | January | Attended for station check Recorded station readings in rounds sheet Reviewed SCADA. | Sutton South River Sewage Pumping Station | 2026-01-22
WW-NORTH | January | Attended for station check Recorded station readings in rounds sheet Reviewed SCADA. | Sutton South River Sewage Pumping Station | 2026-01-08
WW-NORTH | January | Attended for station check Recorded station readings in rounds sheet Completed scheduled work orders Tested panel low temperature alarm - in @ 9:43 (confirmed with ROC) Performed H&S inspection Reviewed SCADA. | Sutton South River Sewage Pumping Station | 2026-01-12
WW-NORTH | January | Attended for station check Recorded station readings in rounds sheet Reviewed SCADA. | Sutton South River Sewage Pumping Station | 2026-01-15
WW-NORTH | January | Performed mobile generator test run (located at Sutton WRRF) and recorded readings in rounds sheet. | Sutton South River Sewage Pumping Station | 2026-01-09
WW-NORTH | January | Attended for station check Recorded station readings in rounds sheet Reviewed SCADA. | Sutton South River Sewage Pumping Station | 2026-01-05
WW-NORTH | January | Attended for station check Recorded station readings in rounds sheet Checked pump house - p.1 running in duty Reviewed SCADA/trends. | Sutton High Street Sewage Pumping Station | 2026-01-19
WW-NORTH | January | Attended for wetwell inspection Notified ROC of work being completed Tested wet well high level alarm - in @ 13:49. | Sutton High Street Sewage Pumping Station | 2026-01-19
WW-NORTH | January | Attended for station check Recorded station readings in rounds sheet Checked pump house - p.2 running in duty Reviewed SCADA/trends. | Sutton High Street Sewage Pumping Station | 2026-01-29
WW-NORTH | January | On site to preform a pump by changing the motor pulley from 9.25? to 10.3? and ran the pump at 100%. VFD ramped the motor down after about 30 seconds on over current. Put the smaller pulley back and left the pump in auto | Sutton High Street Sewage Pumping Station | 2026-01-26
WW-NORTH | January | Attended for station check Recorded station/monthly meter readings in rounds sheet Checked pump house - p.2 running in duty (maintenance working on p.1) Performed station housekeeping Reviewed SCADA/trends. | Sutton High Street Sewage Pumping Station | 2026-01-26
WW-NORTH | January | Attended for station check Recorded station readings in rounds sheet Checked pump house - p.2 running in duty Inspected facility outfall Reviewed SCADA/trends. | Sutton High Street Sewage Pumping Station | 2026-01-22
WW-NORTH | January | Measured motor shaft for new sheaves Checked for air relief bypassing. Will look into ordering new parts. | Sutton High Street Sewage Pumping Station | 2026-01-13
WW-NORTH | January | Attended for station check Recorded station readings in rounds sheet Checked pump house - p.2 running in duty Reviewed SCADA/trends. | Sutton High Street Sewage Pumping Station | 2026-01-15
WW-NORTH | January | Attended for station check Recorded station readings in rounds sheet Checked pump house - p.1 running in duty Reviewed SCADA/trends. | Sutton High Street Sewage Pumping Station | 2026-01-12
WW-NORTH | January | Attended for station check Recorded station readings in rounds sheet Checked pump house - p.2 running in duty Reviewed SCADA/trends. | Sutton High Street Sewage Pumping Station | 2026-01-08
WW-NORTH | January | Attended for station check Recorded station readings in rounds sheet Completed scheduled work orders and notified ROC of work being completed Performed standby generator test run and recorded readings in rounds sheet Start: 640.1 h Stop: 641.2 h Run time: 1.1 h Tested diesel containment flood alarm - in @ 9:09 Exercised pump house valves Performed H&S inspection Tested wet well/building low temperature alarms - in @ 10:00/10:30 Reviewed SCADA/trends. | Sutton High Street Sewage Pumping Station | 2026-01-05
WW-NORTH | January | Performed facility station check Data in SharePoint Equipment OOS: none | Keswick Joe Dales Sewage Pumping Station | 2026-01-22
WW-NORTH | January | Performed facility station check Data in SharePoint Equipment OOS: none | Keswick Joe Dales Sewage Pumping Station | 2026-01-29
WW-NORTH | January | OnSite to check station Review scada/trends No alarms Enter data in sharepoint | Keswick Joe Dales Sewage Pumping Station | 2026-01-26
WW-NORTH | January | Performed facility station check Data in SharePoint Equipment OOS: none | Keswick Joe Dales Sewage Pumping Station | 2026-01-19
WW-NORTH | January | Performed facility station check Data in SharePoint Equipment OOS: none | Keswick Joe Dales Sewage Pumping Station | 2026-01-15
WW-NORTH | January | Onsite to check station plus complete work orders Alert ROC Review scada/trends No alarms Enter data in sharepoint Hazardous waste removal Jhsc inspection Ocu maintenance - swap mist eliminator Heat radiator exchange check Diesel test run - data in sharepoint | Keswick Joe Dales Sewage Pumping Station | 2026-01-08
WW-NORTH | January | Performed facility station check Data in SharePoint Completed monthly PM work order: -Consolidated dry well inspection Flow rates @ Pump speed 100% (WWL = 1.93 m) P1 = 52 L/s P2 = 55 L/s P3 = 51 L/s Equipment OOS: none | Keswick Joe Dales Sewage Pumping Station | 2026-01-12
WW-NORTH | January | Checked station Viewed HMI and trends Checked dry well area Cleaned bar screen equipment Recorded readings in SharePoint | Georgina No. 4 Sewage Pumping Station | 2026-01-26
WW-NORTH | January | Performed facility station check Data in SharePoint Turned on breaker to OCU room heater (#5) Equipment OOS: none | Keswick Joe Dales Sewage Pumping Station | 2026-01-05
WW-NORTH | January | Performed facility station check Data in sharepoint Observed bar screen and compactor running; oil reservoir ok Equipment OOS: none | Georgina No. 4 Sewage Pumping Station | 2026-01-15
WW-NORTH | January | Performed facility station check Data in sharepoint Observed bar screen and compactor running; oil reservoir ok Equipment OOS: none | Georgina No. 4 Sewage Pumping Station | 2026-01-29
WW-NORTH | January | Performed facility station check Data in sharepoint Observed bar screen and compactor running; oil reservoir ok Equipment OOS: none | Georgina No. 4 Sewage Pumping Station | 2026-01-22
WW-NORTH | January | Performed facility station check Data in sharepoint Observed bar screen and compactor running; oil reservoir ok Completed monthly PM work orders: -Air handling unit service -Hoist inspection Adjusted bar screen sheet metal ramp into compactor; there was a small gap debris was falling through Equipment OOS: none | Georgina No. 4 Sewage Pumping Station | 2026-01-19
WW-NORTH | January | Performed consolidated bar screen and screw conveyer cleaning work order. | Georgina No. 4 Sewage Pumping Station | 2026-01-23
WW-NORTH | January | Performed facility station check Data in sharepoint Observed bar screen and compactor running; oil reservoir ok Brought bar screen bin back inside Equipment OOS: none | Georgina No. 4 Sewage Pumping Station | 2026-01-12
WW-NORTH | January | Attended for station check Recorded station readings in rounds sheet Checked dry well - p.3 running in duty Cleaned bar screen and surrounding area Reviewed SCADA/trends. | Georgina No. 4 Sewage Pumping Station | 2026-01-08
WW-NORTH | January | Performed facility station check Data in sharepoint Topped up bar screen oil reservoir Completed monthly PM work orders: -Odour control scrubber system -JHSC H&S inspection -Bar screen bin removal and replacement -Consolidated dry well inspection -Generator test run Date: January 05, 2026 Start time: 09:38 Start hours: 505.4 Stop Hours: 506.6 Run Time hours: 1.2 Start Fuel: 780 L (79.8 cm) / 773 L (79.2 cm) Stop Fuel: 759 L (77.9 cm) / 756 L (77.6 cm) Pre run checks: Battery Cell Levels: Ok Battery Terminals and Cables: Ok Oil Level: Ok Coolant Level: Ok Fluid Leaks: Ok Coolant Recirculating pump: Ok Faulty Gauges: Ok Operating Current: 68 Amps Operating Frequency: 60.0 Hz Operating Voltage: 600 Volts Engine speed: 1800 RPM Water/coolant Temp: 152 F Oil Pressure: 134 psi Equipment OOS: none | Georgina No. 4 Sewage Pumping Station | 2026-01-05
WW-NORTH | January | On site to install the new check valve on the floor drain. Cut the pipe and glue on the pvc fitting but will return to install the valve once the glue sets. Also preformed PMs on the bar screen and auger. | Georgina No. 4 Sewage Pumping Station | 2026-01-05
WW-NORTH | January | Completed monthly PM work orders: -Flow control valve inspection -Sump pit inspection -Air valve inspection | Newmarket Pinch Valves | 2026-01-21
WEST | January | -on site for station check -all ok | King City Wells 3 & 4 | 2026-01-16
WEST | January | On site for station check. Site offline . Gate secure. No other issues to report. | King City Wells 3 & 4 | 2026-01-23
WEST | January | On site for station check Site offline Site secure No issues found | King City Wells 3 & 4 | 2026-01-09
WEST | January | -on site to complete station check -site out of service -site secure -no issues found -completed JHSC Health and Safety Inspection | King City Wells 3 & 4 | 2026-01-02
WEST | January | Tested Chlorine leak detector. Equipment okay. Informed ROC about the work beforehand. All alarms cleared. | Kleinburg Wells 3 and 4 | 2026-01-19
WEST | January | -on site to complete station check and collect samples -sample work order # W11538528 -site offline and isolated from distribution system 08:54 - started well #4 in local running to waste at 26.4 l/s 08:55 - started well #3 in local running to waste at 25.4 l/s -checked equipment -reviewed trends -analyzer reagents ok 09:28 - collected weekly well #3 raw water micro. sample 09:28 - collected weekly well #4 raw water micro. sample -put both wells back into local off -no issues found -completed work orders, informed ROC of work: -completed Deep Well Exhaust Valve, Maintenance -completed Manual Valve, Exercise -completed Check Valve, Inspection -completed Ventilation System - Exhaust Fans -completed Pressure Relief Valve, Inspection -completed Chlorine Scrubber, Check -completed Turbidimeter Maintenance -cleaned and verified turbidimeter, no issues -completed Chlorine Analyzer, Maintenance -completed zero calibration on influent and effluent analyzers -added grit and electrolyte to free chlorine analyzers -verified analyzers after maintenance: 09:59 - influent analyzer = 0.01 mg/L Grab = 0.01 mg/L 10:01 - effluent analyzer = 0.00 mg/L Grab = 0.02 mg/L 10:03 - Treated Analyzer readings: Free Chlorine = 0.04 mg/L Total Chlorine = 1.95 mg/L 10:03 - Treated Grabs: Free Chlorine = 0.03 mg/L Total Chlorine = 2.01/2.03/2.03 mg/L 10:14 - adjusted treated total chlorine analyzer to 2.02 mg/L based on average of 3 grabs -completed Chemical System Inspection - Silicate -pump #1 OOS, ran pump #2 into calibration column - flow ok -completed Ammonia System, Inspection -ran both pumps into calibration column -completed Chemical System Inspection - Chlorine -completed vacuum test on both chlorinators -no issues -site back to normal operation | Kleinburg Wells 3 and 4 | 2026-01-21
WEST | January | -on site to complete station check and collect samples -site offline and isolated from distribution system -sample work order # W11551066 11:09 - started well #3 in local running to waste at 25.4 l/s 11:09 - started well #4 in local running to waste at 26.0 l/s -checked equipment -reviewed trends -analyzer reagents ok -verified treated water chlorine analyzers: 11:16 - Analyzer readings: Free Chlorine = 0.11 mg/L Total Chlorine = 2.03 mg/L 11:16 - Grabs: Free Chlorine = 0.02/0.03/0.01 mg/L Total Chlorine = 2.02 mg/L 11:22 - adjusted treated free chlorine analyzer to 0.02 mg/L based on average of 3 grabs 11:45 - collected weekly well #3 raw water micro. sample 11:45 - collected weekly well #4 raw water micro. sample -put both wells back into local off -no issues found | Kleinburg Wells 3 and 4 | 2026-01-28
WEST | January | On site for station check, W11523000 Micro Sampling and W11476610 Q1 Water Samples-Kleinburg Wells 3,4 12:48- Ran wells in local to waste - distribution valve locked out. 13:00-Verified Analyzers Free Cl2 Grab - 0.03mg/L; Analyzer :-0.32mg/L Zero calibrated and adjusted analyzer up to 0.03 mg/L Total Cl2 Grab - 1.90 mg/L; Analyzer 1.84 mg/L Reagents all okay Samples collected 13:33- put well local off after sampling equipment okay. | Kleinburg Wells 3 and 4 | 2026-01-14
WEST | January | On site for station check and W11503511 Micro Sampling 13:15- Ran wells in local to waste - distribution valve locked out. 13:25-Verified Analyzers Free Cl2 Grab - 0.03mg/L; Analyzer 0.00mg/L Total Cl2 Grab - 2.00 mg/L; Analyzer 1.95 mg/L Reagents all okay Samples collected 13:46-Wells back offline after sampling equipment okay. | Kleinburg Wells 3 and 4 | 2026-01-07
WEST | January | Onsite for the following PM Work orders. Informed ROC about the works being done. W11497683 KLW34, Diesel Generator Test Run Pre check Battery okay- 26.5V Coolant- Okay Oil - Okay Before Start Start time- 10:40 Run time- 414.9 hr Fuel level-1962L/38cm KLPSWL pump 3 running Manual. After Stop Stop time- 11:43 Run time- 416.1 hr Fuel level-1930L/37.5 cm W11498941- Chlorine Cylinder Emergency Repair Kit inspection W11498315- JHSC health and safety inspection. | Kleinburg Wells 3 and 4 | 2026-01-08
WEST | January | Onsite for station check and to collect weekly micro sample W11550991 Tower draining Checked residuals mg/L Common/Pre Inj @13:13 Total analyzer 3.45 grab 3.44 Free grab 0.03 Mcl grab 3.07 Post Inj @1318 Total analyzer 4.25 grab 4.14 Free grab 0.02 | Schomberg Elevated Tank | 2026-01-28
WEST | January | -on site to replace hypo lines -replaced lines and fittings, installed containment -primed pump #1 line, pump #2 OOS -no issues | Schomberg Elevated Tank | 2026-01-22
WEST | January | On site to top up hypo (4 jugs) level sensor monitor blank. | Schomberg Elevated Tank | 2026-01-30
WEST | January | Onsite for station check Tower draining Checked residuals mg/l Common inlet @1124 Total analyzer 3.50 grab 3.48 Free grab 0.04 Mcl grab 2.96 Post inj @1131 Total analyzer 4.25 grab 4.28 Free grab 0.03 | Schomberg Elevated Tank | 2026-01-23
WEST | January | Onsite for station check Tower draining Checked residuals mg/l @1144 Post inj Total analyzer 3.57 grab 3.48 Free grab 0.08 Changed reagent in post inj cl2 analyzer Common/ pre inj @1200 Total analyzer 3.52 grab 3.38 Free grab 0.05 Mcl grab 2.94 | Schomberg Elevated Tank | 2026-01-16
WEST | January | Tower draining 12:22 Checked trends and residuals, mg/l. Equipment in all good function and state 12:34 Pre injection, free grab 0.09. Total grab 3.43 vs 3.55. Monochloramine 3.13 12:41 Post injection, free grab 0.08. Total grab 4.40 vs analyzer total 4.51 | Schomberg Elevated Tank | 2026-01-30
WEST | January | Onsite for station check Tower draining Checked residuals mg/l Common @1151 Total analyzer 3.44 grab 3.48 Free grab 0.05 Mcl grab 2.77 Post inj @1153 Total analyzer 4.66 grab 4.40 Free grab 0.07 | Schomberg Elevated Tank | 2026-01-26
WEST | January | Onsite to complete work orders Cleaned cl27 sc analyzers Grabs before Pre inj Total analyzer 3.51 grab 3.38 Post Total analyzer 4.41 grab 4.40 After Pre inj Total analyzer 3.48 grab 3.17 Post inj Total analyzer 4.17 grab 4.06 Deep cycled duty to 5% Changed duty start and stop from 10-40 back to 15-45% Ran the portable generator with no issues | Schomberg Elevated Tank | 2026-01-22
WEST | January | Onsite for station check and to collect weekly micro sample W11538476 Tower draining Checked residuals mg/l Common/pre inj @1134 Total analyzer 3.63 grab 3.60 Free grab 0.05 Mcl grab 2.98 Post inj @1140 Total analyzer 4.37 grab 4.40 Free grab 0.07 Reagents ok Ran hypo p1 to sight glass Max flow 135 ml/min @100% P2 still oos Completed jhsc | Schomberg Elevated Tank | 2026-01-21
WEST | January | Onsite for station check and to collect weekly micro sample and Q1 quarterly sample Tower filling Post inj @1258 Total analyzer 3.56 grab 3.62 Free grab 0.08 Deactivated duty Common /pre inj @1323 Total analyzer 3.56 grab 3.44 Free grab 0.04 Mcl grab 3.02 To collect samples on down cycle | Schomberg Elevated Tank | 2026-01-14
WEST | January | Onsite for station check Tower filling about hit stop setpoint Post inj @0929 Total analyzer 3.70 grab 3.68 Free grab 0.04 Pre inj/ common @0948 Total analyzer 3.60 grab 3.60 Free grab 0.06 Mcl grab 3.09 Topped up hypo tank | Schomberg Elevated Tank | 2026-01-19
WEST | January | Restarted the Operator Interface Terminal due to Windows Video driver updates. Notified the Remote Operations Center before restarting the OIT. | Schomberg Elevated Tank | 2026-01-15
WEST | January | Onsite for station check Tower filling Post inj @1107 Total analyzer 3.77 grab 3.72 Free grab 0.10 Common/ pre inj @1110 Total analyzer 3.11 grab 3.24 Free grab 0.02 Noticed discharge valve leak message in hypo pump 2. Tried to adjust off gas valve Changed reagents in common cl17sc | Schomberg Elevated Tank | 2026-01-12
WEST | January | On site to troubleshoot Hypo P1. Bleeder valve on pump head has failed, threads are warn and valve does not hold in place. Swapped P1 bleeder valve with P2 and tested ran. Max flow = 136ml/min at 15% (136-142 range). Request quotation for new pump heads and bleeder valves for replacement. | Schomberg Elevated Tank | 2026-01-12
WEST | January | Onsite for station check Tower draining Checked residuals mg/l Common inlet @1114 Total analyzer 3.51 grab 03.44 Free grab 0.07 Mcl grab 2.97 Post inj @1120 Total analyzer 4.50 grab 4,40 Topped up hypo tank | Schomberg Elevated Tank | 2026-01-09
WEST | January | On site with Sean Peoples to investigate Hypo rm. heater. Found motor bearing to be faulty, requires replacement. New 240v, 3kw heater installed. | Schomberg Elevated Tank | 2026-01-02
WEST | January | Onsite for station check and to collect weekly micro sample and Q1 ndma W11476810 W11503459 Tower draining Checked residuals mg/l Post inj @1215 Total analyzer 4.74 grab 4.14 Free grab 0.08 Common/ pre inj @1217 Total analyzer 3.50 grab 3.48 Free grab 0.05 Mcl 2.92 | Schomberg Elevated Tank | 2026-01-07
WEST | January | -on site to complete station check and to collect sample for in house lab analysis -hypo pump DF = 113% -hypo pump #2 OOS - tower draining at 25.5 l/s, level = 44% - reviewed trends - CL17 reagents ok - checked equipment -recorded readings in PWQ sheet - no issues found -verified analyzers: 12:59 - common inlet/outlet TCL analyzer = 3.62 mg/L 12:59 - common inlet/ outlet grab: FCL = 0.00 mg/L TCL = 3.64 mg/L Mono = 3.04 mg/L 13:20 - post injection TCL analyzer = 3.54 mg/L 13:20 - post injection grab: TCL = 3.46 mg/L | Schomberg Elevated Tank | 2026-01-02
WEST | January | Onsite for station check Tower draining Checked residuals mg/L Common @1131 Total analyzer 3.53 grab 3.54 Free grab 0.05 Mcl grab 2.94 Post inj @1142 Total analyzer 3.45 grab 3.40 Free grab 0.08 Hypo p2 ops, tried to prime in local when trying to run in manual remote, fault to start alarm came in | Schomberg Elevated Tank | 2026-01-05
WW-CEAST | January | Weather today Mostly Cloudy and -12 Celsius -On site to complete work order W11528325. -Completed station check. -Entered station readings into SharePoint. -All pumps available in all-stop auto duty rotation. -Standby power generator available in auto. -Checked valve room/dry well. -Station operations normal. | Aurora Henderson Sewage Pumping Station | 2026-01-16
WW-CEAST | January | On site completed work orders. Station Check (See details on SharePoint) All pumps available in all-stop auto duty rotation. Standby power generator available in auto. Checked valve room/dry well, ok. Station operations normal. Odour control scrubber system inspection, ok. | Aurora Henderson Sewage Pumping Station | 2026-01-19
WW-CEAST | January | Weather today Snow and -13 Celsius -On site to complete work order W11542236. -Completed station check. -Entered station readings into SharePoint. -All pumps available in all-stop auto duty rotation. -Standby power generator available in auto. -Checked valve room/dry well. -Station operations normal. | Aurora Henderson Sewage Pumping Station | 2026-01-23
WW-CEAST | January | Weather today Mostly Cloudy and -16 Celsius -On site to complete work order W11554547. -Completed station check. -Entered station readings into SharePoint. -All pumps available in all-stop auto duty rotation. -Standby power generator available in auto. -Checked valve room/dry well. -Station operations normal. | Aurora Henderson Sewage Pumping Station | 2026-01-30
WW-CEAST | January | -on site to meet WA Stephenson and CPD Jose Oliveira to investigate interconnect and forcemain 2 actuators that have issues with their display -WA Stephenson talked to supplier for the rotork valves, they will get their electrician/technician on site Thursday Feb 22 at 08:30 to investigate further -suspected electrical issue, fuse in actuator or relay blown, issue not confirmed -will meet contractor on site Thursday to hopefully get issue resolved -hatch 5 is in alarm and cannot arm building, notified security, security is trying to get approval to remove hatch 5 from inhibiting arming the building as the hatch is closed and locked. -reviewed SCADA -inspected site -station okay | Aurora Henderson Sewage Pumping Station | 2026-01-20
WW-CEAST | January | On site to troubleshoot 2 valve actuator fault with Rotork/CD/WSP/WAS. Rotork was able to resolve issue for the interconnect valve with new mainboard installed. Rotork changed the main board/checked all the wires for the forcemain 2 discharge valve. Alarm was able to be cleared but scada is not acknowledging the valve position coming from the actuator. Called Artour (PCS) and he confirmed actuator is somehow getting fully open/fully close signal at the same time. Rotork further looking into this issue. Investigation concluded that FM2MV1 is missing a wire for open/close. Lexsan will need to be scheduled to come onsite to troubleshoot this wiring. Confirmed FM2MV1 fully open in L, showing as half open in local on scada | Aurora Henderson Sewage Pumping Station | 2026-01-22
WW-CEAST | January | Station check complete and the readings have been entered into the sharepoint | Aurora Henderson Sewage Pumping Station | 2026-01-26
WW-CEAST | January | Station check complete and the readings have been entered into the sharepoint Tested building hi/lo temp, dry well flood. Ok Building temp alarms take about 7 mins for it to appear on scada alarm banner | Aurora Henderson Sewage Pumping Station | 2026-01-12
WW-CEAST | January | -station check of site and work orders -reviewed SCADA -inspected site -entered data into SharePoint -valve exercising -actuator exercising/inspection -Housekeeping -station okay | Aurora Henderson Sewage Pumping Station | 2026-01-09
WW-CEAST | January | Weather today Overcast and 1 Celsius -On site to complete work order W11491051, W11491103, W11490819, W11507743, W11507769, W11508060. -Completed station check. -Entered station and standby power generator readings into SharePoint. -All pumps available in all-stop auto duty rotation. -Hazardous Waste collection and removal. -JHSC Health and Safety inspection. RS Pump inspection. -Pump 1 running at 50% speed and 53.7 L/s flow at 341 kPa. -Pump 2 running at 50% speed and 53.1 L/s flow at 330 kPa. -Pump 3 running at 50% Speed and 52.7 L/s flow at 337 kPa. -Pump 4 running at 50% Speed and 55.1 L/s flow at 342 kPa. -Check valve inspection. -Air Relief Valve inspection. -Standby power generator test run. -Standby power generator available in auto. -Checked valve room/dry well. -Station back in auto from PAC mode. -Station operations normal. | Aurora Henderson Sewage Pumping Station | 2026-01-08
WW-CEAST | January | On site to reset Boiler #1 W11565052. | Aurora Henderson Sewage Pumping Station | 2026-01-06
WW-CEAST | January | Weather today Clear and -9 Celsius -On site to complete work order W11490829. -Completed station check. -Entered station readings into SharePoint. -All pumps available in all-stop auto duty rotation. -Pump 4 currently running in auto as duty 1 with 53.0 L/s flow at 335 kPa. -Standby power generator available in auto. -Checked valve room/dry well. -Station operations normal. | Aurora Henderson Sewage Pumping Station | 2026-01-02
WW-CEAST | January | Weather today Snow and -3 Celsius -On site to complete work order W11495704. -Completed station check. -Entered station readings into SharePoint. -All pumps available in all-stop auto duty rotation. -Pump 1 currently running in auto as duty 1 with 53.9 L/s flow at 341 kPa. -Standby power generator available in auto. -Checked valve room/dry well. -Station operations normal. | Aurora Henderson Sewage Pumping Station | 2026-01-05
WW-CEAST | January | Weather today A Few Clouds and -13 Celsius -On site to complete work orders W11532648, W11532510. -Completed station check. -Entered station readings into SharePoint. -Fans 1 and 2 running in auto. -Nutrient tank batch mixing - tank filled up to desired level. - System 1 recirculation pump #2 OOS. - System 2 recirculation pump #1 OOS. -Standby power generator available in auto | Oak Ridges Air Management Facility | 2026-01-23
WW-CEAST | January | Station check complete and the reading have been entered into the sharepoint. Topped up nutrient tank. Found make up water valve for system 1 closed while system 2 was open. Also noticed difference of water level for both BFT which system 1 was significantly lower than the other one with the make up valve closed. pH difference was also observed as tank 1 was @ 1.6 while the other tank was @ 1.9 Notified CD/NAC that I opened the system 1 make up water valve via email. | Oak Ridges Air Management Facility | 2026-01-30
WW-CEAST | January | On site to assist Contractors (NAC, AECOM, Pump Supplier and Biorem) with the installation and testing of recirculation pump 2 at system unit 2. Recirculation pump 1 at system unit 2, and recirculation pumps 1 and 2 at system unit 1 has been ran tested, too. At 1:00pm, all recirculation pumps, except recirculation pump 2 at system unit 2, has been put in local and LOTO by NAC staff, for further inspection. Recirculation pumps 2 and 1 at system unit 1 and 2, respectively, removed on site for testing/inspection at pump supplier's warehouse. | Oak Ridges Air Management Facility | 2026-01-21
WW-CEAST | January | Weather today Partly Cloudy and -15 Celsius -On site to complete work orders W11515114, W11515527. -perform a station check. -Entered station readings into SharePoint. -Nutrient tank batch mixing. - System 2 recirculation pump #2 put in local for contractor to perform work on pump 2. | Oak Ridges Air Management Facility | 2026-01-16
WW-CEAST | January | Weather today Snow and -14 Celsius -On site to complete work order W11590185. -Operator Support on Site for Recirculation Pump Testing. -Shutting down the AMF fans and operated the recirculation pumps in Local Mode. -Fans back on and station back to normal operation. | Oak Ridges Air Management Facility | 2026-01-15
WW-CEAST | January | Weather today A Few Clouds and -16 Celsius -On site to complete work orders W11621031, W11621029. - Operator Support For Shut Down of MAU. - Operator Support For BIOREM Recirculation System Work. | Oak Ridges Air Management Facility | 2026-01-29
WW-CEAST | January | On site for recirc pump test with CD/Biorem. Shut off both fans for them to observe noise coming from the recirc pumps. 3 out of 4 pumps were tested ok, system 2 pump 1 had the most vibration. This will be looked at by the contractors. Put both Fans back on in auto, all system operating as intended after the pump test | Oak Ridges Air Management Facility | 2026-01-08
WW-CEAST | January | Weather today Snow and -4 Celsius -On site to complete work orders W11496495, W11496272. -perform a station check. -Entered station readings into SharePoint. -Nutrient tank batch mixing. | Oak Ridges Air Management Facility | 2026-01-05
EAST | January | On site for preventative maintenance Completed MIT and daily filter performance review and log - all okay Completed permeate turbidimeter maintenance and cleaning Batched citric acid tank for R Clean Inspected station and equipment - all okay | Georgina Water Treatment Plant | 2026-01-27
EAST | January | On site for preventative maintenance Completed Air compressor system inspection Air dryer check Air compressor maintenance Chlorine scrubber media sampling SO2 cylinder emergency kit inspection Station and equipment okay | Georgina Water Treatment Plant | 2026-01-16
EAST | January | Work on pvc pipe leak Glue in 6 inch coupling 90 and flange | Georgina Water Treatment Plant | 2026-01-21
EAST | January | Restarted the Local SCADA server due to Windows updates. Notified the Remote Operations Center and the OIC. Plant was shutdown during the work. | Georgina Water Treatment Plant | 2026-01-22
EAST | January | Turned on train 5 and initiated MIT at 07:20. | Georgina Water Treatment Plant | 2026-01-22
EAST | January | On site for station check and equipment verifications Reviewed MIT and daily filter performance on all membrane trains - All passed and within range - recorded readings into PWQ sheets Train #6 neutralization aborted alarm came in previously @09:38. The train never went through neutralization after the alarms came in, and did not complete the M-clean. Initiated a neutralization sequence on train #6 @14:00. Placed train back to standby @14:35 Made adjustment to close speed setpoint on the Backpulse tank clearwell fill valve. (Maintenance had repaired the line last week, and ops had found the valve was closing too quickly, causing some water hammer in the line. Reduced the close speed controller so the valve closes gradually. Made adjustments to train #7 clean / recirc feed valve that had failed to open earlier today. Adjusted the open speed, and the close limit, suspecting that the valve is getting stuck when trying to open Reduced high lift flow to 180 L/s Increased High lift flow back to 200 L/s @15:02 Completed PWQ sheets and data collection Reviewed station trending Station ok | Georgina Water Treatment Plant | 2026-01-30
EAST | January | Onsite to commission the Chlorine Booster pumps and installing new Discharge Header Analyzer (pH, Total Chlorine, Temperature and Turbidity) and the Raw Water Analyzer. The new analyzer was taken offline at 10:15am, to test and commission the analyzers we switch over the supply water intake to potable water. At 12:30pm we switched the Discharge Analyzer water supply was flipped back to normal operation, the Raw Water Analyzer supply water was switched to portable water for testing purposes. All analyzers are back on normal supplied water as of 1:14pm. Had to download to the PAC to change a IP address on the Chlorine Pump 2 | Georgina Water Treatment Plant | 2026-01-28
EAST | January | On site for monthly maintenance: Informed ROC Reviewed MIT and daily filter performance on all membrane trains - all passed and within range - recorded readings in PWQ sheets - Treated Header turbidity analyzer maintenance - GAC 1-4 Turbidity analyzer maintenance - High lift pump and motor inspection - High lift flow control valves test @10:25 - Initiated Hypo Recovery clean on train #5 Collected first grab sample on train #5 Hypo R-clean @12:00 (530 mg/L, pH = 10.01) @13:05 - Placed Uvs to auto, duty is active @13:05 Conducted GAC #1 filter backwash - informed ROC (OJT with Jackie S and Jack P) Placed GAC filter OOS in backwash filtration setpoints page Completed backwash using backwash Pump #1 - GAC inlet valve fault came in when first attempt to open, tried a second time and it opened okay Started GAC1 filter to waste @14:45 Collected second grab sample on train #5 hypo clean @15:05 - 330 mg/L, pH = 9.96 Stopped filter to waste @15:38, placed GAC1 back in service Equipment OOS: Sludge P3, Bisulfite P2 Station okay | Georgina Water Treatment Plant | 2026-01-15
EAST | January | On site for station check and preventative maintenance 8:45 Activated duty 1 to start plant and opened BKWS_MW1 to fill backwash clearwell, currently 4.91 M 8:54 Placed GAC4 OOS for backwash 8:59 Completed MIT and daily filter performance review and log - all okay 9:00 Closed GAC4 inlet valve to initiate GAC4 backwash, informed ROC to disregard alarms 9:02 Closed BKWS_MV1, finished filling backwash clearwell, level is 6.00 M 9:03 Manual open GAC4 effluent valve to drain GAC4 down to 3.0 M: 25% open setpoint, 27% real actuation as per SCADA, draining 51 L/s 9:26 Manual close GAC4 effluent valve, achieved GAC4 level 3.03 M 9:27 Manual close SV to turbidimeter, disregard turbidity alarms 9:28 Open backwash drain valve, backwash inlet valve and backwash pump recirculating valve 9:29 Backwash pump 2 manual on 9:30 Initiate two minute low wash. BKWS_PMP2_FCV1 manual open 25%, 136 L/s 9:32 Initiate seven minute high wash. BKWS_PMP2_FCV1 manual open 40%, 263 L/s 9:38 Initiate second two minute low wash. BKWS_PMP2_FCV1 manual open 25%, 166 L/s 9:40 Closed backwash drain valve to fill GAC4 9:49 Closed backwash flow control valve, shut down backwash pump, closed backwash inlet valve, closed backwash pump recirculating valve. GAC4 level 4.72 M. GAC4 settling 10:13 Opened GAC4 inlet valve, SV to turbidimeter and filter to waste valve - initiated filter to waste 10:32 Opened BKWS_MV1 to fill backwash clearwell, initial level: 2.86 M 11:09 Closed BKWS_MV1, backwash clearwell level: 5.28 M 11:57 Opened BKWS_MV1 to fill backwash clearwell. Closed GAC4 waste valve, completed filter to waste achieving a turbidity of 0.072 NTU. 11:59 GAC4 back in service 12:07 BKWS_MV1 closed, backwash clearwell level 5.99 M 14:45 Completed lab and station rounds Station and equipment okay | Georgina Water Treatment Plant | 2026-01-26
EAST | January | 7:55 Activated plant duty 1, placed GAC3 out of service, BKWS_MV1 manual open to top up Backwash clearwell to 6.0M 8:02 Completed MIT and daily filter performance review and log - all okay 8:28 BKWS_MV1 manual closed, backwash clearwell top up complete to 6.01M, initiating backwash of GAC3 and informed ROC 8:35 Train 2 transmembrane pressure at limit - Train 2 placed out of service 8:43 Initiated M Clean on Train 2 8:50 Isolated GAC3 turbidimeter for GAC3 backwash - okay to disregard turbidity alarms 9:20 Completed backwash of GAC3, allowing filter bed to settle before running to waste. Opened BKWS_MV1 to top up backwash clearwell 9:31 Initiated GAC3 filter to waste and opened turbidimeter solenoid valve to monitor turbidity 10:03 BKWS_MV1 closed - achieved 4.87M in the backwash clearwell, continuing to filter GAC3 to waste 11:15 Completed lab and station rounds - recorded observations in the shared PWQ sheet 11:24 Finished filter to waste, achieved 0.209 NTU, and returned GAC3 to service 11:56 Train 2 placed back in service after completion of M Clean 12:05 Topped up sodium hydroxide tank, Start 42, Stop 82 L Completed aeration blower maintenance, SO2 leak detector test, handheld spectrophotometer verification, permeate pump room housekeeping Station and equipment okay | Georgina Water Treatment Plant | 2026-01-23
EAST | January | On site for preventative maintenance work orders Completed MIT and daily filter performance review and log - all okay 10:12 Deactivated duty to initiate generator test run - Genset shut down on overcrank and failed to transfer - Informed CMS Team Lead Tyler Zimmerman-Jones, he will dispatch someone to investigate 10:44 Activated duty 1 10:55 BKWS_MV1 manual open to top up Backwash clearwell 13:04 Initiated generator test run 13:10 Train 2 permeate turbidity fault - okay to disregard, as a result of genset test Train 8 neutralization aborted alarm - neutralization was achieved prior to initiation of generator test and transfer - verified with grab sample (pH 7.80, TCl 0.10 mg/L) - placed back in service Generator test: Fuel level Start 0.74 M Stop 0.72 M Hours Start 512.62 Stop 513.97 Run statistics: Frequency 60 Hz Voltage 600 V Power 390 kW Current 270 A Truck bay gas leak alarm generated as a result of the generator test run - directed Remote Operator Connor to disregard 14:20 Train 2 permeate turbidity fault on station transfer back to utility power, plant was off - okay to disregard 14:46 Activated duty and placed station back in service | Georgina Water Treatment Plant | 2026-01-20
EAST | January | On site to respond to backpulse tank level hihi alarm. Tank 1?s fill valve is leaking while in closed position. Adjusted the close limit of the tank 1 fill valve, tested it several times, it is still leaking a bit. Its open/close speed is extremely slow.? Placed it man/off. Will investigate further tomorrow. Placed Backpulse tank 2 fill valve in lead duty. Tighten the bolts of the actuator so secured against the base plate.? Train 4 had intermittent low TMP alarm, reviewed the trend. It was spiking due to flow change. Plant is in production.? OOS equipment stayed the same as day shift: sludge P3, SBS P2.? | Georgina Water Treatment Plant | 2026-01-20
EAST | January | On site for sampling W11538406 and station check 9:20 Activated duty 1 9:31 Initiated Train 5 R clean 10:09 Completed MIT and Membrane performance review - all okay 10:30 Train 5 R clean soaking start point, pH 3.24, TCl 0.35 mg/L 12:05 Collected raw and treated water samples, W11538406, as well as GLIP samples Treated water FCl 2.11 mg/L; TCl 2.24 mg/L Verified chlorine analyzers (Grab/ Analyzer, in mg/L) Contact tank 1 FCl, 12:46, 2.82/ 2.71 Contact tank 2 FCl, 12:49, 1.93/ 1.87 Clearwell 1 FCl, 12:52, 2.48/ 2.57 Clearwell 2 FCl, 12:53, 2.00/ 1.90 Post clearwell, 12:54, 1.89/ 1.98 Keswick treated FCl, 12:59, 1.86/ 1.92 Keswick treated TCl, 12:59, 2.18/ 2.19 Sutton treated FCl, 13:00, 1.90/ 1.99 Sutton treated TCl, 13:00, 2.14/ 2.23 13:35 Completed sampling, lab and station rounds 14:25 Train 5 R clean soaking mid point, pH 3.19 Recorded observations in the shared PWQ sheet Station and equipment okay | Georgina Water Treatment Plant | 2026-01-21
EAST | January | Cleaned citric acid day tank as well as containment area. Filled the priming reservoirs with potable water. ? Maintenance crew completed the repair on the PVC line (backpulse supply line from service water). Re-Plumbed air supply line to actuator, BKPL_TK_PV3. Will test its function tomorrow since it is interlocked due to train 5's R clean process. Tested backpulse tank1 fill valve. Placed it in auto duty 1. It opened too slowly that it had fail to open alarm. Placed backpulse tank 2 fill valve in duty 1.? ? ? | Georgina Water Treatment Plant | 2026-01-21
EAST | January | 13:15 Placed train 2 permeate pump speed to manual 68%. Flow is around 38 l/s, TMP is around -59 kpa.? 13:20 Placed train 4 permeate pump speed to manual 68%. Flow is around 39 l/s, TMP is around -58 kpa.? 13:43 Sutton header grab chlorine residuals are: FCL = 2.00 mg/l, TCL = 2.34 mg/l. Sutton header analyzer readings are: FCL = 2.62 mg/l, TCL = 2.29 mg/l. 13:46 Standardized Sutton free analyzer reading according to 3 grabs' average.? 13:50 Keswick header grab chlorine residuals are: FCL = 2.03 mg/l, TCL = 2.26 mg/l. Keswick header analyzer readings are: FCL = 1.98 mg/l, TCL = 2.23. mg/l. 13:59 Deactivated plant duty.? Noticed a water hammer on Lowlift discharge header on duty shut?off. 14:40 grab total cl2 on raw water = 0.24 mg/l, analyzer = 0.12 mg/l Grab total cl2 on LL discharge = 0.17 mg/l, analyzer = 0.13 mg/l.? 14:47 standardized raw water chlorine analyzer reading according to 3 grabs? average.? 14:55 contractors work is done. Reactivated duty 15:03 duty was deactivated by central team. Communicated with team, activated again.? New low lift chlorine analyzers are commissioned today. Pre-chlorination is enabled to test the new instruments as well as chlorine booster pumps starters. | Georgina Water Treatment Plant | 2026-01-28
EAST | January | On site for station check, equipment verification and lab analysis. 9:25 Reviewed MIT and filter performance on all membrane trains - all passed and within range. Recorded readings into PWQ sheets. 10:10 activated system duty 10:30 Train 5 shutdown on turbidity hihi alarm, reviewed trends. Turbidity spike on start up, cleared alarm, placed train in backwash and return to service. 14:14 UV high dosage alarm, caused by backwash clearwell being filled with one train running. Completed Plant PWQ sheets, verified chemical dosages. Topped up citric acid tank. Verified analyzer readings - CT tanks, Clearwells, Treated, no adjustments needed. Reviewed trends - no issues. Equipment OOS: sludge pump 3 and SBS pump 2. Station ok. | Georgina Water Treatment Plant | 2026-01-16
EAST | January | On site for station check and lab 9:30 Train 2 - MIT test failed - restarted MIT test and passed 9:48 Activated duty 9:50 Confirmed all trains passed MIT and each membrane meets operating specifications 11:50 Completed station rounds and lab - recorded observations in the shared PWQ Sheet - Rotated raw water sample pumps - P3 to P2 - Placed BOGE air compressor off and Kaiser in lead - Rotated backpulse fill valves - BKPL_TK1 in lead - Rotated post chlorinator ejectors 12:37 Completed low lift station check 13:30 Received citric acid delivery Station and equipment okay | Georgina Water Treatment Plant | 2026-01-19
EAST | January | Received call from ROC about make up air handling unit OOS. Asked supervisor if it was actionable for a call out. It was directed to not go out. Called ROC that it is a disregard till Monday. | Georgina Water Treatment Plant | 2026-01-23
EAST | January | 13:13 LLP3 had uncommanded stop alarm.? Placed it back in duty 1. It is running OK. However, the hydraulic valve uncommanded close alarm came in on duty shut off. Reset alarm. Tested BKPS_TK_PV3 by open/close it, the PSW supply to backpulse tank is back in service.? However, there is excessive water hammer when the valve is closed.? Reset the flame failure for chemical room MAU.? | Georgina Water Treatment Plant | 2026-01-22
EAST | January | 9:00 On site for station check 9:15 Completed MIT and daily filter performance review and log - all okay 9:24 Verified backwash clearwell level of 6.01 M, initiating backwash of GAC2 11:07 Completed manual backwash of GAC 2 and initiated filter to waste 12:55 Filtered GAC 2 to waste to 0.083 NTU and returned to service 14:00 Completed chlorine tonner bank 1 change, chlorine system inspection and chlorine leak test Station and equipment okay | Georgina Water Treatment Plant | 2026-01-22
EAST | January | On site for sampling and station check Activated duty 1, 8:50 Train 2 MIT sequence abort alarm - 8:57 Train 2 off and restart MIT GRTPLL Pre-chlorination booster pump 1 overload - Lexan on site working on pre-chlorination booster pumps and chlorine analyzers. Disregard pH, temperature and chlorine alarms. Chris Scott on site supervising work with Lexan. Placed Train 2 back in service after MIT complete and passed, 9:31 Initiated Hypo R Clean on Train 6, chemical injection via recirculation by CIP_PMP1, 9:32 Completed MIT and daily filter performance review and log - all okay Collected raw water GLIP and micro sample W11550855, 10:25 Enabled low lift chlorination for zebra mussel control (pre-chlorination) for Lexan low lift chlorine system work, chlorinator 8 is in duty 1, chlorine booster pump 2, 10:40 Verified Train 6 hypo R clean hypo concentration for soak = 375 ppm, 10:58 Collected treated water samples, W11550855, 12:15 FCl 2.16 mg/L TCl 2.29 mg/L Duty 1 deactivated to assist Lexan low lift work, 14:03. Dan Zhou on site at the low lift building to supervise and assist Lexan as required. New pre-chlorination chlorine analyzers have been commissioned. Pre-chlorination will be in service for a test one week in duration. Post-chlorine dosage factor lowered by 2 as a consideration. Completed lab and station rounds, 14:24 Station and equipment okay | Georgina Water Treatment Plant | 2026-01-28
EAST | January | At 17:06 on 01/25/2026 informed ROC to up flow at GWTP from 180l/s to 200l/s due to KWTP being off. This is a contingency entry. | Georgina Water Treatment Plant | 2026-01-29
EAST | January | Changed Train 6 status to ON to initiate MIT. Changed train 4 status to OFF to abort M-Clean pending. Then put back ON to start production. | Georgina Water Treatment Plant | 2026-01-29
EAST | January | Performed lab analysis. See Lab sheet for detailed information. ? 11:35 Keswick header fluoride grab = 0.817 mg/l, analyzer = 0.58 mg/l. Sutton header fluoride grab = 0.798, analyzer = 0.52 mg/l. 11:40 standardized both fluoride analyzer readings according to 3 grabs? average. 11:43 Fluoride pump 1 DF lowered from 1.09 to 0.95. 11:46 man/start clear well re-circulation pump. 12:11 Switched fluoride pump to pump 2. 12:30 lowered fluoride pump 2 dose factor from 0.65 to 0.50. 12:45 Placed LLP2 in duty 1, its hydraulic valve in-commanded close alarm came in. Reset alarm, LLP2 is back in standby. Will test it tomorrow. Train 4 CIP inlet valve had fail to open alarm. Ack+reset alarm, the valve opened.? Equipment OOS: sludge pump 3, SBS pump2, chlorine toner 1.? ? | Georgina Water Treatment Plant | 2026-01-19
EAST | January | Completed assigned work orders: Chlorine emergency repair kit inspection. Sutton/Keswick Header chlorine analyzers maintenance and inspection. Housekeeping (Chlorine and scrubber rooms). | Georgina Water Treatment Plant | 2026-01-23
EAST | January | On 01/28/2026 at 01:58 received call from ROC about train 2 failed MIT result. Informed ROC at this time to put train 2 to off. This entry is a contingency entry for this issue. | Georgina Water Treatment Plant | 2026-01-29
EAST | January | On site to respond to reports of generator over crank alarm. Suspect intermittent issue with the speed sensing relay inside the engine controller cabinet. Disassembled and cleaned potentiometer inside speed sensing relay. Tested numerous times and generator started correctly every time. Operations ran station generator test successfully. | Georgina Water Treatment Plant | 2026-01-20
EAST | January | GWLL - Completed station check at Low Lift building. Completed housekeeping. | Georgina Water Treatment Plant | 2026-01-26
EAST | January | On site for OJT for train membrane repair. Train 6 shut down on hihi NTU at 12:43, Joe Mazza is taking grab on mNTU to confirm if analyzer is reading correctly. Train 4 is currently off for membrane repair grab was 50mNTU and the analyzer is currently 44mNTU. Ack and rest alarm at 12:57 put train 6 to off at 12:57 and putting train 6 into a backwash at 12:57. This is to clear the mNTU alarms. Manually pressurizing train 4 to check for leaks in the membranes. Started pressurizing at 13:03 on the low pressure side. Reviewed MIT and daily filter performance on all trains - all passed. Low lift analyzers both new and old are running concurrently. | Georgina Water Treatment Plant | 2026-01-29
EAST | January | Initiated MIT on train #1 @07:41 - It was left off after recovery clean yesterday. MIT passed: High: 3.83 kpa, Low: 3.42 kpa. All okay, placed train #1 to ON Initiated Recovery clean Hypo @08:12 on train #3 | Georgina Water Treatment Plant | 2026-01-08
EAST | January | On site for station check, lab analysis and to collect weekly micro samples (W11522789) and monthly THM samples (W11503189) Reviewed MIT and daily filter performance on all membrane trains - all passed and within range - recorded station readings in PWQ sheets Completed Plant PWQ sheets and data collection Contractors on site for new PT and CT in low lifts 3 and 4. Low lift station had to be completely shutdown to work on low lifts 3 and 4. Various alarms generated during their work. (Membrane Low tank level alarms, Low lift equipment fault alarms, estop alarms) All alarms cleared and low lifts pumps 3 and 4 back in service and in duty Received Sodium Bisulfite delivery: Start: 0.33 m, Stop: 0.92 m @09:32 - Activated system duty Collected Raw water samples @10:55 - Micro and THM samples Collected GLIP samples Verified analyzer readings with grab chlorine residuals: Contact tanks, Clearwells, Treated Residuals: (Grab / Analyzer) @11:28 CT #1: 2.48 / 2.47 @11:30 CT #2: 1.84 / 1.89 @11:33 CW #1: 2.12 / 2.12 @11:34 CW #2: 1.74 / 1.72 @11:38 Post CW: 1.70, 1.67, 1.70 / 2.27 - Adjusted to 1.70 based on average of grabs @11:40 Sutton Free: 1.83 / 1.87 @11:40 Sutton Total: 2.15 / 2.08 @11:46 Keswick Free: 1.72 / 1.71 @11:46 Keswick Total: 1.96 / 1.95 Collected Treated samples @11:50 - Micro and THM Completed lab analysis on Raw, Treated and Permeate waters Operational Adjustments: Chlorinator #5 Dosage factor 53 ----> 52% Chlorinator #6 Dosage factor 54 ----> 53% Completed washwater and water to the lake analyzer maintenance. Attempted to calibrate east sedimentation tank analyzer, but after span calibration the analyzer went hihi. Shut off water supply to analyzer for tonight, and will look at it again tomorrow. Took grab residual @15:00 - 0.00 mg/L, all okay Reviewed trends, equipment OOS: Sludge P3, Bisulfite P2 Station ok | Georgina Water Treatment Plant | 2026-01-14
EAST | January | On site for station check, lab analysis and data collection, and OJT with Adeela Khan from ROC Reviewed MIT and daily filter performance on all membrane trains - all passed and within range - recorded readings in PWQ sheets @08:50 - Initiated Recovery Clean acid on train #3 @09:50 - Collected first grab sample on train #3 acid clean - pH = 3.10 Completed Plant PWQ sheets, dosage verifications, and data collection @14:10 - Collected second grab sample on train #3 acid clean - pH = 3.12 Completed Washwater pump maintenance and duty rotation Completed sludge pump maintenance Train #3 remains in Recovery clean, in neautralization Reviewed trends, equipment OOS: Sludge P3, Bisulfite P2 Station ok | Georgina Water Treatment Plant | 2026-01-09
EAST | January | Trains 7 aborted M-clean and shut down as notified by ROC. During remote scada review, noticed backpulse tanks level dropped again to 0.6m (second time in 2 days, same time) backpulse pumps lockout on flow low low alarm. Backpulse tanks level at 0.6m Arrived on site, found all permeate turb analyzer fault due to empty permeate header, no flow to analyzers, opened UV system effluent valve 1 to bring back water from the GACs to prime permeate header and to analyzers. Purged air out of both permeate headers and permeate header turbidity analyzers sample lines, returned effluent valves in to auto. Cleared alarms. Reviewed MITs on trains, all trains passed MITs. Activated duty, no issues | Georgina Water Treatment Plant | 2026-01-11
EAST | January | Trains 3 and 4 aborted M-cleans and shut down as notified by ROC. During remote scada review, noticed backpulse tank 1 inlet valve (in lead duty) failed to open causing backpulse pumps to lockout on flow low low alarm. Tried to opened in manual and it failed as well. Backpulse tanks level at 0.9m Placed tank2 inlet valve in manual and opened, filled backpulse tanks enough to clear interlock on alarms. Backpulse tanks drained permeate header during tank fill which triggered turbidity fault on all permeate turbidity analyzers. Arrived on site, opened UV system effluent valve 1 to bring back water from the GACs to prime permeate header and to analyzers. Purged air out of both permeate headers and permeate header turbidity analyzers sample lines, returned effluent valves in to auto. Cleared alarms. Reviewed MITs on trains, all trains passed MITs. Activated duty, no issues Did visual inspection on backpulse tank 1 inlet valve, noticed actuator is disconnected from valve rendering it inoperable. Placed in manual for MAINT to investigate further after the weekend. Placed tank2 inlet valve in lead duty. Make up site unit I coil low temp alarm. Checked LED screen on unit for alarms ~ Combustion air fan feedback missing. Changed out filter, cleared and reset alarm. Unit back in service. Monitor station operations for few mins before leaving site Notified ROC. | Georgina Water Treatment Plant | 2026-01-10
EAST | January | On site for station check, equipment verifications and lab analysis Reviewed MIT and daily filter performance on all membrane trains - all passed and within range - recorded readings into PWQ sheets Worked with mechanical on resolving issues with backpulse tank fill valve #1 While mechanical was working on the valve, the permeate common header had drained, causing turbidity faults on all the trains from @09:56 to @10:37. Placed UVs to manual off @10:50 - Opened UV 1 inlet and outlet valves to backfill the permeate header. Header is recharged and cleared air from line. Resolved outstanding turbidity faults on membrane trains 7, 5 and 3. Lines were airlocked due to the permeate header emptying. Cleared alarms, placed UV valves back to auto Placed UVs to auto @11:35 - duty activated Recieved Hypo delivery - 1000L Operational adjustments: - Duty rotated clearwell chlorinators - Placed chlorinator #5 to D1. Verified chlorinator performance after switching - Duty rotated clearwell solenoid chlorine valves - placed valve #1 to D1 - Duty rotated raw water sampling pumps - placed P3 to D1 Completed Plant PWQ sheets, verified chemical dosages Verified analyzer readings - CT tanks, Clearwells, Treated Adjusted post clearwell analyzer from 1.51 to 1.75 mg/L based on average of 3 grabs Initiated an MIT on train #2 @14:16 to test pressure decay. MIT numbers are higher than usual since doing recovery clean on train #2. MIT passed - located a decent size leak on cassette C, will address at a later date. MIT passed. Span calibration on east sedimentation tank chlorine analyzer Reviewed trends, equipment OOS: None Station ok | Georgina Water Treatment Plant | 2026-01-12
EAST | January | On site to assist with HLP4 commissioning and testing. Plant duty is active and HLP2 is in lead duty. Contractors verified motor rotation direction is good. However, VFD/Multilin setup is not complete and mechanical seal is not complete. Did not test HLP4 today. HLP4 remains offline and isolated. All alarms associated with HLP4 are to be disregarded. Train 3 finished R clean. Placed it online and in production. | Georgina Water Treatment Plant | 2026-01-08
EAST | January | Low Lift Building - Completed the following work orders: JHSC inspections, Turbidity analyzer maintenance, Chlorine analyzer maintenance. | Georgina Water Treatment Plant | 2026-01-08
EAST | January | Confirmed with contractors that there is no HLP4 pump test today.? 09:24 grab fluoride residual from Sutton header?= 0.808 mg/l, analyzer = 0.99 mg/l.? grab fluoride residual from Keswick header = 0.576 mg/l, analyzer = 0.94 mg/l.? 09:35 2nd and 3rd Sutton fluoride grab = 0.816 mg/l, 0.841 mg/l.? 09:35 2nd and 3rd Keswick fluoride grab = 0.788 mg/l, 0.829 mg/l.? Verified calculated fluoride dose = 0.74 mg/l. 09:50 adjusted Sutton fluoride analyzer to 0.82 mg/l adjusted Keswick fluoride analyzer to 0.80 mg/s. 10:11 Keswick header grab free cl2 = 1.69 mg/l, analyzer free = 1.62 mg/l. Grab total cl2 = 1.96 mg/l, analyzer = 1.83 mg/l, standardized total analyzer reading according to 3 grabs' average.? 10:36 post clear well grab free cl2 = 1.67 mg/l, analyzer. = 2.41 mg/l. Standardized the reading accordingly. 11:28 adjusted fluoride analyzer reading according to 3 grabs' average again. (Plant is active) Decreased fluoride pump 1 DF from 1.14 to 1.09.? other lab results are entered in Lab sheet.? | Georgina Water Treatment Plant | 2026-01-09
EAST | January | On site for monthly maintenance - Informed ROC of work to be completed Reviewed MIT and daily filter performance on all membrane trains - All passed and within range - recorded readings in PWQ sheets Completed UV system cleaning with Jack P and Jackie S. Informed ROC of alarms Contractors on site at Low lift for the low lift pump 1 and 2 PT and CT installation @10:50 - Opened train #1 raw water valve, and started low lift pump #1 to test after contractors were working on it. Ran low lift pump #1 at different speeds to test to ensure operation is normal. While running, the pump interlocked on uncomanded stop, and hydraulic valve uncomanded close. Worked with Eaton and Lexsan to resolve the issues with Low lift #1 from 11:00 to 11:45. Ran the low lift #1 to train #1 while tested, caused low tank level alarms in train #1. Placed low lift #1 back to auto once completed testing, all okay @11:20 - Backpulse pumps lolo flow and interlock, and train #7 neutralization aborted alarms. Cause of alarms was the result of the Permeate header draining empty again. Also caused multiple turbidity faults. This is a known issue, as the backpulse tanks are drawn down for Maintenance cleans while the plant is off, while also draining the permeate header. The service water line that normally feeds the backpulse tanks is currently OOS due to a pipe break. Opened the UV inlet and outlet valves to backfill the permeate line and fill the backpulse tanks. Worked with Jack P and Jackie Saunders. Cleared turbidity fault alarms once the common header was full again @11:55 - Initiated neutralization sequence on train #7 as it had aborted during the previous alarm sequence Completed UV system calibrations on UV #1 and #2 - No issues with calibrations, recorded data in PWQ sheets @13:46 to 13:55 - Tested low lift pump #2 after contractors had worked on it. They made the same changes as pump #1. No concerns found with testing. Ran the low lift to train #1 again while testing. @13:48 Activated system duty - with UV #2 in duty 1 Disabled Maintenance Cleans on trains 1-4 on Saturdays Disabled Maintenance cleans on trains 5-8 on Sundays Placed Low lifts 1 and 2 in Duty 1 and 2, to test overnight after contractors work on them today Alarms cleared, equipment back to auto | Georgina Water Treatment Plant | 2026-01-13
EAST | January | On site for monthly maintenance Train #1 shutdown on hihi turbidity @09:00 - Reviewed trends, turbidity spiked on startup. First run after Recovery clean. Placed train to backwash and back into service Reviewed MIT and daily filter performance on all membrane trains - MIT's all passed. Daily filter performance readings all within range. Collected first grab sample on train #3 hypo R-clean - 460 mg/L Cl2, pH = 9.94 Completed the following WO's: - Low lift flow control valves inspection and test - Cleaned Y-strainers, engaged e-stops on low lift pumps during work. Caused LL hydraulic valve alarms - Low lift pump and motor inspection - Caustic soda pumps inspection and maintenance: Also topped up day tank from 28 to 108 L - Sodium bisulfite pumps inspection and maintenance - Completed chlorine analyzer maintenance on CT tanks and clearwells, topped up electrolyte and grit. Cleaning and Verification of analyzers completed yesterday - Membrane cassette and tank inspections Collected second grab sample for train #3 hypo recovery clean @13:55 - 430 mg/L cl2, pH = 9.89 Station ok | Georgina Water Treatment Plant | 2026-01-08
EAST | January | @17:16 - ROC called for Train #7 shutdown alarm. Reviewed trends, unclear what cause the shutdown, turbidity trends are normal. Placed train back to standby, duty is off | Georgina Water Treatment Plant | 2026-01-05
EAST | January | On site for station check, lab analysis and to collect weekly micro samples (W11503389) and monthly algae samples (W11503534) - Initiated Recovery clean acid on train #1 @08:53. Prepared citric acid day tank for recovery clean - Reviewed MIT and daily filter performance on all membrane trains - ZW1 performance yesterday low alarm is active. The train had completed a recovery clean hypo yesterday, causing elevated turbidity on startup. Reviewed trends, filter performance is currently 99.19% for the day yesterday, and 99.91% for the month. Will continue to monitor. MIT numbers all passed, no issues - recorded readings into PWQ sheets @09:37 - Activated Keswick and Sutton Duty - Controlling ET @68% Collected first grab sample on train #1 acid clean @10:25 - pH = 3.12 Collected Raw samples @09:45 - Micro and Algae Collected weekly GLIP samples Enabled Maintenance cleans on the weekends, as with recovery cleans being completed during the week, M-cleans have no been occuring as often - Enabled Trains #1 to #4 on Saturdays - Enabled Trains #5 to #8 on Sundays Verification on Chlorine analyzers in basement: CT Tanks, Clearwells, Treated, Residual Management @11:40 CT#1 - Grabs: 2.48, 2.50, 2.48 / Analyzer: 2.25 - Adjusted analyzer to 2.48 mg/L based on grabs @11:44 CT#2 - Grab: 1.60 / Analyzer: 1.57 @11:46 CW#1 - Grab: 1.74 / Analyzer: 1.73 @11:48 CW#2 - Grab: 1.33 / Analyzer: 1.30 @11:51 Post CW - Grab: 1.79 / Analyzer: 1.78 @11:54 Sutton free - Grab: 1.80 / Analyzer: 1.73 @11:54 Sutton total - Grab: 2.04 / Analyzer: 1.97 @11:59 Keswick free - Grab: 1.85 / Analyzer: 1.78 @11:59 Keswick total - Grab: 2.07 / Analyzer: 2.05 Collected Treated samples from Keswick header @12:05 - Micro and Algae Collected operational monitoring samples (In-house lab) Collected second grab sample from train #1 Recovery clean @12:17 - pH = 2.98 Completed Plant PWQ sheets and data collection Completed Lab data sheets for Raw, Treated and Permeate Reviewed trends Train #1 finishing Recovery Clean acid, will request ROC to place train back to standby after completed Station ok | Georgina Water Treatment Plant | 2026-01-07
EAST | January | On site for monthly maintenance: Informed ROC - Initiated Recovery clean Hypo on train #1 @08:25 - Initiated MIT on train #4 @08:40 - it was left off after recovery clean yesterday. MIT passed: High: 5.11 kpa, Low: 1.41 kpa. Placed train #4 to ON, in standby - JHSC Health and safety inspection from 09:28 to 10:35. Triggered eyewash alarms - Clearwell draining pump / manual valves exercises - UVT analyzer dehumidifier element change out - Caused UVT fault and OOR alarms, cleared alarms. - Permeate and CIP chlorine analyzer maintenance - Permeate header turbidity analyzer maintenance and calibration - Sodium hypo pumps inspection - Lab reagents inventory / replace System duty reached start setpoint and activated @11:00 - Controlling tower level is 45% - Triggered chemical containment flood alarms - SBS, Hypo, Fluoride - Triggered SO2 leak alarms in SO2 room and SBS room R-clean was initially started with heated clean, the boilers are not working very well due to the cold water temperature. Disabled the heating, and started R-clean soak. Due to the heat maintain also being enabled, the R-clean tried to call for more chemical injection @13:00. Stopped hypo pumps, and placed them to manual off. Insufficient chemical alarm came in on train #1, disregard alarm, chemical content is sufficient, verified with grab sample. Collected first Grab sample on train #1 Recovery clean @12:50 - 360 ppm, 9.77 pH. - Will leave hypo pumps manual off for duration on R-clean, and will clear alarms after. Adjusted Clearwell chlorine dosing factors: - Chlorinator #5: 54 to 53% - Chlorinator #6: 55 to 54% Collected Second grab sample on train #1 Recovery clean @15:20 - 380 ppm, 9.78 pH Equipment OOS: Sludge P3, Bisulfite P2, Hypo pumps OOS for the time being, will place back to auto after R-clean is done Equipment back to auto, station ok | Georgina Water Treatment Plant | 2026-01-06
EAST | January | ROC called regarding train #4 shutdown @11:11 - Train 4 shutdown on turbidity hihi. Reviewed trends, spiked on startup and immediately came back down. Train #4 did a recovery clean yesterday, has not ran in production since the clean, suspect that is the cause of the turbidity spike. @11:15 placed train 4 to backwash and back in service, will monitor on next startup | Georgina Water Treatment Plant | 2026-01-03
EAST | January | ROC called regarding Train #8 TMP Lolo alarm, train shutdown. Second time it has came in today. Requested ROC to disregard until tomorrow. Train left in shutdown mode | Georgina Water Treatment Plant | 2026-01-01
EAST | January | On site for station check, equipment verifications and lab analysis Initiated Recovery clean Hypo on train #4 @09:27. Initiated MIT on train #8 @09:35 - It was left off last night due to TMP lolo alarms. Opened the isolated cassette on train #8 to test MIT on train #8 with all cassettes open. Train #8 passed: High: 2.54, Low: 1.36 kpa. Placed train #8 to on. All cassettes are open on train #8 Reviewed MIT and daily filter performance on all membrane trains - all passed and within range - recorded readings into PWQ sheets Activated system duty @10:35 for station checks Train #4 R-clean: Observed that the hypo tank level has not changed since start of R-clean. Chemical injection step has passed, train is in the heating process to 15 C. Calculated that the hypo from last recovery clean used 0.08 m of the tank. Manually injected hypo from 11:13 to 11:44. Tank level went from 1.04 m to 0.97 m = 110.86 L. Took first grab residual on Recovery clean @14:25 - 250 mg/L / 9.68 pH Completed plant PWQ sheets and data collection Completed lab analysis for raw and treated water - see lab data sheets Verification of chlorine analyzers in basement: Contact tanks, clearwells, treated, residual management @14:10 - Adjusted Keswick header FCL from 2.08 mg/L to 1.99 mg/L Cycled power to particle counter units, alarms cleared. ROC informed in shift report to disregard if it comes back in Reviewed trends, equipment OOS: Sludge P3, Bisulfite P2 Train #4 remains in Recovery clean, will monitor throughout the day remotely Station ok | Georgina Water Treatment Plant | 2026-01-02
EAST | January | Responding to site for trains #1 and 2 turbidity faults and for backpulse system issues that occurred earlier in the day CMU5#W11552922 - Trains #1 and 2 turbidity analyzers were airlocked, due the emptying on the permeate header during backpulse issues this morning. Cleared air from turbidity lines, faults cleared. Trains available to run now. - @13:34 Train #8 TMP lolo alarm came in, interlocking the train. Reviewed trend and saw that the trend for TMP was very erratic during the run cycle. Placed train to backwash, and reset alarms, back in service. Train #8 will have recovery cleans completed next to address TMP alarms. Inspected train on filter top and noticed that there is 1 high pressure cassette isolated, both halves, likely contributing to the TMP alarms. Unclear why they are isolated, will test cassettes for leaks in coming days - Increased plant flow back to 180 L/s - Observed both train #1 and 2 running, both seem okay Performed MIT review and daily / monthly filter performance review on all membrane trains - all passed, and within range - recorded readings in PWQ sheets No further issues on site, plant is running, controlling ET @53% | Georgina Water Treatment Plant | 2026-01-01
EAST | January | On site for station check, equipment verifications and lab analysis Prepared Citric acid tank for Recovery clean - Initiated train #4 Acid R-clean @09:12 Topped up Sodium hydroxide day tank to 95L Activated system duty @09:40 for station check Reviewed MIT and daily filter performance on all membrane trains - all passed and within range - recorded into PWQ sheets. Completed PWQ sheets. plant rounds and data collection. Operations and adjustments: Duty rotated raw water sampling pumps - Duty rotated clearwell solenoid valves - placed valve #2 in D1 @11:43 Duty rotated clearwell chlorinators - placed chlorinator #6 to D1 @11:44 Duty rotated low lift sampling pumps - placed P1 to D1 Verified Basement chlorine analyzers: Contact tanks, Clearwell, Treated, Residual management. Made the following adjustments: @13:29 - Adjusted Post Clearwell analyzer from 1.40 mg/L to 1.90 mg/L @13:05 - Adjusted sutton TCL from 2.31 mg/L to 2.19 mg/L Completed in-house lab analysis on Raw and treated water Completed low lift station check and mussel plate inspection Reviewed trends, equipment OOS: Sludge P3, Bisulfite P2 Station ok | Georgina Water Treatment Plant | 2026-01-05
EAST | January | Reviewed monthly filter performances data and all of them are compliant. | Georgina Water Treatment Plant | 2026-01-02
EAST | January | Placed train #4 to standby, it completed recovery clean. Plant duty is off | Georgina Water Treatment Plant | 2026-01-02
EAST | January | ROC called for Train #3 shutdown on neutralization and backpulse flow lolo alarms Noticed that the backpulse tank was low at 0.63 m. Opened tank 2 fill vlave to fill tanks, now at 0.92 m Trains #4 and 8 faulted on turbidity fault. Suspect the the permeate pipe has partially drained, causing all of these alarms. - Opened UV 1 influent and effluent valves, to fill up the permeate pipe back from the GAC inlet channel - @11:32: caused UV reactor 1 effluent / influent vlaves failed to open and seq/start fault. - @11:34: Train #3 alarms and backpulse pump alarms cleared. Initiated a neutralization sequence on train #3 - sequence aborted again on lolo flow. - Opened UV valves again fully, and filled backpulse tanks and the permeate header for a long time period this time. Filled backpulse tanks, causing a high alarm - Initiated Backpulse on train #4 @11:50, it went through okay, no alarms generated - Closed UV 1 valves, placed back to auto Placed UV 1 to auto @12:09, it started in auto. Will monitor plant on startup. After the plant started, there is an outstanding turbidity faults on trains 1 and 2 that are not clearing. Will attend site, requested at CMU5 from ROC Backpulse system appears to be working as normal now. Plaaced UV2 back to auto as well Trains #1 and 2 are not able to currently run, so reduced high lift flow to 150 L/s until resolved | Georgina Water Treatment Plant | 2026-01-01
EAST | January | @19:00 - Placed Hypo pumps 1 and 2 back to auto, cleared alarms @19:19 - placed train #1 to standby, and enabled demand override. Recovery clean is complete. All okay | Georgina Water Treatment Plant | 2026-01-06