## Aurora SPS
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS
12277089 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12277089 | 1 | 2026-01-02 09:48 | 2026-01-02 09:47 | Barry Middleton (WW-CEAST) @ Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility - AUSSMP Date Work Completed: 2026-01-02 09:47 ————————————————————— Weather today Clear and -9 Celsius -On site to complete work order W11489844. -Completed station check. -Entered station readings into SharePoint. -Pumps 2, 4, 5 and 6 available in timed auto duty rotation every 3 hours. -Pump 3, which is in manual/duty 7, out of service due to discharge flow fault. -Pump 1 is in manual/duty 7. -Standby power generators available in auto. -Checked dry well, Ok. -All lines available in auto at the dump pad for the haulers. -Checked bar screens. Rotated bin. Cleaned bar screen room of rags. -Two rag bins pushed outside last week not pick up by Miller Waste. ————————————————————— • Attachments: 0
12283807 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12283807 | 2 | 2026-01-05 13:26 | 2026-01-05 13:25 | Barry Middleton (WW-CEAST) @ Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility - AUSSMP Date Work Completed: 2026-01-05 13:25 ————————————————————— Weather today Overcast and -3 Celsius -On site to complete work orders W11493907, W11472962. -Completed station check. -Entered station readings into SharePoint. -Pumps 2, 4, 5 and 6 available in timed auto duty rotation every 3 hours. -Pump 3, which is in manual/duty 7, out of service due to discharge flow fault. -Pump 1 is in manual/duty 7. -Standby power generators available in auto. -Checked dry well, Ok. -All lines available in auto at the dump pad for the haulers. -Checked bar screens. Rotated bin. Cleaned bar screen room of rags. -SCADA Review. ————————————————————— • Attachments: 0
12291962 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12291962 | 1 | 2026-01-07 09:19 | 2026-01-07 09:19 | Barry Middleton (WW-CEAST) @ Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility - AUSSMP Date Work Completed: 2026-01-07 09:19 ————————————————————— Weather today Overcast and 1 Celsius -On site to complete work order W11501989, W11489032, W11489032, W11500942, W11502470, W11491164, W11489432. -Completed station check. -Entered station and generator readings into SharePoint. -Bar screen bin removal and replacement. -Air compressor inspection and cleaning. -Standby Power Generators 1, 2, and 3 test run. -Hazardous waste collection and removal. -JHSC Health and Safety Inspection. -Pumps 2, 4, 5 and 6 available in timed auto duty rotation every 3 hours. -Pump 3, which is in manual/duty 7, out of service due to discharge flow fault. -Pump 1 is in manual/duty 7. -Standby power generators available in auto. -Checked dry well, Ok. -All lines available in auto at the dump pad for the haulers. -Checked bar screens. Rotated bin. Cleaned bar screen room of rags. -Bar Screen Bin Removal and Replacement - pushed rag bins out for pick up by Miller Waste. ————————————————————— • Attachments: 0
12299102 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12299102 | 1 | 2026-01-09 14:08 | 2026-01-09 14:08 | Barry Middleton (WW-CEAST) @ Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility - AUSSMP Date Work Completed: 2026-01-09 14:08 ————————————————————— Weather today Overcast and 5 Celsius -On site to complete work orders W11565192, W11509779. -Completed station check. -Entered station readings into SharePoint. -Unit Heater replacement and MCC 5 Shutdown. -Unit Heater in screen room have been replaced. -Pumps 2, 4, 5 and 6 available in timed auto duty rotation every 3 hours. -Pump 3, which is in manual/duty 7, out of service due to discharge flow fault. -Pump 1 is in manual/duty 7. -Standby power generators available in auto. -Checked dry well, Ok. -All lines available in auto at the dump pad for the haulers. -Checked bar screens. Rotated bin. Cleaned bar screen room of rags. ————————————————————— • Attachments: 0
12298353 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12298353 | 1 | 2026-01-09 11:02 | 2026-01-09 10:56 | Bill Van Bakel (WW-MAINT) @ Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility - AUSSMP Date Work Completed: 2026-01-09 10:56 ————————————————————— On site for pump 1 discharge valve. Found the actuator to be faulty we will source a replacement. Will on site we found bar screen 2 to be tripped on overload. Adjusted the rake on both screens and preformed a pm on both. Screens are in service ————————————————————— • Worked With: Terry Cantwell • Attachments: 0
12303618 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12303618 | 5 | 2026-01-12 09:50 | 2026-01-12 09:49 | Marcos Tungcol (WW-CEAST) @ Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility - AUSSMP Date Work Completed: 2026-01-12 09:49 ————————————————————— On site completed Station Check. Pumps 2, 4 and 6 available in timed auto duty rotation every 3 hours. Pump 1 out of service due to discharge valve issue. Pump 3 still in manual/duty 7 but has been primed and available if needed and can be ran remotely. Pump 5, while on site developed leakage alarm. It is now in manual/duty 7. Created work order request for CMS to check the problem ( W11581590). All standby power generators available in auto. Checked dry well, ok. Checked bar screens. Rotated rag bin. Cleaned bar screen room of rags. All lines available in auto at the dump pad for the haulers to be used. As per Team Lead’s instruction, put pump 3 in duty 1 and ran. It is not registering any flow reading in its discharge flow FIT due to fault and also at the combined flow FIT. It seems, there is flows coming out since the wet well level is not really going up. It, somewhat, maintaining the wet well level. Pump 5 back in service. CMS fixed the problem. See eLogbook entry of CMS above. Aurora is now back to 4 pumps in auto. Pump 3 is available when needed. ————————————————————— • Attachments: 0
12317980 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12317980 | 1 | 2026-01-16 12:59 | 2026-01-16 12:59 | Barry Middleton (WW-CEAST) @ Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility - AUSSMP Date Work Completed: 2026-01-16 12:59 ————————————————————— Weather today Mostly cloudy and -6 Celsius -On site to complete work order W11527342. -Completed station check. -Entered station readings into SharePoint. -Pumps 2, 4, 5, and 6 available in timed auto duty rotation every 3 hours. -Pump 1 out of service due to discharge valve issue. -Pump 3 still in manual/duty 7 but has been primed and available if needed and can be ran remotely. -Standby power generators available in auto. -Checked dry well, Ok. -All lines available in auto at the dump pad for the haulers. -Checked bar screens and Rotated bin. -Cleaned bar screen room of rags and bar screen oil full. ————————————————————— • Attachments: 0
12328940 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12328940 | 1 | 2026-01-21 15:01 | 2026-01-21 14:56 | Bill Van Bakel (WW-MAINT) @ Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility - AUSSMP Date Work Completed: 2026-01-21 14:56 ————————————————————— On site to replace pump 1 with a rebuild with a new bowl. Pump is installed but not in service due to the discharge valve actuator has failed and we are waiting for delivery. ————————————————————— • Worked With: Brent Ste-Croix, Christian Streef, Satnam Mann, Terry Cantwell • Attachments: 0
12347556 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12347556 | 1 | 2026-01-30 11:48 | 2026-01-30 11:47 | Barry Middleton (WW-CEAST) @ Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility - AUSSMP Date Work Completed: 2026-01-30 11:47 ————————————————————— Weather today Mostly Cloudy and -16 Celsius -On site to complete work order W11553698, W11599965. -Completed station check. -Entered station readings into SharePoint. -East Forcemain trial isolation is now back in service. -East and West Forcemainare now in timed auto duty rotation every 4 hours. -Pumps 2, 3, 4, 5, and 6 available in timed auto duty rotation every 3 hours. -Pump 1 out of service due to discharge valve issue. -Standby power generators available in auto. -Checked dry well, Ok. -All lines available in auto at the dump pad for the haulers. -Checked bar screens and Rotated bin. -Cleaned bar screen room of rags and bar screen oil full. ————————————————————— • Attachments: 0

## Leslie SPS
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS
12277197 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12277197 | 1 | 2026-01-02 12:27 | 2026-01-02 12:27 | Barry Middleton (WW-CEAST) @ Markham Leslie Pumping Station - LSSS Date Work Completed: 2026-01-02 12:27 ————————————————————— Weather today Partly Cloudy and -5 Celsius -On site to complete work orders W114690096, W11472957. -Completed station check. -Entered station readings into SharePoint. -Pumps 3, 2, 5, and 6 available in timed-auto duty rotation every 4 hours. -Pumps 1 and 4 out of service. -All standby power generators available in auto. -Switched sump pump duty. -Drained condensates from the surge tanks air compressors. -Checked dry well, ok. -Checked bar screens. Switched rag bin. Cleaned/hosed down bar screen room. -Bar Screen Bin Removal and Replacement - pushed rag bins back in after pick up by Miller Waste. -SCADA Review. ————————————————————— • Attachments: 0
12287366 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12287366 | 1 | 2026-01-06 23:37 | 2026-01-06 23:37 | Barry Middleton (WW-CEAST) @ Markham Leslie Pumping Station - LSSS Date Work Completed: 2026-01-06 23:37 ————————————————————— -On site responding to Generator #1 and #2 Warning alarms also generator #3 not in Auto alarm W11565200. -On arrival I tried to reset generator #3 but unable to reset or clear alarms. -I didn’t see any issues or alarms on generator #1 and #2 and also unable to clear alarms. -Notified ROC to call in the on call electrician Kyle Rae. -Test ran Generators but only generator #1 and #2 started generator #3 didn’t start. -Will leave station with the generators #1 and #2 available for tonight and finish troubleshooting tomorrow. -Pumps 3, 2, 5, and 6 available in timed-auto duty rotation every 4 hours. -Pumps 1 and 4 out of service -Cleared outstanding alarms but unable to clear outstanding alarms for generators. ————————————————————— • Attachments: 0
12291963 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12291963 | 3 | 2026-01-07 09:25 | 2026-01-07 09:22 | Daniel Kim (WW-CEAST) @ Markham Leslie Pumping Station - LSSS Date Work Completed: 2026-01-07 09:22 ————————————————————— On-site to complete Maximo w.os and to look into generator alarms from last night. Station check complete and the readings have been entered into the SharePoint. CMS/PCS investigated Generator alarms today. Found Generator 3 PGC needs to be replaced. CMS/PCS will schedule Thomson control to be on-site to further investigate this issue. Generator 1,2,3 warning alarms, Generator PGC/DCG not in auto alarms outstanding for the generators. Transfer test last night confirmed Generator 1 and 2 are available as an emergency power. If Generator 3 is needed in case of Powerfail, CMS electricians would need to be called out to manually start gen 3 and close G3 breaker switch Pushed out rag bins for pick up. Screen room roll-up door control still not working, PS aware of this issue. Cleaned screen room floor ————————————————————— • Attachments: 0
12296021 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12296021 | 5 | 2026-01-08 20:06 | 2026-01-08 20:03 | Chris Rodie (WW-CEAST) @ Markham Leslie Pumping Station - LSSS Date Work Completed: 2026-01-08 20:03 ————————————————————— -on site with PCS and electrical to fix generator 1 and 2 issues, after PCG controller is having an issue -generator 3 remains OOS -put pump 5 duty 1 auto, active, pump 6 duty 2 auto, off -pumps 1 OOS, pumps 2,3 manual off to test generators 1 and 2 -will be testing generator 1 and 2 with PCS electrical to get them back in service -all 3 generators are running, was able to get gen 3 working as well, half the facility is on generator power to test generator performance, pump 3 manual on -generators seem to be working properly after PCS/electrical work -tested all 3 generators on load, after PCG controller repair, ongoing issue seems to be resolved -electrical Dan Boate, PCS Artour Litvinov and Matt Spitzig on site -will put pumps 2,3,5,6 back to auto, and site back on utility power before leaving -notifying ROC ————————————————————— • Worked With: Artour Litvinov, Daniel Boate, Matt Spitzig • Attachments: 0
12296021 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12296021 | 5 | 2026-01-08 20:06 | 2026-01-08 20:03 | Chris Rodie (WW-CEAST) @ Markham Leslie Pumping Station - LSSS Date Work Completed: 2026-01-08 20:03 ————————————————————— -on site with PCS and electrical to fix generator 1 and 2 issues, after PCG controller is having an issue -generator 3 remains OOS -put pump 5 duty 1 auto, active, pump 6 duty 2 auto, off -pumps 1 OOS, pumps 2,3 manual off to test generators 1 and 2 -will be testing generator 1 and 2 with PCS electrical to get them back in service -all 3 generators are running, was able to get gen 3 working as well, half the facility is on generator power to test generator performance, pump 3 manual on -generators seem to be working properly after PCS/electrical work -tested all 3 generators on load, after PCG controller repair, ongoing issue seems to be resolved -electrical Dan Boate, PCS Artour Litvinov and Matt Spitzig on site -will put pumps 2,3,5,6 back to auto, and site back on utility power before leaving -notifying ROC ————————————————————— • Worked With: Artour Litvinov, Daniel Boate, Matt Spitzig • Attachments: 0
12299188 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12299188 | 1 | 2026-01-09 16:16 | 2026-01-09 16:15 | Kevin Shaji (WW-CEAST) @ Markham Leslie Pumping Station - LSSS Date Work Completed: 2026-01-09 16:15 ————————————————————— Station check completed, readings entered into SharePoint. Checked drywell. OK Pumps 3, 2, 5, and 6 available in timed-auto duty rotation every 4 hours. Pumps 1 and 4 out of service. All standby power generators available in auto. Drained condensates from the surge tanks air compressors. Checked screen room. changed out rag bin. Found plugged drain and mess under the screw press. Screen was missing in the screw press causing rags to just drop through the screw press drain. Created CMU W11576992 to install the missing screen. Daniel capped the drain temporarily. Cleaned the area after clearing the mess. Hoist inspection WO completed ————————————————————— • Attachments: 0
12303814 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12303814 | 1 | 2026-01-12 14:50 | 2026-01-12 14:50 | Kevin Shaji (WW-CEAST) @ Markham Leslie Pumping Station - LSSS Date Work Completed: 2026-01-12 14:50 ————————————————————— Station Check completed(See details on SharePoint). Checked drywell. OK Checked screen room, changed out rag bin. Cleaned/hose down screen room. Pumps 3, 5, and 6 available in timed-auto duty rotation every 4 hours. Pumps 1,2 and 4 out of service. All standby power generators available in auto. Drained condensates from the surge tanks air compressors. Cleaned board room and entrance area for city of Toronto meeting. Checked screen room. Replaced rag bins. Screen room overhead doors fixed by property services. ————————————————————— • Attachments: 0
12317986 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12317986 | 1 | 2026-01-16 13:15 | 2026-01-16 13:15 | Kevin Shaji (WW-CEAST) @ Markham Leslie Pumping Station - LSSS Date Work Completed: 2026-01-16 13:15 ————————————————————— Station Check completed(See details on SharePoint). Checked drywell. OK Checked screen room, changed out rag bin. Cleaned/hose down screen room. Pumps 3, 2, 5, and 6 available in timed-auto duty rotation every 4 hours. Pumps 1 and 4 out of service. All standby power generators available in auto. Drained condensates from the surge tanks air compressors. ————————————————————— • Attachments: 0

## Bogart SPS
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS
12303569 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12303569 | 1900-01-01 | 2026-01-12 08:54 | 2026-01-12 08:54 | Daniel Kim (WW-CEAST) @ Newmarket Bogart Creek Sewage Pumping Station - NMSSHS Date Work Completed: 2026-01-12 08:54 ————————————————————— Station check complete and the readings have been entered into the sharepoint Created CMU3 for INST to investigate oxygen lolo ————————————————————— • Attachments: 0

## Newmarket SPS
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS
12318572 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12318572 | 1899-12-31 | 2026-01-18 22:11 | 2026-01-18 22:04 | Ricardo Locatelli (INST) @ Newmarket Sewage Pumping Station & Equalization Tank - NMSSBP Date Work Completed: 2026-01-18 22:04 ————————————————————— Onsite for CMU5. Screen room frozen, water pipe burst and sprayed water on surge tank LITs. LITs not responding Accompanied OIC into screen room. Used some heat to defrost LIT impulse lines. Flushed impulse lines. LITs reading back to normal. Cleared associated alarms. Removed surge tanks from maintenance mode. Placed RSP’s duties back to auto. Monitored for a short time. All ok Informed ROC and left site This is the second year in a row that this issue has occurred. System should be reviewed ————————————————————— • Attachments: 0 | 1
12343000 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12343000 | 1900-01-01 | 2026-01-28 08:04 | 2026-01-28 08:01 | David Dougherty (WW-MAINT) @ Newmarket Sewage Pumping Station & Equalization Tank - NMSSBP Date Work Completed: 2026-01-28 08:01 ————————————————————— On site to check pump 1 RTD fault. Found RTD 6 for motor windings failed high. Turned off fault for RTD 6 on multilin relay. Fault has been reset, test ran pump 1 with the help of operations, pump ran without fault. Pump 1 is to be left off but is available to run if needed in an emergency. After checking all the wiring connections, RTD 6 reading returned to normal. Enabled RTD 6 faults on multilin. Asked operations to put pump1 back in auto duty for testing. If RTD 6 fault happens again we will come back and disable fault and leave pump 1 in off and for emergency use only. ————————————————————— • Attachments: 0
12343007 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12343007 | 1900-01-02 | 2026-01-28 08:27 | 2026-01-28 08:26 | Marcos Tungcol (WW-CEAST) @ Newmarket Sewage Pumping Station & Equalization Tank - NMSSBP Date Work Completed: 2026-01-28 08:26 ————————————————————— On site completed work orders. Station Check (See entries on SharePoint). Put pump 1 back in service after CMS troubleshoot the problem. Currently, pump 1 is running in auto as duty 1, with a flow of 253.1 L/s at 32% auto speed minimum setpoint and at 149 kPa. All pumps now are available in timed-auto duty rotation every 3 hours. Standby power generator available in auto. Checked dry well, ok. Checked bar screens. Levelled rags from the bin. Switched rag bin. Cleaned screen room of rags. Bar Screen Bin Removal and Replacement - rag bins pushed out for pick up by Miller Waste tomorrow. Air Compressors Cleaning and Inspection HVAC BAS System General Alarm still outstanding. Station operations normal, as intended. ————————————————————— • Attachments: 0

## Mt. Albert WRRF
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS
12277234 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12277234 | 1899-12-31 | 2026-01-02 13:55 | 2026-01-02 13:54 | Daniel Kim (WW-CEAST) @ Mount Albert Water Resource Recovery Facility - MTSP Date Work Completed: 2026-01-02 13:54 ————————————————————— Lab and station check complete. All the readings have been entered into the sharepoint. Batch wasted 20m3 in total. Dosed 4 bags of soda ash into the aeration tank. Created CMU3 for headworks O2 sensor as it is currently reading around 9% ————————————————————— • Attachments: 0
12284024 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12284024 | 1899-12-31 | 2026-01-05 14:39 | 2026-01-05 14:39 | Eric Simanovskis (INST) @ Mount Albert Water Resource Recovery Facility - MTSP Date Work Completed: 2026-01-05 14:39 ————————————————————— Attending site to check oxygen sensor (W11555069). Sensor has failed. Replaced failed sensor and calibrated, ROC was notified after sensor was replaced and SCADA alarms were cleared. ————————————————————— • Attachments: 0
12292140 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12292140 | 1900-01-03 | 2026-01-07 11:16 | 2026-01-07 11:16 | Philip Romito (WW-CEAST) @ Mount Albert Water Resource Recovery Facility - MTSP Date Work Completed: 2026-01-07 11:16 ————————————————————— -On site to complete work orders. -Station check completed, readings entered into SharePoint. -Verified alum dosing and sand filter operation. -Air compressors 1-2 cleaning and inspection completed. -Consolidated headworks inspection completed. -Greased travelling screen and cleaned out back compartment . -Screw press inspection completed. -Grit screw press inspection completed and unit greased. -Vortex 1-2 inspections completed. -Black and McDonald on site for electrical investigation regarding OCU motor. OCU remains OOS. ————————————————————— • Worked With: Terry Reed • Attachments: 0
12299054 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12299054 | 1899-12-31 | 2026-01-09 13:25 | 2026-01-09 13:17 | Satnam Mann (WW-MAINT) @ Mount Albert Water Resource Recovery Facility - MTSP Date Work Completed: 2026-01-09 13:17 ————————————————————— Onsite to review why effluent pump #1 is the only pump working Upon inspection found pump alternator relay faulty Parts no longer available waiting for new replacement parts ————————————————————— • Attachments: 0
12328769 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12328769 | 1900-01-02 | 2026-01-21 11:27 | 2026-01-21 11:27 | Philip Romito (WW-CEAST) @ Mount Albert Water Resource Recovery Facility - MTSP Date Work Completed: 2026-01-21 11:27 ————————————————————— -On site to complete work orders. -RAS inlet chamber and post aeration alum chambers cleaned out. -Station check completed, readings entered into SharePoint. -Verified alum dosing and sand filter operation. -OCU OOS. -Compressor 1 Motor Overload Alarm came in this afternoon, found drain line on air compressor 2 tank continually blowing out air. Isolated drain line with ball valve on line. Unable to reset motor overload alarm on compressor 1 despite attempt to reset on panel and cycle power at breaker. Work request created for maintenance team. Compressor 1 currently OOS, Compressor 2 running in auto. ————————————————————— • Worked With: Terry Reed • Attachments: 0
12331379 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12331379 | 1899-12-31 | 2026-01-22 15:19 | 2026-01-22 08:31 | Philip Romito (WW-CEAST) @ Mount Albert Water Resource Recovery Facility - MTSP Date Work Completed: 2026-01-22 08:31 ————————————————————— -On site to perform a station check and to assist CPD/contractors with air compressor repairs. -Readings entered into SharePoint. -Verified alum dosing and sand filter operation. -Contractors able to make repairs to both air compressors 1 and 2, both air compressors back in auto duty rotation. -OCU remains OOS. ————————————————————— • Worked With: Terry Reed • Attachments: 0
12337971 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12337971 | 1899-12-31 | 2026-01-26 12:15 | 2026-01-26 08:35 | Philip Romito (WW-CEAST) @ Mount Albert Water Resource Recovery Facility - MTSP Date Work Completed: 2026-01-26 08:35 ————————————————————— -On site to complete work orders. -Grit bin out for pickup tomorrow. -Shoveled and salted stairs and walkways. -Station check completed, readings entered into SharePoint. -Verified alum dosing and sand filter operation. -OCU remains OOS. -Air compressor drain lines manually closed until drain line solenoids can be repaired. ————————————————————— • Worked With: Terry Reed • Attachments: 0
12347587 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12347587 | 1899-12-31 | 2026-01-30 13:00 | 2026-01-30 08:10 | Philip Romito (WW-CEAST) @ Mount Albert Water Resource Recovery Facility - MTSP Date Work Completed: 2026-01-30 08:10 ————————————————————— -Station check completed, readings entered into SharePoint. -Verified alum dosing and sand filter operation. -Added two bags of soda ash to each aeration tank. -Worked on cleaning up process building. -OCU remains OOS. ————————————————————— • Worked With: Terry Reed • Attachments: 0

## King City SPS
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS

## Black Creek SPS
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS
12287106 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12287106 | 2 | 2026-01-06 13:16 | 2026-01-06 13:16 | Young Jung (WW-WEST) @ Vaughan Black Creek Pumping Station - BLSS Date Work Completed: 2026-01-06 13:16 ————————————————————— - Levelled and pushed bin out for pick up. Cleaned up the general area - Performed JHSC inspection. No issues - Performed station check and recorded readings on SharePoint. No new issues. - Contractor onsite for the semi annual diesel generator testing. Notified ROC of the work being performed - Performed monthly generator testing. Inspected the generators and fuel level. Started the generator at 9:58. Recorded readings on SharePoint after 30 minutes, no issues. Ran for approximately one hour. Runtime for generator 1 from 477.9 hrs to 479.0 hrs - Started generator 2 at 11:07. Recorded readings after 30 minutes. Run time for generator 2 from 490.6 hrs to 491.6 hrs. No issues with readings. - Fuel level readings before: 97 cm (6173 L). After gen test 95 cm (6053 L) - Reset alarms caused by generator test. - Checked for hazardous waste. None found - Inspected the odour control unit. No issues. Filters below 2.5 inch and does not need cleaning - Inspected the hoist system. No issues Update: pump 4 check valve not closing. Will monitor and create a work order ————————————————————— • Attachments: 0 | 1
12299105 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12299105 | 2 | 2026-01-09 14:19 | 2026-01-09 14:15 | Lauren Swanson (WW-WEST) @ Vaughan Black Creek Pumping Station - BLSS Date Work Completed: 2026-01-09 14:15 ————————————————————— Onsite for station check and pump run tests Station check completed reviewed trends and added data into SharePoint. Empty bin pushed back in, bar screen ok. Pump1 582.5 at 299kpa Pump 2 460.8 at 264kpa at 100% Pump 3 136.7L/s at 215kpa at 100% Pump4 444.2 at 268kpa at 100% Pump 5 tripped on overcurrent causing pump 5 uncommanded stop alarm, pump 5 multiplying trip ALRM and pump 5 disc valve uncommanded close alarm. Upon checking pump 5 in B4 there’s seem to be a leak in the pump. Unsure if this is related to the pump not running. Team lead informed and WO created Left pump 5 in manual off and OOS ————————————————————— • Attachments: 0 | 1
12303661 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12303661 | 1 | 2026-01-12 11:30 | 2026-01-12 11:24 | Lauren Swanson (WW-WEST) @ Vaughan Black Creek Pumping Station - BLSS Date Work Completed: 2026-01-12 11:24 ————————————————————— Called ROC to inform of work being done Completed dry well inspection. Inspected check valves. Tested dry well flood alarm and checked sump pit operation. Tested dialer alarm - alarm received by ROC. Tested hi/lo temp alarm. Inspected RS pumps and ran pumps in manual Pump 1 - 581.9L/s at 290KPa Pump 2 - 469L/s at 262kpa at 100% Pump 3 - 126.4L/s at 212kpa at 100% Pump 4 - 453.5L/s at 207kpa at 100% Pump 5 - OOS Actuated suction valves and inspected RS valves. Flushed and inspected air relief valves Completed wet well inspection Cleaned and lubricated the bar screen ————————————————————— • Attachments: 0 | 1
12317962 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12317962 | 1 | 2026-01-16 12:37 | 2026-01-16 12:35 | Lauren Swanson (WW-WEST) @ Vaughan Black Creek Pumping Station - BLSS Date Work Completed: 2026-01-16 12:35 ————————————————————— Onsite for station check and weekly pump run test. Station check complete - no new issues. Reviewed trends and entered data into SharePoint. Ran pump test: Pump1 - 583.9L/s at285kpa Pump 2 - 465.5L/s at 260kpa at 100% Pump 3 130.2L/s at 214kpa at 100% Pump4 - 460.8L/s at 269kpa at 100% Pump 5 -OOS ————————————————————— • Attachments: 0 | 1
12325280 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12325280 | 1 | 2026-01-20 10:47 | 2026-01-20 10:46 | Young Jung (WW-WEST) @ Vaughan Black Creek Pumping Station - BLSS Date Work Completed: 2026-01-20 10:46 ————————————————————— - Checked station and trends. Recorded readings on SharePoint. No new issues - Created work order for screen room oxygen Lolo alarm. ————————————————————— • Attachments: 0 | 1
12333757 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12333757 | 1 | 2026-01-23 13:16 | 2026-01-23 13:16 | Young Jung (WW-WEST) @ Vaughan Black Creek Pumping Station - BLSS Date Work Completed: 2026-01-23 13:16 ————————————————————— - Raked bin and cleaned area. Pushed bin back in - Checked screen, oil is good - Performed weekly pump test. Ran each pumps 1-4 manually, one at a time, and recorded readings. Check valve for pump 3 not closing. Work order already created. Pump 5 OOS Pump 1: 581 L/s, pressure 289 kPa Pump 2: 453.4 L/s at 100%, pressure 262 kPa Pump 3: 133.4 L/s at 100% speed, pressure 215 kPa Pump 4: 467 L/s at 100% speed, pressure 273 kPa - Checked station and recorded readings on SharePoint. No new issues found ————————————————————— • Attachments: 0 | 1
12339999 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12339999 | 1899-12-31 | 2026-01-27 14:11 | 2026-01-27 14:10 | Young Jung (WW-WEST) @ Vaughan Black Creek Pumping Station - BLSS Date Work Completed: 2026-01-27 14:10 ————————————————————— - Checked screen, oil is good - Performed weekly pump test. Ran each pumps 1-4 manually, one at a time, and recorded readings. Check valve for pump 3 not closing. Work order already created. Pump 5 OOS Pump 1: 589 L/s, pressure 294 kPa Pump 2: 471 L/s at 100%, pressure 268 kPa Pump 3: 131.7 L/s at 100% speed, pressure 214 kPa Pump 4: 462.7 L/s at 100% speed, pressure 277 kPa - Checked station and recorded readings on SharePoint. Found leak coming through the clean out of the sanitary drain line on B5. Seems the screw is loose or the the line is plugged. Ladder is not tall enough and cannot reach the ceiling safely to remedy the issue. Notified TL ————————————————————— • Attachments: 0 | 1899-12-31

## Nobleton WRRF
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS

## Schomberg WRRF
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS
12339948 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12339948 | 1 | 2026-01-27 13:11 | 2026-01-27 12:44 | Eric Simanovskis (INST) @ Schomberg Water Resource Recovery Facility - SHSP Date Work Completed: 2026-01-27 12:44 ————————————————————— Attending site to replace Alum Pumps 6 & 7 flowmeter (W11523891). While setting up the replacement flowmeter, I noticed that the low-flow cutoff was set to 20mL/minute on the existing flowmeter. I have now changed the low-flow cutoff to 5mL/minute in the existing flowmeter to see if this corrects the issue. Also, replaced Screen Room Oxygen sensor (W11526277). ROC was notified before and after maintenance activities. ————————————————————— • Attachments: 0 | 1
12317998 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12317998 | 3 | 2026-01-16 13:29 | 2026-01-16 13:29 | Lance Johnson (LEADS) @ Schomberg Water Resource Recovery Facility - SHSP Date Work Completed: 2026-01-16 13:29 ————————————————————— Supernated STT and released to SHT. Completed labs and entered data in ACE sheets. Completed station check. No issues found. Cleaned TSS probe. Created work order for effluent pump 3 that faulted yesterday. ————————————————————— • Attachments: 0 | 1
12295849 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12295849 | 4 | 2026-01-08 13:26 | 2026-01-08 13:25 | Lance Johnson (LEADS) @ Schomberg Water Resource Recovery Facility - SHSP Date Work Completed: 2026-01-08 13:25 ————————————————————— Completed labs and entered data in ace sheets. Completed station check. No issues found. Inspected aeration blowers. Blower 1 leaked oil out of the drive side. Wiped up oil. Topped up oil. Created a work order (W11573836). Inspected sludge blowers. No issues. Inspected vortex blowers. No issues. Cleaned and inspected new air compressors. No new issues found. Replaced sludge blower room supply fan filter. ————————————————————— • Attachments: 0 | 1
12292293 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12292293 | 1 | 2026-01-07 14:59 | 2026-01-07 14:58 | Lance Johnson (LEADS) @ Schomberg Water Resource Recovery Facility - SHSP Date Work Completed: 2026-01-07 14:58 ————————————————————— Completed labs and entered numbers in ACE sheets. Created work order for Sludge Blower 2 fan overload alarm (W11570169) Completed D.O. probe maintenance. ————————————————————— • Attachments: 0 | 1

## Kleinburg WRRF
12347943 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12347943 | 1 | 2026-01-31 10:51 | 2026-01-27 15:30 | Young Jung (WW-WEST) @ Kleinburg Water Resource Recovery Facility - KBSPF Date Work Completed: 2026-01-27 15:30 ————————————————————— There's a gap in the effluent flow trend on January 27 from 8:42 until 20:32. Gap likely due to faulty effluent flow transmitter. Created work order to instrumentation and notified PCS on call about the gap on January 31, 2026 at 10:30. Also notified TL ————————————————————— • Attachments: 0 • [REMOTE ENTRY]

## Pine Valley
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS
WW-WEST | Vaughan Pine Valley Pumping Station | 2026-01-06 | Onsite for station check - reviewed trends and added data into SharePoint. H2S out of range alarm present on arrival - alarm would not clear. Created work order W11565040. No new issues otherwise. | 1 | 1 | 1

## Humber SPS
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS

## Holland Landing SPS
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS

## Joe Dales SPS
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS | 1

## Keswick SPS
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS | 1
12344995 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12344995 | 1899-12-31 | 2026-01-29 14:49 | 2026-01-29 14:48 | Tyson Cornish (WW-NORTH) @ Keswick Sewage Pumping Station - KSSSQW Date Work Completed: 2026-01-29 14:48 ————————————————————— Performed facility station check Data in sharepoint Completed monthly PM work orders -Hoist system inspection -Consolidated dry well inspection Sump pump 2 not working Auto dialer test not working Flow rates @ Pump speed 100% (WWL = 2.31 m) P1 = 204 L/s P2 = 216 L/s P3 = 207 L/s P4 = 210 L/s Equipment OOS: Odour control system and sump pump 2 ————————————————————— • Attachments: 0

## Keswick WRRF
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS
12277233 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12277233 | 1 | 2026-01-02 13:56 | 2026-01-02 13:50 | Ricardo Locatelli (INST) @ Keswick Water Resource Recovery Facility - KSSP Date Work Completed: 2026-01-02 13:50 ————————————————————— Onsite for annual calibrations Informed ROC and operations Operations placed train 1 to OFF for me Performed maintenance on NIT and calibrated Calibrated FIT and PIT. PIT reconfigured to show PV in kPa Calibrated UVD FIT 1 and 2 as well as CIP FIT PEFF_FIT1 has electronic issues. Will create follow up w/o. Informed operations Cleared associated alarms Informed operation and ROC Left site ————————————————————— • Attachments: 0
12278976 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12278976 | 3 | 2026-01-04 07:06 | 2026-01-04 09:54 | Neil Ott (WW-NORTH) @ Keswick Water Resource Recovery Facility - KSSP Date Work Completed: 2026-01-04 09:54 ————————————————————— Attended for sludge handling Decanted/transferred sludge thickening tanks Switched WAS feed to sludge thickening tank 2 Checked bar screen and raked bin Ran train 3 for a cycle and membrane blower 2 faulted during backwash, returned train status to off and notified ROC Switched active NaOH pump to p.2 (pump on the right) and returned pH setpoints to 6.0 and 6.5 (medium and fine injection). ————————————————————— • Attachments: 0
12334185 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12334185 | 1 | 2026-01-25 08:03 | 2026-01-25 08:01 | Chris Colangelo (WW-NORTH) @ Keswick Water Resource Recovery Facility - KSSP Date Work Completed: 2026-01-25 08:01 ————————————————————— Onsite for sludge handling Receive call at 07:10hrs regarding train 2 shutdown and membrane blower 2 shutdown on lolo airflow. Reset train alarms - check trends and prime train 2 Monitor backwash sequence with no issues. Train 2 and membrane blower 2 back in service ————————————————————— • Attachments: 0
12343308 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12343308 | 1 | 2026-01-28 14:11 | 2026-01-28 13:59 | Darren Boddy (WW-NORTH) @ Keswick Water Resource Recovery Facility - KSSP Date Work Completed: 2026-01-28 13:59 ————————————————————— on site at 0700hrs sludge handling. WAS now feeding STT2 station check lab and readings weekly samples collected and delivered to Harry Walker Headworks screen room cleaned Tss probe maintenance Investigated chemical room for CIP neutralization not working properly due to freezing in room. Heaters added with extension chords running in room. Property services looking into it. Uv rotation alum board exercised. ————————————————————— • Attachments: 0
12347451 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12347451 | 1 | 2026-01-30 10:27 | 2026-01-30 10:21 | Bill Van Bakel (WW-MAINT) @ Keswick Water Resource Recovery Facility - KSSP Date Work Completed: 2026-01-30 10:21 ————————————————————— On site to look at permeate valve leaking air. Operated the valve and found no issues. Also changed the actuators on train 4-5 air scour lines. Line 1 has a small leak but we need to order a replacement ————————————————————— • Worked With: Terry Cantwell • Attachments: 0

## Queensville SPS
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS
12312094 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12312094 | 1 | 2026-01-14 13:54 | 2026-01-14 13:47 | Tyson Cornish (WW-NORTH) @ Queensville West Sewage Pumping Station - QVSSSC Date Work Completed: 2026-01-14 13:47 ————————————————————— Continued work removing channel grinder. Discovered motor coupler rubber insert broken. Will return to continue at a later date ————————————————————— • Attachments: 0
12315580 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12315580 | 1 | 2026-01-15 13:16 | 2026-01-15 13:13 | Michael Balmer (WW-NORTH) @ Queensville West Sewage Pumping Station - QVSSSC Date Work Completed: 2026-01-15 13:13 ————————————————————— Completed assigned EZMax work orders: - Actuator exercise - Diesel containment inspection Also assisted maintenance with grinder inspection / replacement - isolated inlet channel valve before grinder. Flow is being fed to wet wells through bar screens. ————————————————————— • Attachments: 0

## Sutton WRRF
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS | 1
12312058 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12312058 | 1 | 2026-01-14 12:32 | 2026-01-14 12:30 | Terry Cantwell (WW-MAINT) @ Sutton Water Resource Recovery Facility - SUSP Date Work Completed: 2026-01-14 12:30 ————————————————————— Remove and replace flow meter. Electricians require additional parts to complete wiring. ————————————————————— • Worked With: Bill Van Bakel, Satnam Mann • Attachments: 0
12167801 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12167801 | 6 | 2025-11-14 09:38 | 2025-11-14 09:36 | Chris Colangelo (WW-NORTH) @ Sutton Water Resource Recovery Facility - SUSP Date Work Completed: 2025-11-14 09:36 ————————————————————— Onsite for daily operations Review scada/trends No decant - stt ready for gfl load Check station Filters ok Electrical onsite to replace UV UPS batteries. 0938hrs turn off filter feed pumps 0941hrs verify UV effluent flow meter reads 0L/s CPD onsite to to investigate pressure switches on compressors 10:11hrs place filter feed pumps back in auto Clear UV alarms Collect in house lab samples Increase wasting on SBR1 from 240s to 300s Increase wasting on SBR2 from 240s to 360s ————————————————————— • Attachments: 0
12202020 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12202020 | 1 | 2025-12-01 13:44 | 2025-12-01 13:44 | Neil Ott (WW-NORTH) @ Sutton Water Resource Recovery Facility - SUSP Date Work Completed: 2025-12-01 13:44 ————————————————————— Attended for daily operations Performed station check Completed lab and entered readings into ACE sheet Decanted sludge thickening tank and initiated transfer while hauler took load Hosed bar screen and surrounding area Received fault alarm on lagoon flowmeter - notified instrumentation of issue and disconnected power to unit so it will not read flow Checked into flow readings on SBR diversion EQ line - removed snow from the flume and the reading returned to 0 L/s Checked sand filters. ————————————————————— • Attachments: 0