## Aurora SPS
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS
12261334 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12261334 | 3 | 2025-12-24 08:46 | 2025-12-24 08:45 | Marcos Tungcol (WW-CEAST) @ Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility - AUSSMP Date Work Completed: 2025-12-24 08:45 ————————————————————— On site completed work orders. Station Check (See details on SharePoint) Pumps 2, 4, 5 and 6 available in timed auto duty rotation every 3 hours. Pump 3, which is in manual/duty 7, out of service due to discharge flow fault. Pump 1, which is in manual/duty 7, out of service due to leakage alarm. Standby power generators available in auto. All lines available in auto at the dump pad for the haulers. Dewatered EQ Tanks from 11 m3 to 5 m3. Cleared/reset dehumidifier alarm. Air Compressors Inspection and Cleaning Screen Bin Removal and Replacement - completed by Daniel Kim. Levelled rags. Switched bin. Pushed out rag bins to be pick up by Miller Waste. ————————————————————— • Attachments: 0
12273824 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12273824 | 1 | 2025-12-31 15:00 | 2025-12-31 14:59 | Barry Middleton (WW-CEAST) @ Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility - AUSSMP Date Work Completed: 2025-12-31 14:59 ————————————————————— Weather today Overcast and -4 Celsius -On site to complete work orders W11482489, W11481886, W11472947. -Completed station check. -Entered station readings into SharePoint. -Pumps 2, 4, 5 and 6 available in timed auto duty rotation every 3 hours. -Pump 3, which is in manual/duty 7, out of service due to discharge flow fault. -Pump 1 is in manual/duty 7. -Standby power generators available in auto. -Checked dry well, Ok. -All lines available in auto at the dump pad for the haulers. -Checked bar screens. Rotated bin. Cleaned bar screen room of rags. -Two rag bins pushed outside last week not pick up by Miller Waste. -SCADA Review. ————————————————————— • Attachments: 0
12226975 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12226975 | 1 | 2025-12-10 10:40 | 2025-12-10 10:38 | Bill Van Bakel (WW-MAINT) @ Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility - AUSSMP Date Work Completed: 2025-12-10 10:38 ————————————————————— On site for PIT leak on pump 5. Replaced a 3/4 nipple ————————————————————— • Attachments: 0
12233553 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12233553 | 1900-01-02 | 2025-12-12 12:27 | 2025-12-12 12:27 | Marcos Tungcol (WW-CEAST) @ Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility - AUSSMP Date Work Completed: 2025-12-12 12:27 ————————————————————— On site for Station Check (See details on SharePoint) All pumps available in timed auto duty rotation every 3 hours, except, pump 3, which is in manual/duty 7, out of service, discharge flow fault. Currently, 3 duty pumps are running with a flows of 1109 L/s. Standby power generators available in auto. Checked dry well, ok. Checked bar screens. Levelled rags from the rag bin. Cleaned bar screen room. Removed rags/dirt from the conveyor motor box. Pushed rag bins back inside the screen room after picked up by Miller Waste yesterday. All lines available at the dump pad for haulers to use. Checked Unit Heaters 3 and 4 inside the bar screen room. Verified and confirmed, they are not working. Power is ON but no heat coming out. There is LOTO tag in the MCC, which says, “motor thermal overload tripped.” Informed Acting Team Lead (Philip R.). ————————————————————— • Attachments: 0
12237938 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12237938 | 8 | 2025-12-15 10:17 | 2025-12-15 10:16 | Marcos Tungcol (WW-CEAST) @ Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility - AUSSMP Date Work Completed: 2025-12-15 10:16 ————————————————————— On site completed work orders. Station Check (See details on SharePoint) All pumps available in timed auto duty rotation every 3 hours, except, pump 3, which is in manual/duty 7, out of service, discharge flow fault. Standby power generators available in auto. Checked dry well, ok. Checked bar screens. Levelled rags from the rag bin. Cleaned bar screen room. Removed rags/dirt from the conveyor motor box. All lines available at the dump pad for haulers to use. Consolidated Monthly Dry Well Pump Floor Inspection 1 - Auto Dialer Alarm Test - received by ROC. 2 - High Low Temperature Alarm Test - received by ROC. 3 - Dry Well Flood Alarm Test - received by ROC. 4 - Sump Pit Inspection 5 - RS Pump and Motor Inspection Pump 1 (VFD) - @ 0% speed, 315 L/s, 770 kPa, 357 A, 517 V, 54 Hz, 1077 Rpm; 40% speed, 380 L/s, 786 kPa, 459 A, 536 V, 55 Hz, 1116 Rpm Pump 2 (VFD) - @ 0% speed, 290 L/s, 766 kPa, 364 A, 517 V, 54 Hz, 1077 Rpm; 40% speed, 390 L/s, 773 kPa, 443 A, 536 V, 56 Hz, 1116 Rpm Pump 3 (Constant) - Out of service Pump 4 (Constant) - 474 L/s, 757 kPa, 450 A, 598 V, 60 Hz Pump 5 (VFD) - @ 0% speed, 316 L/s, 765 kPa, 375 A, 517 V, 54 Hz, 1077 Rpm; 40% speed, 388 L/s, 782 kPa, 463 A, 536 V, 55 Hz, 1115 Rpm Pump 6 (VFD) - @ 0% speed, 288 L/s, 771 kPa, 364 A, 517 V, 54 Hz, 1077 Rpm; 40% speed, 380 L/s, 771 kPa, 459 A, 536 V, 55 Hz, 1115 Rpm 6 - Check Valves Inspection 7 - Air Compressors Inspection Cleared/reset all alarms Station back to normal operations. ————————————————————— • Attachments: 0
12245992 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12245992 | 1 | 2025-12-17 13:04 | 2025-12-17 13:01 | Marcos Tungcol (WW-CEAST) @ Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility - AUSSMP Date Work Completed: 2025-12-17 13:01 ————————————————————— On site completed work orders. Station Check (See details on SharePoint) All pumps available in timed auto duty rotation every 3 hours, except, pump 3, which is in manual/duty 7, out of service, discharge flow fault. Standby power generators available in auto. Checked dry well, ok. Checked bar screens. Levelled rags from the rag bin. Cleaned/hosed down bar screen room. Removed rags/dirt from the conveyor motor box. Flushed screw press drain. Added oil to the reservoir tank of screen 1. All lines available at the dump pad for haulers to use. Air Compressors Inspection and Cleaning. ————————————————————— • Attachments: 0
12250881 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12250881 | 4 | 2025-12-19 09:49 | 2025-12-19 09:49 | Marcos Tungcol (WW-CEAST) @ Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility - AUSSMP Date Work Completed: 2025-12-19 09:49 ————————————————————— On site for Station Check (See details on SharePoint) All pumps available in timed auto duty rotation every 3 hours, except, pump 3, which is in manual/duty 7, out of service, discharge flow fault. Standby power generators available in auto. Checked dry well, ok. Checked bar screens. Levelled rags from the rag bin. Switched rag bin. Cleaned bar screen room. Lines 1 and 2 available in auto at the dump pad for haulers to use. Line 3 interlocked due to overtorque. Unclogged line 3. Cleared/reset alarm. Line 3 is now available in auto. ————————————————————— • Attachments: 0
12251242 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12251242 | 1 | 2025-12-20 12:17 | 2025-12-20 12:16 | Chris Rodie (WW-CEAST) @ Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility - AUSSMP Date Work Completed: 2025-12-20 12:16 ————————————————————— -investigated pump 1 leakage alarm and mv2 actuator fault alarm -actuator display is blank, and not displaying status, needs to be looked at by electrical -pump 1 leakage alarm is outstanding, WO created for maintenance ————————————————————— • Attachments: 0
12255133 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12255133 | 4 | 2025-12-22 12:02 | 2025-12-22 12:02 | Marcos Tungcol (WW-CEAST) @ Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility - AUSSMP Date Work Completed: 2025-12-22 12:02 ————————————————————— On site completed work orders. Station Check (See details on SharePoint) Pumps 2, 4, 5 and 6 available in timed auto duty rotation every 3 hours. Pump 3, which is in manual/duty 7, out of service due to discharge flow fault. Pump 1, which is in manual/duty 7, out of service due to leakage alarm. Standby power generators available in auto. Checked dry well, ok. Checked bar screens. Levelled rags from the rag bin. Cleaned bar screen room. Flushed screw press drain. Removed rags/dirt from inside the conveyor motor box. All lines available in auto at the dump pad for haulers. EQ Tanks Odour Control Scrubber System Inspection ————————————————————— • Attachments: 0
12261401 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12261401 | 1 | 2025-12-24 11:03 | 2025-12-24 11:02 | Christian Streef (WW-MAINT) @ Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility - AUSSMP Date Work Completed: 2025-12-24 11:02 ————————————————————— On site to drain leakage chamber on pump #1. Filled with glycol. Pump drained approx 10L. Filled about 8L. ————————————————————— • Worked With: Martin deVries • Attachments: 0

## Leslie SPS
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS
12201962 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12201962 | 1900-01-03 | 2025-12-01 11:41 | 2025-12-01 11:41 | Barry Middleton (WW-CEAST) @ Markham Leslie Pumping Station - LSSS Date Work Completed: 2025-12-01 11:41 ————————————————————— Weather today Clear and -11 Celsius -On site to complete work orders W11409947, W11411376, W11411443. -Completed station check. -Entered station readings into SharePoint. -Two-Way Radio Functional test. -Pumps 2, 3, 5 and 6 available in timed-auto duty rotation every 4 hours. -Pump 1 out of service for repair and taken out of site. -Pump 4 out of service for repair. -All standby power generators available in auto. -Drained condensates from the surge tanks air compressors. -Checked dry well, ok. -Checked bar screens. Switched rag bin. Cleaned/hosed down bar screen room. ————————————————————— • Attachments: 0
12213481 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12213481 | 1899-12-31 | 2025-12-05 09:21 | 2025-12-05 09:21 | Barry Middleton (WW-CEAST) @ Markham Leslie Pumping Station - LSSS Date Work Completed: 2025-12-05 09:21 ————————————————————— Weather today Overcast and -7 Celsius -On site to complete work order W11426317. -Completed station check. -Entered station readings into SharePoint. -Pumps 2, 3, 5 and 6 available in timed-auto duty rotation every 4 hours. -Pump 1 out of service for repair and taken out of site. -Pump 4 out of service for repair. -All standby power generators available in auto. -Switched sump pump duty. -Drained condensates from the surge tanks air compressors. -Checked dry well, ok. -Checked bar screens. Switched rag bin. Cleaned/hosed down bar screen room. -Bar Screen Bin Removal and Replacement - pushed rag bins back in the screen room after pick up by Miller Waste. ————————————————————— • Attachments: 0
12219326 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12219326 | 1900-01-02 | 2025-12-08 13:23 | 2025-12-08 13:22 | Barry Middleton (WW-CEAST) @ Markham Leslie Pumping Station - LSSS Date Work Completed: 2025-12-08 13:22 ————————————————————— Weather today Clear and -6 Celsius -On site to complete work order W11431335, W11430091, W11428909, W11431682, W11428992, W11497362. -Completed station check. -Entered station readings into SharePoint. -Hoist Inspection. -Surge tank inspection. -Odour control scrubber system inspection. -Pumps 2, 3, 5 and 6 available in timed-auto duty rotation every 4 hours. -Pump 1 out of service for repair and taken out of site. -Pump 4 out of service for repair. -Tested standby power generator #1 Failed to start alarm from previous generator test run. -Tested standby power generator #1 at 10:20 am and also at 1:00 pm with centralized maintenance electrical. -All standby power generators available in auto. -Switched sump pump duty. -Drained condensates from the surge tanks air compressors. -Checked dry well, ok. -Checked bar screens. Switched rag bin. Cleaned/hosed down bar screen room. ————————————————————— • Worked With: Kevin Shaji • Attachments: 0
12227059 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12227059 | 2 | 2025-12-10 13:01 | 2025-12-10 13:01 | Barry Middleton (WW-CEAST) @ Markham Leslie Pumping Station - LSSS Date Work Completed: 2025-12-10 13:01 ————————————————————— Weather today Rain and snow mixed and 2 Celsius -On site to complete work orders W11431335, W11437556, W11437764, W11439401. -Completed station check. -Entered station readings into SharePoint. - Check valve inspection - Dry well flood alarm test - Sump pit inspection - RS pump & motor inspection - BAS check - Seal Water Strainer - Air Compressor Inspection -RS Pumps and Motors Inspection. -Pumps 1 and 4 out of service for repair. -Pump 2 @ 0% speed: 1008 L/s, 470 kPa, 48 Hz, 125 A, 581 RPM, 435 Kw / @ 100% speed: 1824 L/s, 437 kPa, 60 Hz, 173 A, 716 RPM, 894 Kw. -Pump 3 Constant Speed: 1259 L/s. -Pump 5 @ 0% speed: 870.7 L/s, 415 kPa, 49Hz, 125 A, 581 RPM, 423 Kw / @ 100% speed: 1719 L/s, 441 kPa, 60 Hz, 176 A, 716 RPM, 909 Kw. -Pump 6 Constant Speed: 1152 L/s. -Pumps 2, 3, 5 and 6 available in timed-auto duty rotation every 4 hours. -Pump 1 and 4 out of service for repair. -All standby power generators available in auto. -Drained condensates from the surge tanks air compressors. -Checked dry well, ok. -Checked bar screens. Switched rag bin. Cleaned/hosed down bar screen room. -Bar Screen Bin Removal and Replacement - pushed rag bins outside the screen room for pick up by Miller Waste tomorrow. ————————————————————— • Attachments: 0
12233634 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12233634 | 1899-12-31 | 2025-12-12 15:23 | 2025-12-12 15:23 | Barry Middleton (WW-CEAST) @ Markham Leslie Pumping Station - LSSS Date Work Completed: 2025-12-12 15:23 ————————————————————— Weather today Clear and -4 Celsius -On site to complete work orders W11431335, W11437764, W11444677, W11465031. -Completed station check. -Entered station readings into SharePoint. -Investigated bar screen #2 fault alarm. -Comprehensive Housekeeping. -Pumps 2, 3, 5 and 6 available in timed-auto duty rotation every 4 hours. -Pump 1 out of service for repair and taken off site. -Pump 4 out of service for repair. -All standby power generators available in auto. -Switched sump pump duty. -Drained condensates from the surge tanks air compressors. -Checked dry well, ok. -Checked bar screens. Switched rag bin. Cleaned/hosed down bar screen room. -Bar Screen Bin Removal and Replacement - pushed rag bins back in the screen room after pick up by Miller Waste. ————————————————————— • Attachments: 0
12237941 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12237941 | 1899-12-31 | 2025-12-15 10:22 | 2025-12-15 10:22 | Barry Middleton (WW-CEAST) @ Markham Leslie Pumping Station - LSSS Date Work Completed: 2025-12-15 10:22 ————————————————————— Weather today Snow and -7 Celsius -On site to complete work orders W11449182, W11448009. -Completed station check. -Entered station readings into SharePoint. -pump # 2 is currently being work on by centralized maintenance. -Pumps 3, 5 and 6 available in timed-auto duty rotation every 4 hours. -Pump 1 out of service for repair and taken out of site. -Pump 4 out of service for repair. -Tested standby power generator #1 Failed to start alarm from previous generator test run. -Tested standby power generator #1 at 10:20 am and also at 1:00 pm with centralized maintenance electrical. -All standby power generators available in auto. -Switched sump pump duty. -Drained condensates from the surge tanks air compressors. -Checked dry well, ok. -Checked bar screens. Switched rag bin. Cleaned/hosed down bar screen room. ————————————————————— • Attachments: 0
12246058 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12246058 | 1900-01-01 | 2025-12-17 14:14 | 2025-12-17 11:10 | Philip Romito (WW-CEAST) @ Markham Leslie Pumping Station - LSSS Date Work Completed: 2025-12-17 11:10 ————————————————————— -On site to clean Bayview Steeles mist eliminator filters. -Hosed down filters in screen room and left sitting out to dry. -Fixed leak on upper screw press drain line. -Hosed down floors in screen room. -Pumps 1 and 4 OOS. -Crane Tech is on site continuing repairs to lower level hoist. ————————————————————— • Worked With: Kevin Shaji • Attachments: 0
12250874 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12250874 | 1899-12-31 | 2025-12-19 09:30 | 2025-12-19 09:30 | Barry Middleton (WW-CEAST) @ Markham Leslie Pumping Station - LSSS Date Work Completed: 2025-12-19 09:30 ————————————————————— Weather today Rain and Snow mixed and 2 Celsius -On site to complete work order W11460249. -Completed station check. -Entered station readings into SharePoint. -Pumps 3, 2, 5, and 6 available in timed-auto duty rotation every 4 hours. -Pumps 1 and 4 out of service. -All standby power generators available in auto. -Drained condensates from the surge tanks air compressors. -Checked dry well, ok. -Checked bar screens. Switched rag bin. Cleaned/hosed down bar screen room. -Bar Screen Bin Removal and Replacement - pushed rag bins back in the screen room after pick up by Miller Waste. ————————————————————— • Attachments: 0
12255115 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12255115 | 1899-12-31 | 2025-12-22 11:15 | 2025-12-22 11:15 | Barry Middleton (WW-CEAST) @ Markham Leslie Pumping Station - LSSS Date Work Completed: 2025-12-22 11:15 ————————————————————— Weather today A few clouds and -4 Celsius -On site to complete work order W11463780. -Completed station check. -Entered station readings into SharePoint. -Pumps 3, 2, 5, and 6 available in timed-auto duty rotation every 4 hours. -Pumps 1 and 4 out of service. -All standby power generators available in auto. -Switched sump pump duty. -Drained condensates from the surge tanks air compressors. -Checked dry well, ok. -Checked bar screens. Switched rag bin. Cleaned/hosed down bar screen room. ————————————————————— • Attachments: 0
12261396 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12261396 | 1899-12-31 | 2025-12-24 10:54 | 2025-12-24 10:54 | Barry Middleton (WW-CEAST) @ Markham Leslie Pumping Station - LSSS Date Work Completed: 2025-12-24 10:54 ————————————————————— Weather today Clear and -2 Celsius -On site to complete work orders W11469148, W11469335. -Completed station check. -Entered station readings into SharePoint. -Pumps 3, 2, 5, and 6 available in timed-auto duty rotation every 4 hours. -Pumps 1 and 4 out of service. -All standby power generators available in auto. -Switched sump pump duty. -Drained condensates from the surge tanks air compressors. -Checked dry well, ok. -Checked bar screens. Switched rag bin. Cleaned/hosed down bar screen room. -Bar Screen Bin Removal and Replacement - pushed rag bins out for pick up by Miller Waste. ————————————————————— • Attachments: 0
12273823 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12273823 | 1899-12-31 | 2025-12-31 14:57 | 2025-12-31 14:57 | Barry Middleton (WW-CEAST) @ Markham Leslie Pumping Station - LSSS Date Work Completed: 2025-12-31 14:57 ————————————————————— Weather today Partly Cloudy and -5 Celsius -On site to complete work orders W11479427, W11482733, W11482920. -Completed station check. -Entered station readings into SharePoint. -Pumps 3, 2, 5, and 6 available in timed-auto duty rotation every 4 hours. -Pumps 1 and 4 out of service. -All standby power generators available in auto. -Switched sump pump duty. -Drained condensates from the surge tanks air compressors. -Checked dry well, ok. -Checked bar screens. Switched rag bin. Cleaned/hosed down bar screen room. -Bar Screen Bin Removal and Replacement - pushed rag bins out for pick up by Miller Waste. ————————————————————— • Attachments: 0
1

## Bogart SPS
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS
[6 empty] | 12269093 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12269093 | 1 | 2025-12-29 17:15 | 2025-12-29 17:12 | Chris Rodie (WW-CEAST) @ Newmarket Bogart Creek Sewage Pumping Station - NMSSHS Date Work Completed: 2025-12-29 17:12 ————————————————————— -sump pumps not producing flow -pumped down flood in basement, site is dry now -pump 3 manual off as air valve is leaking water, can be ran in emergencies -Satnam Mann from electrical is on site to investigate pump issue -site is dry and sump pumps can be replaced tomorrow -portable sump pump issue setup to quickly pump down any future floods -site okay until tomorrow ————————————————————— • Worked With: Satnam Mann • Attachments: 0

## Newmarket SPS
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS
12258379 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12258379 | 1899-12-31 | 2025-12-23 17:18 | 2025-12-23 17:16 | Chris Rodie (WW-CEAST) @ Newmarket Sewage Pumping Station & Equalization Tank - NMSSBP Date Work Completed: 2025-12-23 17:16 ————————————————————— -on site for bar screen 1 over torque -reset bar screen monitored, took a few resets to start working normal again, rake is level, chains are on. -no issues visible -reset alarms -inlet gate can be closed remotely if it trips again tonight it can be investigated by mechanical tomorrow if it continues -site okay, pump 2 remains OOS, and will be reinstated tomorrow ————————————————————— • Attachments: 0 | 1
12214200 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12214200 | 1900-01-01 | 2025-12-07 10:06 | 2025-12-07 10:04 | Marcos Tungcol (WW-CEAST) @ Newmarket Sewage Pumping Station & Equalization Tank - NMSSBP Date Work Completed: 2025-12-07 10:04 ————————————————————— On site responded to a call from the ROC regarding mechanical screen 1 overtorque alarm. Cleared/reset fault alarm, ran bar screen for several cycles, ok. Bar screen back in service. At around 10: 11 am, it overtorque again. Found rake hitting the scraper when it is running. Cleared/reset alarm, ran again, again it is hitting the scraper. Put bar screen out of service. Closed Sluice Gate MV1. Created work order request to CMS for repair. Informed ROC (Carter D.). ————————————————————— • Attachments: 0
12218848 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12218848 | 1899-12-31 | 2025-12-08 10:05 | 2025-12-08 09:42 | Bill Van Bakel (WW-MAINT) @ Newmarket Sewage Pumping Station & Equalization Tank - NMSSBP Date Work Completed: 2025-12-08 09:42 ————————————————————— On site for bar screen 1 over torque. Found loose bolts on the motor bracket and also adjusted the sensor. Had Terry open the channel and put it back in auto ————————————————————— • Worked With: Terry Reed • Attachments: 0
12219370 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12219370 | 2 | 2025-12-08 13:55 | 2025-12-08 11:15 | Terry Reed (WW-CEAST) @ Newmarket Sewage Pumping Station & Equalization Tank - NMSSBP Date Work Completed: 2025-12-08 11:15 ————————————————————— Took station readings and entered into SharePoint,,, reviewed trends - all good. Levelled off bin in the screening room and emptied the top of the auger,, flushed out drain screen as well as the drain hose - moved bin over to fill the other half. Checked both compressors oil/belts - OK. Also checked pump floor - all good. Station running under normal ops - pump 2 is OOS. Bar screen 1 is back in service and inlet channel has been opened. ————————————————————— • Attachments: 0

## Mt. Albert WRRF
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS
12201751 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12201751 | 1900-01-06 | 2025-12-01 08:15 | 2025-12-01 08:15 | Philip Romito (WW-CEAST) @ Mount Albert Water Resource Recovery Facility - MTSP Date Work Completed: 2025-12-01 08:15 ————————————————————— -On site to complete work orders. -Decanted STT to headworks, then emptied tank to SHT. -Completed lab analysis, entered results into SharePoint. -Added two bags of soda ash to each aeration tank. -Batch wasted 8m3. Ran RAS pumps at 100% when returning to service. -Monthly JHSC H&S inspection completed, no issues noted. -1157 - Transferred site to generator power. -1305 - Transferred site back to utility power. -Monthly diesel generator test run completed, readings entered into SharePoint. -Generator start hours: 486.2, stop hours: 487.5, run time: 1.3hrs. -Post aeration alum chamber and RAS inlet chambers cleaned out. -Clarifier 2 is drained and OOS for weir cover installation. -RAS Pump 1 and WAS Pump 1 OOS while Clarifier 2 is OOS. ————————————————————— • Worked With: Chris Rodie • Attachments: 0 | 1
12206266 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12206266 | 1900-01-03 | 2025-12-03 08:12 | 2025-12-03 08:12 | Philip Romito (WW-CEAST) @ Mount Albert Water Resource Recovery Facility - MTSP Date Work Completed: 2025-12-03 08:12 ————————————————————— -On site to complete work orders. -Decanted STT to headworks, then emptied tank into SHT. -Completed lab analysis, entered results into SharePoint. -Batch wasted 8m3. Mistakenly also batch wasted 8m3 from OOS Clarifier 2. -Ran RAS pumps at 100% speed when returning to service. -Added two bags of soda ash to each aeration tank. -Station check completed, readings entered into SharePoint. -Verified sand filter operation and alum dosing. -Clarifier 2 OOS, WAS Pump 1 OOS, RAS Pump 1 OOS. -Contractors on site working on installing Clarifier 2 weir covers. -Aeration Blower 3 had multiple Failed to Start Alarms this afternoon. Failed to start in auto and manual multiple times. Found small air leak on discharge coupling, tightened bolts, air no longer leaking. Also found air leak on discharge header coupling, also tightened bolts and air is no longer leaking. Test ran Aeration Blower 3 in local with no issues, but again failed to start in manual or auto. Will create work request for maintenance team to continue troubleshooting. Inspected belts, filter, oil levels, but found no issues. ————————————————————— • Worked With: Chris Rodie • Attachments: 0 | 1
12213450 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12213450 | 1900-01-05 | 2025-12-05 08:34 | 2025-12-05 08:34 | Philip Romito (WW-CEAST) @ Mount Albert Water Resource Recovery Facility - MTSP Date Work Completed: 2025-12-05 08:34 ————————————————————— -On site to complete lab analysis and sludge handling. -Emptied STT to SHT. -Completed lab analysis, entered results into SharePoint. -Added two bags of soda ash to each aeration tank. -Batch wasted 10m3, ran RAS pumps at 100% when returning to service. -Completed site walkthrough with Jacobs. -Clarifier 2 OOS for weir cover installation, WAS pump 1 OOS, RAS pump 1 OOS. -Aeration Blower 3 OOS, but can run in local. ————————————————————— • Worked With: Philip Romito, Chris Rodie • Attachments: 0 | 1
12219380 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12219380 | 1899-12-31 | 2025-12-08 14:06 | 2025-12-08 08:30 | Philip Romito (WW-CEAST) @ Mount Albert Water Resource Recovery Facility - MTSP Date Work Completed: 2025-12-08 08:30 ————————————————————— -On site to complete lab analysis and sludge handling. -Decanted STT to headworks, tank then emptied into SHT. -Completed lab analysis, entered results into SharePoint. -Batch wasted 10m3, ran RAS pumps at 100% speed when returning to service. -Added two bags of soda ash to each aeration tank. -Clarifier 2 remains OOS for weir cover installation, WAS pump 1 and RAS pump 1 also OOS. ————————————————————— • Worked With: Chris Rodie • Attachments: 0 | 1
12226796 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12226796 | 1900-01-02 | 2025-12-10 08:22 | 2025-12-10 08:22 | Philip Romito (WW-CEAST) @ Mount Albert Water Resource Recovery Facility - MTSP Date Work Completed: 2025-12-10 08:22 ————————————————————— -On site to complete work orders. -Decanted STT to headworks, then emptied tank into SHT. -Added two bags of soda ash to each aeration tank. -Completed lab analysis, entered results into SharePoint. -Batch wasted 10m3, ran RAS pumps at 100% speed when returning to service. -Station check completed, readings entered into SharePoint. -Verified alum dosing and sand filter operation. -DO probe verification completed. -Scum pumps 1-2 inspection completed. -WAS pumps 1-2 inspection completed. -Aeration Blower 3 OOS. -Clarifier 2 OOS for weir cover installation, WAS Pump 1 OOS, RAS Pump 1 OOS. ————————————————————— • Attachments: 0 | 1
12233313 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12233313 | 1900-01-03 | 2025-12-12 08:41 | 2025-12-12 08:41 | Philip Romito (WW-CEAST) @ Mount Albert Water Resource Recovery Facility - MTSP Date Work Completed: 2025-12-12 08:41 ————————————————————— -On site to complete work orders. -Station check completed, readings entered into SharePoint. -Verified sand filter operation and alum dosing. -Pulled and inspected DO probes. -Travelling screen maintenance completed. Cleaned out back compartment and greased unit. Created work request for failed bearing on brush shaft. -Screw press maintenance completed. -Grit dewatering screw press maintenance completed. -Clarifier 2 remains OOS for weir cover installation. WAS Pump 1 OOS, RAS Pump 1 OOS. -OCU OOS due to failed motor. -Aeration Blower 3 OOS, but can be run in local. ————————————————————— • Worked With: Kevin Shaji • Attachments: 0 | 1
12238026 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12238026 | 1899-12-31 | 2025-12-15 11:45 | 2025-12-14 07:05 | Terry Reed (WW-CEAST) @ Mount Albert Water Resource Recovery Facility - MTSP Date Work Completed: 2025-12-14 07:05 ————————————————————— Completed sludge processing along with the lab work and entered results into SharePoint,, wasted 10m3 and added 4 bags of soda ash. Station running under normal ops- WAS pump 1 is OOS due to work on the clarifier. ————————————————————— • Attachments: 0
12241797 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12241797 | 1900-01-02 | 2025-12-16 08:25 | 2025-12-16 08:25 | Philip Romito (WW-CEAST) @ Mount Albert Water Resource Recovery Facility - MTSP Date Work Completed: 2025-12-16 08:25 ————————————————————— -On site for lab analysis and sludge handling work. -Decanted STT to headworks, then emptied tank into SHT. -Added two bags of soda ash to each aeration tank. -Completed lab analysis, entered results into SharePoint. -Batch wasted 10m3, ran RAS pumps at 100% speed when returning to service. -Clarifier 2 OOS, WAS Pump 1 OOS, RAS Pump 1 OOS. -Aeration Blower 3 OOS, but can be run in local. ————————————————————— • Worked With: Chris Rodie • Attachments: 0
12248388 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12248388 | 1900-01-01 | 2025-12-18 08:44 | 2025-12-18 08:43 | Chris Rodie (WW-CEAST) @ Mount Albert Water Resource Recovery Facility - MTSP Date Work Completed: 2025-12-18 08:43 ————————————————————— -station check of site -reviewed SCADA -inspected site -entered data into SharePoint -cleaned alum injection chamber -cleaned RAS chamber -hosed UV channel -Sand Filter Service Filter #1 -clarifier 2 is OOS, began filling clarifier 2 with effluent water -disregard final effluent flow lolo alarm, this is due to filling clarifier 2 with effluent water, which is robbing from the flowmeter -clarifier 2 will be put back online tomorrow -station okay ————————————————————— • Worked With: Kevin Shaji, Philip Romito • Attachments: 0
12250905 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12250905 | 1900-01-03 | 2025-12-19 10:37 | 2025-12-19 09:18 | Philip Romito (WW-CEAST) @ Mount Albert Water Resource Recovery Facility - MTSP Date Work Completed: 2025-12-19 09:18 ————————————————————— -On site for lab analysis and sludge handling work. -Clarifier 2 had been filling with effluent water overnight. Ice is now completely gone. Turned off effluent pump 2 and removed hose from clarifier. Test ran Clarifier 2 in auto with no issues. Observed multiple arm rotations with no issues, then opened Clarifier 2 inlet gate from aeration tanks. Continued to let RAS Pumps pull from Clarifier 1 for several hours. Following batch wasting, placed WAS Pump 1 and RAS Pump 1 back into service. Test ran RAS pump 1 and ran at 100% speed to test flows, no issues noted. -Clarifier 2 back in service, WAS pump 1 and RAS pump 1 also now back in service. -Re-valved RAS pumps, RAS pumps 1 and 2 are now valved to draw from Clarifier 2 and RAS pumps 3 is valved to draw from Clarifier 1. -Decanted STT to headworks, emptied STT to SHT following batch wasting. -Added two bags of soda ash to each aeration tank. -Completed lab analysis, entered results into SharePoint. -Batch wasted 10m3, ran RAS pumps at 100% speed when returning to service. -Verified sand filter operation and alum dosing. -Aeration Blower 3 OOS, but can be run in local. ————————————————————— • Worked With: Kevin Shaji • Attachments: 0
12255232 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12255232 | 1900-01-02 | 2025-12-22 14:29 | 2025-12-22 08:50 | Philip Romito (WW-CEAST) @ Mount Albert Water Resource Recovery Facility - MTSP Date Work Completed: 2025-12-22 08:50 ————————————————————— -On site to complete work orders. -Decanted STT to headworks, then emptied tank into SHT. -Added two bags of soda ash to each aeration tank. -Received delivery for new OCU fan motor. Placed motor in garage, installation planned for tomorrow. -Completed lab analysis, entered results into SharePoint. -Batch wasted 16m3, ran RAS pumps at 100% speed when returning to service. -Cleaned out RAS inlet chamber and post aeration alum chamber. Removed rags from aeration tank inlet gates -Cleaned off DO probes, reattached air blow-off lines to both probes, both had become disconnected. -Aeration blower 3 OOS, but can be run in local. ————————————————————— • Worked With: Chris Rodie • Attachments: 0
12258330 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12258330 | 1900-01-01 | 2025-12-23 13:54 | 2025-12-23 09:50 | Philip Romito (WW-CEAST) @ Mount Albert Water Resource Recovery Facility - MTSP Date Work Completed: 2025-12-23 09:50 ————————————————————— -On site to complete lab analysis and sludge handling. -Decanted STT to headworks. -Added two bags of soda ash to each aeration tank. -Completed lab analysis and entered results into SharePoint. -Batch wasted 20m3, ran RAS pumps at 100% speed when returning to service. -OCU motor repairs delayed until early next year. -Aeration blower 3 OOS, can be run in local. ————————————————————— • Worked With: Chris Rodie • Attachments: 0

## King City SPS
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS
12222566 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12222566 | 1 | 2025-12-09 13:55 | 2025-12-09 13:54 | Young Jung (WW-WEST) @ King City Pumping Station - KCSSKR Date Work Completed: 2025-12-09 13:54 ————————————————————— Checked station and recorded readings on SharePoint. Checked bin room. Cleaned area and flushed drain line Generator room dampers stays open and does not close. Upon inspection, damper control panel fails to get information. BR3 is tripped and trips when the power to the panel is turned on. Created work order to address the issue ————————————————————— • Attachments: 0
12250837 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12250837 | 3 | 2025-12-19 08:02 | 2025-12-19 08:00 | Daniel Hirstwood (LEADS) @ King City Pumping Station - KCSSKR Date Work Completed: 2025-12-19 08:00 ————————————————————— Notified by email that RS pumps 2 & 3 were OOS following a power blip. Arrived and reset the disconnect on RS Pump 3 and the reset button on RS pump 2 MCC. Reset alarms on SCADA. Station checks, SharePoint readings and review of continuous monitoring data. Push in miller waste bin. ————————————————————— • Worked With: Young Jung • Attachments: 0
12250918 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12250918 | 1 | 2025-12-19 11:16 | 2025-12-19 11:16 | Brent Ste-Croix (WW-MAINT) @ King City Pumping Station - KCSSKR Date Work Completed: 2025-12-19 11:16 ————————————————————— Upon responding to the pump failure at King city we were able to observe pump 1 running in auto. Pump 2, Pump 3 both faulted at the drive displaying a F37 fault which means one of two things. Phase loss or Phase imbalance. We were able to check the line voltage and it was above 600v and around 350 phase to ground on each phase. We reset Pump 2 and let it Run through a cycle. The output off the drive was 350v on each phase to ground which is right around where it should be while operating. The current across the phases was put by over 20a between phase B -A,C (A128 B108 C127) this leads me to believe the windings on the motor have seen spikes and are deteriorating . While operating the soft start is displaying A code of A37 Which, according to the manual means there is a current imbalance on the motor, should the imbalance go outside this threshold. It will give us the same F 37 fault That is displayed during a phase loss which we were able to see on Scada here this morning. We performed tests on pump three and then pump one and all three pumps are giving us the same information. I've informed Bill and we will be looking at servicing these pump motors as soon as possible ————————————————————— • Attachments: 0
12265633 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12265633 | 1 | 2025-12-28 23:15 | 2025-12-28 23:13 | Gavin Walker (WW-WEST) @ King City Pumping Station - KCSSKR Date Work Completed: 2025-12-28 23:13 ————————————————————— On site to reset all pumps that were knocked oos due to power blips Reset pumps, wet wells, bar screen and screw compactor Pumped down the wet wells Had to reset the pumps another 3 times due to power issues Left pump 3 oos as a back up pump ————————————————————— • Attachments: 0
12268977 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12268977 | 1 | 2025-12-29 11:15 | 2025-12-29 11:12 | Young Jung (WW-WEST) @ King City Pumping Station - KCSSKR Date Work Completed: 2025-12-29 11:12 ————————————————————— Arrived on site to reset pump 1 after it faulted due to ongoing power issue. Generator running upon arrival. Noticed the street lights are out of power too. Notified on call operator to monitor the town’s power outage. Pump 1 and 2 are in duty rotation. Pump 3 is in duty 3 and in manual and will be used in case of emergencies. ————————————————————— • Attachments: 0

## Black Creek SPS
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS
12213659 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12213659 | 1 | 2025-12-05 11:31 | 2025-12-05 11:31 | Young Jung (WW-WEST) @ Vaughan Black Creek Pumping Station - BLSS Date Work Completed: 2025-12-05 11:31 ————————————————————— - Checked station and recorded readings on SharePoint - Levelled bin - Notified supervisor to escalate the previously created archibus to address the black creek Lo Lo temperature - Performed weekly pump test. Ran each pumps 1-5 manually, one at a time, and recorded readings. Check valve for pump 3 not closing. Work order already created Pump 1: 587 L/s, pressure 295 kPa Pump 2: 452 L/s at 100%, pressure 266 kPa Pump 3: 128 L/s at 100% speed, pressure 214 kPa Pump 4: 465 L/s at 100% speed, pressure 279 kPa Pump 5: 561 L/s at 100% speed, pressure 286 kPa - seal water pressure relieve valve tested. Cleaned strainers after isolating, all very clean. checked valve operation. No issues - Found leak on service water line and the insulation is full of water. Does not seem like condensation due to the sheer amount water dripping. Located on B1. Created work order - Found another leak on the sanitary drain prime line located on B1. WO created ————————————————————— • Attachments: 0
12258283 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12258283 | 1 | 2025-12-23 12:03 | 2025-12-23 12:03 | Young Jung (WW-WEST) @ Vaughan Black Creek Pumping Station - BLSS Date Work Completed: 2025-12-23 12:03 ————————————————————— - Raked bin and cleaned area. Pushed bin out for pickup - Checked screen and topped up oil hopper - Performed weekly pump test. Ran each pumps 1-5 manually, one at a time, and recorded readings. Check valve for pump 3 not closing. Work order already created Pump 1: 573 L/s, pressure 304 kPa Pump 2: 446 L/s at 100%, pressure 267 kPa Pump 3: 130.7 L/s at 100% speed, pressure 215 kPa Pump 4: 457 L/s at 100% speed, pressure 271 kPa Pump 5: 560.9 L/s at 100% speed, pressure 288 kPa - bell contractor onsite working on security system - Checked station and recorded readings on SharePoint. Reset tripped radiator fan 3 ————————————————————— • Attachments: 0

## Schomberg WRRF
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS
12201741 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12201741 | 2 | 2025-12-01 07:48 | 2025-12-01 07:50 | Marcus Remonde (WW-WEST) @ Schomberg Water Resource Recovery Facility - SHSP Date Work Completed: 2025-12-01 07:50 ————————————————————— Remotely Placed Supernatant Drain Valve in Manual Open. Remotely Rotated WAS Pump Duties. Pump #2 Manual Off, Pump #1 in Auto. Remotely Rotated RAS Pump Duties. Pump #1 in Duty #1, Pump #3 in Duty #3, OOS. Remotely Responded to Alum Pumps #6 and 7 No Flow Alarms. Acknowledged and Reset Alarms. Returned Both Pumps to Duty. Decant Complete. Remotely Closed Supernatant Valve in Manual. ————————————————————— • Attachments: 0 • [REMOTE ENTRY]
12213487 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12213487 | 7 | 2025-12-05 09:42 | 2025-12-05 14:00 | Marcus Remonde (WW-WEST) @ Schomberg Water Resource Recovery Facility - SHSP Date Work Completed: 2025-12-05 14:00 ————————————————————— In to Complete Scheduled WOs. Notified ROC. Lowered and Activated Decant Pump. Placed Plant Service Water Line in OOS Aer. Tank #2 and Commenced Filling Process for CPD Led Foundation Leak Investigation. Placed Scum Pump #2 in Manual On, Recirculated Scum Tank, Returned to Manual Off. Placed Scum Valve in Manual Discharge and Activated Scum Pump #2 in Manual. Scum Tank Drawdown Complete. Returned All to Auto and Service. Decant Complete, Raised and Deactivated Decant Pump. Sludge Transfer Valve Manual Open, Transferred Thickened Sludge. Transfer Valve Returned to Manual Closed. Completed Filter Inlet TSS Sensor Inspection. Placed Unit in Calibration Mode Locally, Cleaned Probe. No Issues Found. Returned to Service. Completed Aer. Blowers #1-4 Inspections. Filters OK. Replaced Belts on Aer. Blower #3. Topped Up Oil Reservoirs on Aer. Blowers #1 and 4. No Other Issues Found. Returned All to Service. Cleared Associated Alarms. OOS Aer. Tank #2 Filling Process to be Continued. Deactivated and Removed Plant Service Water Line. ————————————————————— • Attachments: 0
12214190 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12214190 | 3 | 2025-12-07 06:25 | 2025-12-07 06:30 | Marcus Remonde (WW-WEST) @ Schomberg Water Resource Recovery Facility - SHSP Date Work Completed: 2025-12-07 06:30 ————————————————————— In Responding to UV System Major Fault Alarm Communicated by the ROC. Found UV Bank B with a Burnt Bulb, Whilst UV Bank A Continues to Experience Possible Fuse Related Issues with Rack #5 (WO Already Generated —> W11475704). Both Banks Running Simultaneously in Auto. Placed Both Units in Manual Locally. Deactivated UV B and Replaced Burnt Out Bulb. Tested Unit, No Further Issues Found. Returned Both to Auto and Service. Cleared Associated Alarm. UV Bank A to Remain in Auto and Alarm Locally Until WO Request Completed by Maintenance. ————————————————————— • Attachments: 0
12227420 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12227420 | 2 | 2025-12-11 04:43 | 2025-12-11 04:45 | Marcus Remonde (WW-WEST) @ Schomberg Water Resource Recovery Facility - SHSP Date Work Completed: 2025-12-11 04:45 ————————————————————— Remotely Responded to RAS Pumps #3 No Flow Alarm Communicated by the ROC. Remotely Rotated RAS Pump Duties. Pump #2 in Duty #1, Pump #3 in Duty #3, OOS. Flow Restored and Alarm Cleared. ————————————————————— • Attachments: 0 • [REMOTE ENTRY]
12233440 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12233440 | 5 | 2025-12-12 09:45 | 2025-12-12 13:55 | Marcus Remonde (WW-WEST) @ Schomberg Water Resource Recovery Facility - SHSP Date Work Completed: 2025-12-12 13:55 ————————————————————— In to Complete Scheduled WOs. Notified ROC. Lowered and Activated Decant Pump. Decant Complete, Raised and Deactivated Decant Pump. Sludge Transfer Valve Manual Open, Transferred Thickened Sludge. Transfer Valve Returned to Manual Closed. OOS Aer. Tank #2 Filling Process Complete. Deactivated and Removed Plant Service Water Line. Completed Process Building and Blower Building Sump System Inspections. Tested Hi Level Float Alarms. Confirmed Reception by the ROC. No Issues Found. Returned to Service. Cleared Associated Alarms. Completed Scum Pumps #1 and 2 Inspections. Couplings and Oil Levels OK. Greased Bearings. Returned to Service. ————————————————————— • Attachments: 0
12238024 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12238024 | 3 | 2025-12-15 11:37 | 2025-12-15 14:15 | Marcus Remonde (WW-WEST) @ Schomberg Water Resource Recovery Facility - SHSP Date Work Completed: 2025-12-15 14:15 ————————————————————— In to Complete Scheduled WOs. Notified ROC. Lowered and Activated Decant Pump. Rotated WAS Pump Duties. Pump #2 Manual Off, Pump #1 in Auto. Rotated RAS Pump Duties. Pump #1 in Duty #1, Pump #3 in Duty #3, OOS. Decant Complete, Raised and Deactivated Decant Pump. Sludge Transfer Valve Manual Open, Transferred Thickened Sludge. Transfer Valve Returned to Manual Closed. Placed Scum Pump #2 in Manual On, Recirculated Scum Tank, Returned to Manual Off. Placed Scum Valve in Manual Discharge and Activated Scum Pump #2 in Manual. Scum Tank Drawdown Complete. Returned All to Auto and Service. Rebuilt Alum Pumps #6 and 7. Returned to Service and Tested Units. No Issues Found. ————————————————————— • Attachments: 0
12248338 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12248338 | 1 | 2025-12-18 07:10 | 2025-12-18 07:10 | Marcus Remonde (WW-WEST) @ Schomberg Water Resource Recovery Facility - SHSP Date Work Completed: 2025-12-18 07:10 ————————————————————— Remotely Reviewed SCADA and Trends. Recurrent Screen Room O2 Concentrations Hi and HiHi Alarms Outstanding. Created WO for Instrumentation —> W11526277. ————————————————————— • Attachments: 0 • [REMOTE ENTRY]
12248545 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12248545 | 1 | 2025-12-18 12:07 | 2025-12-18 12:05 | Terry Cantwell (WW-MAINT) @ Schomberg Water Resource Recovery Facility - SHSP Date Work Completed: 2025-12-18 12:05 ————————————————————— Troubleshoot blower 2 and 3. Found blower 2 pressure gauge is not receiving enough air pressure to register. Cleaned filter and no change. Removed brass filter and gauge is operational. Blower 3 filter minder gauge is not working. New gauge is required. ————————————————————— • Worked With: Marcus Remonde • Attachments: 0
12255052 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12255052 | 5 | 2025-12-22 10:42 | 2025-12-22 14:45 | Marcus Remonde (WW-WEST) @ Schomberg Water Resource Recovery Facility - SHSP Date Work Completed: 2025-12-22 14:45 ————————————————————— In to Complete Scheduled WOs. WAS Pump #1 Cumulatively Auto-Wasted 167 m3 Over the Span of the Weekend. Lowered and Activated Decant Pump. Rotated WAS Pump Duties. Pump #1 Manual Off, Pump #2 in Auto. Rotated RAS Pump Duties. Pump #3 in Duty #1, Pump #1 in Duty #3, OOS. Decant Complete, Raised and Deactivated Decant Pump. Sludge Transfer Valve Manual Open, Transferred Thickened Sludge. Transfer Valve Returned to Manual Closed. Completed Alum Pumps #6 and 7 Drawdown Testing and Panel Board Cleaning. Returned to Service. ————————————————————— • Attachments: 0
12269350 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12269350 | 1 | 2025-12-30 04:11 | 2025-12-30 04:06 | Lauren Swanson (WW-WEST) @ Schomberg Water Resource Recovery Facility - SHSP Date Work Completed: 2025-12-30 04:06 ————————————————————— Onsite for call out due to UV bank 1B major fault alarm due to blown bulb. UV bank 1A in local off for repairs. Set UV bank 1A to manual on to replace blown bulb UV bank 1B bulb out in rack 5 bulb 1. Replaced. UV bank 1B back in auto and UV bank 1A back in local off. ————————————————————— • Attachments: 0
12206350 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12206350 | 6 | 2025-12-03 10:40 | 2025-12-03 13:40 | Marcus Remonde (WW-WEST) @ Schomberg Water Resource Recovery Facility - SHSP Date Work Completed: 2025-12-03 13:40 ————————————————————— In to Complete Scheduled WOs. Notified ROC. Lowered and Activated Decant Pump. Received Alum Delivery. Reviewed and Signed Documentation. Alum Tank Levels: 0.90/0.90 —> 2.34/2.36m. Decant Complete, Raised and Deactivated Decant Pump. Sludge Transfer Valve Manual Open, Transferred Thickened Sludge. Transfer Valve Returned to Manual Closed. Identified Possible Diatomaceous Particles within FE Holding Tank and FE Composite Samples, Potentially Affecting and Increasing FE TSS Results. Particles Do Not Appear to be Present in Clarifier Effluent or UV Channel. Reference Attached Photos. Notified TL and Supervisor. Identified Potential Slow Diesel Generator Fuel Leak Located on the Units’s Fuel Return Line. Leak is Contained within Fuel Containment and Does Not Appear to be Free Flowing. Notified TL and Appropriate Staff for Further Inspection. Completed Aer. DO Sensor Maintenance. Placed Probes in Calibration Mode. Cleaned and Inspected Units, No Issues Found. Returned to Service. ————————————————————— • Attachments: 7

## Nobleton WRRF
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS
12210851 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12210851 | 2 | 2025-12-04 15:00 | 2025-12-04 14:58 | Lance Johnson (LEADS) @ Nobleton Water Resource Recovery Facility - NBSP Date Work Completed: 2025-12-04 14:58 ————————————————————— Started supernate pump. Removed floating solids from filtration inlet channel. Removed floating solids from aeration tank surface. Checked for aeration tank air line condensation. None found. Confirmed D O probe operation. Okay. Checked heat trace on headworks building. Not okay. Created work order for repair. ————————————————————— • Attachments: 0
12227140 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12227140 | 2 | 2025-12-10 15:24 | 2025-12-10 15:22 | Harie Rajamithiran (WW-WEST) @ Nobleton Water Resource Recovery Facility - NBSP Date Work Completed: 2025-12-10 15:22 ————————————————————— Harie Rajamithiran(OIT) working under the direction of Lance Johnson(OIC) -Completed station check and found aeration blower #1 rubber flange leak , created work order for the repair -Inspected aeration blowers -Cleaned aeration inlet/outlet rags -Checked online DO probes ————————————————————— • Worked With: Lance Johnson • Attachments: 0
12238173 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12238173 | 1 | 2025-12-15 14:36 | 2025-12-15 14:36 | Young Jung (WW-WEST) @ Nobleton Water Resource Recovery Facility - NBSP Date Work Completed: 2025-12-15 14:36 ————————————————————— - Received alum delivery at 13:00. Checked certificate of authenticity. Signed all papers. Received from 0.86 m to 3.62 m. No issues while receiving. For payment processing, sent a copy to Adriana Posea - Performed in-house lab and recorded readings on SharePoint - Decanted the sludge thickening tank. Once done, transferred sludge into the holding tank - Added 2 bags of soda ash per each aeration tank - Performed station check and recorded readings on SharePoint - Created work order for process building gas detector alarm and warning - Made sampling bottles for sampling tomorrow ————————————————————— • Attachments: 0
12241864 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12241864 | 1 | 2025-12-16 10:41 | 2025-12-16 10:39 | David Dougherty (WW-MAINT) @ Nobleton Water Resource Recovery Facility - NBSP Date Work Completed: 2025-12-16 10:39 ————————————————————— On site to troubleshoot head works screenings press heat trace. Controller display is not functioning correctly but the heat trace is still working. Have to source a replacement controller. ————————————————————— • Attachments: 0
12248392 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12248392 | 1 | 2025-12-18 08:56 | 2025-12-18 08:55 | Terry Cantwell (WW-MAINT) @ Nobleton Water Resource Recovery Facility - NBSP Date Work Completed: 2025-12-18 08:55 ————————————————————— Checked with operator and found blower 1 rubber out let is leaking. Measured outlet pipe and will get new outlet rubber to make repairs. ————————————————————— • Attachments: 0

## Kleinburg WRRF
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS
12206523 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12206523 | 1 | 2025-12-03 14:38 | 2025-12-03 14:23 | Harie Rajamithiran (WW-WEST) @ Kleinburg Water Resource Recovery Facility - KBSPF Date Work Completed: 2025-12-03 14:23 ————————————————————— Harie Rajamithiran(OIT) working under the direction of Daniel Hirstwood(OIC) -Entered aeration tank#2 for maintenance activities, replaced worn out membrane diffusers, added new membrane diffusers and caps on empty heads -Started filling aeration tank#2 using 2 submersible pumps with flow coming from aeration tank#1 -Opened inlet gate to aeration tank#2 -Alum lines are frozen on aeration tank#2, torched the ends a little bit to try and melt the ice, unsuccessful and will attempt again tomorrow -Discovered a leak at the hydrant near aeration tank#1, maintenance was arrived and made a temporary patch. To drain the hydrant, wash pumps were turned off and maintenance will come back to fix the hydrant. ————————————————————— • Worked With: Daniel Hirstwood, Young Jung • Attachments: 0
12210659 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12210659 | 3 | 2025-12-04 11:16 | 2025-12-04 11:14 | Lauren Swanson (WW-WEST) @ Kleinburg Water Resource Recovery Facility - KBSPF Date Work Completed: 2025-12-04 11:14 ————————————————————— Completed daily lab and station check - added data Into SharePoint. Turned RAS off at 8:27am and set WAS to waste 30m3 from 9am to 11am. RAS resumed when wasting completed. WAS set back to manual. Added 8 bags of soda ash into hopper. Increased soda ash dosage run time from 6.75seconds/h to 7.00seconds/h. Exercised RAS/WAS valves. Alum line to aeration tank 2 still frozen. Dan Hirstwood onsite to attempt to melt ice in lines but unsuccessful. Maintenance will be onsite tomorrow to try to replace line. Leaving aeration tank 2 inlet gates closed until alum line is fixed. ————————————————————— • Attachments: 0
12222600 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12222600 | 2 | 2025-12-09 14:27 | 2025-12-09 14:25 | Lauren Swanson (WW-WEST) @ Kleinburg Water Resource Recovery Facility - KBSPF Date Work Completed: 2025-12-09 14:25 ————————————————————— Collected weekly regulatory samples. Completed daily lab and station check - no new issues. Added data into SharePoint. Wasted 15.04m3 from clarifier 1 and wasted 10.07m3 from clarifier 2. Added 8 bags of soda ash to hopper. Completed odour control unit inspection and filled inspection sheet. Created WO for outstanding generator room temp alarm. Filter reject sump pump 1, RSMP_PMP1 - E stop alarm came in at 2:21pm after pump ran - found breaker had tripped in MCC room. Reset breaker and cleared alarm. RSMP_PMP1 ran in duty with no issues. Will continue to monitor. ————————————————————— • Attachments: 0
12231093 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12231093 | 1 | 2025-12-11 15:08 | 2025-12-11 14:45 | Lauren Swanson (WW-WEST) @ Kleinburg Water Resource Recovery Facility - KBSPF Date Work Completed: 2025-12-11 14:45 ————————————————————— Completed daily lab and station check no new issues added data into SharePoint. Enabled batch wasting mode at 10am and set auto waste for 20m3 from 11am to 12pm. Manually wasted an extra 5m3 from clarifier 2. RAS returned to operation when wasting complete. Added 8 bags of soda ash to hopper. Cleaned rags from bar screen and confirmed operation. Manually ran filters to confirm operation and hosed filters down. Opened WAS_MV3 to sludge holding to clear interlock on WAS pumps 3 and 4 to complete monthly inspection. WAS pump 4 low on oil due to loose bolt. Tightened bolt and added extra oil. Ran pump locally and confirmed operation. Placed pump back into local off. WAS pump 3 oil level good. Ran manually and coupler seized shortly after running. Stopped pump and placed back into local off. Informed team lead of pump seizing for further investigation. Returned WAS_MV3 to close to sludge holding tank ————————————————————— • Attachments: 0
12238207 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12238207 | 1 | 2025-12-15 14:51 | 2025-12-15 14:43 | Lauren Swanson (WW-WEST) @ Kleinburg Water Resource Recovery Facility - KBSPF Date Work Completed: 2025-12-15 14:43 ————————————————————— Reset Filter Reject sump pump 1 e stop alarm and cleared, ran multiple cycles without tripping again- continuing to monitor throughout the day. Completed daily lab and station check - no new issues added data into SharePoint. Enabled batch wasting mode at 9am and set WAS to auto waste to waste 20m3 from 10am to 11am wasting 10m3 from each clarifier. Reset RAS pumps upon wasting completion. Increased soda ash dosage from 7.25seconds/h to 7.50seconds/h. Due to decreased alkalinity results in lab. Added 8 bags of soda ash to hopper, cleaned bar screen and distribution chamber stem. Inspected RSHW_BLO 1 and 2. Both have good oil levels and clean filters. Ran both to confirm operation. Cleared rags from aeration tank. Noticed leak on effluent hydrant beside aeration tank getting worse, created WO- W11516113. Released condensation from aeration tank lines. ————————————————————— • Attachments: 0
12237796 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12237796 | 1 | 2025-12-15 07:27 | 2025-12-15 07:25 | Marcus Remonde (WW-WEST) @ Kleinburg Water Resource Recovery Facility - KBSPF Date Work Completed: 2025-12-15 07:25 ————————————————————— Remotely Responded to Reject Sump Pump #1 E-Stop Alarm Communicated by the ROC. Alarm has been Recurrent and Requires Closer Maintenance Inspection. Created WO —> W11515727. Alarm Remains Outstanding. ————————————————————— • Attachments: 0 • [REMOTE ENTRY]
12255161 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12255161 | 2 | 2025-12-22 12:59 | 2025-12-22 12:56 | Lauren Swanson (WW-WEST) @ Kleinburg Water Resource Recovery Facility - KBSPF Date Work Completed: 2025-12-22 12:56 ————————————————————— Filter reject sump pump 1 e stop alarm present upon arrival, reset and cleared alarm. Filter reject sump pump 1 e stop alarm came back in at 9:51am - reset and cleared alarm - so far alarm has not come back in and has run multiple cycles. This is a known issue with a work order made, will continue to monitor. Completed daily lab and station check - no new issues. Added data into SharePoint. Auto wasted 50m3 from 10am to 1pm. WAS pumps back in manual and RAS back in operation after wasting completion. Added 9 bags of soda ash to hopper. Cleaned rags from bar screen. Bled condensation from aeration condensation line. ————————————————————— • Attachments: 0
12270779 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12270779 | 1 | 2025-12-30 13:47 | 2025-12-30 13:44 | Lauren Swanson (WW-WEST) @ Kleinburg Water Resource Recovery Facility - KBSPF Date Work Completed: 2025-12-30 13:44 ————————————————————— Collected weekly regulatory samples. Completed daily lab and station check - no new issues. Added data into SharePoint. Created WO for diversion tank lvl hihi alarm. Reset filter reject sump pump 1 e stop alarm. Enabled batch wasting at 9am and set auto waste for 20m3 from 10am to 11am. Upon wasting completion WAS pumps placed back in auto and RAS back in operation. Added 12 bags of soda ash to hopper. Cleaned bar screen. Inspected odour control unit and completed inspection form. ————————————————————— • Attachments: 0

## Humber SPS
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS
12258230 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12258230 | 2 | 2025-12-23 09:53 | 2025-12-23 09:53 | Young Jung (WW-WEST) @ Vaughan Humber Pumping Station - HMSS Date Work Completed: 2025-12-23 09:53 ————————————————————— - Pushed bin out for pickup - Checked station and recorded readings on SharePoint - Found pump 2 check valve o ring/seal leaking. Created work order - Found pump 3 check valve not fully closing. Created work order. Placed pump 3 out of service and locked out and tagged out. Fully closed inlet and discharge valve, and locked out and tagged out. - Collected weekly regulatory samples ————————————————————— • Attachments: 0
12261353 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12261353 | 1 | 2025-12-24 09:53 | 2025-12-24 09:43 | Bill Van Bakel (WW-MAINT) @ Vaughan Humber Pumping Station - HMSS Date Work Completed: 2025-12-24 09:43 ————————————————————— On site to look at check valves 2 and3. Tighten the packing on 2 and stopped the leak. Had the operators removed the locks from pump 3. Back flow is about 4 ls which does not drive the pump. The pump can be left in duty and if the back flow gets worse we will revisit it at a later date ————————————————————— • Worked With: Terry Cantwell, Gavin Walker, Young Jung • Attachments: 0
12261360 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12261360 | 1 | 2025-12-24 10:01 | 2025-12-24 10:01 | Gavin Walker (WW-WEST) @ Vaughan Humber Pumping Station - HMSS Date Work Completed: 2025-12-24 10:01 ————————————————————— Placed rag bins back inside Put pump 3 back in service and test ran it to ensure proper check valve operation Everything operating as intended ————————————————————— • Attachments: 0

## Pine Valley
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS

## Holland Landing SPS
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS

## Joe Dales SPS
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS | 1

## Keswick SPS
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS | 1
12237906 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12237906 | 1899-12-31 | 2025-12-15 09:39 | 2025-12-15 09:35 | Tyson Cornish (WW-NORTH) @ Keswick Sewage Pumping Station - KSSSQW Date Work Completed: 2025-12-15 09:35 ————————————————————— Performed facility station check Data in sharepoint Completed monthly PM work order -Heat trace inspection Equipment OOS: Odour control system ————————————————————— • Attachments: 0

## Keswick WRRF
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS
12238157 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12238157 | 1 | 2025-12-15 14:19 | 2025-12-15 14:15 | Redempto Balaga (INST) @ Keswick Water Resource Recovery Facility - KSSP Date Work Completed: 2025-12-15 14:15 ————————————————————— Assisted maintenance on relocating suction header PIT. It was lower down 191cm (18.7kPa). Adjusted the offset to compensate the new location and PIT should read -18.7 (kPa) at atmosphere. Pump 1 to 3 were completed today. Pump 1 and 2 run without any issues. Pump 3 will be running once duty is activated. No other issues encountered. ————————————————————— • Attachments: 0
12241830 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12241830 | 1 | 2025-12-16 09:49 | 2025-12-16 09:43 | Bill Van Bakel (WW-MAINT) @ Keswick Water Resource Recovery Facility - KSSP Date Work Completed: 2025-12-16 09:43 ————————————————————— On site to finish moving the pits on the back pulse line for the membranes ————————————————————— • Worked With: Redempto Balaga, Martin deVries, Satnam Mann • Attachments: 0
12241850 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12241850 | 1 | 2025-12-16 10:11 | 2025-12-16 10:09 | Redempto Balaga (INST) @ Keswick Water Resource Recovery Facility - KSSP Date Work Completed: 2025-12-16 10:09 ————————————————————— Assisted maintenance on relocating suction header PIT. It was lower down 191cm (18.7kPa). Adjusted the offset to compensate the new location and PIT should read -18.7 (kPa) at atmosphere. Pump 4 and 5 were completed and operator put it back in service. No other issues encountered. ————————————————————— • Attachments: 0

## Queensville SPS
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS

## Sutton WRRF
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS | 1
12222530 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12222530 | 3 | 2025-12-09 13:06 | 2025-12-09 13:06 | Neil Ott (WW-NORTH) @ Sutton Water Resource Recovery Facility - SUSP Date Work Completed: 2025-12-09 13:06 ————————————————————— Attended for daily operations Performed station check Completed lab and entered readings into ACE sheet Decanted sludge holding/thickening tanks and initiated transfer Collected weekly regulatory samples and delivered to Newmarket Hosed bar screen and surrounding area Rolled out headworks bins for pick up Increased filter feed max flow bias from 17 to 20 L/s Placed channel 1 UV banks in local off due to malfunctioning outlet gate, and notified ROC that the channel will be OOS tonight. ————————————————————— • Attachments: 0
12222629 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12222629 | 2 | 2025-12-09 15:16 | 2025-12-09 14:56 | Chase James (WW-NORTH) @ Sutton Water Resource Recovery Facility - SUSP Date Work Completed: 2025-12-09 14:56 ————————————————————— UV disinfection bypass at the Sutton wastewater treatment facility. Samples have been collected and delivered to 145 harry walker Cause: One of the two discharge gates malfunctioned. The issue has been identified, and gate valve will be fixed. The plant is now operating normally through UV channel 2 Time start- 09:33am stop- 09:53am Volume 24m3 MECP: Jeremy Weiss # 1-PW6YJE York region public health: Kathryn Damas # 4297300 conservation authority has been emailed ————————————————————— • Attachments: 0
12226801 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12226801 | 2 | 2025-12-10 09:02 | 2025-12-10 09:02 | Matthew Turner (WW-MAINT) @ Sutton Water Resource Recovery Facility - SUSP Date Work Completed: 2025-12-10 09:02 ————————————————————— Uv gate repair, removed actuator new nut required ————————————————————— • Worked With: Terry Cantwell • Attachments: 0
12241879 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12241879 | 1 | 2025-12-16 11:20 | 2025-12-16 11:16 | Chase James (WW-NORTH) @ Sutton Water Resource Recovery Facility - SUSP Date Work Completed: 2025-12-16 11:16 ————————————————————— Grit vortex #2 bypass gate installed due to system failure. Vortex chamber is full of grit. Pumped down and notified supervisor and team lead to get a vac truck Decant and transfer sludge Check air relief on sludge blowers Found a bracket broken on the new air compressors . Will be fixed under warranty Grease SBR decant arms Exercise gate valve Clear rags from inlet gates ————————————————————— • Attachments: 0
12245993 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12245993 | 1 | 2025-12-17 13:09 | 2025-12-17 13:06 | Bill Van Bakel (WW-MAINT) @ Sutton Water Resource Recovery Facility - SUSP Date Work Completed: 2025-12-17 13:06 ————————————————————— On site to reinstall the actuator on channel 1 UV. The electrician will come at a later date to program it ————————————————————— • Worked With: Terry Cantwell • Attachments: 0
12255236 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12255236 | 2 | 2025-12-22 14:37 | 2025-12-22 14:37 | Neil Ott (WW-NORTH) @ Sutton Water Resource Recovery Facility - SUSP Date Work Completed: 2025-12-22 14:37 ————————————————————— Attended for daily operations Performed station check Completed lab and entered readings into ACE sheet Decanted sludge thickening tank and initiated transfer while hauler took load Hosed bar screen and surrounding area Checked sand filters - mega lifted filter B3 Diverted 308 m3 combined from the three pumping stations to the lagoon from 10:19-14:05 while WESSUC cleaned grit vortexes and headworks inlet pit Kyle/Sean (electrical) were here to program UV channel 1 outlet actuator, left channel 1 UVs in local off for the night. ————————————————————— • Worked With: Chase James • Attachments: 0
12258315 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12258315 | 2 | 2025-12-23 13:35 | 2025-12-23 13:35 | Neil Ott (WW-NORTH) @ Sutton Water Resource Recovery Facility - SUSP Date Work Completed: 2025-12-23 13:35 ————————————————————— Attended for daily operations Performed station check Completed lab and entered readings into ACE sheet Decanted sludge thickening tank and initiated transfer Collected weekly regulatory samples for delivery to Newmarket Hosed bar screen and surrounding area Received alum delivery Turned off sludge holding blowers for a decant tomorrow Completed scheduled work orders and notified ROC of work being completed Performed alum drawdown tests and flushed alum line with hot water Rolled out headworks bins for pick up Completed UV rotation - tested new gate in channel 1, then returned bank 2B to service Checked sand filters - worked on mega lift repairs Consultant was here to look at air compressor bracket deficiency. ————————————————————— • Worked With: Chase James • Attachments: 0