## Aurora SPS
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS
12417378 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12417378 | 1 | 2026-02-27 13:42 | 2026-02-27 13:40 | Kevin Shaji (WW-CEAST) @ Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility - AUSSMP Date Work Completed: 2026-02-27 13:40 ————————————————————— Station check completed. See details on sharepoint. pumps 2,3,5 and 6 available in timed auto duty rotation every 3 hours. pumps 1 and 4 still oos. All standby power generators available in auto. Checked dry well. Checked screen room. ok. Bypass sampling kit inspection completed. Odour control scrubber system inspection completed. All lines except no.1 available at the dump pad for haulers to use. ————————————————————— • Attachments: 0
12413530 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12413530 | 1 | 2026-02-25 13:14 | 2026-02-25 13:11 | Kevin Shaji (WW-CEAST) @ Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility - AUSSMP Date Work Completed: 2026-02-25 13:11 ————————————————————— Station check completed. See details on sharepoint. pumps 2,3,5 and 6 available in timed auto duty rotation every 3 hours. pumps 1 and 4 still oos. All standby power generators available in auto. Checked dry well. Air compressors inspection and cleaning completed. checked bar screens. switched out rag bins. All lines except no.1 available at the dump pad for haulers to use. ————————————————————— • Attachments: 0
12410354 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12410354 | 1 | 2026-02-24 14:27 | 2026-02-24 14:23 | Bill Van Bakel (WW-MAINT) @ Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility - AUSSMP Date Work Completed: 2026-02-24 14:23 ————————————————————— On site to install the new limitork on pump 1 discharge valve. Supplier sent the wrong parts and will ship it asap ————————————————————— • Worked With: David Dougherty, Terry Cantwell, Brent Ste-Croix • Attachments: 0
12405798 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12405798 | 1 | 2026-02-23 15:18 | 2026-02-23 15:13 | Kevin Shaji (WW-CEAST) @ Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility - AUSSMP Date Work Completed: 2026-02-23 15:13 ————————————————————— Station check completed. See details on sharepoint. Pumps 2,5 & 6 available in timed auto duty rotation every 3 hours. Pump #3 discharge valve for east forcemain is tripped. Unable to clear the 'hardware failure' status on the actuator. Maintenance will check this soon. Pumps 1,3 and 4 remain oos. Checked dry well. ok checked bar screens. changed out rag bins. All lines except 1 available at the dump pad for haulers to use. ————————————————————— • Attachments: 0
12401694 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12401694 | 1 | 2026-02-20 14:25 | 2026-02-20 14:17 | David Dougherty (WW-MAINT) @ Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility - AUSSMP Date Work Completed: 2026-02-20 14:17 ————————————————————— On site to work on pump 4. Continued troubleshooting electrical problem. Checked motor cables and power wiring. Sourced replacement fuse. Was able to power up MCC with motor disconnected. Fault history in Eaton Soft Starter indicated SCR shorted fault. Suspect soft starter failure. Need to source replacement. ————————————————————— • Attachments: 0
12401482 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12401482 | 1 | 2026-02-20 11:14 | 2026-02-20 11:13 | Chris Rodie (WW-CEAST) @ Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility - AUSSMP Date Work Completed: 2026-02-20 11:13 ————————————————————— -station check of site -reviewed SCADA -entered data into sharepoint -inspected site -rotated bin in screen room -Pump 1 and 4 remain OOS -station okay ————————————————————— • Attachments: 0
12398877 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12398877 | 1 | 2026-02-19 17:16 | 2026-02-19 17:15 | Chris Rodie (WW-CEAST) @ Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility - AUSSMP Date Work Completed: 2026-02-19 17:15 ————————————————————— -on site at dump pad for line 3 valve overtorque -cleared line, valve was clogged with zip ties, a hauler keeps flushing zip ties and it is an issue -reset alarms on SCADA -line 2 and 3 available, 1 OOS for valve upgrades ————————————————————— • Attachments: 0
12398531 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12398531 | 4 | 2026-02-19 08:15 | 2026-02-19 08:14 | Philip Romito (WW-CEAST) @ Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility - AUSSMP Date Work Completed: 2026-02-19 08:14 ————————————————————— -On site to complete work orders. -Consolidated wet well inspection work order completed. -Tipping bucket operational checks completed. -Bar screen cleaning and lubrication completed. -Screw conveyor cleaning and lubrication completed. -Screw press dewatering compartment and drain line flushed. -Sluice gate valve exercises completed. -Wet well valve exercise completed. -Wet well inspection and cleaning completed. -Wet well high level alarm test completed and confirmed by ROC. -Surge tank inspection consolidated work order completed. -Surge tank and inspection completed. -Surge tank valve and actuator, exercise and inspection completed. -Surge tank drain valve inspection completed. -Transmission line flushing completed on both surge tanks. -Cleared all alarms generated from work orders. -Pumps 1 and 4 remain OOS. -Line 1 at the dump pad OOS for valve replacement. ————————————————————— • Worked With: Kevin Shaji • Attachments: 0
12393004 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12393004 | 1 | 2026-02-17 14:40 | 2026-02-17 14:38 | David Dougherty (WW-MAINT) @ Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility - AUSSMP Date Work Completed: 2026-02-17 14:38 ————————————————————— On site to troubleshoot pump 4. Found main fuses blown. Checked motor, wiring, supply and control power. Suspect winding contamination. Removed cable entry lid. Found heavy contamination. Unwired pump so mechanics can remove pump. Pump 4 is out of service. ————————————————————— • Attachments: 0
12393001 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12393001 | 1 | 2026-02-17 14:38 | 2026-02-17 14:36 | Martin deVries (WW-MAINT) @ Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility - AUSSMP Date Work Completed: 2026-02-17 14:36 ————————————————————— On site to remove pump 4 for service, remove actuator from dump pad line one, and greased pump 3 force main discharge vale ————————————————————— • Worked With: Bill Van Bakel, Christian Streef • Attachments: 0
12380473 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12380473 | 1 | 2026-02-11 10:13 | 2026-02-11 10:13 | Barry Middleton (WW-CEAST) @ Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility - AUSSMP Date Work Completed: 2026-02-11 10:13 ————————————————————— Weather today Snow and -1 Celsius -On site to complete work orders W11587339, W11586377. -Completed station check. -Entered station readings into SharePoint. -Air Compressors inspection. -Pumps 2, 3, 4, 5, and 6 available in timed auto duty rotation every 3 hours. -Pump 1 out of service due to discharge valve issue. -Standby power generators available in auto. -Checked dry well, Ok. -All lines available in auto at the dump pad for the haulers. -Checked bar screens and Rotated bin. -Cleaned bar screen room of rags and bar screen oil full. -Unclogged drain lines on screw conveyor 3. ————————————————————— • Attachments: 0
12367920 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12367920 | 3 | 2026-02-07 00:03 | 2026-02-07 04:00 | Daniel Kim (WW-CEAST) @ Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility - AUSSMP Date Work Completed: 2026-02-07 04:00 ————————————————————— On site in response to barscreen 1 overtorque alarm. Both barscreen OOS. Cleared screen 1 overtorque and attempted to run it in auto. Unit faulted out right away. Noticed rake has fallen near bottom sprocket in crooked position. Got ROC to call in Oncall CMS(Lee F) to site. Cleared overtorque for screen 2 and attempted to run it. Found rake is scratching the plate as it is travelling upwards creating loud screeching sound. Stopped the rake at the top. Lee F and I put screen 2 back in service after adjusting the position of the rake. Inlet gate to screen 2 has been open. Inlet gate to screen 1 has been closed. Notified ROC. Screen 1 OOS, screen 2 back in service ————————————————————— • Attachments: 0
12367702 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12367702 | 1 | 2026-02-06 14:35 | 2026-02-06 14:33 | Kevin Shaji (WW-CEAST) @ Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility - AUSSMP Date Work Completed: 2026-02-06 14:33 ————————————————————— Station check completed. See details on sharepoint. All pumps available in timed auto duty rotation every 3 hours except pump 1 which is OOS. Cleared pump 3 E Disc Hdr MV4 alarm on scada. All standby power generators available in auto. Checked dry well. OK. Air dryers inspection and cleaning completed. checked screen room. OK. All lines available at the dump pad for haulers to use. ————————————————————— • Attachments: 0
12361344 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12361344 | 1 | 2026-02-04 14:54 | 2026-02-04 14:53 | Kevin Shaji (WW-CEAST) @ Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility - AUSSMP Date Work Completed: 2026-02-04 14:53 ————————————————————— Station check completed. See details on sharepoint. All pumps available in timed auto duty rotation every 3 hours except pump 1 which is OOS due to discharge valve issue All standby power generators available in auto. Checked dry well. Air compressors inspection and cleaning completed. JHSC Health and Safety Inspection completed. checked bar screens. Bar Screen Bin Removal and Replacement All lines available at the dump pad for haulers to use. ————————————————————— • Attachments: 0
12353500 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12353500 | 1 | 2026-02-02 16:04 | 2026-02-02 16:04 | Kevin Shaji (WW-CEAST) @ Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility - AUSSMP Date Work Completed: 2026-02-02 16:04 ————————————————————— Station check completed. See details on sharepoint. All pumps available in timed auto duty rotation every 3 hours except pump 1 which is OOS due to discharge valve issue All standby power generators available in auto. Hazardous Waste Collection and Removal Checked dry well. Checked bar screens. switched out rag bin. Added oil on the reservoir tank. All lines available at the dump pad for haulers to use. ————————————————————— • Attachments: 0

## Leslie SPS
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS
12417214 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12417214 | 2 | 2026-02-27 09:24 | 2026-02-27 09:23 | Chris Rodie (WW-CEAST) @ Markham Leslie Pumping Station - LSSS Date Work Completed: 2026-02-27 09:23 ————————————————————— -station check of site -reviewed SCADA -inspected site -entered data into SharePoint -rotated bins in screen room -pump 1 OOS, fault alarm, Fault 47 Stack Overtemp, notifying maintenance, WO already created, will add to it -5 pumps available in auto -station okay ————————————————————— • Attachments: 0
12414863 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12414863 | 3 | 2026-02-26 10:18 | 2026-02-26 10:16 | Chris Rodie (WW-CEAST) @ Markham Leslie Pumping Station - LSSS Date Work Completed: 2026-02-26 10:16 ————————————————————— -on site for Housekeeping, cleaning up garbage around site on various floors -running pump 1 in auto duty 1, if it trips on bearing high temp, or another alarm, WO will be created, ongoing issues with pump 1 -completed alarm investigation -W11692845- Leslie Pump 1 High Bearing Temp Alarm created -station okay, only 5 pumps in auto/duty rotation, pump 1 OOS ————————————————————— • Attachments: 0
12414863 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12414863 | 3 | 2026-02-26 10:18 | 2026-02-26 10:16 | Chris Rodie (WW-CEAST) @ Markham Leslie Pumping Station - LSSS Date Work Completed: 2026-02-26 10:16 ————————————————————— -on site for Housekeeping, cleaning up garbage around site on various floors -running pump 1 in auto duty 1, if it trips on bearing high temp, or another alarm, WO will be created, ongoing issues with pump 1 -completed alarm investigation -W11692845- Leslie Pump 1 High Bearing Temp Alarm created -station okay, only 5 pumps in auto/duty rotation, pump 1 OOS ————————————————————— • Attachments: 0
12410278 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12410278 | 1 | 2026-02-24 12:38 | 2026-02-24 12:35 | Chris Rodie (WW-CEAST) @ Markham Leslie Pumping Station - LSSS Date Work Completed: 2026-02-24 12:35 ————————————————————— -ran pump 1 with maintenance, upper bearing on pump is overheating -pump is manual off but available if needed to run -wet well consolidated work order completed -pump 2 was put OOS for the seal water, but back online before end of day -all 6 pumps can run, but pump 1 is manual off for the night, but available if needed -station okay ————————————————————— • Attachments: 0
12405605 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12405605 | 1 | 2026-02-23 11:45 | 2026-02-23 11:40 | Kevin Shaji (WW-CEAST) @ Markham Leslie Pumping Station - LSSS Date Work Completed: 2026-02-23 11:40 ————————————————————— Station Check completed (See details on SharePoint). Checked drywell. cleaned dry well area Checked screen room, changed out rag bin. Cleaned/hose down screen room. Switched pumps duty to timed mode from all-stop. Pumps 3, 4, 5, and 6 available in timed-auto duty rotation every 4 hours. pump 1 faulted on 'stack overtemp' alarm. cleared the alarm. pump 2 seal water line has a pinhole leak. created work request W11683392 for maintenance to fix. Pump 1 & 2 taken oos. All standby power generators available in auto. Drained condensates from the surge tanks air compressors. ————————————————————— • Attachments: 0
12401352 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12401352 | 2 | 2026-02-20 08:30 | 2026-02-20 08:29 | Chris Rodie (WW-CEAST) @ Markham Leslie Pumping Station - LSSS Date Work Completed: 2026-02-20 08:29 ————————————————————— -station check of site -reviewed SCADA -entered data into sharepoint -inspected site -rotated bins in screen room -pump 1 locked out late wednesday afternoon on a high bearing temp alarm, it was left off and OOS. Reset alarm on pump today and returned pump 1 back to auto duty rotation. All 6 pumps available. If pump 1 overheats again, we will leave it OOS for the weekend and get mechanical to investigate. Cleaned the screen on the seal water system, and opened the valve all the way to get as much seal water to pump 1 as possible. Will see if this helps. -station okay ————————————————————— • Attachments: 0
12380517 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12380517 | 2 | 2026-02-11 10:23 | 2026-02-11 10:20 | Chris Rodie (WW-CEAST) @ Markham Leslie Pumping Station - LSSS Date Work Completed: 2026-02-11 10:20 ————————————————————— -station check of site -entered data into sharepoint -inspected site -reviewed SCADA -notified ROC of work being performed -WAJAX on site for generator maintenance -YR maintenance and electrical on site for pump 1 repairs -generators started at 11:58 Generator 1: Start Hours:230.24 Stop Hours:231.42 Generator 2: Start Hours:117.40 Stop Hours:119.35 Generator 3: Start Hours:103.59 Stop Hours:105.54 Bulk Fuel Tank Start: 23,437L Fuel Stop: 22,572L -generator 1 went into shutdown due to low oil level, topped up oil, reset alarms, put generator 1 back to auto, generator started up and ran for remainder of 1 hour test run, sync/load shared with other generators Generator Run Time: 1.95 hrs -generators off at 13:52 -test successful, back on utility power, reset alarms -pump 1 remains OOS -all other pumps in auto and reset -Generator 1-3 Monthly Test Run -Hazard Waste Removal-no hazardous waste -Leslie Scrubber Inspection -bin replacement/screen room inspection -station okay ————————————————————— • Attachments: 0
12376292 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12376292 | 4 | 2026-02-10 13:57 | 2026-02-10 10:00 | Philip Romito (WW-CEAST) @ Markham Leslie Pumping Station - LSSS Date Work Completed: 2026-02-10 10:00 ————————————————————— -On site to complete work orders. -Completed consolidated monthly dry well pump floor inspection work order. -Sump pit inspection completed. Tested Sump Level HiHi Alarm and confirmed with ROC. -Dry well flood alarm does not exist at this site, tested sump level HiHi in its place. -High low temp alarm does not exist at this site, temperatures tracked on BAS site. -BAS check completed. -Auto dialer test completed and confirmed with ROC. -Air compressor inspection completed, checked belts, oil, filters. -Seal water strainer checks completed. -Pump 1 OOS. -Pump 6 in auto duty rotation, but discharge valve is leaking, issue already reported to maintenance team. -Bar Screen 2 fault came in at 0928 this morning, reset fault and test ran screen for multiple cycles with no issues. Left bar screen 2 running in auto. Topped up oil on both bar screens. -RS Pump and Motor Inspection completed: -Pump 1 OOS -Pump 2: 1710L/s at 100% speed. -Pump 3: 1300L/s. -Pump 4: 1290L/s. -Pump 5: 1570L/s at 100% speed. -Pump 6: 1190L/s. -Check valve inspections completed. -Air relief valve inspections completed. ————————————————————— • Attachments: 0
12371998 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12371998 | 1 | 2026-02-09 09:55 | 2026-02-09 09:54 | Barry Middleton (WW-CEAST) @ Markham Leslie Pumping Station - LSSS Date Work Completed: 2026-02-09 09:54 ————————————————————— Weather today Clear and -16 Celsius -On site to complete work orders W11579343. -Completed station check. -Entered station readings into SharePoint. -Pumps 2, 3, 4, 5, and 6 available in timed-auto duty rotation every 4 hours. -Pumps 1 out of service. -All standby power generators available in auto. -Switched sump pump duty. -Drained condensates from the surge tanks air compressors. -Checked dry well, ok. -Checked bar screens. Switched rag bin. Cleaned/hosed down bar screen room. ————————————————————— • Attachments: 0

## Bogart SPS
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS
12383951 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12383951 | 1900-01-01 | 2026-02-12 08:01 | 2026-02-12 08:01 | Philip Romito (WW-CEAST) @ Newmarket Bogart Creek Sewage Pumping Station - NMSSHS Date Work Completed: 2026-02-12 08:01 ————————————————————— -On site to complete work orders. -Completed comprehensive housekeeping tasks. -Found outlet air line for OCU has completely torn off unit. Work request created. ————————————————————— • Attachments: 0

## Newmarket SPS
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS
12413346 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12413346 | 1899-12-31 | 2026-02-25 09:44 | 2026-02-25 09:42 | Kevin Shaji (WW-CEAST) @ Newmarket Sewage Pumping Station & Equalization Tank - NMSSBP Date Work Completed: 2026-02-25 09:42 ————————————————————— Station Check completed (See details on SharePoint). All pumps available in auto duty rotation. Standby power generator available in auto. Checked dry well, ok. checked screen room. Placed the bar screen bin outside for removal. Bar screen 2 put back to service after maintenance worked on the over-torque fault. Air compressors inspection and cleaning completed. ————————————————————— • Attachments: 0 | 1
12410524 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12410524 | 1899-12-31 | 2026-02-25 03:24 | 2026-02-25 03:22 | Chris Rodie (WW-CEAST) @ Newmarket Sewage Pumping Station & Equalization Tank - NMSSBP Date Work Completed: 2026-02-25 03:22 ————————————————————— -on site for bar screen 1 overtorque, reset bar screen, watched it travel, no issues, over torque occurs upon flinging rags, bar screen 1 back in service -bar screen 2 overtorque, screen 2 remains OOS with inlet gate closed, cannot be reset, WO created for maintenance ————————————————————— • Attachments: 0
12410185 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12410185 | 1899-12-31 | 2026-02-24 11:02 | 2026-02-23 13:30 | Terry Reed (WW-CEAST) @ Newmarket Sewage Pumping Station & Equalization Tank - NMSSBP Date Work Completed: 2026-02-23 13:30 ————————————————————— Took station readings and entered into Sharepoint - reviewed trends - all good, levelled out bin in the screening room and bar screen 2 is OOS - not sure why (Chris) . Checked pump floor - all good . Emptied all the garbage and swept and mopped out both the office and the washroom. Station running under normal ops - just bar screen 2 OOS - I will find out more tomorrow. ————————————————————— • Attachments: 0
12368017 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12368017 | 1900-01-02 | 2026-02-07 14:40 | 2026-02-07 14:39 | Daniel Kim (WW-CEAST) @ Newmarket Sewage Pumping Station & Equalization Tank - NMSSBP Date Work Completed: 2026-02-07 14:39 ————————————————————— On site in response to mech screen 2 overtorque. Cleared the alarm and ran the screen on hand, noticed rake was slightly to the left touching the plate as it is moving upwards. Called ROC to call in 2nd Ops to close the inlet gate to screen 2 Marcus R on site to assist. Closed inlet gate to screen 2 and put both inlet gates 1 and 2 in remote to be able to operate it remotely without entering wet well. Notified ROC Screen 2 placed OOS, Screen 1 operating as intended. ————————————————————— • Attachments: 0

## Mt. Albert WRRF
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS
12414982 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12414982 | 1900-01-01 | 2026-02-26 12:38 | 2026-02-26 07:30 | Terry Reed (WW-CEAST) @ Mount Albert Water Resource Recovery Facility - MTSP Date Work Completed: 2026-02-26 07:30 ————————————————————— Put two bags of soda ash into the aeration tanks and set two up for later,, started de-cant pump and collected the comp samples from yesterdays samples and delivered them to Harry Walker. completed Lab work and wasted 10m3 and added 4 bags of soda ash in total. leaned out post aeration tank and the entry flow gates and also washed down the UV channel. Went through the station sand filters working well, Bar screen just went OOS (flowing through by pass bar screen) I have put in a WO for maintenance. OC unit is still OOS. ————————————————————— • Attachments: 0
12410344 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12410344 | 1900-01-03 | 2026-02-24 14:21 | 2026-02-24 08:15 | Terry Reed (WW-CEAST) @ Mount Albert Water Resource Recovery Facility - MTSP Date Work Completed: 2026-02-24 08:15 ————————————————————— Put two bags in and set two bags up to put in later, and started de-cant pump. Flushed both sand filter reject lines also checked both clarifiers - oil level OK,I did NOT drain the water as I did that 2 weeks ago - same for the greasing. Went through the station - sand filters working good. The OC unit is still OOS put station is running under normal ops. ————————————————————— • Worked With: Marcos Tungcol • Attachments: 0
12408727 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12408727 | 1900-01-01 | 2026-02-24 09:19 | 2026-02-23 08:10 | Terry Reed (WW-CEAST) @ Mount Albert Water Resource Recovery Facility - MTSP Date Work Completed: 2026-02-23 08:10 ————————————————————— Shut off de-cant pump and emptied thickening tank into holding tank. Put two bags of soda ash into the aeration tanks and set up two for later. Pushed bin out for pick up and cleaned around the gates and also the post aeration tank - not much at all in the tank. Checked sand filter operation - all good. Station running under normal ops - no new issues were found , OC is still OOS ————————————————————— • Worked With: Marcos Tungcol • Attachments: 0
12398675 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12398675 | 1900-01-01 | 2026-02-19 12:10 | 2026-02-17 08:15 | Terry Reed (WW-CEAST) @ Mount Albert Water Resource Recovery Facility - MTSP Date Work Completed: 2026-02-17 08:15 ————————————————————— Put 2 bags of soda ash into the aeration tanks and set the next two up,, started the de-cant pump. went through the station - sand filters working good and i washed down the clarifiers scum trough. Cleaned out the post aeration tank and also the gates of the aeration inlet. Station running under normal ops - no issues were observed. Odour Control is still OOS. ————————————————————— • Attachments: 0
12384095 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12384095 | 1900-01-02 | 2026-02-12 11:58 | 2026-02-12 08:00 | Terry Reed (WW-CEAST) @ Mount Albert Water Resource Recovery Facility - MTSP Date Work Completed: 2026-02-12 08:00 ————————————————————— Dropped in 2 bags of soda ash and set up 2 other bags for the aeration tanks also started de-cant pump. Started the Lab and sludge processing and entered results from the Lab into Sharepoint. Wasted 20m3 today and went through the Head works building - greased the travelling bar screen and cleaned out the back plate. Checked the vortex and both are turning. OC unit is still OOS. ————————————————————— • Attachments: 0
12380809 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12380809 | 1899-12-31 | 2026-02-11 12:14 | 2026-02-11 08:00 | Terry Reed (WW-CEAST) @ Mount Albert Water Resource Recovery Facility - MTSP Date Work Completed: 2026-02-11 08:00 ————————————————————— Dumped two bags of soda ash into the aeration tank and set up the next two for later,, started de-cant pump and also collected weekly samples for the Lab,, Delivered samples to Harry Walker after collecting the samples at Mt. Albert PS. Back from drop off of the samples and checked all the cranes - all good and working. Went through the station and just the OC unit is still OOS. Rest of the station is running fine. ————————————————————— • Attachments: 0
12380806 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12380806 | 1899-12-31 | 2026-02-11 11:57 | 2026-02-10 08:20 | Terry Reed (WW-CEAST) @ Mount Albert Water Resource Recovery Facility - MTSP Date Work Completed: 2026-02-10 08:20 ————————————————————— Dumped 2 bags of soda ash intro the aeration tanks and set 2 up for later,, also started the de-cant pump. Went through the station - sand filters working great , set up hose and flushed both reject lines. checked blower room - all looks good and the air compressors as well. Station running under normal ops - no issues were found, OC unit is still OOS ————————————————————— • Attachments: 0
12367521 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12367521 | 1900-01-01 | 2026-02-06 12:02 | 2026-02-06 08:00 | Terry Reed (WW-CEAST) @ Mount Albert Water Resource Recovery Facility - MTSP Date Work Completed: 2026-02-06 08:00 ————————————————————— Completed Lab work and sludge processing,, entered results from the Lab into Sharepoint. Did not waste today and added 4 bags of soda ash. Had Alum delivery today (16000L) and Orlando to pick up the sludge. Went through the station - sand filters are working good and RAZ pumps have good flow. OC unit is still OOS, ————————————————————— • Attachments: 0
12365074 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12365074 | 2 | 2026-02-05 14:21 | 2026-02-05 11:00 | Terry Reed (WW-CEAST) @ Mount Albert Water Resource Recovery Facility - MTSP Date Work Completed: 2026-02-05 11:00 ————————————————————— came to the plant and set up the soda ash and turned the de-cant pump on for Marcos,, went to the pumping station and back at 11,, cleaned out the post aeration tank and also the inlet channel gates as well,, went through the station and everything is running fine. OC unit is still OOS though. ————————————————————— • Attachments: 0
12361255 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12361255 | 3 | 2026-02-04 12:37 | 2026-02-04 08:10 | Terry Reed (WW-CEAST) @ Mount Albert Water Resource Recovery Facility - MTSP Date Work Completed: 2026-02-04 08:10 ————————————————————— Set up soda ash - put 2 bags in and 2 set up and waiting,, started de-cant pump and collected weekly samples for the Lab. After dropping off samples cleaned the scum trough - hosed it down till ice was gone. Went through the station and all looks good - Odour Control is still OOS but everything else looks good. ————————————————————— • Worked With: Marcos Tungcol • Attachments: 0
12349187 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12349187 | 2 | 2026-02-01 10:00 | 2026-02-01 10:00 | Philip Romito (WW-CEAST) @ Mount Albert Water Resource Recovery Facility - MTSP Date Work Completed: 2026-02-01 10:00 ————————————————————— -On site for lab analysis and sludge handling work. -Entered lab results into SharePoint. -Decanted STT to headworks, then emptied tank into SHT. -Added two bags of soda ash to each aeration tank. -Batch wasted 10m3, ran RAS pumps at 100% speed when returning to service. -Verified alum dosing and sand filter operation. -OCU remains OOS. ————————————————————— • Attachments: 0

## King City SPS
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS

## Black Creek SPS
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS
12367578 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12367578 | 1 | 2026-02-06 13:11 | 2026-02-06 13:09 | Lauren Swanson (WW-WEST) @ Vaughan Black Creek Pumping Station - BLSS Date Work Completed: 2026-02-06 13:09 ————————————————————— Onsite for station check - no new issues reviewed trends and added data into SharePoint. Completed weekly RS pump run test - no new issues Pump1 -573.1L/s at 297kPa Pump 2 - 453.2 L/s at 100% at 262kPA Pump 3 131.3L/s at 100% and 215kPA Pump4 - 460.3 L/s at 100% at 265kPA Pump 5 -OOS pumps placed back into Auto and put in duty. Pump 5 remains in manual OOS Inspected seal water and cleaned screens - all clear and functioning. ————————————————————— • Attachments: 0
12376670 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12376670 | 2 | 2026-02-11 01:34 | 2026-02-11 01:45 | David Dougherty (WW-MAINT) @ Vaughan Black Creek Pumping Station - BLSS Date Work Completed: 2026-02-11 01:45 ————————————————————— On site to troubleshoot disconnect switch for South Force Main Valve MV-11. Disconnect switch in internally corroded. Lubricated to allow the disconnect to close again. Tested disconnect function. Ok. Should be replace in the near future. ————————————————————— • Attachments: 0
12401550 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12401550 | 1 | 2026-02-20 11:44 | 2026-02-20 11:44 | Young Jung (WW-WEST) @ Vaughan Black Creek Pumping Station - BLSS Date Work Completed: 2026-02-20 11:44 ————————————————————— - Checked screen, oil is good. Levelled bin - Pushed bin back in - Performed weekly pump test. Ran each pumps 1-4 manually, one at a time, and recorded readings. Check valve for pump 3 not closing. Work order already created. Pump 5 OOS Pump 1: 570.2 L/s, pressure 305 kPa Pump 2: 450 L/s at 100%, pressure 267 kPa Pump 3: 132.4 L/s at 100% speed, pressure 214 kPa Pump 4: 466 L/s at 100% speed, pressure 265 kPa - Checked station and recorded readings on SharePoint. Trends okay. Noticed high vibration on pump 1. Will monitor ————————————————————— • Attachments: 0

## Nobleton WRRF
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS

## Schomberg WRRF
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS
12353462 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12353462 | 1 | 2026-02-02 15:17 | 2026-02-02 15:13 | David Dougherty (WW-MAINT) @ Schomberg Water Resource Recovery Facility - SHSP Date Work Completed: 2026-02-02 15:13 ————————————————————— On site to continue work on effluent pump 3. Effluent pump 3 is still out of service. ————————————————————— • Attachments: 0 | Resolved last month meeting - In Auto, stopped status on SCADA
12405570 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12405570 | 3 | 2026-02-23 11:11 | 2026-02-23 11:04 | Lance Johnson (LEADS) @ Schomberg Water Resource Recovery Facility - SHSP Date Work Completed: 2026-02-23 11:04 ————————————————————— Supernated STT and released to SHT. Completed labs and entered data in ace sheets. Completed station check. UV bank b, rack 7 not lighting up and causing alarm. Problem with power at the socket for rack 7. Created W11693400. Cleaned blower building. Cleaned UV/FE channel. ————————————————————— • Attachments: 0

## Kleinburg WRRF
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS
12353403 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12353403 | 1 | 2026-02-02 14:14 | 2026-02-02 14:11 | Terry Cantwell (WW-MAINT) @ Kleinburg Water Resource Recovery Facility - KBSPF Date Work Completed: 2026-02-02 14:11 ————————————————————— On site for high fuel temperature alarm. Fuel system is cool. Cleared alarm 263. Unplugged sensor to confirm location of sensor. Alarm 263 came back in. Test ran generator okay Fuel was not overheating. Will order a fuel temperature sensor to replace. ————————————————————— • Worked With: Lauren Swanson, Marcus Remonde • Attachments: 0

## Pine Valley
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS
12376133 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12376133 | 1 | 2026-02-10 11:46 | 2026-02-10 11:44 | Young Jung (WW-WEST) @ Vaughan Humber Pumping Station - HMSS Date Work Completed: 2026-02-10 11:44 ————————————————————— Checked station and trends, and recorded readings on SharePoint. Levelled bin and pushed bin out for pick up. Salted in front of the screen door Created a work order to address no power and no audible alarm on RFLM-1 diesel tank fill monitor ————————————————————— • Attachments: 0

## Humber SPS
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS

## Holland Landing SPS
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS

## Joe Dales SPS
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS | 1

## Keswick SPS
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS
12405563 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12405563 | 1900-01-01 | 2026-02-23 10:52 | 2026-02-23 10:52 | Darren Boddy (WW-NORTH) @ Keswick Sewage Pumping Station - KSSSQW Date Work Completed: 2026-02-23 10:52 ————————————————————— station checks sharepoint data entry OCU oos (warranty) ————————————————————— • Attachments: 0
12384149 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12384149 | 2 | 2026-02-12 13:42 | 2026-02-12 13:41 | Darren Boddy (WW-NORTH) @ Keswick Sewage Pumping Station - KSSSQW Date Work Completed: 2026-02-12 13:41 ————————————————————— station checks sharepoint data entry OCU oos (warranty) ————————————————————— • Attachments: 0

## Queensville SPS
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS
12353083 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12353083 | 1 | 2026-02-02 10:41 | 2026-02-02 10:41 | Tyson Cornish (WW-NORTH) @ Queensville West Sewage Pumping Station - QVSSSC Date Work Completed: 2026-02-02 10:41 ————————————————————— Performed facility station check Data in sharepoint Equipment OOS: Channel grinder ————————————————————— • Attachments: 0
12372116 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12372116 | 3 | 2026-02-09 11:32 | 2026-02-09 11:31 | Darren Boddy (WW-NORTH) @ Queensville West Sewage Pumping Station - QVSSSC Date Work Completed: 2026-02-09 11:31 ————————————————————— on site 1115hrs unable to time in on site, keeps requesting to time out, even though its timed out. station checks health and safety checks. ocu inspection, property services was on site. Heater in OCU room broken, property services looking for a new one to install. channel grinder oos. ————————————————————— • Attachments: 0 • [REMOTE ENTRY]
12376290 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12376290 | 1 | 2026-02-10 13:52 | 2026-02-10 13:52 | Tyson Cornish (WW-NORTH) @ Queensville West Sewage Pumping Station - QVSSSC Date Work Completed: 2026-02-10 13:52 ————————————————————— On site responding to Generator fault & LIT 3/4 OOR -Upon arrival, there was no power at the facility but the ATS panel was indicating we were connected to utility power with 600 V on each phase. Switched power to generator power but still the same issue. Although I was able to run a pump in local. -Appears there was a power blip which briefly caused the generator to start. The generator breaker tripped, along with MCC "Panel AA". The tripped MCC Panel AA was the culprit- once breaker was reset, facility power resumed and facility was operating normally. -It was found that the "duct heater"(1, 3, & 5) breaker in "distribution panel AA", was tripped and resetting this caused it to immediately trip again, subsequently tripping MCC "Panel AA". Work order for property services to address this issue will be created. -WWEL_LIT2 (wet well 1 hydrostatic level) began reading OOR once the other issue resolved. Instrumentation will respond to site to correct the issue. Equipment OOS: channel grinder and wet well 1 hydrostatic level ————————————————————— • Attachments: 0
12384078 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12384078 | 3 | 2026-02-12 11:31 | 2026-02-12 11:28 | Tyson Cornish (WW-NORTH) @ Queensville West Sewage Pumping Station - QVSSSC Date Work Completed: 2026-02-12 11:28 ————————————————————— Performed facility station check Data in sharepoint On site to provide operational support for CPD performing pump vibration testing. Placed pumps in manual to increase the wet well level. Ran each pump in local at 52, 56, and 60 Hz separately and running together. Placed facility back to auto and observed normal operation. Equipment OOS: Channel grinder and WW1 hydrostatic transmitter ————————————————————— • Attachments: 0
12413452 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12413452 | 1 | 2026-02-25 11:36 | 2026-02-25 11:35 | David Dougherty (WW-MAINT) @ Queensville West Sewage Pumping Station - QVSSSC Date Work Completed: 2026-02-25 11:35 ————————————————————— On site to assist with replacement channel grinder, reconnection and testing. Channel grinder back in service. ————————————————————— • Worked With: Satnam Mann • Attachments: 0

## Sutton WRRF
1