## Aurora SPS
WW-CEAST | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-03-02 | -station check of site -reviewed SCADA -inspected site -entered data into sharepoint -pump 1 and 4 are OOS, 4 pumps available -station okay | 0.99994 | 1 | 1
WW-CEAST | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-03-03 | -on site for monthly work orders -Aurora SPS Consolidated Wetwell and Outfall Inspection -Monthly Surge Tank Inspection -Aurora EQ Tipping Bucket Test -outfall is okay, creek is well below duckbill -pump 1 was tested from the request of maintenance, leakage alarm came in, pump 1 is manual off, duty 7 -pump 4 is OOS -4 pumps available -Housekeeping of site, cleaned up garbage on all levels -station okay | 1 | 1 | 1
WW-CEAST | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-03-04 | -station check of site -reviewed SCADA -entered data into SharePoint -inspected site -rotated bin in screen room -pumps 1 and 4 manual off, duty 7, maintenance working on them -on site for monthly work orders -Air Compressor Inspection -Air Dryer Inspection -JHSC Inspection -bins out for pickup, cleaned screen room -pump 1 back to auto duty 1, running with no issues -5 pumps available in auto, pump 4 OOS -backflushed line 2 at dump pad, cleared alarm, back to available -station okay | 1 | 1 | 1
WW-CEAST | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-03-18 | -On site to complete work orders. -Alectra on site for hydro meter replacement. Discovered meter due for replacement was for solar power, so no disruption to station power is needed. -0855 - Transferred station to generator power. -Upon transfer to generator power, Generator 3 fuel filter primer cap blew out of the filter causing diesel fuel to spill onto ground. Immediately stopped Generator 3 and used absorbent pads to contain and clean up fuel spill. -0956 - Transferred site back to utility power. -Monthly diesel generator test run completed, readings entered into SharePoint. -Generator 1: Start: 629.3hrs, Stop: 630.4hrs, Run time: 1.1hrs. -Generator 2: Start: 621.5hrs, Stop: 622.6hrs, Run time: 1.1hrs. -Generator 3: Start: 825.3hrs, Stop 825.3hrs. -Generator 3 OOS until repairs can be made. -Station check completed, readings entered into SharePoint. -Checked drywell. -Air compressors, inspection and cleaning completed. -Checked screen room, changed out rag bin, bar screen oil topped up. -Bar screen rag bin removal completed, bins out for pick up. -Pump 4 OOS, Generator 3 OOS. | 1 | 1 | 1
WW-CEAST | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-03-20 | -station check of site -reviewed SCADA -inspected site -entered data into sharepoint -cleaned screen room, rotated bin as necessary -inspected generator 3, back to auto/available -station okay | 0.0013622 | 0 | 0
WW-CEAST | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-03-23 | -station check of site -reviewed SCADA -inspected site -entered data into SharePoint -rotated bin in screen room, cleaned screen room -reset pump 1 for discharge valve fault -pump 4 remains OOS, 5 pumps available -locked out and tagged out East Forcemain for gravity sewer cleaning south of Bloomington: all 6 pumps east discharge valves are in local stop, east surge tanks valve are closed and depowered, East forcemain common discharge valve is local closed, and depowered, ISS east discharge valve is local closed, in local stop -setpoints on SCADA show East is not in service, west forcemain is manually selected as in service -notified ROC and CEWW of East Forcemain OOS -station okay | 1 | 1 | 1
WW-CEAST | Aurora Sewage Pumping Station, Equalization Tank & Hauled Waste Receiving Facility | 2026-03-30 | -On site to perform a station check. -Entered station readings into SharePoint. -Checked drywell. -Checked screen room, raked rag bin, bar screen oil topped up, cleaned rags off conveyors and floor. -Pump 4 OOS. | 0.99942 | 1 | 1

## Leslie SPS
WW-CEAST | Markham Leslie Pumping Station | 2026-03-02 | -On site to complete work orders. -Station check completed, readings entered into SharePoint. -Reset Earth Fault on AHU1. -Reset Fault 47, Stack Overtemp Fault on Pump 1. -Test ran Pump 1 in auto, duty 1. Pump 1 ran for just under two hours before faulting again. Fault 47, Overtemp Fault back on Pump 1 MCC panel and SCADA is showing Fault Alarm, Motor/Bearing High Temp Alarm, and Motor/Bearing High Temp Trip Alarm. -Left Pump 1 in manual off, OOS for the night. -Hoist inspections completed on site, no issues noted. -Checked screen room, flushed screw press drain lines, replaced bins, cleaned floor in screen room. -Pump 1 OOS. | 1 | 1 | 1
WW-CEAST | Markham Leslie Pumping Station | 2026-03-04 | -On site to complete work orders. -Station check completed, readings entered into SharePoint. -Checked screen room, changed out rag bin, hosed down floor, repositioned screw press to better align with floor drain. -Bar screen bin removal completed. -Monthly diesel generator test run completed, readings entered into SharePoint. -1058 - Transferred site to generator power. -1241 - Transferred site back to utility power. -Gen. 1: Start hours: 231:42, Stop hours: 233:41, Run time: 1hr, 59min. -Gen. 2: Start hours: 119:35, Stop hours: 121:33, Run time: 1hr, 58min. -Gen. 3: Start hours: 105:54, Stop hours: 107:52, Run time: 1hr, 58min. -Hazardous waste collection and removal completed. -Overflow kit inspection completed. -Ran Pump 1 in auto, duty 1. Pump ran from 12:55-1450 before faulting again on Motor/Bearing High Temp Alarms. Left pump faulted and OOS for the night. -Pump 5 OOS with VFD Fault following generator testing. Work request created for issue. | 1 | 1 | 1
WW-CEAST | Markham Leslie Pumping Station | 2026-03-06 | -On site to complete work orders. -Station check completed, readings entered into SharePoint. -Checked screen room, changed out rag bin, flushed screw press drain lines, replaced bins following pick up. -Monthly JHSC H&S inspection completed, no issues noted. -Consolidated Dry Well Pump Floor Inspection completed. -RS pump & motor inspection completed. -Pump 1: 1310L/s. -Pump 2: 975L/s at 0% speed, 1230L/s at 25%, 1460L/s at 50%, 1860L/s at 100%. -Pump 3: 1310L/s. -Pump 4: 1290L/s. -Pump 5 OOS. -Pump 6: 1165L/s. -Check valve inspections completed. -Sump pit inspection completed. -Dry well flood alarm completed, Sump High High Level Alarm confirmed by ROC. -Air relief valve inspection completed. -Seal water strainer inspection completed. -Air compressor inspection completed. -BAS check completed. -Ran Pump 1 in auto duty 1 again until it failed again on Motor/Bearing High Temp Alarm. -Pumps 1 and 5 remain OOS. | 1 | 1 | 1
WW-CEAST | Markham Leslie Pumping Station | 2026-03-09 | -On site to complete work orders. -Washed Bayview Steeles OCF mist eliminator filters in screen room and left filters out to dry. -Checked screen room, changed out rag bin, flushed screw press drain lines, hosed down floor. -Odour control scrubber system inspection completed. Inspected filters, greased fan shaft in screen room OCU. -Station check completed, readings entered into SharePoint. -Bypass sampling kit inspection completed. -Ran Pump 1 in auto, duty 1 until Motor/Bearing High Temp Alarms came back in. -At 1132, Generator 3 Warning Alarm and Generator 3 DGC Not in Auto Alarm came in. Inspected Generator 3, found generator screen/panel blank, appears as though their is no power to Gen. 3 panel. Unable to reset alarms locally on generator or at GMCP panel. Work request created for issue. -Pump 1 and 5 OOS, Generator 3 OOS. | 1 | 1 | 1
WW-CEAST | Markham Leslie Pumping Station | 2026-03-10 | On site to check pump 5 VFD. Found auxiliary power fault. Was able to reset fault. Suspect it happened during power transfer last week. Operations tested pump 5 in manual. Pump is working ok. Pump 5 back in auto duty rotation. Also onsite to check generator 3. Local control panel screen was off. Found loose fuse holder on front of panel. Repaired. Screen is back on. No more issues. | 1 | 1 | 1
WW-CEAST | Markham Leslie Pumping Station | 2026-03-25 | -On site to perform a station check. -Entered station readings into SharePoint. -Checked drywell, drained condensate from air compressor tanks. -Ran Pump 1 in auto, duty 1 until pump faulted again. -Pump 1 remains OOS. -Rag bins placed out for pickup. | 0.99999 | 1 | 1
WW-CEAST | Markham Leslie Pumping Station | 2026-03-27 | -On site to perform a station check. -Entered station readings into SharePoint. -Checked drywell. -Reset fault on Pump 1 and test run pump for maintenance team. -Checked screen room, changed out rag bin for the weekend, replaced bins following pick up, flushed screw press drain lines, bar screen oil topped up. -Assisted maintenance team with pump testing and maintenance activities. -Pump 1 is currently still running, but if it faults again it will remain OOS for the weekend. | 0.99999 | 1 | 1

## Newmarket SPS
WW-CEAST | Newmarket Sewage Pumping Station & Equalization Tank | 2026-03-19 | On site to perform pm on air compressors. Changed oil and checked air filters. Inspected bar screens found barscreen #2 out of alignment when travelling over top sprockets. Found top drive sprocket key and key way worn. Removed and ordered parts. Waiting for parts to install. | 0.0091628 | 0 | 0
WW-CEAST | Newmarket Sewage Pumping Station & Equalization Tank | 2026-03-31 | @8:25 - Placed pumps 1 and 3 OOS in manual off to leave 2 other pumps running in auto and in manual speed of 30% to slow down flow to Aurora SPS. | 0.99969 | 1 | 1

## Mt. Albert SPS
WW-CEAST | Mount Albert Pumping Station | 2026-03-31 | -On site to respond to communications failure alarm reported by ROC. PCS on-call has also been notified and is on route to site. -0405 - Upon arrival to site, swipe card reader not working, local SCADA OIT panel is blank and not working, Pumps both displaying No Communication faults on panels. Wet well level is at 4.08m. Tried resetting pump faults on local panel, but pumps will not run in remote or local. Wet well backup mode is in Auto, but pumps not running. -Called on-call electrician, tried cycling power to pumps, but still not working. Tried disconnecting power for 5-10min, but pumps still not working when turned back on. On-call electrician on route to site. -0431 - Contacted ROC to initiate emergency vac truck procedure and have trucks dispatched to site. -Tried transferring site to generator power, suspecting possible phase loss on site. Unable to get generator to turn on, e-key not working on any locks on site. -Briefly left site to bump e-key at MTA WRRF. When back on site, e-key still not working. Cut lock to generator building. Generator screen is blank and unresponsive. Generator will not run in remote or manual. -0512 - Wessuc confirmed they have vac truck and tanker on route to site. -Electricians and PCS arrived at site and found multiple damaged pieces of equipment due to a suspected lightning strike on the building. They immediately began work to restore functionality of damaged equipment. -0631 - Wessuc informed of delays and that they were still approximately 1.5hrs away. -0645 - Informed SAC of ongoing spill. Spoke with environmental officer Edhilvia Campos and was assigned event# 1QG1QRG. -0655 - Informed York Region local health unit of ongoing spill. Spoke with health officer David Huang. -0700 - Notified LSCRA of ongoing spill. -0815 - Wessuc arrived on site and began setting up hoses to pump down wet well. Began pumping down wet well at approximately 0830. -0830 - Collected spill samples with Chris Rodie, CoC# W11769441. -0925 - Electricians able to get one pump running on site and began pumping down wet well to forcemain along with Wessuc pumping wet well to vac truck. -0957 - Wet well at 3.99m, below the overflow level. Spill has ended. -Kevin Shaji arrived at site to complete weekly sample collection. -When Wessuc had completed their emergency wet well pumping activities, accompanied vac truck to site of spill, which was a local East Gwillimbury manhole between the southeast corner of the Foodland parking lot and the railroad tracks. Wessuc cleaned solids and liquid from surrounding area, as well as removed excess solids from local sewer. While on site, visited by local Public Heath Inspector Darja Montsenko, who also observed spill location during cleanup and afterwards. -Instrumentation team on site to replace damaged flowmeter and level sensor. -Electricians and PCS team able to get both station pumps repaired and operational in auto. -Temporary generator set up on site and tested in manual and in auto, with a full station transfer test. -Composite sampler reset for 0700 April 7, 2026. Sample jug cleaned. -Security system and swipe card reader on site not working. Informed supervisor of issue and work request created. -Station is back running normally. Temporary generator set up on site. Both pumps available and in local. | 1 | 1 | 1
WW-CEAST | Mount Albert Pumping Station | 2026-03-31 | Attending site to replace wetwell level transmitter and flowmeter (W11769917). Devices were damaged due to electrical storm. Replaced, configured and tested wetwell level transmitter with Art. Parth and Rick replaced and configured discharge flowmeter. | 0.99985 | 1 | 1

## Mt. Albert WRRF
WW-CEAST | Mount Albert Water Resource Recovery Facility | 2026-03-01 | -On site for sludge handling and lab analysis. -Added two bags of soda ash to each aeration tank. -Unable to decant STT. Hose has multiple holes right above connection to decant pump and is producing no flow. Emptied approximately 2m out of STT to make room for auto wasting tonight. -Raked manual bar screen. -Completed lab analysis and entered results into SharePoint. -Ran RAS pumps at 100% speed for several minutes. -Verified sand filter operation and alum dosing. -Cleaned solids off top of post aeration alum chamber. -Verified clarifier heater are both still running. -OCU and traveling screen remain OOS. | 1 | 1 | 1
WW-CEAST | Mount Albert Water Resource Recovery Facility | 2026-03-03 | -On site to complete work orders. -Added two bags of soda ash to each aeration tank. -Raked manual bar screen. -Cleaned out RAS inlet chamber and post aeration alum chamber. Cleaned rags off aeration tank inlet gates and DO probes. -Station check completed, readings entered into SharePoint. -Verified alum dosing and sand filter operation. -Monthly diesel generator test run completed, readings entered into SharePoint. -1013 - Transferred station to generator power. -1122 - Station transferred back to utility power. -Generator start hours: 492.3, stop hours: 493.5, run time: 1.2hrs. -Switched grit bins following pick up. -Clarifier scum system cleaning completed. Cleaned out clarifier scum troughs, hosed down walls of scum tank and ran Scum Pump 1 in local to pump out tank following cleaning. -Traveling screen and OCU remain OOS. | 0.99999 | 1 | 1
WW-CEAST | Mount Albert Water Resource Recovery Facility | 2026-03-06 | Completed in-house lab Analysis (See details on SharePoint) Decanting STT into the Headworks. Transferred the sludge and processing. Added two bags each of Soda Ash into each Aeration Tanks Removed rags from the sluice gates of Aeration Tanks Post Filtration/UV channel hose down. Clarifier #1 taken OOS due to gearbox issue. Emptying clarifier #1 now. Bar screen put back to service. | 0.99999 | 1 | 1
WW-CEAST | Mount Albert Water Resource Recovery Facility | 2026-03-06 | put two bags of soda ash into the aeration tanks and set two up for later. Started grabbing samples for the Lab and Daniel had switched WO to Kevin,, went through the station and sand filters working great and started de-cant pump. Clarifier 1 arm stopped turning, got a hold of Bill (maintenance) and he's on his way. Cleaned out the post aeration tank as well as the inlet gates while waiting. There was no Hazardous waste to dispose of and went through the weekly alarm management for EOC and YDOC and there were no changes to either site. Started emptying clarifier #1 due to gear box in motor is broken - Daniel showed up and walked us through switching everything over. Continued draining for two hours and i'll be in on the weekend to complete. Bill and Terry - maintenance got the bar screen working again so we closed off the by-pass and now flow is going through the bar screen. Clarifier 1 is down but the rest of the station is running fine. | 1 | 1 | 1
WW-CEAST | Mount Albert Water Resource Recovery Facility | 2026-03-13 | On site completed work orders. Station Check (See details on SharePoint). STT decanted, afterwards remaining sludge dumped into the SHT. Added two bags of Soda Ash into each Aeration Tanks. Checked Alum dosing injection points at prefilter and post aeration. Removed rags from the inlet/outlet sluice gates at aeration tanks. Weekly alarm management - only clarifier 1 no RAS pump running is the alarm due to clarifier 1 out of service. Clarifier 1 sludge cleanout - ACCUWORX on site to clean clarifier 1 in preparation for the gear box repair/replacement. | 1 | 1 | 1
WW-CEAST | Mount Albert Water Resource Recovery Facility | 2026-03-19 | Put in 2 bags of soda ash and set 2 up for later,, Kevin started de-cant pump and then I worked with Kevin on his Lab work to speed it up and get a lot more organized. Went through the station, UV bank 1 is OOS - sand filters working great. Checked the hoist in the aeration room and the sand filter room - all good. Cleaned out the post aeration tank and the inlet channel gates, Washed down the UV channel and shut down the effluent pumps for the night to make sure we have no breaks again. Hopefully this helped Kevin out with his Lab work, UV 1 is OOS along with clarifier 1 the rest of the station is running fine. | 1 | 1 | 1
WW-CEAST | Mount Albert Water Resource Recovery Facility | 2026-03-23 | Put 4 bags of soda ash in and started de-cant pump,, Daniel and I isolated the inlet at the headworks and are diverting flow to the lagoon (@ approx. 08:25 ) Put 3 knife gates in place to re-direct flow to the lagoon. Accuworxs here and are pumping down post aeration tank, Retrieved the grating at approx. 14:00 hrs and then put the station back to normal ops by removing gates from the headworks. Station back to normal ops - clarifier 1 and UV bank 1A are still OOS. | 0.99973 | 1 | 1
WW-CEAST | Mount Albert Water Resource Recovery Facility | 2026-03-26 | -On site to complete work orders. -GFL/Accuworx on site for Clarifier 1 cleaning. -Two bags of soda ash added to each aeration tank. -Cleaned out RAS inlet chamber and post aeration alum mixing chamber. -Mechanics and electricians have completed repair work on Clarifier 1. Clarifier 1 locked out at local disconnect with station lock until clarifier cleaning is completed. -Worked on UV room cleaning. Removed old/broken items. Cleaned floors. -UV Bank 1A OOS, Clarifier 1 OOS, RAS Pump 3 OOS, WAS Pump 2 OOS, OCU OOS. | 1 | 1 | 1

## King City SPS
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS

## Black Creek SPS
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS
WW-WEST | Vaughan Black Creek Pumping Station | 2026-03-31 | onsite for station check - no new issues. reviewed trends and added data into sharepoint. pump run test: pump 1 - 553.1L/s at 300kPa pump 2 - 450.4L/s at 268lPa at 100% pump 3 - 133.0L/s at 214lPa at 100% pump 4 - 467.1L/s at 261kPa at 100% pump 5 - OOS (known issue) All pumps placed back into auto and back into duty rotation. pushed barscreen bin outside for pick up. completed comprehensive housekeeping - cleaned bathroom and entrance. | 0.99999 | 1 | 1
WW-WEST | Vaughan Black Creek Pumping Station | 2026-03-09 | Onsite for PMs with Marcus. Completed dry well consolidated inspection. Wetwell and barscreen consolidated inspection and air relief valve flushing. Created work order for pump 4 check valve not closing. | 0.98012 | 1 | 1
WW-WEST | Vaughan Black Creek Pumping Station | 2026-03-13 | Station checks, SharePoint readings and review of continuous monitoring data Level screen room bin and clean floor. Pump test runs on pump 1 & 4. - ok- Pump 3 running on entry and 2/5 OOS. | 0.99965 | 1 | 1
WW-WEST | Vaughan Black Creek Pumping Station | 2026-03-06 | Onsite for station check. Pump run test and seal water test pm. Station check ok - no new issues. Reviewed trends and added data into SharePoint. Pushed empty bin back in and topped up oil on bar screen. Pump run test : Pump1 - 601.7L/s at 281kPa Pump 2 - 469.9L/s at 100% at 257kPa Pump 3 - 133.3L/s at 100% at 214kPa Pump4 - 470.1L/s at 100% at 267kPA Pump 5 -OOS Completed seal water test PM no new issues. Checked seal water screens - all clear. | 0.036247 | 0 | 1
WW-WEST | Vaughan Black Creek Pumping Station | 2026-03-09 | In to Complete Scheduled WOs. Notified ROC. Manually Rotated Scrubber Blower Duties. Blower #2 in Duty #1, Pump #1 in Duty #2. Completed Bar-screen and Wet Well Inspections. Tested Wet Well Overflow Alarms. Confirmed Reception by the ROC. No Issues Found. Returned to Service. Cleared Associated Alarms. Completed Consolidated Dry Well Inspections. Tested Hi/Lo Temperature and Dry Well Flood Alarms. Confirmed Reception by the ROC. Returned to Service. Cleared Associated Alarms. Pump #2 Failed to Start on Several Attempts, Using Multiple Methods, Such as Manual Start and Auto Duty Start. Suspected Discharge Valve Communication Error. Created Follow Up WO for PCS ?> W11719088. Pump #2 Manual Off and OOS Until Issue Rectified. Completed FM Air Valve Flushing and Inspections with No Issues. Returned to Service. | 1 | 1 | 1
WW-WEST | Vaughan Black Creek Pumping Station | 2026-03-20 | Onsite for station check and weekly pump run test. No new issues. Reviewed trends and added data into SharePoint. Pump run test: Pump1 - 571.5L/s at 303kPa Pump 2 - OOS Pump 3 - 131.3L/s at 215kPa Pump4 - 473.8L/s at 269kPa Pump 5 -OOS After running pump 4 and placing it in manual off - discharge valve closed alarm came in. Reset and cleared alarm. Checked discharge and check valve all normal. Will continue to monitor. Returned all in service pumps back to auto. Pumps 2 and 5 left in manual off. Known issues with work orders created. Bar screen running and operating normally. | 1 | 1 | 1
WW-WEST | Vaughan Black Creek Pumping Station | 2026-03-17 | Onsite for station check - no new issues. Reviewed trends and entered data into SharePoint Pumps #2 and #5 still OOS - known issues with WO made Ran pump 4 to try to replicate the disch. Valve closed alarm from yesterday - alarm did not come in and pump ran normally. Checked contact on the valve and it appeared normal. Bin pushed out for pick up. Barscreen room ok. | 1 | 1 | 1

## Nobleton WRRF
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS
WW-WEST | Nobleton Water Resource Recovery Facility | 2026-03-30 | Received call from ROC for Mech. bar screen OOS alarm. (ongoing issue) Arrived onsite at 3:15am, Inlet channel hi level alarm present due to channel backing up. Reset bar screen and cleared alarms. Bar screen running operationally with no issues found - will continue to monitor. | 1 | 1 | 1
WW-WEST | Nobleton Water Resource Recovery Facility | 2026-03-06 | - Supernated sludge thickening tank. - Transferred sludge from the thickening tank to the sludge holding tank - Completed in-house lab and recorded readings on SharePoint. No issues. - Added 2 bags of soda ash each to aeration tank 1 and 2. - Checked station and recorded readings on SharePoint. - Enabled RAS batch wasting mode at 09:08. - Set auto wasting for 15 m^3 from train 1 and 15 m^3 from train 2 between 10:00 and 12:00. - Wasted another 5 m^3 from train 1. Then reset RAS batch wasting mode at 11:57. - Created W11714307 for alum pump 5. Pump works well in manual but displays error when analogue signal cable is plugged in. - Reduced air lift flow rates for both grit vortexes. Found the water was flowing too quickly over the weir. Flows slower and carries fewer solids over at the lower flow rate. | 0.99993 | 1 | 1
12433849 | https://mas.manage.prod.apps.prod.york.cohesivecloud.app/ezmaxmobile/elogbook/viewtask.action?id=12433849 | 1 | 2026-03-05 15:18 | 2026-03-05 15:07 | Young Jung (WW-WEST) @ Nobleton Water Resource Recovery Facility - NBSP Date Work Completed: 2026-03-05 15:07 ————————————————————— - Performed in-house lab and recorded readings on SharePoint. No issues - Added 2 bags of soda ash each to aeration tank 1 and 2 - Checked station and recorded readings on SharePoint - Enabled RAS batch wasting mode at 10:08. Wasted 15 m^3 from train 1 and 15 m^3 from train 2 then reset RAS batch wasting mode at 13:47 - Plant water booster pump is cycling too much. This eventually causes pumps to fault on high and low pressure. This issue seems to have been going on for a while. Upon inspection, it seems RT1 and RT2 temperature protection relay faulted and is showing red. In addition, the discharge side fails to maintain adequate pressure while the plant water demand is low (vortex water scour not active at the time, no plant water usage from hydrant, etc). This is causing the pump to cycle on constantly to boost the pressure. The pressure tank seems to be okay with no leaks. Pressure switch differential settings seem okay. The check valve seems to be the culprit. I’ve tried to isolate the lead pump, pump 1, and the hissing sound stopped but the system still loses pressure fast. Therefore, it seems to be leaking on both sides. Created work order for maintenance and notified team - Received soda as delivery at 14:50. Received 250 bags. Signed all papers ————————————————————— • Attachments: 0
WW-WEST | Nobleton Water Resource Recovery Facility | 2026-03-12 | Completed daily lab and added data into SharePoint. Completed station check - effluent pump still cycling on and off with high pressure, known issue with WO. Filter cell 4 plugged - unplugged and working normally. Other filter cells working well. Decanted sludge thickening tank. Placed WAS pumps and valves into auto and Enabled batch wasting at 830am and set auto waste for 30m3 from 10am to 12pm. Placed WAS pumps and valves back in manual upon wasting completion. Bled condensation from aeration condensation lines. Added 2 bags of soda ash to aeration tanks per train. Assisted Young and Harie with sludge pump PMs | 1 | 1 | 1
11531377 | https://mas.manage.prod.apps.prod.york.cohesivecloud.app/ezmaxmobile/elogbook/viewtask.action?id=11531377 | 1 | 2025-03-19 15:39 | 2025-03-19 15:38 | Young Jung (WW-WEST) @ Nobleton Water Resource Recovery Facility - NBSP Date Work Completed: 2025-03-19 15:38 ————————————————————— - Checked station and trends, and recorded readings on SharePoint - Reset exhaust fan 307 - Unclogged filter 1 north cell - Found flame failure alarm for the blower room. Notified TL - Smelled of gas near the makeup air unit above the headworks building. Notified TL and to create an Archibus - Reset plant water system - Assisted contractor for the noise study. Notified ROC that the generator will be turned on for the noise study. Turned on the generator at 11:41. Fuel level at 33 inch at start and once done, fuel level at 33 inch. Generator hours from 288.51 hrs to 289.18 hrs - Cleaned fly trap ————————————————————— • Attachments: 0
10646801 | https://mas.manage.prod.apps.prod.york.cohesivecloud.app/ezmaxmobile/elogbook/viewtask.action?id=10646801 | 1 | 2024-04-19 11:25 | 2024-04-19 11:21 | Young Jung (AREA 6) @ Nobleton Water Resource Recovery Facility - NBSP Date Work Completed: 2024-04-19 11:21 ————————————————————— Young Jung (OIT) working under the direction of Daniel Hirstwood (OIC) - checked station and performed in-house lab, and recorded readings on SharePoint - reset plant water system due to high and low pressure alarm - gave a tour of the plant to the WiFi team - transferred sludge from the sludge thickening tank to the sludge holding tank - GFL picked up a sludge load - wasted 20 m^3 from train 1 and 20 m^3 from train 2 then reset RAS batch wasting mode. Placed WAS valves back to manual off ————————————————————— • Attachments: 0
10646801 | https://mas.manage.prod.apps.prod.york.cohesivecloud.app/ezmaxmobile/elogbook/viewtask.action?id=10646801 | 1 | 2024-04-19 11:25 | 2024-04-19 11:21 | Young Jung (AREA 6) @ Nobleton Water Resource Recovery Facility - NBSP Date Work Completed: 2024-04-19 11:21 ————————————————————— Young Jung (OIT) working under the direction of Daniel Hirstwood (OIC) - checked station and performed in-house lab, and recorded readings on SharePoint - reset plant water system due to high and low pressure alarm - gave a tour of the plant to the WiFi team - transferred sludge from the sludge thickening tank to the sludge holding tank - GFL picked up a sludge load - wasted 20 m^3 from train 1 and 20 m^3 from train 2 then reset RAS batch wasting mode. Placed WAS valves back to manual off ————————————————————— • Attachments: 0
10439721 | https://mas.manage.prod.apps.prod.york.cohesivecloud.app/ezmaxmobile/elogbook/viewtask.action?id=10439721 | 1 | 2024-01-31 14:18 | 2024-01-31 14:15 | Young Jung (AREA 6) @ Nobleton Water Resource Recovery Facility - NBSP Date Work Completed: 2024-01-31 14:15 ————————————————————— Young Jung (OIT) working under the direction of Daniel Hirstwood (OIC) - Collected weekly regulatory samples - Decanted then transferred sludge from the sludge thickening tank to the sludge holding tank - Performed station check and in-house lab, and recorded readings on SharePoint. Reset plant water system due to high and low pressure alarm. - Enabled RAS batch wasting mode at 8:13. Turned WAS valve 2 and 3 to auto. Turned WAS pumps 1 and 2 to auto. - Wasted 25m^3 from clarifier 1 and 25m^3 from clarifier 2 then rest RAS batch wasting mode at 12:00. Once done, turned WAS valve 2 and 3 to manual. Turned WAS pumps 1 and 2 to manual off. - Added 1 bag of soda ash each to aeration tank 1 and tank 2 - Performed DO probe maintenance after holding outputs at the aeration tank 1 and tank 2. Cleaned sensor and removed rags. Checked DO readings, all okay. Removed outputs once done - Removed floating solids or debris from aeration tank 1 and tank 2 surfaces - Removed rags from the aeration tank 1 and tank 2 outlet weir - Bled air from the condensation line at the aeration tank 1 and tank 2 ————————————————————— • Attachments: 0

## Schomberg WRRF
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS
12463101 | https://mas.manage.prod.apps.prod.york.cohesivecloud.app/ezmaxmobile/elogbook/viewtask.action?id=12463101 | 1 | 2026-03-17 14:28 | 2026-03-17 14:25 | Marcus Remonde (WW-WEST) @ Schomberg Water Resource Recovery Facility - SHSP Date Work Completed: 2026-03-17 14:25 ————————————————————— In to Complete Scheduled WO. Notified ROC. Completed Consolidated Aer., Sludge and Vortex Blower Inspections. Topped Up Oil Reservoirs and Replaced Air Filters Where Necessary. All Belts OK. Returned to Service and Cleared Associated Alarms. Created Follow-Up WO Regarding Aer. Blower #1 Oil Leak for Maint. —> W11740816. ————————————————————— • Attachments: 0
12466420 | https://mas.manage.prod.apps.prod.york.cohesivecloud.app/ezmaxmobile/elogbook/viewtask.action?id=12466420 | 1 | 2026-03-18 14:50 | 2026-03-18 14:46 | Gavin Walker (WW-WEST) @ Schomberg Water Resource Recovery Facility - SHSP Date Work Completed: 2026-03-18 14:46 ————————————————————— Completed the station check and daily lab work Batch wasted 51m3 overnight Cleaned the DO probes Aeration blower 1 cooling fan faulted and cannot be reset Blower 1 is currently left out of service ————————————————————— • Attachments: 0
12475495 | https://mas.manage.prod.apps.prod.york.cohesivecloud.app/ezmaxmobile/elogbook/viewtask.action?id=12475495 | 1 | 2026-03-23 10:26 | 2026-03-23 10:23 | Bill Van Bakel (WW-MAINT) @ Schomberg Water Resource Recovery Facility - SHSP Date Work Completed: 2026-03-23 10:23 ————————————————————— On site for blower 1 oil leak. We will return with seals ————————————————————— • Worked With: Terry Cantwell • Attachments: 0

## Kleinburg WRRF
WW-WEST | Kleinburg Water Resource Recovery Facility | 2026-03-18 | Supernated STT and released to SHT. Completed labs and entered data in ace sheet. Completed station check. No issues found. Enabled was timer at 09:49. Set autowasting for 15 m3 per train in 3 cycles each between 10:00 and 12:00. Autowasting volumes are correct with waste pumps in auto speed. Added 8 bags to soda ash hopper. Completed housekeeping work order for headworks building. Completed DO probe maintenance. Created work order (W11744156) for service water pipe in need of re-securing to wall in headworks. | 0.99618 | 1

## Humber SPS
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS
WW-WEST | Vaughan Humber Pumping Station | 2026-03-16 | In to Investigate Bar-screen #2 Fault Communicated by the ROC. Found Bar-screen Torque Overload Fault due to Rake Misalignment. Placed Bar-screen in Local Off/OOS and Isolated Inlet Valve. Bar-screen #2 Not in Auto Alarm to Remain Outstanding. Adjusted Bar-screen #1 Run Time Interval: 12.5 ?> 6 mins. Created Follow-Up WO for Maint. ?> W11737270. Will Communicate with Appropriate Staff for Remedy at Next Earliest Convenience. | 1 | 1 | 1

## Holland Landing SPS
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS

## Joe Dales SPS
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS | 1

## Sutton WRRF
LOG ID | URL | VERSION | FIRST SAVED DATE | DATE WORK COMPLETED | LOG ENTRY DETAILS | 1
12429399 | https://maximo.york.ca/ezmaxmobile/elogbook/viewtask.action?id=12429399 | 2 | 2026-03-04 09:35 | 2026-03-04 09:33 | Eric Simanovskis (INST) @ Sutton Water Resource Recovery Facility - SUSP Date Work Completed: 2026-03-04 09:33 ————————————————————— Attending site to commission and verify the Lagoon Flowmeter - SUSP_SUSPLG_LGN_FIT1 (W11479921). Configured device, added asset number and verified function. ROC was notified before and after maintenance activities. ————————————————————— • Attachments: 0
WW-NORTH | Sutton Water Resource Recovery Facility | 2026-03-09 | Performed station check Decanted and transferred STT Completed lab analysis and entered readings into SharePoint GFL took sludge load 51m3 Upon arrival noticed dewatering screw press hopper, which is fed from the bar screen, was full. - Inspected screw press and found it to be sheered in half. - Switched bar screen and screw press to local off. - Pulled gate to manual bar screen and placed it into channel feeding offline bar screen. Maintenance on site to begin repairs on screw press. | 0.96616 | 1 | 0
WW-NORTH | Sutton Water Resource Recovery Facility | 2026-03-11 | 07:34 Diverted High St SPS to lagoon and returned Woodriver SPS to plant and placed lagoon pumps to manual off\ 11:36 Placed lagoon pumps back to auto Performed facility station check Completed Lab analysis: Data in Sharepoint Collected Weekly Samples: Sewage (W11656781) Raw @ 09:25 / Effluent @ 0920 Decanted Sludge holding tank Transferred Sludge thickening tank Inspected headworks: leveled grit bin and raked manual bar screen GFL hauled sludge = 51m3 Adjusted Lagoon hydrostatic level Lo alarm: 0.70 m ==> 0.30 m Equipment OOS: Mechanical bar screen | 1 | 1 | 1
WW-NORTH | Sutton Water Resource Recovery Facility | 2026-03-13 | On site for the broken screen auger and meet green frog. A quote was requested for a new auger | 0.99992 | 1 | 1
WW-NORTH | Sutton Water Resource Recovery Facility | 2026-03-20 | Performed facility station check Completed Lab analysis: Data in Sharepoint Decanted Sludge thickening tank Transferred Sludge holding tank Inspected headworks: leveled grit bin and raked manual bar screen Replaced ballast on UV Bank 1B: lamps 1/2- replaced with new ballast. Cleaned effluent sample jug and lines Equipment OOS: Mechanical bar screen and building effluent pump 2 | 0.99994 | 1 | 1
WW-NORTH | Sutton Water Resource Recovery Facility | 2026-03-23 | On site to finish install of effluent pump. Ran tested and put back in service. | 0.00043223 | 0 | 0
WW-NORTH | Sutton Water Resource Recovery Facility | 2026-03-31 | Diverted Woodriver Bend to lagoon @ 08:56 hrs Adjusted Flow bias max: 10 L/s --> 15 L/s Performed facility station check Completed Lab analysis: Data in Sharepoint Collected Weekly Samples: Sewage (W11705266) Raw @ 09:30 / Effluent @ 09:35 Decanted Sludge thickening tank Transferred Sludge holding tank Inspected headworks: leveled grit bin and raked manual bar screen GFL hauled sludge = 38 m3 Diverted Woodriver Bend to lagoon at 08:56 hrs Adjusted Flow bias max: 10 L/s --> 15 L/s Filter B-F3 airlift not throwing sand- pulled and is now functioning Filter A-F1 airlift not throwing sand and unable to pull up airlift. Lanced with air but still unable to budge. Will continue troubleshooting tomorrow Equipment OOS: Mechanical bar screen | 1 | 1 | 1